## spec
Param_ID | Value
RM22TG20
RM22TG20standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22TG20product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TG20marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TG20directives | 2014/35/EU
RM22TG20directives | 2014/30/EU
RM22TG20directives | 2011/65/EU
RM22TG20
RM22TG20 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM22TG20 | Class C ¦ Germanisher Lloyd,Environmental category,
RM22TG20ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22TG20ambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM22TG20relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM22TG20 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22TG20vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22TG20shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22TG20bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22TG20seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22TG20IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22TG20IP degree of protection | IP40 ¦ IEC60529,Housing,
RM22TG20IP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22TG20
RM22TG20width | 22.5 ¦ ,Width,
RM22TG20height | 90 ¦ ,Height,
RM22TG20depth | 73 ¦ ,Depth,
RM22TG20net weight | 95
RM22TG20mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22TG20mounting support | - ¦ IEC/EN 60715,With socket,
RM22TG20mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22TG20Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM22TG20Minimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM22TG20connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22TG20connections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22TG20connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22TG20connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22TG20tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM22TG20cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM22TG20duty time | 1
RM22TG20
RM22TG20electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22TG20electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22TG20electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22TG20electromagnetic compatibility | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22TG20electromagnetic compatibility | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22TG20electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22TG20electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22TG20electromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22TG20electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22TG20electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM22TG20electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22TG20electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22TG20electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22TG20electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22TG20electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22TG20electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22TG20electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22TG20electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22TG20electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22TG20
RM22TG20pollution degree | 3 ¦ IEC60664-1
RM22TG20overvoltage category | 3 ¦ IEC60664-1
RM22TG20circuit group | L1, L2, L3 ¦ ,Supply,Terminal
RM22TG20circuit group | - ¦ ,Input 1,
RM22TG20circuit group | - ¦ ,Input 2,
RM22TG20circuit group | - ¦ ,Input 3,
RM22TG20circuit group | 11,12,14 ¦ ,Output 1,
RM22TG20circuit group | 21,22,24 ¦ ,Output 2,
RM22TG20 | 208..480 AC ¦ ,Supply,Rated
RM22TG20 | - ¦ ,Input 1,Voltage
RM22TG20 | - ¦ ,Input 2,Spec
RM22TG20 | - ¦ ,Input 3,
RM22TG20 | 250V ¦ ,Output 1,
RM22TG20 | 250V ¦ ,Output 2,
RM22TG20[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM22TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM22TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM22TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM22TG20[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22TG20[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22TG20[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM22TG20[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 2,
RM22TG20[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM22TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22TG20[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22TG20[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22TG20[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22TG20[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22TG20dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM22TG20dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM22TG20dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM22TG20dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22TG20dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22TG20dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22TG20dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM22TG20dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM22TG20dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM22TG20dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM22TG20dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM22TG20dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM22TG20dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22TG20dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22TG20dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22TG20insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM22TG20insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM22TG20insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM22TG20insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22TG20insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22TG20insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22TG20insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM22TG20insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM22TG20insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM22TG20insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM22TG20insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM22TG20insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM22TG20insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22TG20insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22TG20insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22TG20
RM22TG20[Us] rated supply voltage | ~ 3 x 208…3 x 480
RM22TG20supply voltage limits | ~ 3 x 183…3 x 528
RM22TG20polarity | -
RM22TG20supply frequency | 50 / 60
RM22TG20supply frequency | 45…66
RM22TG20power consumption | 18VA @ 480VAC, 60Hz 12VA @ 400VAC, 50Hz
RM22TG20immunity to microbreaks | 0
RM22TG20supply terminal | L1-L3
RM22TG20on-load factor | 1
RM22TG20release of input voltage | -
RM22TG20
RM22TG20monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost ,
RM22TG20monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence,
RM22TG20monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TG20monitoring functions | - ¦ ,Over voltage,
RM22TG20monitoring functions | - ¦ ,Undervoltage ,
RM22TG20monitoring functions | - ¦ ,Phase asymmetry,
RM22TG20monitoring functions | - ¦ ,Disconnection of neutral,
RM22TG20monitoring functions | - ¦ ,Voltage Regeneration,
RM22TG20monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage,
RM22TG20monitoring functions | - ¦ ,Extreme overvoltage,
RM22TG20monitoring functions | - ¦ ,Extreme asymmetry,
RM22TG20 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM22TG20internal input resistance | - ¦ ,Internal input resistance,
RM22TG20input terminal | L1-L2-L3 ¦ ,Input terminal,
RM22TG20Input nominal voltage selection | - ¦ ,Input nominal voltage selection,
RM22TG20permissible input overload | - ¦ ,permissible input overload,
RM22TG20input frequency | 50 / 60 ¦ ,Rated frequency,
RM22TG20input frequency | 45…66 ¦ ,Frequency operating range,
RM22TG20setting accuracy of the switching threshold | - ¦ ,Setting accuracy,
RM22TG20repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22TG20measurement method | Non True RMS ¦ ,Measurement method,
RM22TG20switching threshold drift | - ¦ ,Measurement error with supply voltage variation,
RM22TG20switching threshold drift | - ¦ ,Measurement error with temperature variation,
RM22TG20maximum measuring cycle | - ¦ ,Maximum measuring cycles,
RM22TG20measurement range | - ¦ ,Phase lost ,
RM22TG20measurement range | - ¦ ,Phase sequence,
RM22TG20measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TG20measurement range | - ¦ ,Over voltage,
RM22TG20measurement range | - ¦ ,Undervoltage ,
RM22TG20measurement range | - ¦ ,Phase asymmetry,
RM22TG20measurement range | - ¦ ,Disconnection of neutral,
RM22TG20measurement range | - ¦ ,Voltage Regeneration,
RM22TG20measurement range | - ¦ ,Extreme undervoltage,
RM22TG20measurement range | - ¦ ,Extreme Overvoltage,
RM22TG20measurement range | - ¦ ,Extreme Asymmetry,
RM22TG20tripping threshold | 1 or more phase cut ¦ ,Phase cut,
RM22TG20tripping threshold | Total swap of phase Internal design spec: L31 lag L21 =< 10o or L31 lag L21 >= 150o ¦ ,Phase sequence,
RM22TG20tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TG20tripping threshold | - ¦ ,Over voltage,
RM22TG20tripping threshold | - ¦ ,Undervoltage ,
RM22TG20tripping threshold | - ¦ ,Phase asymmetry,
RM22TG20tripping threshold | - ¦ ,Disconnection of neutral,
RM22TG20tripping threshold | - ¦ ,Voltage Regeneration,
RM22TG20tripping threshold | 2 or more phase < 100V Internal design spec: 2 or more phase <150V +/- 10% ¦ ,Extreme undervoltage (Phase loss),
RM22TG20tripping threshold | - ¦ ,Extreme Overvoltage,
RM22TG20tripping threshold | - ¦ ,Extreme Asymmetry,
RM22TG20hysteresis | All phase cut recover ¦ ,Phase cut,
RM22TG20hysteresis | Total phase swap recover Internal design spec: L31 lag L21 >= 15o or L31 lag L21 <= 135o ¦ ,Phase sequence,
RM22TG20hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TG20hysteresis | - ¦ ,Over voltage,
RM22TG20hysteresis | - ¦ ,Undervoltage ,
RM22TG20hysteresis | - ¦ ,Phase asymmetry,
RM22TG20hysteresis | - ¦ ,Disconnection of neutral,
RM22TG20hysteresis | - ¦ ,Voltage Regeneration,
RM22TG20hysteresis | All phases > 183V Internal design spec: All phases >153V +/- 10% ¦ ,Extreme undervoltage (Phase loss),
RM22TG20hysteresis | - ¦ ,Extreme Overvoltage,
RM22TG20hysteresis | - ¦ ,Extreme Asymmetry,
RM22TG20
RM22TG20output type | 2 x C/O relay contacts
RM22TG20output terminal | 15-16-18, 25-26-28
RM22TG20output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22TG20output logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22TG20contacts material | Cadmium free
RM22TG20mechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22TG20electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22TG20electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22TG20electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22TG20electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22TG20[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22TG20[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22TG20maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22TG20maximum switching capacity | 8A ¦ ,Maximum switching current,
RM22TG20maximum switching capacity | - ¦ ,Maximum switching capacity,
RM22TG20minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22TG20minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22TG20minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22TG20maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22TG20maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22TG20thermal current | 8A ¦ IEC60947-5-1
RM22TG20short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22TG20short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22TG20
RM22TG20time delay type | Yes ¦ ,"OFF" delay,
RM22TG20time delay type | - ¦ ,"ON" delay,
RM22TG20time delay type | - ¦ ,Inhibition,
RM22TG20time delay range | - ¦ ,"OFF" delay,
RM22TG20time delay range | - ¦ ,"ON" delay,
RM22TG20time delay range | - ¦ ,Inhibition,
RM22TG20response time | 0
RM22TG20response time | -
RM22TG20response time | -
RM22TG20response time | -
RM22TG20response time | -
RM22TG20power on delay | 0
RM22TG20reset time | 0
RM22TG20reset time | - ¦ ,through front panel reset,
RM22TG20reset time | - ¦ ,through input control reset,
RM22TG20setting accuracy of time delay | -
RM22TG20repeat accuracy of time delay | -
RM22TG20time delay drift | -
RM22TG20time delay drift | -
RM22TG20
RM22TG20status LED | Un (Green) R (Amber)
RM22TG20local signalling | Un - ON ¦ ,Power supply availability,
RM22TG20local signalling | Un - OFF ¦ ,Power supply not availability,
RM22TG20local signalling | - ¦ ,Timing in-progress,
RM22TG20local signalling | R - ON ¦ ,Output is energized,
RM22TG20local signalling | R - OFF ¦ ,Output is de-energized,
RM22TG20local signalling | - ¦ ,Range Setting Changes,
RM22TG20local signalling | - ¦ ,Phase Cut,
RM22TG20local signalling | - ¦ ,Phase Sequence Swap,
RM22TG20local signalling | - ¦ ,Undervoltage <U,
RM22TG20local signalling | - ¦ ,Overvoltage >U,
RM22TG20local signalling | - ¦ ,Phase Asymmetry,
RM22TG20local signalling | - ¦ ,Voltage Regeneration,
RM22TG20local signalling | - ¦ ,Extreme Undervoltage <U (Phase loss),
RM22TG20local signalling | - ¦ ,Extreme Overvoltage >U,
RM22TG20local signalling | - ¦ ,Extreme Phase Asymmetry,
RM22TG20
RM22TG20 | No
RM22TG20 | 1) Will always illuminated when power is supplied to the product
RM22TG20diagnostic button | Output will be de-energized when activated
RM22TG20 | -
RM22TG20 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22TG20
RM22TG20safety reliability data | 8,100,000 hours ¦ ,MTTF,
RM22TG20safety reliability data | 850,000 hours ¦ ,B10,
RM22TG20 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22TG20 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22TG20
RM22TG20 | Drawing / Diagram
RM22TR33
RM22TR33standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22TR33product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TR33marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TR33directives | 2014/35/EU
RM22TR33directives | 2014/30/EU
RM22TR33directives | 2011/65/EU
RM22TR33
RM22TR33 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM22TR33 | Class C ¦ Germanisher Lloyd,Environmental category,
RM22TR33ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22TR33ambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM22TR33relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM22TR33 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22TR33vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22TR33shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22TR33bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22TR33seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22TR33IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22TR33IP degree of protection | IP40 ¦ IEC60529,Housing,
RM22TR33IP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22TR33
RM22TR33width | 22.5 ¦ ,Width,
RM22TR33height | 90 ¦ ,Height,
RM22TR33depth | 73 ¦ ,Depth,
RM22TR33net weight | 95
RM22TR33mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22TR33mounting support | - ¦ IEC/EN 60715,With socket,
RM22TR33mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22TR33Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM22TR33Minimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM22TR33connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22TR33connections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22TR33connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22TR33connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22TR33tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM22TR33cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM22TR33duty time | 1
RM22TR33
RM22TR33electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22TR33electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22TR33electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22TR33electromagnetic compatibility | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22TR33electromagnetic compatibility | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22TR33electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22TR33electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22TR33electromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22TR33electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22TR33electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM22TR33electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22TR33electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22TR33electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22TR33electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22TR33electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22TR33electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22TR33electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22TR33electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22TR33electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22TR33
RM22TR33pollution degree | 3 ¦ IEC60664-1
RM22TR33overvoltage category | 3 ¦ IEC60664-1
RM22TR33circuit group | L1, L2, L3 ¦ ,Supply,Terminal
RM22TR33circuit group | - ¦ ,Input 1,
RM22TR33circuit group | - ¦ ,Input 2,
RM22TR33circuit group | - ¦ ,Input 3,
RM22TR33circuit group | 11,12,14 ¦ ,Output 1,
RM22TR33circuit group | 21,22,24 ¦ ,Output 2,
RM22TR33 | 380..480 AC ¦ ,Supply,Rated
RM22TR33 | - ¦ ,Input 1,Voltage
RM22TR33 | - ¦ ,Input 2,Spec
RM22TR33 | - ¦ ,Input 3,
RM22TR33 | 250V ¦ ,Output 1,
RM22TR33 | 250V ¦ ,Output 2,
RM22TR33[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM22TR33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM22TR33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM22TR33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM22TR33[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22TR33[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22TR33[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22TR33[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22TR33[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22TR33[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM22TR33[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 2,
RM22TR33[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22TR33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM22TR33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22TR33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22TR33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22TR33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22TR33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22TR33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22TR33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22TR33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22TR33[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22TR33[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22TR33[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22TR33[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22TR33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22TR33dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM22TR33dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM22TR33dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM22TR33dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22TR33dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22TR33dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22TR33dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM22TR33dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM22TR33dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM22TR33dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM22TR33dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM22TR33dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM22TR33dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22TR33dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22TR33dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22TR33insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM22TR33insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM22TR33insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM22TR33insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22TR33insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22TR33insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22TR33insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM22TR33insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM22TR33insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM22TR33insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM22TR33insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM22TR33insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM22TR33insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22TR33insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22TR33insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22TR33
RM22TR33[Us] rated supply voltage | ~ 3 x 380… 3 x 480
RM22TR33supply voltage limits | ~ 3 x 304…3 x 576
RM22TR33polarity | -
RM22TR33supply frequency | 50 / 60
RM22TR33supply frequency | 45…66
RM22TR33power consumption | 18VA @ 480VAC, 60Hz 12VA @ 400VAC, 50Hz
RM22TR33immunity to microbreaks | 0
RM22TR33supply terminal | L1-L3
RM22TR33on-load factor | 1
RM22TR33release of input voltage | -
RM22TR33
RM22TR33monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost ,
RM22TR33monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence,
RM22TR33monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Over / undervoltage (symmetry windows mode),
RM22TR33monitoring functions | - ¦ ,Over voltage,
RM22TR33monitoring functions | - ¦ ,Undervoltage ,
RM22TR33monitoring functions | - ¦ ,Phase asymmetry,
RM22TR33monitoring functions | - ¦ ,Disconnection of neutral,
RM22TR33monitoring functions | - ¦ ,Voltage Regeneration,
RM22TR33monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage,
RM22TR33monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage,
RM22TR33monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM22TR33 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM22TR33internal input resistance | - ¦ ,Internal input resistance,
RM22TR33input terminal | L1-L2-L3 ¦ ,Input terminal,
RM22TR33Input nominal voltage selection | 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM22TR33permissible input overload | - ¦ ,permissible input overload,
RM22TR33input frequency | 50 / 60 ¦ ,Rated frequency,
RM22TR33input frequency | 45…66 ¦ ,Frequency operating range,
RM22TR33setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM22TR33repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22TR33measurement method | True RMS ¦ ,Measurement method,
RM22TR33switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation,
RM22TR33switching threshold drift | < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22TR33maximum measuring cycle | 170ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM22TR33measurement range | - ¦ ,Phase lost ,
RM22TR33measurement range | - ¦ ,Phase sequence,
RM22TR33measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TR33measurement range | +2…+20 % in the ranges 3 x 380…480 ¦ ,Over voltage,
RM22TR33measurement range | -2…-20 % in the ranges 3 x 380…480 ¦ ,Undervoltage ,
RM22TR33measurement range | - ¦ ,Phase asymmetry,
RM22TR33measurement range | - ¦ ,Disconnection of neutral,
RM22TR33measurement range | - ¦ ,Voltage Regeneration,
RM22TR33measurement range | - ¦ ,Extreme undervoltage,
RM22TR33measurement range | - ¦ ,Extreme Overvoltage,
RM22TR33measurement range | - ¦ ,Extreme Asymmetry,
RM22TR33tripping threshold | 1 or more phase cut ¦ ,Phase cut,
RM22TR33tripping threshold | Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence,
RM22TR33tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TR33tripping threshold | Adjustable 2%...20% of selected Un ¦ ,Over voltage,
RM22TR33tripping threshold | Adjustable 2%...20% of selected Un ¦ ,Undervoltage ,
RM22TR33tripping threshold | - ¦ ,Phase asymmetry,
RM22TR33tripping threshold | - ¦ ,Disconnection of neutral,
RM22TR33tripping threshold | - ¦ ,Voltage Regeneration,
RM22TR33tripping threshold | 1 or more phase < 250V Internal design spec: 1 or more phase <290V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM22TR33tripping threshold | Internal design spec: 593V +/- 5% ¦ ,Extreme Overvoltage,
RM22TR33tripping threshold | Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM22TR33hysteresis | All phase cut recover ¦ ,Phase cut,
RM22TR33hysteresis | Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence,
RM22TR33hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TR33hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Over voltage,
RM22TR33hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage ,
RM22TR33hysteresis | - ¦ ,Phase asymmetry,
RM22TR33hysteresis | - ¦ ,Disconnection of neutral,
RM22TR33hysteresis | - ¦ ,Voltage Regeneration,
RM22TR33hysteresis | All phases > 315V Internal design spec: All phases >296V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM22TR33hysteresis | Internal design spec: All phases <583V +/- 5% ¦ ,Extreme Overvoltage,
RM22TR33hysteresis | - ¦ ,Extreme Asymmetry,
RM22TR33
RM22TR33output type | 2 x C/O relay contacts
RM22TR33output terminal | 15-16-18, 25-26-28
RM22TR33output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22TR33output logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22TR33contacts material | Cadmium free
RM22TR33mechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22TR33electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22TR33electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22TR33electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22TR33electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22TR33[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22TR33[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22TR33maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22TR33maximum switching capacity | 8A ¦ ,Maximum switching current,
RM22TR33maximum switching capacity | - ¦ ,Maximum switching capacity,
RM22TR33minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22TR33minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22TR33minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22TR33maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22TR33maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22TR33thermal current | 8A ¦ IEC60947-5-1
RM22TR33short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22TR33short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22TR33
RM22TR33time delay type | Yes ¦ ,"OFF" delay,
RM22TR33time delay type | Yes ¦ ,"ON" delay,
RM22TR33time delay type | - ¦ ,Inhibition,
RM22TR33time delay range | Adjustable 0.1…30 ¦ ,"OFF" delay,
RM22TR33time delay range | Adjustable 0.1…30 ¦ ,"ON" delay,
RM22TR33time delay range | - ¦ ,Inhibition,
RM22TR33response time | 0
RM22TR33response time | -
RM22TR33response time | -
RM22TR33response time | -
RM22TR33response time | -
RM22TR33power on delay | 0
RM22TR33reset time | 0
RM22TR33reset time | - ¦ ,through front panel reset,
RM22TR33reset time | - ¦ ,through input control reset,
RM22TR33setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM22TR33repeat accuracy of time delay | +/- 3%
RM22TR33time delay drift | < 1
RM22TR33time delay drift | < 0.05
RM22TR33
RM22TR33status LED | Dial pointer (Green) R (Amber) Def (Red)
RM22TR33local signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22TR33local signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22TR33local signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22TR33local signalling | R - ON ¦ ,Output is energized,
RM22TR33local signalling | R - OFF ¦ ,Output is de-energized,
RM22TR33local signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22TR33local signalling | Def - Permanent OFF ¦ ,Phase Cut,
RM22TR33local signalling | Def - Permanent ON ¦ ,Phase Sequence Swap,
RM22TR33local signalling | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Undervoltage <U,
RM22TR33local signalling | Def - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Overvoltage >U,
RM22TR33local signalling | - ¦ ,Phase Asymmetry,
RM22TR33local signalling | - ¦ ,Voltage Regeneration,
RM22TR33local signalling | Def - Permanent OFF ¦ ,Extreme Undervoltage <U (Phase loss),
RM22TR33local signalling | Def - Permanent ON ¦ ,Extreme Overvoltage >U,
RM22TR33local signalling | - ¦ ,Extreme Phase Asymmetry,
RM22TR33
RM22TR33 | Yes
RM22TR33 | 1) Will always illuminated when power is supplied to the product
RM22TR33diagnostic button | Output will be de-energized when activated
RM22TR33 | -
RM22TR33 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22TR33
RM22TR33safety reliability data | 3,400,000 hours ¦ ,MTTF,
RM22TR33safety reliability data | 350,000 hours ¦ ,B10,
RM22TR33 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22TR33 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22TR33
RM22TR33 | Drawing / Diagram
RM22TR31
RM22TR31standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22TR31product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TR31marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TR31directives | 2014/35/EU
RM22TR31directives | 2014/30/EU
RM22TR31directives | 2011/65/EU
RM22TR31
RM22TR31 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM22TR31 | Class C ¦ Germanisher Lloyd,Environmental category,
RM22TR31ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22TR31ambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM22TR31relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM22TR31 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22TR31vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22TR31shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22TR31bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22TR31seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22TR31IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22TR31IP degree of protection | IP40 ¦ IEC60529,Housing,
RM22TR31IP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22TR31
RM22TR31width | 22.5 ¦ ,Width,
RM22TR31height | 90 ¦ ,Height,
RM22TR31depth | 73 ¦ ,Depth,
RM22TR31net weight | 95
RM22TR31mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22TR31mounting support | - ¦ IEC/EN 60715,With socket,
RM22TR31mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22TR31Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM22TR31Minimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM22TR31connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22TR31connections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22TR31connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22TR31connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22TR31tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM22TR31cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM22TR31duty time | 1
RM22TR31
RM22TR31electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22TR31electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22TR31electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22TR31electromagnetic compatibility | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22TR31electromagnetic compatibility | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22TR31electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22TR31electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22TR31electromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22TR31electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22TR31electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM22TR31electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22TR31electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22TR31electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22TR31electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22TR31electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22TR31electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22TR31electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22TR31electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22TR31electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22TR31
RM22TR31pollution degree | 3 ¦ IEC60664-1
RM22TR31overvoltage category | 3 ¦ IEC60664-1
RM22TR31circuit group | L1, L2, L3 ¦ ,Supply,Terminal
RM22TR31circuit group | - ¦ ,Input 1,
RM22TR31circuit group | - ¦ ,Input 2,
RM22TR31circuit group | - ¦ ,Input 3,
RM22TR31circuit group | 11,12,14 ¦ ,Output 1,
RM22TR31circuit group | 21,22,24 ¦ ,Output 2,
RM22TR31 | 208..240 AC ¦ ,Supply,Rated
RM22TR31 | - ¦ ,Input 1,Voltage
RM22TR31 | - ¦ ,Input 2,Spec
RM22TR31 | - ¦ ,Input 3,
RM22TR31 | 250V ¦ ,Output 1,
RM22TR31 | 250V ¦ ,Output 2,
RM22TR31[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM22TR31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM22TR31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM22TR31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM22TR31[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22TR31[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22TR31[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22TR31[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22TR31[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22TR31[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM22TR31[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 2,
RM22TR31[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22TR31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM22TR31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22TR31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22TR31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22TR31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22TR31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22TR31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22TR31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22TR31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22TR31[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22TR31[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22TR31[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22TR31[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22TR31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22TR31dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM22TR31dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM22TR31dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM22TR31dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22TR31dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22TR31dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22TR31dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM22TR31dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM22TR31dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM22TR31dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM22TR31dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM22TR31dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM22TR31dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22TR31dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22TR31dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22TR31insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM22TR31insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM22TR31insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM22TR31insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22TR31insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22TR31insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22TR31insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM22TR31insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM22TR31insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM22TR31insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM22TR31insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM22TR31insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM22TR31insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22TR31insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22TR31insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22TR31
RM22TR31[Us] rated supply voltage | ~ 3 x 200…3 x 240
RM22TR31supply voltage limits | ~ 3 x 160…3 x 288
RM22TR31polarity | -
RM22TR31supply frequency | 50 / 60
RM22TR31supply frequency | 45…66
RM22TR31power consumption | 10VA @ 240VAC, 60Hz
RM22TR31immunity to microbreaks | 0
RM22TR31supply terminal | L1-L3
RM22TR31on-load factor | 1
RM22TR31release of input voltage | -
RM22TR31
RM22TR31monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost ,
RM22TR31monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence,
RM22TR31monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Over / undervoltage (symmetry windows mode),
RM22TR31monitoring functions | - ¦ ,Over voltage,
RM22TR31monitoring functions | - ¦ ,Undervoltage ,
RM22TR31monitoring functions | - ¦ ,Phase asymmetry,
RM22TR31monitoring functions | - ¦ ,Disconnection of neutral,
RM22TR31monitoring functions | - ¦ ,Voltage Regeneration,
RM22TR31monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage,
RM22TR31monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage,
RM22TR31monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM22TR31 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM22TR31internal input resistance | - ¦ ,Internal input resistance,
RM22TR31input terminal | L1-L2-L3 ¦ ,Input terminal,
RM22TR31Input nominal voltage selection | 200, 208, 220, 240 ¦ ,Input nominal voltage selection,
RM22TR31permissible input overload | - ¦ ,permissible input overload,
RM22TR31input frequency | 50 / 60 ¦ ,Rated frequency,
RM22TR31input frequency | 45…66 ¦ ,Frequency operating range,
RM22TR31setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM22TR31repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22TR31measurement method | True RMS ¦ ,Measurement method,
RM22TR31switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation,
RM22TR31switching threshold drift | < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22TR31maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM22TR31measurement range | - ¦ ,Phase lost ,
RM22TR31measurement range | - ¦ ,Phase sequence,
RM22TR31measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TR31measurement range | +2…+20 % in the ranges 3 x ~200…240 ¦ ,Over voltage,
RM22TR31measurement range | -2…-20 % in the ranges 3 x ~ 200…240 ¦ ,Undervoltage ,
RM22TR31measurement range | - ¦ ,Phase asymmetry,
RM22TR31measurement range | - ¦ ,Disconnection of neutral,
RM22TR31measurement range | - ¦ ,Voltage Regeneration,
RM22TR31measurement range | - ¦ ,Extreme undervoltage,
RM22TR31measurement range | - ¦ ,Extreme Overvoltage,
RM22TR31measurement range | - ¦ ,Extreme Asymmetry,
RM22TR31tripping threshold | 1 or more phase cut ¦ ,Phase cut,
RM22TR31tripping threshold | Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence,
RM22TR31tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TR31tripping threshold | Adjustable 2%...20% of selected Un ¦ ,Over voltage,
RM22TR31tripping threshold | Adjustable 2%...20% of selected Un ¦ ,Undervoltage ,
RM22TR31tripping threshold | - ¦ ,Phase asymmetry,
RM22TR31tripping threshold | - ¦ ,Disconnection of neutral,
RM22TR31tripping threshold | - ¦ ,Voltage Regeneration,
RM22TR31tripping threshold | 1 or more phase < 150V Internal design spec: 1 or more phase <160V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM22TR31tripping threshold | Internal design spec: 297V +/- 5% ¦ ,Extreme Overvoltage,
RM22TR31tripping threshold | Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM22TR31hysteresis | All phase cut recover ¦ ,Phase cut,
RM22TR31hysteresis | Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence,
RM22TR31hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TR31hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Over voltage,
RM22TR31hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage ,
RM22TR31hysteresis | - ¦ ,Phase asymmetry,
RM22TR31hysteresis | - ¦ ,Disconnection of neutral,
RM22TR31hysteresis | - ¦ ,Voltage Regeneration,
RM22TR31hysteresis | All phases > 175V Internal design spec: All phases >163V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM22TR31hysteresis | Internal design spec: All phases <287V +/- 5% ¦ ,Extreme Overvoltage,
RM22TR31hysteresis | - ¦ ,Extreme Asymmetry,
RM22TR31
RM22TR31output type | 2 x C/O relay contacts
RM22TR31output terminal | 15-16-18, 25-26-28
RM22TR31output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22TR31output logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22TR31contacts material | Cadmium free
RM22TR31mechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22TR31electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22TR31electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22TR31electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22TR31electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22TR31[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22TR31[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22TR31maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22TR31maximum switching capacity | 8A ¦ ,Maximum switching current,
RM22TR31maximum switching capacity | - ¦ ,Maximum switching capacity,
RM22TR31minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22TR31minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22TR31minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22TR31maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22TR31maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22TR31thermal current | 8A ¦ IEC60947-5-1
RM22TR31short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22TR31short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22TR31
RM22TR31time delay type | Yes ¦ ,"OFF" delay,
RM22TR31time delay type | Yes ¦ ,"ON" delay,
RM22TR31time delay type | - ¦ ,Inhibition,
RM22TR31time delay range | Adjustable 0.1…30 ¦ ,"OFF" delay,
RM22TR31time delay range | Adjustable 0.1…30 ¦ ,"ON" delay,
RM22TR31time delay range | - ¦ ,Inhibition,
RM22TR31response time | 0
RM22TR31response time | -
RM22TR31response time | -
RM22TR31response time | -
RM22TR31response time | -
RM22TR31power on delay | 0
RM22TR31reset time | 0
RM22TR31reset time | - ¦ ,through front panel reset,
RM22TR31reset time | - ¦ ,through input control reset,
RM22TR31setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM22TR31repeat accuracy of time delay | +/- 3%
RM22TR31time delay drift | < 1
RM22TR31time delay drift | < 0.05
RM22TR31
RM22TR31status LED | Dial pointer (Green) R (Amber) Def (Red)
RM22TR31local signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22TR31local signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22TR31local signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22TR31local signalling | R - ON ¦ ,Output is energized,
RM22TR31local signalling | R - OFF ¦ ,Output is de-energized,
RM22TR31local signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22TR31local signalling | Def - Permanent OFF ¦ ,Phase Cut,
RM22TR31local signalling | Def - Permanent ON ¦ ,Phase Sequence Swap,
RM22TR31local signalling | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Undervoltage <U,
RM22TR31local signalling | Def - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Overvoltage >U,
RM22TR31local signalling | - ¦ ,Phase Asymmetry,
RM22TR31local signalling | - ¦ ,Voltage Regeneration,
RM22TR31local signalling | Def - Permanent OFF ¦ ,Extreme Undervoltage <U (Phase loss),
RM22TR31local signalling | Def - Permanent ON ¦ ,Extreme Overvoltage >U,
RM22TR31local signalling | - ¦ ,Extreme Phase Asymmetry,
RM22TR31
RM22TR31 | Yes
RM22TR31 | 1) Will always illuminated when power is supplied to the product
RM22TR31diagnostic button | Output will be de-energized when activated
RM22TR31 | -
RM22TR31 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22TR31
RM22TR31safety reliability data | 3,400,000 hours ¦ ,MTTF,
RM22TR31safety reliability data | 350,000 hours ¦ ,B10,
RM22TR31 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22TR31 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22TR31
RM22TR31 | Drawing / Diagram
RM22TU23
RM22TU23standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22TU23product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TU23marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TU23directives | 2014/35/EU
RM22TU23directives | 2014/30/EU
RM22TU23directives | 2011/65/EU
RM22TU23
RM22TU23 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM22TU23 | Class C ¦ Germanisher Lloyd,Environmental category,
RM22TU23ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22TU23ambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM22TU23relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM22TU23 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22TU23vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22TU23shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22TU23bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22TU23seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22TU23IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22TU23IP degree of protection | IP40 ¦ IEC60529,Housing,
RM22TU23IP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22TU23
RM22TU23width | 22.5 ¦ ,Width,
RM22TU23height | 90 ¦ ,Height,
RM22TU23depth | 73 ¦ ,Depth,
RM22TU23net weight | 95
RM22TU23mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22TU23mounting support | - ¦ IEC/EN 60715,With socket,
RM22TU23mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22TU23Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM22TU23Minimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM22TU23connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22TU23connections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22TU23connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22TU23connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22TU23tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM22TU23cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM22TU23duty time | 1
RM22TU23
RM22TU23electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22TU23electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22TU23electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22TU23electromagnetic compatibility | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22TU23electromagnetic compatibility | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22TU23electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22TU23electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22TU23electromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22TU23electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22TU23electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM22TU23electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22TU23electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22TU23electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22TU23electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22TU23electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22TU23electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22TU23electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22TU23electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22TU23electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22TU23
RM22TU23pollution degree | 3 ¦ IEC60664-1
RM22TU23overvoltage category | 3 ¦ IEC60664-1
RM22TU23circuit group | L1, L2, L3 ¦ ,Supply,Terminal
RM22TU23circuit group | - ¦ ,Input 1,
RM22TU23circuit group | - ¦ ,Input 2,
RM22TU23circuit group | - ¦ ,Input 3,
RM22TU23circuit group | 11,12,14 ¦ ,Output 1,
RM22TU23circuit group | 21,22,24 ¦ ,Output 2,
RM22TU23 | 380..480 AC ¦ ,Supply,Rated
RM22TU23 | - ¦ ,Input 1,Voltage
RM22TU23 | - ¦ ,Input 2,Spec
RM22TU23 | - ¦ ,Input 3,
RM22TU23 | 250V ¦ ,Output 1,
RM22TU23 | 250V ¦ ,Output 2,
RM22TU23[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM22TU23[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM22TU23[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM22TU23[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM22TU23[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22TU23[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22TU23[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22TU23[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22TU23[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22TU23[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM22TU23[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 2,
RM22TU23[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22TU23[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM22TU23[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22TU23[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22TU23[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22TU23[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22TU23[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22TU23[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22TU23[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22TU23[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22TU23[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22TU23[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22TU23[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22TU23[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22TU23[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22TU23dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM22TU23dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM22TU23dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM22TU23dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22TU23dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22TU23dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22TU23dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM22TU23dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM22TU23dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM22TU23dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM22TU23dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM22TU23dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM22TU23dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22TU23dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22TU23dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22TU23insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM22TU23insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM22TU23insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM22TU23insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22TU23insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22TU23insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22TU23insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM22TU23insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM22TU23insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM22TU23insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM22TU23insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM22TU23insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM22TU23insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22TU23insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22TU23insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22TU23
RM22TU23[Us] rated supply voltage | ~ 3 x 380… 3 x 480
RM22TU23supply voltage limits | ~ 3 x 304…3 x 576
RM22TU23polarity | -
RM22TU23supply frequency | 50 / 60
RM22TU23supply frequency | 45…66
RM22TU23power consumption | 15VA
RM22TU23immunity to microbreaks | 0
RM22TU23supply terminal | L1-L3
RM22TU23on-load factor | 1
RM22TU23release of input voltage | -
RM22TU23
RM22TU23monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost ,
RM22TU23monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence,
RM22TU23monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TU23monitoring functions | - ¦ ,Over voltage,
RM22TU23monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Undervoltage ,
RM22TU23monitoring functions | - ¦ ,Phase asymmetry,
RM22TU23monitoring functions | - ¦ ,Disconnection of neutral,
RM22TU23monitoring functions | - ¦ ,Voltage Regeneration,
RM22TU23monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage,
RM22TU23monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage,
RM22TU23monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM22TU23 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM22TU23internal input resistance | - ¦ ,Internal input resistance,
RM22TU23input terminal | L1-L2-L3 ¦ ,Input terminal,
RM22TU23Input nominal voltage selection | 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM22TU23permissible input overload | - ¦ ,permissible input overload,
RM22TU23input frequency | 50 / 60 ¦ ,Rated frequency,
RM22TU23input frequency | 45…66 ¦ ,Frequency operating range,
RM22TU23setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM22TU23repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22TU23measurement method | True RMS ¦ ,Measurement method,
RM22TU23switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation,
RM22TU23switching threshold drift | < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22TU23maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM22TU23measurement range | - ¦ ,Phase lost ,
RM22TU23measurement range | - ¦ ,Phase sequence,
RM22TU23measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TU23measurement range | - ¦ ,Over voltage,
RM22TU23measurement range | -2…-20 % in the ranges 3 x 380…480 ¦ ,Undervoltage ,
RM22TU23measurement range | - ¦ ,Phase asymmetry,
RM22TU23measurement range | - ¦ ,Disconnection of neutral,
RM22TU23measurement range | - ¦ ,Voltage Regeneration,
RM22TU23measurement range | - ¦ ,Extreme undervoltage,
RM22TU23measurement range | - ¦ ,Extreme Overvoltage,
RM22TU23measurement range | - ¦ ,Extreme Asymmetry,
RM22TU23tripping threshold | 1 or more phase cut ¦ ,Phase cut,
RM22TU23tripping threshold | Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence,
RM22TU23tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TU23tripping threshold | - ¦ ,Over voltage,
RM22TU23tripping threshold | Adjustable 2%...20% of selected Un ¦ ,Undervoltage ,
RM22TU23tripping threshold | - ¦ ,Phase asymmetry,
RM22TU23tripping threshold | - ¦ ,Disconnection of neutral,
RM22TU23tripping threshold | - ¦ ,Voltage Regeneration,
RM22TU23tripping threshold | 1 or more phase < 250V Internal design spec: 1 or more phase <290V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM22TU23tripping threshold | Internal design spec: 593V +/- 5% ¦ ,Extreme Overvoltage,
RM22TU23tripping threshold | Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM22TU23hysteresis | All phase cut recover ¦ ,Phase cut,
RM22TU23hysteresis | Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence,
RM22TU23hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TU23hysteresis | - ¦ ,Over voltage,
RM22TU23hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage ,
RM22TU23hysteresis | - ¦ ,Phase asymmetry,
RM22TU23hysteresis | - ¦ ,Disconnection of neutral,
RM22TU23hysteresis | - ¦ ,Voltage Regeneration,
RM22TU23hysteresis | All phases > 315V Internal design spec: All phases >296V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM22TU23hysteresis | Internal design spec: All phases <583V +/- 5% ¦ ,Extreme Overvoltage,
RM22TU23hysteresis | - ¦ ,Extreme Asymmetry,
RM22TU23
RM22TU23output type | 2 x C/O relay contacts
RM22TU23output terminal | 15-16-18, 25-26-28
RM22TU23output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22TU23output logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22TU23contacts material | Cadmium free
RM22TU23mechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22TU23electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22TU23electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22TU23electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22TU23electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22TU23[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22TU23[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22TU23maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22TU23maximum switching capacity | 8A ¦ ,Maximum switching current,
RM22TU23maximum switching capacity | - ¦ ,Maximum switching capacity,
RM22TU23minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22TU23minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22TU23minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22TU23maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22TU23maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22TU23thermal current | 8A ¦ IEC60947-5-1
RM22TU23short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22TU23short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22TU23
RM22TU23time delay type | Yes ¦ ,"OFF" delay,
RM22TU23time delay type | - ¦ ,"ON" delay,
RM22TU23time delay type | - ¦ ,Inhibition,
RM22TU23time delay range | - ¦ ,"OFF" delay,
RM22TU23time delay range | - ¦ ,"ON" delay,
RM22TU23time delay range | - ¦ ,Inhibition,
RM22TU23response time | 0
RM22TU23response time | -
RM22TU23response time | -
RM22TU23response time | -
RM22TU23response time | -
RM22TU23power on delay | 0
RM22TU23reset time | 0
RM22TU23reset time | - ¦ ,through front panel reset,
RM22TU23reset time | - ¦ ,through input control reset,
RM22TU23setting accuracy of time delay | -
RM22TU23repeat accuracy of time delay | -
RM22TU23time delay drift | -
RM22TU23time delay drift | -
RM22TU23
RM22TU23status LED | Dial pointer (Green) R (Amber) Def (Red)
RM22TU23local signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22TU23local signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22TU23local signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22TU23local signalling | R - ON ¦ ,Output is energized,
RM22TU23local signalling | R - OFF ¦ ,Output is de-energized,
RM22TU23local signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22TU23local signalling | Def - Permanent OFF ¦ ,Phase Cut,
RM22TU23local signalling | Def - Permanent ON ¦ ,Phase Sequence Swap,
RM22TU23local signalling | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Undervoltage <U,
RM22TU23local signalling | - ¦ ,Overvoltage >U,
RM22TU23local signalling | - ¦ ,Phase Asymmetry,
RM22TU23local signalling | - ¦ ,Voltage Regeneration,
RM22TU23local signalling | Def - Permanent OFF ¦ ,Extreme Undervoltage <U (Phase loss),
RM22TU23local signalling | Def - Permanent ON ¦ ,Extreme Overvoltage >U,
RM22TU23local signalling | - ¦ ,Extreme Phase Asymmetry,
RM22TU23
RM22TU23 | Yes
RM22TU23 | 1) Will always illuminated when power is supplied to the product
RM22TU23diagnostic button | Output will be de-energized when activated
RM22TU23 | -
RM22TU23 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22TU23
RM22TU23safety reliability data | 3,400,000 hours ¦ ,MTTF,
RM22TU23safety reliability data | 350,000 hours ¦ ,B10,
RM22TU23 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22TU23 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22TU23
RM22TU23 | Drawing / Diagram
RM22TU21
RM22TU21standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22TU21product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TU21marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TU21directives | 2014/35/EU
RM22TU21directives | 2014/30/EU
RM22TU21directives | 2011/65/EU
RM22TU21
RM22TU21 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM22TU21 | Class C ¦ Germanisher Lloyd,Environmental category,
RM22TU21ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22TU21ambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM22TU21relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM22TU21 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22TU21vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22TU21shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22TU21bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22TU21seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22TU21IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22TU21IP degree of protection | IP40 ¦ IEC60529,Housing,
RM22TU21IP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22TU21
RM22TU21width | 22.5 ¦ ,Width,
RM22TU21height | 90 ¦ ,Height,
RM22TU21depth | 73 ¦ ,Depth,
RM22TU21net weight | 95
RM22TU21mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22TU21mounting support | - ¦ IEC/EN 60715,With socket,
RM22TU21mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22TU21Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM22TU21Minimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM22TU21connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22TU21connections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22TU21connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22TU21connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22TU21tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM22TU21cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM22TU21duty time | 1
RM22TU21
RM22TU21electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22TU21electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22TU21electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22TU21electromagnetic compatibility | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22TU21electromagnetic compatibility | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22TU21electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22TU21electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22TU21electromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22TU21electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22TU21electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM22TU21electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22TU21electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22TU21electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22TU21electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22TU21electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22TU21electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22TU21electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22TU21electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22TU21electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22TU21
RM22TU21pollution degree | 3 ¦ IEC60664-1
RM22TU21overvoltage category | 3 ¦ IEC60664-1
RM22TU21circuit group | L1, L2, L3 ¦ ,Supply,Terminal
RM22TU21circuit group | - ¦ ,Input 1,
RM22TU21circuit group | - ¦ ,Input 2,
RM22TU21circuit group | - ¦ ,Input 3,
RM22TU21circuit group | 11,12,14 ¦ ,Output 1,
RM22TU21circuit group | 21,22,24 ¦ ,Output 2,
RM22TU21 | 208..240 AC ¦ ,Supply,Rated
RM22TU21 | - ¦ ,Input 1,Voltage
RM22TU21 | - ¦ ,Input 2,Spec
RM22TU21 | - ¦ ,Input 3,
RM22TU21 | 250V ¦ ,Output 1,
RM22TU21 | 250V ¦ ,Output 2,
RM22TU21[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM22TU21[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM22TU21[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM22TU21[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM22TU21[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22TU21[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22TU21[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22TU21[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22TU21[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22TU21[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM22TU21[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 2,
RM22TU21[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22TU21[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM22TU21[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22TU21[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22TU21[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22TU21[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22TU21[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22TU21[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22TU21[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22TU21[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22TU21[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22TU21[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22TU21[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22TU21[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22TU21[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22TU21dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM22TU21dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM22TU21dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM22TU21dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22TU21dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22TU21dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22TU21dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM22TU21dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM22TU21dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM22TU21dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM22TU21dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM22TU21dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM22TU21dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22TU21dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22TU21dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22TU21insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM22TU21insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM22TU21insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM22TU21insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22TU21insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22TU21insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22TU21insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM22TU21insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM22TU21insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM22TU21insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM22TU21insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM22TU21insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM22TU21insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22TU21insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22TU21insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22TU21
RM22TU21[Us] rated supply voltage | ~ 3 x 200…3 x 240
RM22TU21supply voltage limits | ~ 3 x 160…3 x 288
RM22TU21polarity | -
RM22TU21supply frequency | 50 / 60
RM22TU21supply frequency | 45…66
RM22TU21power consumption | 10VA
RM22TU21immunity to microbreaks | 0
RM22TU21supply terminal | L1-L3
RM22TU21on-load factor | 1
RM22TU21release of input voltage | -
RM22TU21
RM22TU21monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost ,
RM22TU21monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence,
RM22TU21monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TU21monitoring functions | - ¦ ,Over voltage,
RM22TU21monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Undervoltage ,
RM22TU21monitoring functions | - ¦ ,Phase asymmetry,
RM22TU21monitoring functions | - ¦ ,Disconnection of neutral,
RM22TU21monitoring functions | - ¦ ,Voltage Regeneration,
RM22TU21monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage,
RM22TU21monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage,
RM22TU21monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM22TU21 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM22TU21internal input resistance | - ¦ ,Internal input resistance,
RM22TU21input terminal | L1-L2-L3 ¦ ,Input terminal,
RM22TU21Input nominal voltage selection | 200, 208, 220, 240 ¦ ,Input nominal voltage selection,
RM22TU21permissible input overload | - ¦ ,permissible input overload,
RM22TU21input frequency | 50 / 60 ¦ ,Rated frequency,
RM22TU21input frequency | 45…66 ¦ ,Frequency operating range,
RM22TU21setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM22TU21repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22TU21measurement method | True RMS ¦ ,Measurement method,
RM22TU21switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation,
RM22TU21switching threshold drift | < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22TU21maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM22TU21measurement range | - ¦ ,Phase lost ,
RM22TU21measurement range | - ¦ ,Phase sequence,
RM22TU21measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TU21measurement range | - ¦ ,Over voltage,
RM22TU21measurement range | -2…-20 % in the ranges 3 x ~ 200…240 ¦ ,Undervoltage ,
RM22TU21measurement range | - ¦ ,Phase asymmetry,
RM22TU21measurement range | - ¦ ,Disconnection of neutral,
RM22TU21measurement range | - ¦ ,Voltage Regeneration,
RM22TU21measurement range | - ¦ ,Extreme undervoltage,
RM22TU21measurement range | - ¦ ,Extreme Overvoltage,
RM22TU21measurement range | - ¦ ,Extreme Asymmetry,
RM22TU21tripping threshold | 1 or more phase cut ¦ ,Phase cut,
RM22TU21tripping threshold | Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence,
RM22TU21tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TU21tripping threshold | - ¦ ,Over voltage,
RM22TU21tripping threshold | Adjustable 2%...20% of selected Un ¦ ,Undervoltage ,
RM22TU21tripping threshold | - ¦ ,Phase asymmetry,
RM22TU21tripping threshold | - ¦ ,Disconnection of neutral,
RM22TU21tripping threshold | - ¦ ,Voltage Regeneration,
RM22TU21tripping threshold | 1 or more phase < 150V Internal design spec: 1 or more phase <160V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM22TU21tripping threshold | Internal design spec: 297V +/- 5% ¦ ,Extreme Overvoltage,
RM22TU21tripping threshold | Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM22TU21hysteresis | All phase cut recover ¦ ,Phase cut,
RM22TU21hysteresis | Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence,
RM22TU21hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TU21hysteresis | - ¦ ,Over voltage,
RM22TU21hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage ,
RM22TU21hysteresis | - ¦ ,Phase asymmetry,
RM22TU21hysteresis | - ¦ ,Disconnection of neutral,
RM22TU21hysteresis | - ¦ ,Voltage Regeneration,
RM22TU21hysteresis | All phases > 175V Internal design spec: All phases >163V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM22TU21hysteresis | Internal design spec: All phases <287V +/- 5% ¦ ,Extreme Overvoltage,
RM22TU21hysteresis | - ¦ ,Extreme Asymmetry,
RM22TU21
RM22TU21output type | 2 x C/O relay contacts
RM22TU21output terminal | 15-16-18, 25-26-28
RM22TU21output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22TU21output logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22TU21contacts material | Cadmium free
RM22TU21mechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22TU21electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22TU21electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22TU21electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22TU21electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22TU21[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22TU21[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22TU21maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22TU21maximum switching capacity | 8A ¦ ,Maximum switching current,
RM22TU21maximum switching capacity | - ¦ ,Maximum switching capacity,
RM22TU21minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22TU21minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22TU21minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22TU21maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22TU21maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22TU21thermal current | 8A ¦ IEC60947-5-1
RM22TU21short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22TU21short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22TU21
RM22TU21time delay type | Yes ¦ ,"OFF" delay,
RM22TU21time delay type | - ¦ ,"ON" delay,
RM22TU21time delay type | - ¦ ,Inhibition,
RM22TU21time delay range | - ¦ ,"OFF" delay,
RM22TU21time delay range | - ¦ ,"ON" delay,
RM22TU21time delay range | - ¦ ,Inhibition,
RM22TU21response time | 0
RM22TU21response time | -
RM22TU21response time | -
RM22TU21response time | -
RM22TU21response time | -
RM22TU21power on delay | 0
RM22TU21reset time | 0
RM22TU21reset time | - ¦ ,through front panel reset,
RM22TU21reset time | - ¦ ,through input control reset,
RM22TU21setting accuracy of time delay | -
RM22TU21repeat accuracy of time delay | -
RM22TU21time delay drift | -
RM22TU21time delay drift | -
RM22TU21
RM22TU21status LED | Dial pointer (Green) R (Amber) Def (Red)
RM22TU21local signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22TU21local signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22TU21local signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22TU21local signalling | R - ON ¦ ,Output is energized,
RM22TU21local signalling | R - OFF ¦ ,Output is de-energized,
RM22TU21local signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22TU21local signalling | Def - Permanent OFF ¦ ,Phase Cut,
RM22TU21local signalling | Def - Permanent ON ¦ ,Phase Sequence Swap,
RM22TU21local signalling | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Undervoltage <U,
RM22TU21local signalling | - ¦ ,Overvoltage >U,
RM22TU21local signalling | - ¦ ,Phase Asymmetry,
RM22TU21local signalling | - ¦ ,Voltage Regeneration,
RM22TU21local signalling | Def - Permanent OFF ¦ ,Extreme Undervoltage <U (Phase loss),
RM22TU21local signalling | Def - Permanent ON ¦ ,Extreme Overvoltage >U,
RM22TU21local signalling | - ¦ ,Extreme Phase Asymmetry,
RM22TU21
RM22TU21 | Yes
RM22TU21 | 1) Will always illuminated when power is supplied to the product
RM22TU21diagnostic button | Output will be de-energized when activated
RM22TU21 | -
RM22TU21 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22TU21
RM22TU21safety reliability data | 3,400,000 hours ¦ ,MTTF,
RM22TU21safety reliability data | 350,000 hours ¦ ,B10,
RM22TU21 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22TU21 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22TU21
RM22TU21 | Drawing / Diagram
RM22TA33
RM22TA33standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22TA33product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TA33marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TA33directives | 2014/35/EU
RM22TA33directives | 2014/30/EU
RM22TA33directives | 2011/65/EU
RM22TA33
RM22TA33 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM22TA33 | Class C ¦ Germanisher Lloyd,Environmental category,
RM22TA33ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22TA33ambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM22TA33relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM22TA33 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22TA33vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22TA33shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22TA33bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22TA33seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22TA33IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22TA33IP degree of protection | IP40 ¦ IEC60529,Housing,
RM22TA33IP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22TA33
RM22TA33width | 22.5 ¦ ,Width,
RM22TA33height | 90 ¦ ,Height,
RM22TA33depth | 73 ¦ ,Depth,
RM22TA33net weight | 95
RM22TA33mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22TA33mounting support | - ¦ IEC/EN 60715,With socket,
RM22TA33mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22TA33Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM22TA33Minimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM22TA33connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22TA33connections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22TA33connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22TA33connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22TA33tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM22TA33cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM22TA33duty time | 1
RM22TA33
RM22TA33electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22TA33electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22TA33electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22TA33electromagnetic compatibility | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22TA33electromagnetic compatibility | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22TA33electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22TA33electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22TA33electromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22TA33electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22TA33electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM22TA33electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22TA33electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22TA33electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22TA33electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22TA33electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22TA33electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22TA33electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22TA33electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22TA33electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22TA33
RM22TA33pollution degree | 3 ¦ IEC60664-1
RM22TA33overvoltage category | 3 ¦ IEC60664-1
RM22TA33circuit group | L1, L2, L3 ¦ ,Supply,Terminal
RM22TA33circuit group | - ¦ ,Input 1,
RM22TA33circuit group | - ¦ ,Input 2,
RM22TA33circuit group | - ¦ ,Input 3,
RM22TA33circuit group | 11,12,14 ¦ ,Output 1,
RM22TA33circuit group | 21,22,24 ¦ ,Output 2,
RM22TA33 | 380..480 AC ¦ ,Supply,Rated
RM22TA33 | - ¦ ,Input 1,Voltage
RM22TA33 | - ¦ ,Input 2,Spec
RM22TA33 | - ¦ ,Input 3,
RM22TA33 | 250V ¦ ,Output 1,
RM22TA33 | 250V ¦ ,Output 2,
RM22TA33[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM22TA33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM22TA33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM22TA33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM22TA33[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22TA33[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22TA33[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22TA33[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22TA33[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22TA33[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM22TA33[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 2,
RM22TA33[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22TA33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM22TA33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22TA33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22TA33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22TA33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22TA33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22TA33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22TA33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22TA33[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22TA33[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22TA33[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22TA33[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22TA33[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22TA33[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22TA33dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM22TA33dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM22TA33dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM22TA33dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22TA33dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22TA33dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22TA33dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM22TA33dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM22TA33dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM22TA33dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM22TA33dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM22TA33dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM22TA33dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22TA33dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22TA33dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22TA33insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM22TA33insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM22TA33insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM22TA33insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22TA33insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22TA33insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22TA33insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM22TA33insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM22TA33insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM22TA33insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM22TA33insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM22TA33insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM22TA33insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22TA33insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22TA33insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22TA33
RM22TA33[Us] rated supply voltage | ~ 3 x 380… 3 x 480
RM22TA33supply voltage limits | ~ 3 x 304…3 x 576
RM22TA33polarity | -
RM22TA33supply frequency | 50 / 60
RM22TA33supply frequency | 45…66
RM22TA33power consumption | 15VA
RM22TA33immunity to microbreaks | 0
RM22TA33supply terminal | L1-L3
RM22TA33on-load factor | 1
RM22TA33release of input voltage | -
RM22TA33
RM22TA33monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost ,
RM22TA33monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence,
RM22TA33monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TA33monitoring functions | - ¦ ,Over voltage,
RM22TA33monitoring functions | - ¦ ,Undervoltage ,
RM22TA33monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Phase asymmetry,
RM22TA33monitoring functions | - ¦ ,Disconnection of neutral,
RM22TA33monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Voltage Regeneration,
RM22TA33monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage,
RM22TA33monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage,
RM22TA33monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM22TA33 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM22TA33internal input resistance | - ¦ ,Internal input resistance,
RM22TA33input terminal | L1-L2-L3 ¦ ,Input terminal,
RM22TA33Input nominal voltage selection | 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM22TA33permissible input overload | - ¦ ,permissible input overload,
RM22TA33input frequency | 50 / 60 ¦ ,Rated frequency,
RM22TA33input frequency | 45…66 ¦ ,Frequency operating range,
RM22TA33setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM22TA33repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22TA33measurement method | True RMS ¦ ,Measurement method,
RM22TA33switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation,
RM22TA33switching threshold drift | < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22TA33maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM22TA33measurement range | - ¦ ,Phase lost ,
RM22TA33measurement range | - ¦ ,Phase sequence,
RM22TA33measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TA33measurement range | - ¦ ,Over voltage,
RM22TA33measurement range | - ¦ ,Undervoltage ,
RM22TA33measurement range | +5…+15 % in the ranges 3 x ~ 380…480 ¦ ,Phase asymmetry,
RM22TA33measurement range | - ¦ ,Disconnection of neutral,
RM22TA33measurement range | - ¦ ,Voltage Regeneration,
RM22TA33measurement range | - ¦ ,Extreme undervoltage,
RM22TA33measurement range | - ¦ ,Extreme Overvoltage,
RM22TA33measurement range | - ¦ ,Extreme Asymmetry,
RM22TA33tripping threshold | 1 or more phase cut ¦ ,Phase cut,
RM22TA33tripping threshold | Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence,
RM22TA33tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TA33tripping threshold | - ¦ ,Over voltage,
RM22TA33tripping threshold | - ¦ ,Undervoltage ,
RM22TA33tripping threshold | Adjustable 5%...15% of selected Un ¦ ,Phase asymmetry,
RM22TA33tripping threshold | - ¦ ,Disconnection of neutral,
RM22TA33tripping threshold | 1 or more phase < 70% of selected Un Internal design spec: 30% +/- 5% ¦ ,Voltage Regeneration,
RM22TA33tripping threshold | 1 or more phase < 250V Internal design spec: 1 or more phase <290V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM22TA33tripping threshold | Internal design spec: 593V +/- 5% ¦ ,Extreme Overvoltage,
RM22TA33tripping threshold | Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM22TA33hysteresis | All phase cut recover ¦ ,Phase cut,
RM22TA33hysteresis | Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence,
RM22TA33hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TA33hysteresis | - ¦ ,Over voltage,
RM22TA33hysteresis | - ¦ ,Undervoltage ,
RM22TA33hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Phase asymmetry,
RM22TA33hysteresis | - ¦ ,Disconnection of neutral,
RM22TA33hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Voltage Regeneration,
RM22TA33hysteresis | All phases > 315V Internal design spec: All phases >296V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM22TA33hysteresis | Internal design spec: All phases <583V +/- 5% ¦ ,Extreme Overvoltage,
RM22TA33hysteresis | - ¦ ,Extreme Asymmetry,
RM22TA33
RM22TA33output type | 2 x C/O relay contacts
RM22TA33output terminal | 15-16-18, 25-26-28
RM22TA33output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22TA33output logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22TA33contacts material | Cadmium free
RM22TA33mechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22TA33electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22TA33electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22TA33electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22TA33electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22TA33[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22TA33[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22TA33maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22TA33maximum switching capacity | 8A ¦ ,Maximum switching current,
RM22TA33maximum switching capacity | - ¦ ,Maximum switching capacity,
RM22TA33minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22TA33minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22TA33minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22TA33maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22TA33maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22TA33thermal current | 8A ¦ IEC60947-5-1
RM22TA33short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22TA33short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22TA33
RM22TA33time delay type | Yes ¦ ,"OFF" delay,
RM22TA33time delay type | - ¦ ,"ON" delay,
RM22TA33time delay type | - ¦ ,Inhibition,
RM22TA33time delay range | Adjustable 0.1…30 ¦ ,"OFF" delay,
RM22TA33time delay range | - ¦ ,"ON" delay,
RM22TA33time delay range | - ¦ ,Inhibition,
RM22TA33response time | 0
RM22TA33response time | -
RM22TA33response time | -
RM22TA33response time | -
RM22TA33response time | -
RM22TA33power on delay | 0
RM22TA33reset time | 0
RM22TA33reset time | - ¦ ,through front panel reset,
RM22TA33reset time | - ¦ ,through input control reset,
RM22TA33setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM22TA33repeat accuracy of time delay | +/- 3%
RM22TA33time delay drift | < 1
RM22TA33time delay drift | < 0.05
RM22TA33
RM22TA33status LED | Dial pointer (Green) R (Amber) Def (Red)
RM22TA33local signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22TA33local signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22TA33local signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22TA33local signalling | R - ON ¦ ,Output is energized,
RM22TA33local signalling | R - OFF ¦ ,Output is de-energized,
RM22TA33local signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22TA33local signalling | Def - Permanent OFF ¦ ,Phase Cut,
RM22TA33local signalling | Def - Permanent ON ¦ ,Phase Sequence Swap,
RM22TA33local signalling | - ¦ ,Undervoltage <U,
RM22TA33local signalling | - ¦ ,Overvoltage >U,
RM22TA33local signalling | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Phase Asymmetry,
RM22TA33local signalling | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Voltage Regeneration,
RM22TA33local signalling | Def - Permanent OFF ¦ ,Extreme Undervoltage <U (Phase loss),
RM22TA33local signalling | Def - Permanent ON ¦ ,Extreme Overvoltage >U,
RM22TA33local signalling | Def - Permanent OFF ¦ ,Extreme Phase Asymmetry,
RM22TA33
RM22TA33 | Yes
RM22TA33 | 1) Will always illuminated when power is supplied to the product
RM22TA33diagnostic button | Output will be de-energized when activated
RM22TA33 | -
RM22TA33 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22TA33
RM22TA33safety reliability data | 3,400,000 hours ¦ ,MTTF,
RM22TA33safety reliability data | 350,000 hours ¦ ,B10,
RM22TA33 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22TA33 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22TA33
RM22TA33 | Drawing / Diagram
RM22TA31
RM22TA31standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22TA31product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TA31marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TA31directives | 2014/35/EU
RM22TA31directives | 2014/30/EU
RM22TA31directives | 2011/65/EU
RM22TA31
RM22TA31 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM22TA31 | Class C ¦ Germanisher Lloyd,Environmental category,
RM22TA31ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22TA31ambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM22TA31relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM22TA31 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22TA31vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22TA31shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22TA31bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22TA31seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22TA31IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22TA31IP degree of protection | IP40 ¦ IEC60529,Housing,
RM22TA31IP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22TA31
RM22TA31width | 22.5 ¦ ,Width,
RM22TA31height | 90 ¦ ,Height,
RM22TA31depth | 73 ¦ ,Depth,
RM22TA31net weight | 95
RM22TA31mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22TA31mounting support | - ¦ IEC/EN 60715,With socket,
RM22TA31mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22TA31Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM22TA31Minimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM22TA31connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22TA31connections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22TA31connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22TA31connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22TA31tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM22TA31cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM22TA31duty time | 1
RM22TA31
RM22TA31electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22TA31electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22TA31electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22TA31electromagnetic compatibility | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22TA31electromagnetic compatibility | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22TA31electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22TA31electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22TA31electromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22TA31electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22TA31electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM22TA31electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22TA31electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22TA31electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22TA31electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22TA31electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22TA31electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22TA31electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22TA31electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22TA31electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22TA31
RM22TA31pollution degree | 3 ¦ IEC60664-1
RM22TA31overvoltage category | 3 ¦ IEC60664-1
RM22TA31circuit group | L1, L2, L3 ¦ ,Supply,Terminal
RM22TA31circuit group | - ¦ ,Input 1,
RM22TA31circuit group | - ¦ ,Input 2,
RM22TA31circuit group | - ¦ ,Input 3,
RM22TA31circuit group | 11,12,14 ¦ ,Output 1,
RM22TA31circuit group | 21,22,24 ¦ ,Output 2,
RM22TA31 | 208..240 AC ¦ ,Supply,Rated
RM22TA31 | - ¦ ,Input 1,Voltage
RM22TA31 | - ¦ ,Input 2,Spec
RM22TA31 | - ¦ ,Input 3,
RM22TA31 | 250V ¦ ,Output 1,
RM22TA31 | 250V ¦ ,Output 2,
RM22TA31[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM22TA31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM22TA31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM22TA31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM22TA31[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22TA31[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22TA31[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22TA31[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22TA31[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22TA31[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM22TA31[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 2,
RM22TA31[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22TA31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM22TA31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22TA31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22TA31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22TA31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22TA31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22TA31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22TA31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22TA31[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22TA31[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22TA31[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22TA31[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22TA31[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22TA31[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22TA31dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM22TA31dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM22TA31dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM22TA31dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22TA31dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22TA31dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22TA31dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM22TA31dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM22TA31dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM22TA31dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM22TA31dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM22TA31dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM22TA31dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22TA31dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22TA31dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22TA31insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM22TA31insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM22TA31insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM22TA31insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22TA31insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22TA31insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22TA31insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM22TA31insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM22TA31insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM22TA31insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM22TA31insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM22TA31insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM22TA31insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22TA31insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22TA31insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22TA31
RM22TA31[Us] rated supply voltage | ~ 3 x 200…3 x 240
RM22TA31supply voltage limits | ~ 3 x 160…3 x 288
RM22TA31polarity | -
RM22TA31supply frequency | 50 / 60
RM22TA31supply frequency | 45…66
RM22TA31power consumption | 10VA
RM22TA31immunity to microbreaks | 0
RM22TA31supply terminal | L1-L3
RM22TA31on-load factor | 1
RM22TA31release of input voltage | -
RM22TA31
RM22TA31monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost ,
RM22TA31monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence,
RM22TA31monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TA31monitoring functions | - ¦ ,Over voltage,
RM22TA31monitoring functions | - ¦ ,Undervoltage ,
RM22TA31monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Phase asymmetry,
RM22TA31monitoring functions | - ¦ ,Disconnection of neutral,
RM22TA31monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Voltage Regeneration,
RM22TA31monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage,
RM22TA31monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage,
RM22TA31monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM22TA31 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM22TA31internal input resistance | - ¦ ,Internal input resistance,
RM22TA31input terminal | L1-L2-L3 ¦ ,Input terminal,
RM22TA31Input nominal voltage selection | 200, 208, 220, 240 ¦ ,Input nominal voltage selection,
RM22TA31permissible input overload | - ¦ ,permissible input overload,
RM22TA31input frequency | 50 / 60 ¦ ,Rated frequency,
RM22TA31input frequency | 45…66 ¦ ,Frequency operating range,
RM22TA31setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM22TA31repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22TA31measurement method | True RMS ¦ ,Measurement method,
RM22TA31switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation,
RM22TA31switching threshold drift | < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22TA31maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM22TA31measurement range | - ¦ ,Phase lost ,
RM22TA31measurement range | - ¦ ,Phase sequence,
RM22TA31measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TA31measurement range | - ¦ ,Over voltage,
RM22TA31measurement range | - ¦ ,Undervoltage ,
RM22TA31measurement range | +5…+15 % in the ranges 3 x ~ 200…240 ¦ ,Phase asymmetry,
RM22TA31measurement range | - ¦ ,Disconnection of neutral,
RM22TA31measurement range | - ¦ ,Voltage Regeneration,
RM22TA31measurement range | - ¦ ,Extreme undervoltage,
RM22TA31measurement range | - ¦ ,Extreme Overvoltage,
RM22TA31measurement range | - ¦ ,Extreme Asymmetry,
RM22TA31tripping threshold | 1 or more phase cut ¦ ,Phase cut,
RM22TA31tripping threshold | Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence,
RM22TA31tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TA31tripping threshold | - ¦ ,Over voltage,
RM22TA31tripping threshold | - ¦ ,Undervoltage ,
RM22TA31tripping threshold | Adjustable 5%...15% of selected Un ¦ ,Phase asymmetry,
RM22TA31tripping threshold | - ¦ ,Disconnection of neutral,
RM22TA31tripping threshold | 1 or more phase < 70% of selected Un Internal design spec: 30% +/- 5% ¦ ,Voltage Regeneration,
RM22TA31tripping threshold | 1 or more phase < 150V Internal design spec: 1 or more phase <160V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM22TA31tripping threshold | Internal design spec: 297V +/- 5% ¦ ,Extreme Overvoltage,
RM22TA31tripping threshold | Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM22TA31hysteresis | All phase cut recover ¦ ,Phase cut,
RM22TA31hysteresis | Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence,
RM22TA31hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM22TA31hysteresis | - ¦ ,Over voltage,
RM22TA31hysteresis | - ¦ ,Undervoltage ,
RM22TA31hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Phase asymmetry,
RM22TA31hysteresis | - ¦ ,Disconnection of neutral,
RM22TA31hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Voltage Regeneration,
RM22TA31hysteresis | All phases > 175V Internal design spec: All phases >163V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM22TA31hysteresis | Internal design spec: All phases <287V +/- 5% ¦ ,Extreme Overvoltage,
RM22TA31hysteresis | - ¦ ,Extreme Asymmetry,
RM22TA31
RM22TA31output type | 2 x C/O relay contacts
RM22TA31output terminal | 15-16-18, 25-26-28
RM22TA31output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22TA31output logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22TA31contacts material | Cadmium free
RM22TA31mechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22TA31electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22TA31electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22TA31electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22TA31electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22TA31[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22TA31[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22TA31maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22TA31maximum switching capacity | 8A ¦ ,Maximum switching current,
RM22TA31maximum switching capacity | - ¦ ,Maximum switching capacity,
RM22TA31minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22TA31minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22TA31minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22TA31maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22TA31maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22TA31thermal current | 8A ¦ IEC60947-5-1
RM22TA31short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22TA31short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22TA31
RM22TA31time delay type | Yes ¦ ,"OFF" delay,
RM22TA31time delay type | - ¦ ,"ON" delay,
RM22TA31time delay type | - ¦ ,Inhibition,
RM22TA31time delay range | Adjustable 0.1…30 ¦ ,"OFF" delay,
RM22TA31time delay range | - ¦ ,"ON" delay,
RM22TA31time delay range | - ¦ ,Inhibition,
RM22TA31response time | 0
RM22TA31response time | -
RM22TA31response time | -
RM22TA31response time | -
RM22TA31response time | -
RM22TA31power on delay | 0
RM22TA31reset time | 0
RM22TA31reset time | - ¦ ,through front panel reset,
RM22TA31reset time | - ¦ ,through input control reset,
RM22TA31setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM22TA31repeat accuracy of time delay | +/- 3%
RM22TA31time delay drift | < 1
RM22TA31time delay drift | < 0.05
RM22TA31
RM22TA31status LED | Dial pointer (Green) R (Amber) Def (Red)
RM22TA31local signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22TA31local signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22TA31local signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22TA31local signalling | R - ON ¦ ,Output is energized,
RM22TA31local signalling | R - OFF ¦ ,Output is de-energized,
RM22TA31local signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22TA31local signalling | Def - Permanent OFF ¦ ,Phase Cut,
RM22TA31local signalling | Def - Permanent ON ¦ ,Phase Sequence Swap,
RM22TA31local signalling | - ¦ ,Undervoltage <U,
RM22TA31local signalling | - ¦ ,Overvoltage >U,
RM22TA31local signalling | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Phase Asymmetry,
RM22TA31local signalling | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Voltage Regeneration,
RM22TA31local signalling | Def - Permanent OFF ¦ ,Extreme Undervoltage <U (Phase loss),
RM22TA31local signalling | Def - Permanent ON ¦ ,Extreme Overvoltage >U,
RM22TA31local signalling | Def - Permanent OFF ¦ ,Extreme Phase Asymmetry,
RM22TA31
RM22TA31 | Yes
RM22TA31 | 1) Will always illuminated when power is supplied to the product
RM22TA31diagnostic button | Output will be de-energized when activated
RM22TA31 | -
RM22TA31 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22TA31
RM22TA31safety reliability data | 3,400,000 hours ¦ ,MTTF,
RM22TA31safety reliability data | 350,000 hours ¦ ,B10,
RM22TA31 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22TA31 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22TA31
RM22TA31 | Drawing / Diagram
RM17TG20
RM17TG20standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM17TG20product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TG20marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TG20directives | 2014/35/EU
RM17TG20directives | 2014/30/EU
RM17TG20directives | 2011/65/EU
RM17TG20
RM17TG20 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM17TG20 | Class C ¦ Germanisher Lloyd,Environmental category,
RM17TG20ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM17TG20ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM17TG20relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM17TG20 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM17TG20vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM17TG20shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM17TG20bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM17TG20seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM17TG20IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM17TG20IP degree of protection | IP30 ¦ IEC60529,Housing,
RM17TG20IP degree of protection | - ¦ IEC60529,Front Panel,
RM17TG20
RM17TG20width | 17.5 ¦ ,Width,
RM17TG20height | 90 ¦ ,Height,
RM17TG20depth | 72 ¦ ,Depth,
RM17TG20net weight | 85
RM17TG20mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM17TG20mounting support | - ¦ IEC/EN 60715,With socket,
RM17TG20mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM17TG20Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM17TG20Minimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM17TG20connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM17TG20connections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM17TG20connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM17TG20connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM17TG20tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM17TG20cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM17TG20duty time | 1
RM17TG20
RM17TG20electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM17TG20electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM17TG20electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM17TG20electromagnetic compatibility | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM17TG20electromagnetic compatibility | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge,
RM17TG20electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM17TG20electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM17TG20electromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM17TG20electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM17TG20electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM17TG20electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM17TG20electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM17TG20electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM17TG20electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM17TG20electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM17TG20electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM17TG20electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM17TG20electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM17TG20electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM17TG20
RM17TG20pollution degree | 3 ¦ IEC60664-1
RM17TG20overvoltage category | 3 ¦ IEC60664-1
RM17TG20circuit group | L1, L2, L3 ¦ ,Supply,Terminal
RM17TG20circuit group | - ¦ ,Input 1,
RM17TG20circuit group | - ¦ ,Input 2,
RM17TG20circuit group | - ¦ ,Input 3,
RM17TG20circuit group | 11,12,14 ¦ ,Output 1,
RM17TG20circuit group | 21,22,24 ¦ ,Output 2,
RM17TG20 | 208..440 AC ¦ ,Supply,Rated
RM17TG20 | - ¦ ,Input 1,Voltage
RM17TG20 | - ¦ ,Input 2,Spec
RM17TG20 | - ¦ ,Input 3,
RM17TG20 | 250V ¦ ,Output 1,
RM17TG20 | 250V ¦ ,Output 2,
RM17TG20[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM17TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM17TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM17TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM17TG20[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM17TG20[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM17TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM17TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM17TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM17TG20[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM17TG20[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 2,
RM17TG20[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM17TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM17TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM17TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM17TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM17TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM17TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM17TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM17TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM17TG20[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM17TG20[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM17TG20[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM17TG20[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM17TG20[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM17TG20[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM17TG20dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM17TG20dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM17TG20dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM17TG20dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM17TG20dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM17TG20dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM17TG20dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM17TG20dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM17TG20dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM17TG20dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM17TG20dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM17TG20dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM17TG20dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM17TG20dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM17TG20dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM17TG20insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM17TG20insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM17TG20insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM17TG20insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM17TG20insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM17TG20insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM17TG20insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM17TG20insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM17TG20insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM17TG20insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM17TG20insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM17TG20insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM17TG20insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM17TG20insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM17TG20insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM17TG20
RM17TG20[Us] rated supply voltage | ~ 3 x 208…3 x 440
RM17TG20supply voltage limits | ~ 3 x 183…3 x 484
RM17TG20polarity | -
RM17TG20supply frequency | 50 / 60
RM17TG20supply frequency | 45…66
RM17TG20power consumption | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz
RM17TG20immunity to microbreaks | 0
RM17TG20supply terminal | L1-L3
RM17TG20on-load factor | 1
RM17TG20release of input voltage | -
RM17TG20
RM17TG20monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost ,
RM17TG20monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence,
RM17TG20monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17TG20monitoring functions | - ¦ ,Over voltage,
RM17TG20monitoring functions | - ¦ ,Undervoltage ,
RM17TG20monitoring functions | - ¦ ,Phase asymmetry,
RM17TG20monitoring functions | - ¦ ,Disconnection of neutral,
RM17TG20monitoring functions | - ¦ ,Voltage Regeneration,
RM17TG20monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage,
RM17TG20monitoring functions | - ¦ ,Extreme overvoltage,
RM17TG20monitoring functions | - ¦ ,Extreme asymmetry,
RM17TG20 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM17TG20internal input resistance | - ¦ ,Internal input resistance,
RM17TG20input terminal | L1-L2-L3 ¦ ,Input terminal,
RM17TG20Input nominal voltage selection | - ¦ ,Input nominal voltage selection,
RM17TG20permissible input overload | - ¦ ,permissible input overload,
RM17TG20input frequency | 50 / 60 ¦ ,Rated frequency,
RM17TG20input frequency | 45…66 ¦ ,Frequency operating range,
RM17TG20setting accuracy of the switching threshold | - ¦ ,Setting accuracy,
RM17TG20repeat accuracy of the switching threshold | - ¦ ,Repeat accuracy (constant parameters),
RM17TG20measurement method | Non True RMS ¦ ,Measurement method,
RM17TG20switching threshold drift | - ¦ ,Measurement error with supply voltage variation,
RM17TG20switching threshold drift | - ¦ ,Measurement error with temperature variation,
RM17TG20maximum measuring cycle | - ¦ ,Maximum measuring cycles,
RM17TG20measurement range | - ¦ ,Phase lost ,
RM17TG20measurement range | - ¦ ,Phase sequence,
RM17TG20measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17TG20measurement range | - ¦ ,Over voltage,
RM17TG20measurement range | - ¦ ,Undervoltage ,
RM17TG20measurement range | - ¦ ,Phase asymmetry,
RM17TG20measurement range | - ¦ ,Disconnection of neutral,
RM17TG20measurement range | - ¦ ,Voltage Regeneration,
RM17TG20measurement range | - ¦ ,Extreme undervoltage,
RM17TG20measurement range | - ¦ ,Extreme Overvoltage,
RM17TG20measurement range | - ¦ ,Extreme Asymmetry,
RM17TG20tripping threshold | 1 or more phase cut ¦ ,Phase cut,
RM17TG20tripping threshold | Total swap of phase Internal design spec: L31 lag L21 =< 10o or L31 lag L21 >= 150o ¦ ,Phase sequence,
RM17TG20tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17TG20tripping threshold | - ¦ ,Over voltage,
RM17TG20tripping threshold | - ¦ ,Undervoltage ,
RM17TG20tripping threshold | - ¦ ,Phase asymmetry,
RM17TG20tripping threshold | - ¦ ,Disconnection of neutral,
RM17TG20tripping threshold | - ¦ ,Voltage Regeneration,
RM17TG20tripping threshold | 2 or more phase < 100V Internal design spec: 2 or more phase <150V +/- 10% ¦ ,Extreme undervoltage (Phase loss),
RM17TG20tripping threshold | - ¦ ,Extreme Overvoltage,
RM17TG20tripping threshold | - ¦ ,Extreme Asymmetry,
RM17TG20hysteresis | All phase cut recover ¦ ,Phase cut,
RM17TG20hysteresis | Total phase swap recover Internal design spec: L31 lag L21 >= 15o or L31 lag L21 <= 135o ¦ ,Phase sequence,
RM17TG20hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17TG20hysteresis | - ¦ ,Over voltage,
RM17TG20hysteresis | - ¦ ,Undervoltage ,
RM17TG20hysteresis | - ¦ ,Phase asymmetry,
RM17TG20hysteresis | - ¦ ,Disconnection of neutral,
RM17TG20hysteresis | - ¦ ,Voltage Regeneration,
RM17TG20hysteresis | All phases > 183V Internal design spec: All phases >153V +/- 10% ¦ ,Extreme undervoltage (Phase loss),
RM17TG20hysteresis | - ¦ ,Extreme Overvoltage,
RM17TG20hysteresis | - ¦ ,Extreme Asymmetry,
RM17TG20
RM17TG20output type | 2 x C/O relay contacts
RM17TG20output terminal | 11-12-14, 21-22-24
RM17TG20output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM17TG20output logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM17TG20contacts material | Cadmium free
RM17TG20mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM17TG20electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM17TG20electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM17TG20electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM17TG20electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM17TG20[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM17TG20[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM17TG20maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM17TG20maximum switching capacity | 5A ¦ ,Maximum switching current,
RM17TG20maximum switching capacity | - ¦ ,Maximum switching capacity,
RM17TG20minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM17TG20minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM17TG20minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM17TG20maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM17TG20maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM17TG20thermal current | 5A ¦ IEC60947-5-1
RM17TG20short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse,
RM17TG20short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM17TG20
RM17TG20time delay type | - ¦ ,"OFF" delay,
RM17TG20time delay type | - ¦ ,"ON" delay,
RM17TG20time delay type | - ¦ ,Inhibition,
RM17TG20time delay range | - ¦ ,"OFF" delay,
RM17TG20time delay range | - ¦ ,"ON" delay,
RM17TG20time delay range | - ¦ ,Inhibition,
RM17TG20response time | 0
RM17TG20response time | -
RM17TG20response time | -
RM17TG20response time | -
RM17TG20response time | -
RM17TG20power on delay | 0
RM17TG20reset time | 0
RM17TG20reset time | - ¦ ,through front panel reset,
RM17TG20reset time | - ¦ ,through input control reset,
RM17TG20setting accuracy of time delay | -
RM17TG20repeat accuracy of time delay | -
RM17TG20time delay drift | -
RM17TG20time delay drift | -
RM17TG20
RM17TG20status LED | R (Amber)
RM17TG20local signalling | - ¦ ,Power supply availability,
RM17TG20local signalling | - ¦ ,Power supply not availability,
RM17TG20local signalling | - ¦ ,Timing in-progress,
RM17TG20local signalling | R - ON ¦ ,Output is energized,
RM17TG20local signalling | R - OFF ¦ ,Output is de-energized,
RM17TG20local signalling | - ¦ ,Range Setting Changes,
RM17TG20local signalling | - ¦ ,Phase Cut,
RM17TG20local signalling | - ¦ ,Phase Sequence Swap,
RM17TG20local signalling | - ¦ ,Undervoltage <U,
RM17TG20local signalling | - ¦ ,Overvoltage >U,
RM17TG20local signalling | - ¦ ,Phase Asymmetry,
RM17TG20local signalling | - ¦ ,Voltage Regeneration,
RM17TG20local signalling | - ¦ ,Extreme Undervoltage <U (Phase loss),
RM17TG20local signalling | - ¦ ,Extreme Overvoltage >U,
RM17TG20local signalling | - ¦ ,Extreme Phase Asymmetry,
RM17TG20
RM17TG20 | No
RM17TG20 | -
RM17TG20diagnostic button | -
RM17TG20 | -
RM17TG20 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM17TG20
RM17TG20safety reliability data | 8,100,000 hours ¦ ,MTTF,
RM17TG20safety reliability data | 850,000 hours ¦ ,B10,
RM17TG20 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM17TG20 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM17TG20
RM17TG20 | Drawing / Diagram
84873021
84873021standards | Same as RM17TG20
84873021product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873021marking | UL, CSA, GL, CCC, CE, China ROHS
84873021directives | Same as RM17TG20
84873021directives | Same as RM17TG20
84873021directives | Same as RM17TG20
84873021
84873021 | Same as RM17TG20 ¦ IEC60721-3-3,Climatic category,
84873021 | Same as RM17TG20 ¦ Germanisher Lloyd,Environmental category,
84873021ambient air temperature for storage | Same as RM17TG20 ¦ ,Storage,
84873021ambient air temperature for operation | Same as RM17TG20 ¦ ,Operation,
84873021relative humidity | Same as RM17TG20 ¦ IEC60068-2-30,Damp heat,XX
84873021 | Same as RM17TG20 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873021vibration resistance | Same as RM17TG20 ¦ IEC60068-2-6
84873021shock resistance | Same as RM17TG20 ¦ IEC60068-2-27
84873021bump resistance | Same as RM17TG20 ¦ IEC60068-2-29
84873021seismic resistance | Same as RM17TG20 ¦ IEC60068-3-3
84873021IP degree of protection | Same as RM17TG20 ¦ IEC60529,Terminal Block,
84873021IP degree of protection | Same as RM17TG20 ¦ IEC60529,Housing,
84873021IP degree of protection | Same as RM17TG20 ¦ IEC60529,Front Panel,
84873021
84873021width | Same as RM17TG20 ¦ ,Width,
84873021height | Same as RM17TG20 ¦ ,Height,
84873021depth | Same as RM17TG20 ¦ ,Depth,
84873021net weight | Same as RM17TG20
84873021mounting support | Same as RM17TG20 ¦ IEC/EN 60715,Without socket,
84873021mounting support | Same as RM17TG20 ¦ IEC/EN 60715,With socket,
84873021mounting position | Same as RM17TG20 ¦ ,In relation to normal vertical mounting plane,
84873021Minimum distance to adjacent devices | Same as RM17TG20 ¦ ,Horizontal,
84873021Minimum distance to adjacent devices | Same as RM17TG20 ¦ ,Vertical,
84873021connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873021connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873021connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Solid cable (spring terminal),
84873021connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Flexible cable (spring terminal),
84873021tightening torque | Same as RM17TG20 ¦ IEC60947-1,Tightening torque,
84873021cable stripping length | Same as RM17TG20 ¦ ,Cable stripping length,
84873021duty time | Same as RM17TG20
84873021
84873021electromagnetic compatibility | Same as RM17TG20 ¦ ,Generic immunity standard,
84873021electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-2,Electrostatic discharge,
84873021electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873021electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-4,Fast transient / burst,
84873021electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-5,Surge,
84873021electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-6,Conducted RF disturbance,
84873021electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-8,Power frequency magnetic field,
84873021electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873021electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873021electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-29,DC voltage interruption,
84873021electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-13,Low frequency harmonics,
84873021electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873021electromagnetic compatibility | Same as RM17TG20 ¦ ,Generic emission standard,
84873021electromagnetic compatibility | Same as RM17TG20 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873021electromagnetic compatibility | Same as RM17TG20 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873021electromagnetic compatibility | Same as RM17TG20 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873021electromagnetic compatibility | Same as RM17TG20 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873021electromagnetic compatibility | Same as RM17TG20 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873021electromagnetic compatibility | Same as RM17TG20 ¦ Germanisher Lloyd,Conducted emission,
84873021
84873021pollution degree | Same as RM17TG20 ¦ IEC60664-1
84873021overvoltage category | Same as RM17TG20 ¦ IEC60664-1
84873021circuit group | Same as RM17TG20 ¦ ,Supply,Terminal
84873021circuit group | Same as RM17TG20 ¦ ,Input 1,
84873021circuit group | Same as RM17TG20 ¦ ,Input 2,
84873021circuit group | Same as RM17TG20 ¦ ,Input 3,
84873021circuit group | Same as RM17TG20 ¦ ,Output 1,
84873021circuit group | Same as RM17TG20 ¦ ,Output 2,
84873021 | Same as RM17TG20 ¦ ,Supply,Rated
84873021 | Same as RM17TG20 ¦ ,Input 1,Voltage
84873021 | Same as RM17TG20 ¦ ,Input 2,Spec
84873021 | Same as RM17TG20 ¦ ,Input 3,
84873021 | Same as RM17TG20 ¦ ,Output 1,
84873021 | Same as RM17TG20 ¦ ,Output 2,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Output 1,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Output 2,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 2,Isolated
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 3,Circuit
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Output 1,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Output 2,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Output 1 / Output 2,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 1,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 2,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 1,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 2,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 1,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 2,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 2,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Input 3,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 3,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Output 1,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Output 2,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 2,Isolated
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 3,Circuit
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Output 1,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Output 2,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Output 1 / Output 2,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 1,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 2,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 1,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 2,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 1,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 2,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 2,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Input 3,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 3,
84873021dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 1,
84873021dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 2,
84873021dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 3,
84873021dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Output 1,
84873021dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Output 2,
84873021dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Output 1 / Output 2,
84873021dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 1,
84873021dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 2,
84873021dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 1,
84873021dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 2,
84873021dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 1,
84873021dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 2,
84873021dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 2,
84873021dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Input 3,
84873021dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 3,
84873021insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 1,
84873021insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 2,
84873021insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 3,
84873021insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Output 1,
84873021insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Output 2,
84873021insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Output 1 / Output 2,
84873021insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 1,
84873021insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 2,
84873021insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 1,
84873021insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 2,
84873021insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 1,
84873021insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 2,
84873021insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 2,
84873021insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Input 3,
84873021insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 3,
84873021
84873021[Us] rated supply voltage | Same as RM17TG20
84873021supply voltage limits | Same as RM17TG20
84873021polarity | Same as RM17TG20
84873021supply frequency | Same as RM17TG20
84873021supply frequency | Same as RM17TG20
84873021power consumption | Same as RM17TG20
84873021immunity to microbreaks | Same as RM17TG20
84873021supply terminal | Same as RM17TG20
84873021on-load factor | Same as RM17TG20
84873021release of input voltage | Same as RM17TG20
84873021
84873021monitoring functions | Same as RM17TG20 ¦ ,Phase lost ,
84873021monitoring functions | Same as RM17TG20 ¦ ,Phase sequence,
84873021monitoring functions | Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode),
84873021monitoring functions | Same as RM17TG20 ¦ ,Over voltage,
84873021monitoring functions | Same as RM17TG20 ¦ ,Undervoltage ,
84873021monitoring functions | Same as RM17TG20 ¦ ,Phase asymmetry,
84873021monitoring functions | Same as RM17TG20 ¦ ,Disconnection of neutral,
84873021monitoring functions | Same as RM17TG20 ¦ ,Voltage Regeneration,
84873021monitoring functions | Same as RM17TG20 ¦ ,Extreme undervoltage,
84873021monitoring functions | Same as RM17TG20 ¦ ,Extreme overvoltage,
84873021monitoring functions | Same as RM17TG20 ¦ ,Extreme asymmetry,
84873021 | Same as RM17TG20 ¦ ,Measurement mode,
84873021internal input resistance | Same as RM17TG20 ¦ ,Internal input resistance,
84873021input terminal | Same as RM17TG20 ¦ ,Input terminal,
84873021Input nominal voltage selection | Same as RM17TG20 ¦ ,Input nominal voltage selection,
84873021permissible input overload | Same as RM17TG20 ¦ ,permissible input overload,
84873021input frequency | Same as RM17TG20 ¦ ,Rated frequency,
84873021input frequency | Same as RM17TG20 ¦ ,Frequency operating range,
84873021setting accuracy of the switching threshold | Same as RM17TG20 ¦ ,Setting accuracy,
84873021repeat accuracy of the switching threshold | Same as RM17TG20 ¦ ,Repeat accuracy (constant parameters),
84873021measurement method | Same as RM17TG20 ¦ ,Measurement method,
84873021switching threshold drift | Same as RM17TG20 ¦ ,Measurement error with supply voltage variation,
84873021switching threshold drift | Same as RM17TG20 ¦ ,Measurement error with temperature variation,
84873021maximum measuring cycle | Same as RM17TG20 ¦ ,Maximum measuring cycles,
84873021measurement range | Same as RM17TG20 ¦ ,Phase lost ,
84873021measurement range | Same as RM17TG20 ¦ ,Phase sequence,
84873021measurement range | Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode),
84873021measurement range | Same as RM17TG20 ¦ ,Over voltage,
84873021measurement range | Same as RM17TG20 ¦ ,Undervoltage ,
84873021measurement range | Same as RM17TG20 ¦ ,Phase asymmetry,
84873021measurement range | Same as RM17TG20 ¦ ,Disconnection of neutral,
84873021measurement range | Same as RM17TG20 ¦ ,Voltage Regeneration,
84873021measurement range | Same as RM17TG20 ¦ ,Extreme undervoltage,
84873021measurement range | Same as RM17TG20 ¦ ,Extreme Overvoltage,
84873021measurement range | Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873021tripping threshold | Same as RM17TG20 ¦ ,Phase cut,
84873021tripping threshold | Same as RM17TG20 ¦ ,Phase sequence,
84873021tripping threshold | Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode),
84873021tripping threshold | Same as RM17TG20 ¦ ,Over voltage,
84873021tripping threshold | Same as RM17TG20 ¦ ,Undervoltage ,
84873021tripping threshold | Same as RM17TG20 ¦ ,Phase asymmetry,
84873021tripping threshold | Same as RM17TG20 ¦ ,Disconnection of neutral,
84873021tripping threshold | Same as RM17TG20 ¦ ,Voltage Regeneration,
84873021tripping threshold | Same as RM17TG20 ¦ ,Extreme undervoltage (Phase loss),
84873021tripping threshold | Same as RM17TG20 ¦ ,Extreme Overvoltage,
84873021tripping threshold | Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873021hysteresis | Same as RM17TG20 ¦ ,Phase cut,
84873021hysteresis | Same as RM17TG20 ¦ ,Phase sequence,
84873021hysteresis | Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode),
84873021hysteresis | Same as RM17TG20 ¦ ,Over voltage,
84873021hysteresis | Same as RM17TG20 ¦ ,Undervoltage ,
84873021hysteresis | Same as RM17TG20 ¦ ,Phase asymmetry,
84873021hysteresis | Same as RM17TG20 ¦ ,Disconnection of neutral,
84873021hysteresis | Same as RM17TG20 ¦ ,Voltage Regeneration,
84873021hysteresis | Same as RM17TG20 ¦ ,Extreme undervoltage (Phase loss),
84873021hysteresis | Same as RM17TG20 ¦ ,Extreme Overvoltage,
84873021hysteresis | Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873021
84873021output type | Same as RM17TG20
84873021output terminal | Same as RM17TG20
84873021output logic | Same as RM17TG20 ¦ ,R1 (11-12-14),
84873021output logic | Same as RM17TG20 ¦ ,R2 (21-22-24),
84873021contacts material | Same as RM17TG20
84873021mechanical durability | Same as RM17TG20 ¦ IEC61810-1
84873021electrical durability | Same as RM17TG20 ¦ IEC60947-4-1,AC-1,
84873021electrical durability | Same as RM17TG20 ¦ IEC60947-4-1,DC-1,
84873021electrical durability | Same as RM17TG20 ¦ IEC60947-5-1,AC-15,
84873021electrical durability | Same as RM17TG20 ¦ IEC60947-5-1,DC-13,
84873021[Ue] rated operational voltage | Same as RM17TG20 ¦ IEC61810-1,Rated switching voltage,
84873021[Ie] rated operational current | Same as RM17TG20 ¦ IEC61810-1,Rated switching current,
84873021maximum switching capacity | Same as RM17TG20 ¦ ,Maximum switching voltage,
84873021maximum switching capacity | Same as RM17TG20 ¦ ,Maximum switching current,
84873021maximum switching capacity | Same as RM17TG20 ¦ ,Maximum switching capacity,
84873021minimum switching capacity | Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching voltage,
84873021minimum switching capacity | Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching current,
84873021minimum switching capacity | Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching capacity,
84873021maximum voltage drop | Same as RM17TG20 ¦ IEC62314,Only for solid state output,
84873021maximum leakage current | Same as RM17TG20 ¦ IEC62314,Only for solid state output,
84873021thermal current | Same as RM17TG20 ¦ IEC60947-5-1
84873021short circuit protection | Same as RM17TG20 ¦ IEC60947-5-1,Relay Output by external fuse,
84873021short circuit protection | Same as RM17TG20 ¦ IEC62314,Solid State Output by external fuse,
84873021
84873021time delay type | Same as RM17TG20 ¦ ,"OFF" delay,
84873021time delay type | Same as RM17TG20 ¦ ,"ON" delay,
84873021time delay type | Same as RM17TG20 ¦ ,Inhibition,
84873021time delay range | Same as RM17TG20 ¦ ,"OFF" delay,
84873021time delay range | Same as RM17TG20 ¦ ,"ON" delay,
84873021time delay range | Same as RM17TG20 ¦ ,Inhibition,
84873021response time | Same as RM17TG20 ¦ ,on crossing the threshold,
84873021response time | Same as RM17TG20
84873021response time | Same as RM17TG20
84873021response time | Same as RM17TG20
84873021response time | Same as RM17TG20
84873021power on delay | Same as RM17TG20
84873021reset time | Same as RM17TG20 ¦ ,through Un power reset,
84873021reset time | Same as RM17TG20 ¦ ,through front panel reset,
84873021reset time | Same as RM17TG20 ¦ ,through input control reset,
84873021setting accuracy of time delay | Same as RM17TG20
84873021repeat accuracy of time delay | Same as RM17TG20
84873021time delay drift | Same as RM17TG20
84873021time delay drift | Same as RM17TG20
84873021
84873021status LED | Same as RM17TG20
84873021local signalling | Same as RM17TG20 ¦ ,Power supply availability,
84873021local signalling | Same as RM17TG20 ¦ ,Power supply not availability,
84873021local signalling | Same as RM17TG20 ¦ ,Timing in-progress,
84873021local signalling | Same as RM17TG20 ¦ ,Output is energized,
84873021local signalling | Same as RM17TG20 ¦ ,Output is de-energized,
84873021local signalling | Same as RM17TG20 ¦ ,Range Setting Changes,
84873021local signalling | Same as RM17TG20 ¦ ,Phase Cut,
84873021local signalling | Same as RM17TG20 ¦ ,Phase Sequence Swap,
84873021local signalling | Same as RM17TG20 ¦ ,Undervoltage <U,
84873021local signalling | Same as RM17TG20 ¦ ,Overvoltage >U,
84873021local signalling | Same as RM17TG20 ¦ ,Phase Asymmetry,
84873021local signalling | Same as RM17TG20 ¦ ,Voltage Regeneration,
84873021local signalling | Same as RM17TG20 ¦ ,Extreme Undervoltage <U (Phase loss),
84873021local signalling | Same as RM17TG20 ¦ ,Extreme Overvoltage >U,
84873021local signalling | Same as RM17TG20 ¦ ,Extreme Phase Asymmetry,
84873021
84873021 | Same as RM17TG20
84873021 | Same as RM17TG20
84873021diagnostic button | Same as RM17TG20
84873021 | Same as RM17TG20
84873021 | Same as RM17TG20
84873021
84873021safety reliability data | Same as RM17TG20 ¦ ,MTTF,
84873021safety reliability data | Same as RM17TG20 ¦ ,B10,
84873021 | Same as RM17TG20 ¦ ,MTTFd,
84873021 | Same as RM17TG20 ¦ ,B10d,
84873021
84873021 | Drawing / Diagram
84873891
84873891standards | Same as RM17TG20
84873891product certifications | UL, CSA, CE, China ROHS
84873891marking | UL, CSA, CE, China ROHS
84873891directives | Same as RM17TG20
84873891directives | Same as RM17TG20
84873891directives | Same as RM17TG20
84873891
84873891 | Same as RM17TG20 ¦ IEC60721-3-3,Climatic category,
84873891 | Same as RM17TG20 ¦ Germanisher Lloyd,Environmental category,
84873891ambient air temperature for storage | Same as RM17TG20 ¦ ,Storage,
84873891ambient air temperature for operation | Same as RM17TG20 ¦ ,Operation,
84873891relative humidity | Same as RM17TG20 ¦ IEC60068-2-30,Damp heat,XX
84873891 | Same as RM17TG20 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873891vibration resistance | Same as RM17TG20 ¦ IEC60068-2-6
84873891shock resistance | Same as RM17TG20 ¦ IEC60068-2-27
84873891bump resistance | Same as RM17TG20 ¦ IEC60068-2-29
84873891seismic resistance | Same as RM17TG20 ¦ IEC60068-3-3
84873891IP degree of protection | Same as RM17TG20 ¦ IEC60529,Terminal Block,
84873891IP degree of protection | Same as RM17TG20 ¦ IEC60529,Housing,
84873891IP degree of protection | - ¦ IEC60529,Front Panel,
84873891
84873891width | Same as RM17TG20 ¦ ,Width,
84873891height | Same as RM17TG20 ¦ ,Height,
84873891depth | Same as RM17TG20 ¦ ,Depth,
84873891net weight | Same as RM17TG20
84873891mounting support | Same as RM17TG20 ¦ IEC/EN 60715,Without socket,
84873891mounting support | Same as RM17TG20 ¦ IEC/EN 60715,With socket,
84873891mounting position | Same as RM17TG20 ¦ ,In relation to normal vertical mounting plane,
84873891Minimum distance to adjacent devices | Same as RM17TG20 ¦ ,Horizontal,
84873891Minimum distance to adjacent devices | Same as RM17TG20 ¦ ,Vertical,
84873891connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873891connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873891connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Solid cable (spring terminal),
84873891connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Flexible cable (spring terminal),
84873891tightening torque | Same as RM17TG20 ¦ IEC60947-1,Tightening torque,
84873891cable stripping length | Same as RM17TG20 ¦ ,Cable stripping length,
84873891duty time | Same as RM17TG20
84873891
84873891electromagnetic compatibility | Same as RM17TG20 ¦ ,Generic immunity standard,
84873891electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-2,Electrostatic discharge,
84873891electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873891electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-4,Fast transient / burst,
84873891electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-5,Surge,
84873891electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-6,Conducted RF disturbance,
84873891electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-8,Power frequency magnetic field,
84873891electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873891electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873891electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-29,DC voltage interruption,
84873891electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-13,Low frequency harmonics,
84873891electromagnetic compatibility | Same as RM17TG20 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873891electromagnetic compatibility | Same as RM17TG20 ¦ ,Generic emission standard,
84873891electromagnetic compatibility | Same as RM17TG20 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873891electromagnetic compatibility | Same as RM17TG20 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873891electromagnetic compatibility | Same as RM17TG20 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873891electromagnetic compatibility | Same as RM17TG20 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873891electromagnetic compatibility | Same as RM17TG20 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873891electromagnetic compatibility | Same as RM17TG20 ¦ Germanisher Lloyd,Conducted emission,
84873891
84873891pollution degree | Same as RM17TG20 ¦ IEC60664-1
84873891overvoltage category | Same as RM17TG20 ¦ IEC60664-1
84873891circuit group | Same as RM17TG20 ¦ ,Supply,Terminal
84873891circuit group | Same as RM17TG20 ¦ ,Input 1,
84873891circuit group | Same as RM17TG20 ¦ ,Input 2,
84873891circuit group | Same as RM17TG20 ¦ ,Input 3,
84873891circuit group | Same as RM17TG20 ¦ ,Output 1,
84873891circuit group | Same as RM17TG20 ¦ ,Output 2,
84873891 | Same as RM17TG20 ¦ ,Supply,Rated
84873891 | Same as RM17TG20 ¦ ,Input 1,Voltage
84873891 | Same as RM17TG20 ¦ ,Input 2,Spec
84873891 | Same as RM17TG20 ¦ ,Input 3,
84873891 | Same as RM17TG20 ¦ ,Output 1,
84873891 | Same as RM17TG20 ¦ ,Output 2,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Output 1,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Output 2,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 2,Isolated
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 3,Circuit
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Output 1,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Output 2,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Output 1 / Output 2,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 1,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 2,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 1,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 2,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 1,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 2,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 2,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Input 3,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 3,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Output 1,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Output 2,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 2,Isolated
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 3,Circuit
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Output 1,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Output 2,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Output 1 / Output 2,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 1,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 2,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 1,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 2,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 1,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 2,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 2,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Input 3,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 3,
84873891dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 1,
84873891dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 2,
84873891dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 3,
84873891dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Output 1,
84873891dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Output 2,
84873891dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Output 1 / Output 2,
84873891dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 1,
84873891dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 2,
84873891dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 1,
84873891dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 2,
84873891dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 1,
84873891dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 2,
84873891dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 2,
84873891dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Input 3,
84873891dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 3,
84873891insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 1,
84873891insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 2,
84873891insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 3,
84873891insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Output 1,
84873891insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Output 2,
84873891insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Output 1 / Output 2,
84873891insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 1,
84873891insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 2,
84873891insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 1,
84873891insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 2,
84873891insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 1,
84873891insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 2,
84873891insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 2,
84873891insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Input 3,
84873891insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 3,
84873891
84873891[Us] rated supply voltage | Same as RM17TG20
84873891supply voltage limits | Same as RM17TG20
84873891polarity | Same as RM17TG20
84873891supply frequency | Same as RM17TG20
84873891supply frequency | Same as RM17TG20
84873891power consumption | Same as RM17TG20
84873891immunity to microbreaks | Same as RM17TG20
84873891supply terminal | Same as RM17TG20
84873891on-load factor | Same as RM17TG20
84873891release of input voltage | Same as RM17TG20
84873891
84873891monitoring functions | Same as RM17TG20 ¦ ,Phase lost ,
84873891monitoring functions | Same as RM17TG20 ¦ ,Phase sequence,
84873891monitoring functions | Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode),
84873891monitoring functions | Same as RM17TG20 ¦ ,Over voltage,
84873891monitoring functions | Same as RM17TG20 ¦ ,Undervoltage ,
84873891monitoring functions | Same as RM17TG20 ¦ ,Phase asymmetry,
84873891monitoring functions | Same as RM17TG20 ¦ ,Disconnection of neutral,
84873891monitoring functions | Same as RM17TG20 ¦ ,Voltage Regeneration,
84873891monitoring functions | Same as RM17TG20 ¦ ,Extreme undervoltage,
84873891monitoring functions | Same as RM17TG20 ¦ ,Extreme overvoltage,
84873891monitoring functions | Same as RM17TG20 ¦ ,Extreme asymmetry,
84873891 | Same as RM17TG20 ¦ ,Measurement mode,
84873891internal input resistance | Same as RM17TG20 ¦ ,Internal input resistance,
84873891input terminal | Same as RM17TG20 ¦ ,Input terminal,
84873891Input nominal voltage selection | Same as RM17TG20 ¦ ,Input nominal voltage selection,
84873891permissible input overload | Same as RM17TG20 ¦ ,permissible input overload,
84873891input frequency | Same as RM17TG20 ¦ ,Rated frequency,
84873891input frequency | Same as RM17TG20 ¦ ,Frequency operating range,
84873891setting accuracy of the switching threshold | Same as RM17TG20 ¦ ,Setting accuracy,
84873891repeat accuracy of the switching threshold | Same as RM17TG20 ¦ ,Repeat accuracy (constant parameters),
84873891measurement method | Same as RM17TG20 ¦ ,Measurement method,
84873891switching threshold drift | Same as RM17TG20 ¦ ,Measurement error with supply voltage variation,
84873891switching threshold drift | Same as RM17TG20 ¦ ,Measurement error with temperature variation,
84873891maximum measuring cycle | Same as RM17TG20 ¦ ,Maximum measuring cycles,
84873891measurement range | Same as RM17TG20 ¦ ,Phase lost ,
84873891measurement range | Same as RM17TG20 ¦ ,Phase sequence,
84873891measurement range | Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode),
84873891measurement range | Same as RM17TG20 ¦ ,Over voltage,
84873891measurement range | Same as RM17TG20 ¦ ,Undervoltage ,
84873891measurement range | Same as RM17TG20 ¦ ,Phase asymmetry,
84873891measurement range | Same as RM17TG20 ¦ ,Disconnection of neutral,
84873891measurement range | Same as RM17TG20 ¦ ,Voltage Regeneration,
84873891measurement range | Same as RM17TG20 ¦ ,Extreme undervoltage,
84873891measurement range | Same as RM17TG20 ¦ ,Extreme Overvoltage,
84873891measurement range | Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873891tripping threshold | Same as RM17TG20 ¦ ,Phase cut,
84873891tripping threshold | Same as RM17TG20 ¦ ,Phase sequence,
84873891tripping threshold | Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode),
84873891tripping threshold | Same as RM17TG20 ¦ ,Over voltage,
84873891tripping threshold | Same as RM17TG20 ¦ ,Undervoltage ,
84873891tripping threshold | Same as RM17TG20 ¦ ,Phase asymmetry,
84873891tripping threshold | Same as RM17TG20 ¦ ,Disconnection of neutral,
84873891tripping threshold | Same as RM17TG20 ¦ ,Voltage Regeneration,
84873891tripping threshold | Same as RM17TG20 ¦ ,Extreme undervoltage (Phase loss),
84873891tripping threshold | Same as RM17TG20 ¦ ,Extreme Overvoltage,
84873891tripping threshold | Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873891hysteresis | Same as RM17TG20 ¦ ,Phase cut,
84873891hysteresis | Same as RM17TG20 ¦ ,Phase sequence,
84873891hysteresis | Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode),
84873891hysteresis | Same as RM17TG20 ¦ ,Over voltage,
84873891hysteresis | Same as RM17TG20 ¦ ,Undervoltage ,
84873891hysteresis | Same as RM17TG20 ¦ ,Phase asymmetry,
84873891hysteresis | Same as RM17TG20 ¦ ,Disconnection of neutral,
84873891hysteresis | Same as RM17TG20 ¦ ,Voltage Regeneration,
84873891hysteresis | Same as RM17TG20 ¦ ,Extreme undervoltage (Phase loss),
84873891hysteresis | Same as RM17TG20 ¦ ,Extreme Overvoltage,
84873891hysteresis | Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873891
84873891output type | Same as RM17TG20
84873891output terminal | Same as RM17TG20
84873891output logic | Same as RM17TG20 ¦ ,R1 (11-12-14),
84873891output logic | Same as RM17TG20 ¦ ,R2 (21-22-24),
84873891contacts material | Same as RM17TG20
84873891mechanical durability | Same as RM17TG20 ¦ IEC61810-1
84873891electrical durability | Same as RM17TG20 ¦ IEC60947-4-1,AC-1,
84873891electrical durability | Same as RM17TG20 ¦ IEC60947-4-1,DC-1,
84873891electrical durability | Same as RM17TG20 ¦ IEC60947-5-1,AC-15,
84873891electrical durability | Same as RM17TG20 ¦ IEC60947-5-1,DC-13,
84873891[Ue] rated operational voltage | Same as RM17TG20 ¦ IEC61810-1,Rated switching voltage,
84873891[Ie] rated operational current | Same as RM17TG20 ¦ IEC61810-1,Rated switching current,
84873891maximum switching capacity | Same as RM17TG20 ¦ ,Maximum switching voltage,
84873891maximum switching capacity | Same as RM17TG20 ¦ ,Maximum switching current,
84873891maximum switching capacity | Same as RM17TG20 ¦ ,Maximum switching capacity,
84873891minimum switching capacity | Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching voltage,
84873891minimum switching capacity | Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching current,
84873891minimum switching capacity | Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching capacity,
84873891maximum voltage drop | Same as RM17TG20 ¦ IEC62314,Only for solid state output,
84873891maximum leakage current | Same as RM17TG20 ¦ IEC62314,Only for solid state output,
84873891thermal current | Same as RM17TG20 ¦ IEC60947-5-1
84873891short circuit protection | Same as RM17TG20 ¦ IEC60947-5-1,Relay Output by external fuse,
84873891short circuit protection | Same as RM17TG20 ¦ IEC62314,Solid State Output by external fuse,
84873891
84873891time delay type | Same as RM17TG20 ¦ ,"OFF" delay,
84873891time delay type | Same as RM17TG20 ¦ ,"ON" delay,
84873891time delay type | Same as RM17TG20 ¦ ,Inhibition,
84873891time delay range | Same as RM17TG20 ¦ ,"OFF" delay,
84873891time delay range | Same as RM17TG20 ¦ ,"ON" delay,
84873891time delay range | Same as RM17TG20 ¦ ,Inhibition,
84873891response time | Same as RM17TG20 ¦ ,on crossing the threshold,
84873891response time | Same as RM17TG20
84873891response time | Same as RM17TG20
84873891response time | Same as RM17TG20
84873891response time | Same as RM17TG20
84873891power on delay | Same as RM17TG20
84873891reset time | Same as RM17TG20 ¦ ,through Un power reset,
84873891reset time | Same as RM17TG20 ¦ ,through front panel reset,
84873891reset time | Same as RM17TG20 ¦ ,through input control reset,
84873891setting accuracy of time delay | Same as RM17TG20
84873891repeat accuracy of time delay | Same as RM17TG20
84873891time delay drift | Same as RM17TG20
84873891time delay drift | Same as RM17TG20
84873891
84873891status LED | Same as RM17TG20
84873891local signalling | Same as RM17TG20 ¦ ,Power supply availability,
84873891local signalling | Same as RM17TG20 ¦ ,Power supply not availability,
84873891local signalling | Same as RM17TG20 ¦ ,Timing in-progress,
84873891local signalling | Same as RM17TG20 ¦ ,Output is energized,
84873891local signalling | Same as RM17TG20 ¦ ,Output is de-energized,
84873891local signalling | Same as RM17TG20 ¦ ,Range Setting Changes,
84873891local signalling | Same as RM17TG20 ¦ ,Phase Cut,
84873891local signalling | Same as RM17TG20 ¦ ,Phase Sequence Swap,
84873891local signalling | Same as RM17TG20 ¦ ,Undervoltage <U,
84873891local signalling | Same as RM17TG20 ¦ ,Overvoltage >U,
84873891local signalling | Same as RM17TG20 ¦ ,Phase Asymmetry,
84873891local signalling | Same as RM17TG20 ¦ ,Voltage Regeneration,
84873891local signalling | Same as RM17TG20 ¦ ,Extreme Undervoltage <U (Phase loss),
84873891local signalling | Same as RM17TG20 ¦ ,Extreme Overvoltage >U,
84873891local signalling | Same as RM17TG20 ¦ ,Extreme Phase Asymmetry,
84873891
84873891 | Same as RM17TG20
84873891 | Same as RM17TG20
84873891diagnostic button | Same as RM17TG20
84873891 | Same as RM17TG20
84873891 | Same as RM17TG20
84873891
84873891safety reliability data | Same as RM17TG20 ¦ ,MTTF,
84873891safety reliability data | Same as RM17TG20 ¦ ,B10,
84873891 | Same as RM17TG20 ¦ ,MTTFd,
84873891 | Same as RM17TG20 ¦ ,B10d,
84873891
84873891 | Drawing / Diagram
RM17TG00
RM17TG00standards | Same as RM17TG20
RM17TG00product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TG00marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TG00directives | Same as RM17TG20
RM17TG00directives | Same as RM17TG20
RM17TG00directives | Same as RM17TG20
RM17TG00
RM17TG00 | Same as RM17TG20 ¦ IEC60721-3-3,Climatic category,
RM17TG00 | Same as RM17TG20 ¦ Germanisher Lloyd,Environmental category,
RM17TG00ambient air temperature for storage | Same as RM17TG20 ¦ ,Storage,
RM17TG00ambient air temperature for operation | Same as RM17TG20 ¦ ,Operation,
RM17TG00relative humidity | Same as RM17TG20 ¦ IEC60068-2-30,Damp heat,XX
RM17TG00 | Same as RM17TG20 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM17TG00vibration resistance | Same as RM17TG20 ¦ IEC60068-2-6
RM17TG00shock resistance | Same as RM17TG20 ¦ IEC60068-2-27
RM17TG00bump resistance | Same as RM17TG20 ¦ IEC60068-2-29
RM17TG00seismic resistance | Same as RM17TG20 ¦ IEC60068-3-3
RM17TG00IP degree of protection | Same as RM17TG20 ¦ IEC60529,Terminal Block,
RM17TG00IP degree of protection | Same as RM17TG20 ¦ IEC60529,Housing,
RM17TG00IP degree of protection | Same as RM17TG20 ¦ IEC60529,Front Panel,
RM17TG00
RM17TG00width | Same as RM17TG20 ¦ ,Width,
RM17TG00height | Same as RM17TG20 ¦ ,Height,
RM17TG00depth | Same as RM17TG20 ¦ ,Depth,
RM17TG00net weight | Same as RM17TG20
RM17TG00mounting support | Same as RM17TG20 ¦ IEC/EN 60715,Without socket,
RM17TG00mounting support | Same as RM17TG20 ¦ IEC/EN 60715,With socket,
RM17TG00mounting position | Same as RM17TG20 ¦ ,In relation to normal vertical mounting plane,
RM17TG00Minimum distance to adjacent devices | Same as RM17TG20 ¦ ,Horizontal,
RM17TG00Minimum distance to adjacent devices | Same as RM17TG20 ¦ ,Vertical,
RM17TG00connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM17TG00connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM17TG00connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Solid cable (spring terminal),
RM17TG00connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Flexible cable (spring terminal),
RM17TG00tightening torque | Same as RM17TG20 ¦ IEC60947-1,Tightening torque,
RM17TG00cable stripping length | Same as RM17TG20 ¦ ,Cable stripping length,
RM17TG00duty time | Same as RM17TG20
RM17TG00
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ ,Generic immunity standard,
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-2,Electrostatic discharge,
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-4,Fast transient / burst,
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-5,Surge,
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-6,Conducted RF disturbance,
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-8,Power frequency magnetic field,
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-18,1 MHz oscillation wave,
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-29,DC voltage interruption,
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-13,Low frequency harmonics,
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ ,Generic emission standard,
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ Germanisher Lloyd,Conducted emission,
RM17TG00
RM17TG00pollution degree | Same as RM17TG20 ¦ IEC60664-1
RM17TG00overvoltage category | Same as RM17TG20 ¦ IEC60664-1
RM17TG00circuit group | Same as RM17TG20 ¦ ,Supply,Terminal
RM17TG00circuit group | Same as RM17TG20 ¦ ,Input 1,
RM17TG00circuit group | Same as RM17TG20 ¦ ,Input 2,
RM17TG00circuit group | Same as RM17TG20 ¦ ,Input 3,
RM17TG00circuit group | Same as RM17TG20 ¦ ,Output 1,
RM17TG00circuit group | Same as RM17TG20 ¦ ,Output 2,
RM17TG00 | 208..480 AC ¦ ,Supply,Rated
RM17TG00 | Same as RM17TG20 ¦ ,Input 1,Voltage
RM17TG00 | Same as RM17TG20 ¦ ,Input 2,Spec
RM17TG00 | Same as RM17TG20 ¦ ,Input 3,
RM17TG00 | 250V ¦ ,Output 1,
RM17TG00 | - ¦ ,Output 2,
RM17TG00[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM17TG00[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1,
RM17TG00[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2,
RM17TG00[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3,
RM17TG00[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM17TG00[Ui] rated insulation voltage | - ¦ IEC60664-1,Output 2,
RM17TG00[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM17TG00[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 2,Isolated
RM17TG00[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 3,Circuit
RM17TG00[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM17TG00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Output 2,
RM17TG00[Ui] rated insulation voltage | - ¦ IEC60664-1,Output 1 / Output 2,
RM17TG00[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 1,
RM17TG00[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 2,
RM17TG00[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 1,
RM17TG00[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 2,
RM17TG00[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 1,
RM17TG00[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 2,
RM17TG00[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 2,
RM17TG00[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Input 3,
RM17TG00[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 3,
RM17TG00[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1,
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2,
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3,
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Output 1,
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Output 2,
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 2,Isolated
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 3,Circuit
RM17TG00[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM17TG00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Output 2,
RM17TG00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1 / Output 2,
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 1,
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 2,
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 1,
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 2,
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 1,
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 2,
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 2,
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Input 3,
RM17TG00[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 3,
RM17TG00dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 1,
RM17TG00dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 2,
RM17TG00dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 3,
RM17TG00dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM17TG00dielectric strength | - ¦ IEC60255-27,Supply / Output 2,
RM17TG00dielectric strength | - ¦ IEC60255-27,Output 1 / Output 2,
RM17TG00dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 1,
RM17TG00dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 2,
RM17TG00dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 1,
RM17TG00dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 2,
RM17TG00dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 1,
RM17TG00dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 2,
RM17TG00dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 2,
RM17TG00dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Input 3,
RM17TG00dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 3,
RM17TG00insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 1,
RM17TG00insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 2,
RM17TG00insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 3,
RM17TG00insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM17TG00insulation resistance | - ¦ IEC60255-27,Supply / Output 2,
RM17TG00insulation resistance | - ¦ IEC60255-27,Output 1 / Output 2,
RM17TG00insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 1,
RM17TG00insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 2,
RM17TG00insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 1,
RM17TG00insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 2,
RM17TG00insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 1,
RM17TG00insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 2,
RM17TG00insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 2,
RM17TG00insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Input 3,
RM17TG00insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 3,
RM17TG00
RM17TG00[Us] rated supply voltage | ~ 3 x 208…3 x 480
RM17TG00supply voltage limits | ~ 3 x 183…3 x 528
RM17TG00polarity | -
RM17TG00supply frequency | Same as RM17TG20
RM17TG00supply frequency | Same as RM17TG20
RM17TG00power consumption | Same as RM17TG20
RM17TG00immunity to microbreaks | Same as RM17TG20
RM17TG00supply terminal | Same as RM17TG20
RM17TG00on-load factor | Same as RM17TG20
RM17TG00release of input voltage | Same as RM17TG20
RM17TG00
RM17TG00monitoring functions | Same as RM17TG20 ¦ ,Phase lost ,
RM17TG00monitoring functions | Same as RM17TG20 ¦ ,Phase sequence,
RM17TG00monitoring functions | Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode),
RM17TG00monitoring functions | Same as RM17TG20 ¦ ,Over voltage,
RM17TG00monitoring functions | Same as RM17TG20 ¦ ,Undervoltage ,
RM17TG00monitoring functions | Same as RM17TG20 ¦ ,Phase asymmetry,
RM17TG00monitoring functions | Same as RM17TG20 ¦ ,Disconnection of neutral,
RM17TG00monitoring functions | Same as RM17TG20 ¦ ,Voltage Regeneration,
RM17TG00monitoring functions | Same as RM17TG20 ¦ ,Extreme undervoltage,
RM17TG00monitoring functions | Same as RM17TG20 ¦ ,Extreme overvoltage,
RM17TG00monitoring functions | Same as RM17TG20 ¦ ,Extreme asymmetry,
RM17TG00 | Same as RM17TG20 ¦ ,Measurement mode,
RM17TG00internal input resistance | - ¦ ,Internal input resistance,
RM17TG00input terminal | Same as RM17TG20 ¦ ,Input terminal,
RM17TG00Input nominal voltage selection | - ¦ ,Input nominal voltage selection,
RM17TG00permissible input overload | - ¦ ,permissible input overload,
RM17TG00input frequency | Same as RM17TG20 ¦ ,Rated frequency,
RM17TG00input frequency | Same as RM17TG20 ¦ ,Frequency operating range,
RM17TG00setting accuracy of the switching threshold | Same as RM17TG20 ¦ ,Setting accuracy,
RM17TG00repeat accuracy of the switching threshold | Same as RM17TG20 ¦ ,Repeat accuracy (constant parameters),
RM17TG00measurement method | Same as RM17TG20 ¦ ,Measurement method,
RM17TG00switching threshold drift | Same as RM17TG20 ¦ ,Measurement error with supply voltage variation,
RM17TG00switching threshold drift | Same as RM17TG20 ¦ ,Measurement error with temperature variation,
RM17TG00maximum measuring cycle | Same as RM17TG20 ¦ ,Maximum measuring cycles,
RM17TG00measurement range | Same as RM17TG20 ¦ ,Phase lost ,
RM17TG00measurement range | Same as RM17TG20 ¦ ,Phase sequence,
RM17TG00measurement range | Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode),
RM17TG00measurement range | Same as RM17TG20 ¦ ,Over voltage,
RM17TG00measurement range | Same as RM17TG20 ¦ ,Undervoltage ,
RM17TG00measurement range | Same as RM17TG20 ¦ ,Phase asymmetry,
RM17TG00measurement range | Same as RM17TG20 ¦ ,Disconnection of neutral,
RM17TG00measurement range | Same as RM17TG20 ¦ ,Voltage Regeneration,
RM17TG00measurement range | Same as RM17TG20 ¦ ,Extreme undervoltage,
RM17TG00measurement range | Same as RM17TG20 ¦ ,Extreme Overvoltage,
RM17TG00measurement range | Same as RM17TG20 ¦ ,Extreme Asymmetry,
RM17TG00tripping threshold | Same as RM17TG20 ¦ ,Phase cut,
RM17TG00tripping threshold | Same as RM17TG20 ¦ ,Phase sequence,
RM17TG00tripping threshold | Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode),
RM17TG00tripping threshold | Same as RM17TG20 ¦ ,Over voltage,
RM17TG00tripping threshold | Same as RM17TG20 ¦ ,Undervoltage ,
RM17TG00tripping threshold | Same as RM17TG20 ¦ ,Phase asymmetry,
RM17TG00tripping threshold | Same as RM17TG20 ¦ ,Disconnection of neutral,
RM17TG00tripping threshold | Same as RM17TG20 ¦ ,Voltage Regeneration,
RM17TG00tripping threshold | Same as RM17TG20 ¦ ,Extreme undervoltage (Phase loss),
RM17TG00tripping threshold | Same as RM17TG20 ¦ ,Extreme Overvoltage,
RM17TG00tripping threshold | Same as RM17TG20 ¦ ,Extreme Asymmetry,
RM17TG00hysteresis | Same as RM17TG20 ¦ ,Phase cut,
RM17TG00hysteresis | Same as RM17TG20 ¦ ,Phase sequence,
RM17TG00hysteresis | Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode),
RM17TG00hysteresis | Same as RM17TG20 ¦ ,Over voltage,
RM17TG00hysteresis | Same as RM17TG20 ¦ ,Undervoltage ,
RM17TG00hysteresis | Same as RM17TG20 ¦ ,Phase asymmetry,
RM17TG00hysteresis | Same as RM17TG20 ¦ ,Disconnection of neutral,
RM17TG00hysteresis | Same as RM17TG20 ¦ ,Voltage Regeneration,
RM17TG00hysteresis | Same as RM17TG20 ¦ ,Extreme undervoltage (Phase loss),
RM17TG00hysteresis | Same as RM17TG20 ¦ ,Extreme Overvoltage,
RM17TG00hysteresis | Same as RM17TG20 ¦ ,Extreme Asymmetry,
RM17TG00
RM17TG00output type | 1 x C/O relay contacts
RM17TG00output terminal | Same as RM17TG20
RM17TG00output logic | Same as RM17TG20 ¦ ,R1 (11-12-14),
RM17TG00output logic | Same as RM17TG20 ¦ ,R2 (21-22-24),
RM17TG00contacts material | Same as RM17TG20
RM17TG00mechanical durability | Same as RM17TG20 ¦ IEC61810-1
RM17TG00electrical durability | Same as RM17TG20 ¦ IEC60947-4-1,AC-1,
RM17TG00electrical durability | Same as RM17TG20 ¦ IEC60947-4-1,DC-1,
RM17TG00electrical durability | Same as RM17TG20 ¦ IEC60947-5-1,AC-15,
RM17TG00electrical durability | Same as RM17TG20 ¦ IEC60947-5-1,DC-13,
RM17TG00[Ue] rated operational voltage | Same as RM17TG20 ¦ IEC61810-1,Rated switching voltage,
RM17TG00[Ie] rated operational current | Same as RM17TG20 ¦ IEC61810-1,Rated switching current,
RM17TG00maximum switching capacity | Same as RM17TG20 ¦ ,Maximum switching voltage,
RM17TG00maximum switching capacity | Same as RM17TG20 ¦ ,Maximum switching current,
RM17TG00maximum switching capacity | Same as RM17TG20 ¦ ,Maximum switching capacity,
RM17TG00minimum switching capacity | Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching voltage,
RM17TG00minimum switching capacity | Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching current,
RM17TG00minimum switching capacity | Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching capacity,
RM17TG00maximum voltage drop | Same as RM17TG20 ¦ IEC62314,Only for solid state output,
RM17TG00maximum leakage current | Same as RM17TG20 ¦ IEC62314,Only for solid state output,
RM17TG00thermal current | Same as RM17TG20 ¦ IEC60947-5-1
RM17TG00short circuit protection | Same as RM17TG20 ¦ IEC60947-5-1,Relay Output by external fuse,
RM17TG00short circuit protection | Same as RM17TG20 ¦ IEC62314,Solid State Output by external fuse,
RM17TG00
RM17TG00time delay type | Same as RM17TG20 ¦ ,"OFF" delay,
RM17TG00time delay type | Same as RM17TG20 ¦ ,"ON" delay,
RM17TG00time delay type | Same as RM17TG20 ¦ ,Inhibition,
RM17TG00time delay range | Same as RM17TG20 ¦ ,"OFF" delay,
RM17TG00time delay range | Same as RM17TG20 ¦ ,"ON" delay,
RM17TG00time delay range | Same as RM17TG20 ¦ ,Inhibition,
RM17TG00response time | Same as RM17TG20 ¦ ,on crossing the threshold,
RM17TG00response time | Same as RM17TG20
RM17TG00response time | Same as RM17TG20
RM17TG00response time | Same as RM17TG20
RM17TG00response time | Same as RM17TG20
RM17TG00power on delay | Same as RM17TG20
RM17TG00reset time | Same as RM17TG20 ¦ ,through Un power reset,
RM17TG00reset time | Same as RM17TG20 ¦ ,through front panel reset,
RM17TG00reset time | Same as RM17TG20 ¦ ,through input control reset,
RM17TG00setting accuracy of time delay | Same as RM17TG20
RM17TG00repeat accuracy of time delay | Same as RM17TG20
RM17TG00time delay drift | Same as RM17TG20
RM17TG00time delay drift | Same as RM17TG20
RM17TG00
RM17TG00status LED | Same as RM17TG20
RM17TG00local signalling | Same as RM17TG20 ¦ ,Power supply availability,
RM17TG00local signalling | Same as RM17TG20 ¦ ,Power supply not availability,
RM17TG00local signalling | Same as RM17TG20 ¦ ,Timing in-progress,
RM17TG00local signalling | Same as RM17TG20 ¦ ,Output is energized,
RM17TG00local signalling | Same as RM17TG20 ¦ ,Output is de-energized,
RM17TG00local signalling | Same as RM17TG20 ¦ ,Range Setting Changes,
RM17TG00local signalling | Same as RM17TG20 ¦ ,Phase Cut,
RM17TG00local signalling | Same as RM17TG20 ¦ ,Phase Sequence Swap,
RM17TG00local signalling | Same as RM17TG20 ¦ ,Undervoltage <U,
RM17TG00local signalling | Same as RM17TG20 ¦ ,Overvoltage >U,
RM17TG00local signalling | Same as RM17TG20 ¦ ,Phase Asymmetry,
RM17TG00local signalling | Same as RM17TG20 ¦ ,Voltage Regeneration,
RM17TG00local signalling | Same as RM17TG20 ¦ ,Extreme Undervoltage <U (Phase loss),
RM17TG00local signalling | Same as RM17TG20 ¦ ,Extreme Overvoltage >U,
RM17TG00local signalling | Same as RM17TG20 ¦ ,Extreme Phase Asymmetry,
RM17TG00
RM17TG00 | Same as RM17TG20
RM17TG00 | Same as RM17TG20
RM17TG00diagnostic button | Same as RM17TG20
RM17TG00 | Same as RM17TG20
RM17TG00 | Same as RM17TG20
RM17TG00
RM17TG00safety reliability data | Same as RM17TG20 ¦ ,MTTF,
RM17TG00safety reliability data | Same as RM17TG20 ¦ ,B10,
RM17TG00 | Same as RM17TG20 ¦ ,MTTFd,
RM17TG00 | Same as RM17TG20 ¦ ,B10d,
RM17TG00
RM17TG00 | Drawing / Diagram
RM10TG00
RM10TG00standards | Same as RM17TG00
RM10TG00product certifications | CCC, CE, China ROHS
RM10TG00marking | CCC, CE, China ROHS
RM10TG00directives | Same as RM17TG00
RM10TG00directives | Same as RM17TG00
RM10TG00directives | Same as RM17TG00
RM10TG00
RM10TG00 | Same as RM17TG00 ¦ IEC60721-3-3,Climatic category,
RM10TG00 | Same as RM17TG00 ¦ Germanisher Lloyd,Environmental category,
RM10TG00ambient air temperature for storage | Same as RM17TG00 ¦ ,Storage,
RM10TG00ambient air temperature for operation | Same as RM17TG00 ¦ ,Operation,
RM10TG00relative humidity | Same as RM17TG00 ¦ IEC60068-2-30,Damp heat,XX
RM10TG00 | Same as RM17TG00 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM10TG00vibration resistance | Same as RM17TG00 ¦ IEC60068-2-6
RM10TG00shock resistance | Same as RM17TG00 ¦ IEC60068-2-27
RM10TG00bump resistance | Same as RM17TG00 ¦ IEC60068-2-29
RM10TG00seismic resistance | Same as RM17TG00 ¦ IEC60068-3-3
RM10TG00IP degree of protection | Same as RM17TG00 ¦ IEC60529,Terminal Block,
RM10TG00IP degree of protection | Same as RM17TG00 ¦ IEC60529,Housing,
RM10TG00IP degree of protection | Same as RM17TG00 ¦ IEC60529,Front Panel,
RM10TG00
RM10TG00width | Same as RM17TG00 ¦ ,Width,
RM10TG00height | Same as RM17TG00 ¦ ,Height,
RM10TG00depth | Same as RM17TG00 ¦ ,Depth,
RM10TG00net weight | Same as RM17TG00
RM10TG00mounting support | Same as RM17TG00 ¦ IEC/EN 60715,Without socket,
RM10TG00mounting support | Same as RM17TG00 ¦ IEC/EN 60715,With socket,
RM10TG00mounting position | Same as RM17TG00 ¦ ,In relation to normal vertical mounting plane,
RM10TG00Minimum distance to adjacent devices | Same as RM17TG00 ¦ ,Horizontal,
RM10TG00Minimum distance to adjacent devices | Same as RM17TG00 ¦ ,Vertical,
RM10TG00connections - terminals | Same as RM17TG00 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM10TG00connections - terminals | Same as RM17TG00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM10TG00connections - terminals | Same as RM17TG00 ¦ IEC60947-1,Solid cable (spring terminal),
RM10TG00connections - terminals | Same as RM17TG00 ¦ IEC60947-1,Flexible cable (spring terminal),
RM10TG00tightening torque | Same as RM17TG00 ¦ IEC60947-1,Tightening torque,
RM10TG00cable stripping length | Same as RM17TG00 ¦ ,Cable stripping length,
RM10TG00duty time | Same as RM17TG00
RM10TG00
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ ,Generic immunity standard,
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-2,Electrostatic discharge,
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-4,Fast transient / burst,
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-5,Surge,
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-6,Conducted RF disturbance,
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-8,Power frequency magnetic field,
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-18,1 MHz oscillation wave,
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-29,DC voltage interruption,
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-13,Low frequency harmonics,
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ ,Generic emission standard,
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ Germanisher Lloyd,Conducted emission,
RM10TG00
RM10TG00pollution degree | Same as RM17TG00 ¦ IEC60664-1
RM10TG00overvoltage category | Same as RM17TG00 ¦ IEC60664-1
RM10TG00circuit group | Same as RM17TG00 ¦ ,Supply,Terminal
RM10TG00circuit group | Same as RM17TG00 ¦ ,Input 1,
RM10TG00circuit group | Same as RM17TG00 ¦ ,Input 2,
RM10TG00circuit group | Same as RM17TG00 ¦ ,Input 3,
RM10TG00circuit group | Same as RM17TG00 ¦ ,Output 1,
RM10TG00circuit group | Same as RM17TG00 ¦ ,Output 2,
RM10TG00 | Same as RM17TG00 ¦ ,Supply,Rated
RM10TG00 | Same as RM17TG00 ¦ ,Input 1,Voltage
RM10TG00 | Same as RM17TG00 ¦ ,Input 2,Spec
RM10TG00 | Same as RM17TG00 ¦ ,Input 3,
RM10TG00 | Same as RM17TG00 ¦ ,Output 1,
RM10TG00 | Same as RM17TG00 ¦ ,Output 2,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Output 1,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Output 2,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 2,Isolated
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 3,Circuit
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Output 1,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Output 2,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Output 1 / Output 2,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 1,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 2,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 1,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 2,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 1,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 2,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 2,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Input 3,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 3,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Output 1,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Output 2,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 2,Isolated
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 3,Circuit
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Output 1,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Output 2,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Output 1 / Output 2,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 1,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 2,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 1,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 2,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 1,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 2,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 2,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Input 3,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 3,
RM10TG00dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 1,
RM10TG00dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 2,
RM10TG00dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 3,
RM10TG00dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Output 1,
RM10TG00dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Output 2,
RM10TG00dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Output 1 / Output 2,
RM10TG00dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 1,
RM10TG00dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 2,
RM10TG00dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 1,
RM10TG00dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 2,
RM10TG00dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 1,
RM10TG00dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 2,
RM10TG00dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 2,
RM10TG00dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Input 3,
RM10TG00dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 3,
RM10TG00insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 1,
RM10TG00insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 2,
RM10TG00insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 3,
RM10TG00insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Output 1,
RM10TG00insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Output 2,
RM10TG00insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Output 1 / Output 2,
RM10TG00insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 1,
RM10TG00insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 2,
RM10TG00insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 1,
RM10TG00insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 2,
RM10TG00insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 1,
RM10TG00insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 2,
RM10TG00insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 2,
RM10TG00insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Input 3,
RM10TG00insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 3,
RM10TG00
RM10TG00[Us] rated supply voltage | Same as RM17TG00
RM10TG00supply voltage limits | Same as RM17TG00
RM10TG00polarity | Same as RM17TG00
RM10TG00supply frequency | Same as RM17TG00
RM10TG00supply frequency | Same as RM17TG00
RM10TG00power consumption | Same as RM17TG00
RM10TG00immunity to microbreaks | Same as RM17TG00
RM10TG00supply terminal | Same as RM17TG00
RM10TG00on-load factor | Same as RM17TG00
RM10TG00release of input voltage | Same as RM17TG00
RM10TG00
RM10TG00monitoring functions | Same as RM17TG00 ¦ ,Phase lost ,
RM10TG00monitoring functions | Same as RM17TG00 ¦ ,Phase sequence,
RM10TG00monitoring functions | Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode),
RM10TG00monitoring functions | Same as RM17TG00 ¦ ,Over voltage,
RM10TG00monitoring functions | Same as RM17TG00 ¦ ,Undervoltage ,
RM10TG00monitoring functions | Same as RM17TG00 ¦ ,Phase asymmetry,
RM10TG00monitoring functions | Same as RM17TG00 ¦ ,Disconnection of neutral,
RM10TG00monitoring functions | Same as RM17TG00 ¦ ,Voltage Regeneration,
RM10TG00monitoring functions | Same as RM17TG00 ¦ ,Extreme undervoltage,
RM10TG00monitoring functions | Same as RM17TG00 ¦ ,Extreme overvoltage,
RM10TG00monitoring functions | Same as RM17TG00 ¦ ,Extreme asymmetry,
RM10TG00 | Same as RM17TG00 ¦ ,Measurement mode,
RM10TG00internal input resistance | Same as RM17TG00 ¦ ,Internal input resistance,
RM10TG00input terminal | Same as RM17TG00 ¦ ,Input terminal,
RM10TG00Input nominal voltage selection | Same as RM17TG00 ¦ ,Input nominal voltage selection,
RM10TG00permissible input overload | Same as RM17TG00 ¦ ,permissible input overload,
RM10TG00input frequency | Same as RM17TG00 ¦ ,Rated frequency,
RM10TG00input frequency | Same as RM17TG00 ¦ ,Frequency operating range,
RM10TG00setting accuracy of the switching threshold | Same as RM17TG00 ¦ ,Setting accuracy,
RM10TG00repeat accuracy of the switching threshold | Same as RM17TG00 ¦ ,Repeat accuracy (constant parameters),
RM10TG00measurement method | Same as RM17TG00 ¦ ,Measurement method,
RM10TG00switching threshold drift | Same as RM17TG00 ¦ ,Measurement error with supply voltage variation,
RM10TG00switching threshold drift | Same as RM17TG00 ¦ ,Measurement error with temperature variation,
RM10TG00maximum measuring cycle | Same as RM17TG00 ¦ ,Maximum measuring cycles,
RM10TG00measurement range | Same as RM17TG00 ¦ ,Phase lost ,
RM10TG00measurement range | Same as RM17TG00 ¦ ,Phase sequence,
RM10TG00measurement range | Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode),
RM10TG00measurement range | Same as RM17TG00 ¦ ,Over voltage,
RM10TG00measurement range | Same as RM17TG00 ¦ ,Undervoltage ,
RM10TG00measurement range | Same as RM17TG00 ¦ ,Phase asymmetry,
RM10TG00measurement range | Same as RM17TG00 ¦ ,Disconnection of neutral,
RM10TG00measurement range | Same as RM17TG00 ¦ ,Voltage Regeneration,
RM10TG00measurement range | Same as RM17TG00 ¦ ,Extreme undervoltage,
RM10TG00measurement range | Same as RM17TG00 ¦ ,Extreme Overvoltage,
RM10TG00measurement range | Same as RM17TG00 ¦ ,Extreme Asymmetry,
RM10TG00tripping threshold | Same as RM17TG00 ¦ ,Phase cut,
RM10TG00tripping threshold | Same as RM17TG00 ¦ ,Phase sequence,
RM10TG00tripping threshold | Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode),
RM10TG00tripping threshold | Same as RM17TG00 ¦ ,Over voltage,
RM10TG00tripping threshold | Same as RM17TG00 ¦ ,Undervoltage ,
RM10TG00tripping threshold | Same as RM17TG00 ¦ ,Phase asymmetry,
RM10TG00tripping threshold | Same as RM17TG00 ¦ ,Disconnection of neutral,
RM10TG00tripping threshold | Same as RM17TG00 ¦ ,Voltage Regeneration,
RM10TG00tripping threshold | Same as RM17TG00 ¦ ,Extreme undervoltage (Phase loss),
RM10TG00tripping threshold | Same as RM17TG00 ¦ ,Extreme Overvoltage,
RM10TG00tripping threshold | Same as RM17TG00 ¦ ,Extreme Asymmetry,
RM10TG00hysteresis | Same as RM17TG00 ¦ ,Phase cut,
RM10TG00hysteresis | Same as RM17TG00 ¦ ,Phase sequence,
RM10TG00hysteresis | Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode),
RM10TG00hysteresis | Same as RM17TG00 ¦ ,Over voltage,
RM10TG00hysteresis | Same as RM17TG00 ¦ ,Undervoltage ,
RM10TG00hysteresis | Same as RM17TG00 ¦ ,Phase asymmetry,
RM10TG00hysteresis | Same as RM17TG00 ¦ ,Disconnection of neutral,
RM10TG00hysteresis | Same as RM17TG00 ¦ ,Voltage Regeneration,
RM10TG00hysteresis | Same as RM17TG00 ¦ ,Extreme undervoltage (Phase loss),
RM10TG00hysteresis | Same as RM17TG00 ¦ ,Extreme Overvoltage,
RM10TG00hysteresis | Same as RM17TG00 ¦ ,Extreme Asymmetry,
RM10TG00
RM10TG00output type | Same as RM17TG00
RM10TG00output terminal | Same as RM17TG00
RM10TG00output logic | Same as RM17TG00 ¦ ,R1 (11-12-14),
RM10TG00output logic | Same as RM17TG00 ¦ ,R2 (21-22-24),
RM10TG00contacts material | Same as RM17TG00
RM10TG00mechanical durability | Same as RM17TG00 ¦ IEC61810-1
RM10TG00electrical durability | Same as RM17TG00 ¦ IEC60947-4-1,AC-1,
RM10TG00electrical durability | Same as RM17TG00 ¦ IEC60947-4-1,DC-1,
RM10TG00electrical durability | Same as RM17TG00 ¦ IEC60947-5-1,AC-15,
RM10TG00electrical durability | Same as RM17TG00 ¦ IEC60947-5-1,DC-13,
RM10TG00[Ue] rated operational voltage | Same as RM17TG00 ¦ IEC61810-1,Rated switching voltage,
RM10TG00[Ie] rated operational current | Same as RM17TG00 ¦ IEC61810-1,Rated switching current,
RM10TG00maximum switching capacity | Same as RM17TG00 ¦ ,Maximum switching voltage,
RM10TG00maximum switching capacity | Same as RM17TG00 ¦ ,Maximum switching current,
RM10TG00maximum switching capacity | Same as RM17TG00 ¦ ,Maximum switching capacity,
RM10TG00minimum switching capacity | Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching voltage,
RM10TG00minimum switching capacity | Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching current,
RM10TG00minimum switching capacity | Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching capacity,
RM10TG00maximum voltage drop | Same as RM17TG00 ¦ IEC62314,Only for solid state output,
RM10TG00maximum leakage current | Same as RM17TG00 ¦ IEC62314,Only for solid state output,
RM10TG00thermal current | Same as RM17TG00 ¦ IEC60947-5-1
RM10TG00short circuit protection | Same as RM17TG00 ¦ IEC60947-5-1,Relay Output by external fuse,
RM10TG00short circuit protection | Same as RM17TG00 ¦ IEC62314,Solid State Output by external fuse,
RM10TG00
RM10TG00time delay type | Same as RM17TG00 ¦ ,"OFF" delay,
RM10TG00time delay type | Same as RM17TG00 ¦ ,"ON" delay,
RM10TG00time delay type | Same as RM17TG00 ¦ ,Inhibition,
RM10TG00time delay range | Same as RM17TG00 ¦ ,"OFF" delay,
RM10TG00time delay range | Same as RM17TG00 ¦ ,"ON" delay,
RM10TG00time delay range | Same as RM17TG00 ¦ ,Inhibition,
RM10TG00response time | Same as RM17TG00 ¦ ,on crossing the threshold,
RM10TG00response time | Same as RM17TG00
RM10TG00response time | Same as RM17TG00
RM10TG00response time | Same as RM17TG00
RM10TG00response time | Same as RM17TG00
RM10TG00power on delay | Same as RM17TG00
RM10TG00reset time | Same as RM17TG00 ¦ ,through Un power reset,
RM10TG00reset time | Same as RM17TG00 ¦ ,through front panel reset,
RM10TG00reset time | Same as RM17TG00 ¦ ,through input control reset,
RM10TG00setting accuracy of time delay | Same as RM17TG00
RM10TG00repeat accuracy of time delay | Same as RM17TG00
RM10TG00time delay drift | Same as RM17TG00
RM10TG00time delay drift | Same as RM17TG00
RM10TG00
RM10TG00status LED | Same as RM17TG00
RM10TG00local signalling | Same as RM17TG00 ¦ ,Power supply availability,
RM10TG00local signalling | Same as RM17TG00 ¦ ,Power supply not availability,
RM10TG00local signalling | Same as RM17TG00 ¦ ,Timing in-progress,
RM10TG00local signalling | Same as RM17TG00 ¦ ,Output is energized,
RM10TG00local signalling | Same as RM17TG00 ¦ ,Output is de-energized,
RM10TG00local signalling | Same as RM17TG00 ¦ ,Range Setting Changes,
RM10TG00local signalling | Same as RM17TG00 ¦ ,Phase Cut,
RM10TG00local signalling | Same as RM17TG00 ¦ ,Phase Sequence Swap,
RM10TG00local signalling | Same as RM17TG00 ¦ ,Undervoltage <U,
RM10TG00local signalling | Same as RM17TG00 ¦ ,Overvoltage >U,
RM10TG00local signalling | Same as RM17TG00 ¦ ,Phase Asymmetry,
RM10TG00local signalling | Same as RM17TG00 ¦ ,Voltage Regeneration,
RM10TG00local signalling | Same as RM17TG00 ¦ ,Extreme Undervoltage <U (Phase loss),
RM10TG00local signalling | Same as RM17TG00 ¦ ,Extreme Overvoltage >U,
RM10TG00local signalling | Same as RM17TG00 ¦ ,Extreme Phase Asymmetry,
RM10TG00
RM10TG00 | Same as RM17TG00
RM10TG00 | Same as RM17TG00
RM10TG00diagnostic button | Same as RM17TG00
RM10TG00 | Same as RM17TG00
RM10TG00 | Same as RM17TG00
RM10TG00
RM10TG00safety reliability data | Same as RM17TG00 ¦ ,MTTF,
RM10TG00safety reliability data | Same as RM17TG00 ¦ ,B10,
RM10TG00 | Same as RM17TG00 ¦ ,MTTFd,
RM10TG00 | Same as RM17TG00 ¦ ,B10d,
RM10TG00
RM10TG00 | Drawing / Diagram
84873029
84873029standards | Same as RM17TG00
84873029product certifications | UL, CSA, CCC, CE, China ROHS
84873029marking | UL, CSA, CCC, CE, China ROHS
84873029directives | Same as RM17TG00
84873029directives | Same as RM17TG00
84873029directives | Same as RM17TG00
84873029
84873029 | Same as RM17TG00 ¦ IEC60721-3-3,Climatic category,
84873029 | Same as RM17TG00 ¦ Germanisher Lloyd,Environmental category,
84873029ambient air temperature for storage | Same as RM17TG00 ¦ ,Storage,
84873029ambient air temperature for operation | Same as RM17TG00 ¦ ,Operation,
84873029relative humidity | Same as RM17TG00 ¦ IEC60068-2-30,Damp heat,XX
84873029 | Same as RM17TG00 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873029vibration resistance | Same as RM17TG00 ¦ IEC60068-2-6
84873029shock resistance | Same as RM17TG00 ¦ IEC60068-2-27
84873029bump resistance | Same as RM17TG00 ¦ IEC60068-2-29
84873029seismic resistance | Same as RM17TG00 ¦ IEC60068-3-3
84873029IP degree of protection | Same as RM17TG00 ¦ IEC60529,Terminal Block,
84873029IP degree of protection | Same as RM17TG00 ¦ IEC60529,Housing,
84873029IP degree of protection | Same as RM17TG00 ¦ IEC60529,Front Panel,
84873029
84873029width | Same as RM17TG00 ¦ ,Width,
84873029height | Same as RM17TG00 ¦ ,Height,
84873029depth | Same as RM17TG00 ¦ ,Depth,
84873029net weight | Same as RM17TG00
84873029mounting support | Same as RM17TG00 ¦ IEC/EN 60715,Without socket,
84873029mounting support | Same as RM17TG00 ¦ IEC/EN 60715,With socket,
84873029mounting position | Same as RM17TG00 ¦ ,In relation to normal vertical mounting plane,
84873029Minimum distance to adjacent devices | Same as RM17TG00 ¦ ,Horizontal,
84873029Minimum distance to adjacent devices | Same as RM17TG00 ¦ ,Vertical,
84873029connections - terminals | Same as RM17TG00 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873029connections - terminals | Same as RM17TG00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873029connections - terminals | Same as RM17TG00 ¦ IEC60947-1,Solid cable (spring terminal),
84873029connections - terminals | Same as RM17TG00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873029tightening torque | Same as RM17TG00 ¦ IEC60947-1,Tightening torque,
84873029cable stripping length | Same as RM17TG00 ¦ ,Cable stripping length,
84873029duty time | Same as RM17TG00
84873029
84873029electromagnetic compatibility | Same as RM17TG00 ¦ ,Generic immunity standard,
84873029electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-2,Electrostatic discharge,
84873029electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873029electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-4,Fast transient / burst,
84873029electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-5,Surge,
84873029electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-6,Conducted RF disturbance,
84873029electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-8,Power frequency magnetic field,
84873029electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873029electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873029electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-29,DC voltage interruption,
84873029electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-13,Low frequency harmonics,
84873029electromagnetic compatibility | Same as RM17TG00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873029electromagnetic compatibility | Same as RM17TG00 ¦ ,Generic emission standard,
84873029electromagnetic compatibility | Same as RM17TG00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873029electromagnetic compatibility | Same as RM17TG00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873029electromagnetic compatibility | Same as RM17TG00 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873029electromagnetic compatibility | Same as RM17TG00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873029electromagnetic compatibility | Same as RM17TG00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873029electromagnetic compatibility | Same as RM17TG00 ¦ Germanisher Lloyd,Conducted emission,
84873029
84873029pollution degree | Same as RM17TG00 ¦ IEC60664-1
84873029overvoltage category | Same as RM17TG00 ¦ IEC60664-1
84873029circuit group | Same as RM17TG00 ¦ ,Supply,Terminal
84873029circuit group | Same as RM17TG00 ¦ ,Input 1,
84873029circuit group | Same as RM17TG00 ¦ ,Input 2,
84873029circuit group | Same as RM17TG00 ¦ ,Input 3,
84873029circuit group | Same as RM17TG00 ¦ ,Output 1,
84873029circuit group | Same as RM17TG00 ¦ ,Output 2,
84873029 | Same as RM17TG00 ¦ ,Supply,Rated
84873029 | Same as RM17TG00 ¦ ,Input 1,Voltage
84873029 | Same as RM17TG00 ¦ ,Input 2,Spec
84873029 | Same as RM17TG00 ¦ ,Input 3,
84873029 | Same as RM17TG00 ¦ ,Output 1,
84873029 | Same as RM17TG00 ¦ ,Output 2,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Output 1,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Output 2,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Output 1,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Output 2,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Output 1 / Output 2,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 1,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 2,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 1,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 2,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 1,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 2,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 2,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Input 3,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 3,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Output 1,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Output 2,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Output 1,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Output 2,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Output 1 / Output 2,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 1,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 2,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 1,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 2,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 1,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 2,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 2,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Input 3,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 3,
84873029dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 1,
84873029dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 2,
84873029dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 3,
84873029dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Output 1,
84873029dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Output 2,
84873029dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Output 1 / Output 2,
84873029dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 1,
84873029dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 2,
84873029dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 1,
84873029dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 2,
84873029dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 1,
84873029dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 2,
84873029dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 2,
84873029dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Input 3,
84873029dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 3,
84873029insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 1,
84873029insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 2,
84873029insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 3,
84873029insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Output 1,
84873029insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Output 2,
84873029insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Output 1 / Output 2,
84873029insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 1,
84873029insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 2,
84873029insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 1,
84873029insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 2,
84873029insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 1,
84873029insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 2,
84873029insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 2,
84873029insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Input 3,
84873029insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 3,
84873029
84873029[Us] rated supply voltage | Same as RM17TG00
84873029supply voltage limits | Same as RM17TG00
84873029polarity | Same as RM17TG00
84873029supply frequency | Same as RM17TG00
84873029supply frequency | Same as RM17TG00
84873029power consumption | Same as RM17TG00
84873029immunity to microbreaks | Same as RM17TG00
84873029supply terminal | Same as RM17TG00
84873029on-load factor | Same as RM17TG00
84873029release of input voltage | Same as RM17TG00
84873029
84873029monitoring functions | Same as RM17TG00 ¦ ,Phase lost ,
84873029monitoring functions | Same as RM17TG00 ¦ ,Phase sequence,
84873029monitoring functions | Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode),
84873029monitoring functions | Same as RM17TG00 ¦ ,Over voltage,
84873029monitoring functions | Same as RM17TG00 ¦ ,Undervoltage ,
84873029monitoring functions | Same as RM17TG00 ¦ ,Phase asymmetry,
84873029monitoring functions | Same as RM17TG00 ¦ ,Disconnection of neutral,
84873029monitoring functions | Same as RM17TG00 ¦ ,Voltage Regeneration,
84873029monitoring functions | Same as RM17TG00 ¦ ,Extreme undervoltage,
84873029monitoring functions | Same as RM17TG00 ¦ ,Extreme overvoltage,
84873029monitoring functions | Same as RM17TG00 ¦ ,Extreme asymmetry,
84873029 | Same as RM17TG00 ¦ ,Measurement mode,
84873029internal input resistance | Same as RM17TG00 ¦ ,Internal input resistance,
84873029input terminal | Same as RM17TG00 ¦ ,Input terminal,
84873029Input nominal voltage selection | Same as RM17TG00 ¦ ,Input nominal voltage selection,
84873029permissible input overload | Same as RM17TG00 ¦ ,permissible input overload,
84873029input frequency | Same as RM17TG00 ¦ ,Rated frequency,
84873029input frequency | Same as RM17TG00 ¦ ,Frequency operating range,
84873029setting accuracy of the switching threshold | Same as RM17TG00 ¦ ,Setting accuracy,
84873029repeat accuracy of the switching threshold | Same as RM17TG00 ¦ ,Repeat accuracy (constant parameters),
84873029measurement method | Same as RM17TG00 ¦ ,Measurement method,
84873029switching threshold drift | Same as RM17TG00 ¦ ,Measurement error with supply voltage variation,
84873029switching threshold drift | Same as RM17TG00 ¦ ,Measurement error with temperature variation,
84873029maximum measuring cycle | Same as RM17TG00 ¦ ,Maximum measuring cycles,
84873029measurement range | Same as RM17TG00 ¦ ,Phase lost ,
84873029measurement range | Same as RM17TG00 ¦ ,Phase sequence,
84873029measurement range | Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode),
84873029measurement range | Same as RM17TG00 ¦ ,Over voltage,
84873029measurement range | Same as RM17TG00 ¦ ,Undervoltage ,
84873029measurement range | Same as RM17TG00 ¦ ,Phase asymmetry,
84873029measurement range | Same as RM17TG00 ¦ ,Disconnection of neutral,
84873029measurement range | Same as RM17TG00 ¦ ,Voltage Regeneration,
84873029measurement range | Same as RM17TG00 ¦ ,Extreme undervoltage,
84873029measurement range | Same as RM17TG00 ¦ ,Extreme Overvoltage,
84873029measurement range | Same as RM17TG00 ¦ ,Extreme Asymmetry,
84873029tripping threshold | Same as RM17TG00 ¦ ,Phase cut,
84873029tripping threshold | Same as RM17TG00 ¦ ,Phase sequence,
84873029tripping threshold | Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode),
84873029tripping threshold | Same as RM17TG00 ¦ ,Over voltage,
84873029tripping threshold | Same as RM17TG00 ¦ ,Undervoltage ,
84873029tripping threshold | Same as RM17TG00 ¦ ,Phase asymmetry,
84873029tripping threshold | Same as RM17TG00 ¦ ,Disconnection of neutral,
84873029tripping threshold | Same as RM17TG00 ¦ ,Voltage Regeneration,
84873029tripping threshold | Same as RM17TG00 ¦ ,Extreme undervoltage (Phase loss),
84873029tripping threshold | Same as RM17TG00 ¦ ,Extreme Overvoltage,
84873029tripping threshold | Same as RM17TG00 ¦ ,Extreme Asymmetry,
84873029hysteresis | Same as RM17TG00 ¦ ,Phase cut,
84873029hysteresis | Same as RM17TG00 ¦ ,Phase sequence,
84873029hysteresis | Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode),
84873029hysteresis | Same as RM17TG00 ¦ ,Over voltage,
84873029hysteresis | Same as RM17TG00 ¦ ,Undervoltage ,
84873029hysteresis | Same as RM17TG00 ¦ ,Phase asymmetry,
84873029hysteresis | Same as RM17TG00 ¦ ,Disconnection of neutral,
84873029hysteresis | Same as RM17TG00 ¦ ,Voltage Regeneration,
84873029hysteresis | Same as RM17TG00 ¦ ,Extreme undervoltage (Phase loss),
84873029hysteresis | Same as RM17TG00 ¦ ,Extreme Overvoltage,
84873029hysteresis | Same as RM17TG00 ¦ ,Extreme Asymmetry,
84873029
84873029output type | Same as RM17TG00
84873029output terminal | Same as RM17TG00
84873029output logic | Same as RM17TG00 ¦ ,R1 (11-12-14),
84873029output logic | Same as RM17TG00 ¦ ,R2 (21-22-24),
84873029contacts material | Same as RM17TG00
84873029mechanical durability | Same as RM17TG00 ¦ IEC61810-1
84873029electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
84873029electrical durability | Same as RM17TG00 ¦ IEC60947-4-1,DC-1,
84873029electrical durability | Same as RM17TG00 ¦ IEC60947-5-1,AC-15,
84873029electrical durability | Same as RM17TG00 ¦ IEC60947-5-1,DC-13,
84873029[Ue] rated operational voltage | Same as RM17TG00 ¦ IEC61810-1,Rated switching voltage,
84873029[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
84873029maximum switching capacity | Same as RM17TG00 ¦ ,Maximum switching voltage,
84873029maximum switching capacity | 8A ¦ ,Maximum switching current,
84873029maximum switching capacity | Same as RM17TG00 ¦ ,Maximum switching capacity,
84873029minimum switching capacity | Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching voltage,
84873029minimum switching capacity | Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching current,
84873029minimum switching capacity | Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching capacity,
84873029maximum voltage drop | Same as RM17TG00 ¦ IEC62314,Only for solid state output,
84873029maximum leakage current | Same as RM17TG00 ¦ IEC62314,Only for solid state output,
84873029thermal current | 8A ¦ IEC60947-5-1
84873029short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
84873029short circuit protection | Same as RM17TG00 ¦ IEC62314,Solid State Output by external fuse,
84873029
84873029time delay type | Same as RM17TG00 ¦ ,"OFF" delay,
84873029time delay type | Same as RM17TG00 ¦ ,"ON" delay,
84873029time delay type | Same as RM17TG00 ¦ ,Inhibition,
84873029time delay range | Same as RM17TG00 ¦ ,"OFF" delay,
84873029time delay range | Same as RM17TG00 ¦ ,"ON" delay,
84873029time delay range | Same as RM17TG00 ¦ ,Inhibition,
84873029response time | Same as RM17TG00 ¦ ,on crossing the threshold,
84873029response time | Same as RM17TG00
84873029response time | Same as RM17TG00
84873029response time | Same as RM17TG00
84873029response time | Same as RM17TG00
84873029power on delay | Same as RM17TG00
84873029reset time | Same as RM17TG00 ¦ ,through Un power reset,
84873029reset time | Same as RM17TG00 ¦ ,through front panel reset,
84873029reset time | Same as RM17TG00 ¦ ,through input control reset,
84873029setting accuracy of time delay | Same as RM17TG00
84873029repeat accuracy of time delay | Same as RM17TG00
84873029time delay drift | Same as RM17TG00
84873029time delay drift | Same as RM17TG00
84873029
84873029status LED | Same as RM17TG00
84873029local signalling | Same as RM17TG00 ¦ ,Power supply availability,
84873029local signalling | Same as RM17TG00 ¦ ,Power supply not availability,
84873029local signalling | Same as RM17TG00 ¦ ,Timing in-progress,
84873029local signalling | Same as RM17TG00 ¦ ,Output is energized,
84873029local signalling | Same as RM17TG00 ¦ ,Output is de-energized,
84873029local signalling | Same as RM17TG00 ¦ ,Range Setting Changes,
84873029local signalling | Same as RM17TG00 ¦ ,Phase Cut,
84873029local signalling | Same as RM17TG00 ¦ ,Phase Sequence Swap,
84873029local signalling | Same as RM17TG00 ¦ ,Undervoltage <U,
84873029local signalling | Same as RM17TG00 ¦ ,Overvoltage >U,
84873029local signalling | Same as RM17TG00 ¦ ,Phase Asymmetry,
84873029local signalling | Same as RM17TG00 ¦ ,Voltage Regeneration,
84873029local signalling | Same as RM17TG00 ¦ ,Extreme Undervoltage <U (Phase loss),
84873029local signalling | Same as RM17TG00 ¦ ,Extreme Overvoltage >U,
84873029local signalling | Same as RM17TG00 ¦ ,Extreme Phase Asymmetry,
84873029
84873029 | Same as RM17TG00
84873029 | Same as RM17TG00
84873029diagnostic button | Same as RM17TG00
84873029 | Same as RM17TG00
84873029 | Same as RM17TG00
84873029
84873029safety reliability data | Same as RM17TG00 ¦ ,MTTF,
84873029safety reliability data | Same as RM17TG00 ¦ ,B10,
84873029 | Same as RM17TG00 ¦ ,MTTFd,
84873029 | Same as RM17TG00 ¦ ,B10d,
84873029
84873029 | Drawing / Diagram
84873890
84873890standards | Same as RM17TG00
84873890product certifications | UL, CSA, CE, China ROHS
84873890marking | UL, CSA, CE, China ROHS
84873890directives | Same as RM17TG00
84873890directives | Same as RM17TG00
84873890directives | Same as RM17TG00
84873890
84873890 | Same as RM17TG00 ¦ IEC60721-3-3,Climatic category,
84873890 | Same as RM17TG00 ¦ Germanisher Lloyd,Environmental category,
84873890ambient air temperature for storage | Same as RM17TG00 ¦ ,Storage,
84873890ambient air temperature for operation | Same as RM17TG00 ¦ ,Operation,
84873890relative humidity | Same as RM17TG00 ¦ IEC60068-2-30,Damp heat,XX
84873890 | Same as RM17TG00 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873890vibration resistance | Same as RM17TG00 ¦ IEC60068-2-6
84873890shock resistance | Same as RM17TG00 ¦ IEC60068-2-27
84873890bump resistance | Same as RM17TG00 ¦ IEC60068-2-29
84873890seismic resistance | Same as RM17TG00 ¦ IEC60068-3-3
84873890IP degree of protection | Same as RM17TG00 ¦ IEC60529,Terminal Block,
84873890IP degree of protection | Same as RM17TG00 ¦ IEC60529,Housing,
84873890IP degree of protection | Same as RM17TG00 ¦ IEC60529,Front Panel,
84873890
84873890width | Same as RM17TG00 ¦ ,Width,
84873890height | Same as RM17TG00 ¦ ,Height,
84873890depth | Same as RM17TG00 ¦ ,Depth,
84873890net weight | Same as RM17TG00
84873890mounting support | Same as RM17TG00 ¦ IEC/EN 60715,Without socket,
84873890mounting support | Same as RM17TG00 ¦ IEC/EN 60715,With socket,
84873890mounting position | Same as RM17TG00 ¦ ,In relation to normal vertical mounting plane,
84873890Minimum distance to adjacent devices | Same as RM17TG00 ¦ ,Horizontal,
84873890Minimum distance to adjacent devices | Same as RM17TG00 ¦ ,Vertical,
84873890connections - terminals | Same as RM17TG00 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873890connections - terminals | Same as RM17TG00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873890connections - terminals | Same as RM17TG00 ¦ IEC60947-1,Solid cable (spring terminal),
84873890connections - terminals | Same as RM17TG00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873890tightening torque | Same as RM17TG00 ¦ IEC60947-1,Tightening torque,
84873890cable stripping length | Same as RM17TG00 ¦ ,Cable stripping length,
84873890duty time | Same as RM17TG00
84873890
84873890electromagnetic compatibility | Same as RM17TG00 ¦ ,Generic immunity standard,
84873890electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-2,Electrostatic discharge,
84873890electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873890electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-4,Fast transient / burst,
84873890electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-5,Surge,
84873890electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-6,Conducted RF disturbance,
84873890electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-8,Power frequency magnetic field,
84873890electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873890electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873890electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-29,DC voltage interruption,
84873890electromagnetic compatibility | Same as RM17TG00 ¦ IEC61000-4-13,Low frequency harmonics,
84873890electromagnetic compatibility | Same as RM17TG00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873890electromagnetic compatibility | Same as RM17TG00 ¦ ,Generic emission standard,
84873890electromagnetic compatibility | Same as RM17TG00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873890electromagnetic compatibility | Same as RM17TG00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873890electromagnetic compatibility | Same as RM17TG00 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873890electromagnetic compatibility | Same as RM17TG00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873890electromagnetic compatibility | Same as RM17TG00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873890electromagnetic compatibility | Same as RM17TG00 ¦ Germanisher Lloyd,Conducted emission,
84873890
84873890pollution degree | Same as RM17TG00 ¦ IEC60664-1
84873890overvoltage category | Same as RM17TG00 ¦ IEC60664-1
84873890circuit group | Same as RM17TG00 ¦ ,Supply,Terminal
84873890circuit group | Same as RM17TG00 ¦ ,Input 1,
84873890circuit group | Same as RM17TG00 ¦ ,Input 2,
84873890circuit group | Same as RM17TG00 ¦ ,Input 3,
84873890circuit group | Same as RM17TG00 ¦ ,Output 1,
84873890circuit group | Same as RM17TG00 ¦ ,Output 2,
84873890 | Same as RM17TG00 ¦ ,Supply,Rated
84873890 | Same as RM17TG00 ¦ ,Input 1,Voltage
84873890 | Same as RM17TG00 ¦ ,Input 2,Spec
84873890 | Same as RM17TG00 ¦ ,Input 3,
84873890 | Same as RM17TG00 ¦ ,Output 1,
84873890 | Same as RM17TG00 ¦ ,Output 2,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Output 1,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Output 2,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Output 1,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Output 2,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Output 1 / Output 2,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 1,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 2,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 1,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 2,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 1,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 2,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 2,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Input 3,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 3,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Output 1,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Output 2,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Output 1,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply / Output 2,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Output 1 / Output 2,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 1,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 2,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 1,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 2,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 1,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 2,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 2,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 2 / Input 3,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 3,
84873890dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 1,
84873890dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 2,
84873890dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 3,
84873890dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Output 1,
84873890dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Output 2,
84873890dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Output 1 / Output 2,
84873890dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 1,
84873890dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 2,
84873890dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 1,
84873890dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 2,
84873890dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 1,
84873890dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 2,
84873890dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 2,
84873890dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Input 3,
84873890dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 3,
84873890insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 1,
84873890insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 2,
84873890insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 3,
84873890insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Output 1,
84873890insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Output 2,
84873890insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Output 1 / Output 2,
84873890insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 1,
84873890insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 2,
84873890insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 1,
84873890insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 2,
84873890insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 1,
84873890insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 2,
84873890insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 2,
84873890insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 2 / Input 3,
84873890insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 3,
84873890
84873890[Us] rated supply voltage | Same as RM17TG00
84873890supply voltage limits | Same as RM17TG00
84873890polarity | Same as RM17TG00
84873890supply frequency | Same as RM17TG00
84873890supply frequency | Same as RM17TG00
84873890power consumption | Same as RM17TG00
84873890immunity to microbreaks | Same as RM17TG00
84873890supply terminal | Same as RM17TG00
84873890on-load factor | Same as RM17TG00
84873890release of input voltage | Same as RM17TG00
84873890
84873890monitoring functions | Same as RM17TG00 ¦ ,Phase lost ,
84873890monitoring functions | Same as RM17TG00 ¦ ,Phase sequence,
84873890monitoring functions | Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode),
84873890monitoring functions | Same as RM17TG00 ¦ ,Over voltage,
84873890monitoring functions | Same as RM17TG00 ¦ ,Undervoltage ,
84873890monitoring functions | Same as RM17TG00 ¦ ,Phase asymmetry,
84873890monitoring functions | Same as RM17TG00 ¦ ,Disconnection of neutral,
84873890monitoring functions | Same as RM17TG00 ¦ ,Voltage Regeneration,
84873890monitoring functions | Same as RM17TG00 ¦ ,Extreme undervoltage,
84873890monitoring functions | Same as RM17TG00 ¦ ,Extreme overvoltage,
84873890monitoring functions | Same as RM17TG00 ¦ ,Extreme asymmetry,
84873890 | Same as RM17TG00 ¦ ,Measurement mode,
84873890internal input resistance | Same as RM17TG00 ¦ ,Internal input resistance,
84873890input terminal | Same as RM17TG00 ¦ ,Input terminal,
84873890Input nominal voltage selection | Same as RM17TG00 ¦ ,Input nominal voltage selection,
84873890permissible input overload | Same as RM17TG00 ¦ ,permissible input overload,
84873890input frequency | Same as RM17TG00 ¦ ,Rated frequency,
84873890input frequency | Same as RM17TG00 ¦ ,Frequency operating range,
84873890setting accuracy of the switching threshold | Same as RM17TG00 ¦ ,Setting accuracy,
84873890repeat accuracy of the switching threshold | Same as RM17TG00 ¦ ,Repeat accuracy (constant parameters),
84873890measurement method | Same as RM17TG00 ¦ ,Measurement method,
84873890switching threshold drift | Same as RM17TG00 ¦ ,Measurement error with supply voltage variation,
84873890switching threshold drift | Same as RM17TG00 ¦ ,Measurement error with temperature variation,
84873890maximum measuring cycle | Same as RM17TG00 ¦ ,Maximum measuring cycles,
84873890measurement range | Same as RM17TG00 ¦ ,Phase lost ,
84873890measurement range | Same as RM17TG00 ¦ ,Phase sequence,
84873890measurement range | Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode),
84873890measurement range | Same as RM17TG00 ¦ ,Over voltage,
84873890measurement range | Same as RM17TG00 ¦ ,Undervoltage ,
84873890measurement range | Same as RM17TG00 ¦ ,Phase asymmetry,
84873890measurement range | Same as RM17TG00 ¦ ,Disconnection of neutral,
84873890measurement range | Same as RM17TG00 ¦ ,Voltage Regeneration,
84873890measurement range | Same as RM17TG00 ¦ ,Extreme undervoltage,
84873890measurement range | Same as RM17TG00 ¦ ,Extreme Overvoltage,
84873890measurement range | Same as RM17TG00 ¦ ,Extreme Asymmetry,
84873890tripping threshold | Same as RM17TG00 ¦ ,Phase cut,
84873890tripping threshold | Same as RM17TG00 ¦ ,Phase sequence,
84873890tripping threshold | Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode),
84873890tripping threshold | Same as RM17TG00 ¦ ,Over voltage,
84873890tripping threshold | Same as RM17TG00 ¦ ,Undervoltage ,
84873890tripping threshold | Same as RM17TG00 ¦ ,Phase asymmetry,
84873890tripping threshold | Same as RM17TG00 ¦ ,Disconnection of neutral,
84873890tripping threshold | Same as RM17TG00 ¦ ,Voltage Regeneration,
84873890tripping threshold | Same as RM17TG00 ¦ ,Extreme undervoltage (Phase loss),
84873890tripping threshold | Same as RM17TG00 ¦ ,Extreme Overvoltage,
84873890tripping threshold | Same as RM17TG00 ¦ ,Extreme Asymmetry,
84873890hysteresis | Same as RM17TG00 ¦ ,Phase cut,
84873890hysteresis | Same as RM17TG00 ¦ ,Phase sequence,
84873890hysteresis | Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode),
84873890hysteresis | Same as RM17TG00 ¦ ,Over voltage,
84873890hysteresis | Same as RM17TG00 ¦ ,Undervoltage ,
84873890hysteresis | Same as RM17TG00 ¦ ,Phase asymmetry,
84873890hysteresis | Same as RM17TG00 ¦ ,Disconnection of neutral,
84873890hysteresis | Same as RM17TG00 ¦ ,Voltage Regeneration,
84873890hysteresis | Same as RM17TG00 ¦ ,Extreme undervoltage (Phase loss),
84873890hysteresis | Same as RM17TG00 ¦ ,Extreme Overvoltage,
84873890hysteresis | Same as RM17TG00 ¦ ,Extreme Asymmetry,
84873890
84873890output type | Same as RM17TG00
84873890output terminal | Same as RM17TG00
84873890output logic | Same as RM17TG00 ¦ ,R1 (11-12-14),
84873890output logic | Same as RM17TG00 ¦ ,R2 (21-22-24),
84873890contacts material | Same as RM17TG00
84873890mechanical durability | Same as RM17TG00 ¦ IEC61810-1
84873890electrical durability | Same as RM17TG00 ¦ IEC60947-4-1,AC-1,
84873890electrical durability | Same as RM17TG00 ¦ IEC60947-4-1,DC-1,
84873890electrical durability | Same as RM17TG00 ¦ IEC60947-5-1,AC-15,
84873890electrical durability | Same as RM17TG00 ¦ IEC60947-5-1,DC-13,
84873890[Ue] rated operational voltage | Same as RM17TG00 ¦ IEC61810-1,Rated switching voltage,
84873890[Ie] rated operational current | Same as RM17TG00 ¦ IEC61810-1,Rated switching current,
84873890maximum switching capacity | Same as RM17TG00 ¦ ,Maximum switching voltage,
84873890maximum switching capacity | Same as RM17TG00 ¦ ,Maximum switching current,
84873890maximum switching capacity | Same as RM17TG00 ¦ ,Maximum switching capacity,
84873890minimum switching capacity | Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching voltage,
84873890minimum switching capacity | Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching current,
84873890minimum switching capacity | Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching capacity,
84873890maximum voltage drop | Same as RM17TG00 ¦ IEC62314,Only for solid state output,
84873890maximum leakage current | Same as RM17TG00 ¦ IEC62314,Only for solid state output,
84873890thermal current | Same as RM17TG00 ¦ IEC60947-5-1
84873890short circuit protection | Same as RM17TG00 ¦ IEC60947-5-1,Relay Output by external fuse,
84873890short circuit protection | Same as RM17TG00 ¦ IEC62314,Solid State Output by external fuse,
84873890
84873890time delay type | Same as RM17TG00 ¦ ,"OFF" delay,
84873890time delay type | Same as RM17TG00 ¦ ,"ON" delay,
84873890time delay type | Same as RM17TG00 ¦ ,Inhibition,
84873890time delay range | Same as RM17TG00 ¦ ,"OFF" delay,
84873890time delay range | Same as RM17TG00 ¦ ,"ON" delay,
84873890time delay range | Same as RM17TG00 ¦ ,Inhibition,
84873890response time | Same as RM17TG00 ¦ ,on crossing the threshold,
84873890response time | Same as RM17TG00
84873890response time | Same as RM17TG00
84873890response time | Same as RM17TG00
84873890response time | Same as RM17TG00
84873890power on delay | Same as RM17TG00
84873890reset time | Same as RM17TG00 ¦ ,through Un power reset,
84873890reset time | Same as RM17TG00 ¦ ,through front panel reset,
84873890reset time | Same as RM17TG00 ¦ ,through input control reset,
84873890setting accuracy of time delay | Same as RM17TG00
84873890repeat accuracy of time delay | Same as RM17TG00
84873890time delay drift | Same as RM17TG00
84873890time delay drift | Same as RM17TG00
84873890
84873890status LED | Same as RM17TG00
84873890local signalling | Same as RM17TG00 ¦ ,Power supply availability,
84873890local signalling | Same as RM17TG00 ¦ ,Power supply not availability,
84873890local signalling | Same as RM17TG00 ¦ ,Timing in-progress,
84873890local signalling | Same as RM17TG00 ¦ ,Output is energized,
84873890local signalling | Same as RM17TG00 ¦ ,Output is de-energized,
84873890local signalling | Same as RM17TG00 ¦ ,Range Setting Changes,
84873890local signalling | Same as RM17TG00 ¦ ,Phase Cut,
84873890local signalling | Same as RM17TG00 ¦ ,Phase Sequence Swap,
84873890local signalling | Same as RM17TG00 ¦ ,Undervoltage <U,
84873890local signalling | Same as RM17TG00 ¦ ,Overvoltage >U,
84873890local signalling | Same as RM17TG00 ¦ ,Phase Asymmetry,
84873890local signalling | Same as RM17TG00 ¦ ,Voltage Regeneration,
84873890local signalling | Same as RM17TG00 ¦ ,Extreme Undervoltage <U (Phase loss),
84873890local signalling | Same as RM17TG00 ¦ ,Extreme Overvoltage >U,
84873890local signalling | Same as RM17TG00 ¦ ,Extreme Phase Asymmetry,
84873890
84873890 | Same as RM17TG00
84873890 | Same as RM17TG00
84873890diagnostic button | Same as RM17TG00
84873890 | Same as RM17TG00
84873890 | Same as RM17TG00
84873890
84873890safety reliability data | Same as RM17TG00 ¦ ,MTTF,
84873890safety reliability data | Same as RM17TG00 ¦ ,B10,
84873890 | Same as RM17TG00 ¦ ,MTTFd,
84873890 | Same as RM17TG00 ¦ ,B10d,
84873890
84873890 | Drawing / Diagram
84873034
84873034standards | Same as RM17TG20
84873034product certifications | UL, CE, China ROHS
84873034marking | UL, CE, China ROHS
84873034directives | Same as RM17TG20
84873034directives | Same as RM17TG20
84873034directives | Same as RM17TG20
84873034
84873034 | Same as RM17TG20 ¦ IEC60721-3-3,Climatic category,
84873034 | Same as RM17TG20 ¦ Germanisher Lloyd,Environmental category,
84873034ambient air temperature for storage | -30oC..+70oC ¦ ,Storage,
84873034ambient air temperature for operation | Same as RM17TG20 ¦ ,Operation,
84873034relative humidity | Same as RM17TG20 ¦ IEC60068-2-30,Damp heat,XX
84873034 | - ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873034vibration resistance | Same as RM17TG20 ¦ IEC60068-2-6
84873034shock resistance | Same as RM17TG20 ¦ IEC60068-2-27
84873034bump resistance | Same as RM17TG20 ¦ IEC60068-2-29
84873034seismic resistance | Same as RM17TG20 ¦ IEC60068-3-3
84873034IP degree of protection | Same as RM17TG20 ¦ IEC60529,Terminal Block,
84873034IP degree of protection | Same as RM17TG20 ¦ IEC60529,Housing,
84873034IP degree of protection | Same as RM17TG20 ¦ IEC60529,Front Panel,
84873034
84873034width | 22.5 ¦ ,Width,
84873034height | 90 ¦ ,Height,
84873034depth | 73 ¦ ,Depth,
84873034net weight | Same as RM17TG20
84873034mounting support | Same as RM17TG20 ¦ IEC/EN 60715,Without socket,
84873034mounting support | Same as RM17TG20 ¦ IEC/EN 60715,With socket,
84873034mounting position | Same as RM17TG20 ¦ ,In relation to normal vertical mounting plane,
84873034Minimum distance to adjacent devices | Same as RM17TG20 ¦ ,Horizontal,
84873034Minimum distance to adjacent devices | Same as RM17TG20 ¦ ,Vertical,
84873034connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873034connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873034connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Solid cable (spring terminal),
84873034connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Flexible cable (spring terminal),
84873034tightening torque | Same as RM17TG20 ¦ IEC60947-1,Tightening torque,
84873034cable stripping length | Same as RM17TG20 ¦ ,Cable stripping length,
84873034duty time | Same as RM17TG20
84873034
84873034electromagnetic compatibility | Same as RM17TG20 ¦ ,Generic immunity standard,
84873034electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-2,Electrostatic discharge,
84873034electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873034electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-4,Fast transient / burst,
84873034electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-5,Surge,
84873034electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-6,Conducted RF disturbance,
84873034electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-8,Power frequency magnetic field,
84873034electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873034electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873034electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-29,DC voltage interruption,
84873034electromagnetic compatibility | Same as RM17TG20 ¦ IEC61000-4-13,Low frequency harmonics,
84873034electromagnetic compatibility | Same as RM17TG20 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873034electromagnetic compatibility | Same as RM17TG20 ¦ ,Generic emission standard,
84873034electromagnetic compatibility | Same as RM17TG20 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873034electromagnetic compatibility | Same as RM17TG20 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873034electromagnetic compatibility | Same as RM17TG20 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873034electromagnetic compatibility | Same as RM17TG20 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873034electromagnetic compatibility | Same as RM17TG20 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873034electromagnetic compatibility | Same as RM17TG20 ¦ Germanisher Lloyd,Conducted emission,
84873034
84873034pollution degree | Same as RM17TG20 ¦ IEC60664-1
84873034overvoltage category | Same as RM17TG20 ¦ IEC60664-1
84873034circuit group | Same as RM17TG20 ¦ ,Supply,Terminal
84873034circuit group | Same as RM17TG20 ¦ ,Input 1,
84873034circuit group | Same as RM17TG20 ¦ ,Input 2,
84873034circuit group | Same as RM17TG20 ¦ ,Input 3,
84873034circuit group | Same as RM17TG20 ¦ ,Output 1,
84873034circuit group | Same as RM17TG20 ¦ ,Output 2,
84873034 | Same as RM17TG20 ¦ ,Supply,Rated
84873034 | Same as RM17TG20 ¦ ,Input 1,Voltage
84873034 | Same as RM17TG20 ¦ ,Input 2,Spec
84873034 | Same as RM17TG20 ¦ ,Input 3,
84873034 | Same as RM17TG20 ¦ ,Output 1,
84873034 | Same as RM17TG20 ¦ ,Output 2,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Output 1,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Output 2,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 2,Isolated
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 3,Circuit
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Output 1,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Output 2,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Output 1 / Output 2,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 1,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 2,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 1,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 2,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 1,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 2,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 2,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Input 3,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 3,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Output 1,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Output 2,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 2,Isolated
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Input 3,Circuit
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Output 1,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply / Output 2,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Output 1 / Output 2,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 1,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 2,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 1,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 2,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 1,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 2,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 2,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 2 / Input 3,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 3,
84873034dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 1,
84873034dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 2,
84873034dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 3,
84873034dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Output 1,
84873034dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Output 2,
84873034dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Output 1 / Output 2,
84873034dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 1,
84873034dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 2,
84873034dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 1,
84873034dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 2,
84873034dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 1,
84873034dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 2,
84873034dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 2,
84873034dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Input 3,
84873034dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 3,
84873034insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 1,
84873034insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 2,
84873034insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 3,
84873034insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Output 1,
84873034insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Output 2,
84873034insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Output 1 / Output 2,
84873034insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 1,
84873034insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 2,
84873034insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 1,
84873034insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 2,
84873034insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 1,
84873034insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 2,
84873034insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 2,
84873034insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 2 / Input 3,
84873034insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 3,
84873034
84873034[Us] rated supply voltage | ~ 3 x 230…3 x 440
84873034supply voltage limits | ~ 3 x 200…3 x 460
84873034polarity | -
84873034supply frequency | Same as RM17TG20
84873034supply frequency | Same as RM17TG20
84873034power consumption | Same as RM17TG20
84873034immunity to microbreaks | Same as RM17TG20
84873034supply terminal | Same as RM17TG20
84873034on-load factor | Same as RM17TG20
84873034release of input voltage | Same as RM17TG20
84873034
84873034monitoring functions | Same as RM17TG20 ¦ ,Phase lost ,
84873034monitoring functions | Same as RM17TG20 ¦ ,Phase sequence,
84873034monitoring functions | Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode),
84873034monitoring functions | Same as RM17TG20 ¦ ,Over voltage,
84873034monitoring functions | Same as RM17TG20 ¦ ,Undervoltage ,
84873034monitoring functions | Same as RM17TG20 ¦ ,Phase asymmetry,
84873034monitoring functions | Same as RM17TG20 ¦ ,Disconnection of neutral,
84873034monitoring functions | Same as RM17TG20 ¦ ,Voltage Regeneration,
84873034monitoring functions | Same as RM17TG20 ¦ ,Extreme undervoltage,
84873034monitoring functions | Same as RM17TG20 ¦ ,Extreme overvoltage,
84873034monitoring functions | Same as RM17TG20 ¦ ,Extreme asymmetry,
84873034 | Same as RM17TG20 ¦ ,Measurement mode,
84873034internal input resistance | Same as RM17TG20 ¦ ,Internal input resistance,
84873034input terminal | Same as RM17TG20 ¦ ,Input terminal,
84873034Input nominal voltage selection | Same as RM17TG21 ¦ ,Input nominal voltage selection,
84873034permissible input overload | Same as RM17TG22 ¦ ,permissible input overload,
84873034input frequency | Same as RM17TG20 ¦ ,Rated frequency,
84873034input frequency | Same as RM17TG20 ¦ ,Frequency operating range,
84873034setting accuracy of the switching threshold | Same as RM17TG20 ¦ ,Setting accuracy,
84873034repeat accuracy of the switching threshold | Same as RM17TG20 ¦ ,Repeat accuracy (constant parameters),
84873034measurement method | Same as RM17TG20 ¦ ,Measurement method,
84873034switching threshold drift | Same as RM17TG20 ¦ ,Measurement error with supply voltage variation,
84873034switching threshold drift | Same as RM17TG20 ¦ ,Measurement error with temperature variation,
84873034maximum measuring cycle | Same as RM17TG20 ¦ ,Maximum measuring cycles,
84873034measurement range | Same as RM17TG20 ¦ ,Phase lost ,
84873034measurement range | Same as RM17TG20 ¦ ,Phase sequence,
84873034measurement range | Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode),
84873034measurement range | Same as RM17TG20 ¦ ,Over voltage,
84873034measurement range | Same as RM17TG20 ¦ ,Undervoltage ,
84873034measurement range | Same as RM17TG20 ¦ ,Phase asymmetry,
84873034measurement range | Same as RM17TG20 ¦ ,Disconnection of neutral,
84873034measurement range | Same as RM17TG20 ¦ ,Voltage Regeneration,
84873034measurement range | Same as RM17TG20 ¦ ,Extreme undervoltage,
84873034measurement range | Same as RM17TG20 ¦ ,Extreme Overvoltage,
84873034measurement range | Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873034tripping threshold | Same as RM17TG20 ¦ ,Phase cut,
84873034tripping threshold | Same as RM17TG20 ¦ ,Phase sequence,
84873034tripping threshold | Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode),
84873034tripping threshold | Same as RM17TG20 ¦ ,Over voltage,
84873034tripping threshold | Same as RM17TG20 ¦ ,Undervoltage ,
84873034tripping threshold | Same as RM17TG20 ¦ ,Phase asymmetry,
84873034tripping threshold | Same as RM17TG20 ¦ ,Disconnection of neutral,
84873034tripping threshold | Same as RM17TG20 ¦ ,Voltage Regeneration,
84873034tripping threshold | Same as RM17TG20 ¦ ,Extreme undervoltage (Phase loss),
84873034tripping threshold | Same as RM17TG20 ¦ ,Extreme Overvoltage,
84873034tripping threshold | Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873034hysteresis | Same as RM17TG20 ¦ ,Phase cut,
84873034hysteresis | Same as RM17TG20 ¦ ,Phase sequence,
84873034hysteresis | Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode),
84873034hysteresis | Same as RM17TG20 ¦ ,Over voltage,
84873034hysteresis | Same as RM17TG20 ¦ ,Undervoltage ,
84873034hysteresis | Same as RM17TG20 ¦ ,Phase asymmetry,
84873034hysteresis | Same as RM17TG20 ¦ ,Disconnection of neutral,
84873034hysteresis | Same as RM17TG20 ¦ ,Voltage Regeneration,
84873034hysteresis | Same as RM17TG20 ¦ ,Extreme undervoltage (Phase loss),
84873034hysteresis | Same as RM17TG20 ¦ ,Extreme Overvoltage,
84873034hysteresis | Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873034
84873034output type | Same as RM17TG20
84873034output terminal | Same as RM17TG20
84873034output logic | Same as RM17TG20 ¦ ,R1 (11-12-14),
84873034output logic | Same as RM17TG20 ¦ ,R2 (21-22-24),
84873034contacts material | Same as RM17TG20
84873034mechanical durability | Same as RM17TG20 ¦ IEC61810-1
84873034electrical durability | Same as RM17TG20 ¦ IEC60947-4-1,AC-1,
84873034electrical durability | Same as RM17TG20 ¦ IEC60947-4-1,DC-1,
84873034electrical durability | Same as RM17TG20 ¦ IEC60947-5-1,AC-15,
84873034electrical durability | Same as RM17TG20 ¦ IEC60947-5-1,DC-13,
84873034[Ue] rated operational voltage | Same as RM17TG20 ¦ IEC61810-1,Rated switching voltage,
84873034[Ie] rated operational current | Same as RM17TG20 ¦ IEC61810-1,Rated switching current,
84873034maximum switching capacity | Same as RM17TG20 ¦ ,Maximum switching voltage,
84873034maximum switching capacity | Same as RM17TG20 ¦ ,Maximum switching current,
84873034maximum switching capacity | Same as RM17TG20 ¦ ,Maximum switching capacity,
84873034minimum switching capacity | Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching voltage,
84873034minimum switching capacity | Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching current,
84873034minimum switching capacity | Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching capacity,
84873034maximum voltage drop | Same as RM17TG20 ¦ IEC62314,Only for solid state output,
84873034maximum leakage current | Same as RM17TG20 ¦ IEC62314,Only for solid state output,
84873034thermal current | Same as RM17TG20 ¦ IEC60947-5-1
84873034short circuit protection | Same as RM17TG20 ¦ IEC60947-5-1,Relay Output by external fuse,
84873034short circuit protection | Same as RM17TG20 ¦ IEC62314,Solid State Output by external fuse,
84873034
84873034time delay type | Same as RM17TG20 ¦ ,"OFF" delay,
84873034time delay type | Same as RM17TG20 ¦ ,"ON" delay,
84873034time delay type | Same as RM17TG20 ¦ ,Inhibition,
84873034time delay range | Same as RM17TG20 ¦ ,"OFF" delay,
84873034time delay range | Same as RM17TG20 ¦ ,"ON" delay,
84873034time delay range | Same as RM17TG20 ¦ ,Inhibition,
84873034response time | Same as RM17TG20 ¦ ,on crossing the threshold,
84873034response time | Same as RM17TG20
84873034response time | Same as RM17TG20
84873034response time | Same as RM17TG20
84873034response time | Same as RM17TG20
84873034power on delay | Same as RM17TG20
84873034reset time | Same as RM17TG20 ¦ ,through Un power reset,
84873034reset time | Same as RM17TG20 ¦ ,through front panel reset,
84873034reset time | Same as RM17TG20 ¦ ,through input control reset,
84873034setting accuracy of time delay | Same as RM17TG20
84873034repeat accuracy of time delay | Same as RM17TG20
84873034time delay drift | Same as RM17TG20
84873034time delay drift | Same as RM17TG20
84873034
84873034status LED | R (Amber)
84873034local signalling | - ¦ ,Power supply availability,
84873034local signalling | - ¦ ,Power supply not availability,
84873034local signalling | - ¦ ,Timing in-progress,
84873034local signalling | R - ON ¦ ,Output is energized,
84873034local signalling | R - OFF ¦ ,Output is de-energized,
84873034local signalling | - ¦ ,Range Setting Changes,
84873034local signalling | Same as RM17TG20 ¦ ,Phase Cut,
84873034local signalling | Same as RM17TG20 ¦ ,Phase Sequence Swap,
84873034local signalling | Same as RM17TG20 ¦ ,Undervoltage <U,
84873034local signalling | Same as RM17TG20 ¦ ,Overvoltage >U,
84873034local signalling | Same as RM17TG20 ¦ ,Phase Asymmetry,
84873034local signalling | Same as RM17TG20 ¦ ,Voltage Regeneration,
84873034local signalling | Same as RM17TG20 ¦ ,Extreme Undervoltage <U (Phase loss),
84873034local signalling | Same as RM17TG20 ¦ ,Extreme Overvoltage >U,
84873034local signalling | Same as RM17TG20 ¦ ,Extreme Phase Asymmetry,
84873034
84873034 | Same as RM17TG20
84873034 | Same as RM17TG20
84873034diagnostic button | Same as RM17TG20
84873034 | Same as RM17TG20
84873034 | Same as RM17TG20
84873034
84873034safety reliability data | Same as RM17TG20 ¦ ,MTTF,
84873034safety reliability data | Same as RM17TG20 ¦ ,B10,
84873034 | Same as RM17TG20 ¦ ,MTTFd,
84873034 | Same as RM17TG20 ¦ ,B10d,
84873034
84873034 | Drawing / Diagram
84873195
84873195standards | Same as 84873034
84873195product certifications | Same as 84873034
84873195marking | Same as 84873034
84873195directives | Same as 84873034
84873195directives | Same as 84873034
84873195directives | Same as 84873034
84873195
84873195 | Same as 84873034 ¦ IEC60721-3-3,Climatic category,
84873195 | Same as 84873034 ¦ Germanisher Lloyd,Environmental category,
84873195ambient air temperature for storage | Same as 84873034 ¦ ,Storage,
84873195ambient air temperature for operation | Same as 84873034 ¦ ,Operation,
84873195relative humidity | Same as 84873034 ¦ IEC60068-2-30,Damp heat,XX
84873195 | Same as 84873034 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873195vibration resistance | Same as 84873034 ¦ IEC60068-2-6
84873195shock resistance | Same as 84873034 ¦ IEC60068-2-27
84873195bump resistance | Same as 84873034 ¦ IEC60068-2-29
84873195seismic resistance | Same as 84873034 ¦ IEC60068-3-3
84873195IP degree of protection | Same as 84873034 ¦ IEC60529,Terminal Block,
84873195IP degree of protection | Same as 84873034 ¦ IEC60529,Housing,
84873195IP degree of protection | Same as 84873034 ¦ IEC60529,Front Panel,
84873195
84873195width | Same as 84873034 ¦ ,Width,
84873195height | Same as 84873034 ¦ ,Height,
84873195depth | Same as 84873034 ¦ ,Depth,
84873195net weight | Same as 84873034
84873195mounting support | Same as 84873034 ¦ IEC/EN 60715,Without socket,
84873195mounting support | Same as 84873034 ¦ IEC/EN 60715,With socket,
84873195mounting position | Same as 84873034 ¦ ,In relation to normal vertical mounting plane,
84873195Minimum distance to adjacent devices | Same as 84873034 ¦ ,Horizontal,
84873195Minimum distance to adjacent devices | Same as 84873034 ¦ ,Vertical,
84873195connections - terminals | Same as 84873034 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873195connections - terminals | Same as 84873034 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873195connections - terminals | Same as 84873034 ¦ IEC60947-1,Solid cable (spring terminal),
84873195connections - terminals | Same as 84873034 ¦ IEC60947-1,Flexible cable (spring terminal),
84873195tightening torque | Same as 84873034 ¦ IEC60947-1,Tightening torque,
84873195cable stripping length | Same as 84873034 ¦ ,Cable stripping length,
84873195duty time | Same as 84873034
84873195
84873195electromagnetic compatibility | Same as 84873034 ¦ ,Generic immunity standard,
84873195electromagnetic compatibility | Same as 84873034 ¦ IEC61000-4-2,Electrostatic discharge,
84873195electromagnetic compatibility | Same as 84873034 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873195electromagnetic compatibility | Same as 84873034 ¦ IEC61000-4-4,Fast transient / burst,
84873195electromagnetic compatibility | Same as 84873034 ¦ IEC61000-4-5,Surge,
84873195electromagnetic compatibility | Same as 84873034 ¦ IEC61000-4-6,Conducted RF disturbance,
84873195electromagnetic compatibility | Same as 84873034 ¦ IEC61000-4-8,Power frequency magnetic field,
84873195electromagnetic compatibility | Same as 84873034 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873195electromagnetic compatibility | Same as 84873034 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873195electromagnetic compatibility | Same as 84873034 ¦ IEC61000-4-29,DC voltage interruption,
84873195electromagnetic compatibility | Same as 84873034 ¦ IEC61000-4-13,Low frequency harmonics,
84873195electromagnetic compatibility | Same as 84873034 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873195electromagnetic compatibility | Same as 84873034 ¦ ,Generic emission standard,
84873195electromagnetic compatibility | Same as 84873034 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873195electromagnetic compatibility | Same as 84873034 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873195electromagnetic compatibility | Same as 84873034 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873195electromagnetic compatibility | Same as 84873034 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873195electromagnetic compatibility | Same as 84873034 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873195electromagnetic compatibility | Same as 84873034 ¦ Germanisher Lloyd,Conducted emission,
84873195
84873195pollution degree | Same as 84873034 ¦ IEC60664-1
84873195overvoltage category | Same as 84873034 ¦ IEC60664-1
84873195circuit group | Same as 84873034 ¦ ,Supply,Terminal
84873195circuit group | Same as 84873034 ¦ ,Input 1,
84873195circuit group | Same as 84873034 ¦ ,Input 2,
84873195circuit group | Same as 84873034 ¦ ,Input 3,
84873195circuit group | Same as 84873034 ¦ ,Output 1,
84873195circuit group | Same as 84873034 ¦ ,Output 2,
84873195 | Same as 84873034 ¦ ,Supply,Rated
84873195 | Same as 84873034 ¦ ,Input 1,Voltage
84873195 | Same as 84873034 ¦ ,Input 2,Spec
84873195 | Same as 84873034 ¦ ,Input 3,
84873195 | Same as 84873034 ¦ ,Output 1,
84873195 | Same as 84873034 ¦ ,Output 2,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Supply,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Input 1,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Input 2,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Input 3,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Output 1,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Output 2,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Supply / Input 2,Isolated
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Supply / Input 3,Circuit
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Supply / Output 1,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Supply / Output 2,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Output 1 / Output 2,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Input 1 / Output 1,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Input 1 / Output 2,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Input 2 / Output 1,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Input 2 / Output 2,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Input 3 / Output 1,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Input 3 / Output 2,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Input 1 / Input 2,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Input 2 / Input 3,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Input 1 / Input 3,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Supply,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Input 1,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Input 2,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Input 3,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Output 1,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Output 2,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Supply / Input 2,Isolated
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Supply / Input 3,Circuit
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Supply / Output 1,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Supply / Output 2,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Output 1 / Output 2,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Input 1 / Output 1,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Input 1 / Output 2,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Input 2 / Output 1,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Input 2 / Output 2,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Input 3 / Output 1,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Input 3 / Output 2,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Input 1 / Input 2,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Input 2 / Input 3,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Input 1 / Input 3,
84873195dielectric strength | Same as 84873034 ¦ IEC60255-27,Supply / Input 1,
84873195dielectric strength | Same as 84873034 ¦ IEC60255-27,Supply / Input 2,
84873195dielectric strength | Same as 84873034 ¦ IEC60255-27,Supply / Input 3,
84873195dielectric strength | Same as 84873034 ¦ IEC60255-27,Supply / Output 1,
84873195dielectric strength | Same as 84873034 ¦ IEC60255-27,Supply / Output 2,
84873195dielectric strength | Same as 84873034 ¦ IEC60255-27,Output 1 / Output 2,
84873195dielectric strength | Same as 84873034 ¦ IEC60255-27,Input 1 / Output 1,
84873195dielectric strength | Same as 84873034 ¦ IEC60255-27,Input 1 / Output 2,
84873195dielectric strength | Same as 84873034 ¦ IEC60255-27,Input 2 / Output 1,
84873195dielectric strength | Same as 84873034 ¦ IEC60255-27,Input 2 / Output 2,
84873195dielectric strength | Same as 84873034 ¦ IEC60255-27,Input 3 / Output 1,
84873195dielectric strength | Same as 84873034 ¦ IEC60255-27,Input 3 / Output 2,
84873195dielectric strength | Same as 84873034 ¦ IEC60255-27,Input 1 / Input 2,
84873195dielectric strength | Same as 84873034 ¦ IEC60255-27,Input 2 / Input 3,
84873195dielectric strength | Same as 84873034 ¦ IEC60255-27,Input 1 / Input 3,
84873195insulation resistance | Same as 84873034 ¦ IEC60255-27,Supply / Input 1,
84873195insulation resistance | Same as 84873034 ¦ IEC60255-27,Supply / Input 2,
84873195insulation resistance | Same as 84873034 ¦ IEC60255-27,Supply / Input 3,
84873195insulation resistance | Same as 84873034 ¦ IEC60255-27,Supply / Output 1,
84873195insulation resistance | Same as 84873034 ¦ IEC60255-27,Supply / Output 2,
84873195insulation resistance | Same as 84873034 ¦ IEC60255-27,Output 1 / Output 2,
84873195insulation resistance | Same as 84873034 ¦ IEC60255-27,Input 1 / Output 1,
84873195insulation resistance | Same as 84873034 ¦ IEC60255-27,Input 1 / Output 2,
84873195insulation resistance | Same as 84873034 ¦ IEC60255-27,Input 2 / Output 1,
84873195insulation resistance | Same as 84873034 ¦ IEC60255-27,Input 2 / Output 2,
84873195insulation resistance | Same as 84873034 ¦ IEC60255-27,Input 3 / Output 1,
84873195insulation resistance | Same as 84873034 ¦ IEC60255-27,Input 3 / Output 2,
84873195insulation resistance | Same as 84873034 ¦ IEC60255-27,Input 1 / Input 2,
84873195insulation resistance | Same as 84873034 ¦ IEC60255-27,Input 2 / Input 3,
84873195insulation resistance | Same as 84873034 ¦ IEC60255-27,Input 1 / Input 3,
84873195
84873195[Us] rated supply voltage | Same as 84873034
84873195supply voltage limits | Same as 84873034
84873195polarity | Same as 84873034
84873195supply frequency | Same as 84873034
84873195supply frequency | Same as 84873034
84873195power consumption | 28VA @ 480VAC, 60Hz 18VA @ 415VAC, 50Hz
84873195immunity to microbreaks | Same as 84873034
84873195supply terminal | Same as 84873034
84873195on-load factor | Same as 84873034
84873195release of input voltage | Same as 84873034
84873195
84873195monitoring functions | Same as 84873034 ¦ ,Phase lost ,
84873195monitoring functions | Same as 84873034 ¦ ,Phase sequence,
84873195monitoring functions | Same as 84873034 ¦ ,Over / undervoltage (symmetry windows mode),
84873195monitoring functions | Same as 84873034 ¦ ,Over voltage,
84873195monitoring functions | Same as 84873034 ¦ ,Undervoltage ,
84873195monitoring functions | Same as 84873034 ¦ ,Phase asymmetry,
84873195monitoring functions | Same as 84873034 ¦ ,Disconnection of neutral,
84873195monitoring functions | Same as 84873034 ¦ ,Voltage Regeneration,
84873195monitoring functions | Same as 84873034 ¦ ,Extreme undervoltage,
84873195monitoring functions | Same as 84873034 ¦ ,Extreme overvoltage,
84873195monitoring functions | Same as 84873034 ¦ ,Extreme asymmetry,
84873195 | Same as 84873034 ¦ ,Measurement mode,
84873195internal input resistance | Same as 84873034 ¦ ,Internal input resistance,
84873195input terminal | Same as 84873034 ¦ ,Input terminal,
84873195Input nominal voltage selection | Same as 84873034 ¦ ,Input nominal voltage selection,
84873195permissible input overload | Same as 84873034 ¦ ,permissible input overload,
84873195input frequency | Same as 84873034 ¦ ,Rated frequency,
84873195input frequency | Same as 84873034 ¦ ,Frequency operating range,
84873195setting accuracy of the switching threshold | Same as 84873034 ¦ ,Setting accuracy,
84873195repeat accuracy of the switching threshold | Same as 84873034 ¦ ,Repeat accuracy (constant parameters),
84873195measurement method | Same as 84873034 ¦ ,Measurement method,
84873195switching threshold drift | Same as 84873034 ¦ ,Measurement error with supply voltage variation,
84873195switching threshold drift | Same as 84873034 ¦ ,Measurement error with temperature variation,
84873195maximum measuring cycle | Same as 84873034 ¦ ,Maximum measuring cycles,
84873195measurement range | Same as 84873034 ¦ ,Phase lost ,
84873195measurement range | Same as 84873034 ¦ ,Phase sequence,
84873195measurement range | Same as 84873034 ¦ ,Over / undervoltage (symmetry windows mode),
84873195measurement range | Same as 84873034 ¦ ,Over voltage,
84873195measurement range | Same as 84873034 ¦ ,Undervoltage ,
84873195measurement range | Same as 84873034 ¦ ,Phase asymmetry,
84873195measurement range | Same as 84873034 ¦ ,Disconnection of neutral,
84873195measurement range | Same as 84873034 ¦ ,Voltage Regeneration,
84873195measurement range | Same as 84873034 ¦ ,Extreme undervoltage,
84873195measurement range | Same as 84873034 ¦ ,Extreme Overvoltage,
84873195measurement range | Same as 84873034 ¦ ,Extreme Asymmetry,
84873195tripping threshold | Same as 84873034 ¦ ,Phase cut,
84873195tripping threshold | Same as 84873034 ¦ ,Phase sequence,
84873195tripping threshold | Same as 84873034 ¦ ,Over / undervoltage (symmetry windows mode),
84873195tripping threshold | Same as 84873034 ¦ ,Over voltage,
84873195tripping threshold | Same as 84873034 ¦ ,Undervoltage ,
84873195tripping threshold | Same as 84873034 ¦ ,Phase asymmetry,
84873195tripping threshold | Same as 84873034 ¦ ,Disconnection of neutral,
84873195tripping threshold | Same as 84873034 ¦ ,Voltage Regeneration,
84873195tripping threshold | Same as 84873034 ¦ ,Extreme undervoltage (Phase loss),
84873195tripping threshold | Same as 84873034 ¦ ,Extreme Overvoltage,
84873195tripping threshold | Same as 84873034 ¦ ,Extreme Asymmetry,
84873195hysteresis | Same as 84873034 ¦ ,Phase cut,
84873195hysteresis | Same as 84873034 ¦ ,Phase sequence,
84873195hysteresis | Same as 84873034 ¦ ,Over / undervoltage (symmetry windows mode),
84873195hysteresis | Same as 84873034 ¦ ,Over voltage,
84873195hysteresis | Same as 84873034 ¦ ,Undervoltage ,
84873195hysteresis | Same as 84873034 ¦ ,Phase asymmetry,
84873195hysteresis | Same as 84873034 ¦ ,Disconnection of neutral,
84873195hysteresis | Same as 84873034 ¦ ,Voltage Regeneration,
84873195hysteresis | Same as 84873034 ¦ ,Extreme undervoltage (Phase loss),
84873195hysteresis | Same as 84873034 ¦ ,Extreme Overvoltage,
84873195hysteresis | Same as 84873034 ¦ ,Extreme Asymmetry,
84873195
84873195output type | Same as 84873034
84873195output terminal | Same as 84873034
84873195output logic | Same as 84873034 ¦ ,R1 (11-12-14),
84873195output logic | Same as 84873034 ¦ ,R2 (21-22-24),
84873195contacts material | Same as 84873034
84873195mechanical durability | Same as 84873034 ¦ IEC61810-1
84873195electrical durability | Same as 84873034 ¦ IEC60947-4-1,AC-1,
84873195electrical durability | Same as 84873034 ¦ IEC60947-4-1,DC-1,
84873195electrical durability | Same as 84873034 ¦ IEC60947-5-1,AC-15,
84873195electrical durability | Same as 84873034 ¦ IEC60947-5-1,DC-13,
84873195[Ue] rated operational voltage | Same as 84873034 ¦ IEC61810-1,Rated switching voltage,
84873195[Ie] rated operational current | Same as 84873034 ¦ IEC61810-1,Rated switching current,
84873195maximum switching capacity | Same as 84873034 ¦ ,Maximum switching voltage,
84873195maximum switching capacity | Same as 84873034 ¦ ,Maximum switching current,
84873195maximum switching capacity | Same as 84873034 ¦ ,Maximum switching capacity,
84873195minimum switching capacity | Same as 84873034 ¦ IEC60947-5-4,Minimum switching voltage,
84873195minimum switching capacity | Same as 84873034 ¦ IEC60947-5-4,Minimum switching current,
84873195minimum switching capacity | Same as 84873034 ¦ IEC60947-5-4,Minimum switching capacity,
84873195maximum voltage drop | Same as 84873034 ¦ IEC62314,Only for solid state output,
84873195maximum leakage current | Same as 84873034 ¦ IEC62314,Only for solid state output,
84873195thermal current | Same as 84873034 ¦ IEC60947-5-1
84873195short circuit protection | Same as 84873034 ¦ IEC60947-5-1,Relay Output by external fuse,
84873195short circuit protection | Same as 84873034 ¦ IEC62314,Solid State Output by external fuse,
84873195
84873195time delay type | Same as 84873034 ¦ ,"OFF" delay,
84873195time delay type | Same as 84873034 ¦ ,"ON" delay,
84873195time delay type | Same as 84873034 ¦ ,Inhibition,
84873195time delay range | Same as 84873034 ¦ ,"OFF" delay,
84873195time delay range | Same as 84873034 ¦ ,"ON" delay,
84873195time delay range | Same as 84873034 ¦ ,Inhibition,
84873195response time | Same as 84873034 ¦ ,on crossing the threshold,
84873195response time | Same as 84873034
84873195response time | Same as 84873034
84873195response time | Same as 84873034
84873195response time | Same as 84873034
84873195power on delay | Same as 84873034
84873195reset time | Same as 84873034 ¦ ,through Un power reset,
84873195reset time | Same as 84873034 ¦ ,through front panel reset,
84873195reset time | Same as 84873034 ¦ ,through input control reset,
84873195setting accuracy of time delay | Same as 84873034
84873195repeat accuracy of time delay | Same as 84873034
84873195time delay drift | Same as 84873034
84873195time delay drift | Same as 84873034
84873195
84873195status LED | Rel (Amber)
84873195local signalling | - ¦ ,Power supply availability,
84873195local signalling | - ¦ ,Power supply not availability,
84873195local signalling | - ¦ ,Timing in-progress,
84873195local signalling | R - ON ¦ ,Output is energized,
84873195local signalling | R - OFF ¦ ,Output is de-energized,
84873195local signalling | - ¦ ,Range Setting Changes,
84873195local signalling | Same as 84873034 ¦ ,Phase Cut,
84873195local signalling | Same as 84873034 ¦ ,Phase Sequence Swap,
84873195local signalling | Same as 84873034 ¦ ,Undervoltage <U,
84873195local signalling | Same as 84873034 ¦ ,Overvoltage >U,
84873195local signalling | Same as 84873034 ¦ ,Phase Asymmetry,
84873195local signalling | Same as 84873034 ¦ ,Voltage Regeneration,
84873195local signalling | Same as 84873034 ¦ ,Extreme Undervoltage <U (Phase loss),
84873195local signalling | Same as 84873034 ¦ ,Extreme Overvoltage >U,
84873195local signalling | Same as 84873034 ¦ ,Extreme Phase Asymmetry,
84873195
84873195 | Same as 84873034
84873195 | Same as 84873034
84873195diagnostic button | Same as 84873034
84873195 | Same as 84873034
84873195 | Same as 84873034
84873195
84873195safety reliability data | Same as 84873034 ¦ ,MTTF,
84873195safety reliability data | Same as 84873034 ¦ ,B10,
84873195 | Same as 84873034 ¦ ,MTTFd,
84873195 | Same as 84873034 ¦ ,B10d,
84873195
84873195 | Drawing / Diagram
RM17TE00
RM17TE00standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM17TE00product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TE00marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TE00directives | 2014/35/EU
RM17TE00directives | 2014/30/EU
RM17TE00directives | 2011/65/EU
RM17TE00
RM17TE00 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM17TE00 | Class C ¦ Germanisher Lloyd,Environmental category,
RM17TE00ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM17TE00ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM17TE00relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM17TE00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM17TE00vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM17TE00shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM17TE00bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM17TE00seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM17TE00IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM17TE00IP degree of protection | IP30 ¦ IEC60529,Housing,
RM17TE00IP degree of protection | - ¦ IEC60529,Front Panel,
RM17TE00
RM17TE00width | 17.5 ¦ ,Width,
RM17TE00height | 90 ¦ ,Height,
RM17TE00depth | 72 ¦ ,Depth,
RM17TE00net weight | 80
RM17TE00mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM17TE00mounting support | - ¦ IEC/EN 60715,With socket,
RM17TE00mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM17TE00Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM17TE00Minimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM17TE00connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM17TE00connections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM17TE00connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM17TE00connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM17TE00tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM17TE00cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM17TE00duty time | 1
RM17TE00
RM17TE00electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM17TE00electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM17TE00electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM17TE00electromagnetic compatibility | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM17TE00electromagnetic compatibility | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge,
RM17TE00electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM17TE00electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM17TE00electromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM17TE00electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM17TE00electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM17TE00electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM17TE00electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM17TE00electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM17TE00electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM17TE00electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM17TE00electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM17TE00electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM17TE00electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM17TE00electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM17TE00
RM17TE00pollution degree | 3 ¦ IEC60664-1
RM17TE00overvoltage category | 3 ¦ IEC60664-1
RM17TE00circuit group | L1, L2, L3 ¦ ,Supply,Terminal
RM17TE00circuit group | - ¦ ,Input 1,
RM17TE00circuit group | - ¦ ,Input 2,
RM17TE00circuit group | - ¦ ,Input 3,
RM17TE00circuit group | 11,12,14 ¦ ,Output 1,
RM17TE00circuit group | - ¦ ,Output 2,
RM17TE00 | 208..480 AC ¦ ,Supply,Rated
RM17TE00 | - ¦ ,Input 1,Voltage
RM17TE00 | - ¦ ,Input 2,Spec
RM17TE00 | - ¦ ,Input 3,
RM17TE00 | 250V ¦ ,Output 1,
RM17TE00 | - ¦ ,Output 2,
RM17TE00[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM17TE00[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Output 2,
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM17TE00[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Output 2,
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Output 1 / Output 2,
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM17TE00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM17TE00[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM17TE00[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Output 2,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1 / Output 2,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM17TE00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM17TE00dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM17TE00dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM17TE00dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM17TE00dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM17TE00dielectric strength | - ¦ IEC60255-27,Supply / Output 2,
RM17TE00dielectric strength | - ¦ IEC60255-27,Output 1 / Output 2,
RM17TE00dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM17TE00dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM17TE00dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM17TE00dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM17TE00dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM17TE00dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM17TE00dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM17TE00dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM17TE00dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM17TE00insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM17TE00insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM17TE00insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM17TE00insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM17TE00insulation resistance | - ¦ IEC60255-27,Supply / Output 2,
RM17TE00insulation resistance | - ¦ IEC60255-27,Output 1 / Output 2,
RM17TE00insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM17TE00insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM17TE00insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM17TE00insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM17TE00insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM17TE00insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM17TE00insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM17TE00insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM17TE00insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM17TE00
RM17TE00[Us] rated supply voltage | ~ 3 x 208…3 x 480
RM17TE00supply voltage limits | ~ 3 x 183…3 x 528
RM17TE00polarity | -
RM17TE00supply frequency | 50 / 60
RM17TE00supply frequency | 45…66
RM17TE00power consumption | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz
RM17TE00immunity to microbreaks | 0
RM17TE00supply terminal | L1-L3
RM17TE00on-load factor | 1
RM17TE00release of input voltage | -
RM17TE00
RM17TE00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost ,
RM17TE00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence,
RM17TE00monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Over / undervoltage (symmetry windows mode),
RM17TE00monitoring functions | - ¦ ,Over voltage,
RM17TE00monitoring functions | - ¦ ,Undervoltage ,
RM17TE00monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Phase asymmetry,
RM17TE00monitoring functions | - ¦ ,Disconnection of neutral,
RM17TE00monitoring functions | - ¦ ,Voltage Regeneration,
RM17TE00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage,
RM17TE00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage,
RM17TE00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM17TE00 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM17TE00internal input resistance | - ¦ ,Internal input resistance,
RM17TE00input terminal | L1-L2-L3 ¦ ,Input terminal,
RM17TE00Input nominal voltage selection | 208, 220, 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM17TE00permissible input overload | - ¦ ,permissible input overload,
RM17TE00input frequency | 50 / 60 ¦ ,Rated frequency,
RM17TE00input frequency | 45…66 ¦ ,Frequency operating range,
RM17TE00setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM17TE00repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM17TE00measurement method | True RMS ¦ ,Measurement method,
RM17TE00switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation,
RM17TE00switching threshold drift | < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM17TE00maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM17TE00measurement range | - ¦ ,Phase lost ,
RM17TE00measurement range | - ¦ ,Phase sequence,
RM17TE00measurement range | -2…-20 % in the ranges 3 x ~ 380…480 -2…-12 % in the range 3 x ~ 208 -2…-17 % in the range 3 x ~ 220 +2…+20 % in the ranges 3 x ~ 208…440 +2…+10 % in the range 3 x ~ 480 ¦ ,Over / undervoltage (symmetry windows mode),
RM17TE00measurement range | - ¦ ,Over voltage,
RM17TE00measurement range | - ¦ ,Undervoltage ,
RM17TE00measurement range | +5…+15 % in the ranges 3 x ~ 208…480 ¦ ,Phase asymmetry,
RM17TE00measurement range | - ¦ ,Disconnection of neutral,
RM17TE00measurement range | - ¦ ,Voltage Regeneration,
RM17TE00measurement range | - ¦ ,Extreme undervoltage,
RM17TE00measurement range | - ¦ ,Extreme Overvoltage,
RM17TE00measurement range | - ¦ ,Extreme Asymmetry,
RM17TE00tripping threshold | 1 or more phase cut ¦ ,Phase cut,
RM17TE00tripping threshold | Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence,
RM17TE00tripping threshold | Adjustable 2%...20% of selected Un ¦ ,Over / undervoltage (symmetry windows mode),
RM17TE00tripping threshold | - ¦ ,Over voltage,
RM17TE00tripping threshold | - ¦ ,Undervoltage ,
RM17TE00tripping threshold | Adjustable 5%...15% of selected Un ¦ ,Phase asymmetry,
RM17TE00tripping threshold | - ¦ ,Disconnection of neutral,
RM17TE00tripping threshold | - ¦ ,Voltage Regeneration,
RM17TE00tripping threshold | 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM17TE00tripping threshold | Internal design spec: 543V +/- 5% ¦ ,Extreme Overvoltage,
RM17TE00tripping threshold | Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM17TE00hysteresis | All phase cut recover ¦ ,Phase cut,
RM17TE00hysteresis | Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence,
RM17TE00hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Over / undervoltage (symmetry windows mode),
RM17TE00hysteresis | - ¦ ,Over voltage,
RM17TE00hysteresis | - ¦ ,Undervoltage ,
RM17TE00hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Phase asymmetry,
RM17TE00hysteresis | - ¦ ,Disconnection of neutral,
RM17TE00hysteresis | - ¦ ,Voltage Regeneration,
RM17TE00hysteresis | All phases > 195V Internal design spec: All phases >180V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM17TE00hysteresis | Internal design spec: All phases <533V +/- 5% ¦ ,Extreme Overvoltage,
RM17TE00hysteresis | - ¦ ,Extreme Asymmetry,
RM17TE00
RM17TE00output type | 1 x C/O relay contacts
RM17TE00output terminal | 11-12-14
RM17TE00output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM17TE00output logic | - ¦ ,R2 (21-22-24),
RM17TE00contacts material | Cadmium free
RM17TE00mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM17TE00electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM17TE00electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM17TE00electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM17TE00electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM17TE00[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM17TE00[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM17TE00maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM17TE00maximum switching capacity | 5A ¦ ,Maximum switching current,
RM17TE00maximum switching capacity | - ¦ ,Maximum switching capacity,
RM17TE00minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM17TE00minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM17TE00minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM17TE00maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM17TE00maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM17TE00thermal current | 5A ¦ IEC60947-5-1
RM17TE00short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse,
RM17TE00short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM17TE00
RM17TE00time delay type | Yes ¦ ,"OFF" delay,
RM17TE00time delay type | - ¦ ,"ON" delay,
RM17TE00time delay type | - ¦ ,Inhibition,
RM17TE00time delay range | Adjustable 0.1…10 ¦ ,"OFF" delay,
RM17TE00time delay range | - ¦ ,"ON" delay,
RM17TE00time delay range | - ¦ ,Inhibition,
RM17TE00response time | 0
RM17TE00response time | -
RM17TE00response time | -
RM17TE00response time | -
RM17TE00response time | -
RM17TE00power on delay | 0
RM17TE00reset time | 0
RM17TE00reset time | - ¦ ,through front panel reset,
RM17TE00reset time | - ¦ ,through input control reset,
RM17TE00setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM17TE00repeat accuracy of time delay | +/- 3%
RM17TE00time delay drift | -
RM17TE00time delay drift | -
RM17TE00
RM17TE00status LED | Un (Green) R (Amber)
RM17TE00local signalling | Un - ON ¦ ,Power supply availability,
RM17TE00local signalling | Un - OFF ¦ ,Power supply not availability,
RM17TE00local signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM17TE00local signalling | R - ON ¦ ,Output is energized,
RM17TE00local signalling | R - OFF ¦ ,Output is de-energized,
RM17TE00local signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM17TE00local signalling | - ¦ ,Phase Cut,
RM17TE00local signalling | - ¦ ,Phase Sequence Swap,
RM17TE00local signalling | - ¦ ,Undervoltage <U,
RM17TE00local signalling | - ¦ ,Overvoltage >U,
RM17TE00local signalling | - ¦ ,Phase Asymmetry,
RM17TE00local signalling | - ¦ ,Voltage Regeneration,
RM17TE00local signalling | - ¦ ,Extreme Undervoltage <U (Phase loss),
RM17TE00local signalling | - ¦ ,Extreme Overvoltage >U,
RM17TE00local signalling | - ¦ ,Extreme Phase Asymmetry,
RM17TE00
RM17TE00 | Yes
RM17TE00 | -
RM17TE00diagnostic button | -
RM17TE00 | -
RM17TE00 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM17TE00
RM17TE00safety reliability data | 4,400,000 hours ¦ ,MTTF,
RM17TE00safety reliability data | 470,000 hours ¦ ,B10,
RM17TE00 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM17TE00 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM17TE00
RM17TE00 | Drawing / Diagram
RM10TE00
RM10TE00standards | Same as RM17TE00
RM10TE00product certifications | CCC, CE, China ROHS
RM10TE00marking | CCC, CE, China ROHS
RM10TE00directives | Same as RM17TE00
RM10TE00directives | Same as RM17TE00
RM10TE00directives | Same as RM17TE00
RM10TE00
RM10TE00 | Same as RM17TE00 ¦ IEC60721-3-3,Climatic category,
RM10TE00 | Same as RM17TE00 ¦ Germanisher Lloyd,Environmental category,
RM10TE00ambient air temperature for storage | Same as RM17TE00 ¦ ,Storage,
RM10TE00ambient air temperature for operation | Same as RM17TE00 ¦ ,Operation,
RM10TE00relative humidity | Same as RM17TE00 ¦ IEC60068-2-30,Damp heat,XX
RM10TE00 | Same as RM17TE00 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM10TE00vibration resistance | Same as RM17TE00 ¦ IEC60068-2-6
RM10TE00shock resistance | Same as RM17TE00 ¦ IEC60068-2-27
RM10TE00bump resistance | Same as RM17TE00 ¦ IEC60068-2-29
RM10TE00seismic resistance | Same as RM17TE00 ¦ IEC60068-3-3
RM10TE00IP degree of protection | Same as RM17TE00 ¦ IEC60529,Terminal Block,
RM10TE00IP degree of protection | Same as RM17TE00 ¦ IEC60529,Housing,
RM10TE00IP degree of protection | Same as RM17TE00 ¦ IEC60529,Front Panel,
RM10TE00
RM10TE00width | Same as RM17TE00 ¦ ,Width,
RM10TE00height | Same as RM17TE00 ¦ ,Height,
RM10TE00depth | Same as RM17TE00 ¦ ,Depth,
RM10TE00net weight | Same as RM17TE00
RM10TE00mounting support | Same as RM17TE00 ¦ IEC/EN 60715,Without socket,
RM10TE00mounting support | Same as RM17TE00 ¦ IEC/EN 60715,With socket,
RM10TE00mounting position | Same as RM17TE00 ¦ ,In relation to normal vertical mounting plane,
RM10TE00Minimum distance to adjacent devices | Same as RM17TE00 ¦ ,Horizontal,
RM10TE00Minimum distance to adjacent devices | Same as RM17TE00 ¦ ,Vertical,
RM10TE00connections - terminals | Same as RM17TE00 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM10TE00connections - terminals | Same as RM17TE00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM10TE00connections - terminals | Same as RM17TE00 ¦ IEC60947-1,Solid cable (spring terminal),
RM10TE00connections - terminals | Same as RM17TE00 ¦ IEC60947-1,Flexible cable (spring terminal),
RM10TE00tightening torque | Same as RM17TE00 ¦ IEC60947-1,Tightening torque,
RM10TE00cable stripping length | Same as RM17TE00 ¦ ,Cable stripping length,
RM10TE00duty time | Same as RM17TE00
RM10TE00
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ ,Generic immunity standard,
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-2,Electrostatic discharge,
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-4,Fast transient / burst,
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-5,Surge,
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-6,Conducted RF disturbance,
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-8,Power frequency magnetic field,
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-18,1 MHz oscillation wave,
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-29,DC voltage interruption,
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-13,Low frequency harmonics,
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ ,Generic emission standard,
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ Germanisher Lloyd,Conducted emission,
RM10TE00
RM10TE00pollution degree | Same as RM17TE00 ¦ IEC60664-1
RM10TE00overvoltage category | Same as RM17TE00 ¦ IEC60664-1
RM10TE00circuit group | Same as RM17TE00 ¦ ,Supply,Terminal
RM10TE00circuit group | Same as RM17TE00 ¦ ,Input 1,
RM10TE00circuit group | Same as RM17TE00 ¦ ,Input 2,
RM10TE00circuit group | Same as RM17TE00 ¦ ,Input 3,
RM10TE00circuit group | Same as RM17TE00 ¦ ,Output 1,
RM10TE00circuit group | Same as RM17TE00 ¦ ,Output 2,
RM10TE00 | Same as RM17TE00 ¦ ,Supply,Rated
RM10TE00 | Same as RM17TE00 ¦ ,Input 1,Voltage
RM10TE00 | Same as RM17TE00 ¦ ,Input 2,Spec
RM10TE00 | Same as RM17TE00 ¦ ,Input 3,
RM10TE00 | Same as RM17TE00 ¦ ,Output 1,
RM10TE00 | Same as RM17TE00 ¦ ,Output 2,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Supply,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 2,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 3,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Output 1,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Output 2,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Input 2,Isolated
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Input 3,Circuit
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Output 1,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Output 2,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Output 1 / Output 2,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1 / Output 1,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1 / Output 2,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 2 / Output 1,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 2 / Output 2,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 3 / Output 1,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 3 / Output 2,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1 / Input 2,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 2 / Input 3,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1 / Input 3,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Supply,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 2,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 3,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Output 1,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Output 2,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Input 2,Isolated
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Input 3,Circuit
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Output 1,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Output 2,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Output 1 / Output 2,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1 / Output 1,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1 / Output 2,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 2 / Output 1,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 2 / Output 2,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 3 / Output 1,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 3 / Output 2,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1 / Input 2,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 2 / Input 3,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1 / Input 3,
RM10TE00dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Supply / Input 1,
RM10TE00dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Supply / Input 2,
RM10TE00dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Supply / Input 3,
RM10TE00dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Supply / Output 1,
RM10TE00dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Supply / Output 2,
RM10TE00dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Output 1 / Output 2,
RM10TE00dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 1 / Output 1,
RM10TE00dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 1 / Output 2,
RM10TE00dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 2 / Output 1,
RM10TE00dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 2 / Output 2,
RM10TE00dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 3 / Output 1,
RM10TE00dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 3 / Output 2,
RM10TE00dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 1 / Input 2,
RM10TE00dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 2 / Input 3,
RM10TE00dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 1 / Input 3,
RM10TE00insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Supply / Input 1,
RM10TE00insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Supply / Input 2,
RM10TE00insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Supply / Input 3,
RM10TE00insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Supply / Output 1,
RM10TE00insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Supply / Output 2,
RM10TE00insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Output 1 / Output 2,
RM10TE00insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 1 / Output 1,
RM10TE00insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 1 / Output 2,
RM10TE00insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 2 / Output 1,
RM10TE00insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 2 / Output 2,
RM10TE00insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 3 / Output 1,
RM10TE00insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 3 / Output 2,
RM10TE00insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 1 / Input 2,
RM10TE00insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 2 / Input 3,
RM10TE00insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 1 / Input 3,
RM10TE00
RM10TE00[Us] rated supply voltage | Same as RM17TE00
RM10TE00supply voltage limits | Same as RM17TE00
RM10TE00polarity | Same as RM17TE00
RM10TE00supply frequency | Same as RM17TE00
RM10TE00supply frequency | Same as RM17TE00
RM10TE00power consumption | Same as RM17TE00
RM10TE00immunity to microbreaks | Same as RM17TE00
RM10TE00supply terminal | Same as RM17TE00
RM10TE00on-load factor | Same as RM17TE00
RM10TE00release of input voltage | Same as RM17TE00
RM10TE00
RM10TE00monitoring functions | Same as RM17TE00 ¦ ,Phase lost ,
RM10TE00monitoring functions | Same as RM17TE00 ¦ ,Phase sequence,
RM10TE00monitoring functions | Same as RM17TE00 ¦ ,Over / undervoltage (symmetry windows mode),
RM10TE00monitoring functions | Same as RM17TE00 ¦ ,Over voltage,
RM10TE00monitoring functions | Same as RM17TE00 ¦ ,Undervoltage ,
RM10TE00monitoring functions | Same as RM17TE00 ¦ ,Phase asymmetry,
RM10TE00monitoring functions | Same as RM17TE00 ¦ ,Disconnection of neutral,
RM10TE00monitoring functions | Same as RM17TE00 ¦ ,Voltage Regeneration,
RM10TE00monitoring functions | Same as RM17TE00 ¦ ,Extreme undervoltage,
RM10TE00monitoring functions | Same as RM17TE00 ¦ ,Extreme overvoltage,
RM10TE00monitoring functions | Same as RM17TE00 ¦ ,Extreme asymmetry,
RM10TE00 | Same as RM17TE00 ¦ ,Measurement mode,
RM10TE00internal input resistance | Same as RM17TE00 ¦ ,Internal input resistance,
RM10TE00input terminal | Same as RM17TE00 ¦ ,Input terminal,
RM10TE00Input nominal voltage selection | Same as RM17TE00 ¦ ,Input nominal voltage selection,
RM10TE00permissible input overload | Same as RM17TE00 ¦ ,permissible input overload,
RM10TE00input frequency | Same as RM17TE00 ¦ ,Rated frequency,
RM10TE00input frequency | Same as RM17TE00 ¦ ,Frequency operating range,
RM10TE00setting accuracy of the switching threshold | Same as RM17TE00 ¦ ,Setting accuracy,
RM10TE00repeat accuracy of the switching threshold | Same as RM17TE00 ¦ ,Repeat accuracy (constant parameters),
RM10TE00measurement method | Same as RM17TE00 ¦ ,Measurement method,
RM10TE00switching threshold drift | Same as RM17TE00 ¦ ,Measurement error with supply voltage variation,
RM10TE00switching threshold drift | Same as RM17TE00 ¦ ,Measurement error with temperature variation,
RM10TE00maximum measuring cycle | Same as RM17TE00 ¦ ,Maximum measuring cycles,
RM10TE00measurement range | Same as RM17TE00 ¦ ,Phase lost ,
RM10TE00measurement range | Same as RM17TE00 ¦ ,Phase sequence,
RM10TE00measurement range | Same as RM17TE00 ¦ ,Over / undervoltage (symmetry windows mode),
RM10TE00measurement range | Same as RM17TE00 ¦ ,Over voltage,
RM10TE00measurement range | Same as RM17TE00 ¦ ,Undervoltage ,
RM10TE00measurement range | Same as RM17TE00 ¦ ,Phase asymmetry,
RM10TE00measurement range | Same as RM17TE00 ¦ ,Disconnection of neutral,
RM10TE00measurement range | Same as RM17TE00 ¦ ,Voltage Regeneration,
RM10TE00measurement range | Same as RM17TE00 ¦ ,Extreme undervoltage,
RM10TE00measurement range | Same as RM17TE00 ¦ ,Extreme Overvoltage,
RM10TE00measurement range | Same as RM17TE00 ¦ ,Extreme Asymmetry,
RM10TE00tripping threshold | Same as RM17TE00 ¦ ,Phase cut,
RM10TE00tripping threshold | Same as RM17TE00 ¦ ,Phase sequence,
RM10TE00tripping threshold | Same as RM17TE00 ¦ ,Over / undervoltage (symmetry windows mode),
RM10TE00tripping threshold | Same as RM17TE00 ¦ ,Over voltage,
RM10TE00tripping threshold | Same as RM17TE00 ¦ ,Undervoltage ,
RM10TE00tripping threshold | Same as RM17TE00 ¦ ,Phase asymmetry,
RM10TE00tripping threshold | Same as RM17TE00 ¦ ,Disconnection of neutral,
RM10TE00tripping threshold | Same as RM17TE00 ¦ ,Voltage Regeneration,
RM10TE00tripping threshold | Same as RM17TE00 ¦ ,Extreme undervoltage (Phase loss),
RM10TE00tripping threshold | Same as RM17TE00 ¦ ,Extreme Overvoltage,
RM10TE00tripping threshold | Same as RM17TE00 ¦ ,Extreme Asymmetry,
RM10TE00hysteresis | Same as RM17TE00 ¦ ,Phase cut,
RM10TE00hysteresis | Same as RM17TE00 ¦ ,Phase sequence,
RM10TE00hysteresis | Same as RM17TE00 ¦ ,Over / undervoltage (symmetry windows mode),
RM10TE00hysteresis | Same as RM17TE00 ¦ ,Over voltage,
RM10TE00hysteresis | Same as RM17TE00 ¦ ,Undervoltage ,
RM10TE00hysteresis | Same as RM17TE00 ¦ ,Phase asymmetry,
RM10TE00hysteresis | Same as RM17TE00 ¦ ,Disconnection of neutral,
RM10TE00hysteresis | Same as RM17TE00 ¦ ,Voltage Regeneration,
RM10TE00hysteresis | Same as RM17TE00 ¦ ,Extreme undervoltage (Phase loss),
RM10TE00hysteresis | Same as RM17TE00 ¦ ,Extreme Overvoltage,
RM10TE00hysteresis | Same as RM17TE00 ¦ ,Extreme Asymmetry,
RM10TE00
RM10TE00output type | Same as RM17TE00
RM10TE00output terminal | Same as RM17TE00
RM10TE00output logic | Same as RM17TE00 ¦ ,R1 (11-12-14),
RM10TE00output logic | Same as RM17TE00 ¦ ,R2 (21-22-24),
RM10TE00contacts material | Same as RM17TE00
RM10TE00mechanical durability | Same as RM17TE00 ¦ IEC61810-1
RM10TE00electrical durability | Same as RM17TE00 ¦ IEC60947-4-1,AC-1,
RM10TE00electrical durability | Same as RM17TE00 ¦ IEC60947-4-1,DC-1,
RM10TE00electrical durability | Same as RM17TE00 ¦ IEC60947-5-1,AC-15,
RM10TE00electrical durability | Same as RM17TE00 ¦ IEC60947-5-1,DC-13,
RM10TE00[Ue] rated operational voltage | Same as RM17TE00 ¦ IEC61810-1,Rated switching voltage,
RM10TE00[Ie] rated operational current | Same as RM17TE00 ¦ IEC61810-1,Rated switching current,
RM10TE00maximum switching capacity | Same as RM17TE00 ¦ ,Maximum switching voltage,
RM10TE00maximum switching capacity | Same as RM17TE00 ¦ ,Maximum switching current,
RM10TE00maximum switching capacity | Same as RM17TE00 ¦ ,Maximum switching capacity,
RM10TE00minimum switching capacity | Same as RM17TE00 ¦ IEC60947-5-4,Minimum switching voltage,
RM10TE00minimum switching capacity | Same as RM17TE00 ¦ IEC60947-5-4,Minimum switching current,
RM10TE00minimum switching capacity | Same as RM17TE00 ¦ IEC60947-5-4,Minimum switching capacity,
RM10TE00maximum voltage drop | Same as RM17TE00 ¦ IEC62314,Only for solid state output,
RM10TE00maximum leakage current | Same as RM17TE00 ¦ IEC62314,Only for solid state output,
RM10TE00thermal current | Same as RM17TE00 ¦ IEC60947-5-1
RM10TE00short circuit protection | Same as RM17TE00 ¦ IEC60947-5-1,Relay Output by external fuse,
RM10TE00short circuit protection | Same as RM17TE00 ¦ IEC62314,Solid State Output by external fuse,
RM10TE00
RM10TE00time delay type | Same as RM17TE00 ¦ ,"OFF" delay,
RM10TE00time delay type | Same as RM17TE00 ¦ ,"ON" delay,
RM10TE00time delay type | Same as RM17TE00 ¦ ,Inhibition,
RM10TE00time delay range | Same as RM17TE00 ¦ ,"OFF" delay,
RM10TE00time delay range | Same as RM17TE00 ¦ ,"ON" delay,
RM10TE00time delay range | Same as RM17TE00 ¦ ,Inhibition,
RM10TE00response time | Same as RM17TE00 ¦ ,on crossing the threshold,
RM10TE00response time | Same as RM17TE00
RM10TE00response time | Same as RM17TE00
RM10TE00response time | Same as RM17TE00
RM10TE00response time | Same as RM17TE00
RM10TE00power on delay | Same as RM17TE00
RM10TE00reset time | Same as RM17TE00 ¦ ,through Un power reset,
RM10TE00reset time | Same as RM17TE00 ¦ ,through front panel reset,
RM10TE00reset time | Same as RM17TE00 ¦ ,through input control reset,
RM10TE00setting accuracy of time delay | Same as RM17TE00
RM10TE00repeat accuracy of time delay | Same as RM17TE00
RM10TE00time delay drift | Same as RM17TE00
RM10TE00time delay drift | Same as RM17TE00
RM10TE00
RM10TE00status LED | Same as RM17TE00
RM10TE00local signalling | Same as RM17TE00 ¦ ,Power supply availability,
RM10TE00local signalling | Same as RM17TE00 ¦ ,Power supply not availability,
RM10TE00local signalling | Same as RM17TE00 ¦ ,Timing in-progress,
RM10TE00local signalling | Same as RM17TE00 ¦ ,Output is energized,
RM10TE00local signalling | Same as RM17TE00 ¦ ,Output is de-energized,
RM10TE00local signalling | Same as RM17TE00 ¦ ,Range Setting Changes,
RM10TE00local signalling | Same as RM17TE00 ¦ ,Phase Cut,
RM10TE00local signalling | Same as RM17TE00 ¦ ,Phase Sequence Swap,
RM10TE00local signalling | Same as RM17TE00 ¦ ,Undervoltage <U,
RM10TE00local signalling | Same as RM17TE00 ¦ ,Overvoltage >U,
RM10TE00local signalling | Same as RM17TE00 ¦ ,Phase Asymmetry,
RM10TE00local signalling | Same as RM17TE00 ¦ ,Voltage Regeneration,
RM10TE00local signalling | Same as RM17TE00 ¦ ,Extreme Undervoltage <U (Phase loss),
RM10TE00local signalling | Same as RM17TE00 ¦ ,Extreme Overvoltage >U,
RM10TE00local signalling | Same as RM17TE00 ¦ ,Extreme Phase Asymmetry,
RM10TE00
RM10TE00 | Same as RM17TE00
RM10TE00 | Same as RM17TE00
RM10TE00diagnostic button | Same as RM17TE00
RM10TE00 | Same as RM17TE00
RM10TE00 | Same as RM17TE00
RM10TE00
RM10TE00safety reliability data | Same as RM17TE00 ¦ ,MTTF,
RM10TE00safety reliability data | Same as RM17TE00 ¦ ,B10,
RM10TE00 | Same as RM17TE00 ¦ ,MTTFd,
RM10TE00 | Same as RM17TE00 ¦ ,B10d,
RM10TE00
RM10TE00 | Drawing / Diagram
84873025
84873025standards | Same as RM17TE00
84873025product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873025marking | UL, CSA, GL, CCC, CE, China ROHS
84873025directives | Same as RM17TE00
84873025directives | Same as RM17TE00
84873025directives | Same as RM17TE00
84873025
84873025 | Same as RM17TE00 ¦ IEC60721-3-3,Climatic category,
84873025 | Same as RM17TE00 ¦ Germanisher Lloyd,Environmental category,
84873025ambient air temperature for storage | Same as RM17TE00 ¦ ,Storage,
84873025ambient air temperature for operation | Same as RM17TE00 ¦ ,Operation,
84873025relative humidity | Same as RM17TE00 ¦ IEC60068-2-30,Damp heat,XX
84873025 | Same as RM17TE00 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873025vibration resistance | Same as RM17TE00 ¦ IEC60068-2-6
84873025shock resistance | Same as RM17TE00 ¦ IEC60068-2-27
84873025bump resistance | Same as RM17TE00 ¦ IEC60068-2-29
84873025seismic resistance | Same as RM17TE00 ¦ IEC60068-3-3
84873025IP degree of protection | Same as RM17TE00 ¦ IEC60529,Terminal Block,
84873025IP degree of protection | Same as RM17TE00 ¦ IEC60529,Housing,
84873025IP degree of protection | Same as RM17TE00 ¦ IEC60529,Front Panel,
84873025
84873025width | Same as RM17TE00 ¦ ,Width,
84873025height | Same as RM17TE00 ¦ ,Height,
84873025depth | Same as RM17TE00 ¦ ,Depth,
84873025net weight | Same as RM17TE00
84873025mounting support | Same as RM17TE00 ¦ IEC/EN 60715,Without socket,
84873025mounting support | Same as RM17TE00 ¦ IEC/EN 60715,With socket,
84873025mounting position | Same as RM17TE00 ¦ ,In relation to normal vertical mounting plane,
84873025Minimum distance to adjacent devices | Same as RM17TE00 ¦ ,Horizontal,
84873025Minimum distance to adjacent devices | Same as RM17TE00 ¦ ,Vertical,
84873025connections - terminals | Same as RM17TE00 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873025connections - terminals | Same as RM17TE00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873025connections - terminals | Same as RM17TE00 ¦ IEC60947-1,Solid cable (spring terminal),
84873025connections - terminals | Same as RM17TE00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873025tightening torque | Same as RM17TE00 ¦ IEC60947-1,Tightening torque,
84873025cable stripping length | Same as RM17TE00 ¦ ,Cable stripping length,
84873025duty time | Same as RM17TE00
84873025
84873025electromagnetic compatibility | Same as RM17TE00 ¦ ,Generic immunity standard,
84873025electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-2,Electrostatic discharge,
84873025electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873025electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-4,Fast transient / burst,
84873025electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-5,Surge,
84873025electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-6,Conducted RF disturbance,
84873025electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-8,Power frequency magnetic field,
84873025electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873025electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873025electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-29,DC voltage interruption,
84873025electromagnetic compatibility | Same as RM17TE00 ¦ IEC61000-4-13,Low frequency harmonics,
84873025electromagnetic compatibility | Same as RM17TE00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873025electromagnetic compatibility | Same as RM17TE00 ¦ ,Generic emission standard,
84873025electromagnetic compatibility | Same as RM17TE00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873025electromagnetic compatibility | Same as RM17TE00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873025electromagnetic compatibility | Same as RM17TE00 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873025electromagnetic compatibility | Same as RM17TE00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873025electromagnetic compatibility | Same as RM17TE00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873025electromagnetic compatibility | Same as RM17TE00 ¦ Germanisher Lloyd,Conducted emission,
84873025
84873025pollution degree | Same as RM17TE00 ¦ IEC60664-1
84873025overvoltage category | Same as RM17TE00 ¦ IEC60664-1
84873025circuit group | Same as RM17TE00 ¦ ,Supply,Terminal
84873025circuit group | Same as RM17TE00 ¦ ,Input 1,
84873025circuit group | Same as RM17TE00 ¦ ,Input 2,
84873025circuit group | Same as RM17TE00 ¦ ,Input 3,
84873025circuit group | Same as RM17TE00 ¦ ,Output 1,
84873025circuit group | Same as RM17TE00 ¦ ,Output 2,
84873025 | Same as RM17TE00 ¦ ,Supply,Rated
84873025 | Same as RM17TE00 ¦ ,Input 1,Voltage
84873025 | Same as RM17TE00 ¦ ,Input 2,Spec
84873025 | Same as RM17TE00 ¦ ,Input 3,
84873025 | Same as RM17TE00 ¦ ,Output 1,
84873025 | Same as RM17TE00 ¦ ,Output 2,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Supply,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 2,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 3,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Output 1,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Output 2,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Output 1,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Output 2,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Output 1 / Output 2,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1 / Output 1,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1 / Output 2,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 2 / Output 1,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 2 / Output 2,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 3 / Output 1,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 3 / Output 2,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1 / Input 2,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 2 / Input 3,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1 / Input 3,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Supply,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 2,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 3,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Output 1,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Output 2,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Output 1,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Supply / Output 2,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Output 1 / Output 2,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1 / Output 1,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1 / Output 2,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 2 / Output 1,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 2 / Output 2,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 3 / Output 1,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 3 / Output 2,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1 / Input 2,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 2 / Input 3,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Input 1 / Input 3,
84873025dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Supply / Input 1,
84873025dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Supply / Input 2,
84873025dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Supply / Input 3,
84873025dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Supply / Output 1,
84873025dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Supply / Output 2,
84873025dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Output 1 / Output 2,
84873025dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 1 / Output 1,
84873025dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 1 / Output 2,
84873025dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 2 / Output 1,
84873025dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 2 / Output 2,
84873025dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 3 / Output 1,
84873025dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 3 / Output 2,
84873025dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 1 / Input 2,
84873025dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 2 / Input 3,
84873025dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Input 1 / Input 3,
84873025insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Supply / Input 1,
84873025insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Supply / Input 2,
84873025insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Supply / Input 3,
84873025insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Supply / Output 1,
84873025insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Supply / Output 2,
84873025insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Output 1 / Output 2,
84873025insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 1 / Output 1,
84873025insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 1 / Output 2,
84873025insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 2 / Output 1,
84873025insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 2 / Output 2,
84873025insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 3 / Output 1,
84873025insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 3 / Output 2,
84873025insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 1 / Input 2,
84873025insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 2 / Input 3,
84873025insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Input 1 / Input 3,
84873025
84873025[Us] rated supply voltage | Same as RM17TE00
84873025supply voltage limits | Same as RM17TE00
84873025polarity | Same as RM17TE00
84873025supply frequency | Same as RM17TE00
84873025supply frequency | Same as RM17TE00
84873025power consumption | Same as RM17TE00
84873025immunity to microbreaks | Same as RM17TE00
84873025supply terminal | Same as RM17TE00
84873025on-load factor | Same as RM17TE00
84873025release of input voltage | Same as RM17TE00
84873025
84873025monitoring functions | Same as RM17TE00 ¦ ,Phase lost ,
84873025monitoring functions | Same as RM17TE00 ¦ ,Phase sequence,
84873025monitoring functions | Same as RM17TE00 ¦ ,Over / undervoltage (symmetry windows mode),
84873025monitoring functions | Same as RM17TE00 ¦ ,Over voltage,
84873025monitoring functions | Same as RM17TE00 ¦ ,Undervoltage ,
84873025monitoring functions | Same as RM17TE00 ¦ ,Phase asymmetry,
84873025monitoring functions | Same as RM17TE00 ¦ ,Disconnection of neutral,
84873025monitoring functions | Same as RM17TE00 ¦ ,Voltage Regeneration,
84873025monitoring functions | Same as RM17TE00 ¦ ,Extreme undervoltage,
84873025monitoring functions | Same as RM17TE00 ¦ ,Extreme overvoltage,
84873025monitoring functions | Same as RM17TE00 ¦ ,Extreme asymmetry,
84873025 | Same as RM17TE00 ¦ ,Measurement mode,
84873025internal input resistance | Same as RM17TE00 ¦ ,Internal input resistance,
84873025input terminal | Same as RM17TE00 ¦ ,Input terminal,
84873025Input nominal voltage selection | Same as RM17TE00 ¦ ,Input nominal voltage selection,
84873025permissible input overload | Same as RM17TE00 ¦ ,permissible input overload,
84873025input frequency | Same as RM17TE00 ¦ ,Rated frequency,
84873025input frequency | Same as RM17TE00 ¦ ,Frequency operating range,
84873025setting accuracy of the switching threshold | Same as RM17TE00 ¦ ,Setting accuracy,
84873025repeat accuracy of the switching threshold | Same as RM17TE00 ¦ ,Repeat accuracy (constant parameters),
84873025measurement method | Same as RM17TE00 ¦ ,Measurement method,
84873025switching threshold drift | Same as RM17TE00 ¦ ,Measurement error with supply voltage variation,
84873025switching threshold drift | Same as RM17TE00 ¦ ,Measurement error with temperature variation,
84873025maximum measuring cycle | Same as RM17TE00 ¦ ,Maximum measuring cycles,
84873025measurement range | Same as RM17TE00 ¦ ,Phase lost ,
84873025measurement range | Same as RM17TE00 ¦ ,Phase sequence,
84873025measurement range | Same as RM17TE00 ¦ ,Over / undervoltage (symmetry windows mode),
84873025measurement range | Same as RM17TE00 ¦ ,Over voltage,
84873025measurement range | Same as RM17TE00 ¦ ,Undervoltage ,
84873025measurement range | Same as RM17TE00 ¦ ,Phase asymmetry,
84873025measurement range | Same as RM17TE00 ¦ ,Disconnection of neutral,
84873025measurement range | Same as RM17TE00 ¦ ,Voltage Regeneration,
84873025measurement range | Same as RM17TE00 ¦ ,Extreme undervoltage,
84873025measurement range | Same as RM17TE00 ¦ ,Extreme Overvoltage,
84873025measurement range | Same as RM17TE00 ¦ ,Extreme Asymmetry,
84873025tripping threshold | Same as RM17TE00 ¦ ,Phase cut,
84873025tripping threshold | Same as RM17TE00 ¦ ,Phase sequence,
84873025tripping threshold | Same as RM17TE00 ¦ ,Over / undervoltage (symmetry windows mode),
84873025tripping threshold | Same as RM17TE00 ¦ ,Over voltage,
84873025tripping threshold | Same as RM17TE00 ¦ ,Undervoltage ,
84873025tripping threshold | Same as RM17TE00 ¦ ,Phase asymmetry,
84873025tripping threshold | Same as RM17TE00 ¦ ,Disconnection of neutral,
84873025tripping threshold | Same as RM17TE00 ¦ ,Voltage Regeneration,
84873025tripping threshold | Same as RM17TE00 ¦ ,Extreme undervoltage (Phase loss),
84873025tripping threshold | Same as RM17TE00 ¦ ,Extreme Overvoltage,
84873025tripping threshold | Same as RM17TE00 ¦ ,Extreme Asymmetry,
84873025hysteresis | Same as RM17TE00 ¦ ,Phase cut,
84873025hysteresis | Same as RM17TE00 ¦ ,Phase sequence,
84873025hysteresis | Same as RM17TE00 ¦ ,Over / undervoltage (symmetry windows mode),
84873025hysteresis | Same as RM17TE00 ¦ ,Over voltage,
84873025hysteresis | Same as RM17TE00 ¦ ,Undervoltage ,
84873025hysteresis | Same as RM17TE00 ¦ ,Phase asymmetry,
84873025hysteresis | Same as RM17TE00 ¦ ,Disconnection of neutral,
84873025hysteresis | Same as RM17TE00 ¦ ,Voltage Regeneration,
84873025hysteresis | Same as RM17TE00 ¦ ,Extreme undervoltage (Phase loss),
84873025hysteresis | Same as RM17TE00 ¦ ,Extreme Overvoltage,
84873025hysteresis | Same as RM17TE00 ¦ ,Extreme Asymmetry,
84873025
84873025output type | Same as RM17TE00
84873025output terminal | Same as RM17TE00
84873025output logic | Same as RM17TE00 ¦ ,R1 (11-12-14),
84873025output logic | Same as RM17TE00 ¦ ,R2 (21-22-24),
84873025contacts material | Same as RM17TE00
84873025mechanical durability | Same as RM17TE00 ¦ IEC61810-1
84873025electrical durability | Same as RM17TE00 ¦ IEC60947-4-1,AC-1,
84873025electrical durability | Same as RM17TE00 ¦ IEC60947-4-1,DC-1,
84873025electrical durability | Same as RM17TE00 ¦ IEC60947-5-1,AC-15,
84873025electrical durability | Same as RM17TE00 ¦ IEC60947-5-1,DC-13,
84873025[Ue] rated operational voltage | Same as RM17TE00 ¦ IEC61810-1,Rated switching voltage,
84873025[Ie] rated operational current | Same as RM17TE00 ¦ IEC61810-1,Rated switching current,
84873025maximum switching capacity | Same as RM17TE00 ¦ ,Maximum switching voltage,
84873025maximum switching capacity | Same as RM17TE00 ¦ ,Maximum switching current,
84873025maximum switching capacity | Same as RM17TE00 ¦ ,Maximum switching capacity,
84873025minimum switching capacity | Same as RM17TE00 ¦ IEC60947-5-4,Minimum switching voltage,
84873025minimum switching capacity | Same as RM17TE00 ¦ IEC60947-5-4,Minimum switching current,
84873025minimum switching capacity | Same as RM17TE00 ¦ IEC60947-5-4,Minimum switching capacity,
84873025maximum voltage drop | Same as RM17TE00 ¦ IEC62314,Only for solid state output,
84873025maximum leakage current | Same as RM17TE00 ¦ IEC62314,Only for solid state output,
84873025thermal current | Same as RM17TE00 ¦ IEC60947-5-1
84873025short circuit protection | Same as RM17TE00 ¦ IEC60947-5-1,Relay Output by external fuse,
84873025short circuit protection | Same as RM17TE00 ¦ IEC62314,Solid State Output by external fuse,
84873025
84873025time delay type | Same as RM17TE00 ¦ ,"OFF" delay,
84873025time delay type | Same as RM17TE00 ¦ ,"ON" delay,
84873025time delay type | Same as RM17TE00 ¦ ,Inhibition,
84873025time delay range | Same as RM17TE00 ¦ ,"OFF" delay,
84873025time delay range | Same as RM17TE00 ¦ ,"ON" delay,
84873025time delay range | Same as RM17TE00 ¦ ,Inhibition,
84873025response time | Same as RM17TE00 ¦ ,on crossing the threshold,
84873025response time | Same as RM17TE00
84873025response time | Same as RM17TE00
84873025response time | Same as RM17TE00
84873025response time | Same as RM17TE00
84873025power on delay | Same as RM17TE00
84873025reset time | Same as RM17TE00 ¦ ,through Un power reset,
84873025reset time | Same as RM17TE00 ¦ ,through front panel reset,
84873025reset time | Same as RM17TE00 ¦ ,through input control reset,
84873025setting accuracy of time delay | Same as RM17TE00
84873025repeat accuracy of time delay | Same as RM17TE00
84873025time delay drift | Same as RM17TE00
84873025time delay drift | Same as RM17TE00
84873025
84873025status LED | Same as RM17TE00
84873025local signalling | Same as RM17TE00 ¦ ,Power supply availability,
84873025local signalling | Same as RM17TE00 ¦ ,Power supply not availability,
84873025local signalling | Same as RM17TE00 ¦ ,Timing in-progress,
84873025local signalling | Same as RM17TE00 ¦ ,Output is energized,
84873025local signalling | Same as RM17TE00 ¦ ,Output is de-energized,
84873025local signalling | Same as RM17TE00 ¦ ,Range Setting Changes,
84873025local signalling | Same as RM17TE00 ¦ ,Phase Cut,
84873025local signalling | Same as RM17TE00 ¦ ,Phase Sequence Swap,
84873025local signalling | Same as RM17TE00 ¦ ,Undervoltage <U,
84873025local signalling | Same as RM17TE00 ¦ ,Overvoltage >U,
84873025local signalling | Same as RM17TE00 ¦ ,Phase Asymmetry,
84873025local signalling | Same as RM17TE00 ¦ ,Voltage Regeneration,
84873025local signalling | Same as RM17TE00 ¦ ,Extreme Undervoltage <U (Phase loss),
84873025local signalling | Same as RM17TE00 ¦ ,Extreme Overvoltage >U,
84873025local signalling | Same as RM17TE00 ¦ ,Extreme Phase Asymmetry,
84873025
84873025 | Same as RM17TE00
84873025 | Same as RM17TE00
84873025diagnostic button | Same as RM17TE00
84873025 | Same as RM17TE00
84873025 | Same as RM17TE00
84873025
84873025safety reliability data | Same as RM17TE00 ¦ ,MTTF,
84873025safety reliability data | Same as RM17TE00 ¦ ,B10,
84873025 | Same as RM17TE00 ¦ ,MTTFd,
84873025 | Same as RM17TE00 ¦ ,B10d,
84873025
84873025 | Drawing / Diagram
RM17TU00
RM17TU00standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM17TU00product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TU00marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TU00directives | 2014/35/EU
RM17TU00directives | 2014/30/EU
RM17TU00directives | 2011/65/EU
RM17TU00
RM17TU00 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM17TU00 | Class C ¦ Germanisher Lloyd,Environmental category,
RM17TU00ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM17TU00ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM17TU00relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM17TU00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM17TU00vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM17TU00shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM17TU00bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM17TU00seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM17TU00IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM17TU00IP degree of protection | IP30 ¦ IEC60529,Housing,
RM17TU00IP degree of protection | - ¦ IEC60529,Front Panel,
RM17TU00
RM17TU00width | 17.5 ¦ ,Width,
RM17TU00height | 90 ¦ ,Height,
RM17TU00depth | 72 ¦ ,Depth,
RM17TU00net weight | 80
RM17TU00mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM17TU00mounting support | - ¦ IEC/EN 60715,With socket,
RM17TU00mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM17TU00Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM17TU00Minimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM17TU00connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM17TU00connections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM17TU00connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM17TU00connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM17TU00tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM17TU00cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM17TU00duty time | 1
RM17TU00
RM17TU00electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM17TU00electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM17TU00electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM17TU00electromagnetic compatibility | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM17TU00electromagnetic compatibility | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge,
RM17TU00electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM17TU00electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM17TU00electromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM17TU00electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM17TU00electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM17TU00electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM17TU00electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM17TU00electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM17TU00electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM17TU00electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM17TU00electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM17TU00electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM17TU00electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM17TU00electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM17TU00
RM17TU00pollution degree | 3 ¦ IEC60664-1
RM17TU00overvoltage category | 3 ¦ IEC60664-1
RM17TU00circuit group | L1, L2, L3 ¦ ,Supply,Terminal
RM17TU00circuit group | - ¦ ,Input 1,
RM17TU00circuit group | - ¦ ,Input 2,
RM17TU00circuit group | - ¦ ,Input 3,
RM17TU00circuit group | 11,12,14 ¦ ,Output 1,
RM17TU00circuit group | - ¦ ,Output 2,
RM17TU00 | 208..480 AC ¦ ,Supply,Rated
RM17TU00 | - ¦ ,Input 1,Voltage
RM17TU00 | - ¦ ,Input 2,Spec
RM17TU00 | - ¦ ,Input 3,
RM17TU00 | 250V ¦ ,Output 1,
RM17TU00 | - ¦ ,Output 2,
RM17TU00[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM17TU00[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Output 2,
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM17TU00[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Output 2,
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Output 1 / Output 2,
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM17TU00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM17TU00[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM17TU00[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Output 2,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1 / Output 2,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM17TU00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM17TU00dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM17TU00dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM17TU00dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM17TU00dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM17TU00dielectric strength | - ¦ IEC60255-27,Supply / Output 2,
RM17TU00dielectric strength | - ¦ IEC60255-27,Output 1 / Output 2,
RM17TU00dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM17TU00dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM17TU00dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM17TU00dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM17TU00dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM17TU00dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM17TU00dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM17TU00dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM17TU00dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM17TU00insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM17TU00insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM17TU00insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM17TU00insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM17TU00insulation resistance | - ¦ IEC60255-27,Supply / Output 2,
RM17TU00insulation resistance | - ¦ IEC60255-27,Output 1 / Output 2,
RM17TU00insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM17TU00insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM17TU00insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM17TU00insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM17TU00insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM17TU00insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM17TU00insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM17TU00insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM17TU00insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM17TU00
RM17TU00[Us] rated supply voltage | ~ 3 x 208…3 x 480
RM17TU00supply voltage limits | ~ 3 x 183…3 x 528
RM17TU00polarity | -
RM17TU00supply frequency | 50 / 60
RM17TU00supply frequency | 45…66
RM17TU00power consumption | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz
RM17TU00immunity to microbreaks | 0
RM17TU00supply terminal | L1-L3
RM17TU00on-load factor | 1
RM17TU00release of input voltage | -
RM17TU00
RM17TU00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost ,
RM17TU00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence,
RM17TU00monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17TU00monitoring functions | - ¦ ,Over voltage,
RM17TU00monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Undervoltage ,
RM17TU00monitoring functions | - ¦ ,Phase asymmetry,
RM17TU00monitoring functions | - ¦ ,Disconnection of neutral,
RM17TU00monitoring functions | - ¦ ,Voltage Regeneration,
RM17TU00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage,
RM17TU00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage,
RM17TU00monitoring functions | - ¦ ,Extreme asymmetry,
RM17TU00 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM17TU00internal input resistance | - ¦ ,Internal input resistance,
RM17TU00input terminal | L1-L2-L3 ¦ ,Input terminal,
RM17TU00Input nominal voltage selection | 208, 220, 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM17TU00permissible input overload | - ¦ ,permissible input overload,
RM17TU00input frequency | 50 / 60 ¦ ,Rated frequency,
RM17TU00input frequency | 45…66 ¦ ,Frequency operating range,
RM17TU00setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM17TU00repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM17TU00measurement method | True RMS ¦ ,Measurement method,
RM17TU00switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation,
RM17TU00switching threshold drift | < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM17TU00maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM17TU00measurement range | - ¦ ,Phase lost ,
RM17TU00measurement range | - ¦ ,Phase sequence,
RM17TU00measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17TU00measurement range | - ¦ ,Over voltage,
RM17TU00measurement range | -2…-20 % in the ranges 3 x ~ 380…480 -2…-12 % in the range 3 x ~ 208 -2…-17 % in the range 3 x ~ 220 ¦ ,Undervoltage ,
RM17TU00measurement range | - ¦ ,Phase asymmetry,
RM17TU00measurement range | - ¦ ,Disconnection of neutral,
RM17TU00measurement range | - ¦ ,Voltage Regeneration,
RM17TU00measurement range | - ¦ ,Extreme undervoltage,
RM17TU00measurement range | - ¦ ,Extreme Overvoltage,
RM17TU00measurement range | - ¦ ,Extreme Asymmetry,
RM17TU00tripping threshold | 1 or more phase cut ¦ ,Phase cut,
RM17TU00tripping threshold | Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence,
RM17TU00tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17TU00tripping threshold | - ¦ ,Over voltage,
RM17TU00tripping threshold | Adjustable 2%...20% of selected Un ¦ ,Undervoltage ,
RM17TU00tripping threshold | - ¦ ,Phase asymmetry,
RM17TU00tripping threshold | - ¦ ,Disconnection of neutral,
RM17TU00tripping threshold | - ¦ ,Voltage Regeneration,
RM17TU00tripping threshold | 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM17TU00tripping threshold | Internal design spec: 543V +/- 5% ¦ ,Extreme Overvoltage,
RM17TU00tripping threshold | - ¦ ,Extreme Asymmetry,
RM17TU00hysteresis | All phase cut recover ¦ ,Phase cut,
RM17TU00hysteresis | Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence,
RM17TU00hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17TU00hysteresis | - ¦ ,Over voltage,
RM17TU00hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage ,
RM17TU00hysteresis | - ¦ ,Phase asymmetry,
RM17TU00hysteresis | - ¦ ,Disconnection of neutral,
RM17TU00hysteresis | - ¦ ,Voltage Regeneration,
RM17TU00hysteresis | All phases > 195V Internal design spec: All phases >180V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM17TU00hysteresis | Internal design spec: All phases <533V +/- 5% ¦ ,Extreme Overvoltage,
RM17TU00hysteresis | - ¦ ,Extreme Asymmetry,
RM17TU00
RM17TU00output type | 1 x C/O relay contacts
RM17TU00output terminal | 11-12-14
RM17TU00output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM17TU00output logic | - ¦ ,R2 (21-22-24),
RM17TU00contacts material | Cadmium free
RM17TU00mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM17TU00electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM17TU00electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM17TU00electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM17TU00electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM17TU00[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM17TU00[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM17TU00maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM17TU00maximum switching capacity | 5A ¦ ,Maximum switching current,
RM17TU00maximum switching capacity | - ¦ ,Maximum switching capacity,
RM17TU00minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM17TU00minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM17TU00minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM17TU00maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM17TU00maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM17TU00thermal current | 5A ¦ IEC60947-5-1
RM17TU00short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse,
RM17TU00short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM17TU00
RM17TU00time delay type | Yes ¦ ,"OFF" delay,
RM17TU00time delay type | - ¦ ,"ON" delay,
RM17TU00time delay type | - ¦ ,Inhibition,
RM17TU00time delay range | Adjustable 0.1…10 ¦ ,"OFF" delay,
RM17TU00time delay range | - ¦ ,"ON" delay,
RM17TU00time delay range | - ¦ ,Inhibition,
RM17TU00response time | 0
RM17TU00response time | -
RM17TU00response time | -
RM17TU00response time | -
RM17TU00response time | -
RM17TU00power on delay | 0
RM17TU00reset time | 0
RM17TU00reset time | - ¦ ,through front panel reset,
RM17TU00reset time | - ¦ ,through input control reset,
RM17TU00setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM17TU00repeat accuracy of time delay | +/- 3%
RM17TU00time delay drift | -
RM17TU00time delay drift | -
RM17TU00
RM17TU00status LED | Un (Green) R (Amber)
RM17TU00local signalling | Un - ON ¦ ,Power supply availability,
RM17TU00local signalling | Un - OFF ¦ ,Power supply not availability,
RM17TU00local signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM17TU00local signalling | R - ON ¦ ,Output is energized,
RM17TU00local signalling | R - OFF ¦ ,Output is de-energized,
RM17TU00local signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM17TU00local signalling | - ¦ ,Phase Cut,
RM17TU00local signalling | - ¦ ,Phase Sequence Swap,
RM17TU00local signalling | - ¦ ,Undervoltage <U,
RM17TU00local signalling | - ¦ ,Overvoltage >U,
RM17TU00local signalling | - ¦ ,Phase Asymmetry,
RM17TU00local signalling | - ¦ ,Voltage Regeneration,
RM17TU00local signalling | - ¦ ,Extreme Undervoltage <U (Phase loss),
RM17TU00local signalling | - ¦ ,Extreme Overvoltage >U,
RM17TU00local signalling | - ¦ ,Extreme Phase Asymmetry,
RM17TU00
RM17TU00 | Yes
RM17TU00 | -
RM17TU00diagnostic button | -
RM17TU00 | -
RM17TU00 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM17TU00
RM17TU00safety reliability data | 4,400,000 hours ¦ ,MTTF,
RM17TU00safety reliability data | 470,000 hours ¦ ,B10,
RM17TU00 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM17TU00 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM17TU00
RM17TU00 | Drawing / Diagram
84873023
84873023standards | Same as RM17TU00
84873023product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873023marking | UL, CSA, GL, CCC, CE, China ROHS
84873023directives | Same as RM17TU00
84873023directives | Same as RM17TU00
84873023directives | Same as RM17TU00
84873023
84873023 | Same as RM17TU00 ¦ IEC60721-3-3,Climatic category,
84873023 | Same as RM17TU00 ¦ Germanisher Lloyd,Environmental category,
84873023ambient air temperature for storage | Same as RM17TU00 ¦ ,Storage,
84873023ambient air temperature for operation | Same as RM17TU00 ¦ ,Operation,
84873023relative humidity | Same as RM17TU00 ¦ IEC60068-2-30,Damp heat,XX
84873023 | Same as RM17TU00 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873023vibration resistance | Same as RM17TU00 ¦ IEC60068-2-6
84873023shock resistance | Same as RM17TU00 ¦ IEC60068-2-27
84873023bump resistance | Same as RM17TU00 ¦ IEC60068-2-29
84873023seismic resistance | Same as RM17TU00 ¦ IEC60068-3-3
84873023IP degree of protection | Same as RM17TU00 ¦ IEC60529,Terminal Block,
84873023IP degree of protection | Same as RM17TU00 ¦ IEC60529,Housing,
84873023IP degree of protection | Same as RM17TU00 ¦ IEC60529,Front Panel,
84873023
84873023width | Same as RM17TU00 ¦ ,Width,
84873023height | Same as RM17TU00 ¦ ,Height,
84873023depth | Same as RM17TU00 ¦ ,Depth,
84873023net weight | Same as RM17TU00
84873023mounting support | Same as RM17TU00 ¦ IEC/EN 60715,Without socket,
84873023mounting support | Same as RM17TU00 ¦ IEC/EN 60715,With socket,
84873023mounting position | Same as RM17TU00 ¦ ,In relation to normal vertical mounting plane,
84873023Minimum distance to adjacent devices | Same as RM17TU00 ¦ ,Horizontal,
84873023Minimum distance to adjacent devices | Same as RM17TU00 ¦ ,Vertical,
84873023connections - terminals | Same as RM17TU00 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873023connections - terminals | Same as RM17TU00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873023connections - terminals | Same as RM17TU00 ¦ IEC60947-1,Solid cable (spring terminal),
84873023connections - terminals | Same as RM17TU00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873023tightening torque | Same as RM17TU00 ¦ IEC60947-1,Tightening torque,
84873023cable stripping length | Same as RM17TU00 ¦ ,Cable stripping length,
84873023duty time | Same as RM17TU00
84873023
84873023electromagnetic compatibility | Same as RM17TU00 ¦ ,Generic immunity standard,
84873023electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-2,Electrostatic discharge,
84873023electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873023electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-4,Fast transient / burst,
84873023electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-5,Surge,
84873023electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-6,Conducted RF disturbance,
84873023electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-8,Power frequency magnetic field,
84873023electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873023electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873023electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-29,DC voltage interruption,
84873023electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-13,Low frequency harmonics,
84873023electromagnetic compatibility | Same as RM17TU00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873023electromagnetic compatibility | Same as RM17TU00 ¦ ,Generic emission standard,
84873023electromagnetic compatibility | Same as RM17TU00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873023electromagnetic compatibility | Same as RM17TU00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873023electromagnetic compatibility | Same as RM17TU00 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873023electromagnetic compatibility | Same as RM17TU00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873023electromagnetic compatibility | Same as RM17TU00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873023electromagnetic compatibility | Same as RM17TU00 ¦ Germanisher Lloyd,Conducted emission,
84873023
84873023pollution degree | Same as RM17TU00 ¦ IEC60664-1
84873023overvoltage category | Same as RM17TU00 ¦ IEC60664-1
84873023circuit group | Same as RM17TU00 ¦ ,Supply,Terminal
84873023circuit group | Same as RM17TU00 ¦ ,Input 1,
84873023circuit group | Same as RM17TU00 ¦ ,Input 2,
84873023circuit group | Same as RM17TU00 ¦ ,Input 3,
84873023circuit group | Same as RM17TU00 ¦ ,Output 1,
84873023circuit group | Same as RM17TU00 ¦ ,Output 2,
84873023 | Same as RM17TU00 ¦ ,Supply,Rated
84873023 | Same as RM17TU00 ¦ ,Input 1,Voltage
84873023 | Same as RM17TU00 ¦ ,Input 2,Spec
84873023 | Same as RM17TU00 ¦ ,Input 3,
84873023 | Same as RM17TU00 ¦ ,Output 1,
84873023 | Same as RM17TU00 ¦ ,Output 2,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Supply,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 2,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 3,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Output 1,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Output 2,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Output 1,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Output 2,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Output 1 / Output 2,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1 / Output 1,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1 / Output 2,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 2 / Output 1,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 2 / Output 2,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 3 / Output 1,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 3 / Output 2,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1 / Input 2,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 2 / Input 3,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1 / Input 3,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Supply,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 2,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 3,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Output 1,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Output 2,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Output 1,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Output 2,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Output 1 / Output 2,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1 / Output 1,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1 / Output 2,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 2 / Output 1,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 2 / Output 2,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 3 / Output 1,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 3 / Output 2,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1 / Input 2,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 2 / Input 3,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1 / Input 3,
84873023dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Supply / Input 1,
84873023dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Supply / Input 2,
84873023dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Supply / Input 3,
84873023dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Supply / Output 1,
84873023dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Supply / Output 2,
84873023dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Output 1 / Output 2,
84873023dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 1 / Output 1,
84873023dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 1 / Output 2,
84873023dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 2 / Output 1,
84873023dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 2 / Output 2,
84873023dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 3 / Output 1,
84873023dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 3 / Output 2,
84873023dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 1 / Input 2,
84873023dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 2 / Input 3,
84873023dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 1 / Input 3,
84873023insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Supply / Input 1,
84873023insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Supply / Input 2,
84873023insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Supply / Input 3,
84873023insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Supply / Output 1,
84873023insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Supply / Output 2,
84873023insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Output 1 / Output 2,
84873023insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 1 / Output 1,
84873023insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 1 / Output 2,
84873023insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 2 / Output 1,
84873023insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 2 / Output 2,
84873023insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 3 / Output 1,
84873023insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 3 / Output 2,
84873023insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 1 / Input 2,
84873023insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 2 / Input 3,
84873023insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 1 / Input 3,
84873023
84873023[Us] rated supply voltage | Same as RM17TU00
84873023supply voltage limits | Same as RM17TU00
84873023polarity | Same as RM17TU00
84873023supply frequency | Same as RM17TU00
84873023supply frequency | Same as RM17TU00
84873023power consumption | Same as RM17TU00
84873023immunity to microbreaks | Same as RM17TU00
84873023supply terminal | Same as RM17TU00
84873023on-load factor | Same as RM17TU00
84873023release of input voltage | Same as RM17TU00
84873023
84873023monitoring functions | Same as RM17TU00 ¦ ,Phase lost ,
84873023monitoring functions | Same as RM17TU00 ¦ ,Phase sequence,
84873023monitoring functions | Same as RM17TU00 ¦ ,Over / undervoltage (symmetry windows mode),
84873023monitoring functions | Same as RM17TU00 ¦ ,Over voltage,
84873023monitoring functions | Same as RM17TU00 ¦ ,Undervoltage ,
84873023monitoring functions | Same as RM17TU00 ¦ ,Phase asymmetry,
84873023monitoring functions | Same as RM17TU00 ¦ ,Disconnection of neutral,
84873023monitoring functions | Same as RM17TU00 ¦ ,Voltage Regeneration,
84873023monitoring functions | Same as RM17TU00 ¦ ,Extreme undervoltage,
84873023monitoring functions | Same as RM17TU00 ¦ ,Extreme overvoltage,
84873023monitoring functions | Same as RM17TU00 ¦ ,Extreme asymmetry,
84873023 | Same as RM17TU00 ¦ ,Measurement mode,
84873023internal input resistance | Same as RM17TU00 ¦ ,Internal input resistance,
84873023input terminal | Same as RM17TU00 ¦ ,Input terminal,
84873023Input nominal voltage selection | Same as RM17TU00 ¦ ,Input nominal voltage selection,
84873023permissible input overload | Same as RM17TU00 ¦ ,permissible input overload,
84873023input frequency | Same as RM17TU00 ¦ ,Rated frequency,
84873023input frequency | Same as RM17TU00 ¦ ,Frequency operating range,
84873023setting accuracy of the switching threshold | Same as RM17TU00 ¦ ,Setting accuracy,
84873023repeat accuracy of the switching threshold | Same as RM17TU00 ¦ ,Repeat accuracy (constant parameters),
84873023measurement method | Same as RM17TU00 ¦ ,Measurement method,
84873023switching threshold drift | Same as RM17TU00 ¦ ,Measurement error with supply voltage variation,
84873023switching threshold drift | Same as RM17TU00 ¦ ,Measurement error with temperature variation,
84873023maximum measuring cycle | Same as RM17TU00 ¦ ,Maximum measuring cycles,
84873023measurement range | Same as RM17TU00 ¦ ,Phase lost ,
84873023measurement range | Same as RM17TU00 ¦ ,Phase sequence,
84873023measurement range | Same as RM17TU00 ¦ ,Over / undervoltage (symmetry windows mode),
84873023measurement range | Same as RM17TU00 ¦ ,Over voltage,
84873023measurement range | Same as RM17TU00 ¦ ,Undervoltage ,
84873023measurement range | Same as RM17TU00 ¦ ,Phase asymmetry,
84873023measurement range | Same as RM17TU00 ¦ ,Disconnection of neutral,
84873023measurement range | Same as RM17TU00 ¦ ,Voltage Regeneration,
84873023measurement range | Same as RM17TU00 ¦ ,Extreme undervoltage,
84873023measurement range | Same as RM17TU00 ¦ ,Extreme Overvoltage,
84873023measurement range | Same as RM17TU00 ¦ ,Extreme Asymmetry,
84873023tripping threshold | Same as RM17TU00 ¦ ,Phase cut,
84873023tripping threshold | Same as RM17TU00 ¦ ,Phase sequence,
84873023tripping threshold | Same as RM17TU00 ¦ ,Over / undervoltage (symmetry windows mode),
84873023tripping threshold | Same as RM17TU00 ¦ ,Over voltage,
84873023tripping threshold | Same as RM17TU00 ¦ ,Undervoltage ,
84873023tripping threshold | Same as RM17TU00 ¦ ,Phase asymmetry,
84873023tripping threshold | Same as RM17TU00 ¦ ,Disconnection of neutral,
84873023tripping threshold | Same as RM17TU00 ¦ ,Voltage Regeneration,
84873023tripping threshold | Same as RM17TU00 ¦ ,Extreme undervoltage (Phase loss),
84873023tripping threshold | Same as RM17TU00 ¦ ,Extreme Overvoltage,
84873023tripping threshold | Same as RM17TU00 ¦ ,Extreme Asymmetry,
84873023hysteresis | Same as RM17TU00 ¦ ,Phase cut,
84873023hysteresis | Same as RM17TU00 ¦ ,Phase sequence,
84873023hysteresis | Same as RM17TU00 ¦ ,Over / undervoltage (symmetry windows mode),
84873023hysteresis | Same as RM17TU00 ¦ ,Over voltage,
84873023hysteresis | Same as RM17TU00 ¦ ,Undervoltage ,
84873023hysteresis | Same as RM17TU00 ¦ ,Phase asymmetry,
84873023hysteresis | Same as RM17TU00 ¦ ,Disconnection of neutral,
84873023hysteresis | Same as RM17TU00 ¦ ,Voltage Regeneration,
84873023hysteresis | Same as RM17TU00 ¦ ,Extreme undervoltage (Phase loss),
84873023hysteresis | Same as RM17TU00 ¦ ,Extreme Overvoltage,
84873023hysteresis | Same as RM17TU00 ¦ ,Extreme Asymmetry,
84873023
84873023output type | Same as RM17TU00
84873023output terminal | Same as RM17TU00
84873023output logic | Same as RM17TU00 ¦ ,R1 (11-12-14),
84873023output logic | Same as RM17TU00 ¦ ,R2 (21-22-24),
84873023contacts material | Same as RM17TU00
84873023mechanical durability | Same as RM17TU00 ¦ IEC61810-1
84873023electrical durability | Same as RM17TU00 ¦ IEC60947-4-1,AC-1,
84873023electrical durability | Same as RM17TU00 ¦ IEC60947-4-1,DC-1,
84873023electrical durability | Same as RM17TU00 ¦ IEC60947-5-1,AC-15,
84873023electrical durability | Same as RM17TU00 ¦ IEC60947-5-1,DC-13,
84873023[Ue] rated operational voltage | Same as RM17TU00 ¦ IEC61810-1,Rated switching voltage,
84873023[Ie] rated operational current | Same as RM17TU00 ¦ IEC61810-1,Rated switching current,
84873023maximum switching capacity | Same as RM17TU00 ¦ ,Maximum switching voltage,
84873023maximum switching capacity | Same as RM17TU00 ¦ ,Maximum switching current,
84873023maximum switching capacity | Same as RM17TU00 ¦ ,Maximum switching capacity,
84873023minimum switching capacity | Same as RM17TU00 ¦ IEC60947-5-4,Minimum switching voltage,
84873023minimum switching capacity | Same as RM17TU00 ¦ IEC60947-5-4,Minimum switching current,
84873023minimum switching capacity | Same as RM17TU00 ¦ IEC60947-5-4,Minimum switching capacity,
84873023maximum voltage drop | Same as RM17TU00 ¦ IEC62314,Only for solid state output,
84873023maximum leakage current | Same as RM17TU00 ¦ IEC62314,Only for solid state output,
84873023thermal current | Same as RM17TU00 ¦ IEC60947-5-1
84873023short circuit protection | Same as RM17TU00 ¦ IEC60947-5-1,Relay Output by external fuse,
84873023short circuit protection | Same as RM17TU00 ¦ IEC62314,Solid State Output by external fuse,
84873023
84873023time delay type | Same as RM17TU00 ¦ ,"OFF" delay,
84873023time delay type | Same as RM17TU00 ¦ ,"ON" delay,
84873023time delay type | Same as RM17TU00 ¦ ,Inhibition,
84873023time delay range | Same as RM17TU00 ¦ ,"OFF" delay,
84873023time delay range | Same as RM17TU00 ¦ ,"ON" delay,
84873023time delay range | Same as RM17TU00 ¦ ,Inhibition,
84873023response time | Same as RM17TU00 ¦ ,on crossing the threshold,
84873023response time | Same as RM17TU00
84873023response time | Same as RM17TU00
84873023response time | Same as RM17TU00
84873023response time | Same as RM17TU00
84873023power on delay | Same as RM17TU00
84873023reset time | Same as RM17TU00 ¦ ,through Un power reset,
84873023reset time | Same as RM17TU00 ¦ ,through front panel reset,
84873023reset time | Same as RM17TU00 ¦ ,through input control reset,
84873023setting accuracy of time delay | Same as RM17TU00
84873023repeat accuracy of time delay | Same as RM17TU00
84873023time delay drift | Same as RM17TU00
84873023time delay drift | Same as RM17TU00
84873023
84873023status LED | Same as RM17TU00
84873023local signalling | Same as RM17TU00 ¦ ,Power supply availability,
84873023local signalling | Same as RM17TU00 ¦ ,Power supply not availability,
84873023local signalling | Same as RM17TU00 ¦ ,Timing in-progress,
84873023local signalling | Same as RM17TU00 ¦ ,Output is energized,
84873023local signalling | Same as RM17TU00 ¦ ,Output is de-energized,
84873023local signalling | Same as RM17TU00 ¦ ,Range Setting Changes,
84873023local signalling | Same as RM17TU00 ¦ ,Phase Cut,
84873023local signalling | Same as RM17TU00 ¦ ,Phase Sequence Swap,
84873023local signalling | Same as RM17TU00 ¦ ,Undervoltage <U,
84873023local signalling | Same as RM17TU00 ¦ ,Overvoltage >U,
84873023local signalling | Same as RM17TU00 ¦ ,Phase Asymmetry,
84873023local signalling | Same as RM17TU00 ¦ ,Voltage Regeneration,
84873023local signalling | Same as RM17TU00 ¦ ,Extreme Undervoltage <U (Phase loss),
84873023local signalling | Same as RM17TU00 ¦ ,Extreme Overvoltage >U,
84873023local signalling | Same as RM17TU00 ¦ ,Extreme Phase Asymmetry,
84873023
84873023 | Same as RM17TU00
84873023 | Same as RM17TU00
84873023diagnostic button | Same as RM17TU00
84873023 | Same as RM17TU00
84873023 | Same as RM17TU00
84873023
84873023safety reliability data | Same as RM17TU00 ¦ ,MTTF,
84873023safety reliability data | Same as RM17TU00 ¦ ,B10,
84873023 | Same as RM17TU00 ¦ ,MTTFd,
84873023 | Same as RM17TU00 ¦ ,B10d,
84873023
84873023 | Drawing / Diagram
84873805
84873805standards | Same as RM17TU00
84873805product certifications | UL, CSA, CE, China ROHS
84873805marking | UL, CSA, CE, China ROHS
84873805directives | Same as RM17TU00
84873805directives | Same as RM17TU00
84873805directives | Same as RM17TU00
84873805
84873805 | Same as RM17TU00 ¦ IEC60721-3-3,Climatic category,
84873805 | Same as RM17TU00 ¦ Germanisher Lloyd,Environmental category,
84873805ambient air temperature for storage | Same as RM17TU00 ¦ ,Storage,
84873805ambient air temperature for operation | Same as RM17TU00 ¦ ,Operation,
84873805relative humidity | Same as RM17TU00 ¦ IEC60068-2-30,Damp heat,XX
84873805 | Same as RM17TU00 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873805vibration resistance | Same as RM17TU00 ¦ IEC60068-2-6
84873805shock resistance | Same as RM17TU00 ¦ IEC60068-2-27
84873805bump resistance | Same as RM17TU00 ¦ IEC60068-2-29
84873805seismic resistance | Same as RM17TU00 ¦ IEC60068-3-3
84873805IP degree of protection | Same as RM17TU00 ¦ IEC60529,Terminal Block,
84873805IP degree of protection | Same as RM17TU00 ¦ IEC60529,Housing,
84873805IP degree of protection | Same as RM17TU00 ¦ IEC60529,Front Panel,
84873805
84873805width | Same as RM17TU00 ¦ ,Width,
84873805height | Same as RM17TU00 ¦ ,Height,
84873805depth | Same as RM17TU00 ¦ ,Depth,
84873805net weight | Same as RM17TU00
84873805mounting support | Same as RM17TU00 ¦ IEC/EN 60715,Without socket,
84873805mounting support | Same as RM17TU00 ¦ IEC/EN 60715,With socket,
84873805mounting position | Same as RM17TU00 ¦ ,In relation to normal vertical mounting plane,
84873805Minimum distance to adjacent devices | Same as RM17TU00 ¦ ,Horizontal,
84873805Minimum distance to adjacent devices | Same as RM17TU00 ¦ ,Vertical,
84873805connections - terminals | Same as RM17TU00 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873805connections - terminals | Same as RM17TU00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873805connections - terminals | Same as RM17TU00 ¦ IEC60947-1,Solid cable (spring terminal),
84873805connections - terminals | Same as RM17TU00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873805tightening torque | Same as RM17TU00 ¦ IEC60947-1,Tightening torque,
84873805cable stripping length | Same as RM17TU00 ¦ ,Cable stripping length,
84873805duty time | Same as RM17TU00
84873805
84873805electromagnetic compatibility | Same as RM17TU00 ¦ ,Generic immunity standard,
84873805electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-2,Electrostatic discharge,
84873805electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873805electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-4,Fast transient / burst,
84873805electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-5,Surge,
84873805electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-6,Conducted RF disturbance,
84873805electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-8,Power frequency magnetic field,
84873805electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873805electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873805electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-29,DC voltage interruption,
84873805electromagnetic compatibility | Same as RM17TU00 ¦ IEC61000-4-13,Low frequency harmonics,
84873805electromagnetic compatibility | Same as RM17TU00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873805electromagnetic compatibility | Same as RM17TU00 ¦ ,Generic emission standard,
84873805electromagnetic compatibility | Same as RM17TU00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873805electromagnetic compatibility | Same as RM17TU00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873805electromagnetic compatibility | Same as RM17TU00 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873805electromagnetic compatibility | Same as RM17TU00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873805electromagnetic compatibility | Same as RM17TU00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873805electromagnetic compatibility | Same as RM17TU00 ¦ Germanisher Lloyd,Conducted emission,
84873805
84873805pollution degree | Same as RM17TU00 ¦ IEC60664-1
84873805overvoltage category | Same as RM17TU00 ¦ IEC60664-1
84873805circuit group | Same as RM17TU00 ¦ ,Supply,Terminal
84873805circuit group | Same as RM17TU00 ¦ ,Input 1,
84873805circuit group | Same as RM17TU00 ¦ ,Input 2,
84873805circuit group | Same as RM17TU00 ¦ ,Input 3,
84873805circuit group | Same as RM17TU00 ¦ ,Output 1,
84873805circuit group | Same as RM17TU00 ¦ ,Output 2,
84873805 | Same as RM17TU00 ¦ ,Supply,Rated
84873805 | Same as RM17TU00 ¦ ,Input 1,Voltage
84873805 | Same as RM17TU00 ¦ ,Input 2,Spec
84873805 | Same as RM17TU00 ¦ ,Input 3,
84873805 | Same as RM17TU00 ¦ ,Output 1,
84873805 | Same as RM17TU00 ¦ ,Output 2,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Supply,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 2,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 3,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Output 1,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Output 2,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Output 1,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Output 2,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Output 1 / Output 2,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1 / Output 1,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1 / Output 2,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 2 / Output 1,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 2 / Output 2,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 3 / Output 1,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 3 / Output 2,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1 / Input 2,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 2 / Input 3,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1 / Input 3,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Supply,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 2,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 3,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Output 1,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Output 2,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Output 1,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Supply / Output 2,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Output 1 / Output 2,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1 / Output 1,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1 / Output 2,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 2 / Output 1,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 2 / Output 2,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 3 / Output 1,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 3 / Output 2,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1 / Input 2,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 2 / Input 3,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Input 1 / Input 3,
84873805dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Supply / Input 1,
84873805dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Supply / Input 2,
84873805dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Supply / Input 3,
84873805dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Supply / Output 1,
84873805dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Supply / Output 2,
84873805dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Output 1 / Output 2,
84873805dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 1 / Output 1,
84873805dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 1 / Output 2,
84873805dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 2 / Output 1,
84873805dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 2 / Output 2,
84873805dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 3 / Output 1,
84873805dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 3 / Output 2,
84873805dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 1 / Input 2,
84873805dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 2 / Input 3,
84873805dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Input 1 / Input 3,
84873805insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Supply / Input 1,
84873805insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Supply / Input 2,
84873805insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Supply / Input 3,
84873805insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Supply / Output 1,
84873805insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Supply / Output 2,
84873805insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Output 1 / Output 2,
84873805insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 1 / Output 1,
84873805insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 1 / Output 2,
84873805insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 2 / Output 1,
84873805insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 2 / Output 2,
84873805insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 3 / Output 1,
84873805insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 3 / Output 2,
84873805insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 1 / Input 2,
84873805insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 2 / Input 3,
84873805insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Input 1 / Input 3,
84873805
84873805[Us] rated supply voltage | Same as RM17TU00
84873805supply voltage limits | Same as RM17TU00
84873805polarity | Same as RM17TU00
84873805supply frequency | Same as RM17TU00
84873805supply frequency | Same as RM17TU00
84873805power consumption | Same as RM17TU00
84873805immunity to microbreaks | Same as RM17TU00
84873805supply terminal | Same as RM17TU00
84873805on-load factor | Same as RM17TU00
84873805release of input voltage | Same as RM17TU00
84873805
84873805monitoring functions | Same as RM17TU00 ¦ ,Phase lost ,
84873805monitoring functions | Same as RM17TU00 ¦ ,Phase sequence,
84873805monitoring functions | Same as RM17TU00 ¦ ,Over / undervoltage (symmetry windows mode),
84873805monitoring functions | Same as RM17TU00 ¦ ,Over voltage,
84873805monitoring functions | Same as RM17TU00 ¦ ,Undervoltage ,
84873805monitoring functions | Same as RM17TU00 ¦ ,Phase asymmetry,
84873805monitoring functions | Same as RM17TU00 ¦ ,Disconnection of neutral,
84873805monitoring functions | Same as RM17TU00 ¦ ,Voltage Regeneration,
84873805monitoring functions | Same as RM17TU00 ¦ ,Extreme undervoltage,
84873805monitoring functions | Same as RM17TU00 ¦ ,Extreme overvoltage,
84873805monitoring functions | Same as RM17TU00 ¦ ,Extreme asymmetry,
84873805 | Same as RM17TU00 ¦ ,Measurement mode,
84873805internal input resistance | Same as RM17TU00 ¦ ,Internal input resistance,
84873805input terminal | Same as RM17TU00 ¦ ,Input terminal,
84873805Input nominal voltage selection | - ¦ ,Input nominal voltage selection,
84873805permissible input overload | Same as RM17TU00 ¦ ,permissible input overload,
84873805input frequency | Same as RM17TU00 ¦ ,Rated frequency,
84873805input frequency | Same as RM17TU00 ¦ ,Frequency operating range,
84873805setting accuracy of the switching threshold | Same as RM17TU00 ¦ ,Setting accuracy,
84873805repeat accuracy of the switching threshold | Same as RM17TU00 ¦ ,Repeat accuracy (constant parameters),
84873805measurement method | Same as RM17TU00 ¦ ,Measurement method,
84873805switching threshold drift | Same as RM17TU00 ¦ ,Measurement error with supply voltage variation,
84873805switching threshold drift | Same as RM17TU00 ¦ ,Measurement error with temperature variation,
84873805maximum measuring cycle | Same as RM17TU00 ¦ ,Maximum measuring cycles,
84873805measurement range | Same as RM17TU00 ¦ ,Phase lost ,
84873805measurement range | Same as RM17TU00 ¦ ,Phase sequence,
84873805measurement range | Same as RM17TU00 ¦ ,Over / undervoltage (symmetry windows mode),
84873805measurement range | Same as RM17TU00 ¦ ,Over voltage,
84873805measurement range | Fixed 400 ¦ ,Undervoltage ,
84873805measurement range | Same as RM17TU00 ¦ ,Phase asymmetry,
84873805measurement range | Same as RM17TU00 ¦ ,Disconnection of neutral,
84873805measurement range | Same as RM17TU00 ¦ ,Voltage Regeneration,
84873805measurement range | Same as RM17TU00 ¦ ,Extreme undervoltage,
84873805measurement range | Same as RM17TU00 ¦ ,Extreme Overvoltage,
84873805measurement range | Same as RM17TU00 ¦ ,Extreme Asymmetry,
84873805tripping threshold | Same as RM17TU00 ¦ ,Phase cut,
84873805tripping threshold | Same as RM17TU00 ¦ ,Phase sequence,
84873805tripping threshold | Same as RM17TU00 ¦ ,Over / undervoltage (symmetry windows mode),
84873805tripping threshold | Same as RM17TU00 ¦ ,Over voltage,
84873805tripping threshold | Fixed -10% of Un ¦ ,Undervoltage ,
84873805tripping threshold | Same as RM17TU00 ¦ ,Phase asymmetry,
84873805tripping threshold | Same as RM17TU00 ¦ ,Disconnection of neutral,
84873805tripping threshold | Same as RM17TU00 ¦ ,Voltage Regeneration,
84873805tripping threshold | Same as RM17TU00 ¦ ,Extreme undervoltage (Phase loss),
84873805tripping threshold | Same as RM17TU00 ¦ ,Extreme Overvoltage,
84873805tripping threshold | Same as RM17TU00 ¦ ,Extreme Asymmetry,
84873805hysteresis | Same as RM17TU00 ¦ ,Phase cut,
84873805hysteresis | Same as RM17TU00 ¦ ,Phase sequence,
84873805hysteresis | Same as RM17TU00 ¦ ,Over / undervoltage (symmetry windows mode),
84873805hysteresis | Same as RM17TU00 ¦ ,Over voltage,
84873805hysteresis | Fixed 5% of selected Un Internal design spec: 5% +/- 1.5% ¦ ,Undervoltage ,
84873805hysteresis | Same as RM17TU00 ¦ ,Phase asymmetry,
84873805hysteresis | Same as RM17TU00 ¦ ,Disconnection of neutral,
84873805hysteresis | Same as RM17TU00 ¦ ,Voltage Regeneration,
84873805hysteresis | Same as RM17TU00 ¦ ,Extreme undervoltage (Phase loss),
84873805hysteresis | Same as RM17TU00 ¦ ,Extreme Overvoltage,
84873805hysteresis | Same as RM17TU00 ¦ ,Extreme Asymmetry,
84873805
84873805output type | Same as RM17TU00
84873805output terminal | Same as RM17TU00
84873805output logic | Same as RM17TU00 ¦ ,R1 (11-12-14),
84873805output logic | Same as RM17TU00 ¦ ,R2 (21-22-24),
84873805contacts material | Same as RM17TU00
84873805mechanical durability | Same as RM17TU00 ¦ IEC61810-1
84873805electrical durability | Same as RM17TU00 ¦ IEC60947-4-1,AC-1,
84873805electrical durability | Same as RM17TU00 ¦ IEC60947-4-1,DC-1,
84873805electrical durability | Same as RM17TU00 ¦ IEC60947-5-1,AC-15,
84873805electrical durability | Same as RM17TU00 ¦ IEC60947-5-1,DC-13,
84873805[Ue] rated operational voltage | Same as RM17TU00 ¦ IEC61810-1,Rated switching voltage,
84873805[Ie] rated operational current | Same as RM17TU00 ¦ IEC61810-1,Rated switching current,
84873805maximum switching capacity | Same as RM17TU00 ¦ ,Maximum switching voltage,
84873805maximum switching capacity | Same as RM17TU00 ¦ ,Maximum switching current,
84873805maximum switching capacity | Same as RM17TU00 ¦ ,Maximum switching capacity,
84873805minimum switching capacity | Same as RM17TU00 ¦ IEC60947-5-4,Minimum switching voltage,
84873805minimum switching capacity | Same as RM17TU00 ¦ IEC60947-5-4,Minimum switching current,
84873805minimum switching capacity | Same as RM17TU00 ¦ IEC60947-5-4,Minimum switching capacity,
84873805maximum voltage drop | Same as RM17TU00 ¦ IEC62314,Only for solid state output,
84873805maximum leakage current | Same as RM17TU00 ¦ IEC62314,Only for solid state output,
84873805thermal current | Same as RM17TU00 ¦ IEC60947-5-1
84873805short circuit protection | Same as RM17TU00 ¦ IEC60947-5-1,Relay Output by external fuse,
84873805short circuit protection | Same as RM17TU00 ¦ IEC62314,Solid State Output by external fuse,
84873805
84873805time delay type | Same as RM17TU00 ¦ ,"OFF" delay,
84873805time delay type | Same as RM17TU00 ¦ ,"ON" delay,
84873805time delay type | Same as RM17TU00 ¦ ,Inhibition,
84873805time delay range | Fixed 3.5s +/- 5% ¦ ,"OFF" delay,
84873805time delay range | Same as RM17TU00 ¦ ,"ON" delay,
84873805time delay range | Same as RM17TU00 ¦ ,Inhibition,
84873805response time | Same as RM17TU00 ¦ ,on crossing the threshold,
84873805response time | Same as RM17TU00
84873805response time | Same as RM17TU00
84873805response time | Same as RM17TU00
84873805response time | Same as RM17TU00
84873805power on delay | Same as RM17TU00
84873805reset time | Same as RM17TU00 ¦ ,through Un power reset,
84873805reset time | Same as RM17TU00 ¦ ,through front panel reset,
84873805reset time | Same as RM17TU00 ¦ ,through input control reset,
84873805setting accuracy of time delay | Same as RM17TU00
84873805repeat accuracy of time delay | Same as RM17TU00
84873805time delay drift | Same as RM17TU00
84873805time delay drift | Same as RM17TU00
84873805
84873805status LED | R (Amber)
84873805local signalling | - ¦ ,Power supply availability,
84873805local signalling | - ¦ ,Power supply not availability,
84873805local signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
84873805local signalling | R - ON ¦ ,Output is energized,
84873805local signalling | R - OFF ¦ ,Output is de-energized,
84873805local signalling | - ¦ ,Range Setting Changes,
84873805local signalling | Same as RM17TU00 ¦ ,Phase Cut,
84873805local signalling | Same as RM17TU00 ¦ ,Phase Sequence Swap,
84873805local signalling | Same as RM17TU00 ¦ ,Undervoltage <U,
84873805local signalling | Same as RM17TU00 ¦ ,Overvoltage >U,
84873805local signalling | Same as RM17TU00 ¦ ,Phase Asymmetry,
84873805local signalling | Same as RM17TU00 ¦ ,Voltage Regeneration,
84873805local signalling | Same as RM17TU00 ¦ ,Extreme Undervoltage <U (Phase loss),
84873805local signalling | Same as RM17TU00 ¦ ,Extreme Overvoltage >U,
84873805local signalling | Same as RM17TU00 ¦ ,Extreme Phase Asymmetry,
84873805
84873805 | Same as RM17TU00
84873805 | Same as RM17TU00
84873805diagnostic button | Same as RM17TU00
84873805 | Same as RM17TU00
84873805 | Same as RM17TU00
84873805
84873805safety reliability data | Same as RM17TU00 ¦ ,MTTF,
84873805safety reliability data | Same as RM17TU00 ¦ ,B10,
84873805 | Same as RM17TU00 ¦ ,MTTFd,
84873805 | Same as RM17TU00 ¦ ,B10d,
84873805
84873805 | Drawing / Diagram
RM17TA00
RM17TA00standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM17TA00product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TA00marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TA00directives | 2014/35/EU
RM17TA00directives | 2014/30/EU
RM17TA00directives | 2011/65/EU
RM17TA00
RM17TA00 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM17TA00 | Class C ¦ Germanisher Lloyd,Environmental category,
RM17TA00ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM17TA00ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM17TA00relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM17TA00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM17TA00vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM17TA00shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM17TA00bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM17TA00seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM17TA00IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM17TA00IP degree of protection | IP30 ¦ IEC60529,Housing,
RM17TA00IP degree of protection | - ¦ IEC60529,Front Panel,
RM17TA00
RM17TA00width | 17.5 ¦ ,Width,
RM17TA00height | 90 ¦ ,Height,
RM17TA00depth | 72 ¦ ,Depth,
RM17TA00net weight | 80
RM17TA00mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM17TA00mounting support | - ¦ IEC/EN 60715,With socket,
RM17TA00mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM17TA00Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM17TA00Minimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM17TA00connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM17TA00connections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM17TA00connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM17TA00connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM17TA00tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM17TA00cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM17TA00duty time | 1
RM17TA00
RM17TA00electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM17TA00electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM17TA00electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM17TA00electromagnetic compatibility | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM17TA00electromagnetic compatibility | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge,
RM17TA00electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM17TA00electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM17TA00electromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM17TA00electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM17TA00electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM17TA00electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM17TA00electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM17TA00electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM17TA00electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM17TA00electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM17TA00electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM17TA00electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM17TA00electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM17TA00electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM17TA00
RM17TA00pollution degree | 3 ¦ IEC60664-1
RM17TA00overvoltage category | 3 ¦ IEC60664-1
RM17TA00circuit group | L1, L2, L3 ¦ ,Supply,Terminal
RM17TA00circuit group | - ¦ ,Input 1,
RM17TA00circuit group | - ¦ ,Input 2,
RM17TA00circuit group | - ¦ ,Input 3,
RM17TA00circuit group | 11,12,14 ¦ ,Output 1,
RM17TA00circuit group | - ¦ ,Output 2,
RM17TA00 | 208..480 AC ¦ ,Supply,Rated
RM17TA00 | - ¦ ,Input 1,Voltage
RM17TA00 | - ¦ ,Input 2,Spec
RM17TA00 | - ¦ ,Input 3,
RM17TA00 | 250V ¦ ,Output 1,
RM17TA00 | - ¦ ,Output 2,
RM17TA00[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM17TA00[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Output 2,
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM17TA00[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Output 2,
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Output 1 / Output 2,
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM17TA00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM17TA00[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM17TA00[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Output 2,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1 / Output 2,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM17TA00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM17TA00dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM17TA00dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM17TA00dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM17TA00dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM17TA00dielectric strength | - ¦ IEC60255-27,Supply / Output 2,
RM17TA00dielectric strength | - ¦ IEC60255-27,Output 1 / Output 2,
RM17TA00dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM17TA00dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM17TA00dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM17TA00dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM17TA00dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM17TA00dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM17TA00dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM17TA00dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM17TA00dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM17TA00insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM17TA00insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM17TA00insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM17TA00insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM17TA00insulation resistance | - ¦ IEC60255-27,Supply / Output 2,
RM17TA00insulation resistance | - ¦ IEC60255-27,Output 1 / Output 2,
RM17TA00insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM17TA00insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM17TA00insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM17TA00insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM17TA00insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM17TA00insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM17TA00insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM17TA00insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM17TA00insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM17TA00
RM17TA00[Us] rated supply voltage | ~ 3 x 208…3 x 480
RM17TA00supply voltage limits | ~ 3 x 183…3 x 528
RM17TA00polarity | -
RM17TA00supply frequency | 50 / 60
RM17TA00supply frequency | 45…66
RM17TA00power consumption | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz
RM17TA00immunity to microbreaks | 0
RM17TA00supply terminal | L1-L3
RM17TA00on-load factor | 1
RM17TA00release of input voltage | -
RM17TA00
RM17TA00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost ,
RM17TA00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence,
RM17TA00monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17TA00monitoring functions | - ¦ ,Over voltage,
RM17TA00monitoring functions | - ¦ ,Undervoltage ,
RM17TA00monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Phase asymmetry,
RM17TA00monitoring functions | - ¦ ,Disconnection of neutral,
RM17TA00monitoring functions | - ¦ ,Voltage Regeneration,
RM17TA00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage,
RM17TA00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage,
RM17TA00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM17TA00 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM17TA00internal input resistance | - ¦ ,Internal input resistance,
RM17TA00input terminal | L1-L2-L3 ¦ ,Input terminal,
RM17TA00Input nominal voltage selection | 208, 220, 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM17TA00permissible input overload | - ¦ ,permissible input overload,
RM17TA00input frequency | 50 / 60 ¦ ,Rated frequency,
RM17TA00input frequency | 45…66 ¦ ,Frequency operating range,
RM17TA00setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM17TA00repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM17TA00measurement method | True RMS ¦ ,Measurement method,
RM17TA00switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation,
RM17TA00switching threshold drift | < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM17TA00maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM17TA00measurement range | - ¦ ,Phase lost ,
RM17TA00measurement range | - ¦ ,Phase sequence,
RM17TA00measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17TA00measurement range | - ¦ ,Over voltage,
RM17TA00measurement range | - ¦ ,Undervoltage ,
RM17TA00measurement range | +5…+15 % in the ranges 3 x ~ 208…480 ¦ ,Phase asymmetry,
RM17TA00measurement range | - ¦ ,Disconnection of neutral,
RM17TA00measurement range | - ¦ ,Voltage Regeneration,
RM17TA00measurement range | - ¦ ,Extreme undervoltage,
RM17TA00measurement range | - ¦ ,Extreme Overvoltage,
RM17TA00measurement range | - ¦ ,Extreme Asymmetry,
RM17TA00tripping threshold | 1 or more phase cut ¦ ,Phase cut,
RM17TA00tripping threshold | Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence,
RM17TA00tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17TA00tripping threshold | - ¦ ,Over voltage,
RM17TA00tripping threshold | - ¦ ,Undervoltage ,
RM17TA00tripping threshold | Adjustable 5%...15% of selected Un ¦ ,Phase asymmetry,
RM17TA00tripping threshold | - ¦ ,Disconnection of neutral,
RM17TA00tripping threshold | - ¦ ,Voltage Regeneration,
RM17TA00tripping threshold | 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM17TA00tripping threshold | Internal design spec: 543V +/- 5% ¦ ,Extreme Overvoltage,
RM17TA00tripping threshold | Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM17TA00hysteresis | All phase cut recover ¦ ,Phase cut,
RM17TA00hysteresis | Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence,
RM17TA00hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17TA00hysteresis | - ¦ ,Over voltage,
RM17TA00hysteresis | - ¦ ,Undervoltage ,
RM17TA00hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Phase asymmetry,
RM17TA00hysteresis | - ¦ ,Disconnection of neutral,
RM17TA00hysteresis | - ¦ ,Voltage Regeneration,
RM17TA00hysteresis | All phases >195V Internal design spec: All phases >180V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM17TA00hysteresis | Internal design spec: All phases <533V +/- 5% ¦ ,Extreme Overvoltage,
RM17TA00hysteresis | - ¦ ,Extreme Asymmetry,
RM17TA00
RM17TA00output type | 1 x C/O relay contacts
RM17TA00output terminal | 11-12-14
RM17TA00output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM17TA00output logic | - ¦ ,R2 (21-22-24),
RM17TA00contacts material | Cadmium free
RM17TA00mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM17TA00electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM17TA00electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM17TA00electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM17TA00electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM17TA00[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM17TA00[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM17TA00maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM17TA00maximum switching capacity | 5A ¦ ,Maximum switching current,
RM17TA00maximum switching capacity | - ¦ ,Maximum switching capacity,
RM17TA00minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM17TA00minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM17TA00minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM17TA00maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM17TA00maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM17TA00thermal current | 5A ¦ IEC60947-5-1
RM17TA00short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse,
RM17TA00short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM17TA00
RM17TA00time delay type | Yes ¦ ,"OFF" delay,
RM17TA00time delay type | - ¦ ,"ON" delay,
RM17TA00time delay type | - ¦ ,Inhibition,
RM17TA00time delay range | Adjustable 0.1…10 ¦ ,"OFF" delay,
RM17TA00time delay range | - ¦ ,"ON" delay,
RM17TA00time delay range | - ¦ ,Inhibition,
RM17TA00response time | 0
RM17TA00response time | -
RM17TA00response time | -
RM17TA00response time | -
RM17TA00response time | -
RM17TA00power on delay | 0
RM17TA00reset time | 0
RM17TA00reset time | - ¦ ,through front panel reset,
RM17TA00reset time | - ¦ ,through input control reset,
RM17TA00setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM17TA00repeat accuracy of time delay | +/- 3%
RM17TA00time delay drift | -
RM17TA00time delay drift | -
RM17TA00
RM17TA00status LED | Un (Green) R (Amber)
RM17TA00local signalling | Un - ON ¦ ,Power supply availability,
RM17TA00local signalling | Un - OFF ¦ ,Power supply not availability,
RM17TA00local signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM17TA00local signalling | R - ON ¦ ,Output is energized,
RM17TA00local signalling | R - OFF ¦ ,Output is de-energized,
RM17TA00local signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM17TA00local signalling | - ¦ ,Phase Cut,
RM17TA00local signalling | - ¦ ,Phase Sequence Swap,
RM17TA00local signalling | - ¦ ,Undervoltage <U,
RM17TA00local signalling | - ¦ ,Overvoltage >U,
RM17TA00local signalling | - ¦ ,Phase Asymmetry,
RM17TA00local signalling | - ¦ ,Voltage Regeneration,
RM17TA00local signalling | - ¦ ,Extreme Undervoltage <U (Phase loss),
RM17TA00local signalling | - ¦ ,Extreme Overvoltage >U,
RM17TA00local signalling | - ¦ ,Extreme Phase Asymmetry,
RM17TA00
RM17TA00 | Yes
RM17TA00 | -
RM17TA00diagnostic button | -
RM17TA00 | -
RM17TA00 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM17TA00
RM17TA00safety reliability data | 4,400,000 hours ¦ ,MTTF,
RM17TA00safety reliability data | 470,000 hours ¦ ,B10,
RM17TA00 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM17TA00 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM17TA00
RM17TA00 | Drawing / Diagram
84873024
84873024standards | Same as RM17TA00
84873024product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873024marking | UL, CSA, GL, CCC, CE, China ROHS
84873024directives | Same as RM17TA00
84873024directives | Same as RM17TA00
84873024directives | Same as RM17TA00
84873024
84873024 | Same as RM17TA00 ¦ IEC60721-3-3,Climatic category,
84873024 | Same as RM17TA00 ¦ Germanisher Lloyd,Environmental category,
84873024ambient air temperature for storage | Same as RM17TA00 ¦ ,Storage,
84873024ambient air temperature for operation | Same as RM17TA00 ¦ ,Operation,
84873024relative humidity | Same as RM17TA00 ¦ IEC60068-2-30,Damp heat,XX
84873024 | Same as RM17TA00 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873024vibration resistance | Same as RM17TA00 ¦ IEC60068-2-6
84873024shock resistance | Same as RM17TA00 ¦ IEC60068-2-27
84873024bump resistance | Same as RM17TA00 ¦ IEC60068-2-29
84873024seismic resistance | Same as RM17TA00 ¦ IEC60068-3-3
84873024IP degree of protection | Same as RM17TA00 ¦ IEC60529,Terminal Block,
84873024IP degree of protection | Same as RM17TA00 ¦ IEC60529,Housing,
84873024IP degree of protection | Same as RM17TA00 ¦ IEC60529,Front Panel,
84873024
84873024width | Same as RM17TA00 ¦ ,Width,
84873024height | Same as RM17TA00 ¦ ,Height,
84873024depth | Same as RM17TA00 ¦ ,Depth,
84873024net weight | Same as RM17TA00
84873024mounting support | Same as RM17TA00 ¦ IEC/EN 60715,Without socket,
84873024mounting support | Same as RM17TA00 ¦ IEC/EN 60715,With socket,
84873024mounting position | Same as RM17TA00 ¦ ,In relation to normal vertical mounting plane,
84873024Minimum distance to adjacent devices | Same as RM17TA00 ¦ ,Horizontal,
84873024Minimum distance to adjacent devices | Same as RM17TA00 ¦ ,Vertical,
84873024connections - terminals | Same as RM17TA00 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873024connections - terminals | Same as RM17TA00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873024connections - terminals | Same as RM17TA00 ¦ IEC60947-1,Solid cable (spring terminal),
84873024connections - terminals | Same as RM17TA00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873024tightening torque | Same as RM17TA00 ¦ IEC60947-1,Tightening torque,
84873024cable stripping length | Same as RM17TA00 ¦ ,Cable stripping length,
84873024duty time | Same as RM17TA00
84873024
84873024electromagnetic compatibility | Same as RM17TA00 ¦ ,Generic immunity standard,
84873024electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-2,Electrostatic discharge,
84873024electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873024electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-4,Fast transient / burst,
84873024electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-5,Surge,
84873024electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-6,Conducted RF disturbance,
84873024electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-8,Power frequency magnetic field,
84873024electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873024electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873024electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-29,DC voltage interruption,
84873024electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-13,Low frequency harmonics,
84873024electromagnetic compatibility | Same as RM17TA00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873024electromagnetic compatibility | Same as RM17TA00 ¦ ,Generic emission standard,
84873024electromagnetic compatibility | Same as RM17TA00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873024electromagnetic compatibility | Same as RM17TA00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873024electromagnetic compatibility | Same as RM17TA00 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873024electromagnetic compatibility | Same as RM17TA00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873024electromagnetic compatibility | Same as RM17TA00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873024electromagnetic compatibility | Same as RM17TA00 ¦ Germanisher Lloyd,Conducted emission,
84873024
84873024pollution degree | Same as RM17TA00 ¦ IEC60664-1
84873024overvoltage category | Same as RM17TA00 ¦ IEC60664-1
84873024circuit group | Same as RM17TA00 ¦ ,Supply,Terminal
84873024circuit group | Same as RM17TA00 ¦ ,Input 1,
84873024circuit group | Same as RM17TA00 ¦ ,Input 2,
84873024circuit group | Same as RM17TA00 ¦ ,Input 3,
84873024circuit group | Same as RM17TA00 ¦ ,Output 1,
84873024circuit group | Same as RM17TA00 ¦ ,Output 2,
84873024 | Same as RM17TA00 ¦ ,Supply,Rated
84873024 | Same as RM17TA00 ¦ ,Input 1,Voltage
84873024 | Same as RM17TA00 ¦ ,Input 2,Spec
84873024 | Same as RM17TA00 ¦ ,Input 3,
84873024 | Same as RM17TA00 ¦ ,Output 1,
84873024 | Same as RM17TA00 ¦ ,Output 2,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Output 1,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Output 2,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Output 1,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Output 2,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Output 1 / Output 2,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 1,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 2,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 1,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 2,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 1,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 2,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 2,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Input 3,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 3,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Output 1,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Output 2,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Output 1,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Output 2,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Output 1 / Output 2,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 1,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 2,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 1,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 2,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 1,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 2,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 2,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Input 3,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 3,
84873024dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 1,
84873024dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 2,
84873024dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 3,
84873024dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Output 1,
84873024dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Output 2,
84873024dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Output 1 / Output 2,
84873024dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 1,
84873024dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 2,
84873024dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 1,
84873024dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 2,
84873024dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 1,
84873024dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 2,
84873024dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 2,
84873024dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Input 3,
84873024dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 3,
84873024insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 1,
84873024insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 2,
84873024insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 3,
84873024insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Output 1,
84873024insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Output 2,
84873024insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Output 1 / Output 2,
84873024insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 1,
84873024insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 2,
84873024insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 1,
84873024insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 2,
84873024insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 1,
84873024insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 2,
84873024insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 2,
84873024insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Input 3,
84873024insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 3,
84873024
84873024[Us] rated supply voltage | Same as RM17TA00
84873024supply voltage limits | Same as RM17TA00
84873024polarity | Same as RM17TA00
84873024supply frequency | Same as RM17TA00
84873024supply frequency | Same as RM17TA00
84873024power consumption | Same as RM17TA00
84873024immunity to microbreaks | Same as RM17TA00
84873024supply terminal | Same as RM17TA00
84873024on-load factor | Same as RM17TA00
84873024release of input voltage | Same as RM17TA00
84873024
84873024monitoring functions | Same as RM17TA00 ¦ ,Phase lost ,
84873024monitoring functions | Same as RM17TA00 ¦ ,Phase sequence,
84873024monitoring functions | Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode),
84873024monitoring functions | Same as RM17TA00 ¦ ,Over voltage,
84873024monitoring functions | Same as RM17TA00 ¦ ,Undervoltage ,
84873024monitoring functions | Same as RM17TA00 ¦ ,Phase asymmetry,
84873024monitoring functions | Same as RM17TA00 ¦ ,Disconnection of neutral,
84873024monitoring functions | Same as RM17TA00 ¦ ,Voltage Regeneration,
84873024monitoring functions | Same as RM17TA00 ¦ ,Extreme undervoltage,
84873024monitoring functions | Same as RM17TA00 ¦ ,Extreme overvoltage,
84873024monitoring functions | Same as RM17TA00 ¦ ,Extreme asymmetry,
84873024 | Same as RM17TA00 ¦ ,Measurement mode,
84873024internal input resistance | Same as RM17TA00 ¦ ,Internal input resistance,
84873024input terminal | Same as RM17TA00 ¦ ,Input terminal,
84873024Input nominal voltage selection | Same as RM17TA00 ¦ ,Input nominal voltage selection,
84873024permissible input overload | Same as RM17TA00 ¦ ,permissible input overload,
84873024input frequency | Same as RM17TA00 ¦ ,Rated frequency,
84873024input frequency | Same as RM17TA00 ¦ ,Frequency operating range,
84873024setting accuracy of the switching threshold | Same as RM17TA00 ¦ ,Setting accuracy,
84873024repeat accuracy of the switching threshold | Same as RM17TA00 ¦ ,Repeat accuracy (constant parameters),
84873024measurement method | Same as RM17TA00 ¦ ,Measurement method,
84873024switching threshold drift | Same as RM17TA00 ¦ ,Measurement error with supply voltage variation,
84873024switching threshold drift | Same as RM17TA00 ¦ ,Measurement error with temperature variation,
84873024maximum measuring cycle | Same as RM17TA00 ¦ ,Maximum measuring cycles,
84873024measurement range | Same as RM17TA00 ¦ ,Phase lost ,
84873024measurement range | Same as RM17TA00 ¦ ,Phase sequence,
84873024measurement range | Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode),
84873024measurement range | Same as RM17TA00 ¦ ,Over voltage,
84873024measurement range | Same as RM17TA00 ¦ ,Undervoltage ,
84873024measurement range | Same as RM17TA00 ¦ ,Phase asymmetry,
84873024measurement range | Same as RM17TA00 ¦ ,Disconnection of neutral,
84873024measurement range | Same as RM17TA00 ¦ ,Voltage Regeneration,
84873024measurement range | Same as RM17TA00 ¦ ,Extreme undervoltage,
84873024measurement range | Same as RM17TA00 ¦ ,Extreme Overvoltage,
84873024measurement range | Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873024tripping threshold | Same as RM17TA00 ¦ ,Phase cut,
84873024tripping threshold | Same as RM17TA00 ¦ ,Phase sequence,
84873024tripping threshold | Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode),
84873024tripping threshold | Same as RM17TA00 ¦ ,Over voltage,
84873024tripping threshold | Same as RM17TA00 ¦ ,Undervoltage ,
84873024tripping threshold | Same as RM17TA00 ¦ ,Phase asymmetry,
84873024tripping threshold | Same as RM17TA00 ¦ ,Disconnection of neutral,
84873024tripping threshold | Same as RM17TA00 ¦ ,Voltage Regeneration,
84873024tripping threshold | Same as RM17TA00 ¦ ,Extreme undervoltage (Phase loss),
84873024tripping threshold | Same as RM17TA00 ¦ ,Extreme Overvoltage,
84873024tripping threshold | Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873024hysteresis | Same as RM17TA00 ¦ ,Phase cut,
84873024hysteresis | Same as RM17TA00 ¦ ,Phase sequence,
84873024hysteresis | Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode),
84873024hysteresis | Same as RM17TA00 ¦ ,Over voltage,
84873024hysteresis | Same as RM17TA00 ¦ ,Undervoltage ,
84873024hysteresis | Same as RM17TA00 ¦ ,Phase asymmetry,
84873024hysteresis | Same as RM17TA00 ¦ ,Disconnection of neutral,
84873024hysteresis | Same as RM17TA00 ¦ ,Voltage Regeneration,
84873024hysteresis | Same as RM17TA00 ¦ ,Extreme undervoltage (Phase loss),
84873024hysteresis | Same as RM17TA00 ¦ ,Extreme Overvoltage,
84873024hysteresis | Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873024
84873024output type | Same as RM17TA00
84873024output terminal | Same as RM17TA00
84873024output logic | Same as RM17TA00 ¦ ,R1 (11-12-14),
84873024output logic | Same as RM17TA00 ¦ ,R2 (21-22-24),
84873024contacts material | Same as RM17TA00
84873024mechanical durability | Same as RM17TA00 ¦ IEC61810-1
84873024electrical durability | Same as RM17TA00 ¦ IEC60947-4-1,AC-1,
84873024electrical durability | Same as RM17TA00 ¦ IEC60947-4-1,DC-1,
84873024electrical durability | Same as RM17TA00 ¦ IEC60947-5-1,AC-15,
84873024electrical durability | Same as RM17TA00 ¦ IEC60947-5-1,DC-13,
84873024[Ue] rated operational voltage | Same as RM17TA00 ¦ IEC61810-1,Rated switching voltage,
84873024[Ie] rated operational current | Same as RM17TA00 ¦ IEC61810-1,Rated switching current,
84873024maximum switching capacity | Same as RM17TA00 ¦ ,Maximum switching voltage,
84873024maximum switching capacity | Same as RM17TA00 ¦ ,Maximum switching current,
84873024maximum switching capacity | Same as RM17TA00 ¦ ,Maximum switching capacity,
84873024minimum switching capacity | Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching voltage,
84873024minimum switching capacity | Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching current,
84873024minimum switching capacity | Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching capacity,
84873024maximum voltage drop | Same as RM17TA00 ¦ IEC62314,Only for solid state output,
84873024maximum leakage current | Same as RM17TA00 ¦ IEC62314,Only for solid state output,
84873024thermal current | Same as RM17TA00 ¦ IEC60947-5-1
84873024short circuit protection | Same as RM17TA00 ¦ IEC60947-5-1,Relay Output by external fuse,
84873024short circuit protection | Same as RM17TA00 ¦ IEC62314,Solid State Output by external fuse,
84873024
84873024time delay type | Same as RM17TA00 ¦ ,"OFF" delay,
84873024time delay type | Same as RM17TA00 ¦ ,"ON" delay,
84873024time delay type | Same as RM17TA00 ¦ ,Inhibition,
84873024time delay range | Same as RM17TA00 ¦ ,"OFF" delay,
84873024time delay range | Same as RM17TA00 ¦ ,"ON" delay,
84873024time delay range | Same as RM17TA00 ¦ ,Inhibition,
84873024response time | Same as RM17TA00 ¦ ,on crossing the threshold,
84873024response time | Same as RM17TA00
84873024response time | Same as RM17TA00
84873024response time | Same as RM17TA00
84873024response time | Same as RM17TA00
84873024power on delay | Same as RM17TA00
84873024reset time | Same as RM17TA00 ¦ ,through Un power reset,
84873024reset time | Same as RM17TA00 ¦ ,through front panel reset,
84873024reset time | Same as RM17TA00 ¦ ,through input control reset,
84873024setting accuracy of time delay | Same as RM17TA00
84873024repeat accuracy of time delay | Same as RM17TA00
84873024time delay drift | Same as RM17TA00
84873024time delay drift | Same as RM17TA00
84873024
84873024status LED | Same as RM17TA00
84873024local signalling | Same as RM17TA00 ¦ ,Power supply availability,
84873024local signalling | Same as RM17TA00 ¦ ,Power supply not availability,
84873024local signalling | Same as RM17TA00 ¦ ,Timing in-progress,
84873024local signalling | Same as RM17TA00 ¦ ,Output is energized,
84873024local signalling | Same as RM17TA00 ¦ ,Output is de-energized,
84873024local signalling | Same as RM17TA00 ¦ ,Range Setting Changes,
84873024local signalling | Same as RM17TA00 ¦ ,Phase Cut,
84873024local signalling | Same as RM17TA00 ¦ ,Phase Sequence Swap,
84873024local signalling | Same as RM17TA00 ¦ ,Undervoltage <U,
84873024local signalling | Same as RM17TA00 ¦ ,Overvoltage >U,
84873024local signalling | Same as RM17TA00 ¦ ,Phase Asymmetry,
84873024local signalling | Same as RM17TA00 ¦ ,Voltage Regeneration,
84873024local signalling | Same as RM17TA00 ¦ ,Extreme Undervoltage <U (Phase loss),
84873024local signalling | Same as RM17TA00 ¦ ,Extreme Overvoltage >U,
84873024local signalling | Same as RM17TA00 ¦ ,Extreme Phase Asymmetry,
84873024
84873024 | Same as RM17TA00
84873024 | Same as RM17TA00
84873024diagnostic button | Same as RM17TA00
84873024 | Same as RM17TA00
84873024 | Same as RM17TA00
84873024
84873024safety reliability data | Same as RM17TA00 ¦ ,MTTF,
84873024safety reliability data | Same as RM17TA00 ¦ ,B10,
84873024 | Same as RM17TA00 ¦ ,MTTFd,
84873024 | Same as RM17TA00 ¦ ,B10d,
84873024
84873024 | Drawing / Diagram
84873892
84873892standards | Same as RM17TA00
84873892product certifications | UL, CSA, CE, China ROHS
84873892marking | UL, CSA, CE, China ROHS
84873892directives | Same as RM17TA00
84873892directives | Same as RM17TA00
84873892directives | Same as RM17TA00
84873892
84873892 | Same as RM17TA00 ¦ IEC60721-3-3,Climatic category,
84873892 | Same as RM17TA00 ¦ Germanisher Lloyd,Environmental category,
84873892ambient air temperature for storage | Same as RM17TA00 ¦ ,Storage,
84873892ambient air temperature for operation | Same as RM17TA00 ¦ ,Operation,
84873892relative humidity | Same as RM17TA00 ¦ IEC60068-2-30,Damp heat,XX
84873892 | Same as RM17TA00 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873892vibration resistance | Same as RM17TA00 ¦ IEC60068-2-6
84873892shock resistance | Same as RM17TA00 ¦ IEC60068-2-27
84873892bump resistance | Same as RM17TA00 ¦ IEC60068-2-29
84873892seismic resistance | Same as RM17TA00 ¦ IEC60068-3-3
84873892IP degree of protection | Same as RM17TA00 ¦ IEC60529,Terminal Block,
84873892IP degree of protection | Same as RM17TA00 ¦ IEC60529,Housing,
84873892IP degree of protection | Same as RM17TA00 ¦ IEC60529,Front Panel,
84873892
84873892width | Same as RM17TA00 ¦ ,Width,
84873892height | Same as RM17TA00 ¦ ,Height,
84873892depth | Same as RM17TA00 ¦ ,Depth,
84873892net weight | Same as RM17TA00
84873892mounting support | Same as RM17TA00 ¦ IEC/EN 60715,Without socket,
84873892mounting support | Same as RM17TA00 ¦ IEC/EN 60715,With socket,
84873892mounting position | Same as RM17TA00 ¦ ,In relation to normal vertical mounting plane,
84873892Minimum distance to adjacent devices | Same as RM17TA00 ¦ ,Horizontal,
84873892Minimum distance to adjacent devices | Same as RM17TA00 ¦ ,Vertical,
84873892connections - terminals | Same as RM17TA00 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873892connections - terminals | Same as RM17TA00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873892connections - terminals | Same as RM17TA00 ¦ IEC60947-1,Solid cable (spring terminal),
84873892connections - terminals | Same as RM17TA00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873892tightening torque | Same as RM17TA00 ¦ IEC60947-1,Tightening torque,
84873892cable stripping length | Same as RM17TA00 ¦ ,Cable stripping length,
84873892duty time | Same as RM17TA00
84873892
84873892electromagnetic compatibility | Same as RM17TA00 ¦ ,Generic immunity standard,
84873892electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-2,Electrostatic discharge,
84873892electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873892electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-4,Fast transient / burst,
84873892electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-5,Surge,
84873892electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-6,Conducted RF disturbance,
84873892electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-8,Power frequency magnetic field,
84873892electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873892electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873892electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-29,DC voltage interruption,
84873892electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-13,Low frequency harmonics,
84873892electromagnetic compatibility | Same as RM17TA00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873892electromagnetic compatibility | Same as RM17TA00 ¦ ,Generic emission standard,
84873892electromagnetic compatibility | Same as RM17TA00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873892electromagnetic compatibility | Same as RM17TA00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873892electromagnetic compatibility | Same as RM17TA00 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873892electromagnetic compatibility | Same as RM17TA00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873892electromagnetic compatibility | Same as RM17TA00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873892electromagnetic compatibility | Same as RM17TA00 ¦ Germanisher Lloyd,Conducted emission,
84873892
84873892pollution degree | Same as RM17TA00 ¦ IEC60664-1
84873892overvoltage category | Same as RM17TA00 ¦ IEC60664-1
84873892circuit group | Same as RM17TA00 ¦ ,Supply,Terminal
84873892circuit group | Same as RM17TA00 ¦ ,Input 1,
84873892circuit group | Same as RM17TA00 ¦ ,Input 2,
84873892circuit group | Same as RM17TA00 ¦ ,Input 3,
84873892circuit group | Same as RM17TA00 ¦ ,Output 1,
84873892circuit group | Same as RM17TA00 ¦ ,Output 2,
84873892 | Same as RM17TA00 ¦ ,Supply,Rated
84873892 | Same as RM17TA00 ¦ ,Input 1,Voltage
84873892 | Same as RM17TA00 ¦ ,Input 2,Spec
84873892 | Same as RM17TA00 ¦ ,Input 3,
84873892 | Same as RM17TA00 ¦ ,Output 1,
84873892 | Same as RM17TA00 ¦ ,Output 2,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Output 1,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Output 2,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Output 1,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Output 2,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Output 1 / Output 2,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 1,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 2,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 1,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 2,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 1,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 2,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 2,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Input 3,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 3,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Output 1,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Output 2,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Output 1,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Output 2,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Output 1 / Output 2,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 1,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 2,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 1,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 2,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 1,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 2,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 2,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Input 3,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 3,
84873892dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 1,
84873892dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 2,
84873892dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 3,
84873892dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Output 1,
84873892dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Output 2,
84873892dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Output 1 / Output 2,
84873892dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 1,
84873892dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 2,
84873892dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 1,
84873892dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 2,
84873892dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 1,
84873892dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 2,
84873892dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 2,
84873892dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Input 3,
84873892dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 3,
84873892insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 1,
84873892insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 2,
84873892insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 3,
84873892insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Output 1,
84873892insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Output 2,
84873892insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Output 1 / Output 2,
84873892insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 1,
84873892insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 2,
84873892insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 1,
84873892insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 2,
84873892insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 1,
84873892insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 2,
84873892insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 2,
84873892insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Input 3,
84873892insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 3,
84873892
84873892[Us] rated supply voltage | Same as RM17TA00
84873892supply voltage limits | Same as RM17TA00
84873892polarity | Same as RM17TA00
84873892supply frequency | Same as RM17TA00
84873892supply frequency | Same as RM17TA00
84873892power consumption | Same as RM17TA00
84873892immunity to microbreaks | Same as RM17TA00
84873892supply terminal | Same as RM17TA00
84873892on-load factor | Same as RM17TA00
84873892release of input voltage | Same as RM17TA00
84873892
84873892monitoring functions | Same as RM17TA00 ¦ ,Phase lost ,
84873892monitoring functions | Same as RM17TA00 ¦ ,Phase sequence,
84873892monitoring functions | Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode),
84873892monitoring functions | Same as RM17TA00 ¦ ,Over voltage,
84873892monitoring functions | Same as RM17TA00 ¦ ,Undervoltage ,
84873892monitoring functions | Same as RM17TA00 ¦ ,Phase asymmetry,
84873892monitoring functions | Same as RM17TA00 ¦ ,Disconnection of neutral,
84873892monitoring functions | Same as RM17TA00 ¦ ,Voltage Regeneration,
84873892monitoring functions | Same as RM17TA00 ¦ ,Extreme undervoltage,
84873892monitoring functions | Same as RM17TA00 ¦ ,Extreme overvoltage,
84873892monitoring functions | Same as RM17TA00 ¦ ,Extreme asymmetry,
84873892 | Same as RM17TA00 ¦ ,Measurement mode,
84873892internal input resistance | Same as RM17TA00 ¦ ,Internal input resistance,
84873892input terminal | Same as RM17TA00 ¦ ,Input terminal,
84873892Input nominal voltage selection | Same as RM17TA00 ¦ ,Input nominal voltage selection,
84873892permissible input overload | Same as RM17TA00 ¦ ,permissible input overload,
84873892input frequency | Same as RM17TA00 ¦ ,Rated frequency,
84873892input frequency | Same as RM17TA00 ¦ ,Frequency operating range,
84873892setting accuracy of the switching threshold | Same as RM17TA00 ¦ ,Setting accuracy,
84873892repeat accuracy of the switching threshold | Same as RM17TA00 ¦ ,Repeat accuracy (constant parameters),
84873892measurement method | Same as RM17TA00 ¦ ,Measurement method,
84873892switching threshold drift | Same as RM17TA00 ¦ ,Measurement error with supply voltage variation,
84873892switching threshold drift | Same as RM17TA00 ¦ ,Measurement error with temperature variation,
84873892maximum measuring cycle | Same as RM17TA00 ¦ ,Maximum measuring cycles,
84873892measurement range | Same as RM17TA00 ¦ ,Phase lost ,
84873892measurement range | Same as RM17TA00 ¦ ,Phase sequence,
84873892measurement range | Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode),
84873892measurement range | Same as RM17TA00 ¦ ,Over voltage,
84873892measurement range | Same as RM17TA00 ¦ ,Undervoltage ,
84873892measurement range | Same as RM17TA00 ¦ ,Phase asymmetry,
84873892measurement range | Same as RM17TA00 ¦ ,Disconnection of neutral,
84873892measurement range | Same as RM17TA00 ¦ ,Voltage Regeneration,
84873892measurement range | Same as RM17TA00 ¦ ,Extreme undervoltage,
84873892measurement range | Same as RM17TA00 ¦ ,Extreme Overvoltage,
84873892measurement range | Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873892tripping threshold | Same as RM17TA00 ¦ ,Phase cut,
84873892tripping threshold | Same as RM17TA00 ¦ ,Phase sequence,
84873892tripping threshold | Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode),
84873892tripping threshold | Same as RM17TA00 ¦ ,Over voltage,
84873892tripping threshold | Same as RM17TA00 ¦ ,Undervoltage ,
84873892tripping threshold | Same as RM17TA00 ¦ ,Phase asymmetry,
84873892tripping threshold | Same as RM17TA00 ¦ ,Disconnection of neutral,
84873892tripping threshold | Same as RM17TA00 ¦ ,Voltage Regeneration,
84873892tripping threshold | Same as RM17TA00 ¦ ,Extreme undervoltage (Phase loss),
84873892tripping threshold | Same as RM17TA00 ¦ ,Extreme Overvoltage,
84873892tripping threshold | Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873892hysteresis | Same as RM17TA00 ¦ ,Phase cut,
84873892hysteresis | Same as RM17TA00 ¦ ,Phase sequence,
84873892hysteresis | Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode),
84873892hysteresis | Same as RM17TA00 ¦ ,Over voltage,
84873892hysteresis | Same as RM17TA00 ¦ ,Undervoltage ,
84873892hysteresis | Same as RM17TA00 ¦ ,Phase asymmetry,
84873892hysteresis | Same as RM17TA00 ¦ ,Disconnection of neutral,
84873892hysteresis | Same as RM17TA00 ¦ ,Voltage Regeneration,
84873892hysteresis | Same as RM17TA00 ¦ ,Extreme undervoltage (Phase loss),
84873892hysteresis | Same as RM17TA00 ¦ ,Extreme Overvoltage,
84873892hysteresis | Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873892
84873892output type | Same as RM17TA00
84873892output terminal | Same as RM17TA00
84873892output logic | Same as RM17TA00 ¦ ,R1 (11-12-14),
84873892output logic | Same as RM17TA00 ¦ ,R2 (21-22-24),
84873892contacts material | Same as RM17TA00
84873892mechanical durability | Same as RM17TA00 ¦ IEC61810-1
84873892electrical durability | Same as RM17TA00 ¦ IEC60947-4-1,AC-1,
84873892electrical durability | Same as RM17TA00 ¦ IEC60947-4-1,DC-1,
84873892electrical durability | Same as RM17TA00 ¦ IEC60947-5-1,AC-15,
84873892electrical durability | Same as RM17TA00 ¦ IEC60947-5-1,DC-13,
84873892[Ue] rated operational voltage | Same as RM17TA00 ¦ IEC61810-1,Rated switching voltage,
84873892[Ie] rated operational current | Same as RM17TA00 ¦ IEC61810-1,Rated switching current,
84873892maximum switching capacity | Same as RM17TA00 ¦ ,Maximum switching voltage,
84873892maximum switching capacity | Same as RM17TA00 ¦ ,Maximum switching current,
84873892maximum switching capacity | Same as RM17TA00 ¦ ,Maximum switching capacity,
84873892minimum switching capacity | Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching voltage,
84873892minimum switching capacity | Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching current,
84873892minimum switching capacity | Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching capacity,
84873892maximum voltage drop | Same as RM17TA00 ¦ IEC62314,Only for solid state output,
84873892maximum leakage current | Same as RM17TA00 ¦ IEC62314,Only for solid state output,
84873892thermal current | Same as RM17TA00 ¦ IEC60947-5-1
84873892short circuit protection | Same as RM17TA00 ¦ IEC60947-5-1,Relay Output by external fuse,
84873892short circuit protection | Same as RM17TA00 ¦ IEC62314,Solid State Output by external fuse,
84873892
84873892time delay type | Same as RM17TA00 ¦ ,"OFF" delay,
84873892time delay type | Same as RM17TA00 ¦ ,"ON" delay,
84873892time delay type | Same as RM17TA00 ¦ ,Inhibition,
84873892time delay range | Same as RM17TA00 ¦ ,"OFF" delay,
84873892time delay range | Same as RM17TA00 ¦ ,"ON" delay,
84873892time delay range | Same as RM17TA00 ¦ ,Inhibition,
84873892response time | Same as RM17TA00 ¦ ,on crossing the threshold,
84873892response time | Same as RM17TA00
84873892response time | Same as RM17TA00
84873892response time | Same as RM17TA00
84873892response time | Same as RM17TA00
84873892power on delay | Same as RM17TA00
84873892reset time | Same as RM17TA00 ¦ ,through Un power reset,
84873892reset time | Same as RM17TA00 ¦ ,through front panel reset,
84873892reset time | Same as RM17TA00 ¦ ,through input control reset,
84873892setting accuracy of time delay | Same as RM17TA00
84873892repeat accuracy of time delay | Same as RM17TA00
84873892time delay drift | Same as RM17TA00
84873892time delay drift | Same as RM17TA00
84873892
84873892status LED | Same as RM17TA00
84873892local signalling | Same as RM17TA00 ¦ ,Power supply availability,
84873892local signalling | Same as RM17TA00 ¦ ,Power supply not availability,
84873892local signalling | Same as RM17TA00 ¦ ,Timing in-progress,
84873892local signalling | Same as RM17TA00 ¦ ,Output is energized,
84873892local signalling | Same as RM17TA00 ¦ ,Output is de-energized,
84873892local signalling | Same as RM17TA00 ¦ ,Range Setting Changes,
84873892local signalling | Same as RM17TA00 ¦ ,Phase Cut,
84873892local signalling | Same as RM17TA00 ¦ ,Phase Sequence Swap,
84873892local signalling | Same as RM17TA00 ¦ ,Undervoltage <U,
84873892local signalling | Same as RM17TA00 ¦ ,Overvoltage >U,
84873892local signalling | Same as RM17TA00 ¦ ,Phase Asymmetry,
84873892local signalling | Same as RM17TA00 ¦ ,Voltage Regeneration,
84873892local signalling | Same as RM17TA00 ¦ ,Extreme Undervoltage <U (Phase loss),
84873892local signalling | Same as RM17TA00 ¦ ,Extreme Overvoltage >U,
84873892local signalling | Same as RM17TA00 ¦ ,Extreme Phase Asymmetry,
84873892
84873892 | Same as RM17TA00
84873892 | Same as RM17TA00
84873892diagnostic button | Same as RM17TA00
84873892 | Same as RM17TA00
84873892 | Same as RM17TA00
84873892
84873892safety reliability data | Same as RM17TA00 ¦ ,MTTF,
84873892safety reliability data | Same as RM17TA00 ¦ ,B10,
84873892 | Same as RM17TA00 ¦ ,MTTFd,
84873892 | Same as RM17TA00 ¦ ,B10d,
84873892
84873892 | Drawing / Diagram
84873804
84873804standards | Same as RM17TA00
84873804product certifications | UL, CSA, CE, China ROHS
84873804marking | UL, CSA, CE, China ROHS
84873804directives | Same as RM17TA00
84873804directives | Same as RM17TA00
84873804directives | Same as RM17TA00
84873804
84873804 | Same as RM17TA00 ¦ IEC60721-3-3,Climatic category,
84873804 | Same as RM17TA00 ¦ Germanisher Lloyd,Environmental category,
84873804ambient air temperature for storage | Same as RM17TA00 ¦ ,Storage,
84873804ambient air temperature for operation | Same as RM17TA00 ¦ ,Operation,
84873804relative humidity | Same as RM17TA00 ¦ IEC60068-2-30,Damp heat,XX
84873804 | Same as RM17TA00 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873804vibration resistance | Same as RM17TA00 ¦ IEC60068-2-6
84873804shock resistance | Same as RM17TA00 ¦ IEC60068-2-27
84873804bump resistance | Same as RM17TA00 ¦ IEC60068-2-29
84873804seismic resistance | Same as RM17TA00 ¦ IEC60068-3-3
84873804IP degree of protection | Same as RM17TA00 ¦ IEC60529,Terminal Block,
84873804IP degree of protection | Same as RM17TA00 ¦ IEC60529,Housing,
84873804IP degree of protection | Same as RM17TA00 ¦ IEC60529,Front Panel,
84873804
84873804width | Same as RM17TA00 ¦ ,Width,
84873804height | Same as RM17TA00 ¦ ,Height,
84873804depth | Same as RM17TA00 ¦ ,Depth,
84873804net weight | Same as RM17TA00
84873804mounting support | Same as RM17TA00 ¦ IEC/EN 60715,Without socket,
84873804mounting support | Same as RM17TA00 ¦ IEC/EN 60715,With socket,
84873804mounting position | Same as RM17TA00 ¦ ,In relation to normal vertical mounting plane,
84873804Minimum distance to adjacent devices | Same as RM17TA00 ¦ ,Horizontal,
84873804Minimum distance to adjacent devices | Same as RM17TA00 ¦ ,Vertical,
84873804connections - terminals | Same as RM17TA00 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873804connections - terminals | Same as RM17TA00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873804connections - terminals | Same as RM17TA00 ¦ IEC60947-1,Solid cable (spring terminal),
84873804connections - terminals | Same as RM17TA00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873804tightening torque | Same as RM17TA00 ¦ IEC60947-1,Tightening torque,
84873804cable stripping length | Same as RM17TA00 ¦ ,Cable stripping length,
84873804duty time | Same as RM17TA00
84873804
84873804electromagnetic compatibility | Same as RM17TA00 ¦ ,Generic immunity standard,
84873804electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-2,Electrostatic discharge,
84873804electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873804electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-4,Fast transient / burst,
84873804electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-5,Surge,
84873804electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-6,Conducted RF disturbance,
84873804electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-8,Power frequency magnetic field,
84873804electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873804electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873804electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-29,DC voltage interruption,
84873804electromagnetic compatibility | Same as RM17TA00 ¦ IEC61000-4-13,Low frequency harmonics,
84873804electromagnetic compatibility | Same as RM17TA00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873804electromagnetic compatibility | Same as RM17TA00 ¦ ,Generic emission standard,
84873804electromagnetic compatibility | Same as RM17TA00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873804electromagnetic compatibility | Same as RM17TA00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873804electromagnetic compatibility | Same as RM17TA00 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873804electromagnetic compatibility | Same as RM17TA00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873804electromagnetic compatibility | Same as RM17TA00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873804electromagnetic compatibility | Same as RM17TA00 ¦ Germanisher Lloyd,Conducted emission,
84873804
84873804pollution degree | Same as RM17TA00 ¦ IEC60664-1
84873804overvoltage category | Same as RM17TA00 ¦ IEC60664-1
84873804circuit group | Same as RM17TA00 ¦ ,Supply,Terminal
84873804circuit group | Same as RM17TA00 ¦ ,Input 1,
84873804circuit group | Same as RM17TA00 ¦ ,Input 2,
84873804circuit group | Same as RM17TA00 ¦ ,Input 3,
84873804circuit group | Same as RM17TA00 ¦ ,Output 1,
84873804circuit group | Same as RM17TA00 ¦ ,Output 2,
84873804 | Same as RM17TA00 ¦ ,Supply,Rated
84873804 | Same as RM17TA00 ¦ ,Input 1,Voltage
84873804 | Same as RM17TA00 ¦ ,Input 2,Spec
84873804 | Same as RM17TA00 ¦ ,Input 3,
84873804 | Same as RM17TA00 ¦ ,Output 1,
84873804 | Same as RM17TA00 ¦ ,Output 2,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Output 1,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Output 2,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Output 1,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Output 2,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Output 1 / Output 2,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 1,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 2,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 1,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 2,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 1,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 2,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 2,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Input 3,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 3,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Output 1,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Output 2,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Output 1,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply / Output 2,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Output 1 / Output 2,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 1,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 2,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 1,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 2,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 1,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 2,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 2,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 2 / Input 3,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 3,
84873804dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 1,
84873804dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 2,
84873804dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 3,
84873804dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Output 1,
84873804dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Output 2,
84873804dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Output 1 / Output 2,
84873804dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 1,
84873804dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 2,
84873804dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 1,
84873804dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 2,
84873804dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 1,
84873804dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 2,
84873804dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 2,
84873804dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Input 3,
84873804dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 3,
84873804insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 1,
84873804insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 2,
84873804insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 3,
84873804insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Output 1,
84873804insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Output 2,
84873804insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Output 1 / Output 2,
84873804insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 1,
84873804insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 2,
84873804insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 1,
84873804insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 2,
84873804insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 1,
84873804insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 2,
84873804insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 2,
84873804insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 2 / Input 3,
84873804insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 3,
84873804
84873804[Us] rated supply voltage | Same as RM17TA00
84873804supply voltage limits | Same as RM17TA00
84873804polarity | Same as RM17TA00
84873804supply frequency | Same as RM17TA00
84873804supply frequency | Same as RM17TA00
84873804power consumption | Same as RM17TA00
84873804immunity to microbreaks | Same as RM17TA00
84873804supply terminal | Same as RM17TA00
84873804on-load factor | Same as RM17TA00
84873804release of input voltage | Same as RM17TA00
84873804
84873804monitoring functions | Same as RM17TA00 ¦ ,Phase lost ,
84873804monitoring functions | Same as RM17TA00 ¦ ,Phase sequence,
84873804monitoring functions | Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode),
84873804monitoring functions | Same as RM17TA00 ¦ ,Over voltage,
84873804monitoring functions | Same as RM17TA00 ¦ ,Undervoltage ,
84873804monitoring functions | Same as RM17TA00 ¦ ,Phase asymmetry,
84873804monitoring functions | Same as RM17TA00 ¦ ,Disconnection of neutral,
84873804monitoring functions | Same as RM17TA00 ¦ ,Voltage Regeneration,
84873804monitoring functions | Same as RM17TA00 ¦ ,Extreme undervoltage,
84873804monitoring functions | Same as RM17TA00 ¦ ,Extreme overvoltage,
84873804monitoring functions | Same as RM17TA00 ¦ ,Extreme asymmetry,
84873804 | Same as RM17TA00 ¦ ,Measurement mode,
84873804internal input resistance | Same as RM17TA00 ¦ ,Internal input resistance,
84873804input terminal | Same as RM17TA00 ¦ ,Input terminal,
84873804Input nominal voltage selection | Same as RM17TA00 ¦ ,Input nominal voltage selection,
84873804permissible input overload | Same as RM17TA00 ¦ ,permissible input overload,
84873804input frequency | Same as RM17TA00 ¦ ,Rated frequency,
84873804input frequency | Same as RM17TA00 ¦ ,Frequency operating range,
84873804setting accuracy of the switching threshold | Same as RM17TA00 ¦ ,Setting accuracy,
84873804repeat accuracy of the switching threshold | Same as RM17TA00 ¦ ,Repeat accuracy (constant parameters),
84873804measurement method | Same as RM17TA00 ¦ ,Measurement method,
84873804switching threshold drift | Same as RM17TA00 ¦ ,Measurement error with supply voltage variation,
84873804switching threshold drift | Same as RM17TA00 ¦ ,Measurement error with temperature variation,
84873804maximum measuring cycle | Same as RM17TA00 ¦ ,Maximum measuring cycles,
84873804measurement range | Same as RM17TA00 ¦ ,Phase lost ,
84873804measurement range | Same as RM17TA00 ¦ ,Phase sequence,
84873804measurement range | Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode),
84873804measurement range | Same as RM17TA00 ¦ ,Over voltage,
84873804measurement range | Same as RM17TA00 ¦ ,Undervoltage ,
84873804measurement range | Same as RM17TA00 ¦ ,Phase asymmetry,
84873804measurement range | Same as RM17TA00 ¦ ,Disconnection of neutral,
84873804measurement range | Same as RM17TA00 ¦ ,Voltage Regeneration,
84873804measurement range | Same as RM17TA00 ¦ ,Extreme undervoltage,
84873804measurement range | Same as RM17TA00 ¦ ,Extreme Overvoltage,
84873804measurement range | Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873804tripping threshold | Same as RM17TA00 ¦ ,Phase cut,
84873804tripping threshold | Same as RM17TA00 ¦ ,Phase sequence,
84873804tripping threshold | Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode),
84873804tripping threshold | Same as RM17TA00 ¦ ,Over voltage,
84873804tripping threshold | Same as RM17TA00 ¦ ,Undervoltage ,
84873804tripping threshold | Same as RM17TA00 ¦ ,Phase asymmetry,
84873804tripping threshold | Same as RM17TA00 ¦ ,Disconnection of neutral,
84873804tripping threshold | Same as RM17TA00 ¦ ,Voltage Regeneration,
84873804tripping threshold | Same as RM17TA00 ¦ ,Extreme undervoltage (Phase loss),
84873804tripping threshold | When > 543V +/- 5% last longer than 2s +/- 10% , output de-energized When > 543V +/- 5% last shorter than 2s +/- 10% , output energized ¦ ,Extreme Overvoltage,
84873804tripping threshold | Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873804hysteresis | Same as RM17TA00 ¦ ,Phase cut,
84873804hysteresis | Same as RM17TA00 ¦ ,Phase sequence,
84873804hysteresis | Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode),
84873804hysteresis | Same as RM17TA00 ¦ ,Over voltage,
84873804hysteresis | Same as RM17TA00 ¦ ,Undervoltage ,
84873804hysteresis | Same as RM17TA00 ¦ ,Phase asymmetry,
84873804hysteresis | Same as RM17TA00 ¦ ,Disconnection of neutral,
84873804hysteresis | Same as RM17TA00 ¦ ,Voltage Regeneration,
84873804hysteresis | Same as RM17TA00 ¦ ,Extreme undervoltage (Phase loss),
84873804hysteresis | Same as RM17TA00 ¦ ,Extreme Overvoltage,
84873804hysteresis | Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873804
84873804output type | Same as RM17TA00
84873804output terminal | Same as RM17TA00
84873804output logic | Same as RM17TA00 ¦ ,R1 (11-12-14),
84873804output logic | Same as RM17TA00 ¦ ,R2 (21-22-24),
84873804contacts material | Same as RM17TA00
84873804mechanical durability | Same as RM17TA00 ¦ IEC61810-1
84873804electrical durability | Same as RM17TA00 ¦ IEC60947-4-1,AC-1,
84873804electrical durability | Same as RM17TA00 ¦ IEC60947-4-1,DC-1,
84873804electrical durability | Same as RM17TA00 ¦ IEC60947-5-1,AC-15,
84873804electrical durability | Same as RM17TA00 ¦ IEC60947-5-1,DC-13,
84873804[Ue] rated operational voltage | Same as RM17TA00 ¦ IEC61810-1,Rated switching voltage,
84873804[Ie] rated operational current | Same as RM17TA00 ¦ IEC61810-1,Rated switching current,
84873804maximum switching capacity | Same as RM17TA00 ¦ ,Maximum switching voltage,
84873804maximum switching capacity | Same as RM17TA00 ¦ ,Maximum switching current,
84873804maximum switching capacity | Same as RM17TA00 ¦ ,Maximum switching capacity,
84873804minimum switching capacity | Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching voltage,
84873804minimum switching capacity | Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching current,
84873804minimum switching capacity | Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching capacity,
84873804maximum voltage drop | Same as RM17TA00 ¦ IEC62314,Only for solid state output,
84873804maximum leakage current | Same as RM17TA00 ¦ IEC62314,Only for solid state output,
84873804thermal current | Same as RM17TA00 ¦ IEC60947-5-1
84873804short circuit protection | Same as RM17TA00 ¦ IEC60947-5-1,Relay Output by external fuse,
84873804short circuit protection | Same as RM17TA00 ¦ IEC62314,Solid State Output by external fuse,
84873804
84873804time delay type | Same as RM17TA00 ¦ ,"OFF" delay,
84873804time delay type | Same as RM17TA00 ¦ ,"ON" delay,
84873804time delay type | Same as RM17TA00 ¦ ,Inhibition,
84873804time delay range | Same as RM17TA00 ¦ ,"OFF" delay,
84873804time delay range | Same as RM17TA00 ¦ ,"ON" delay,
84873804time delay range | Same as RM17TA00 ¦ ,Inhibition,
84873804response time | Same as RM17TA00 ¦ ,on crossing the threshold,
84873804response time | Same as RM17TA00
84873804response time | Same as RM17TA00
84873804response time | Same as RM17TA00
84873804response time | Same as RM17TA00
84873804power on delay | Same as RM17TA00
84873804reset time | Same as RM17TA00 ¦ ,through Un power reset,
84873804reset time | Same as RM17TA00 ¦ ,through front panel reset,
84873804reset time | Same as RM17TA00 ¦ ,through input control reset,
84873804setting accuracy of time delay | Same as RM17TA00
84873804repeat accuracy of time delay | Same as RM17TA00
84873804time delay drift | Same as RM17TA00
84873804time delay drift | Same as RM17TA00
84873804
84873804status LED | Same as RM17TA00
84873804local signalling | Same as RM17TA00 ¦ ,Power supply availability,
84873804local signalling | Same as RM17TA00 ¦ ,Power supply not availability,
84873804local signalling | Same as RM17TA00 ¦ ,Timing in-progress,
84873804local signalling | Same as RM17TA00 ¦ ,Output is energized,
84873804local signalling | Same as RM17TA00 ¦ ,Output is de-energized,
84873804local signalling | Same as RM17TA00 ¦ ,Range Setting Changes,
84873804local signalling | Same as RM17TA00 ¦ ,Phase Cut,
84873804local signalling | Same as RM17TA00 ¦ ,Phase Sequence Swap,
84873804local signalling | Same as RM17TA00 ¦ ,Undervoltage <U,
84873804local signalling | Same as RM17TA00 ¦ ,Overvoltage >U,
84873804local signalling | Same as RM17TA00 ¦ ,Phase Asymmetry,
84873804local signalling | Same as RM17TA00 ¦ ,Voltage Regeneration,
84873804local signalling | Same as RM17TA00 ¦ ,Extreme Undervoltage <U (Phase loss),
84873804local signalling | Same as RM17TA00 ¦ ,Extreme Overvoltage >U,
84873804local signalling | Same as RM17TA00 ¦ ,Extreme Phase Asymmetry,
84873804
84873804 | Same as RM17TA00
84873804 | Same as RM17TA00
84873804diagnostic button | Same as RM17TA00
84873804 | Same as RM17TA00
84873804 | Same as RM17TA00
84873804
84873804safety reliability data | Same as RM17TA00 ¦ ,MTTF,
84873804safety reliability data | Same as RM17TA00 ¦ ,B10,
84873804 | Same as RM17TA00 ¦ ,MTTFd,
84873804 | Same as RM17TA00 ¦ ,B10d,
84873804
84873804 | Drawing / Diagram
RM17TT00
RM17TT00standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM17TT00product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TT00marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TT00directives | 2014/35/EU
RM17TT00directives | 2014/30/EU
RM17TT00directives | 2011/65/EU
RM17TT00
RM17TT00 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM17TT00 | Class C ¦ Germanisher Lloyd,Environmental category,
RM17TT00ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM17TT00ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM17TT00relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM17TT00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM17TT00vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM17TT00shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM17TT00bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM17TT00seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM17TT00IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM17TT00IP degree of protection | IP30 ¦ IEC60529,Housing,
RM17TT00IP degree of protection | - ¦ IEC60529,Front Panel,
RM17TT00
RM17TT00width | 17.5 ¦ ,Width,
RM17TT00height | 90 ¦ ,Height,
RM17TT00depth | 72 ¦ ,Depth,
RM17TT00net weight | 80
RM17TT00mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM17TT00mounting support | - ¦ IEC/EN 60715,With socket,
RM17TT00mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM17TT00Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM17TT00Minimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM17TT00connections - terminals | 1 conductor: 0.5…4 (AWG 20…AWG 11) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM17TT00connections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM17TT00connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM17TT00connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM17TT00tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM17TT00cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM17TT00duty time | 1
RM17TT00
RM17TT00electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM17TT00electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM17TT00electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM17TT00electromagnetic compatibility | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM17TT00electromagnetic compatibility | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge,
RM17TT00electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM17TT00electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM17TT00electromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM17TT00electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM17TT00electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM17TT00electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM17TT00electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM17TT00electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM17TT00electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM17TT00electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM17TT00electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM17TT00electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM17TT00electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM17TT00electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM17TT00
RM17TT00pollution degree | 3 ¦ IEC60664-1
RM17TT00overvoltage category | 3 ¦ IEC60664-1
RM17TT00circuit group | L1, L2, L3 ¦ ,Supply,Terminal
RM17TT00circuit group | - ¦ ,Input 1,
RM17TT00circuit group | - ¦ ,Input 2,
RM17TT00circuit group | - ¦ ,Input 3,
RM17TT00circuit group | 11,12,14 ¦ ,Output 1,
RM17TT00circuit group | - ¦ ,Output 2,
RM17TT00 | 208..480 AC ¦ ,Supply,Rated
RM17TT00 | - ¦ ,Input 1,Voltage
RM17TT00 | - ¦ ,Input 2,Spec
RM17TT00 | - ¦ ,Input 3,
RM17TT00 | 250V ¦ ,Output 1,
RM17TT00 | - ¦ ,Output 2,
RM17TT00[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM17TT00[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Output 2,
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM17TT00[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Output 2,
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Output 1 / Output 2,
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM17TT00[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM17TT00[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM17TT00[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Output 2,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1 / Output 2,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM17TT00[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM17TT00dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM17TT00dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM17TT00dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM17TT00dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM17TT00dielectric strength | - ¦ IEC60255-27,Supply / Output 2,
RM17TT00dielectric strength | - ¦ IEC60255-27,Output 1 / Output 2,
RM17TT00dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM17TT00dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM17TT00dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM17TT00dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM17TT00dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM17TT00dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM17TT00dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM17TT00dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM17TT00dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM17TT00insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM17TT00insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM17TT00insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM17TT00insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM17TT00insulation resistance | - ¦ IEC60255-27,Supply / Output 2,
RM17TT00insulation resistance | - ¦ IEC60255-27,Output 1 / Output 2,
RM17TT00insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM17TT00insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM17TT00insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM17TT00insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM17TT00insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM17TT00insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM17TT00insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM17TT00insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM17TT00insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM17TT00
RM17TT00[Us] rated supply voltage | ~ 3 x 208…3 x 480
RM17TT00supply voltage limits | ~ 3 x 183…3 x 528
RM17TT00polarity | -
RM17TT00supply frequency | 50 / 60
RM17TT00supply frequency | 45…66
RM17TT00power consumption | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz
RM17TT00immunity to microbreaks | 0
RM17TT00supply terminal | L1-L3
RM17TT00on-load factor | 1
RM17TT00release of input voltage | -
RM17TT00
RM17TT00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost ,
RM17TT00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence,
RM17TT00monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17TT00monitoring functions | - ¦ ,Over voltage,
RM17TT00monitoring functions | - ¦ ,Undervoltage ,
RM17TT00monitoring functions | - ¦ ,Phase asymmetry,
RM17TT00monitoring functions | - ¦ ,Disconnection of neutral,
RM17TT00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Voltage Regeneration,
RM17TT00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage,
RM17TT00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage,
RM17TT00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM17TT00 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM17TT00internal input resistance | - ¦ ,Internal input resistance,
RM17TT00input terminal | L1-L2-L3 ¦ ,Input terminal,
RM17TT00Input nominal voltage selection | 208, 220, 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM17TT00permissible input overload | - ¦ ,permissible input overload,
RM17TT00input frequency | 50 / 60 ¦ ,Rated frequency,
RM17TT00input frequency | 45…66 ¦ ,Frequency operating range,
RM17TT00setting accuracy of the switching threshold | - ¦ ,Setting accuracy,
RM17TT00repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM17TT00measurement method | True RMS ¦ ,Measurement method,
RM17TT00switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation,
RM17TT00switching threshold drift | < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM17TT00maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM17TT00measurement range | - ¦ ,Phase lost ,
RM17TT00measurement range | - ¦ ,Phase sequence,
RM17TT00measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17TT00measurement range | - ¦ ,Over voltage,
RM17TT00measurement range | - ¦ ,Undervoltage ,
RM17TT00measurement range | - ¦ ,Phase asymmetry,
RM17TT00measurement range | - ¦ ,Disconnection of neutral,
RM17TT00measurement range | - ¦ ,Voltage Regeneration,
RM17TT00measurement range | - ¦ ,Extreme undervoltage,
RM17TT00measurement range | - ¦ ,Extreme Overvoltage,
RM17TT00measurement range | - ¦ ,Extreme Asymmetry,
RM17TT00tripping threshold | 1 or more phase cut ¦ ,Phase cut,
RM17TT00tripping threshold | Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence,
RM17TT00tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17TT00tripping threshold | - ¦ ,Over voltage,
RM17TT00tripping threshold | - ¦ ,Undervoltage ,
RM17TT00tripping threshold | - ¦ ,Phase asymmetry,
RM17TT00tripping threshold | - ¦ ,Disconnection of neutral,
RM17TT00tripping threshold | 1 or more phase < 70% of selected Un Internal design spec: 30% +/- 5% ¦ ,Voltage Regeneration,
RM17TT00tripping threshold | 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM17TT00tripping threshold | Internal design spec: 543V +/- 5% ¦ ,Extreme Overvoltage,
RM17TT00tripping threshold | Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM17TT00hysteresis | All phase cut recover ¦ ,Phase cut,
RM17TT00hysteresis | Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence,
RM17TT00hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17TT00hysteresis | - ¦ ,Over voltage,
RM17TT00hysteresis | - ¦ ,Undervoltage ,
RM17TT00hysteresis | - ¦ ,Phase asymmetry,
RM17TT00hysteresis | - ¦ ,Disconnection of neutral,
RM17TT00hysteresis | 0.3 ¦ ,Voltage Regeneration,
RM17TT00hysteresis | All phases > 195V Internal design spec: All phases >180V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM17TT00hysteresis | Internal design spec: All phases <533V +/- 5% ¦ ,Extreme Overvoltage,
RM17TT00hysteresis | - ¦ ,Extreme Asymmetry,
RM17TT00
RM17TT00output type | 1 x C/O relay contacts
RM17TT00output terminal | 11-12-14
RM17TT00output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM17TT00output logic | - ¦ ,R2 (21-22-24),
RM17TT00contacts material | Cadmium free
RM17TT00mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM17TT00electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM17TT00electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM17TT00electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM17TT00electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM17TT00[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM17TT00[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM17TT00maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM17TT00maximum switching capacity | 5A ¦ ,Maximum switching current,
RM17TT00maximum switching capacity | - ¦ ,Maximum switching capacity,
RM17TT00minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM17TT00minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM17TT00minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM17TT00maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM17TT00maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM17TT00thermal current | 5A ¦ IEC60947-5-1
RM17TT00short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse,
RM17TT00short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM17TT00
RM17TT00time delay type | - ¦ ,"OFF" delay,
RM17TT00time delay type | - ¦ ,"ON" delay,
RM17TT00time delay type | - ¦ ,Inhibition,
RM17TT00time delay range | - ¦ ,"OFF" delay,
RM17TT00time delay range | - ¦ ,"ON" delay,
RM17TT00time delay range | - ¦ ,Inhibition,
RM17TT00response time | 0
RM17TT00response time | -
RM17TT00response time | -
RM17TT00response time | -
RM17TT00response time | -
RM17TT00power on delay | 0
RM17TT00reset time | 0
RM17TT00reset time | - ¦ ,through front panel reset,
RM17TT00reset time | - ¦ ,through input control reset,
RM17TT00setting accuracy of time delay | -
RM17TT00repeat accuracy of time delay | -
RM17TT00time delay drift | -
RM17TT00time delay drift | -
RM17TT00
RM17TT00status LED | Un (Green) R (Amber)
RM17TT00local signalling | Un - ON ¦ ,Power supply availability,
RM17TT00local signalling | Un - OFF ¦ ,Power supply not availability,
RM17TT00local signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM17TT00local signalling | R - ON ¦ ,Output is energized,
RM17TT00local signalling | R - OFF ¦ ,Output is de-energized,
RM17TT00local signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM17TT00local signalling | - ¦ ,Phase Cut,
RM17TT00local signalling | - ¦ ,Phase Sequence Swap,
RM17TT00local signalling | - ¦ ,Undervoltage <U,
RM17TT00local signalling | - ¦ ,Overvoltage >U,
RM17TT00local signalling | - ¦ ,Phase Asymmetry,
RM17TT00local signalling | - ¦ ,Voltage Regeneration,
RM17TT00local signalling | - ¦ ,Extreme Undervoltage <U (Phase loss),
RM17TT00local signalling | - ¦ ,Extreme Overvoltage >U,
RM17TT00local signalling | - ¦ ,Extreme Phase Asymmetry,
RM17TT00
RM17TT00 | Yes
RM17TT00 | -
RM17TT00diagnostic button | -
RM17TT00 | -
RM17TT00 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM17TT00
RM17TT00safety reliability data | 4,400,000 hours ¦ ,MTTF,
RM17TT00safety reliability data | 470,000 hours ¦ ,B10,
RM17TT00 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM17TT00 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM17TT00
RM17TT00 | Drawing / Diagram
84873022
84873022standards | Same as RM17TT00
84873022product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873022marking | UL, CSA, GL, CCC, CE, China ROHS
84873022directives | Same as RM17TT00
84873022directives | Same as RM17TT00
84873022directives | Same as RM17TT00
84873022
84873022 | Same as RM17TT00 ¦ IEC60721-3-3,Climatic category,
84873022 | Same as RM17TT00 ¦ Germanisher Lloyd,Environmental category,
84873022ambient air temperature for storage | Same as RM17TT00 ¦ ,Storage,
84873022ambient air temperature for operation | Same as RM17TT00 ¦ ,Operation,
84873022relative humidity | Same as RM17TT00 ¦ IEC60068-2-30,Damp heat,XX
84873022 | Same as RM17TT00 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873022vibration resistance | Same as RM17TT00 ¦ IEC60068-2-6
84873022shock resistance | Same as RM17TT00 ¦ IEC60068-2-27
84873022bump resistance | Same as RM17TT00 ¦ IEC60068-2-29
84873022seismic resistance | Same as RM17TT00 ¦ IEC60068-3-3
84873022IP degree of protection | Same as RM17TT00 ¦ IEC60529,Terminal Block,
84873022IP degree of protection | Same as RM17TT00 ¦ IEC60529,Housing,
84873022IP degree of protection | Same as RM17TT00 ¦ IEC60529,Front Panel,
84873022
84873022width | Same as RM17TT00 ¦ ,Width,
84873022height | Same as RM17TT00 ¦ ,Height,
84873022depth | Same as RM17TT00 ¦ ,Depth,
84873022net weight | Same as RM17TT00
84873022mounting support | Same as RM17TT00 ¦ IEC/EN 60715,Without socket,
84873022mounting support | Same as RM17TT00 ¦ IEC/EN 60715,With socket,
84873022mounting position | Same as RM17TT00 ¦ ,In relation to normal vertical mounting plane,
84873022Minimum distance to adjacent devices | Same as RM17TT00 ¦ ,Horizontal,
84873022Minimum distance to adjacent devices | Same as RM17TT00 ¦ ,Vertical,
84873022connections - terminals | Same as RM17TT00 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873022connections - terminals | Same as RM17TT00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873022connections - terminals | Same as RM17TT00 ¦ IEC60947-1,Solid cable (spring terminal),
84873022connections - terminals | Same as RM17TT00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873022tightening torque | Same as RM17TT00 ¦ IEC60947-1,Tightening torque,
84873022cable stripping length | Same as RM17TT00 ¦ ,Cable stripping length,
84873022duty time | Same as RM17TT00
84873022
84873022electromagnetic compatibility | Same as RM17TT00 ¦ ,Generic immunity standard,
84873022electromagnetic compatibility | Same as RM17TT00 ¦ IEC61000-4-2,Electrostatic discharge,
84873022electromagnetic compatibility | Same as RM17TT00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873022electromagnetic compatibility | Same as RM17TT00 ¦ IEC61000-4-4,Fast transient / burst,
84873022electromagnetic compatibility | Same as RM17TT00 ¦ IEC61000-4-5,Surge,
84873022electromagnetic compatibility | Same as RM17TT00 ¦ IEC61000-4-6,Conducted RF disturbance,
84873022electromagnetic compatibility | Same as RM17TT00 ¦ IEC61000-4-8,Power frequency magnetic field,
84873022electromagnetic compatibility | Same as RM17TT00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873022electromagnetic compatibility | Same as RM17TT00 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873022electromagnetic compatibility | Same as RM17TT00 ¦ IEC61000-4-29,DC voltage interruption,
84873022electromagnetic compatibility | Same as RM17TT00 ¦ IEC61000-4-13,Low frequency harmonics,
84873022electromagnetic compatibility | Same as RM17TT00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873022electromagnetic compatibility | Same as RM17TT00 ¦ ,Generic emission standard,
84873022electromagnetic compatibility | Same as RM17TT00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873022electromagnetic compatibility | Same as RM17TT00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873022electromagnetic compatibility | Same as RM17TT00 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873022electromagnetic compatibility | Same as RM17TT00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873022electromagnetic compatibility | Same as RM17TT00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873022electromagnetic compatibility | Same as RM17TT00 ¦ Germanisher Lloyd,Conducted emission,
84873022
84873022pollution degree | Same as RM17TT00 ¦ IEC60664-1
84873022overvoltage category | Same as RM17TT00 ¦ IEC60664-1
84873022circuit group | Same as RM17TT00 ¦ ,Supply,Terminal
84873022circuit group | Same as RM17TT00 ¦ ,Input 1,
84873022circuit group | Same as RM17TT00 ¦ ,Input 2,
84873022circuit group | Same as RM17TT00 ¦ ,Input 3,
84873022circuit group | Same as RM17TT00 ¦ ,Output 1,
84873022circuit group | Same as RM17TT00 ¦ ,Output 2,
84873022 | Same as RM17TT00 ¦ ,Supply,Rated
84873022 | Same as RM17TT00 ¦ ,Input 1,Voltage
84873022 | Same as RM17TT00 ¦ ,Input 2,Spec
84873022 | Same as RM17TT00 ¦ ,Input 3,
84873022 | Same as RM17TT00 ¦ ,Output 1,
84873022 | Same as RM17TT00 ¦ ,Output 2,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Supply,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Input 1,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Input 2,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Input 3,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Output 1,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Output 2,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Supply / Output 1,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Supply / Output 2,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Output 1 / Output 2,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Input 1 / Output 1,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Input 1 / Output 2,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Input 2 / Output 1,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Input 2 / Output 2,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Input 3 / Output 1,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Input 3 / Output 2,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Input 1 / Input 2,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Input 2 / Input 3,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Input 1 / Input 3,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Supply,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Input 1,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Input 2,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Input 3,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Output 1,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Output 2,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Supply / Input 2,Isolated
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Supply / Input 3,Circuit
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Supply / Output 1,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Supply / Output 2,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Output 1 / Output 2,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Input 1 / Output 1,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Input 1 / Output 2,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Input 2 / Output 1,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Input 2 / Output 2,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Input 3 / Output 1,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Input 3 / Output 2,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Input 1 / Input 2,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Input 2 / Input 3,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Input 1 / Input 3,
84873022dielectric strength | Same as RM17TT00 ¦ IEC60255-27,Supply / Input 1,
84873022dielectric strength | Same as RM17TT00 ¦ IEC60255-27,Supply / Input 2,
84873022dielectric strength | Same as RM17TT00 ¦ IEC60255-27,Supply / Input 3,
84873022dielectric strength | Same as RM17TT00 ¦ IEC60255-27,Supply / Output 1,
84873022dielectric strength | Same as RM17TT00 ¦ IEC60255-27,Supply / Output 2,
84873022dielectric strength | Same as RM17TT00 ¦ IEC60255-27,Output 1 / Output 2,
84873022dielectric strength | Same as RM17TT00 ¦ IEC60255-27,Input 1 / Output 1,
84873022dielectric strength | Same as RM17TT00 ¦ IEC60255-27,Input 1 / Output 2,
84873022dielectric strength | Same as RM17TT00 ¦ IEC60255-27,Input 2 / Output 1,
84873022dielectric strength | Same as RM17TT00 ¦ IEC60255-27,Input 2 / Output 2,
84873022dielectric strength | Same as RM17TT00 ¦ IEC60255-27,Input 3 / Output 1,
84873022dielectric strength | Same as RM17TT00 ¦ IEC60255-27,Input 3 / Output 2,
84873022dielectric strength | Same as RM17TT00 ¦ IEC60255-27,Input 1 / Input 2,
84873022dielectric strength | Same as RM17TT00 ¦ IEC60255-27,Input 2 / Input 3,
84873022dielectric strength | Same as RM17TT00 ¦ IEC60255-27,Input 1 / Input 3,
84873022insulation resistance | Same as RM17TT00 ¦ IEC60255-27,Supply / Input 1,
84873022insulation resistance | Same as RM17TT00 ¦ IEC60255-27,Supply / Input 2,
84873022insulation resistance | Same as RM17TT00 ¦ IEC60255-27,Supply / Input 3,
84873022insulation resistance | Same as RM17TT00 ¦ IEC60255-27,Supply / Output 1,
84873022insulation resistance | Same as RM17TT00 ¦ IEC60255-27,Supply / Output 2,
84873022insulation resistance | Same as RM17TT00 ¦ IEC60255-27,Output 1 / Output 2,
84873022insulation resistance | Same as RM17TT00 ¦ IEC60255-27,Input 1 / Output 1,
84873022insulation resistance | Same as RM17TT00 ¦ IEC60255-27,Input 1 / Output 2,
84873022insulation resistance | Same as RM17TT00 ¦ IEC60255-27,Input 2 / Output 1,
84873022insulation resistance | Same as RM17TT00 ¦ IEC60255-27,Input 2 / Output 2,
84873022insulation resistance | Same as RM17TT00 ¦ IEC60255-27,Input 3 / Output 1,
84873022insulation resistance | Same as RM17TT00 ¦ IEC60255-27,Input 3 / Output 2,
84873022insulation resistance | Same as RM17TT00 ¦ IEC60255-27,Input 1 / Input 2,
84873022insulation resistance | Same as RM17TT00 ¦ IEC60255-27,Input 2 / Input 3,
84873022insulation resistance | Same as RM17TT00 ¦ IEC60255-27,Input 1 / Input 3,
84873022
84873022[Us] rated supply voltage | Same as RM17TT00
84873022supply voltage limits | Same as RM17TT00
84873022polarity | Same as RM17TT00
84873022supply frequency | Same as RM17TT00
84873022supply frequency | Same as RM17TT00
84873022power consumption | Same as RM17TT00
84873022immunity to microbreaks | Same as RM17TT00
84873022supply terminal | Same as RM17TT00
84873022on-load factor | Same as RM17TT00
84873022release of input voltage | Same as RM17TT00
84873022
84873022monitoring functions | Same as RM17TT00 ¦ ,Phase lost ,
84873022monitoring functions | Same as RM17TT00 ¦ ,Phase sequence,
84873022monitoring functions | Same as RM17TT00 ¦ ,Over / undervoltage (symmetry windows mode),
84873022monitoring functions | Same as RM17TT00 ¦ ,Over voltage,
84873022monitoring functions | Same as RM17TT00 ¦ ,Undervoltage ,
84873022monitoring functions | Same as RM17TT00 ¦ ,Phase asymmetry,
84873022monitoring functions | Same as RM17TT00 ¦ ,Disconnection of neutral,
84873022monitoring functions | Same as RM17TT00 ¦ ,Voltage Regeneration,
84873022monitoring functions | Same as RM17TT00 ¦ ,Extreme undervoltage,
84873022monitoring functions | Same as RM17TT00 ¦ ,Extreme overvoltage,
84873022monitoring functions | Same as RM17TT00 ¦ ,Extreme asymmetry,
84873022 | Same as RM17TT00 ¦ ,Measurement mode,
84873022internal input resistance | Same as RM17TT00 ¦ ,Internal input resistance,
84873022input terminal | Same as RM17TT00 ¦ ,Input terminal,
84873022Input nominal voltage selection | Same as RM17TT00 ¦ ,Input nominal voltage selection,
84873022permissible input overload | Same as RM17TT00 ¦ ,permissible input overload,
84873022input frequency | Same as RM17TT00 ¦ ,Rated frequency,
84873022input frequency | Same as RM17TT00 ¦ ,Frequency operating range,
84873022setting accuracy of the switching threshold | Same as RM17TT00 ¦ ,Setting accuracy,
84873022repeat accuracy of the switching threshold | Same as RM17TT00 ¦ ,Repeat accuracy (constant parameters),
84873022measurement method | Same as RM17TT00 ¦ ,Measurement method,
84873022switching threshold drift | Same as RM17TT00 ¦ ,Measurement error with supply voltage variation,
84873022switching threshold drift | Same as RM17TT00 ¦ ,Measurement error with temperature variation,
84873022maximum measuring cycle | Same as RM17TT00 ¦ ,Maximum measuring cycles,
84873022measurement range | Same as RM17TT00 ¦ ,Phase lost ,
84873022measurement range | Same as RM17TT00 ¦ ,Phase sequence,
84873022measurement range | Same as RM17TT00 ¦ ,Over / undervoltage (symmetry windows mode),
84873022measurement range | Same as RM17TT00 ¦ ,Over voltage,
84873022measurement range | Same as RM17TT00 ¦ ,Undervoltage ,
84873022measurement range | Same as RM17TT00 ¦ ,Phase asymmetry,
84873022measurement range | Same as RM17TT00 ¦ ,Disconnection of neutral,
84873022measurement range | Same as RM17TT00 ¦ ,Voltage Regeneration,
84873022measurement range | Same as RM17TT00 ¦ ,Extreme undervoltage,
84873022measurement range | Same as RM17TT00 ¦ ,Extreme Overvoltage,
84873022measurement range | Same as RM17TT00 ¦ ,Extreme Asymmetry,
84873022tripping threshold | Same as RM17TT00 ¦ ,Phase cut,
84873022tripping threshold | Same as RM17TT00 ¦ ,Phase sequence,
84873022tripping threshold | Same as RM17TT00 ¦ ,Over / undervoltage (symmetry windows mode),
84873022tripping threshold | Same as RM17TT00 ¦ ,Over voltage,
84873022tripping threshold | Same as RM17TT00 ¦ ,Undervoltage ,
84873022tripping threshold | Same as RM17TT00 ¦ ,Phase asymmetry,
84873022tripping threshold | Same as RM17TT00 ¦ ,Disconnection of neutral,
84873022tripping threshold | Same as RM17TT00 ¦ ,Voltage Regeneration,
84873022tripping threshold | Same as RM17TT00 ¦ ,Extreme undervoltage (Phase loss),
84873022tripping threshold | Same as RM17TT00 ¦ ,Extreme Overvoltage,
84873022tripping threshold | Same as RM17TT00 ¦ ,Extreme Asymmetry,
84873022hysteresis | Same as RM17TT00 ¦ ,Phase cut,
84873022hysteresis | Same as RM17TT00 ¦ ,Phase sequence,
84873022hysteresis | Same as RM17TT00 ¦ ,Over / undervoltage (symmetry windows mode),
84873022hysteresis | Same as RM17TT00 ¦ ,Over voltage,
84873022hysteresis | Same as RM17TT00 ¦ ,Undervoltage ,
84873022hysteresis | Same as RM17TT00 ¦ ,Phase asymmetry,
84873022hysteresis | Same as RM17TT00 ¦ ,Disconnection of neutral,
84873022hysteresis | Same as RM17TT00 ¦ ,Voltage Regeneration,
84873022hysteresis | Same as RM17TT00 ¦ ,Extreme undervoltage (Phase loss),
84873022hysteresis | Same as RM17TT00 ¦ ,Extreme Overvoltage,
84873022hysteresis | Same as RM17TT00 ¦ ,Extreme Asymmetry,
84873022
84873022output type | Same as RM17TT00
84873022output terminal | Same as RM17TT00
84873022output logic | Same as RM17TT00 ¦ ,R1 (11-12-14),
84873022output logic | Same as RM17TT00 ¦ ,R2 (21-22-24),
84873022contacts material | Same as RM17TT00
84873022mechanical durability | Same as RM17TT00 ¦ IEC61810-1
84873022electrical durability | Same as RM17TT00 ¦ IEC60947-4-1,AC-1,
84873022electrical durability | Same as RM17TT00 ¦ IEC60947-4-1,DC-1,
84873022electrical durability | Same as RM17TT00 ¦ IEC60947-5-1,AC-15,
84873022electrical durability | Same as RM17TT00 ¦ IEC60947-5-1,DC-13,
84873022[Ue] rated operational voltage | Same as RM17TT00 ¦ IEC61810-1,Rated switching voltage,
84873022[Ie] rated operational current | Same as RM17TT00 ¦ IEC61810-1,Rated switching current,
84873022maximum switching capacity | Same as RM17TT00 ¦ ,Maximum switching voltage,
84873022maximum switching capacity | Same as RM17TT00 ¦ ,Maximum switching current,
84873022maximum switching capacity | Same as RM17TT00 ¦ ,Maximum switching capacity,
84873022minimum switching capacity | Same as RM17TT00 ¦ IEC60947-5-4,Minimum switching voltage,
84873022minimum switching capacity | Same as RM17TT00 ¦ IEC60947-5-4,Minimum switching current,
84873022minimum switching capacity | Same as RM17TT00 ¦ IEC60947-5-4,Minimum switching capacity,
84873022maximum voltage drop | Same as RM17TT00 ¦ IEC62314,Only for solid state output,
84873022maximum leakage current | Same as RM17TT00 ¦ IEC62314,Only for solid state output,
84873022thermal current | Same as RM17TT00 ¦ IEC60947-5-1
84873022short circuit protection | Same as RM17TT00 ¦ IEC60947-5-1,Relay Output by external fuse,
84873022short circuit protection | Same as RM17TT00 ¦ IEC62314,Solid State Output by external fuse,
84873022
84873022time delay type | Same as RM17TT00 ¦ ,"OFF" delay,
84873022time delay type | Same as RM17TT00 ¦ ,"ON" delay,
84873022time delay type | Same as RM17TT00 ¦ ,Inhibition,
84873022time delay range | Same as RM17TT00 ¦ ,"OFF" delay,
84873022time delay range | Same as RM17TT00 ¦ ,"ON" delay,
84873022time delay range | Same as RM17TT00 ¦ ,Inhibition,
84873022response time | Same as RM17TT00 ¦ ,on crossing the threshold,
84873022response time | Same as RM17TT00
84873022response time | Same as RM17TT00
84873022response time | Same as RM17TT00
84873022response time | Same as RM17TT00
84873022power on delay | Same as RM17TT00
84873022reset time | Same as RM17TT00 ¦ ,through Un power reset,
84873022reset time | Same as RM17TT00 ¦ ,through front panel reset,
84873022reset time | Same as RM17TT00 ¦ ,through input control reset,
84873022setting accuracy of time delay | Same as RM17TT00
84873022repeat accuracy of time delay | Same as RM17TT00
84873022time delay drift | Same as RM17TT00
84873022time delay drift | Same as RM17TT00
84873022
84873022status LED | Same as RM17TT00
84873022local signalling | Same as RM17TT00 ¦ ,Power supply availability,
84873022local signalling | Same as RM17TT00 ¦ ,Power supply not availability,
84873022local signalling | Same as RM17TT00 ¦ ,Timing in-progress,
84873022local signalling | Same as RM17TT00 ¦ ,Output is energized,
84873022local signalling | Same as RM17TT00 ¦ ,Output is de-energized,
84873022local signalling | Same as RM17TT00 ¦ ,Range Setting Changes,
84873022local signalling | Same as RM17TT00 ¦ ,Phase Cut,
84873022local signalling | Same as RM17TT00 ¦ ,Phase Sequence Swap,
84873022local signalling | Same as RM17TT00 ¦ ,Undervoltage <U,
84873022local signalling | Same as RM17TT00 ¦ ,Overvoltage >U,
84873022local signalling | Same as RM17TT00 ¦ ,Phase Asymmetry,
84873022local signalling | Same as RM17TT00 ¦ ,Voltage Regeneration,
84873022local signalling | Same as RM17TT00 ¦ ,Extreme Undervoltage <U (Phase loss),
84873022local signalling | Same as RM17TT00 ¦ ,Extreme Overvoltage >U,
84873022local signalling | Same as RM17TT00 ¦ ,Extreme Phase Asymmetry,
84873022
84873022 | Same as RM17TT00
84873022 | Same as RM17TT00
84873022diagnostic button | Same as RM17TT00
84873022 | Same as RM17TT00
84873022 | Same as RM17TT00
84873022
84873022safety reliability data | Same as RM17TT00 ¦ ,MTTF,
84873022safety reliability data | Same as RM17TT00 ¦ ,B10,
84873022 | Same as RM17TT00 ¦ ,MTTFd,
84873022 | Same as RM17TT00 ¦ ,B10d,
84873022
84873022 | Drawing / Diagram
RM35TF30
RM35TF30standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM35TF30product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35TF30marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35TF30directives | 2014/35/EU
RM35TF30directives | 2014/30/EU
RM35TF30directives | 2011/65/EU
RM35TF30
RM35TF30 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM35TF30 | Class C ¦ Germanisher Lloyd,Environmental category,
RM35TF30ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM35TF30ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM35TF30relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM35TF30 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM35TF30vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM35TF30shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM35TF30bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM35TF30seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM35TF30IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM35TF30IP degree of protection | IP30 ¦ IEC60529,Housing,
RM35TF30IP degree of protection | - ¦ IEC60529,Front Panel,
RM35TF30
RM35TF30width | 35 ¦ ,Width,
RM35TF30height | 90 ¦ ,Height,
RM35TF30depth | 72 ¦ ,Depth,
RM35TF30net weight | 120
RM35TF30mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM35TF30mounting support | - ¦ IEC/EN 60715,With socket,
RM35TF30mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35TF30Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM35TF30Minimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM35TF30connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35TF30connections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35TF30connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM35TF30connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35TF30tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM35TF30cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM35TF30duty time | 1
RM35TF30
RM35TF30electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM35TF30electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM35TF30electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM35TF30electromagnetic compatibility | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM35TF30electromagnetic compatibility | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge,
RM35TF30electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM35TF30electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM35TF30electromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35TF30electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM35TF30electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM35TF30electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM35TF30electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35TF30electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM35TF30electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35TF30electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35TF30electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM35TF30electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35TF30electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35TF30electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35TF30
RM35TF30pollution degree | 3 ¦ IEC60664-1
RM35TF30overvoltage category | 3 ¦ IEC60664-1
RM35TF30circuit group | L1, L2, L3 ¦ ,Supply,Terminal
RM35TF30circuit group | - ¦ ,Input 1,
RM35TF30circuit group | - ¦ ,Input 2,
RM35TF30circuit group | - ¦ ,Input 3,
RM35TF30circuit group | 11,12,14 ¦ ,Output 1,
RM35TF30circuit group | 21,22,24 ¦ ,Output 2,
RM35TF30 | 208..480 AC ¦ ,Supply,Rated
RM35TF30 | - ¦ ,Input 1,Voltage
RM35TF30 | - ¦ ,Input 2,Spec
RM35TF30 | - ¦ ,Input 3,
RM35TF30 | 250V ¦ ,Output 1,
RM35TF30 | 250V ¦ ,Output 2,
RM35TF30[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM35TF30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM35TF30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM35TF30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM35TF30[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM35TF30[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM35TF30[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35TF30[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM35TF30[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM35TF30[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM35TF30[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 2,
RM35TF30[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM35TF30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM35TF30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM35TF30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM35TF30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM35TF30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM35TF30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM35TF30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM35TF30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM35TF30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM35TF30[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM35TF30[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM35TF30[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM35TF30[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM35TF30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM35TF30dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM35TF30dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM35TF30dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM35TF30dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM35TF30dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM35TF30dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM35TF30dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM35TF30dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM35TF30dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM35TF30dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM35TF30dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM35TF30dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM35TF30dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM35TF30dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM35TF30dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM35TF30insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM35TF30insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM35TF30insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM35TF30insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM35TF30insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM35TF30insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM35TF30insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM35TF30insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM35TF30insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM35TF30insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM35TF30insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM35TF30insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM35TF30insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM35TF30insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM35TF30insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM35TF30
RM35TF30[Us] rated supply voltage | ~ 3 x 220…3 x 480
RM35TF30supply voltage limits | ~ 3 x 194…3 x 528
RM35TF30polarity | -
RM35TF30supply frequency | 50 / 60
RM35TF30supply frequency | 45…66
RM35TF30power consumption | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz
RM35TF30immunity to microbreaks | 0
RM35TF30supply terminal | L1-L3
RM35TF30on-load factor | 1
RM35TF30release of input voltage | -
RM35TF30
RM35TF30monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost ,
RM35TF30monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence,
RM35TF30monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM35TF30monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Over voltage,
RM35TF30monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Undervoltage ,
RM35TF30monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Phase asymmetry,
RM35TF30monitoring functions | - ¦ ,Disconnection of neutral,
RM35TF30monitoring functions | - ¦ ,Voltage Regeneration,
RM35TF30monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage,
RM35TF30monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage,
RM35TF30monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM35TF30 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM35TF30internal input resistance | - ¦ ,Internal input resistance,
RM35TF30input terminal | L1-L2-L3 ¦ ,Input terminal,
RM35TF30Input nominal voltage selection | 220, 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM35TF30permissible input overload | - ¦ ,permissible input overload,
RM35TF30input frequency | 50 / 60 ¦ ,Rated frequency,
RM35TF30input frequency | 45…66 ¦ ,Frequency operating range,
RM35TF30setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM35TF30repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM35TF30measurement method | True RMS ¦ ,Measurement method,
RM35TF30switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation,
RM35TF30switching threshold drift | < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM35TF30maximum measuring cycle | 140ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM35TF30measurement range | - ¦ ,Phase lost ,
RM35TF30measurement range | - ¦ ,Phase sequence,
RM35TF30measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM35TF30measurement range | +2…+20 % in the ranges 3 x ~ 220…440 +2…+10 % in the range 3 x ~ 480 ¦ ,Over voltage,
RM35TF30measurement range | -12…-2 % in the range 3 x ~ 220 -20…-2 % in the ranges 3 x ~ 380…480 ¦ ,Undervoltage ,
RM35TF30measurement range | +5…+15 % in the ranges 3 x ~ 220…480 ¦ ,Phase asymmetry,
RM35TF30measurement range | - ¦ ,Disconnection of neutral,
RM35TF30measurement range | - ¦ ,Voltage Regeneration,
RM35TF30measurement range | - ¦ ,Extreme undervoltage,
RM35TF30measurement range | - ¦ ,Extreme Overvoltage,
RM35TF30measurement range | - ¦ ,Extreme Asymmetry,
RM35TF30tripping threshold | 1 or more phase cut ¦ ,Phase cut,
RM35TF30tripping threshold | Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence,
RM35TF30tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM35TF30tripping threshold | Adjustable 2%...20% of selected Un ¦ ,Over voltage,
RM35TF30tripping threshold | Adjustable 2%...20% of selected Un ¦ ,Undervoltage ,
RM35TF30tripping threshold | Adjustable 5%...15% of selected Un ¦ ,Phase asymmetry,
RM35TF30tripping threshold | - ¦ ,Disconnection of neutral,
RM35TF30tripping threshold | - ¦ ,Voltage Regeneration,
RM35TF30tripping threshold | 1 or more phase < 150V Internal design spec: 1 or more phase <188V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM35TF30tripping threshold | Internal design spec: 543V +/- 5% ¦ ,Extreme Overvoltage,
RM35TF30tripping threshold | Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM35TF30hysteresis | All phase cut recover ¦ ,Phase cut,
RM35TF30hysteresis | Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence,
RM35TF30hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM35TF30hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Over voltage,
RM35TF30hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage ,
RM35TF30hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Phase asymmetry,
RM35TF30hysteresis | - ¦ ,Disconnection of neutral,
RM35TF30hysteresis | - ¦ ,Voltage Regeneration,
RM35TF30hysteresis | All phases > 205V Internal design spec: All phases >190V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM35TF30hysteresis | Internal design spec: All phases <533V +/- 5% ¦ ,Extreme Overvoltage,
RM35TF30hysteresis | - ¦ ,Extreme Asymmetry,
RM35TF30
RM35TF30output type | 2 x C/O relay contacts
RM35TF30output terminal | 11-12-14, 21-22-24
RM35TF30output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM35TF30output logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM35TF30contacts material | Cadmium free
RM35TF30mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM35TF30electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM35TF30electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM35TF30electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM35TF30electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM35TF30[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM35TF30[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM35TF30maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM35TF30maximum switching capacity | 5A ¦ ,Maximum switching current,
RM35TF30maximum switching capacity | - ¦ ,Maximum switching capacity,
RM35TF30minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM35TF30minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM35TF30minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM35TF30maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35TF30maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35TF30thermal current | 5A ¦ IEC60947-5-1
RM35TF30short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse,
RM35TF30short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM35TF30
RM35TF30time delay type | Yes ¦ ,"OFF" delay,
RM35TF30time delay type | - ¦ ,"ON" delay,
RM35TF30time delay type | - ¦ ,Inhibition,
RM35TF30time delay range | Adjustable 0.1…10 ¦ ,"OFF" delay,
RM35TF30time delay range | - ¦ ,"ON" delay,
RM35TF30time delay range | - ¦ ,Inhibition,
RM35TF30response time | 0
RM35TF30response time | -
RM35TF30response time | -
RM35TF30response time | -
RM35TF30response time | -
RM35TF30power on delay | 0
RM35TF30reset time | 0
RM35TF30reset time | - ¦ ,through front panel reset,
RM35TF30reset time | - ¦ ,through input control reset,
RM35TF30setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM35TF30repeat accuracy of time delay | +/- 3%
RM35TF30time delay drift | -
RM35TF30time delay drift | -
RM35TF30
RM35TF30status LED | Un (Green) R (Amber) Def (Amber)
RM35TF30local signalling | Un - ON ¦ ,Power supply availability,
RM35TF30local signalling | Un - OFF ¦ ,Power supply not availability,
RM35TF30local signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM35TF30local signalling | R - ON ¦ ,Output is energized,
RM35TF30local signalling | R - OFF ¦ ,Output is de-energized,
RM35TF30local signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM35TF30local signalling | Def - Permanent OFF ¦ ,Phase Cut,
RM35TF30local signalling | Def - Permanent OFF ¦ ,Phase Sequence Swap,
RM35TF30local signalling | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Undervoltage <U,
RM35TF30local signalling | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Overvoltage >U,
RM35TF30local signalling | Def - Permanent ON ¦ ,Phase Asymmetry,
RM35TF30local signalling | - ¦ ,Voltage Regeneration,
RM35TF30local signalling | Def - Permanent OFF ¦ ,Extreme Undervoltage <U (Phase loss),
RM35TF30local signalling | Def - Permanent OFF ¦ ,Extreme Overvoltage >U,
RM35TF30local signalling | Def - Permanent OFF ¦ ,Extreme Phase Asymmetry,
RM35TF30
RM35TF30 | Yes
RM35TF30 | -
RM35TF30diagnostic button | -
RM35TF30 | -
RM35TF30 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM35TF30
RM35TF30safety reliability data | 3,500,000 hours ¦ ,MTTF,
RM35TF30safety reliability data | 360,000 hours ¦ ,B10,
RM35TF30 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM35TF30 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM35TF30
RM35TF30 | Drawing / Diagram
84873026
84873026standards | Same as RM35TF30
84873026product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873026marking | UL, CSA, GL, CCC, CE, China ROHS
84873026directives | Same as RM35TF30
84873026directives | Same as RM35TF30
84873026directives | Same as RM35TF30
84873026
84873026 | Same as RM35TF30 ¦ IEC60721-3-3,Climatic category,
84873026 | Same as RM35TF30 ¦ Germanisher Lloyd,Environmental category,
84873026ambient air temperature for storage | Same as RM35TF30 ¦ ,Storage,
84873026ambient air temperature for operation | Same as RM35TF30 ¦ ,Operation,
84873026relative humidity | Same as RM35TF30 ¦ IEC60068-2-30,Damp heat,XX
84873026 | Same as RM35TF30 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873026vibration resistance | Same as RM35TF30 ¦ IEC60068-2-6
84873026shock resistance | Same as RM35TF30 ¦ IEC60068-2-27
84873026bump resistance | Same as RM35TF30 ¦ IEC60068-2-29
84873026seismic resistance | Same as RM35TF30 ¦ IEC60068-3-3
84873026IP degree of protection | Same as RM35TF30 ¦ IEC60529,Terminal Block,
84873026IP degree of protection | Same as RM35TF30 ¦ IEC60529,Housing,
84873026IP degree of protection | Same as RM35TF30 ¦ IEC60529,Front Panel,
84873026
84873026width | Same as RM35TF30 ¦ ,Width,
84873026height | Same as RM35TF30 ¦ ,Height,
84873026depth | Same as RM35TF30 ¦ ,Depth,
84873026net weight | Same as RM35TF30
84873026mounting support | Same as RM35TF30 ¦ IEC/EN 60715,Without socket,
84873026mounting support | Same as RM35TF30 ¦ IEC/EN 60715,With socket,
84873026mounting position | Same as RM35TF30 ¦ ,In relation to normal vertical mounting plane,
84873026Minimum distance to adjacent devices | Same as RM35TF30 ¦ ,Horizontal,
84873026Minimum distance to adjacent devices | Same as RM35TF30 ¦ ,Vertical,
84873026connections - terminals | Same as RM35TF30 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873026connections - terminals | Same as RM35TF30 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873026connections - terminals | Same as RM35TF30 ¦ IEC60947-1,Solid cable (spring terminal),
84873026connections - terminals | Same as RM35TF30 ¦ IEC60947-1,Flexible cable (spring terminal),
84873026tightening torque | Same as RM35TF30 ¦ IEC60947-1,Tightening torque,
84873026cable stripping length | Same as RM35TF30 ¦ ,Cable stripping length,
84873026duty time | Same as RM35TF30
84873026
84873026electromagnetic compatibility | Same as RM35TF30 ¦ ,Generic immunity standard,
84873026electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-2,Electrostatic discharge,
84873026electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873026electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-4,Fast transient / burst,
84873026electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-5,Surge,
84873026electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-6,Conducted RF disturbance,
84873026electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-8,Power frequency magnetic field,
84873026electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873026electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873026electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-29,DC voltage interruption,
84873026electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-13,Low frequency harmonics,
84873026electromagnetic compatibility | Same as RM35TF30 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873026electromagnetic compatibility | Same as RM35TF30 ¦ ,Generic emission standard,
84873026electromagnetic compatibility | Same as RM35TF30 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873026electromagnetic compatibility | Same as RM35TF30 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873026electromagnetic compatibility | Same as RM35TF30 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873026electromagnetic compatibility | Same as RM35TF30 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873026electromagnetic compatibility | Same as RM35TF30 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873026electromagnetic compatibility | Same as RM35TF30 ¦ Germanisher Lloyd,Conducted emission,
84873026
84873026pollution degree | Same as RM35TF30 ¦ IEC60664-1
84873026overvoltage category | Same as RM35TF30 ¦ IEC60664-1
84873026circuit group | Same as RM35TF30 ¦ ,Supply,Terminal
84873026circuit group | Same as RM35TF30 ¦ ,Input 1,
84873026circuit group | Same as RM35TF30 ¦ ,Input 2,
84873026circuit group | Same as RM35TF30 ¦ ,Input 3,
84873026circuit group | Same as RM35TF30 ¦ ,Output 1,
84873026circuit group | Same as RM35TF30 ¦ ,Output 2,
84873026 | Same as RM35TF30 ¦ ,Supply,Rated
84873026 | Same as RM35TF30 ¦ ,Input 1,Voltage
84873026 | Same as RM35TF30 ¦ ,Input 2,Spec
84873026 | Same as RM35TF30 ¦ ,Input 3,
84873026 | Same as RM35TF30 ¦ ,Output 1,
84873026 | Same as RM35TF30 ¦ ,Output 2,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Output 1,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Output 2,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 2,Isolated
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 3,Circuit
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Output 1,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Output 2,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Output 1 / Output 2,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 1,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 2,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 1,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 2,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 1,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 2,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 2,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Input 3,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 3,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Output 1,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Output 2,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 2,Isolated
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 3,Circuit
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Output 1,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Output 2,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Output 1 / Output 2,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 1,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 2,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 1,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 2,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 1,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 2,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 2,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Input 3,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 3,
84873026dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 1,
84873026dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 2,
84873026dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 3,
84873026dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Output 1,
84873026dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Output 2,
84873026dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Output 1 / Output 2,
84873026dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 1,
84873026dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 2,
84873026dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 1,
84873026dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 2,
84873026dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 1,
84873026dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 2,
84873026dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 2,
84873026dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Input 3,
84873026dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 3,
84873026insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 1,
84873026insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 2,
84873026insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 3,
84873026insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Output 1,
84873026insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Output 2,
84873026insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Output 1 / Output 2,
84873026insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 1,
84873026insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 2,
84873026insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 1,
84873026insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 2,
84873026insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 1,
84873026insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 2,
84873026insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 2,
84873026insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Input 3,
84873026insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 3,
84873026
84873026[Us] rated supply voltage | Same as RM35TF30
84873026supply voltage limits | Same as RM35TF30
84873026polarity | Same as RM35TF30
84873026supply frequency | Same as RM35TF30
84873026supply frequency | Same as RM35TF30
84873026power consumption | Same as RM35TF30
84873026immunity to microbreaks | Same as RM35TF30
84873026supply terminal | Same as RM35TF30
84873026on-load factor | Same as RM35TF30
84873026release of input voltage | Same as RM35TF30
84873026
84873026monitoring functions | Same as RM35TF30 ¦ ,Phase lost ,
84873026monitoring functions | Same as RM35TF30 ¦ ,Phase sequence,
84873026monitoring functions | Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode),
84873026monitoring functions | Same as RM35TF30 ¦ ,Over voltage,
84873026monitoring functions | Same as RM35TF30 ¦ ,Undervoltage ,
84873026monitoring functions | Same as RM35TF30 ¦ ,Phase asymmetry,
84873026monitoring functions | Same as RM35TF30 ¦ ,Disconnection of neutral,
84873026monitoring functions | Same as RM35TF30 ¦ ,Voltage Regeneration,
84873026monitoring functions | Same as RM35TF30 ¦ ,Extreme undervoltage,
84873026monitoring functions | Same as RM35TF30 ¦ ,Extreme overvoltage,
84873026monitoring functions | Same as RM35TF30 ¦ ,Extreme asymmetry,
84873026 | Same as RM35TF30 ¦ ,Measurement mode,
84873026internal input resistance | Same as RM35TF30 ¦ ,Internal input resistance,
84873026input terminal | Same as RM35TF30 ¦ ,Input terminal,
84873026Input nominal voltage selection | Same as RM35TF30 ¦ ,Input nominal voltage selection,
84873026permissible input overload | Same as RM35TF30 ¦ ,permissible input overload,
84873026input frequency | Same as RM35TF30 ¦ ,Rated frequency,
84873026input frequency | Same as RM35TF30 ¦ ,Frequency operating range,
84873026setting accuracy of the switching threshold | Same as RM35TF30 ¦ ,Setting accuracy,
84873026repeat accuracy of the switching threshold | Same as RM35TF30 ¦ ,Repeat accuracy (constant parameters),
84873026measurement method | Same as RM35TF30 ¦ ,Measurement method,
84873026switching threshold drift | Same as RM35TF30 ¦ ,Measurement error with supply voltage variation,
84873026switching threshold drift | Same as RM35TF30 ¦ ,Measurement error with temperature variation,
84873026maximum measuring cycle | Same as RM35TF30 ¦ ,Maximum measuring cycles,
84873026measurement range | Same as RM35TF30 ¦ ,Phase lost ,
84873026measurement range | Same as RM35TF30 ¦ ,Phase sequence,
84873026measurement range | Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode),
84873026measurement range | Same as RM35TF30 ¦ ,Over voltage,
84873026measurement range | Same as RM35TF30 ¦ ,Undervoltage ,
84873026measurement range | Same as RM35TF30 ¦ ,Phase asymmetry,
84873026measurement range | Same as RM35TF30 ¦ ,Disconnection of neutral,
84873026measurement range | Same as RM35TF30 ¦ ,Voltage Regeneration,
84873026measurement range | Same as RM35TF30 ¦ ,Extreme undervoltage,
84873026measurement range | Same as RM35TF30 ¦ ,Extreme Overvoltage,
84873026measurement range | Same as RM35TF30 ¦ ,Extreme Asymmetry,
84873026tripping threshold | Same as RM35TF30 ¦ ,Phase cut,
84873026tripping threshold | Same as RM35TF30 ¦ ,Phase sequence,
84873026tripping threshold | Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode),
84873026tripping threshold | Same as RM35TF30 ¦ ,Over voltage,
84873026tripping threshold | Same as RM35TF30 ¦ ,Undervoltage ,
84873026tripping threshold | Same as RM35TF30 ¦ ,Phase asymmetry,
84873026tripping threshold | Same as RM35TF30 ¦ ,Disconnection of neutral,
84873026tripping threshold | Same as RM35TF30 ¦ ,Voltage Regeneration,
84873026tripping threshold | Same as RM35TF30 ¦ ,Extreme undervoltage (Phase loss),
84873026tripping threshold | Same as RM35TF30 ¦ ,Extreme Overvoltage,
84873026tripping threshold | Same as RM35TF30 ¦ ,Extreme Asymmetry,
84873026hysteresis | Same as RM35TF30 ¦ ,Phase cut,
84873026hysteresis | Same as RM35TF30 ¦ ,Phase sequence,
84873026hysteresis | Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode),
84873026hysteresis | Same as RM35TF30 ¦ ,Over voltage,
84873026hysteresis | Same as RM35TF30 ¦ ,Undervoltage ,
84873026hysteresis | Same as RM35TF30 ¦ ,Phase asymmetry,
84873026hysteresis | Same as RM35TF30 ¦ ,Disconnection of neutral,
84873026hysteresis | Same as RM35TF30 ¦ ,Voltage Regeneration,
84873026hysteresis | Same as RM35TF30 ¦ ,Extreme undervoltage (Phase loss),
84873026hysteresis | Same as RM35TF30 ¦ ,Extreme Overvoltage,
84873026hysteresis | Same as RM35TF30 ¦ ,Extreme Asymmetry,
84873026
84873026output type | Same as RM35TF30
84873026output terminal | Same as RM35TF30
84873026output logic | Same as RM35TF30 ¦ ,R1 (11-12-14),
84873026output logic | Same as RM35TF30 ¦ ,R2 (21-22-24),
84873026contacts material | Same as RM35TF30
84873026mechanical durability | Same as RM35TF30 ¦ IEC61810-1
84873026electrical durability | Same as RM35TF30 ¦ IEC60947-4-1,AC-1,
84873026electrical durability | Same as RM35TF30 ¦ IEC60947-4-1,DC-1,
84873026electrical durability | Same as RM35TF30 ¦ IEC60947-5-1,AC-15,
84873026electrical durability | Same as RM35TF30 ¦ IEC60947-5-1,DC-13,
84873026[Ue] rated operational voltage | Same as RM35TF30 ¦ IEC61810-1,Rated switching voltage,
84873026[Ie] rated operational current | Same as RM35TF30 ¦ IEC61810-1,Rated switching current,
84873026maximum switching capacity | Same as RM35TF30 ¦ ,Maximum switching voltage,
84873026maximum switching capacity | Same as RM35TF30 ¦ ,Maximum switching current,
84873026maximum switching capacity | Same as RM35TF30 ¦ ,Maximum switching capacity,
84873026minimum switching capacity | Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching voltage,
84873026minimum switching capacity | Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching current,
84873026minimum switching capacity | Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching capacity,
84873026maximum voltage drop | Same as RM35TF30 ¦ IEC62314,Only for solid state output,
84873026maximum leakage current | Same as RM35TF30 ¦ IEC62314,Only for solid state output,
84873026thermal current | Same as RM35TF30 ¦ IEC60947-5-1
84873026short circuit protection | Same as RM35TF30 ¦ IEC60947-5-1,Relay Output by external fuse,
84873026short circuit protection | Same as RM35TF30 ¦ IEC62314,Solid State Output by external fuse,
84873026
84873026time delay type | Same as RM35TF30 ¦ ,"OFF" delay,
84873026time delay type | Same as RM35TF30 ¦ ,"ON" delay,
84873026time delay type | Same as RM35TF30 ¦ ,Inhibition,
84873026time delay range | Same as RM35TF30 ¦ ,"OFF" delay,
84873026time delay range | Same as RM35TF30 ¦ ,"ON" delay,
84873026time delay range | Same as RM35TF30 ¦ ,Inhibition,
84873026response time | Same as RM35TF30 ¦ ,on crossing the threshold,
84873026response time | Same as RM35TF30
84873026response time | Same as RM35TF30
84873026response time | Same as RM35TF30
84873026response time | Same as RM35TF30
84873026power on delay | Same as RM35TF30
84873026reset time | Same as RM35TF30 ¦ ,through Un power reset,
84873026reset time | Same as RM35TF30 ¦ ,through front panel reset,
84873026reset time | Same as RM35TF30 ¦ ,through input control reset,
84873026setting accuracy of time delay | Same as RM35TF30
84873026repeat accuracy of time delay | Same as RM35TF30
84873026time delay drift | Same as RM35TF30
84873026time delay drift | Same as RM35TF30
84873026
84873026status LED | Same as RM35TF30
84873026local signalling | Same as RM35TF30 ¦ ,Power supply availability,
84873026local signalling | Same as RM35TF30 ¦ ,Power supply not availability,
84873026local signalling | Same as RM35TF30 ¦ ,Timing in-progress,
84873026local signalling | Same as RM35TF30 ¦ ,Output is energized,
84873026local signalling | Same as RM35TF30 ¦ ,Output is de-energized,
84873026local signalling | Same as RM35TF30 ¦ ,Range Setting Changes,
84873026local signalling | Same as RM35TF30 ¦ ,Phase Cut,
84873026local signalling | Same as RM35TF30 ¦ ,Phase Sequence Swap,
84873026local signalling | Same as RM35TF30 ¦ ,Undervoltage <U,
84873026local signalling | Same as RM35TF30 ¦ ,Overvoltage >U,
84873026local signalling | Same as RM35TF30 ¦ ,Phase Asymmetry,
84873026local signalling | Same as RM35TF30 ¦ ,Voltage Regeneration,
84873026local signalling | Same as RM35TF30 ¦ ,Extreme Undervoltage <U (Phase loss),
84873026local signalling | Same as RM35TF30 ¦ ,Extreme Overvoltage >U,
84873026local signalling | Same as RM35TF30 ¦ ,Extreme Phase Asymmetry,
84873026
84873026 | Same as RM35TF30
84873026 | Same as RM35TF30
84873026diagnostic button | Same as RM35TF30
84873026 | Same as RM35TF30
84873026 | Same as RM35TF30
84873026
84873026safety reliability data | Same as RM35TF30 ¦ ,MTTF,
84873026safety reliability data | Same as RM35TF30 ¦ ,B10,
84873026 | Same as RM35TF30 ¦ ,MTTFd,
84873026 | Same as RM35TF30 ¦ ,B10d,
84873026
84873026 | Drawing / Diagram
84873893
84873893standards | Same as RM35TF30
84873893product certifications | UL, CSA, CE, China ROHS
84873893marking | UL, CSA, CE, China ROHS
84873893directives | Same as RM35TF30
84873893directives | Same as RM35TF30
84873893directives | Same as RM35TF30
84873893
84873893 | Same as RM35TF30 ¦ IEC60721-3-3,Climatic category,
84873893 | Same as RM35TF30 ¦ Germanisher Lloyd,Environmental category,
84873893ambient air temperature for storage | Same as RM35TF30 ¦ ,Storage,
84873893ambient air temperature for operation | Same as RM35TF30 ¦ ,Operation,
84873893relative humidity | Same as RM35TF30 ¦ IEC60068-2-30,Damp heat,XX
84873893 | Same as RM35TF30 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873893vibration resistance | Same as RM35TF30 ¦ IEC60068-2-6
84873893shock resistance | Same as RM35TF30 ¦ IEC60068-2-27
84873893bump resistance | Same as RM35TF30 ¦ IEC60068-2-29
84873893seismic resistance | Same as RM35TF30 ¦ IEC60068-3-3
84873893IP degree of protection | Same as RM35TF30 ¦ IEC60529,Terminal Block,
84873893IP degree of protection | Same as RM35TF30 ¦ IEC60529,Housing,
84873893IP degree of protection | Same as RM35TF30 ¦ IEC60529,Front Panel,
84873893
84873893width | Same as RM35TF30 ¦ ,Width,
84873893height | Same as RM35TF30 ¦ ,Height,
84873893depth | Same as RM35TF30 ¦ ,Depth,
84873893net weight | Same as RM35TF30
84873893mounting support | Same as RM35TF30 ¦ IEC/EN 60715,Without socket,
84873893mounting support | Same as RM35TF30 ¦ IEC/EN 60715,With socket,
84873893mounting position | Same as RM35TF30 ¦ ,In relation to normal vertical mounting plane,
84873893Minimum distance to adjacent devices | Same as RM35TF30 ¦ ,Horizontal,
84873893Minimum distance to adjacent devices | Same as RM35TF30 ¦ ,Vertical,
84873893connections - terminals | Same as RM35TF30 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873893connections - terminals | Same as RM35TF30 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873893connections - terminals | Same as RM35TF30 ¦ IEC60947-1,Solid cable (spring terminal),
84873893connections - terminals | Same as RM35TF30 ¦ IEC60947-1,Flexible cable (spring terminal),
84873893tightening torque | Same as RM35TF30 ¦ IEC60947-1,Tightening torque,
84873893cable stripping length | Same as RM35TF30 ¦ ,Cable stripping length,
84873893duty time | Same as RM35TF30
84873893
84873893electromagnetic compatibility | Same as RM35TF30 ¦ ,Generic immunity standard,
84873893electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-2,Electrostatic discharge,
84873893electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873893electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-4,Fast transient / burst,
84873893electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-5,Surge,
84873893electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-6,Conducted RF disturbance,
84873893electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-8,Power frequency magnetic field,
84873893electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873893electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873893electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-29,DC voltage interruption,
84873893electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-13,Low frequency harmonics,
84873893electromagnetic compatibility | Same as RM35TF30 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873893electromagnetic compatibility | Same as RM35TF30 ¦ ,Generic emission standard,
84873893electromagnetic compatibility | Same as RM35TF30 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873893electromagnetic compatibility | Same as RM35TF30 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873893electromagnetic compatibility | Same as RM35TF30 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873893electromagnetic compatibility | Same as RM35TF30 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873893electromagnetic compatibility | Same as RM35TF30 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873893electromagnetic compatibility | Same as RM35TF30 ¦ Germanisher Lloyd,Conducted emission,
84873893
84873893pollution degree | Same as RM35TF30 ¦ IEC60664-1
84873893overvoltage category | Same as RM35TF30 ¦ IEC60664-1
84873893circuit group | Same as RM35TF30 ¦ ,Supply,Terminal
84873893circuit group | Same as RM35TF30 ¦ ,Input 1,
84873893circuit group | Same as RM35TF30 ¦ ,Input 2,
84873893circuit group | Same as RM35TF30 ¦ ,Input 3,
84873893circuit group | Same as RM35TF30 ¦ ,Output 1,
84873893circuit group | Same as RM35TF30 ¦ ,Output 2,
84873893 | Same as RM35TF30 ¦ ,Supply,Rated
84873893 | Same as RM35TF30 ¦ ,Input 1,Voltage
84873893 | Same as RM35TF30 ¦ ,Input 2,Spec
84873893 | Same as RM35TF30 ¦ ,Input 3,
84873893 | Same as RM35TF30 ¦ ,Output 1,
84873893 | Same as RM35TF30 ¦ ,Output 2,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Output 1,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Output 2,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 2,Isolated
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 3,Circuit
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Output 1,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Output 2,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Output 1 / Output 2,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 1,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 2,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 1,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 2,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 1,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 2,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 2,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Input 3,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 3,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Output 1,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Output 2,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 2,Isolated
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 3,Circuit
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Output 1,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Output 2,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Output 1 / Output 2,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 1,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 2,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 1,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 2,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 1,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 2,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 2,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Input 3,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 3,
84873893dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 1,
84873893dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 2,
84873893dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 3,
84873893dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Output 1,
84873893dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Output 2,
84873893dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Output 1 / Output 2,
84873893dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 1,
84873893dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 2,
84873893dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 1,
84873893dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 2,
84873893dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 1,
84873893dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 2,
84873893dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 2,
84873893dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Input 3,
84873893dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 3,
84873893insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 1,
84873893insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 2,
84873893insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 3,
84873893insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Output 1,
84873893insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Output 2,
84873893insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Output 1 / Output 2,
84873893insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 1,
84873893insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 2,
84873893insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 1,
84873893insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 2,
84873893insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 1,
84873893insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 2,
84873893insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 2,
84873893insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Input 3,
84873893insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 3,
84873893
84873893[Us] rated supply voltage | Same as RM35TF30
84873893supply voltage limits | Same as RM35TF30
84873893polarity | Same as RM35TF30
84873893supply frequency | Same as RM35TF30
84873893supply frequency | Same as RM35TF30
84873893power consumption | Same as RM35TF30
84873893immunity to microbreaks | Same as RM35TF30
84873893supply terminal | Same as RM35TF30
84873893on-load factor | Same as RM35TF30
84873893release of input voltage | Same as RM35TF30
84873893
84873893monitoring functions | Same as RM35TF30 ¦ ,Phase lost ,
84873893monitoring functions | Same as RM35TF30 ¦ ,Phase sequence,
84873893monitoring functions | Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode),
84873893monitoring functions | Same as RM35TF30 ¦ ,Over voltage,
84873893monitoring functions | Same as RM35TF30 ¦ ,Undervoltage ,
84873893monitoring functions | Same as RM35TF30 ¦ ,Phase asymmetry,
84873893monitoring functions | Same as RM35TF30 ¦ ,Disconnection of neutral,
84873893monitoring functions | Same as RM35TF30 ¦ ,Voltage Regeneration,
84873893monitoring functions | Same as RM35TF30 ¦ ,Extreme undervoltage,
84873893monitoring functions | Same as RM35TF30 ¦ ,Extreme overvoltage,
84873893monitoring functions | Same as RM35TF30 ¦ ,Extreme asymmetry,
84873893 | Same as RM35TF30 ¦ ,Measurement mode,
84873893internal input resistance | Same as RM35TF30 ¦ ,Internal input resistance,
84873893input terminal | Same as RM35TF30 ¦ ,Input terminal,
84873893Input nominal voltage selection | Same as RM35TF30 ¦ ,Input nominal voltage selection,
84873893permissible input overload | Same as RM35TF30 ¦ ,permissible input overload,
84873893input frequency | Same as RM35TF30 ¦ ,Rated frequency,
84873893input frequency | Same as RM35TF30 ¦ ,Frequency operating range,
84873893setting accuracy of the switching threshold | Same as RM35TF30 ¦ ,Setting accuracy,
84873893repeat accuracy of the switching threshold | Same as RM35TF30 ¦ ,Repeat accuracy (constant parameters),
84873893measurement method | Same as RM35TF30 ¦ ,Measurement method,
84873893switching threshold drift | Same as RM35TF30 ¦ ,Measurement error with supply voltage variation,
84873893switching threshold drift | Same as RM35TF30 ¦ ,Measurement error with temperature variation,
84873893maximum measuring cycle | Same as RM35TF30 ¦ ,Maximum measuring cycles,
84873893measurement range | Same as RM35TF30 ¦ ,Phase lost ,
84873893measurement range | Same as RM35TF30 ¦ ,Phase sequence,
84873893measurement range | Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode),
84873893measurement range | Same as RM35TF30 ¦ ,Over voltage,
84873893measurement range | Same as RM35TF30 ¦ ,Undervoltage ,
84873893measurement range | Same as RM35TF30 ¦ ,Phase asymmetry,
84873893measurement range | Same as RM35TF30 ¦ ,Disconnection of neutral,
84873893measurement range | Same as RM35TF30 ¦ ,Voltage Regeneration,
84873893measurement range | Same as RM35TF30 ¦ ,Extreme undervoltage,
84873893measurement range | Same as RM35TF30 ¦ ,Extreme Overvoltage,
84873893measurement range | Same as RM35TF30 ¦ ,Extreme Asymmetry,
84873893tripping threshold | Same as RM35TF30 ¦ ,Phase cut,
84873893tripping threshold | Same as RM35TF30 ¦ ,Phase sequence,
84873893tripping threshold | Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode),
84873893tripping threshold | Same as RM35TF30 ¦ ,Over voltage,
84873893tripping threshold | Same as RM35TF30 ¦ ,Undervoltage ,
84873893tripping threshold | Same as RM35TF30 ¦ ,Phase asymmetry,
84873893tripping threshold | Same as RM35TF30 ¦ ,Disconnection of neutral,
84873893tripping threshold | Same as RM35TF30 ¦ ,Voltage Regeneration,
84873893tripping threshold | Same as RM35TF30 ¦ ,Extreme undervoltage (Phase loss),
84873893tripping threshold | Same as RM35TF30 ¦ ,Extreme Overvoltage,
84873893tripping threshold | Same as RM35TF30 ¦ ,Extreme Asymmetry,
84873893hysteresis | Same as RM35TF30 ¦ ,Phase cut,
84873893hysteresis | Same as RM35TF30 ¦ ,Phase sequence,
84873893hysteresis | Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode),
84873893hysteresis | Same as RM35TF30 ¦ ,Over voltage,
84873893hysteresis | Same as RM35TF30 ¦ ,Undervoltage ,
84873893hysteresis | Same as RM35TF30 ¦ ,Phase asymmetry,
84873893hysteresis | Same as RM35TF30 ¦ ,Disconnection of neutral,
84873893hysteresis | Same as RM35TF30 ¦ ,Voltage Regeneration,
84873893hysteresis | Same as RM35TF30 ¦ ,Extreme undervoltage (Phase loss),
84873893hysteresis | Same as RM35TF30 ¦ ,Extreme Overvoltage,
84873893hysteresis | Same as RM35TF30 ¦ ,Extreme Asymmetry,
84873893
84873893output type | Same as RM35TF30
84873893output terminal | Same as RM35TF30
84873893output logic | Same as RM35TF30 ¦ ,R1 (11-12-14),
84873893output logic | Same as RM35TF30 ¦ ,R2 (21-22-24),
84873893contacts material | Same as RM35TF30
84873893mechanical durability | Same as RM35TF30 ¦ IEC61810-1
84873893electrical durability | Same as RM35TF30 ¦ IEC60947-4-1,AC-1,
84873893electrical durability | Same as RM35TF30 ¦ IEC60947-4-1,DC-1,
84873893electrical durability | Same as RM35TF30 ¦ IEC60947-5-1,AC-15,
84873893electrical durability | Same as RM35TF30 ¦ IEC60947-5-1,DC-13,
84873893[Ue] rated operational voltage | Same as RM35TF30 ¦ IEC61810-1,Rated switching voltage,
84873893[Ie] rated operational current | Same as RM35TF30 ¦ IEC61810-1,Rated switching current,
84873893maximum switching capacity | Same as RM35TF30 ¦ ,Maximum switching voltage,
84873893maximum switching capacity | Same as RM35TF30 ¦ ,Maximum switching current,
84873893maximum switching capacity | Same as RM35TF30 ¦ ,Maximum switching capacity,
84873893minimum switching capacity | Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching voltage,
84873893minimum switching capacity | Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching current,
84873893minimum switching capacity | Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching capacity,
84873893maximum voltage drop | Same as RM35TF30 ¦ IEC62314,Only for solid state output,
84873893maximum leakage current | Same as RM35TF30 ¦ IEC62314,Only for solid state output,
84873893thermal current | Same as RM35TF30 ¦ IEC60947-5-1
84873893short circuit protection | Same as RM35TF30 ¦ IEC60947-5-1,Relay Output by external fuse,
84873893short circuit protection | Same as RM35TF30 ¦ IEC62314,Solid State Output by external fuse,
84873893
84873893time delay type | Same as RM35TF30 ¦ ,"OFF" delay,
84873893time delay type | Same as RM35TF30 ¦ ,"ON" delay,
84873893time delay type | Same as RM35TF30 ¦ ,Inhibition,
84873893time delay range | Same as RM35TF30 ¦ ,"OFF" delay,
84873893time delay range | Same as RM35TF30 ¦ ,"ON" delay,
84873893time delay range | Same as RM35TF30 ¦ ,Inhibition,
84873893response time | Same as RM35TF30 ¦ ,on crossing the threshold,
84873893response time | Same as RM35TF30
84873893response time | Same as RM35TF30
84873893response time | Same as RM35TF30
84873893response time | Same as RM35TF30
84873893power on delay | Same as RM35TF30
84873893reset time | Same as RM35TF30 ¦ ,through Un power reset,
84873893reset time | Same as RM35TF30 ¦ ,through front panel reset,
84873893reset time | Same as RM35TF30 ¦ ,through input control reset,
84873893setting accuracy of time delay | Same as RM35TF30
84873893repeat accuracy of time delay | Same as RM35TF30
84873893time delay drift | Same as RM35TF30
84873893time delay drift | Same as RM35TF30
84873893
84873893status LED | Same as RM35TF30
84873893local signalling | Same as RM35TF30 ¦ ,Power supply availability,
84873893local signalling | Same as RM35TF30 ¦ ,Power supply not availability,
84873893local signalling | Same as RM35TF30 ¦ ,Timing in-progress,
84873893local signalling | Same as RM35TF30 ¦ ,Output is energized,
84873893local signalling | Same as RM35TF30 ¦ ,Output is de-energized,
84873893local signalling | Same as RM35TF30 ¦ ,Range Setting Changes,
84873893local signalling | Same as RM35TF30 ¦ ,Phase Cut,
84873893local signalling | Same as RM35TF30 ¦ ,Phase Sequence Swap,
84873893local signalling | Same as RM35TF30 ¦ ,Undervoltage <U,
84873893local signalling | Same as RM35TF30 ¦ ,Overvoltage >U,
84873893local signalling | Same as RM35TF30 ¦ ,Phase Asymmetry,
84873893local signalling | Same as RM35TF30 ¦ ,Voltage Regeneration,
84873893local signalling | Same as RM35TF30 ¦ ,Extreme Undervoltage <U (Phase loss),
84873893local signalling | Same as RM35TF30 ¦ ,Extreme Overvoltage >U,
84873893local signalling | Same as RM35TF30 ¦ ,Extreme Phase Asymmetry,
84873893
84873893 | Same as RM35TF30
84873893 | Same as RM35TF30
84873893diagnostic button | Same as RM35TF30
84873893 | Same as RM35TF30
84873893 | Same as RM35TF30
84873893
84873893safety reliability data | Same as RM35TF30 ¦ ,MTTF,
84873893safety reliability data | Same as RM35TF30 ¦ ,B10,
84873893 | Same as RM35TF30 ¦ ,MTTFd,
84873893 | Same as RM35TF30 ¦ ,B10d,
84873893
84873893 | Drawing / Diagram
RM35TF30SP01
RM35TF30SP01standards | Same as RM35TF30
RM35TF30SP01product certifications | Same as RM35TF30
RM35TF30SP01marking | Same as RM35TF30
RM35TF30SP01directives | Same as RM35TF30
RM35TF30SP01directives | Same as RM35TF30
RM35TF30SP01directives | Same as RM35TF30
RM35TF30SP01
RM35TF30SP01 | Same as RM35TF30 ¦ IEC60721-3-3,Climatic category,
RM35TF30SP01 | Same as RM35TF30 ¦ Germanisher Lloyd,Environmental category,
RM35TF30SP01ambient air temperature for storage | Same as RM35TF30 ¦ ,Storage,
RM35TF30SP01ambient air temperature for operation | Same as RM35TF30 ¦ ,Operation,
RM35TF30SP01relative humidity | Same as RM35TF30 ¦ IEC60068-2-30,Damp heat,XX
RM35TF30SP01 | Same as RM35TF30 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM35TF30SP01vibration resistance | Same as RM35TF30 ¦ IEC60068-2-6
RM35TF30SP01shock resistance | Same as RM35TF30 ¦ IEC60068-2-27
RM35TF30SP01bump resistance | Same as RM35TF30 ¦ IEC60068-2-29
RM35TF30SP01seismic resistance | Same as RM35TF30 ¦ IEC60068-3-3
RM35TF30SP01IP degree of protection | Same as RM35TF30 ¦ IEC60529,Terminal Block,
RM35TF30SP01IP degree of protection | Same as RM35TF30 ¦ IEC60529,Housing,
RM35TF30SP01IP degree of protection | Same as RM35TF30 ¦ IEC60529,Front Panel,
RM35TF30SP01
RM35TF30SP01width | Same as RM35TF30 ¦ ,Width,
RM35TF30SP01height | Same as RM35TF30 ¦ ,Height,
RM35TF30SP01depth | Same as RM35TF30 ¦ ,Depth,
RM35TF30SP01net weight | Same as RM35TF30
RM35TF30SP01mounting support | Same as RM35TF30 ¦ IEC/EN 60715,Without socket,
RM35TF30SP01mounting support | Same as RM35TF30 ¦ IEC/EN 60715,With socket,
RM35TF30SP01mounting position | Same as RM35TF30 ¦ ,In relation to normal vertical mounting plane,
RM35TF30SP01Minimum distance to adjacent devices | Same as RM35TF30 ¦ ,Horizontal,
RM35TF30SP01Minimum distance to adjacent devices | Same as RM35TF30 ¦ ,Vertical,
RM35TF30SP01connections - terminals | Same as RM35TF30 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35TF30SP01connections - terminals | Same as RM35TF30 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35TF30SP01connections - terminals | Same as RM35TF30 ¦ IEC60947-1,Solid cable (spring terminal),
RM35TF30SP01connections - terminals | Same as RM35TF30 ¦ IEC60947-1,Flexible cable (spring terminal),
RM35TF30SP01tightening torque | Same as RM35TF30 ¦ IEC60947-1,Tightening torque,
RM35TF30SP01cable stripping length | Same as RM35TF30 ¦ ,Cable stripping length,
RM35TF30SP01duty time | Same as RM35TF30
RM35TF30SP01
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ ,Generic immunity standard,
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-2,Electrostatic discharge,
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-4,Fast transient / burst,
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-5,Surge,
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-6,Conducted RF disturbance,
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-8,Power frequency magnetic field,
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-18,1 MHz oscillation wave,
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-29,DC voltage interruption,
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ IEC61000-4-13,Low frequency harmonics,
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ ,Generic emission standard,
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ Germanisher Lloyd,Conducted emission,
RM35TF30SP01
RM35TF30SP01pollution degree | Same as RM35TF30 ¦ IEC60664-1
RM35TF30SP01overvoltage category | Same as RM35TF30 ¦ IEC60664-1
RM35TF30SP01circuit group | Same as RM35TF30 ¦ ,Supply,Terminal
RM35TF30SP01circuit group | Same as RM35TF30 ¦ ,Input 1,
RM35TF30SP01circuit group | Same as RM35TF30 ¦ ,Input 2,
RM35TF30SP01circuit group | Same as RM35TF30 ¦ ,Input 3,
RM35TF30SP01circuit group | Same as RM35TF30 ¦ ,Output 1,
RM35TF30SP01circuit group | Same as RM35TF30 ¦ ,Output 2,
RM35TF30SP01 | Same as RM35TF30 ¦ ,Supply,Rated
RM35TF30SP01 | Same as RM35TF30 ¦ ,Input 1,Voltage
RM35TF30SP01 | Same as RM35TF30 ¦ ,Input 2,Spec
RM35TF30SP01 | Same as RM35TF30 ¦ ,Input 3,
RM35TF30SP01 | Same as RM35TF30 ¦ ,Output 1,
RM35TF30SP01 | Same as RM35TF30 ¦ ,Output 2,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Output 1,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Output 2,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 2,Isolated
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 3,Circuit
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Output 1,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Output 2,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Output 1 / Output 2,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 1,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 2,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 1,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 2,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 1,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 2,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 2,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Input 3,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 3,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Output 1,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Output 2,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 2,Isolated
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Input 3,Circuit
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Output 1,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply / Output 2,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Output 1 / Output 2,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 1,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 2,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 1,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 2,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 1,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 2,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 2,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 2 / Input 3,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 3,
RM35TF30SP01dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 1,
RM35TF30SP01dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 2,
RM35TF30SP01dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 3,
RM35TF30SP01dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Output 1,
RM35TF30SP01dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Output 2,
RM35TF30SP01dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Output 1 / Output 2,
RM35TF30SP01dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 1,
RM35TF30SP01dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 2,
RM35TF30SP01dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 1,
RM35TF30SP01dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 2,
RM35TF30SP01dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 1,
RM35TF30SP01dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 2,
RM35TF30SP01dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 2,
RM35TF30SP01dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Input 3,
RM35TF30SP01dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 3,
RM35TF30SP01insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 1,
RM35TF30SP01insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 2,
RM35TF30SP01insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 3,
RM35TF30SP01insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Output 1,
RM35TF30SP01insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Output 2,
RM35TF30SP01insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Output 1 / Output 2,
RM35TF30SP01insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 1,
RM35TF30SP01insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 2,
RM35TF30SP01insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 1,
RM35TF30SP01insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 2,
RM35TF30SP01insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 1,
RM35TF30SP01insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 2,
RM35TF30SP01insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 2,
RM35TF30SP01insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 2 / Input 3,
RM35TF30SP01insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 3,
RM35TF30SP01
RM35TF30SP01[Us] rated supply voltage | Same as RM35TF30
RM35TF30SP01supply voltage limits | Same as RM35TF30
RM35TF30SP01polarity | Same as RM35TF30
RM35TF30SP01supply frequency | Same as RM35TF30
RM35TF30SP01supply frequency | Same as RM35TF30
RM35TF30SP01power consumption | Same as RM35TF30
RM35TF30SP01immunity to microbreaks | Same as RM35TF30
RM35TF30SP01supply terminal | Same as RM35TF30
RM35TF30SP01on-load factor | Same as RM35TF30
RM35TF30SP01release of input voltage | Same as RM35TF30
RM35TF30SP01
RM35TF30SP01monitoring functions | Same as RM35TF30 ¦ ,Phase lost ,
RM35TF30SP01monitoring functions | Same as RM35TF30 ¦ ,Phase sequence,
RM35TF30SP01monitoring functions | Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode),
RM35TF30SP01monitoring functions | Same as RM35TF30 ¦ ,Over voltage,
RM35TF30SP01monitoring functions | Same as RM35TF30 ¦ ,Undervoltage ,
RM35TF30SP01monitoring functions | Same as RM35TF30 ¦ ,Phase asymmetry,
RM35TF30SP01monitoring functions | Same as RM35TF30 ¦ ,Disconnection of neutral,
RM35TF30SP01monitoring functions | Same as RM35TF30 ¦ ,Voltage Regeneration,
RM35TF30SP01monitoring functions | Same as RM35TF30 ¦ ,Extreme undervoltage,
RM35TF30SP01monitoring functions | Same as RM35TF30 ¦ ,Extreme overvoltage,
RM35TF30SP01monitoring functions | Same as RM35TF30 ¦ ,Extreme asymmetry,
RM35TF30SP01 | Same as RM35TF30 ¦ ,Measurement mode,
RM35TF30SP01internal input resistance | Same as RM35TF30 ¦ ,Internal input resistance,
RM35TF30SP01input terminal | Same as RM35TF30 ¦ ,Input terminal,
RM35TF30SP01Input nominal voltage selection | Same as RM35TF30 ¦ ,Input nominal voltage selection,
RM35TF30SP01permissible input overload | Same as RM35TF30 ¦ ,permissible input overload,
RM35TF30SP01input frequency | Same as RM35TF30 ¦ ,Rated frequency,
RM35TF30SP01input frequency | Same as RM35TF30 ¦ ,Frequency operating range,
RM35TF30SP01setting accuracy of the switching threshold | Same as RM35TF30 ¦ ,Setting accuracy,
RM35TF30SP01repeat accuracy of the switching threshold | Same as RM35TF30 ¦ ,Repeat accuracy (constant parameters),
RM35TF30SP01measurement method | Same as RM35TF30 ¦ ,Measurement method,
RM35TF30SP01switching threshold drift | Same as RM35TF30 ¦ ,Measurement error with supply voltage variation,
RM35TF30SP01switching threshold drift | Same as RM35TF30 ¦ ,Measurement error with temperature variation,
RM35TF30SP01maximum measuring cycle | Same as RM35TF30 ¦ ,Maximum measuring cycles,
RM35TF30SP01measurement range | Same as RM35TF30 ¦ ,Phase lost ,
RM35TF30SP01measurement range | Same as RM35TF30 ¦ ,Phase sequence,
RM35TF30SP01measurement range | Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode),
RM35TF30SP01measurement range | Same as RM35TF30 ¦ ,Over voltage,
RM35TF30SP01measurement range | Same as RM35TF30 ¦ ,Undervoltage ,
RM35TF30SP01measurement range | Same as RM35TF30 ¦ ,Phase asymmetry,
RM35TF30SP01measurement range | Same as RM35TF30 ¦ ,Disconnection of neutral,
RM35TF30SP01measurement range | Same as RM35TF30 ¦ ,Voltage Regeneration,
RM35TF30SP01measurement range | Same as RM35TF30 ¦ ,Extreme undervoltage,
RM35TF30SP01measurement range | Same as RM35TF30 ¦ ,Extreme Overvoltage,
RM35TF30SP01measurement range | Same as RM35TF30 ¦ ,Extreme Asymmetry,
RM35TF30SP01tripping threshold | Same as RM35TF30 ¦ ,Phase cut,
RM35TF30SP01tripping threshold | Same as RM35TF30 ¦ ,Phase sequence,
RM35TF30SP01tripping threshold | Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode),
RM35TF30SP01tripping threshold | Same as RM35TF30 ¦ ,Over voltage,
RM35TF30SP01tripping threshold | Same as RM35TF30 ¦ ,Undervoltage ,
RM35TF30SP01tripping threshold | Same as RM35TF30 ¦ ,Phase asymmetry,
RM35TF30SP01tripping threshold | Same as RM35TF30 ¦ ,Disconnection of neutral,
RM35TF30SP01tripping threshold | Same as RM35TF30 ¦ ,Voltage Regeneration,
RM35TF30SP01tripping threshold | Same as RM35TF30 ¦ ,Extreme undervoltage (Phase loss),
RM35TF30SP01tripping threshold | Same as RM35TF30 ¦ ,Extreme Overvoltage,
RM35TF30SP01tripping threshold | Same as RM35TF30 ¦ ,Extreme Asymmetry,
RM35TF30SP01hysteresis | Same as RM35TF30 ¦ ,Phase cut,
RM35TF30SP01hysteresis | Same as RM35TF30 ¦ ,Phase sequence,
RM35TF30SP01hysteresis | Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode),
RM35TF30SP01hysteresis | Fixed 5.35% of selected Un Internal design spec: 5.35% +/- 1.5% ¦ ,Over voltage,
RM35TF30SP01hysteresis | Fixed 5.35% of selected Un Internal design spec: 5.35% +/- 1.5% ¦ ,Undervoltage ,
RM35TF30SP01hysteresis | Same as RM35TF30 ¦ ,Phase asymmetry,
RM35TF30SP01hysteresis | Same as RM35TF30 ¦ ,Disconnection of neutral,
RM35TF30SP01hysteresis | Same as RM35TF30 ¦ ,Voltage Regeneration,
RM35TF30SP01hysteresis | Same as RM35TF30 ¦ ,Extreme undervoltage (Phase loss),
RM35TF30SP01hysteresis | Same as RM35TF30 ¦ ,Extreme Overvoltage,
RM35TF30SP01hysteresis | Same as RM35TF30 ¦ ,Extreme Asymmetry,
RM35TF30SP01
RM35TF30SP01output type | Same as RM35TF30
RM35TF30SP01output terminal | Same as RM35TF30
RM35TF30SP01output logic | Same as RM35TF30 ¦ ,R1 (11-12-14),
RM35TF30SP01output logic | Same as RM35TF30 ¦ ,R2 (21-22-24),
RM35TF30SP01contacts material | Same as RM35TF30
RM35TF30SP01mechanical durability | Same as RM35TF30 ¦ IEC61810-1
RM35TF30SP01electrical durability | Same as RM35TF30 ¦ IEC60947-4-1,AC-1,
RM35TF30SP01electrical durability | Same as RM35TF30 ¦ IEC60947-4-1,DC-1,
RM35TF30SP01electrical durability | Same as RM35TF30 ¦ IEC60947-5-1,AC-15,
RM35TF30SP01electrical durability | Same as RM35TF30 ¦ IEC60947-5-1,DC-13,
RM35TF30SP01[Ue] rated operational voltage | Same as RM35TF30 ¦ IEC61810-1,Rated switching voltage,
RM35TF30SP01[Ie] rated operational current | Same as RM35TF30 ¦ IEC61810-1,Rated switching current,
RM35TF30SP01maximum switching capacity | Same as RM35TF30 ¦ ,Maximum switching voltage,
RM35TF30SP01maximum switching capacity | Same as RM35TF30 ¦ ,Maximum switching current,
RM35TF30SP01maximum switching capacity | Same as RM35TF30 ¦ ,Maximum switching capacity,
RM35TF30SP01minimum switching capacity | Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching voltage,
RM35TF30SP01minimum switching capacity | Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching current,
RM35TF30SP01minimum switching capacity | Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching capacity,
RM35TF30SP01maximum voltage drop | Same as RM35TF30 ¦ IEC62314,Only for solid state output,
RM35TF30SP01maximum leakage current | Same as RM35TF30 ¦ IEC62314,Only for solid state output,
RM35TF30SP01thermal current | Same as RM35TF30 ¦ IEC60947-5-1
RM35TF30SP01short circuit protection | Same as RM35TF30 ¦ IEC60947-5-1,Relay Output by external fuse,
RM35TF30SP01short circuit protection | Same as RM35TF30 ¦ IEC62314,Solid State Output by external fuse,
RM35TF30SP01
RM35TF30SP01time delay type | Same as RM35TF30 ¦ ,"OFF" delay,
RM35TF30SP01time delay type | Same as RM35TF30 ¦ ,"ON" delay,
RM35TF30SP01time delay type | Same as RM35TF30 ¦ ,Inhibition,
RM35TF30SP01time delay range | Same as RM35TF30 ¦ ,"OFF" delay,
RM35TF30SP01time delay range | Same as RM35TF30 ¦ ,"ON" delay,
RM35TF30SP01time delay range | Same as RM35TF30 ¦ ,Inhibition,
RM35TF30SP01response time | Same as RM35TF30 ¦ ,on crossing the threshold,
RM35TF30SP01response time | Same as RM35TF30
RM35TF30SP01response time | Same as RM35TF30
RM35TF30SP01response time | Same as RM35TF30
RM35TF30SP01response time | Same as RM35TF30
RM35TF30SP01power on delay | Same as RM35TF30
RM35TF30SP01reset time | Same as RM35TF30 ¦ ,through Un power reset,
RM35TF30SP01reset time | Same as RM35TF30 ¦ ,through front panel reset,
RM35TF30SP01reset time | Same as RM35TF30 ¦ ,through input control reset,
RM35TF30SP01setting accuracy of time delay | Same as RM35TF30
RM35TF30SP01repeat accuracy of time delay | Same as RM35TF30
RM35TF30SP01time delay drift | Same as RM35TF30
RM35TF30SP01time delay drift | Same as RM35TF30
RM35TF30SP01
RM35TF30SP01status LED | Same as RM35TF30
RM35TF30SP01local signalling | Same as RM35TF30 ¦ ,Power supply availability,
RM35TF30SP01local signalling | Same as RM35TF30 ¦ ,Power supply not availability,
RM35TF30SP01local signalling | Same as RM35TF30 ¦ ,Timing in-progress,
RM35TF30SP01local signalling | Same as RM35TF30 ¦ ,Output is energized,
RM35TF30SP01local signalling | Same as RM35TF30 ¦ ,Output is de-energized,
RM35TF30SP01local signalling | Same as RM35TF30 ¦ ,Range Setting Changes,
RM35TF30SP01local signalling | Same as RM35TF30 ¦ ,Phase Cut,
RM35TF30SP01local signalling | Same as RM35TF30 ¦ ,Phase Sequence Swap,
RM35TF30SP01local signalling | Same as RM35TF30 ¦ ,Undervoltage <U,
RM35TF30SP01local signalling | Same as RM35TF30 ¦ ,Overvoltage >U,
RM35TF30SP01local signalling | Same as RM35TF30 ¦ ,Phase Asymmetry,
RM35TF30SP01local signalling | Same as RM35TF30 ¦ ,Voltage Regeneration,
RM35TF30SP01local signalling | Same as RM35TF30 ¦ ,Extreme Undervoltage <U (Phase loss),
RM35TF30SP01local signalling | Same as RM35TF30 ¦ ,Extreme Overvoltage >U,
RM35TF30SP01local signalling | Same as RM35TF30 ¦ ,Extreme Phase Asymmetry,
RM35TF30SP01
RM35TF30SP01 | Same as RM35TF30
RM35TF30SP01 | Same as RM35TF30
RM35TF30SP01diagnostic button | Same as RM35TF30
RM35TF30SP01 | Same as RM35TF30
RM35TF30SP01 | Same as RM35TF30
RM35TF30SP01
RM35TF30SP01safety reliability data | Same as RM35TF30 ¦ ,MTTF,
RM35TF30SP01safety reliability data | Same as RM35TF30 ¦ ,B10,
RM35TF30SP01 | Same as RM35TF30 ¦ ,MTTFd,
RM35TF30SP01 | Same as RM35TF30 ¦ ,B10d,
RM35TF30SP01
RM35TF30SP01 | Drawing / Diagram
RM35UB330
RM35UB330standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM35UB330product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35UB330marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35UB330directives | 2014/35/EU
RM35UB330directives | 2014/30/EU
RM35UB330directives | 2011/65/EU
RM35UB330
RM35UB330 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM35UB330 | Class C ¦ Germanisher Lloyd,Environmental category,
RM35UB330ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM35UB330ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM35UB330relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM35UB330 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM35UB330vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM35UB330shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM35UB330bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM35UB330seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM35UB330IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM35UB330IP degree of protection | IP30 ¦ IEC60529,Housing,
RM35UB330IP degree of protection | - ¦ IEC60529,Front Panel,
RM35UB330
RM35UB330width | 35 ¦ ,Width,
RM35UB330height | 90 ¦ ,Height,
RM35UB330depth | 72 ¦ ,Depth,
RM35UB330net weight | 130
RM35UB330mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM35UB330mounting support | - ¦ IEC/EN 60715,With socket,
RM35UB330mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35UB330Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM35UB330Minimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM35UB330connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35UB330connections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35UB330connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM35UB330connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35UB330tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM35UB330cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM35UB330duty time | 1
RM35UB330
RM35UB330electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM35UB330electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM35UB330electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM35UB330electromagnetic compatibility | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM35UB330electromagnetic compatibility | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge,
RM35UB330electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM35UB330electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM35UB330electromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35UB330electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM35UB330electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM35UB330electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM35UB330electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35UB330electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM35UB330electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35UB330electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35UB330electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM35UB330electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35UB330electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35UB330electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35UB330
RM35UB330pollution degree | 3 ¦ IEC60664-1
RM35UB330overvoltage category | 3 ¦ IEC60664-1
RM35UB330circuit group | L1, L2, L3 ¦ ,Supply,Terminal
RM35UB330circuit group | - ¦ ,Input 1,
RM35UB330circuit group | - ¦ ,Input 2,
RM35UB330circuit group | - ¦ ,Input 3,
RM35UB330circuit group | 11,12,14 ¦ ,Output 1,
RM35UB330circuit group | 21,22,24 ¦ ,Output 2,
RM35UB330 | 220..480 AC ¦ ,Supply,Rated
RM35UB330 | - ¦ ,Input 1,Voltage
RM35UB330 | - ¦ ,Input 2,Spec
RM35UB330 | - ¦ ,Input 3,
RM35UB330 | 250V ¦ ,Output 1,
RM35UB330 | 250V ¦ ,Output 2,
RM35UB330[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM35UB330[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM35UB330[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM35UB330[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM35UB330[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM35UB330[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM35UB330[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35UB330[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM35UB330[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM35UB330[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM35UB330[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 2,
RM35UB330[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM35UB330[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM35UB330[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM35UB330[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM35UB330[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM35UB330[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM35UB330[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM35UB330[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM35UB330[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM35UB330[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM35UB330[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM35UB330[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM35UB330[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM35UB330[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM35UB330[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM35UB330dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM35UB330dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM35UB330dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM35UB330dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM35UB330dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM35UB330dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM35UB330dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM35UB330dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM35UB330dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM35UB330dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM35UB330dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM35UB330dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM35UB330dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM35UB330dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM35UB330dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM35UB330insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM35UB330insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM35UB330insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM35UB330insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM35UB330insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM35UB330insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM35UB330insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM35UB330insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM35UB330insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM35UB330insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM35UB330insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM35UB330insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM35UB330insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM35UB330insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM35UB330insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM35UB330
RM35UB330[Us] rated supply voltage | ~ 3 x 220…3 x 480
RM35UB330supply voltage limits | ~ 3 x 194…3 x 528
RM35UB330polarity | -
RM35UB330supply frequency | 50 / 60
RM35UB330supply frequency | 45…66
RM35UB330power consumption | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz
RM35UB330immunity to microbreaks | 0
RM35UB330supply terminal | L1-N
RM35UB330on-load factor | 1
RM35UB330release of input voltage | -
RM35UB330
RM35UB330monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost ,
RM35UB330monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence,
RM35UB330monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM35UB330monitoring functions | governed by time delay Tt1, status reflects to R1 ¦ ,Over voltage,
RM35UB330monitoring functions | governed by time delay Tt2, status reflects to R2 ¦ ,Undervoltage ,
RM35UB330monitoring functions | - ¦ ,Phase asymmetry,
RM35UB330monitoring functions | - ¦ ,Disconnection of neutral,
RM35UB330monitoring functions | - ¦ ,Voltage Regeneration,
RM35UB330monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage,
RM35UB330monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage,
RM35UB330monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM35UB330 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM35UB330internal input resistance | - ¦ ,Internal input resistance,
RM35UB330input terminal | L1-L2-L3 ¦ ,Input terminal,
RM35UB330Input nominal voltage selection | 220, 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM35UB330permissible input overload | - ¦ ,permissible input overload,
RM35UB330input frequency | 50 / 60 ¦ ,Rated frequency,
RM35UB330input frequency | 45…66 ¦ ,Frequency operating range,
RM35UB330setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM35UB330repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM35UB330measurement method | True RMS ¦ ,Measurement method,
RM35UB330switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation,
RM35UB330switching threshold drift | < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM35UB330maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM35UB330measurement range | - ¦ ,Phase lost ,
RM35UB330measurement range | - ¦ ,Phase sequence,
RM35UB330measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM35UB330measurement range | +2…+20 % in the ranges 3 x ~ 220…440 +2…+10 % in the range 3 x ~ 480 ¦ ,Over voltage,
RM35UB330measurement range | -12…-2 % in the range 3 x ~ 220 -20…-2 % in the ranges 3 x ~ 380…480 ¦ ,Undervoltage ,
RM35UB330measurement range | - ¦ ,Phase asymmetry,
RM35UB330measurement range | - ¦ ,Disconnection of neutral,
RM35UB330measurement range | - ¦ ,Voltage Regeneration,
RM35UB330measurement range | - ¦ ,Extreme undervoltage,
RM35UB330measurement range | - ¦ ,Extreme Overvoltage,
RM35UB330measurement range | - ¦ ,Extreme Asymmetry,
RM35UB330tripping threshold | 1 or more phase cut ¦ ,Phase cut,
RM35UB330tripping threshold | Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence,
RM35UB330tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM35UB330tripping threshold | Adjustable 2%...20% of selected Un ¦ ,Over voltage,
RM35UB330tripping threshold | Adjustable 2%...20% of selected Un ¦ ,Undervoltage ,
RM35UB330tripping threshold | - ¦ ,Phase asymmetry,
RM35UB330tripping threshold | - ¦ ,Disconnection of neutral,
RM35UB330tripping threshold | - ¦ ,Voltage Regeneration,
RM35UB330tripping threshold | 1 or more phase < 150V Internal design spec: 1 or more phase <188V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM35UB330tripping threshold | Internal design spec: 543V +/- 5% ¦ ,Extreme Overvoltage,
RM35UB330tripping threshold | Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM35UB330hysteresis | All phase cut recover ¦ ,Phase cut,
RM35UB330hysteresis | Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence,
RM35UB330hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM35UB330hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Over voltage,
RM35UB330hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage ,
RM35UB330hysteresis | - ¦ ,Phase asymmetry,
RM35UB330hysteresis | - ¦ ,Disconnection of neutral,
RM35UB330hysteresis | - ¦ ,Voltage Regeneration,
RM35UB330hysteresis | All phases > 205V Internal design spec: All phases >190V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM35UB330hysteresis | Internal design spec: All phases > <533V +/- 5% ¦ ,Extreme Overvoltage,
RM35UB330hysteresis | - ¦ ,Extreme Asymmetry,
RM35UB330
RM35UB330output type | 1 x C/O + 1 x C/O relay contacts
RM35UB330output terminal | 11-12-14, 21-22-24
RM35UB330output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM35UB330output logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM35UB330contacts material | Cadmium free
RM35UB330mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM35UB330electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM35UB330electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM35UB330electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM35UB330electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM35UB330[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM35UB330[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM35UB330maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM35UB330maximum switching capacity | 5A ¦ ,Maximum switching current,
RM35UB330maximum switching capacity | - ¦ ,Maximum switching capacity,
RM35UB330minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM35UB330minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM35UB330minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM35UB330maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35UB330maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35UB330thermal current | 5A ¦ IEC60947-5-1
RM35UB330short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse,
RM35UB330short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM35UB330
RM35UB330time delay type | Yes ¦ ,"OFF" delay,
RM35UB330time delay type | - ¦ ,"ON" delay,
RM35UB330time delay type | - ¦ ,Inhibition,
RM35UB330time delay range | Adjustable Tt1 0.1…30 for overvoltage @ R1 (11-12-14) Adjustable Tt2 0.1…30 for undervoltage @ R2 (21-22-24) ¦ ,"OFF" delay,
RM35UB330time delay range | - ¦ ,"ON" delay,
RM35UB330time delay range | - ¦ ,Inhibition,
RM35UB330response time | 0
RM35UB330response time | -
RM35UB330response time | -
RM35UB330response time | -
RM35UB330response time | -
RM35UB330power on delay | 0
RM35UB330reset time | 0
RM35UB330reset time | - ¦ ,through front panel reset,
RM35UB330reset time | - ¦ ,through input control reset,
RM35UB330setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM35UB330repeat accuracy of time delay | +/- 3%
RM35UB330time delay drift | -
RM35UB330time delay drift | -
RM35UB330
RM35UB330status LED | Un (Green) R1 (Amber) R2 (Amber)
RM35UB330local signalling | Un - ON ¦ ,Power supply availability,
RM35UB330local signalling | Un - OFF ¦ ,Power supply not availability,
RM35UB330local signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM35UB330local signalling | R1 / R2 - ON ¦ ,Output is energized,
RM35UB330local signalling | R 1 / R2 - OFF ¦ ,Output is de-energized,
RM35UB330local signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM35UB330local signalling | R 1 / R2 - OFF ¦ ,Phase Cut,
RM35UB330local signalling | R 1 / R2 - OFF ¦ ,Phase Sequence Swap,
RM35UB330local signalling | R2 - OFF ¦ ,Undervoltage <U,
RM35UB330local signalling | R 1 - OFF ¦ ,Overvoltage >U,
RM35UB330local signalling | - ¦ ,Phase Asymmetry,
RM35UB330local signalling | - ¦ ,Voltage Regeneration,
RM35UB330local signalling | R 1 / R2 - OFF ¦ ,Extreme Undervoltage <U (Phase loss),
RM35UB330local signalling | R 1 / R2 - OFF ¦ ,Extreme Overvoltage >U,
RM35UB330local signalling | - ¦ ,Extreme Phase Asymmetry,
RM35UB330
RM35UB330 | Yes
RM35UB330 | -
RM35UB330diagnostic button | -
RM35UB330 | -
RM35UB330 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM35UB330
RM35UB330safety reliability data | 2,800,000 hours ¦ ,MTTF,
RM35UB330safety reliability data | 300,000 hours ¦ ,B10,
RM35UB330 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM35UB330 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM35UB330
RM35UB330 | Drawing / Diagram
84873220
84873220standards | Same as RM35UB330
84873220product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873220marking | UL, CSA, GL, CCC, CE, China ROHS
84873220directives | Same as RM35UB330
84873220directives | Same as RM35UB330
84873220directives | Same as RM35UB330
84873220
84873220 | Same as RM35UB330 ¦ IEC60721-3-3,Climatic category,
84873220 | Same as RM35UB330 ¦ Germanisher Lloyd,Environmental category,
84873220ambient air temperature for storage | Same as RM35UB330 ¦ ,Storage,
84873220ambient air temperature for operation | Same as RM35UB330 ¦ ,Operation,
84873220relative humidity | Same as RM35UB330 ¦ IEC60068-2-30,Damp heat,XX
84873220 | Same as RM35UB330 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873220vibration resistance | Same as RM35UB330 ¦ IEC60068-2-6
84873220shock resistance | Same as RM35UB330 ¦ IEC60068-2-27
84873220bump resistance | Same as RM35UB330 ¦ IEC60068-2-29
84873220seismic resistance | Same as RM35UB330 ¦ IEC60068-3-3
84873220IP degree of protection | Same as RM35UB330 ¦ IEC60529,Terminal Block,
84873220IP degree of protection | Same as RM35UB330 ¦ IEC60529,Housing,
84873220IP degree of protection | Same as RM35UB330 ¦ IEC60529,Front Panel,
84873220
84873220width | Same as RM35UB330 ¦ ,Width,
84873220height | Same as RM35UB330 ¦ ,Height,
84873220depth | Same as RM35UB330 ¦ ,Depth,
84873220net weight | Same as RM35UB330
84873220mounting support | Same as RM35UB330 ¦ IEC/EN 60715,Without socket,
84873220mounting support | Same as RM35UB330 ¦ IEC/EN 60715,With socket,
84873220mounting position | Same as RM35UB330 ¦ ,In relation to normal vertical mounting plane,
84873220Minimum distance to adjacent devices | Same as RM35UB330 ¦ ,Horizontal,
84873220Minimum distance to adjacent devices | Same as RM35UB330 ¦ ,Vertical,
84873220connections - terminals | Same as RM35UB330 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873220connections - terminals | Same as RM35UB330 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873220connections - terminals | Same as RM35UB330 ¦ IEC60947-1,Solid cable (spring terminal),
84873220connections - terminals | Same as RM35UB330 ¦ IEC60947-1,Flexible cable (spring terminal),
84873220tightening torque | Same as RM35UB330 ¦ IEC60947-1,Tightening torque,
84873220cable stripping length | Same as RM35UB330 ¦ ,Cable stripping length,
84873220duty time | Same as RM35UB330
84873220
84873220electromagnetic compatibility | Same as RM35UB330 ¦ ,Generic immunity standard,
84873220electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-2,Electrostatic discharge,
84873220electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873220electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-4,Fast transient / burst,
84873220electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-5,Surge,
84873220electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-6,Conducted RF disturbance,
84873220electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-8,Power frequency magnetic field,
84873220electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873220electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873220electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-29,DC voltage interruption,
84873220electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-13,Low frequency harmonics,
84873220electromagnetic compatibility | Same as RM35UB330 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873220electromagnetic compatibility | Same as RM35UB330 ¦ ,Generic emission standard,
84873220electromagnetic compatibility | Same as RM35UB330 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873220electromagnetic compatibility | Same as RM35UB330 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873220electromagnetic compatibility | Same as RM35UB330 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873220electromagnetic compatibility | Same as RM35UB330 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873220electromagnetic compatibility | Same as RM35UB330 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873220electromagnetic compatibility | Same as RM35UB330 ¦ Germanisher Lloyd,Conducted emission,
84873220
84873220pollution degree | Same as RM35UB330 ¦ IEC60664-1
84873220overvoltage category | Same as RM35UB330 ¦ IEC60664-1
84873220circuit group | Same as RM35UB330 ¦ ,Supply,Terminal
84873220circuit group | Same as RM35UB330 ¦ ,Input 1,
84873220circuit group | Same as RM35UB330 ¦ ,Input 2,
84873220circuit group | Same as RM35UB330 ¦ ,Input 3,
84873220circuit group | Same as RM35UB330 ¦ ,Output 1,
84873220circuit group | Same as RM35UB330 ¦ ,Output 2,
84873220 | Same as RM35UB330 ¦ ,Supply,Rated
84873220 | Same as RM35UB330 ¦ ,Input 1,Voltage
84873220 | Same as RM35UB330 ¦ ,Input 2,Spec
84873220 | Same as RM35UB330 ¦ ,Input 3,
84873220 | Same as RM35UB330 ¦ ,Output 1,
84873220 | Same as RM35UB330 ¦ ,Output 2,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Supply,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 2,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 3,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Output 1,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Output 2,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Input 2,Isolated
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Input 3,Circuit
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Output 1,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Output 2,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Output 1 / Output 2,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1 / Output 1,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1 / Output 2,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 2 / Output 1,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 2 / Output 2,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 3 / Output 1,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 3 / Output 2,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1 / Input 2,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 2 / Input 3,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1 / Input 3,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Supply,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 2,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 3,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Output 1,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Output 2,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Input 2,Isolated
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Input 3,Circuit
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Output 1,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Output 2,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Output 1 / Output 2,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1 / Output 1,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1 / Output 2,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 2 / Output 1,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 2 / Output 2,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 3 / Output 1,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 3 / Output 2,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1 / Input 2,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 2 / Input 3,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1 / Input 3,
84873220dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Supply / Input 1,
84873220dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Supply / Input 2,
84873220dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Supply / Input 3,
84873220dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Supply / Output 1,
84873220dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Supply / Output 2,
84873220dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Output 1 / Output 2,
84873220dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 1 / Output 1,
84873220dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 1 / Output 2,
84873220dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 2 / Output 1,
84873220dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 2 / Output 2,
84873220dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 3 / Output 1,
84873220dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 3 / Output 2,
84873220dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 1 / Input 2,
84873220dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 2 / Input 3,
84873220dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 1 / Input 3,
84873220insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Supply / Input 1,
84873220insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Supply / Input 2,
84873220insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Supply / Input 3,
84873220insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Supply / Output 1,
84873220insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Supply / Output 2,
84873220insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Output 1 / Output 2,
84873220insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 1 / Output 1,
84873220insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 1 / Output 2,
84873220insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 2 / Output 1,
84873220insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 2 / Output 2,
84873220insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 3 / Output 1,
84873220insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 3 / Output 2,
84873220insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 1 / Input 2,
84873220insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 2 / Input 3,
84873220insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 1 / Input 3,
84873220
84873220[Us] rated supply voltage | Same as RM35UB330
84873220supply voltage limits | Same as RM35UB330
84873220polarity | Same as RM35UB330
84873220supply frequency | Same as RM35UB330
84873220supply frequency | Same as RM35UB330
84873220power consumption | Same as RM35UB330
84873220immunity to microbreaks | Same as RM35UB330
84873220supply terminal | Same as RM35UB330
84873220on-load factor | Same as RM35UB330
84873220release of input voltage | Same as RM35UB330
84873220
84873220monitoring functions | Same as RM35UB330 ¦ ,Phase lost ,
84873220monitoring functions | Same as RM35UB330 ¦ ,Phase sequence,
84873220monitoring functions | Same as RM35UB330 ¦ ,Over / undervoltage (symmetry windows mode),
84873220monitoring functions | Same as RM35UB330 ¦ ,Over voltage,
84873220monitoring functions | Same as RM35UB330 ¦ ,Undervoltage ,
84873220monitoring functions | Same as RM35UB330 ¦ ,Phase asymmetry,
84873220monitoring functions | Same as RM35UB330 ¦ ,Disconnection of neutral,
84873220monitoring functions | Same as RM35UB330 ¦ ,Voltage Regeneration,
84873220monitoring functions | Same as RM35UB330 ¦ ,Extreme undervoltage,
84873220monitoring functions | Same as RM35UB330 ¦ ,Extreme overvoltage,
84873220monitoring functions | Same as RM35UB330 ¦ ,Extreme asymmetry,
84873220 | Same as RM35UB330 ¦ ,Measurement mode,
84873220internal input resistance | Same as RM35UB330 ¦ ,Internal input resistance,
84873220input terminal | Same as RM35UB330 ¦ ,Input terminal,
84873220Input nominal voltage selection | Same as RM35UB330 ¦ ,Input nominal voltage selection,
84873220permissible input overload | Same as RM35UB330 ¦ ,permissible input overload,
84873220input frequency | Same as RM35UB330 ¦ ,Rated frequency,
84873220input frequency | Same as RM35UB330 ¦ ,Frequency operating range,
84873220setting accuracy of the switching threshold | Same as RM35UB330 ¦ ,Setting accuracy,
84873220repeat accuracy of the switching threshold | Same as RM35UB330 ¦ ,Repeat accuracy (constant parameters),
84873220measurement method | Same as RM35UB330 ¦ ,Measurement method,
84873220switching threshold drift | Same as RM35UB330 ¦ ,Measurement error with supply voltage variation,
84873220switching threshold drift | Same as RM35UB330 ¦ ,Measurement error with temperature variation,
84873220maximum measuring cycle | Same as RM35UB330 ¦ ,Maximum measuring cycles,
84873220measurement range | Same as RM35UB330 ¦ ,Phase lost ,
84873220measurement range | Same as RM35UB330 ¦ ,Phase sequence,
84873220measurement range | Same as RM35UB330 ¦ ,Over / undervoltage (symmetry windows mode),
84873220measurement range | Same as RM35UB330 ¦ ,Over voltage,
84873220measurement range | Same as RM35UB330 ¦ ,Undervoltage ,
84873220measurement range | Same as RM35UB330 ¦ ,Phase asymmetry,
84873220measurement range | Same as RM35UB330 ¦ ,Disconnection of neutral,
84873220measurement range | Same as RM35UB330 ¦ ,Voltage Regeneration,
84873220measurement range | Same as RM35UB330 ¦ ,Extreme undervoltage,
84873220measurement range | Same as RM35UB330 ¦ ,Extreme Overvoltage,
84873220measurement range | Same as RM35UB330 ¦ ,Extreme Asymmetry,
84873220tripping threshold | Same as RM35UB330 ¦ ,Phase cut,
84873220tripping threshold | Same as RM35UB330 ¦ ,Phase sequence,
84873220tripping threshold | Same as RM35UB330 ¦ ,Over / undervoltage (symmetry windows mode),
84873220tripping threshold | Same as RM35UB330 ¦ ,Over voltage,
84873220tripping threshold | Same as RM35UB330 ¦ ,Undervoltage ,
84873220tripping threshold | Same as RM35UB330 ¦ ,Phase asymmetry,
84873220tripping threshold | Same as RM35UB330 ¦ ,Disconnection of neutral,
84873220tripping threshold | Same as RM35UB330 ¦ ,Voltage Regeneration,
84873220tripping threshold | Same as RM35UB330 ¦ ,Extreme undervoltage (Phase loss),
84873220tripping threshold | Same as RM35UB330 ¦ ,Extreme Overvoltage,
84873220tripping threshold | Same as RM35UB330 ¦ ,Extreme Asymmetry,
84873220hysteresis | Same as RM35UB330 ¦ ,Phase cut,
84873220hysteresis | Same as RM35UB330 ¦ ,Phase sequence,
84873220hysteresis | Same as RM35UB330 ¦ ,Over / undervoltage (symmetry windows mode),
84873220hysteresis | Same as RM35UB330 ¦ ,Over voltage,
84873220hysteresis | Same as RM35UB330 ¦ ,Undervoltage ,
84873220hysteresis | Same as RM35UB330 ¦ ,Phase asymmetry,
84873220hysteresis | Same as RM35UB330 ¦ ,Disconnection of neutral,
84873220hysteresis | Same as RM35UB330 ¦ ,Voltage Regeneration,
84873220hysteresis | Same as RM35UB330 ¦ ,Extreme undervoltage (Phase loss),
84873220hysteresis | Same as RM35UB330 ¦ ,Extreme Overvoltage,
84873220hysteresis | Same as RM35UB330 ¦ ,Extreme Asymmetry,
84873220
84873220output type | Same as RM35UB330
84873220output terminal | Same as RM35UB330
84873220output logic | Same as RM35UB330 ¦ ,R1 (11-12-14),
84873220output logic | Same as RM35UB330 ¦ ,R2 (21-22-24),
84873220contacts material | Same as RM35UB330
84873220mechanical durability | Same as RM35UB330 ¦ IEC61810-1
84873220electrical durability | Same as RM35UB330 ¦ IEC60947-4-1,AC-1,
84873220electrical durability | Same as RM35UB330 ¦ IEC60947-4-1,DC-1,
84873220electrical durability | Same as RM35UB330 ¦ IEC60947-5-1,AC-15,
84873220electrical durability | Same as RM35UB330 ¦ IEC60947-5-1,DC-13,
84873220[Ue] rated operational voltage | Same as RM35UB330 ¦ IEC61810-1,Rated switching voltage,
84873220[Ie] rated operational current | Same as RM35UB330 ¦ IEC61810-1,Rated switching current,
84873220maximum switching capacity | Same as RM35UB330 ¦ ,Maximum switching voltage,
84873220maximum switching capacity | Same as RM35UB330 ¦ ,Maximum switching current,
84873220maximum switching capacity | Same as RM35UB330 ¦ ,Maximum switching capacity,
84873220minimum switching capacity | Same as RM35UB330 ¦ IEC60947-5-4,Minimum switching voltage,
84873220minimum switching capacity | Same as RM35UB330 ¦ IEC60947-5-4,Minimum switching current,
84873220minimum switching capacity | Same as RM35UB330 ¦ IEC60947-5-4,Minimum switching capacity,
84873220maximum voltage drop | Same as RM35UB330 ¦ IEC62314,Only for solid state output,
84873220maximum leakage current | Same as RM35UB330 ¦ IEC62314,Only for solid state output,
84873220thermal current | Same as RM35UB330 ¦ IEC60947-5-1
84873220short circuit protection | Same as RM35UB330 ¦ IEC60947-5-1,Relay Output by external fuse,
84873220short circuit protection | Same as RM35UB330 ¦ IEC62314,Solid State Output by external fuse,
84873220
84873220time delay type | Same as RM35UB330 ¦ ,"OFF" delay,
84873220time delay type | Same as RM35UB330 ¦ ,"ON" delay,
84873220time delay type | Same as RM35UB330 ¦ ,Inhibition,
84873220time delay range | Same as RM35UB330 ¦ ,"OFF" delay,
84873220time delay range | Same as RM35UB330 ¦ ,"ON" delay,
84873220time delay range | Same as RM35UB330 ¦ ,Inhibition,
84873220response time | Same as RM35UB330 ¦ ,on crossing the threshold,
84873220response time | Same as RM35UB330
84873220response time | Same as RM35UB330
84873220response time | Same as RM35UB330
84873220response time | Same as RM35UB330
84873220power on delay | Same as RM35UB330
84873220reset time | Same as RM35UB330 ¦ ,through Un power reset,
84873220reset time | Same as RM35UB330 ¦ ,through front panel reset,
84873220reset time | Same as RM35UB330 ¦ ,through input control reset,
84873220setting accuracy of time delay | Same as RM35UB330
84873220repeat accuracy of time delay | Same as RM35UB330
84873220time delay drift | Same as RM35UB330
84873220time delay drift | Same as RM35UB330
84873220
84873220status LED | Same as RM35UB330
84873220local signalling | Same as RM35UB330 ¦ ,Power supply availability,
84873220local signalling | Same as RM35UB330 ¦ ,Power supply not availability,
84873220local signalling | Same as RM35UB330 ¦ ,Timing in-progress,
84873220local signalling | Same as RM35UB330 ¦ ,Output is energized,
84873220local signalling | Same as RM35UB330 ¦ ,Output is de-energized,
84873220local signalling | Same as RM35UB330 ¦ ,Range Setting Changes,
84873220local signalling | Same as RM35UB330 ¦ ,Phase Cut,
84873220local signalling | Same as RM35UB330 ¦ ,Phase Sequence Swap,
84873220local signalling | Same as RM35UB330 ¦ ,Undervoltage <U,
84873220local signalling | Same as RM35UB330 ¦ ,Overvoltage >U,
84873220local signalling | Same as RM35UB330 ¦ ,Phase Asymmetry,
84873220local signalling | Same as RM35UB330 ¦ ,Voltage Regeneration,
84873220local signalling | Same as RM35UB330 ¦ ,Extreme Undervoltage <U (Phase loss),
84873220local signalling | Same as RM35UB330 ¦ ,Extreme Overvoltage >U,
84873220local signalling | Same as RM35UB330 ¦ ,Extreme Phase Asymmetry,
84873220
84873220 | Same as RM35UB330
84873220 | Same as RM35UB330
84873220diagnostic button | Same as RM35UB330
84873220 | Same as RM35UB330
84873220 | Same as RM35UB330
84873220
84873220safety reliability data | Same as RM35UB330 ¦ ,MTTF,
84873220safety reliability data | Same as RM35UB330 ¦ ,B10,
84873220 | Same as RM35UB330 ¦ ,MTTFd,
84873220 | Same as RM35UB330 ¦ ,B10d,
84873220
84873220 | Drawing / Diagram
84873894
84873894standards | Same as RM35UB330
84873894product certifications | UL, CSA, CE, China ROHS
84873894marking | UL, CSA, CE, China ROHS
84873894directives | Same as RM35UB330
84873894directives | Same as RM35UB330
84873894directives | Same as RM35UB330
84873894
84873894 | Same as RM35UB330 ¦ IEC60721-3-3,Climatic category,
84873894 | Same as RM35UB330 ¦ Germanisher Lloyd,Environmental category,
84873894ambient air temperature for storage | Same as RM35UB330 ¦ ,Storage,
84873894ambient air temperature for operation | Same as RM35UB330 ¦ ,Operation,
84873894relative humidity | Same as RM35UB330 ¦ IEC60068-2-30,Damp heat,XX
84873894 | Same as RM35UB330 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873894vibration resistance | Same as RM35UB330 ¦ IEC60068-2-6
84873894shock resistance | Same as RM35UB330 ¦ IEC60068-2-27
84873894bump resistance | Same as RM35UB330 ¦ IEC60068-2-29
84873894seismic resistance | Same as RM35UB330 ¦ IEC60068-3-3
84873894IP degree of protection | Same as RM35UB330 ¦ IEC60529,Terminal Block,
84873894IP degree of protection | Same as RM35UB330 ¦ IEC60529,Housing,
84873894IP degree of protection | Same as RM35UB330 ¦ IEC60529,Front Panel,
84873894
84873894width | Same as RM35UB330 ¦ ,Width,
84873894height | Same as RM35UB330 ¦ ,Height,
84873894depth | Same as RM35UB330 ¦ ,Depth,
84873894net weight | Same as RM35UB330
84873894mounting support | Same as RM35UB330 ¦ IEC/EN 60715,Without socket,
84873894mounting support | Same as RM35UB330 ¦ IEC/EN 60715,With socket,
84873894mounting position | Same as RM35UB330 ¦ ,In relation to normal vertical mounting plane,
84873894Minimum distance to adjacent devices | Same as RM35UB330 ¦ ,Horizontal,
84873894Minimum distance to adjacent devices | Same as RM35UB330 ¦ ,Vertical,
84873894connections - terminals | Same as RM35UB330 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873894connections - terminals | Same as RM35UB330 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873894connections - terminals | Same as RM35UB330 ¦ IEC60947-1,Solid cable (spring terminal),
84873894connections - terminals | Same as RM35UB330 ¦ IEC60947-1,Flexible cable (spring terminal),
84873894tightening torque | Same as RM35UB330 ¦ IEC60947-1,Tightening torque,
84873894cable stripping length | Same as RM35UB330 ¦ ,Cable stripping length,
84873894duty time | Same as RM35UB330
84873894
84873894electromagnetic compatibility | Same as RM35UB330 ¦ ,Generic immunity standard,
84873894electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-2,Electrostatic discharge,
84873894electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873894electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-4,Fast transient / burst,
84873894electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-5,Surge,
84873894electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-6,Conducted RF disturbance,
84873894electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-8,Power frequency magnetic field,
84873894electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873894electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873894electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-29,DC voltage interruption,
84873894electromagnetic compatibility | Same as RM35UB330 ¦ IEC61000-4-13,Low frequency harmonics,
84873894electromagnetic compatibility | Same as RM35UB330 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873894electromagnetic compatibility | Same as RM35UB330 ¦ ,Generic emission standard,
84873894electromagnetic compatibility | Same as RM35UB330 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873894electromagnetic compatibility | Same as RM35UB330 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873894electromagnetic compatibility | Same as RM35UB330 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873894electromagnetic compatibility | Same as RM35UB330 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873894electromagnetic compatibility | Same as RM35UB330 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873894electromagnetic compatibility | Same as RM35UB330 ¦ Germanisher Lloyd,Conducted emission,
84873894
84873894pollution degree | Same as RM35UB330 ¦ IEC60664-1
84873894overvoltage category | Same as RM35UB330 ¦ IEC60664-1
84873894circuit group | Same as RM35UB330 ¦ ,Supply,Terminal
84873894circuit group | Same as RM35UB330 ¦ ,Input 1,
84873894circuit group | Same as RM35UB330 ¦ ,Input 2,
84873894circuit group | Same as RM35UB330 ¦ ,Input 3,
84873894circuit group | Same as RM35UB330 ¦ ,Output 1,
84873894circuit group | Same as RM35UB330 ¦ ,Output 2,
84873894 | Same as RM35UB330 ¦ ,Supply,Rated
84873894 | Same as RM35UB330 ¦ ,Input 1,Voltage
84873894 | Same as RM35UB330 ¦ ,Input 2,Spec
84873894 | Same as RM35UB330 ¦ ,Input 3,
84873894 | Same as RM35UB330 ¦ ,Output 1,
84873894 | Same as RM35UB330 ¦ ,Output 2,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Supply,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 2,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 3,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Output 1,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Output 2,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Input 2,Isolated
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Input 3,Circuit
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Output 1,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Output 2,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Output 1 / Output 2,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1 / Output 1,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1 / Output 2,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 2 / Output 1,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 2 / Output 2,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 3 / Output 1,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 3 / Output 2,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1 / Input 2,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 2 / Input 3,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1 / Input 3,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Supply,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 2,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 3,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Output 1,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Output 2,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Input 2,Isolated
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Input 3,Circuit
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Output 1,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Supply / Output 2,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Output 1 / Output 2,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1 / Output 1,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1 / Output 2,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 2 / Output 1,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 2 / Output 2,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 3 / Output 1,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 3 / Output 2,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1 / Input 2,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 2 / Input 3,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Input 1 / Input 3,
84873894dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Supply / Input 1,
84873894dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Supply / Input 2,
84873894dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Supply / Input 3,
84873894dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Supply / Output 1,
84873894dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Supply / Output 2,
84873894dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Output 1 / Output 2,
84873894dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 1 / Output 1,
84873894dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 1 / Output 2,
84873894dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 2 / Output 1,
84873894dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 2 / Output 2,
84873894dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 3 / Output 1,
84873894dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 3 / Output 2,
84873894dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 1 / Input 2,
84873894dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 2 / Input 3,
84873894dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Input 1 / Input 3,
84873894insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Supply / Input 1,
84873894insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Supply / Input 2,
84873894insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Supply / Input 3,
84873894insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Supply / Output 1,
84873894insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Supply / Output 2,
84873894insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Output 1 / Output 2,
84873894insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 1 / Output 1,
84873894insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 1 / Output 2,
84873894insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 2 / Output 1,
84873894insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 2 / Output 2,
84873894insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 3 / Output 1,
84873894insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 3 / Output 2,
84873894insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 1 / Input 2,
84873894insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 2 / Input 3,
84873894insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Input 1 / Input 3,
84873894
84873894[Us] rated supply voltage | Same as RM35UB330
84873894supply voltage limits | Same as RM35UB330
84873894polarity | Same as RM35UB330
84873894supply frequency | Same as RM35UB330
84873894supply frequency | Same as RM35UB330
84873894power consumption | Same as RM35UB330
84873894immunity to microbreaks | Same as RM35UB330
84873894supply terminal | Same as RM35UB330
84873894on-load factor | Same as RM35UB330
84873894release of input voltage | Same as RM35UB330
84873894
84873894monitoring functions | Same as RM35UB330 ¦ ,Phase lost ,
84873894monitoring functions | Same as RM35UB330 ¦ ,Phase sequence,
84873894monitoring functions | Same as RM35UB330 ¦ ,Over / undervoltage (symmetry windows mode),
84873894monitoring functions | Same as RM35UB330 ¦ ,Over voltage,
84873894monitoring functions | Same as RM35UB330 ¦ ,Undervoltage ,
84873894monitoring functions | Same as RM35UB330 ¦ ,Phase asymmetry,
84873894monitoring functions | Same as RM35UB330 ¦ ,Disconnection of neutral,
84873894monitoring functions | Same as RM35UB330 ¦ ,Voltage Regeneration,
84873894monitoring functions | Same as RM35UB330 ¦ ,Extreme undervoltage,
84873894monitoring functions | Same as RM35UB330 ¦ ,Extreme overvoltage,
84873894monitoring functions | Same as RM35UB330 ¦ ,Extreme asymmetry,
84873894 | Same as RM35UB330 ¦ ,Measurement mode,
84873894internal input resistance | Same as RM35UB330 ¦ ,Internal input resistance,
84873894input terminal | Same as RM35UB330 ¦ ,Input terminal,
84873894Input nominal voltage selection | Same as RM35UB330 ¦ ,Input nominal voltage selection,
84873894permissible input overload | Same as RM35UB330 ¦ ,permissible input overload,
84873894input frequency | Same as RM35UB330 ¦ ,Rated frequency,
84873894input frequency | Same as RM35UB330 ¦ ,Frequency operating range,
84873894setting accuracy of the switching threshold | Same as RM35UB330 ¦ ,Setting accuracy,
84873894repeat accuracy of the switching threshold | Same as RM35UB330 ¦ ,Repeat accuracy (constant parameters),
84873894measurement method | Same as RM35UB330 ¦ ,Measurement method,
84873894switching threshold drift | Same as RM35UB330 ¦ ,Measurement error with supply voltage variation,
84873894switching threshold drift | Same as RM35UB330 ¦ ,Measurement error with temperature variation,
84873894maximum measuring cycle | Same as RM35UB330 ¦ ,Maximum measuring cycles,
84873894measurement range | Same as RM35UB330 ¦ ,Phase lost ,
84873894measurement range | Same as RM35UB330 ¦ ,Phase sequence,
84873894measurement range | Same as RM35UB330 ¦ ,Over / undervoltage (symmetry windows mode),
84873894measurement range | Same as RM35UB330 ¦ ,Over voltage,
84873894measurement range | Same as RM35UB330 ¦ ,Undervoltage ,
84873894measurement range | Same as RM35UB330 ¦ ,Phase asymmetry,
84873894measurement range | Same as RM35UB330 ¦ ,Disconnection of neutral,
84873894measurement range | Same as RM35UB330 ¦ ,Voltage Regeneration,
84873894measurement range | Same as RM35UB330 ¦ ,Extreme undervoltage,
84873894measurement range | Same as RM35UB330 ¦ ,Extreme Overvoltage,
84873894measurement range | Same as RM35UB330 ¦ ,Extreme Asymmetry,
84873894tripping threshold | Same as RM35UB330 ¦ ,Phase cut,
84873894tripping threshold | Same as RM35UB330 ¦ ,Phase sequence,
84873894tripping threshold | Same as RM35UB330 ¦ ,Over / undervoltage (symmetry windows mode),
84873894tripping threshold | Same as RM35UB330 ¦ ,Over voltage,
84873894tripping threshold | Same as RM35UB330 ¦ ,Undervoltage ,
84873894tripping threshold | Same as RM35UB330 ¦ ,Phase asymmetry,
84873894tripping threshold | Same as RM35UB330 ¦ ,Disconnection of neutral,
84873894tripping threshold | Same as RM35UB330 ¦ ,Voltage Regeneration,
84873894tripping threshold | Same as RM35UB330 ¦ ,Extreme undervoltage (Phase loss),
84873894tripping threshold | Same as RM35UB330 ¦ ,Extreme Overvoltage,
84873894tripping threshold | Same as RM35UB330 ¦ ,Extreme Asymmetry,
84873894hysteresis | Same as RM35UB330 ¦ ,Phase cut,
84873894hysteresis | Same as RM35UB330 ¦ ,Phase sequence,
84873894hysteresis | Same as RM35UB330 ¦ ,Over / undervoltage (symmetry windows mode),
84873894hysteresis | Same as RM35UB330 ¦ ,Over voltage,
84873894hysteresis | Same as RM35UB330 ¦ ,Undervoltage ,
84873894hysteresis | Same as RM35UB330 ¦ ,Phase asymmetry,
84873894hysteresis | Same as RM35UB330 ¦ ,Disconnection of neutral,
84873894hysteresis | Same as RM35UB330 ¦ ,Voltage Regeneration,
84873894hysteresis | Same as RM35UB330 ¦ ,Extreme undervoltage (Phase loss),
84873894hysteresis | Same as RM35UB330 ¦ ,Extreme Overvoltage,
84873894hysteresis | Same as RM35UB330 ¦ ,Extreme Asymmetry,
84873894
84873894output type | Same as RM35UB330
84873894output terminal | Same as RM35UB330
84873894output logic | Same as RM35UB330 ¦ ,R1 (11-12-14),
84873894output logic | Same as RM35UB330 ¦ ,R2 (21-22-24),
84873894contacts material | Same as RM35UB330
84873894mechanical durability | Same as RM35UB330 ¦ IEC61810-1
84873894electrical durability | Same as RM35UB330 ¦ IEC60947-4-1,AC-1,
84873894electrical durability | Same as RM35UB330 ¦ IEC60947-4-1,DC-1,
84873894electrical durability | Same as RM35UB330 ¦ IEC60947-5-1,AC-15,
84873894electrical durability | Same as RM35UB330 ¦ IEC60947-5-1,DC-13,
84873894[Ue] rated operational voltage | Same as RM35UB330 ¦ IEC61810-1,Rated switching voltage,
84873894[Ie] rated operational current | Same as RM35UB330 ¦ IEC61810-1,Rated switching current,
84873894maximum switching capacity | Same as RM35UB330 ¦ ,Maximum switching voltage,
84873894maximum switching capacity | Same as RM35UB330 ¦ ,Maximum switching current,
84873894maximum switching capacity | Same as RM35UB330 ¦ ,Maximum switching capacity,
84873894minimum switching capacity | Same as RM35UB330 ¦ IEC60947-5-4,Minimum switching voltage,
84873894minimum switching capacity | Same as RM35UB330 ¦ IEC60947-5-4,Minimum switching current,
84873894minimum switching capacity | Same as RM35UB330 ¦ IEC60947-5-4,Minimum switching capacity,
84873894maximum voltage drop | Same as RM35UB330 ¦ IEC62314,Only for solid state output,
84873894maximum leakage current | Same as RM35UB330 ¦ IEC62314,Only for solid state output,
84873894thermal current | Same as RM35UB330 ¦ IEC60947-5-1
84873894short circuit protection | Same as RM35UB330 ¦ IEC60947-5-1,Relay Output by external fuse,
84873894short circuit protection | Same as RM35UB330 ¦ IEC62314,Solid State Output by external fuse,
84873894
84873894time delay type | Same as RM35UB330 ¦ ,"OFF" delay,
84873894time delay type | Same as RM35UB330 ¦ ,"ON" delay,
84873894time delay type | Same as RM35UB330 ¦ ,Inhibition,
84873894time delay range | Same as RM35UB330 ¦ ,"OFF" delay,
84873894time delay range | Same as RM35UB330 ¦ ,"ON" delay,
84873894time delay range | Same as RM35UB330 ¦ ,Inhibition,
84873894response time | Same as RM35UB330 ¦ ,on crossing the threshold,
84873894response time | Same as RM35UB330
84873894response time | Same as RM35UB330
84873894response time | Same as RM35UB330
84873894response time | Same as RM35UB330
84873894power on delay | Same as RM35UB330
84873894reset time | Same as RM35UB330 ¦ ,through Un power reset,
84873894reset time | Same as RM35UB330 ¦ ,through front panel reset,
84873894reset time | Same as RM35UB330 ¦ ,through input control reset,
84873894setting accuracy of time delay | Same as RM35UB330
84873894repeat accuracy of time delay | Same as RM35UB330
84873894time delay drift | Same as RM35UB330
84873894time delay drift | Same as RM35UB330
84873894
84873894status LED | Same as RM35UB330
84873894local signalling | Same as RM35UB330 ¦ ,Power supply availability,
84873894local signalling | Same as RM35UB330 ¦ ,Power supply not availability,
84873894local signalling | Same as RM35UB330 ¦ ,Timing in-progress,
84873894local signalling | Same as RM35UB330 ¦ ,Output is energized,
84873894local signalling | Same as RM35UB330 ¦ ,Output is de-energized,
84873894local signalling | Same as RM35UB330 ¦ ,Range Setting Changes,
84873894local signalling | Same as RM35UB330 ¦ ,Phase Cut,
84873894local signalling | Same as RM35UB330 ¦ ,Phase Sequence Swap,
84873894local signalling | Same as RM35UB330 ¦ ,Undervoltage <U,
84873894local signalling | Same as RM35UB330 ¦ ,Overvoltage >U,
84873894local signalling | Same as RM35UB330 ¦ ,Phase Asymmetry,
84873894local signalling | Same as RM35UB330 ¦ ,Voltage Regeneration,
84873894local signalling | Same as RM35UB330 ¦ ,Extreme Undervoltage <U (Phase loss),
84873894local signalling | Same as RM35UB330 ¦ ,Extreme Overvoltage >U,
84873894local signalling | Same as RM35UB330 ¦ ,Extreme Phase Asymmetry,
84873894
84873894 | Same as RM35UB330
84873894 | Same as RM35UB330
84873894diagnostic button | Same as RM35UB330
84873894 | Same as RM35UB330
84873894 | Same as RM35UB330
84873894
84873894safety reliability data | Same as RM35UB330 ¦ ,MTTF,
84873894safety reliability data | Same as RM35UB330 ¦ ,B10,
84873894 | Same as RM35UB330 ¦ ,MTTFd,
84873894 | Same as RM35UB330 ¦ ,B10d,
84873894
84873894 | Drawing / Diagram
RM35UB3N30
RM35UB3N30standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM35UB3N30product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35UB3N30marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35UB3N30directives | 2014/35/EU
RM35UB3N30directives | 2014/30/EU
RM35UB3N30directives | 2011/65/EU
RM35UB3N30
RM35UB3N30 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM35UB3N30 | Class C ¦ Germanisher Lloyd,Environmental category,
RM35UB3N30ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM35UB3N30ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM35UB3N30relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM35UB3N30 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM35UB3N30vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM35UB3N30shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM35UB3N30bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM35UB3N30seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM35UB3N30IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM35UB3N30IP degree of protection | IP30 ¦ IEC60529,Housing,
RM35UB3N30IP degree of protection | - ¦ IEC60529,Front Panel,
RM35UB3N30
RM35UB3N30width | 35 ¦ ,Width,
RM35UB3N30height | 90 ¦ ,Height,
RM35UB3N30depth | 72 ¦ ,Depth,
RM35UB3N30net weight | 130
RM35UB3N30mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM35UB3N30mounting support | - ¦ IEC/EN 60715,With socket,
RM35UB3N30mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35UB3N30Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM35UB3N30Minimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM35UB3N30connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35UB3N30connections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35UB3N30connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM35UB3N30connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35UB3N30tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM35UB3N30cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM35UB3N30duty time | 1
RM35UB3N30
RM35UB3N30electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM35UB3N30electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM35UB3N30electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM35UB3N30electromagnetic compatibility | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM35UB3N30electromagnetic compatibility | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge,
RM35UB3N30electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM35UB3N30electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM35UB3N30electromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35UB3N30electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM35UB3N30electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM35UB3N30electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM35UB3N30electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35UB3N30electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM35UB3N30electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35UB3N30electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35UB3N30electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM35UB3N30electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35UB3N30electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35UB3N30electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35UB3N30
RM35UB3N30pollution degree | 3 ¦ IEC60664-1
RM35UB3N30overvoltage category | 3 ¦ IEC60664-1
RM35UB3N30circuit group | L1, L2, L3, N ¦ ,Supply,Terminal
RM35UB3N30circuit group | - ¦ ,Input 1,
RM35UB3N30circuit group | - ¦ ,Input 2,
RM35UB3N30circuit group | - ¦ ,Input 3,
RM35UB3N30circuit group | 11,12,14 ¦ ,Output 1,
RM35UB3N30circuit group | 21,22,24 ¦ ,Output 2,
RM35UB3N30 | 120..277 AC ¦ ,Supply,Rated
RM35UB3N30 | - ¦ ,Input 1,Voltage
RM35UB3N30 | - ¦ ,Input 2,Spec
RM35UB3N30 | - ¦ ,Input 3,
RM35UB3N30 | 250V ¦ ,Output 1,
RM35UB3N30 | 250V ¦ ,Output 2,
RM35UB3N30[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM35UB3N30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM35UB3N30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM35UB3N30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM35UB3N30[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM35UB3N30[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM35UB3N30[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35UB3N30[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM35UB3N30[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM35UB3N30[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM35UB3N30[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 2,
RM35UB3N30[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM35UB3N30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM35UB3N30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM35UB3N30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM35UB3N30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM35UB3N30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM35UB3N30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM35UB3N30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM35UB3N30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM35UB3N30[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM35UB3N30[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM35UB3N30[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM35UB3N30[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM35UB3N30[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM35UB3N30[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM35UB3N30dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM35UB3N30dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM35UB3N30dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM35UB3N30dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM35UB3N30dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM35UB3N30dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM35UB3N30dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM35UB3N30dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM35UB3N30dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM35UB3N30dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM35UB3N30dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM35UB3N30dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM35UB3N30dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM35UB3N30dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM35UB3N30dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM35UB3N30insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM35UB3N30insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM35UB3N30insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM35UB3N30insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM35UB3N30insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM35UB3N30insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM35UB3N30insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM35UB3N30insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM35UB3N30insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM35UB3N30insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM35UB3N30insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM35UB3N30insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM35UB3N30insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM35UB3N30insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM35UB3N30insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM35UB3N30
RM35UB3N30[Us] rated supply voltage | ~ 3 x 120…3 x 277
RM35UB3N30supply voltage limits | ~ 3 x 114…3 x 329
RM35UB3N30polarity | -
RM35UB3N30supply frequency | 50 / 60
RM35UB3N30supply frequency | 45…66
RM35UB3N30power consumption | 3.9VA @ 480VAC, 60Hz
RM35UB3N30immunity to microbreaks | 5
RM35UB3N30supply terminal | L1-L3
RM35UB3N30on-load factor | 1
RM35UB3N30release of input voltage | -
RM35UB3N30
RM35UB3N30monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost ,
RM35UB3N30monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence,
RM35UB3N30monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM35UB3N30monitoring functions | governed by time delay Tt1, status reflects to R1 ¦ ,Over voltage,
RM35UB3N30monitoring functions | governed by time delay Tt2, status reflects to R2 ¦ ,Undervoltage ,
RM35UB3N30monitoring functions | - ¦ ,Phase asymmetry,
RM35UB3N30monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Disconnection of neutral,
RM35UB3N30monitoring functions | - ¦ ,Voltage Regeneration,
RM35UB3N30monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage,
RM35UB3N30monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage,
RM35UB3N30monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM35UB3N30 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM35UB3N30internal input resistance | - ¦ ,Internal input resistance,
RM35UB3N30input terminal | L1-L2-L3-N ¦ ,Input terminal,
RM35UB3N30Input nominal voltage selection | 120, 127, 220, 230, 240, 260, 277 ¦ ,Input nominal voltage selection,
RM35UB3N30permissible input overload | - ¦ ,permissible input overload,
RM35UB3N30input frequency | 50 / 60 ¦ ,Rated frequency,
RM35UB3N30input frequency | 45…66 ¦ ,Frequency operating range,
RM35UB3N30setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM35UB3N30repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM35UB3N30measurement method | True RMS ¦ ,Measurement method,
RM35UB3N30switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation,
RM35UB3N30switching threshold drift | < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM35UB3N30maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM35UB3N30measurement range | - ¦ ,Phase lost ,
RM35UB3N30measurement range | - ¦ ,Phase sequence,
RM35UB3N30measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM35UB3N30measurement range | +2…+20 % in the ranges 3 x ~ 120…277 ¦ ,Over voltage,
RM35UB3N30measurement range | -2…-20 % in the ranges 3 x ~ 120…277 ¦ ,Undervoltage ,
RM35UB3N30measurement range | - ¦ ,Phase asymmetry,
RM35UB3N30measurement range | - ¦ ,Disconnection of neutral,
RM35UB3N30measurement range | - ¦ ,Voltage Regeneration,
RM35UB3N30measurement range | - ¦ ,Extreme undervoltage,
RM35UB3N30measurement range | - ¦ ,Extreme Overvoltage,
RM35UB3N30measurement range | - ¦ ,Extreme Asymmetry,
RM35UB3N30tripping threshold | 1 or more phase cut ¦ ,Phase cut,
RM35UB3N30tripping threshold | Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence,
RM35UB3N30tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM35UB3N30tripping threshold | Adjustable 2%...20% of selected Un ¦ ,Over voltage,
RM35UB3N30tripping threshold | Adjustable 2%...20% of selected Un ¦ ,Undervoltage ,
RM35UB3N30tripping threshold | - ¦ ,Phase asymmetry,
RM35UB3N30tripping threshold | Total cut of N ¦ ,Disconnection of neutral,
RM35UB3N30tripping threshold | - ¦ ,Voltage Regeneration,
RM35UB3N30tripping threshold | 1 or more phase < 80V Internal design spec: 1 or more phase <86V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM35UB3N30tripping threshold | Internal design spec: 368V +/- 5% ¦ ,Extreme Overvoltage,
RM35UB3N30tripping threshold | Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM35UB3N30hysteresis | All phase cut recover ¦ ,Phase cut,
RM35UB3N30hysteresis | Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence,
RM35UB3N30hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM35UB3N30hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Over voltage,
RM35UB3N30hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage ,
RM35UB3N30hysteresis | - ¦ ,Phase asymmetry,
RM35UB3N30hysteresis | - ¦ ,Disconnection of neutral,
RM35UB3N30hysteresis | - ¦ ,Voltage Regeneration,
RM35UB3N30hysteresis | All phases > 100V Internal design spec: All phases >88V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM35UB3N30hysteresis | Internal design spec: All phases <358V +/- 5% ¦ ,Extreme Overvoltage,
RM35UB3N30hysteresis | - ¦ ,Extreme Asymmetry,
RM35UB3N30
RM35UB3N30output type | 1 x C/O + 1 x C/O relay contacts
RM35UB3N30output terminal | 11-12-14, 21-22-24
RM35UB3N30output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM35UB3N30output logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM35UB3N30contacts material | Cadmium free
RM35UB3N30mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM35UB3N30electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM35UB3N30electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM35UB3N30electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM35UB3N30electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM35UB3N30[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM35UB3N30[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM35UB3N30maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM35UB3N30maximum switching capacity | 5A ¦ ,Maximum switching current,
RM35UB3N30maximum switching capacity | - ¦ ,Maximum switching capacity,
RM35UB3N30minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM35UB3N30minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM35UB3N30minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM35UB3N30maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35UB3N30maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35UB3N30thermal current | 5A ¦ IEC60947-5-1
RM35UB3N30short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse,
RM35UB3N30short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM35UB3N30
RM35UB3N30time delay type | Yes ¦ ,"OFF" delay,
RM35UB3N30time delay type | - ¦ ,"ON" delay,
RM35UB3N30time delay type | - ¦ ,Inhibition,
RM35UB3N30time delay range | Adjustable Tt1 0.1…30 for overvoltage @ R1 (11-12-14) Adjustable Tt2 0.1…30 for undervoltage @ R2 (21-22-24) ¦ ,"OFF" delay,
RM35UB3N30time delay range | - ¦ ,"ON" delay,
RM35UB3N30time delay range | - ¦ ,Inhibition,
RM35UB3N30response time | 0
RM35UB3N30response time | -
RM35UB3N30response time | -
RM35UB3N30response time | -
RM35UB3N30response time | -
RM35UB3N30power on delay | 0
RM35UB3N30reset time | 0
RM35UB3N30reset time | - ¦ ,through front panel reset,
RM35UB3N30reset time | - ¦ ,through input control reset,
RM35UB3N30setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM35UB3N30repeat accuracy of time delay | +/- 3%
RM35UB3N30time delay drift | -
RM35UB3N30time delay drift | -
RM35UB3N30
RM35UB3N30status LED | Un (Green) R1 (Amber) R2 (Amber)
RM35UB3N30local signalling | Un - ON ¦ ,Power supply availability,
RM35UB3N30local signalling | Un - OFF ¦ ,Power supply not availability,
RM35UB3N30local signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM35UB3N30local signalling | R1 / R2 - ON ¦ ,Output is energized,
RM35UB3N30local signalling | R 1 / R2 - OFF ¦ ,Output is de-energized,
RM35UB3N30local signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM35UB3N30local signalling | R 1 / R2 - OFF ¦ ,Phase Cut,
RM35UB3N30local signalling | R 1 / R2 - OFF ¦ ,Phase Sequence Swap,
RM35UB3N30local signalling | R2 - OFF ¦ ,Undervoltage <U,
RM35UB3N30local signalling | R 1 - OFF ¦ ,Overvoltage >U,
RM35UB3N30local signalling | - ¦ ,Phase Asymmetry,
RM35UB3N30local signalling | - ¦ ,Voltage Regeneration,
RM35UB3N30local signalling | R 1 / R2 - OFF ¦ ,Extreme Undervoltage <U (Phase loss),
RM35UB3N30local signalling | R 1 / R2 - OFF ¦ ,Extreme Overvoltage >U,
RM35UB3N30local signalling | - ¦ ,Extreme Phase Asymmetry,
RM35UB3N30
RM35UB3N30 | Yes
RM35UB3N30 | -
RM35UB3N30diagnostic button | -
RM35UB3N30 | -
RM35UB3N30 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM35UB3N30
RM35UB3N30safety reliability data | 4,400,000 hours ¦ ,MTTF,
RM35UB3N30safety reliability data | 470,000 hours ¦ ,B10,
RM35UB3N30 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM35UB3N30 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM35UB3N30
RM35UB3N30 | Drawing / Diagram
84873221
84873221standards | Same as RM35UB3N30
84873221product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873221marking | UL, CSA, GL, CCC, CE, China ROHS
84873221directives | Same as RM35UB3N30
84873221directives | Same as RM35UB3N30
84873221directives | Same as RM35UB3N30
84873221
84873221 | Same as RM35UB3N30 ¦ IEC60721-3-3,Climatic category,
84873221 | Same as RM35UB3N30 ¦ Germanisher Lloyd,Environmental category,
84873221ambient air temperature for storage | Same as RM35UB3N30 ¦ ,Storage,
84873221ambient air temperature for operation | Same as RM35UB3N30 ¦ ,Operation,
84873221relative humidity | Same as RM35UB3N30 ¦ IEC60068-2-30,Damp heat,XX
84873221 | Same as RM35UB3N30 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873221vibration resistance | Same as RM35UB3N30 ¦ IEC60068-2-6
84873221shock resistance | Same as RM35UB3N30 ¦ IEC60068-2-27
84873221bump resistance | Same as RM35UB3N30 ¦ IEC60068-2-29
84873221seismic resistance | Same as RM35UB3N30 ¦ IEC60068-3-3
84873221IP degree of protection | Same as RM35UB3N30 ¦ IEC60529,Terminal Block,
84873221IP degree of protection | Same as RM35UB3N30 ¦ IEC60529,Housing,
84873221IP degree of protection | Same as RM35UB3N30 ¦ IEC60529,Front Panel,
84873221
84873221width | Same as RM35UB3N30 ¦ ,Width,
84873221height | Same as RM35UB3N30 ¦ ,Height,
84873221depth | Same as RM35UB3N30 ¦ ,Depth,
84873221net weight | Same as RM35UB3N30
84873221mounting support | Same as RM35UB3N30 ¦ IEC/EN 60715,Without socket,
84873221mounting support | Same as RM35UB3N30 ¦ IEC/EN 60715,With socket,
84873221mounting position | Same as RM35UB3N30 ¦ ,In relation to normal vertical mounting plane,
84873221Minimum distance to adjacent devices | Same as RM35UB3N30 ¦ ,Horizontal,
84873221Minimum distance to adjacent devices | Same as RM35UB3N30 ¦ ,Vertical,
84873221connections - terminals | Same as RM35UB3N30 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873221connections - terminals | Same as RM35UB3N30 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873221connections - terminals | Same as RM35UB3N30 ¦ IEC60947-1,Solid cable (spring terminal),
84873221connections - terminals | Same as RM35UB3N30 ¦ IEC60947-1,Flexible cable (spring terminal),
84873221tightening torque | Same as RM35UB3N30 ¦ IEC60947-1,Tightening torque,
84873221cable stripping length | Same as RM35UB3N30 ¦ ,Cable stripping length,
84873221duty time | Same as RM35UB3N30
84873221
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ ,Generic immunity standard,
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-2,Electrostatic discharge,
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-4,Fast transient / burst,
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-5,Surge,
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-6,Conducted RF disturbance,
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-8,Power frequency magnetic field,
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-29,DC voltage interruption,
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-13,Low frequency harmonics,
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ ,Generic emission standard,
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ Germanisher Lloyd,Conducted emission,
84873221
84873221pollution degree | Same as RM35UB3N30 ¦ IEC60664-1
84873221overvoltage category | Same as RM35UB3N30 ¦ IEC60664-1
84873221circuit group | Same as RM35UB3N30 ¦ ,Supply,Terminal
84873221circuit group | Same as RM35UB3N30 ¦ ,Input 1,
84873221circuit group | Same as RM35UB3N30 ¦ ,Input 2,
84873221circuit group | Same as RM35UB3N30 ¦ ,Input 3,
84873221circuit group | Same as RM35UB3N30 ¦ ,Output 1,
84873221circuit group | Same as RM35UB3N30 ¦ ,Output 2,
84873221 | Same as RM35UB3N30 ¦ ,Supply,Rated
84873221 | Same as RM35UB3N30 ¦ ,Input 1,Voltage
84873221 | Same as RM35UB3N30 ¦ ,Input 2,Spec
84873221 | Same as RM35UB3N30 ¦ ,Input 3,
84873221 | Same as RM35UB3N30 ¦ ,Output 1,
84873221 | Same as RM35UB3N30 ¦ ,Output 2,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 2,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 3,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Output 1,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Output 2,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 2,Isolated
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 3,Circuit
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Output 1,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Output 2,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Output 1 / Output 2,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Output 1,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Output 2,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Output 1,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Output 2,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 3 / Output 1,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 3 / Output 2,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Input 2,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Input 3,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Input 3,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 2,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 3,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Output 1,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Output 2,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 2,Isolated
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 3,Circuit
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Output 1,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Output 2,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Output 1 / Output 2,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Output 1,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Output 2,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Output 1,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Output 2,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 3 / Output 1,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 3 / Output 2,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Input 2,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Input 3,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Input 3,
84873221dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 1,
84873221dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 2,
84873221dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 3,
84873221dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Output 1,
84873221dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Output 2,
84873221dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Output 1 / Output 2,
84873221dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Output 1,
84873221dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Output 2,
84873221dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Output 1,
84873221dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Output 2,
84873221dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 3 / Output 1,
84873221dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 3 / Output 2,
84873221dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Input 2,
84873221dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Input 3,
84873221dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Input 3,
84873221insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 1,
84873221insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 2,
84873221insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 3,
84873221insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Output 1,
84873221insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Output 2,
84873221insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Output 1 / Output 2,
84873221insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Output 1,
84873221insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Output 2,
84873221insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Output 1,
84873221insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Output 2,
84873221insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 3 / Output 1,
84873221insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 3 / Output 2,
84873221insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Input 2,
84873221insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Input 3,
84873221insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Input 3,
84873221
84873221[Us] rated supply voltage | Same as RM35UB3N30
84873221supply voltage limits | Same as RM35UB3N30
84873221polarity | Same as RM35UB3N30
84873221supply frequency | Same as RM35UB3N30
84873221supply frequency | Same as RM35UB3N30
84873221power consumption | Same as RM35UB3N30
84873221immunity to microbreaks | Same as RM35UB3N30
84873221supply terminal | Same as RM35UB3N30
84873221on-load factor | Same as RM35UB3N30
84873221release of input voltage | Same as RM35UB3N30
84873221
84873221monitoring functions | Same as RM35UB3N30 ¦ ,Phase lost ,
84873221monitoring functions | Same as RM35UB3N30 ¦ ,Phase sequence,
84873221monitoring functions | Same as RM35UB3N30 ¦ ,Over / undervoltage (symmetry windows mode),
84873221monitoring functions | Same as RM35UB3N30 ¦ ,Over voltage,
84873221monitoring functions | Same as RM35UB3N30 ¦ ,Undervoltage ,
84873221monitoring functions | Same as RM35UB3N30 ¦ ,Phase asymmetry,
84873221monitoring functions | Same as RM35UB3N30 ¦ ,Disconnection of neutral,
84873221monitoring functions | Same as RM35UB3N30 ¦ ,Voltage Regeneration,
84873221monitoring functions | Same as RM35UB3N30 ¦ ,Extreme undervoltage,
84873221monitoring functions | Same as RM35UB3N30 ¦ ,Extreme overvoltage,
84873221monitoring functions | Same as RM35UB3N30 ¦ ,Extreme asymmetry,
84873221 | Same as RM35UB3N30 ¦ ,Measurement mode,
84873221internal input resistance | Same as RM35UB3N30 ¦ ,Internal input resistance,
84873221input terminal | Same as RM35UB3N30 ¦ ,Input terminal,
84873221Input nominal voltage selection | Same as RM35UB3N30 ¦ ,Input nominal voltage selection,
84873221permissible input overload | Same as RM35UB3N30 ¦ ,permissible input overload,
84873221input frequency | Same as RM35UB3N30 ¦ ,Rated frequency,
84873221input frequency | Same as RM35UB3N30 ¦ ,Frequency operating range,
84873221setting accuracy of the switching threshold | Same as RM35UB3N30 ¦ ,Setting accuracy,
84873221repeat accuracy of the switching threshold | Same as RM35UB3N30 ¦ ,Repeat accuracy (constant parameters),
84873221measurement method | Same as RM35UB3N30 ¦ ,Measurement method,
84873221switching threshold drift | Same as RM35UB3N30 ¦ ,Measurement error with supply voltage variation,
84873221switching threshold drift | Same as RM35UB3N30 ¦ ,Measurement error with temperature variation,
84873221maximum measuring cycle | Same as RM35UB3N30 ¦ ,Maximum measuring cycles,
84873221measurement range | Same as RM35UB3N30 ¦ ,Phase lost ,
84873221measurement range | Same as RM35UB3N30 ¦ ,Phase sequence,
84873221measurement range | Same as RM35UB3N30 ¦ ,Over / undervoltage (symmetry windows mode),
84873221measurement range | Same as RM35UB3N30 ¦ ,Over voltage,
84873221measurement range | Same as RM35UB3N30 ¦ ,Undervoltage ,
84873221measurement range | Same as RM35UB3N30 ¦ ,Phase asymmetry,
84873221measurement range | Same as RM35UB3N30 ¦ ,Disconnection of neutral,
84873221measurement range | Same as RM35UB3N30 ¦ ,Voltage Regeneration,
84873221measurement range | Same as RM35UB3N30 ¦ ,Extreme undervoltage,
84873221measurement range | Same as RM35UB3N30 ¦ ,Extreme Overvoltage,
84873221measurement range | Same as RM35UB3N30 ¦ ,Extreme Asymmetry,
84873221tripping threshold | Same as RM35UB3N30 ¦ ,Phase cut,
84873221tripping threshold | Same as RM35UB3N30 ¦ ,Phase sequence,
84873221tripping threshold | Same as RM35UB3N30 ¦ ,Over / undervoltage (symmetry windows mode),
84873221tripping threshold | Same as RM35UB3N30 ¦ ,Over voltage,
84873221tripping threshold | Same as RM35UB3N30 ¦ ,Undervoltage ,
84873221tripping threshold | Same as RM35UB3N30 ¦ ,Phase asymmetry,
84873221tripping threshold | Same as RM35UB3N30 ¦ ,Disconnection of neutral,
84873221tripping threshold | Same as RM35UB3N30 ¦ ,Voltage Regeneration,
84873221tripping threshold | Same as RM35UB3N30 ¦ ,Extreme undervoltage (Phase loss),
84873221tripping threshold | Same as RM35UB3N30 ¦ ,Extreme Overvoltage,
84873221tripping threshold | Same as RM35UB3N30 ¦ ,Extreme Asymmetry,
84873221hysteresis | Same as RM35UB3N30 ¦ ,Phase cut,
84873221hysteresis | Same as RM35UB3N30 ¦ ,Phase sequence,
84873221hysteresis | Same as RM35UB3N30 ¦ ,Over / undervoltage (symmetry windows mode),
84873221hysteresis | Same as RM35UB3N30 ¦ ,Over voltage,
84873221hysteresis | Same as RM35UB3N30 ¦ ,Undervoltage ,
84873221hysteresis | Same as RM35UB3N30 ¦ ,Phase asymmetry,
84873221hysteresis | Same as RM35UB3N30 ¦ ,Disconnection of neutral,
84873221hysteresis | Same as RM35UB3N30 ¦ ,Voltage Regeneration,
84873221hysteresis | Same as RM35UB3N30 ¦ ,Extreme undervoltage (Phase loss),
84873221hysteresis | Same as RM35UB3N30 ¦ ,Extreme Overvoltage,
84873221hysteresis | Same as RM35UB3N30 ¦ ,Extreme Asymmetry,
84873221 | Same as RM35UB3N30
84873221output type | Same as RM35UB3N30
84873221output terminal | Same as RM35UB3N30
84873221output logic | Same as RM35UB3N30 ¦ ,R1 (11-12-14),
84873221output logic | Same as RM35UB3N30 ¦ ,R2 (21-22-24),
84873221contacts material | Same as RM35UB3N30
84873221mechanical durability | Same as RM35UB3N30 ¦ IEC61810-1
84873221electrical durability | Same as RM35UB3N30 ¦ IEC60947-4-1,AC-1,
84873221electrical durability | Same as RM35UB3N30 ¦ IEC60947-4-1,DC-1,
84873221electrical durability | Same as RM35UB3N30 ¦ IEC60947-5-1,AC-15,
84873221electrical durability | Same as RM35UB3N30 ¦ IEC60947-5-1,DC-13,
84873221[Ue] rated operational voltage | Same as RM35UB3N30 ¦ IEC61810-1,Rated switching voltage,
84873221[Ie] rated operational current | Same as RM35UB3N30 ¦ IEC61810-1,Rated switching current,
84873221maximum switching capacity | Same as RM35UB3N30 ¦ ,Maximum switching voltage,
84873221maximum switching capacity | Same as RM35UB3N30 ¦ ,Maximum switching current,
84873221maximum switching capacity | Same as RM35UB3N30 ¦ ,Maximum switching capacity,
84873221minimum switching capacity | Same as RM35UB3N30 ¦ IEC60947-5-4,Minimum switching voltage,
84873221minimum switching capacity | Same as RM35UB3N30 ¦ IEC60947-5-4,Minimum switching current,
84873221minimum switching capacity | Same as RM35UB3N30 ¦ IEC60947-5-4,Minimum switching capacity,
84873221maximum voltage drop | Same as RM35UB3N30 ¦ IEC62314,Only for solid state output,
84873221maximum leakage current | Same as RM35UB3N30 ¦ IEC62314,Only for solid state output,
84873221thermal current | Same as RM35UB3N30 ¦ IEC60947-5-1
84873221short circuit protection | Same as RM35UB3N30 ¦ IEC60947-5-1,Relay Output by external fuse,
84873221short circuit protection | Same as RM35UB3N30 ¦ IEC62314,Solid State Output by external fuse,
84873221
84873221time delay type | Same as RM35UB3N30 ¦ ,"OFF" delay,
84873221time delay type | Same as RM35UB3N30 ¦ ,"ON" delay,
84873221time delay type | Same as RM35UB3N30 ¦ ,Inhibition,
84873221time delay range | Same as RM35UB3N30 ¦ ,"OFF" delay,
84873221time delay range | Same as RM35UB3N30 ¦ ,"ON" delay,
84873221time delay range | Same as RM35UB3N30 ¦ ,Inhibition,
84873221response time | Same as RM35UB3N30 ¦ ,on crossing the threshold,
84873221response time | Same as RM35UB3N30
84873221response time | Same as RM35UB3N30
84873221response time | Same as RM35UB3N30
84873221response time | Same as RM35UB3N30
84873221power on delay | Same as RM35UB3N30
84873221reset time | Same as RM35UB3N30 ¦ ,through Un power reset,
84873221reset time | Same as RM35UB3N30 ¦ ,through front panel reset,
84873221reset time | Same as RM35UB3N30 ¦ ,through input control reset,
84873221setting accuracy of time delay | Same as RM35UB3N30
84873221repeat accuracy of time delay | Same as RM35UB3N30
84873221time delay drift | Same as RM35UB3N30
84873221time delay drift | Same as RM35UB3N30
84873221
84873221status LED | Same as RM35UB3N30
84873221local signalling | Same as RM35UB3N30 ¦ ,Power supply availability,
84873221local signalling | Same as RM35UB3N30 ¦ ,Power supply not availability,
84873221local signalling | Same as RM35UB3N30 ¦ ,Timing in-progress,
84873221local signalling | Same as RM35UB3N30 ¦ ,Output is energized,
84873221local signalling | Same as RM35UB3N30 ¦ ,Output is de-energized,
84873221local signalling | Same as RM35UB3N30 ¦ ,Range Setting Changes,
84873221local signalling | Same as RM35UB3N30 ¦ ,Phase Cut,
84873221local signalling | Same as RM35UB3N30 ¦ ,Phase Sequence Swap,
84873221local signalling | Same as RM35UB3N30 ¦ ,Undervoltage <U,
84873221local signalling | Same as RM35UB3N30 ¦ ,Overvoltage >U,
84873221local signalling | Same as RM35UB3N30 ¦ ,Phase Asymmetry,
84873221local signalling | Same as RM35UB3N30 ¦ ,Voltage Regeneration,
84873221local signalling | Same as RM35UB3N30 ¦ ,Extreme Undervoltage <U (Phase loss),
84873221local signalling | Same as RM35UB3N30 ¦ ,Extreme Overvoltage >U,
84873221local signalling | Same as RM35UB3N30 ¦ ,Extreme Phase Asymmetry,
84873221
84873221 | Same as RM35UB3N30
84873221 | Same as RM35UB3N30
84873221diagnostic button | Same as RM35UB3N30
84873221 | Same as RM35UB3N30
84873221 | Same as RM35UB3N30
84873221
84873221safety reliability data | Same as RM35UB3N30 ¦ ,MTTF,
84873221safety reliability data | Same as RM35UB3N30 ¦ ,B10,
84873221 | Same as RM35UB3N30 ¦ ,MTTFd,
84873221 | Same as RM35UB3N30 ¦ ,B10d,
84873221
84873221 | Drawing / Diagram
84873895
84873895standards | Same as RM35UB3N30
84873895product certifications | UL, CSA, CE, China ROHS
84873895marking | UL, CSA, CE, China ROHS
84873895directives | Same as RM35UB3N30
84873895directives | Same as RM35UB3N30
84873895directives | Same as RM35UB3N30
84873895
84873895 | Same as RM35UB3N30 ¦ IEC60721-3-3,Climatic category,
84873895 | Same as RM35UB3N30 ¦ Germanisher Lloyd,Environmental category,
84873895ambient air temperature for storage | Same as RM35UB3N30 ¦ ,Storage,
84873895ambient air temperature for operation | Same as RM35UB3N30 ¦ ,Operation,
84873895relative humidity | Same as RM35UB3N30 ¦ IEC60068-2-30,Damp heat,XX
84873895 | Same as RM35UB3N30 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873895vibration resistance | Same as RM35UB3N30 ¦ IEC60068-2-6
84873895shock resistance | Same as RM35UB3N30 ¦ IEC60068-2-27
84873895bump resistance | Same as RM35UB3N30 ¦ IEC60068-2-29
84873895seismic resistance | Same as RM35UB3N30 ¦ IEC60068-3-3
84873895IP degree of protection | Same as RM35UB3N30 ¦ IEC60529,Terminal Block,
84873895IP degree of protection | Same as RM35UB3N30 ¦ IEC60529,Housing,
84873895IP degree of protection | Same as RM35UB3N30 ¦ IEC60529,Front Panel,
84873895
84873895width | Same as RM35UB3N30 ¦ ,Width,
84873895height | Same as RM35UB3N30 ¦ ,Height,
84873895depth | Same as RM35UB3N30 ¦ ,Depth,
84873895net weight | Same as RM35UB3N30
84873895mounting support | Same as RM35UB3N30 ¦ IEC/EN 60715,Without socket,
84873895mounting support | Same as RM35UB3N30 ¦ IEC/EN 60715,With socket,
84873895mounting position | Same as RM35UB3N30 ¦ ,In relation to normal vertical mounting plane,
84873895Minimum distance to adjacent devices | Same as RM35UB3N30 ¦ ,Horizontal,
84873895Minimum distance to adjacent devices | Same as RM35UB3N30 ¦ ,Vertical,
84873895connections - terminals | Same as RM35UB3N30 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873895connections - terminals | Same as RM35UB3N30 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873895connections - terminals | Same as RM35UB3N30 ¦ IEC60947-1,Solid cable (spring terminal),
84873895connections - terminals | Same as RM35UB3N30 ¦ IEC60947-1,Flexible cable (spring terminal),
84873895tightening torque | Same as RM35UB3N30 ¦ IEC60947-1,Tightening torque,
84873895cable stripping length | Same as RM35UB3N30 ¦ ,Cable stripping length,
84873895duty time | Same as RM35UB3N30
84873895
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ ,Generic immunity standard,
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-2,Electrostatic discharge,
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-4,Fast transient / burst,
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-5,Surge,
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-6,Conducted RF disturbance,
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-8,Power frequency magnetic field,
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-29,DC voltage interruption,
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ IEC61000-4-13,Low frequency harmonics,
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ ,Generic emission standard,
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ Germanisher Lloyd,Conducted emission,
84873895
84873895pollution degree | Same as RM35UB3N30 ¦ IEC60664-1
84873895overvoltage category | Same as RM35UB3N30 ¦ IEC60664-1
84873895circuit group | Same as RM35UB3N30 ¦ ,Supply,Terminal
84873895circuit group | Same as RM35UB3N30 ¦ ,Input 1,
84873895circuit group | Same as RM35UB3N30 ¦ ,Input 2,
84873895circuit group | Same as RM35UB3N30 ¦ ,Input 3,
84873895circuit group | Same as RM35UB3N30 ¦ ,Output 1,
84873895circuit group | Same as RM35UB3N30 ¦ ,Output 2,
84873895 | Same as RM35UB3N30 ¦ ,Supply,Rated
84873895 | Same as RM35UB3N30 ¦ ,Input 1,Voltage
84873895 | Same as RM35UB3N30 ¦ ,Input 2,Spec
84873895 | Same as RM35UB3N30 ¦ ,Input 3,
84873895 | Same as RM35UB3N30 ¦ ,Output 1,
84873895 | Same as RM35UB3N30 ¦ ,Output 2,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 2,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 3,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Output 1,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Output 2,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 2,Isolated
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 3,Circuit
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Output 1,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Output 2,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Output 1 / Output 2,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Output 1,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Output 2,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Output 1,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Output 2,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 3 / Output 1,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 3 / Output 2,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Input 2,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Input 3,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Input 3,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 2,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 3,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Output 1,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Output 2,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 2,Isolated
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 3,Circuit
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Output 1,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply / Output 2,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Output 1 / Output 2,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Output 1,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Output 2,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Output 1,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Output 2,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 3 / Output 1,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 3 / Output 2,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Input 2,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Input 3,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Input 3,
84873895dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 1,
84873895dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 2,
84873895dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 3,
84873895dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Output 1,
84873895dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Output 2,
84873895dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Output 1 / Output 2,
84873895dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Output 1,
84873895dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Output 2,
84873895dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Output 1,
84873895dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Output 2,
84873895dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 3 / Output 1,
84873895dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 3 / Output 2,
84873895dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Input 2,
84873895dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Input 3,
84873895dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Input 3,
84873895insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 1,
84873895insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 2,
84873895insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 3,
84873895insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Output 1,
84873895insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Output 2,
84873895insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Output 1 / Output 2,
84873895insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Output 1,
84873895insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Output 2,
84873895insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Output 1,
84873895insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Output 2,
84873895insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 3 / Output 1,
84873895insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 3 / Output 2,
84873895insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Input 2,
84873895insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Input 3,
84873895insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Input 3,
84873895
84873895[Us] rated supply voltage | Same as RM35UB3N30
84873895supply voltage limits | Same as RM35UB3N30
84873895polarity | Same as RM35UB3N30
84873895supply frequency | Same as RM35UB3N30
84873895supply frequency | Same as RM35UB3N30
84873895power consumption | Same as RM35UB3N30
84873895immunity to microbreaks | Same as RM35UB3N30
84873895supply terminal | Same as RM35UB3N30
84873895on-load factor | Same as RM35UB3N30
84873895release of input voltage | Same as RM35UB3N30
84873895
84873895monitoring functions | Same as RM35UB3N30 ¦ ,Phase lost ,
84873895monitoring functions | Same as RM35UB3N30 ¦ ,Phase sequence,
84873895monitoring functions | Same as RM35UB3N30 ¦ ,Over / undervoltage (symmetry windows mode),
84873895monitoring functions | Same as RM35UB3N30 ¦ ,Over voltage,
84873895monitoring functions | Same as RM35UB3N30 ¦ ,Undervoltage ,
84873895monitoring functions | Same as RM35UB3N30 ¦ ,Phase asymmetry,
84873895monitoring functions | Same as RM35UB3N30 ¦ ,Disconnection of neutral,
84873895monitoring functions | Same as RM35UB3N30 ¦ ,Voltage Regeneration,
84873895monitoring functions | Same as RM35UB3N30 ¦ ,Extreme undervoltage,
84873895monitoring functions | Same as RM35UB3N30 ¦ ,Extreme overvoltage,
84873895monitoring functions | Same as RM35UB3N30 ¦ ,Extreme asymmetry,
84873895 | Same as RM35UB3N30 ¦ ,Measurement mode,
84873895internal input resistance | Same as RM35UB3N30 ¦ ,Internal input resistance,
84873895input terminal | Same as RM35UB3N30 ¦ ,Input terminal,
84873895Input nominal voltage selection | Same as RM35UB3N30 ¦ ,Input nominal voltage selection,
84873895permissible input overload | Same as RM35UB3N30 ¦ ,permissible input overload,
84873895input frequency | Same as RM35UB3N30 ¦ ,Rated frequency,
84873895input frequency | Same as RM35UB3N30 ¦ ,Frequency operating range,
84873895setting accuracy of the switching threshold | Same as RM35UB3N30 ¦ ,Setting accuracy,
84873895repeat accuracy of the switching threshold | Same as RM35UB3N30 ¦ ,Repeat accuracy (constant parameters),
84873895measurement method | Same as RM35UB3N30 ¦ ,Measurement method,
84873895switching threshold drift | Same as RM35UB3N30 ¦ ,Measurement error with supply voltage variation,
84873895switching threshold drift | Same as RM35UB3N30 ¦ ,Measurement error with temperature variation,
84873895maximum measuring cycle | Same as RM35UB3N30 ¦ ,Maximum measuring cycles,
84873895measurement range | Same as RM35UB3N30 ¦ ,Phase lost ,
84873895measurement range | Same as RM35UB3N30 ¦ ,Phase sequence,
84873895measurement range | Same as RM35UB3N30 ¦ ,Over / undervoltage (symmetry windows mode),
84873895measurement range | Same as RM35UB3N30 ¦ ,Over voltage,
84873895measurement range | Same as RM35UB3N30 ¦ ,Undervoltage ,
84873895measurement range | Same as RM35UB3N30 ¦ ,Phase asymmetry,
84873895measurement range | Same as RM35UB3N30 ¦ ,Disconnection of neutral,
84873895measurement range | Same as RM35UB3N30 ¦ ,Voltage Regeneration,
84873895measurement range | Same as RM35UB3N30 ¦ ,Extreme undervoltage,
84873895measurement range | Same as RM35UB3N30 ¦ ,Extreme Overvoltage,
84873895measurement range | Same as RM35UB3N30 ¦ ,Extreme Asymmetry,
84873895tripping threshold | Same as RM35UB3N30 ¦ ,Phase cut,
84873895tripping threshold | Same as RM35UB3N30 ¦ ,Phase sequence,
84873895tripping threshold | Same as RM35UB3N30 ¦ ,Over / undervoltage (symmetry windows mode),
84873895tripping threshold | Same as RM35UB3N30 ¦ ,Over voltage,
84873895tripping threshold | Same as RM35UB3N30 ¦ ,Undervoltage ,
84873895tripping threshold | Same as RM35UB3N30 ¦ ,Phase asymmetry,
84873895tripping threshold | Same as RM35UB3N30 ¦ ,Disconnection of neutral,
84873895tripping threshold | Same as RM35UB3N30 ¦ ,Voltage Regeneration,
84873895tripping threshold | Same as RM35UB3N30 ¦ ,Extreme undervoltage (Phase loss),
84873895tripping threshold | Same as RM35UB3N30 ¦ ,Extreme Overvoltage,
84873895tripping threshold | Same as RM35UB3N30 ¦ ,Extreme Asymmetry,
84873895hysteresis | Same as RM35UB3N30 ¦ ,Phase cut,
84873895hysteresis | Same as RM35UB3N30 ¦ ,Phase sequence,
84873895hysteresis | Same as RM35UB3N30 ¦ ,Over / undervoltage (symmetry windows mode),
84873895hysteresis | Same as RM35UB3N30 ¦ ,Over voltage,
84873895hysteresis | Same as RM35UB3N30 ¦ ,Undervoltage ,
84873895hysteresis | Same as RM35UB3N30 ¦ ,Phase asymmetry,
84873895hysteresis | Same as RM35UB3N30 ¦ ,Disconnection of neutral,
84873895hysteresis | Same as RM35UB3N30 ¦ ,Voltage Regeneration,
84873895hysteresis | Same as RM35UB3N30 ¦ ,Extreme undervoltage (Phase loss),
84873895hysteresis | Same as RM35UB3N30 ¦ ,Extreme Overvoltage,
84873895hysteresis | Same as RM35UB3N30 ¦ ,Extreme Asymmetry,
84873895 | Same as RM35UB3N30
84873895output type | Same as RM35UB3N30
84873895output terminal | Same as RM35UB3N30
84873895output logic | Same as RM35UB3N30 ¦ ,R1 (11-12-14),
84873895output logic | Same as RM35UB3N30 ¦ ,R2 (21-22-24),
84873895contacts material | Same as RM35UB3N30
84873895mechanical durability | Same as RM35UB3N30 ¦ IEC61810-1
84873895electrical durability | Same as RM35UB3N30 ¦ IEC60947-4-1,AC-1,
84873895electrical durability | Same as RM35UB3N30 ¦ IEC60947-4-1,DC-1,
84873895electrical durability | Same as RM35UB3N30 ¦ IEC60947-5-1,AC-15,
84873895electrical durability | Same as RM35UB3N30 ¦ IEC60947-5-1,DC-13,
84873895[Ue] rated operational voltage | Same as RM35UB3N30 ¦ IEC61810-1,Rated switching voltage,
84873895[Ie] rated operational current | Same as RM35UB3N30 ¦ IEC61810-1,Rated switching current,
84873895maximum switching capacity | Same as RM35UB3N30 ¦ ,Maximum switching voltage,
84873895maximum switching capacity | Same as RM35UB3N30 ¦ ,Maximum switching current,
84873895maximum switching capacity | Same as RM35UB3N30 ¦ ,Maximum switching capacity,
84873895minimum switching capacity | Same as RM35UB3N30 ¦ IEC60947-5-4,Minimum switching voltage,
84873895minimum switching capacity | Same as RM35UB3N30 ¦ IEC60947-5-4,Minimum switching current,
84873895minimum switching capacity | Same as RM35UB3N30 ¦ IEC60947-5-4,Minimum switching capacity,
84873895maximum voltage drop | Same as RM35UB3N30 ¦ IEC62314,Only for solid state output,
84873895maximum leakage current | Same as RM35UB3N30 ¦ IEC62314,Only for solid state output,
84873895thermal current | Same as RM35UB3N30 ¦ IEC60947-5-1
84873895short circuit protection | Same as RM35UB3N30 ¦ IEC60947-5-1,Relay Output by external fuse,
84873895short circuit protection | Same as RM35UB3N30 ¦ IEC62314,Solid State Output by external fuse,
84873895
84873895time delay type | Same as RM35UB3N30 ¦ ,"OFF" delay,
84873895time delay type | Same as RM35UB3N30 ¦ ,"ON" delay,
84873895time delay type | Same as RM35UB3N30 ¦ ,Inhibition,
84873895time delay range | Same as RM35UB3N30 ¦ ,"OFF" delay,
84873895time delay range | Same as RM35UB3N30 ¦ ,"ON" delay,
84873895time delay range | Same as RM35UB3N30 ¦ ,Inhibition,
84873895response time | Same as RM35UB3N30 ¦ ,on crossing the threshold,
84873895response time | Same as RM35UB3N30
84873895response time | Same as RM35UB3N30
84873895response time | Same as RM35UB3N30
84873895response time | Same as RM35UB3N30
84873895power on delay | Same as RM35UB3N30
84873895reset time | Same as RM35UB3N30 ¦ ,through Un power reset,
84873895reset time | Same as RM35UB3N30 ¦ ,through front panel reset,
84873895reset time | Same as RM35UB3N30 ¦ ,through input control reset,
84873895setting accuracy of time delay | Same as RM35UB3N30
84873895repeat accuracy of time delay | Same as RM35UB3N30
84873895time delay drift | Same as RM35UB3N30
84873895time delay drift | Same as RM35UB3N30
84873895
84873895status LED | Same as RM35UB3N30
84873895local signalling | Same as RM35UB3N30 ¦ ,Power supply availability,
84873895local signalling | Same as RM35UB3N30 ¦ ,Power supply not availability,
84873895local signalling | Same as RM35UB3N30 ¦ ,Timing in-progress,
84873895local signalling | Same as RM35UB3N30 ¦ ,Output is energized,
84873895local signalling | Same as RM35UB3N30 ¦ ,Output is de-energized,
84873895local signalling | Same as RM35UB3N30 ¦ ,Range Setting Changes,
84873895local signalling | Same as RM35UB3N30 ¦ ,Phase Cut,
84873895local signalling | Same as RM35UB3N30 ¦ ,Phase Sequence Swap,
84873895local signalling | Same as RM35UB3N30 ¦ ,Undervoltage <U,
84873895local signalling | Same as RM35UB3N30 ¦ ,Overvoltage >U,
84873895local signalling | Same as RM35UB3N30 ¦ ,Phase Asymmetry,
84873895local signalling | Same as RM35UB3N30 ¦ ,Voltage Regeneration,
84873895local signalling | Same as RM35UB3N30 ¦ ,Extreme Undervoltage <U (Phase loss),
84873895local signalling | Same as RM35UB3N30 ¦ ,Extreme Overvoltage >U,
84873895local signalling | Same as RM35UB3N30 ¦ ,Extreme Phase Asymmetry,
84873895
84873895 | Same as RM35UB3N30
84873895 | Same as RM35UB3N30
84873895diagnostic button | Same as RM35UB3N30
84873895 | Same as RM35UB3N30
84873895 | Same as RM35UB3N30
84873895
84873895safety reliability data | Same as RM35UB3N30 ¦ ,MTTF,
84873895safety reliability data | Same as RM35UB3N30 ¦ ,B10,
84873895 | Same as RM35UB3N30 ¦ ,MTTFd,
84873895 | Same as RM35UB3N30 ¦ ,B10d,
84873895
84873895 | Drawing / Diagram
RM17UB310
RM17UB310standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM17UB310product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17UB310marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17UB310directives | 2014/35/EU
RM17UB310directives | 2014/30/EU
RM17UB310directives | 2011/65/EU
RM17UB310
RM17UB310 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM17UB310 | Class C ¦ Germanisher Lloyd,Environmental category,
RM17UB310ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM17UB310ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM17UB310relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM17UB310 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM17UB310vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM17UB310shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM17UB310bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM17UB310seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM17UB310IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM17UB310IP degree of protection | IP30 ¦ IEC60529,Housing,
RM17UB310IP degree of protection | - ¦ IEC60529,Front Panel,
RM17UB310
RM17UB310width | 17.5 ¦ ,Width,
RM17UB310height | 90 ¦ ,Height,
RM17UB310depth | 72 ¦ ,Depth,
RM17UB310net weight | 80
RM17UB310mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM17UB310mounting support | - ¦ IEC/EN 60715,With socket,
RM17UB310mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM17UB310Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM17UB310Minimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM17UB310connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM17UB310connections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM17UB310connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM17UB310connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM17UB310tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM17UB310cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM17UB310duty time | 1
RM17UB310
RM17UB310electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM17UB310electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM17UB310electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM17UB310electromagnetic compatibility | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM17UB310electromagnetic compatibility | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge,
RM17UB310electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM17UB310electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM17UB310electromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM17UB310electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM17UB310electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM17UB310electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM17UB310electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM17UB310electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM17UB310electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM17UB310electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM17UB310electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM17UB310electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM17UB310electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM17UB310electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM17UB310
RM17UB310pollution degree | 3 ¦ IEC60664-1
RM17UB310overvoltage category | 3 ¦ IEC60664-1
RM17UB310circuit group | L1, L2, L3 ¦ ,Supply,Terminal
RM17UB310circuit group | - ¦ ,Input 1,
RM17UB310circuit group | - ¦ ,Input 2,
RM17UB310circuit group | - ¦ ,Input 3,
RM17UB310circuit group | 11,12,14 ¦ ,Output 1,
RM17UB310circuit group | - ¦ ,Output 2,
RM17UB310 | 208..480 AC ¦ ,Supply,Rated
RM17UB310 | - ¦ ,Input 1,Voltage
RM17UB310 | - ¦ ,Input 2,Spec
RM17UB310 | - ¦ ,Input 3,
RM17UB310 | 250V ¦ ,Output 1,
RM17UB310 | - ¦ ,Output 2,
RM17UB310[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply,
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM17UB310[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Output 2,
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM17UB310[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Output 1,
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Output 2,
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Output 1 / Output 2,
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM17UB310[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM17UB310[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM17UB310[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Output 2,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1 / Output 2,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM17UB310[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM17UB310dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM17UB310dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM17UB310dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM17UB310dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM17UB310dielectric strength | - ¦ IEC60255-27,Supply / Output 2,
RM17UB310dielectric strength | - ¦ IEC60255-27,Output 1 / Output 2,
RM17UB310dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM17UB310dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM17UB310dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM17UB310dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM17UB310dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM17UB310dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM17UB310dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM17UB310dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM17UB310dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM17UB310insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM17UB310insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM17UB310insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM17UB310insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM17UB310insulation resistance | - ¦ IEC60255-27,Supply / Output 2,
RM17UB310insulation resistance | - ¦ IEC60255-27,Output 1 / Output 2,
RM17UB310insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM17UB310insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM17UB310insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM17UB310insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM17UB310insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM17UB310insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM17UB310insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM17UB310insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM17UB310insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM17UB310
RM17UB310[Us] rated supply voltage | ~ 3 x 208…3 x 480
RM17UB310supply voltage limits | ~ 3 x 183…3 x 528
RM17UB310polarity | -
RM17UB310supply frequency | 50 / 60
RM17UB310supply frequency | 45…66
RM17UB310power consumption | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz
RM17UB310immunity to microbreaks | 0
RM17UB310supply terminal | L1-L3
RM17UB310on-load factor | 1
RM17UB310release of input voltage | -
RM17UB310
RM17UB310monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost ,
RM17UB310monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence,
RM17UB310monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17UB310monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Over voltage,
RM17UB310monitoring functions | governed by time delay, status reflects to both R1 & R2 ¦ ,Undervoltage ,
RM17UB310monitoring functions | - ¦ ,Phase asymmetry,
RM17UB310monitoring functions | - ¦ ,Disconnection of neutral,
RM17UB310monitoring functions | - ¦ ,Voltage Regeneration,
RM17UB310monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage,
RM17UB310monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage,
RM17UB310monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM17UB310 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM17UB310internal input resistance | - ¦ ,Internal input resistance,
RM17UB310input terminal | L1-L2-L3 ¦ ,Input terminal,
RM17UB310Input nominal voltage selection | 208, 220, 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM17UB310permissible input overload | - ¦ ,permissible input overload,
RM17UB310input frequency | 50 / 60 ¦ ,Rated frequency,
RM17UB310input frequency | 45…66 ¦ ,Frequency operating range,
RM17UB310setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM17UB310repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM17UB310measurement method | True RMS ¦ ,Measurement method,
RM17UB310switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation,
RM17UB310switching threshold drift | < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM17UB310maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM17UB310measurement range | - ¦ ,Phase lost ,
RM17UB310measurement range | - ¦ ,Phase sequence,
RM17UB310measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17UB310measurement range | +2…+20 % in the ranges 3 x ~ 208…440 +2…+10 % in the range 3 x ~ 480 ¦ ,Over voltage,
RM17UB310measurement range | -2…-20 % in the ranges 3 x ~ 380…480 -2…-12 % in the range 3 x ~ 208 -2…-17 % in the range 3 x ~ 220 ¦ ,Undervoltage ,
RM17UB310measurement range | - ¦ ,Phase asymmetry,
RM17UB310measurement range | - ¦ ,Disconnection of neutral,
RM17UB310measurement range | - ¦ ,Voltage Regeneration,
RM17UB310measurement range | - ¦ ,Extreme undervoltage,
RM17UB310measurement range | - ¦ ,Extreme Overvoltage,
RM17UB310measurement range | - ¦ ,Extreme Asymmetry,
RM17UB310tripping threshold | 1 or more phase cut ¦ ,Phase cut,
RM17UB310tripping threshold | Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence,
RM17UB310tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17UB310tripping threshold | Adjustable 2%...20% of selected Un ¦ ,Over voltage,
RM17UB310tripping threshold | Adjustable 2%...20% of selected Un ¦ ,Undervoltage ,
RM17UB310tripping threshold | - ¦ ,Phase asymmetry,
RM17UB310tripping threshold | - ¦ ,Disconnection of neutral,
RM17UB310tripping threshold | - ¦ ,Voltage Regeneration,
RM17UB310tripping threshold | 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM17UB310tripping threshold | Internal design spec: 543V +/- 5% ¦ ,Extreme Overvoltage,
RM17UB310tripping threshold | Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM17UB310hysteresis | All phase cut recover ¦ ,Phase cut,
RM17UB310hysteresis | Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence,
RM17UB310hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM17UB310hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Over voltage,
RM17UB310hysteresis | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage ,
RM17UB310hysteresis | - ¦ ,Phase asymmetry,
RM17UB310hysteresis | - ¦ ,Disconnection of neutral,
RM17UB310hysteresis | - ¦ ,Voltage Regeneration,
RM17UB310hysteresis | All phases > 195V Internal design spec: All phases >180V +/- 5% ¦ ,Extreme undervoltage (Phase loss),
RM17UB310hysteresis | Internal design spec: All phases <533V +/- 5% ¦ ,Extreme Overvoltage,
RM17UB310hysteresis | - ¦ ,Extreme Asymmetry,
RM17UB310
RM17UB310output type | 1 x C/O relay contacts
RM17UB310output terminal | 11-12-14
RM17UB310output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM17UB310output logic | - ¦ ,R2 (21-22-24),
RM17UB310contacts material | Cadmium free
RM17UB310mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM17UB310electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM17UB310electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM17UB310electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM17UB310electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM17UB310[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM17UB310[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM17UB310maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM17UB310maximum switching capacity | 5A ¦ ,Maximum switching current,
RM17UB310maximum switching capacity | - ¦ ,Maximum switching capacity,
RM17UB310minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM17UB310minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM17UB310minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM17UB310maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM17UB310maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM17UB310thermal current | 5A ¦ IEC60947-5-1
RM17UB310short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse,
RM17UB310short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM17UB310
RM17UB310time delay type | Yes ¦ ,"OFF" delay,
RM17UB310time delay type | - ¦ ,"ON" delay,
RM17UB310time delay type | - ¦ ,Inhibition,
RM17UB310time delay range | Adjustable 0.1…30 ¦ ,"OFF" delay,
RM17UB310time delay range | - ¦ ,"ON" delay,
RM17UB310time delay range | - ¦ ,Inhibition,
RM17UB310response time | 0
RM17UB310response time | -
RM17UB310response time | -
RM17UB310response time | -
RM17UB310response time | -
RM17UB310power on delay | 0
RM17UB310reset time | 0
RM17UB310reset time | - ¦ ,through front panel reset,
RM17UB310reset time | - ¦ ,through input control reset,
RM17UB310setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM17UB310repeat accuracy of time delay | +/- 3%
RM17UB310time delay drift | -
RM17UB310time delay drift | -
RM17UB310
RM17UB310status LED | Un (Green) R (Amber)
RM17UB310local signalling | Un - ON ¦ ,Power supply availability,
RM17UB310local signalling | Un - OFF ¦ ,Power supply not availability,
RM17UB310local signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM17UB310local signalling | R - ON ¦ ,Output is energized,
RM17UB310local signalling | R - OFF ¦ ,Output is de-energized,
RM17UB310local signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM17UB310local signalling | - ¦ ,Phase Cut,
RM17UB310local signalling | - ¦ ,Phase Sequence Swap,
RM17UB310local signalling | - ¦ ,Undervoltage <U,
RM17UB310local signalling | - ¦ ,Overvoltage >U,
RM17UB310local signalling | - ¦ ,Phase Asymmetry,
RM17UB310local signalling | - ¦ ,Voltage Regeneration,
RM17UB310local signalling | - ¦ ,Extreme Undervoltage <U (Phase loss),
RM17UB310local signalling | - ¦ ,Extreme Overvoltage >U,
RM17UB310local signalling | - ¦ ,Extreme Phase Asymmetry,
RM17UB310
RM17UB310 | Yes
RM17UB310 | -
RM17UB310diagnostic button | -
RM17UB310 | -
RM17UB310 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM17UB310
RM17UB310safety reliability data | 4,400,000 hours ¦ ,MTTF,
RM17UB310safety reliability data | 470,000 hours ¦ ,B10,
RM17UB310 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM17UB310 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM17UB310
RM17UB310 | Drawing / Diagram
84873222
84873222standards | Same as RM17UB310
84873222product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873222marking | UL, CSA, GL, CCC, CE, China ROHS
84873222directives | Same as RM17UB310
84873222directives | Same as RM17UB310
84873222directives | Same as RM17UB310
84873222
84873222 | Same as RM17UB310 ¦ IEC60721-3-3,Climatic category,
84873222 | Same as RM17UB310 ¦ Germanisher Lloyd,Environmental category,
84873222ambient air temperature for storage | Same as RM17UB310 ¦ ,Storage,
84873222ambient air temperature for operation | Same as RM17UB310 ¦ ,Operation,
84873222relative humidity | Same as RM17UB310 ¦ IEC60068-2-30,Damp heat,XX
84873222 | Same as RM17UB310 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873222vibration resistance | Same as RM17UB310 ¦ IEC60068-2-6
84873222shock resistance | Same as RM17UB310 ¦ IEC60068-2-27
84873222bump resistance | Same as RM17UB310 ¦ IEC60068-2-29
84873222seismic resistance | Same as RM17UB310 ¦ IEC60068-3-3
84873222IP degree of protection | Same as RM17UB310 ¦ IEC60529,Terminal Block,
84873222IP degree of protection | Same as RM17UB310 ¦ IEC60529,Housing,
84873222IP degree of protection | Same as RM17UB310 ¦ IEC60529,Front Panel,
84873222
84873222width | Same as RM17UB310 ¦ ,Width,
84873222height | Same as RM17UB310 ¦ ,Height,
84873222depth | Same as RM17UB310 ¦ ,Depth,
84873222net weight | Same as RM17UB310
84873222mounting support | Same as RM17UB310 ¦ IEC/EN 60715,Without socket,
84873222mounting support | Same as RM17UB310 ¦ IEC/EN 60715,With socket,
84873222mounting position | Same as RM17UB310 ¦ ,In relation to normal vertical mounting plane,
84873222Minimum distance to adjacent devices | Same as RM17UB310 ¦ ,Horizontal,
84873222Minimum distance to adjacent devices | Same as RM17UB310 ¦ ,Vertical,
84873222connections - terminals | Same as RM17UB310 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873222connections - terminals | Same as RM17UB310 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873222connections - terminals | Same as RM17UB310 ¦ IEC60947-1,Solid cable (spring terminal),
84873222connections - terminals | Same as RM17UB310 ¦ IEC60947-1,Flexible cable (spring terminal),
84873222tightening torque | Same as RM17UB310 ¦ IEC60947-1,Tightening torque,
84873222cable stripping length | Same as RM17UB310 ¦ ,Cable stripping length,
84873222duty time | Same as RM17UB310
84873222
84873222electromagnetic compatibility | Same as RM17UB310 ¦ ,Generic immunity standard,
84873222electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-2,Electrostatic discharge,
84873222electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873222electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-4,Fast transient / burst,
84873222electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-5,Surge,
84873222electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-6,Conducted RF disturbance,
84873222electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-8,Power frequency magnetic field,
84873222electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873222electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873222electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-29,DC voltage interruption,
84873222electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-13,Low frequency harmonics,
84873222electromagnetic compatibility | Same as RM17UB310 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873222electromagnetic compatibility | Same as RM17UB310 ¦ ,Generic emission standard,
84873222electromagnetic compatibility | Same as RM17UB310 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873222electromagnetic compatibility | Same as RM17UB310 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873222electromagnetic compatibility | Same as RM17UB310 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873222electromagnetic compatibility | Same as RM17UB310 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873222electromagnetic compatibility | Same as RM17UB310 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873222electromagnetic compatibility | Same as RM17UB310 ¦ Germanisher Lloyd,Conducted emission,
84873222
84873222pollution degree | Same as RM17UB310 ¦ IEC60664-1
84873222overvoltage category | Same as RM17UB310 ¦ IEC60664-1
84873222circuit group | Same as RM17UB310 ¦ ,Supply,Terminal
84873222circuit group | Same as RM17UB310 ¦ ,Input 1,
84873222circuit group | Same as RM17UB310 ¦ ,Input 2,
84873222circuit group | Same as RM17UB310 ¦ ,Input 3,
84873222circuit group | Same as RM17UB310 ¦ ,Output 1,
84873222circuit group | Same as RM17UB310 ¦ ,Output 2,
84873222 | Same as RM17UB310 ¦ ,Supply,Rated
84873222 | Same as RM17UB310 ¦ ,Input 1,Voltage
84873222 | Same as RM17UB310 ¦ ,Input 2,Spec
84873222 | Same as RM17UB310 ¦ ,Input 3,
84873222 | Same as RM17UB310 ¦ ,Output 1,
84873222 | Same as RM17UB310 ¦ ,Output 2,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Supply,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 2,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 3,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Output 1,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Output 2,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Input 2,Isolated
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Input 3,Circuit
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Output 1,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Output 2,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Output 1 / Output 2,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1 / Output 1,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1 / Output 2,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 2 / Output 1,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 2 / Output 2,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 3 / Output 1,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 3 / Output 2,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1 / Input 2,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 2 / Input 3,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1 / Input 3,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Supply,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 2,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 3,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Output 1,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Output 2,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Input 2,Isolated
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Input 3,Circuit
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Output 1,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Output 2,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Output 1 / Output 2,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1 / Output 1,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1 / Output 2,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 2 / Output 1,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 2 / Output 2,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 3 / Output 1,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 3 / Output 2,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1 / Input 2,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 2 / Input 3,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1 / Input 3,
84873222dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Supply / Input 1,
84873222dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Supply / Input 2,
84873222dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Supply / Input 3,
84873222dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Supply / Output 1,
84873222dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Supply / Output 2,
84873222dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Output 1 / Output 2,
84873222dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 1 / Output 1,
84873222dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 1 / Output 2,
84873222dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 2 / Output 1,
84873222dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 2 / Output 2,
84873222dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 3 / Output 1,
84873222dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 3 / Output 2,
84873222dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 1 / Input 2,
84873222dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 2 / Input 3,
84873222dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 1 / Input 3,
84873222insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Supply / Input 1,
84873222insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Supply / Input 2,
84873222insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Supply / Input 3,
84873222insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Supply / Output 1,
84873222insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Supply / Output 2,
84873222insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Output 1 / Output 2,
84873222insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 1 / Output 1,
84873222insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 1 / Output 2,
84873222insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 2 / Output 1,
84873222insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 2 / Output 2,
84873222insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 3 / Output 1,
84873222insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 3 / Output 2,
84873222insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 1 / Input 2,
84873222insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 2 / Input 3,
84873222insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 1 / Input 3,
84873222
84873222[Us] rated supply voltage | Same as RM17UB310
84873222supply voltage limits | Same as RM17UB310
84873222polarity | Same as RM17UB310
84873222supply frequency | Same as RM17UB310
84873222supply frequency | Same as RM17UB310
84873222power consumption | Same as RM17UB310
84873222immunity to microbreaks | Same as RM17UB310
84873222supply terminal | Same as RM17UB310
84873222on-load factor | Same as RM17UB310
84873222release of input voltage | Same as RM17UB310
84873222
84873222monitoring functions | Same as RM17UB310 ¦ ,Phase lost ,
84873222monitoring functions | Same as RM17UB310 ¦ ,Phase sequence,
84873222monitoring functions | Same as RM17UB310 ¦ ,Over / undervoltage (symmetry windows mode),
84873222monitoring functions | Same as RM17UB310 ¦ ,Over voltage,
84873222monitoring functions | Same as RM17UB310 ¦ ,Undervoltage ,
84873222monitoring functions | Same as RM17UB310 ¦ ,Phase asymmetry,
84873222monitoring functions | Same as RM17UB310 ¦ ,Disconnection of neutral,
84873222monitoring functions | Same as RM17UB310 ¦ ,Voltage Regeneration,
84873222monitoring functions | Same as RM17UB310 ¦ ,Extreme undervoltage,
84873222monitoring functions | Same as RM17UB310 ¦ ,Extreme overvoltage,
84873222monitoring functions | Same as RM17UB310 ¦ ,Extreme asymmetry,
84873222 | Same as RM17UB310 ¦ ,Measurement mode,
84873222internal input resistance | Same as RM17UB310 ¦ ,Internal input resistance,
84873222input terminal | Same as RM17UB310 ¦ ,Input terminal,
84873222Input nominal voltage selection | Same as RM17UB310 ¦ ,Input nominal voltage selection,
84873222permissible input overload | Same as RM17UB310 ¦ ,permissible input overload,
84873222input frequency | Same as RM17UB310 ¦ ,Rated frequency,
84873222input frequency | Same as RM17UB310 ¦ ,Frequency operating range,
84873222setting accuracy of the switching threshold | Same as RM17UB310 ¦ ,Setting accuracy,
84873222repeat accuracy of the switching threshold | Same as RM17UB310 ¦ ,Repeat accuracy (constant parameters),
84873222measurement method | Same as RM17UB310 ¦ ,Measurement method,
84873222switching threshold drift | Same as RM17UB310 ¦ ,Measurement error with supply voltage variation,
84873222switching threshold drift | Same as RM17UB310 ¦ ,Measurement error with temperature variation,
84873222maximum measuring cycle | Same as RM17UB310 ¦ ,Maximum measuring cycles,
84873222measurement range | Same as RM17UB310 ¦ ,Phase lost ,
84873222measurement range | Same as RM17UB310 ¦ ,Phase sequence,
84873222measurement range | Same as RM17UB310 ¦ ,Over / undervoltage (symmetry windows mode),
84873222measurement range | Same as RM17UB310 ¦ ,Over voltage,
84873222measurement range | Same as RM17UB310 ¦ ,Undervoltage ,
84873222measurement range | Same as RM17UB310 ¦ ,Phase asymmetry,
84873222measurement range | Same as RM17UB310 ¦ ,Disconnection of neutral,
84873222measurement range | Same as RM17UB310 ¦ ,Voltage Regeneration,
84873222measurement range | Same as RM17UB310 ¦ ,Extreme undervoltage,
84873222measurement range | Same as RM17UB310 ¦ ,Extreme Overvoltage,
84873222measurement range | Same as RM17UB310 ¦ ,Extreme Asymmetry,
84873222tripping threshold | Same as RM17UB310 ¦ ,Phase cut,
84873222tripping threshold | Same as RM17UB310 ¦ ,Phase sequence,
84873222tripping threshold | Same as RM17UB310 ¦ ,Over / undervoltage (symmetry windows mode),
84873222tripping threshold | Same as RM17UB310 ¦ ,Over voltage,
84873222tripping threshold | Same as RM17UB310 ¦ ,Undervoltage ,
84873222tripping threshold | Same as RM17UB310 ¦ ,Phase asymmetry,
84873222tripping threshold | Same as RM17UB310 ¦ ,Disconnection of neutral,
84873222tripping threshold | Same as RM17UB310 ¦ ,Voltage Regeneration,
84873222tripping threshold | Same as RM17UB310 ¦ ,Extreme undervoltage (Phase loss),
84873222tripping threshold | Same as RM17UB310 ¦ ,Extreme Overvoltage,
84873222tripping threshold | Same as RM17UB310 ¦ ,Extreme Asymmetry,
84873222hysteresis | Same as RM17UB310 ¦ ,Phase cut,
84873222hysteresis | Same as RM17UB310 ¦ ,Phase sequence,
84873222hysteresis | Same as RM17UB310 ¦ ,Over / undervoltage (symmetry windows mode),
84873222hysteresis | Same as RM17UB310 ¦ ,Over voltage,
84873222hysteresis | Same as RM17UB310 ¦ ,Undervoltage ,
84873222hysteresis | Same as RM17UB310 ¦ ,Phase asymmetry,
84873222hysteresis | Same as RM17UB310 ¦ ,Disconnection of neutral,
84873222hysteresis | Same as RM17UB310 ¦ ,Voltage Regeneration,
84873222hysteresis | Same as RM17UB310 ¦ ,Extreme undervoltage (Phase loss),
84873222hysteresis | Same as RM17UB310 ¦ ,Extreme Overvoltage,
84873222hysteresis | Same as RM17UB310 ¦ ,Extreme Asymmetry,
84873222
84873222output type | Same as RM17UB310
84873222output terminal | Same as RM17UB310
84873222output logic | Same as RM17UB310 ¦ ,R1 (11-12-14),
84873222output logic | Same as RM17UB310 ¦ ,R2 (21-22-24),
84873222contacts material | Same as RM17UB310
84873222mechanical durability | Same as RM17UB310 ¦ IEC61810-1
84873222electrical durability | Same as RM17UB310 ¦ IEC60947-4-1,AC-1,
84873222electrical durability | Same as RM17UB310 ¦ IEC60947-4-1,DC-1,
84873222electrical durability | Same as RM17UB310 ¦ IEC60947-5-1,AC-15,
84873222electrical durability | Same as RM17UB310 ¦ IEC60947-5-1,DC-13,
84873222[Ue] rated operational voltage | Same as RM17UB310 ¦ IEC61810-1,Rated switching voltage,
84873222[Ie] rated operational current | Same as RM17UB310 ¦ IEC61810-1,Rated switching current,
84873222maximum switching capacity | Same as RM17UB310 ¦ ,Maximum switching voltage,
84873222maximum switching capacity | Same as RM17UB310 ¦ ,Maximum switching current,
84873222maximum switching capacity | Same as RM17UB310 ¦ ,Maximum switching capacity,
84873222minimum switching capacity | Same as RM17UB310 ¦ IEC60947-5-4,Minimum switching voltage,
84873222minimum switching capacity | Same as RM17UB310 ¦ IEC60947-5-4,Minimum switching current,
84873222minimum switching capacity | Same as RM17UB310 ¦ IEC60947-5-4,Minimum switching capacity,
84873222maximum voltage drop | Same as RM17UB310 ¦ IEC62314,Only for solid state output,
84873222maximum leakage current | Same as RM17UB310 ¦ IEC62314,Only for solid state output,
84873222thermal current | Same as RM17UB310 ¦ IEC60947-5-1
84873222short circuit protection | Same as RM17UB310 ¦ IEC60947-5-1,Relay Output by external fuse,
84873222short circuit protection | Same as RM17UB310 ¦ IEC62314,Solid State Output by external fuse,
84873222
84873222time delay type | Same as RM17UB310 ¦ ,"OFF" delay,
84873222time delay type | Same as RM17UB310 ¦ ,"ON" delay,
84873222time delay type | Same as RM17UB310 ¦ ,Inhibition,
84873222time delay range | Same as RM17UB310 ¦ ,"OFF" delay,
84873222time delay range | Same as RM17UB310 ¦ ,"ON" delay,
84873222time delay range | Same as RM17UB310 ¦ ,Inhibition,
84873222response time | Same as RM17UB310 ¦ ,on crossing the threshold,
84873222response time | Same as RM17UB310
84873222response time | Same as RM17UB310
84873222response time | Same as RM17UB310
84873222response time | Same as RM17UB310
84873222power on delay | Same as RM17UB310
84873222reset time | Same as RM17UB310 ¦ ,through Un power reset,
84873222reset time | Same as RM17UB310 ¦ ,through front panel reset,
84873222reset time | Same as RM17UB310 ¦ ,through input control reset,
84873222setting accuracy of time delay | Same as RM17UB310
84873222repeat accuracy of time delay | Same as RM17UB310
84873222time delay drift | Same as RM17UB310
84873222time delay drift | Same as RM17UB310
84873222
84873222status LED | Same as RM17UB310
84873222local signalling | Same as RM17UB310 ¦ ,Power supply availability,
84873222local signalling | Same as RM17UB310 ¦ ,Power supply not availability,
84873222local signalling | Same as RM17UB310 ¦ ,Timing in-progress,
84873222local signalling | Same as RM17UB310 ¦ ,Output is energized,
84873222local signalling | Same as RM17UB310 ¦ ,Output is de-energized,
84873222local signalling | Same as RM17UB310 ¦ ,Range Setting Changes,
84873222local signalling | Same as RM17UB310 ¦ ,Phase Cut,
84873222local signalling | Same as RM17UB310 ¦ ,Phase Sequence Swap,
84873222local signalling | Same as RM17UB310 ¦ ,Undervoltage <U,
84873222local signalling | Same as RM17UB310 ¦ ,Overvoltage >U,
84873222local signalling | Same as RM17UB310 ¦ ,Phase Asymmetry,
84873222local signalling | Same as RM17UB310 ¦ ,Voltage Regeneration,
84873222local signalling | Same as RM17UB310 ¦ ,Extreme Undervoltage <U (Phase loss),
84873222local signalling | Same as RM17UB310 ¦ ,Extreme Overvoltage >U,
84873222local signalling | Same as RM17UB310 ¦ ,Extreme Phase Asymmetry,
84873222
84873222 | Same as RM17UB310
84873222 | Same as RM17UB310
84873222diagnostic button | Same as RM17UB310
84873222 | Same as RM17UB310
84873222 | Same as RM17UB310
84873222
84873222safety reliability data | Same as RM17UB310 ¦ ,MTTF,
84873222safety reliability data | Same as RM17UB310 ¦ ,B10,
84873222 | Same as RM17UB310 ¦ ,MTTFd,
84873222 | Same as RM17UB310 ¦ ,B10d,
84873222
84873222 | Drawing / Diagram
84873896
84873896standards | Same as RM17UB310
84873896product certifications | UL, CSA, CE, China ROHS
84873896marking | UL, CSA, CE, China ROHS
84873896directives | Same as RM17UB310
84873896directives | Same as RM17UB310
84873896directives | Same as RM17UB310
84873896
84873896 | Same as RM17UB310 ¦ IEC60721-3-3,Climatic category,
84873896 | Same as RM17UB310 ¦ Germanisher Lloyd,Environmental category,
84873896ambient air temperature for storage | Same as RM17UB310 ¦ ,Storage,
84873896ambient air temperature for operation | Same as RM17UB310 ¦ ,Operation,
84873896relative humidity | Same as RM17UB310 ¦ IEC60068-2-30,Damp heat,XX
84873896 | Same as RM17UB310 ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873896vibration resistance | Same as RM17UB310 ¦ IEC60068-2-6
84873896shock resistance | Same as RM17UB310 ¦ IEC60068-2-27
84873896bump resistance | Same as RM17UB310 ¦ IEC60068-2-29
84873896seismic resistance | Same as RM17UB310 ¦ IEC60068-3-3
84873896IP degree of protection | Same as RM17UB310 ¦ IEC60529,Terminal Block,
84873896IP degree of protection | Same as RM17UB310 ¦ IEC60529,Housing,
84873896IP degree of protection | Same as RM17UB310 ¦ IEC60529,Front Panel,
84873896
84873896width | Same as RM17UB310 ¦ ,Width,
84873896height | Same as RM17UB310 ¦ ,Height,
84873896depth | Same as RM17UB310 ¦ ,Depth,
84873896net weight | Same as RM17UB310
84873896mounting support | Same as RM17UB310 ¦ IEC/EN 60715,Without socket,
84873896mounting support | Same as RM17UB310 ¦ IEC/EN 60715,With socket,
84873896mounting position | Same as RM17UB310 ¦ ,In relation to normal vertical mounting plane,
84873896Minimum distance to adjacent devices | Same as RM17UB310 ¦ ,Horizontal,
84873896Minimum distance to adjacent devices | Same as RM17UB310 ¦ ,Vertical,
84873896connections - terminals | Same as RM17UB310 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873896connections - terminals | Same as RM17UB310 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873896connections - terminals | Same as RM17UB310 ¦ IEC60947-1,Solid cable (spring terminal),
84873896connections - terminals | Same as RM17UB310 ¦ IEC60947-1,Flexible cable (spring terminal),
84873896tightening torque | Same as RM17UB310 ¦ IEC60947-1,Tightening torque,
84873896cable stripping length | Same as RM17UB310 ¦ ,Cable stripping length,
84873896duty time | Same as RM17UB310
84873896
84873896electromagnetic compatibility | Same as RM17UB310 ¦ ,Generic immunity standard,
84873896electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-2,Electrostatic discharge,
84873896electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873896electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-4,Fast transient / burst,
84873896electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-5,Surge,
84873896electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-6,Conducted RF disturbance,
84873896electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-8,Power frequency magnetic field,
84873896electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873896electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-18,1 MHz oscillation wave,
84873896electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-29,DC voltage interruption,
84873896electromagnetic compatibility | Same as RM17UB310 ¦ IEC61000-4-13,Low frequency harmonics,
84873896electromagnetic compatibility | Same as RM17UB310 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873896electromagnetic compatibility | Same as RM17UB310 ¦ ,Generic emission standard,
84873896electromagnetic compatibility | Same as RM17UB310 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873896electromagnetic compatibility | Same as RM17UB310 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873896electromagnetic compatibility | Same as RM17UB310 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873896electromagnetic compatibility | Same as RM17UB310 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873896electromagnetic compatibility | Same as RM17UB310 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873896electromagnetic compatibility | Same as RM17UB310 ¦ Germanisher Lloyd,Conducted emission,
84873896
84873896pollution degree | Same as RM17UB310 ¦ IEC60664-1
84873896overvoltage category | Same as RM17UB310 ¦ IEC60664-1
84873896circuit group | Same as RM17UB310 ¦ ,Supply,Terminal
84873896circuit group | Same as RM17UB310 ¦ ,Input 1,
84873896circuit group | Same as RM17UB310 ¦ ,Input 2,
84873896circuit group | Same as RM17UB310 ¦ ,Input 3,
84873896circuit group | Same as RM17UB310 ¦ ,Output 1,
84873896circuit group | Same as RM17UB310 ¦ ,Output 2,
84873896 | Same as RM17UB310 ¦ ,Supply,Rated
84873896 | Same as RM17UB310 ¦ ,Input 1,Voltage
84873896 | Same as RM17UB310 ¦ ,Input 2,Spec
84873896 | Same as RM17UB310 ¦ ,Input 3,
84873896 | Same as RM17UB310 ¦ ,Output 1,
84873896 | Same as RM17UB310 ¦ ,Output 2,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Supply,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 2,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 3,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Output 1,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Output 2,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Input 2,Isolated
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Input 3,Circuit
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Output 1,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Output 2,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Output 1 / Output 2,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1 / Output 1,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1 / Output 2,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 2 / Output 1,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 2 / Output 2,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 3 / Output 1,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 3 / Output 2,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1 / Input 2,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 2 / Input 3,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1 / Input 3,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Supply,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 2,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 3,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Output 1,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Output 2,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Input 1,Galvanic
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Input 2,Isolated
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Input 3,Circuit
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Output 1,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Supply / Output 2,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Output 1 / Output 2,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1 / Output 1,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1 / Output 2,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 2 / Output 1,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 2 / Output 2,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 3 / Output 1,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 3 / Output 2,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1 / Input 2,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 2 / Input 3,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Input 1 / Input 3,
84873896dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Supply / Input 1,
84873896dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Supply / Input 2,
84873896dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Supply / Input 3,
84873896dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Supply / Output 1,
84873896dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Supply / Output 2,
84873896dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Output 1 / Output 2,
84873896dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 1 / Output 1,
84873896dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 1 / Output 2,
84873896dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 2 / Output 1,
84873896dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 2 / Output 2,
84873896dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 3 / Output 1,
84873896dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 3 / Output 2,
84873896dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 1 / Input 2,
84873896dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 2 / Input 3,
84873896dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Input 1 / Input 3,
84873896insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Supply / Input 1,
84873896insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Supply / Input 2,
84873896insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Supply / Input 3,
84873896insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Supply / Output 1,
84873896insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Supply / Output 2,
84873896insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Output 1 / Output 2,
84873896insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 1 / Output 1,
84873896insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 1 / Output 2,
84873896insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 2 / Output 1,
84873896insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 2 / Output 2,
84873896insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 3 / Output 1,
84873896insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 3 / Output 2,
84873896insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 1 / Input 2,
84873896insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 2 / Input 3,
84873896insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Input 1 / Input 3,
84873896
84873896[Us] rated supply voltage | Same as RM17UB310
84873896supply voltage limits | Same as RM17UB310
84873896polarity | Same as RM17UB310
84873896supply frequency | Same as RM17UB310
84873896supply frequency | Same as RM17UB310
84873896power consumption | Same as RM17UB310
84873896immunity to microbreaks | Same as RM17UB310
84873896supply terminal | Same as RM17UB310
84873896on-load factor | Same as RM17UB310
84873896release of input voltage | Same as RM17UB310
84873896
84873896monitoring functions | Same as RM17UB310 ¦ ,Phase lost ,
84873896monitoring functions | Same as RM17UB310 ¦ ,Phase sequence,
84873896monitoring functions | Same as RM17UB310 ¦ ,Over / undervoltage (symmetry windows mode),
84873896monitoring functions | Same as RM17UB310 ¦ ,Over voltage,
84873896monitoring functions | Same as RM17UB310 ¦ ,Undervoltage ,
84873896monitoring functions | Same as RM17UB310 ¦ ,Phase asymmetry,
84873896monitoring functions | Same as RM17UB310 ¦ ,Disconnection of neutral,
84873896monitoring functions | Same as RM17UB310 ¦ ,Voltage Regeneration,
84873896monitoring functions | Same as RM17UB310 ¦ ,Extreme undervoltage,
84873896monitoring functions | Same as RM17UB310 ¦ ,Extreme overvoltage,
84873896monitoring functions | Same as RM17UB310 ¦ ,Extreme asymmetry,
84873896 | Same as RM17UB310 ¦ ,Measurement mode,
84873896internal input resistance | Same as RM17UB310 ¦ ,Internal input resistance,
84873896input terminal | Same as RM17UB310 ¦ ,Input terminal,
84873896Input nominal voltage selection | Same as RM17UB310 ¦ ,Input nominal voltage selection,
84873896permissible input overload | Same as RM17UB310 ¦ ,permissible input overload,
84873896input frequency | Same as RM17UB310 ¦ ,Rated frequency,
84873896input frequency | Same as RM17UB310 ¦ ,Frequency operating range,
84873896setting accuracy of the switching threshold | Same as RM17UB310 ¦ ,Setting accuracy,
84873896repeat accuracy of the switching threshold | Same as RM17UB310 ¦ ,Repeat accuracy (constant parameters),
84873896measurement method | Same as RM17UB310 ¦ ,Measurement method,
84873896switching threshold drift | Same as RM17UB310 ¦ ,Measurement error with supply voltage variation,
84873896switching threshold drift | Same as RM17UB310 ¦ ,Measurement error with temperature variation,
84873896maximum measuring cycle | Same as RM17UB310 ¦ ,Maximum measuring cycles,
84873896measurement range | Same as RM17UB310 ¦ ,Phase lost ,
84873896measurement range | Same as RM17UB310 ¦ ,Phase sequence,
84873896measurement range | Same as RM17UB310 ¦ ,Over / undervoltage (symmetry windows mode),
84873896measurement range | Same as RM17UB310 ¦ ,Over voltage,
84873896measurement range | Same as RM17UB310 ¦ ,Undervoltage ,
84873896measurement range | Same as RM17UB310 ¦ ,Phase asymmetry,
84873896measurement range | Same as RM17UB310 ¦ ,Disconnection of neutral,
84873896measurement range | Same as RM17UB310 ¦ ,Voltage Regeneration,
84873896measurement range | Same as RM17UB310 ¦ ,Extreme undervoltage,
84873896measurement range | Same as RM17UB310 ¦ ,Extreme Overvoltage,
84873896measurement range | Same as RM17UB310 ¦ ,Extreme Asymmetry,
84873896tripping threshold | Same as RM17UB310 ¦ ,Phase cut,
84873896tripping threshold | Same as RM17UB310 ¦ ,Phase sequence,
84873896tripping threshold | Same as RM17UB310 ¦ ,Over / undervoltage (symmetry windows mode),
84873896tripping threshold | Same as RM17UB310 ¦ ,Over voltage,
84873896tripping threshold | Same as RM17UB310 ¦ ,Undervoltage ,
84873896tripping threshold | Same as RM17UB310 ¦ ,Phase asymmetry,
84873896tripping threshold | Same as RM17UB310 ¦ ,Disconnection of neutral,
84873896tripping threshold | Same as RM17UB310 ¦ ,Voltage Regeneration,
84873896tripping threshold | Same as RM17UB310 ¦ ,Extreme undervoltage (Phase loss),
84873896tripping threshold | Same as RM17UB310 ¦ ,Extreme Overvoltage,
84873896tripping threshold | Same as RM17UB310 ¦ ,Extreme Asymmetry,
84873896hysteresis | Same as RM17UB310 ¦ ,Phase cut,
84873896hysteresis | Same as RM17UB310 ¦ ,Phase sequence,
84873896hysteresis | Same as RM17UB310 ¦ ,Over / undervoltage (symmetry windows mode),
84873896hysteresis | Same as RM17UB310 ¦ ,Over voltage,
84873896hysteresis | Same as RM17UB310 ¦ ,Undervoltage ,
84873896hysteresis | Same as RM17UB310 ¦ ,Phase asymmetry,
84873896hysteresis | Same as RM17UB310 ¦ ,Disconnection of neutral,
84873896hysteresis | Same as RM17UB310 ¦ ,Voltage Regeneration,
84873896hysteresis | Same as RM17UB310 ¦ ,Extreme undervoltage (Phase loss),
84873896hysteresis | Same as RM17UB310 ¦ ,Extreme Overvoltage,
84873896hysteresis | Same as RM17UB310 ¦ ,Extreme Asymmetry,
84873896
84873896output type | Same as RM17UB310
84873896output terminal | Same as RM17UB310
84873896output logic | Same as RM17UB310 ¦ ,R1 (11-12-14),
84873896output logic | Same as RM17UB310 ¦ ,R2 (21-22-24),
84873896contacts material | Same as RM17UB310
84873896mechanical durability | Same as RM17UB310 ¦ IEC61810-1
84873896electrical durability | Same as RM17UB310 ¦ IEC60947-4-1,AC-1,
84873896electrical durability | Same as RM17UB310 ¦ IEC60947-4-1,DC-1,
84873896electrical durability | Same as RM17UB310 ¦ IEC60947-5-1,AC-15,
84873896electrical durability | Same as RM17UB310 ¦ IEC60947-5-1,DC-13,
84873896[Ue] rated operational voltage | Same as RM17UB310 ¦ IEC61810-1,Rated switching voltage,
84873896[Ie] rated operational current | Same as RM17UB310 ¦ IEC61810-1,Rated switching current,
84873896maximum switching capacity | Same as RM17UB310 ¦ ,Maximum switching voltage,
84873896maximum switching capacity | Same as RM17UB310 ¦ ,Maximum switching current,
84873896maximum switching capacity | Same as RM17UB310 ¦ ,Maximum switching capacity,
84873896minimum switching capacity | Same as RM17UB310 ¦ IEC60947-5-4,Minimum switching voltage,
84873896minimum switching capacity | Same as RM17UB310 ¦ IEC60947-5-4,Minimum switching current,
84873896minimum switching capacity | Same as RM17UB310 ¦ IEC60947-5-4,Minimum switching capacity,
84873896maximum voltage drop | Same as RM17UB310 ¦ IEC62314,Only for solid state output,
84873896maximum leakage current | Same as RM17UB310 ¦ IEC62314,Only for solid state output,
84873896thermal current | Same as RM17UB310 ¦ IEC60947-5-1
84873896short circuit protection | Same as RM17UB310 ¦ IEC60947-5-1,Relay Output by external fuse,
84873896short circuit protection | Same as RM17UB310 ¦ IEC62314,Solid State Output by external fuse,
84873896
84873896time delay type | Same as RM17UB310 ¦ ,"OFF" delay,
84873896time delay type | Same as RM17UB310 ¦ ,"ON" delay,
84873896time delay type | Same as RM17UB310 ¦ ,Inhibition,
84873896time delay range | Same as RM17UB310 ¦ ,"OFF" delay,
84873896time delay range | Same as RM17UB310 ¦ ,"ON" delay,
84873896time delay range | Same as RM17UB310 ¦ ,Inhibition,
84873896response time | Same as RM17UB310 ¦ ,on crossing the threshold,
84873896response time | Same as RM17UB310
84873896response time | Same as RM17UB310
84873896response time | Same as RM17UB310
84873896response time | Same as RM17UB310
84873896power on delay | Same as RM17UB310
84873896reset time | Same as RM17UB310 ¦ ,through Un power reset,
84873896reset time | Same as RM17UB310 ¦ ,through front panel reset,
84873896reset time | Same as RM17UB310 ¦ ,through input control reset,
84873896setting accuracy of time delay | Same as RM17UB310
84873896repeat accuracy of time delay | Same as RM17UB310
84873896time delay drift | Same as RM17UB310
84873896time delay drift | Same as RM17UB310
84873896
84873896status LED | Same as RM17UB310
84873896local signalling | Same as RM17UB310 ¦ ,Power supply availability,
84873896local signalling | Same as RM17UB310 ¦ ,Power supply not availability,
84873896local signalling | Same as RM17UB310 ¦ ,Timing in-progress,
84873896local signalling | Same as RM17UB310 ¦ ,Output is energized,
84873896local signalling | Same as RM17UB310 ¦ ,Output is de-energized,
84873896local signalling | Same as RM17UB310 ¦ ,Range Setting Changes,
84873896local signalling | Same as RM17UB310 ¦ ,Phase Cut,
84873896local signalling | Same as RM17UB310 ¦ ,Phase Sequence Swap,
84873896local signalling | Same as RM17UB310 ¦ ,Undervoltage <U,
84873896local signalling | Same as RM17UB310 ¦ ,Overvoltage >U,
84873896local signalling | Same as RM17UB310 ¦ ,Phase Asymmetry,
84873896local signalling | Same as RM17UB310 ¦ ,Voltage Regeneration,
84873896local signalling | Same as RM17UB310 ¦ ,Extreme Undervoltage <U (Phase loss),
84873896local signalling | Same as RM17UB310 ¦ ,Extreme Overvoltage >U,
84873896local signalling | Same as RM17UB310 ¦ ,Extreme Phase Asymmetry,
84873896
84873896 | Same as RM17UB310
84873896 | Same as RM17UB310
84873896diagnostic button | Same as RM17UB310
84873896 | Same as RM17UB310
84873896 | Same as RM17UB310
84873896
84873896safety reliability data | Same as RM17UB310 ¦ ,MTTF,
84873896safety reliability data | Same as RM17UB310 ¦ ,B10,
84873896 | Same as RM17UB310 ¦ ,MTTFd,
84873896 | Same as RM17UB310 ¦ ,B10d,
84873896
84873896 | Drawing / Diagram
col50
col50standards
col50product certifications
col50marking
col50directives
col50directives
col50directives
col50
col50 | IEC60721-3-3,Climatic category,
col50 | Germanisher Lloyd,Environmental category,
col50ambient air temperature for storage | Storage,
col50ambient air temperature for operation | Operation,
col50relative humidity | IEC60068-2-30,Damp heat,XX
col50 | IEC60947-5-1,Cyclic Damp Heat Test,
col50vibration resistance | IEC60068-2-6
col50shock resistance | IEC60068-2-27
col50bump resistance | IEC60068-2-29
col50seismic resistance | IEC60068-3-3
col50IP degree of protection | IEC60529,Terminal Block,
col50IP degree of protection | IEC60529,Housing,
col50IP degree of protection | IEC60529,Front Panel,
col50
col50width | Width,
col50height | Height,
col50depth | Depth,
col50net weight
col50mounting support | IEC/EN 60715,Without socket,
col50mounting support | IEC/EN 60715,With socket,
col50mounting position | In relation to normal vertical mounting plane,
col50Minimum distance to adjacent devices | Horizontal,
col50Minimum distance to adjacent devices | Vertical,
col50connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
col50connections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
col50connections - terminals | IEC60947-1,Solid cable (spring terminal),
col50connections - terminals | IEC60947-1,Flexible cable (spring terminal),
col50tightening torque | IEC60947-1,Tightening torque,
col50cable stripping length | Cable stripping length,
col50duty time
col50
col50electromagnetic compatibility | Generic immunity standard,
col50electromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
col50electromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
col50electromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
col50electromagnetic compatibility | IEC61000-4-5,Surge,
col50electromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
col50electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
col50electromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
col50electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
col50electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
col50electromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
col50electromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
col50electromagnetic compatibility | Generic emission standard,
col50electromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
col50electromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
col50electromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
col50electromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
col50electromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
col50electromagnetic compatibility | Germanisher Lloyd,Conducted emission,
col50
col50pollution degree | IEC60664-1
col50overvoltage category | IEC60664-1
col50circuit group | Supply,Terminal
col50circuit group | Input 1,
col50circuit group | Input 2,
col50circuit group | Input 3,
col50circuit group | Output 1,
col50circuit group | Output 2,
col50 | Supply,Rated
col50 | Input 1,Voltage
col50 | Input 2,Spec
col50 | Input 3,
col50 | Output 1,
col50 | Output 2,
col50[Ui] rated insulation voltage | IEC60664-1,Supply,
col50[Ui] rated insulation voltage | IEC60664-1,Input 1,
col50[Ui] rated insulation voltage | IEC60664-1,Input 2,
col50[Ui] rated insulation voltage | IEC60664-1,Input 3,
col50[Ui] rated insulation voltage | IEC60664-1,Output 1,
col50[Ui] rated insulation voltage | IEC60664-1,Output 2,
col50[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
col50[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
col50[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
col50[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
col50[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
col50[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
col50[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
col50[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
col50[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
col50[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
col50[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
col50[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
col50[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
col50[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
col50[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
col50dielectric strength | IEC60255-27,Supply / Input 1,
col50dielectric strength | IEC60255-27,Supply / Input 2,
col50dielectric strength | IEC60255-27,Supply / Input 3,
col50dielectric strength | IEC60255-27,Supply / Output 1,
col50dielectric strength | IEC60255-27,Supply / Output 2,
col50dielectric strength | IEC60255-27,Output 1 / Output 2,
col50dielectric strength | IEC60255-27,Input 1 / Output 1,
col50dielectric strength | IEC60255-27,Input 1 / Output 2,
col50dielectric strength | IEC60255-27,Input 2 / Output 1,
col50dielectric strength | IEC60255-27,Input 2 / Output 2,
col50dielectric strength | IEC60255-27,Input 3 / Output 1,
col50dielectric strength | IEC60255-27,Input 3 / Output 2,
col50dielectric strength | IEC60255-27,Input 1 / Input 2,
col50dielectric strength | IEC60255-27,Input 2 / Input 3,
col50dielectric strength | IEC60255-27,Input 1 / Input 3,
col50insulation resistance | IEC60255-27,Supply / Input 1,
col50insulation resistance | IEC60255-27,Supply / Input 2,
col50insulation resistance | IEC60255-27,Supply / Input 3,
col50insulation resistance | IEC60255-27,Supply / Output 1,
col50insulation resistance | IEC60255-27,Supply / Output 2,
col50insulation resistance | IEC60255-27,Output 1 / Output 2,
col50insulation resistance | IEC60255-27,Input 1 / Output 1,
col50insulation resistance | IEC60255-27,Input 1 / Output 2,
col50insulation resistance | IEC60255-27,Input 2 / Output 1,
col50insulation resistance | IEC60255-27,Input 2 / Output 2,
col50insulation resistance | IEC60255-27,Input 3 / Output 1,
col50insulation resistance | IEC60255-27,Input 3 / Output 2,
col50insulation resistance | IEC60255-27,Input 1 / Input 2,
col50insulation resistance | IEC60255-27,Input 2 / Input 3,
col50insulation resistance | IEC60255-27,Input 1 / Input 3,
col50
col50[Us] rated supply voltage
col50supply voltage limits
col50polarity
col50supply frequency
col50supply frequency
col50power consumption
col50immunity to microbreaks
col50supply terminal
col50on-load factor
col50release of input voltage
col50
col50monitoring functions | Phase lost ,
col50monitoring functions | Phase sequence,
col50monitoring functions | Over / undervoltage (symmetry windows mode),
col50monitoring functions | Over voltage,
col50monitoring functions | Undervoltage ,
col50monitoring functions | Phase asymmetry,
col50monitoring functions | Disconnection of neutral,
col50monitoring functions | Voltage Regeneration,
col50monitoring functions | Extreme undervoltage,
col50monitoring functions | Extreme overvoltage,
col50monitoring functions | Extreme asymmetry,
col50 | Measurement mode,
col50internal input resistance | Internal input resistance,
col50input terminal | Input terminal,
col50Input nominal voltage selection | Input nominal voltage selection,
col50permissible input overload | permissible input overload,
col50input frequency | Rated frequency,
col50input frequency | Frequency operating range,
col50setting accuracy of the switching threshold | Setting accuracy,
col50repeat accuracy of the switching threshold | Repeat accuracy (constant parameters),
col50measurement method | Measurement method,
col50switching threshold drift | Measurement error with supply voltage variation,
col50switching threshold drift | Measurement error with temperature variation,
col50maximum measuring cycle | Maximum measuring cycles,
col50measurement range | Phase lost ,
col50measurement range | Phase sequence,
col50measurement range | Over / undervoltage (symmetry windows mode),
col50measurement range | Over voltage,
col50measurement range | Undervoltage ,
col50measurement range | Phase asymmetry,
col50measurement range | Disconnection of neutral,
col50measurement range | Voltage Regeneration,
col50measurement range | Extreme undervoltage,
col50measurement range | Extreme Overvoltage,
col50measurement range | Extreme Asymmetry,
col50tripping threshold | Phase cut,
col50tripping threshold | Phase sequence,
col50tripping threshold | Over / undervoltage (symmetry windows mode),
col50tripping threshold | Over voltage,
col50tripping threshold | Undervoltage ,
col50tripping threshold | Phase asymmetry,
col50tripping threshold | Disconnection of neutral,
col50tripping threshold | Voltage Regeneration,
col50tripping threshold | Extreme undervoltage (Phase loss),
col50tripping threshold | Extreme Overvoltage,
col50tripping threshold | Extreme Asymmetry,
col50hysteresis | Phase cut,
col50hysteresis | Phase sequence,
col50hysteresis | Over / undervoltage (symmetry windows mode),
col50hysteresis | Over voltage,
col50hysteresis | Undervoltage ,
col50hysteresis | Phase asymmetry,
col50hysteresis | Disconnection of neutral,
col50hysteresis | Voltage Regeneration,
col50hysteresis | Extreme undervoltage (Phase loss),
col50hysteresis | Extreme Overvoltage,
col50hysteresis | Extreme Asymmetry,
col50
col50output type
col50output terminal
col50output logic | R1 (11-12-14),
col50output logic | R2 (21-22-24),
col50contacts material
col50mechanical durability | IEC61810-1
col50electrical durability | IEC60947-4-1,AC-1,
col50electrical durability | IEC60947-4-1,DC-1,
col50electrical durability | IEC60947-5-1,AC-15,
col50electrical durability | IEC60947-5-1,DC-13,
col50[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col50[Ie] rated operational current | IEC61810-1,Rated switching current,
col50maximum switching capacity | Maximum switching voltage,
col50maximum switching capacity | Maximum switching current,
col50maximum switching capacity | Maximum switching capacity,
col50minimum switching capacity | IEC60947-5-4,Minimum switching voltage,
col50minimum switching capacity | IEC60947-5-4,Minimum switching current,
col50minimum switching capacity | IEC60947-5-4,Minimum switching capacity,
col50maximum voltage drop | IEC62314,Only for solid state output,
col50maximum leakage current | IEC62314,Only for solid state output,
col50thermal current | IEC60947-5-1
col50short circuit protection | IEC60947-5-1,Relay Output by external fuse,
col50short circuit protection | IEC62314,Solid State Output by external fuse,
col50
col50time delay type | "OFF" delay,
col50time delay type | "ON" delay,
col50time delay type | Inhibition,
col50time delay range | "OFF" delay,
col50time delay range | "ON" delay,
col50time delay range | Inhibition,
col50response time | on crossing the threshold,
col50response time
col50response time
col50response time
col50response time
col50power on delay
col50reset time | through Un power reset,
col50reset time | through front panel reset,
col50reset time | through input control reset,
col50setting accuracy of time delay
col50repeat accuracy of time delay
col50time delay drift
col50time delay drift
col50
col50status LED
col50local signalling | Power supply availability,
col50local signalling | Power supply not availability,
col50local signalling | Timing in-progress,
col50local signalling | Output is energized,
col50local signalling | Output is de-energized,
col50local signalling | Range Setting Changes,
col50local signalling | Phase Cut,
col50local signalling | Phase Sequence Swap,
col50local signalling | Undervoltage <U,
col50local signalling | Overvoltage >U,
col50local signalling | Phase Asymmetry,
col50local signalling | Voltage Regeneration,
col50local signalling | Extreme Undervoltage <U (Phase loss),
col50local signalling | Extreme Overvoltage >U,
col50local signalling | Extreme Phase Asymmetry,
col50
col50
col50
col50diagnostic button
col50
col50
col50
col50safety reliability data | MTTF,
col50safety reliability data | B10,
col50 | MTTFd,
col50 | B10d,
col50
col50
col51
col51standards
col51product certifications
col51marking
col51directives
col51directives
col51directives
col51
col51 | IEC60721-3-3,Climatic category,
col51 | Germanisher Lloyd,Environmental category,
col51ambient air temperature for storage | Storage,
col51ambient air temperature for operation | Operation,
col51relative humidity | IEC60068-2-30,Damp heat,XX
col51 | IEC60947-5-1,Cyclic Damp Heat Test,
col51vibration resistance | IEC60068-2-6
col51shock resistance | IEC60068-2-27
col51bump resistance | IEC60068-2-29
col51seismic resistance | IEC60068-3-3
col51IP degree of protection | IEC60529,Terminal Block,
col51IP degree of protection | IEC60529,Housing,
col51IP degree of protection | IEC60529,Front Panel,
col51
col51width | Width,
col51height | Height,
col51depth | Depth,
col51net weight
col51mounting support | IEC/EN 60715,Without socket,
col51mounting support | IEC/EN 60715,With socket,
col51mounting position | In relation to normal vertical mounting plane,
col51Minimum distance to adjacent devices | Horizontal,
col51Minimum distance to adjacent devices | Vertical,
col51connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
col51connections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
col51connections - terminals | IEC60947-1,Solid cable (spring terminal),
col51connections - terminals | IEC60947-1,Flexible cable (spring terminal),
col51tightening torque | IEC60947-1,Tightening torque,
col51cable stripping length | Cable stripping length,
col51duty time
col51
col51electromagnetic compatibility | Generic immunity standard,
col51electromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
col51electromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
col51electromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
col51electromagnetic compatibility | IEC61000-4-5,Surge,
col51electromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
col51electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
col51electromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
col51electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
col51electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
col51electromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
col51electromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
col51electromagnetic compatibility | Generic emission standard,
col51electromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
col51electromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
col51electromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
col51electromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
col51electromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
col51electromagnetic compatibility | Germanisher Lloyd,Conducted emission,
col51
col51pollution degree | IEC60664-1
col51overvoltage category | IEC60664-1
col51circuit group | Supply,Terminal
col51circuit group | Input 1,
col51circuit group | Input 2,
col51circuit group | Input 3,
col51circuit group | Output 1,
col51circuit group | Output 2,
col51 | Supply,Rated
col51 | Input 1,Voltage
col51 | Input 2,Spec
col51 | Input 3,
col51 | Output 1,
col51 | Output 2,
col51[Ui] rated insulation voltage | IEC60664-1,Supply,
col51[Ui] rated insulation voltage | IEC60664-1,Input 1,
col51[Ui] rated insulation voltage | IEC60664-1,Input 2,
col51[Ui] rated insulation voltage | IEC60664-1,Input 3,
col51[Ui] rated insulation voltage | IEC60664-1,Output 1,
col51[Ui] rated insulation voltage | IEC60664-1,Output 2,
col51[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
col51[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
col51[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
col51[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
col51[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
col51[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
col51[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
col51[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
col51[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
col51[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
col51[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
col51[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
col51[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
col51[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
col51[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
col51dielectric strength | IEC60255-27,Supply / Input 1,
col51dielectric strength | IEC60255-27,Supply / Input 2,
col51dielectric strength | IEC60255-27,Supply / Input 3,
col51dielectric strength | IEC60255-27,Supply / Output 1,
col51dielectric strength | IEC60255-27,Supply / Output 2,
col51dielectric strength | IEC60255-27,Output 1 / Output 2,
col51dielectric strength | IEC60255-27,Input 1 / Output 1,
col51dielectric strength | IEC60255-27,Input 1 / Output 2,
col51dielectric strength | IEC60255-27,Input 2 / Output 1,
col51dielectric strength | IEC60255-27,Input 2 / Output 2,
col51dielectric strength | IEC60255-27,Input 3 / Output 1,
col51dielectric strength | IEC60255-27,Input 3 / Output 2,
col51dielectric strength | IEC60255-27,Input 1 / Input 2,
col51dielectric strength | IEC60255-27,Input 2 / Input 3,
col51dielectric strength | IEC60255-27,Input 1 / Input 3,
col51insulation resistance | IEC60255-27,Supply / Input 1,
col51insulation resistance | IEC60255-27,Supply / Input 2,
col51insulation resistance | IEC60255-27,Supply / Input 3,
col51insulation resistance | IEC60255-27,Supply / Output 1,
col51insulation resistance | IEC60255-27,Supply / Output 2,
col51insulation resistance | IEC60255-27,Output 1 / Output 2,
col51insulation resistance | IEC60255-27,Input 1 / Output 1,
col51insulation resistance | IEC60255-27,Input 1 / Output 2,
col51insulation resistance | IEC60255-27,Input 2 / Output 1,
col51insulation resistance | IEC60255-27,Input 2 / Output 2,
col51insulation resistance | IEC60255-27,Input 3 / Output 1,
col51insulation resistance | IEC60255-27,Input 3 / Output 2,
col51insulation resistance | IEC60255-27,Input 1 / Input 2,
col51insulation resistance | IEC60255-27,Input 2 / Input 3,
col51insulation resistance | IEC60255-27,Input 1 / Input 3,
col51
col51[Us] rated supply voltage
col51supply voltage limits
col51polarity
col51supply frequency
col51supply frequency
col51power consumption
col51immunity to microbreaks
col51supply terminal
col51on-load factor
col51release of input voltage
col51
col51monitoring functions | Phase lost ,
col51monitoring functions | Phase sequence,
col51monitoring functions | Over / undervoltage (symmetry windows mode),
col51monitoring functions | Over voltage,
col51monitoring functions | Undervoltage ,
col51monitoring functions | Phase asymmetry,
col51monitoring functions | Disconnection of neutral,
col51monitoring functions | Voltage Regeneration,
col51monitoring functions | Extreme undervoltage,
col51monitoring functions | Extreme overvoltage,
col51monitoring functions | Extreme asymmetry,
col51 | Measurement mode,
col51internal input resistance | Internal input resistance,
col51input terminal | Input terminal,
col51Input nominal voltage selection | Input nominal voltage selection,
col51permissible input overload | permissible input overload,
col51input frequency | Rated frequency,
col51input frequency | Frequency operating range,
col51setting accuracy of the switching threshold | Setting accuracy,
col51repeat accuracy of the switching threshold | Repeat accuracy (constant parameters),
col51measurement method | Measurement method,
col51switching threshold drift | Measurement error with supply voltage variation,
col51switching threshold drift | Measurement error with temperature variation,
col51maximum measuring cycle | Maximum measuring cycles,
col51measurement range | Phase lost ,
col51measurement range | Phase sequence,
col51measurement range | Over / undervoltage (symmetry windows mode),
col51measurement range | Over voltage,
col51measurement range | Undervoltage ,
col51measurement range | Phase asymmetry,
col51measurement range | Disconnection of neutral,
col51measurement range | Voltage Regeneration,
col51measurement range | Extreme undervoltage,
col51measurement range | Extreme Overvoltage,
col51measurement range | Extreme Asymmetry,
col51tripping threshold | Phase cut,
col51tripping threshold | Phase sequence,
col51tripping threshold | Over / undervoltage (symmetry windows mode),
col51tripping threshold | Over voltage,
col51tripping threshold | Undervoltage ,
col51tripping threshold | Phase asymmetry,
col51tripping threshold | Disconnection of neutral,
col51tripping threshold | Voltage Regeneration,
col51tripping threshold | Extreme undervoltage (Phase loss),
col51tripping threshold | Extreme Overvoltage,
col51tripping threshold | Extreme Asymmetry,
col51hysteresis | Phase cut,
col51hysteresis | Phase sequence,
col51hysteresis | Over / undervoltage (symmetry windows mode),
col51hysteresis | Over voltage,
col51hysteresis | Undervoltage ,
col51hysteresis | Phase asymmetry,
col51hysteresis | Disconnection of neutral,
col51hysteresis | Voltage Regeneration,
col51hysteresis | Extreme undervoltage (Phase loss),
col51hysteresis | Extreme Overvoltage,
col51hysteresis | Extreme Asymmetry,
col51
col51output type
col51output terminal
col51output logic | R1 (11-12-14),
col51output logic | R2 (21-22-24),
col51contacts material
col51mechanical durability | IEC61810-1
col51electrical durability | IEC60947-4-1,AC-1,
col51electrical durability | IEC60947-4-1,DC-1,
col51electrical durability | IEC60947-5-1,AC-15,
col51electrical durability | IEC60947-5-1,DC-13,
col51[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col51[Ie] rated operational current | IEC61810-1,Rated switching current,
col51maximum switching capacity | Maximum switching voltage,
col51maximum switching capacity | Maximum switching current,
col51maximum switching capacity | Maximum switching capacity,
col51minimum switching capacity | IEC60947-5-4,Minimum switching voltage,
col51minimum switching capacity | IEC60947-5-4,Minimum switching current,
col51minimum switching capacity | IEC60947-5-4,Minimum switching capacity,
col51maximum voltage drop | IEC62314,Only for solid state output,
col51maximum leakage current | IEC62314,Only for solid state output,
col51thermal current | IEC60947-5-1
col51short circuit protection | IEC60947-5-1,Relay Output by external fuse,
col51short circuit protection | IEC62314,Solid State Output by external fuse,
col51
col51time delay type | "OFF" delay,
col51time delay type | "ON" delay,
col51time delay type | Inhibition,
col51time delay range | "OFF" delay,
col51time delay range | "ON" delay,
col51time delay range | Inhibition,
col51response time | on crossing the threshold,
col51response time
col51response time
col51response time
col51response time
col51power on delay
col51reset time | through Un power reset,
col51reset time | through front panel reset,
col51reset time | through input control reset,
col51setting accuracy of time delay
col51repeat accuracy of time delay
col51time delay drift
col51time delay drift
col51
col51status LED
col51local signalling | Power supply availability,
col51local signalling | Power supply not availability,
col51local signalling | Timing in-progress,
col51local signalling | Output is energized,
col51local signalling | Output is de-energized,
col51local signalling | Range Setting Changes,
col51local signalling | Phase Cut,
col51local signalling | Phase Sequence Swap,
col51local signalling | Undervoltage <U,
col51local signalling | Overvoltage >U,
col51local signalling | Phase Asymmetry,
col51local signalling | Voltage Regeneration,
col51local signalling | Extreme Undervoltage <U (Phase loss),
col51local signalling | Extreme Overvoltage >U,
col51local signalling | Extreme Phase Asymmetry,
col51
col51
col51
col51diagnostic button
col51
col51
col51
col51safety reliability data | MTTF,
col51safety reliability data | B10,
col51 | MTTFd,
col51 | B10d,
col51
col51
col52
col52standards
col52product certifications
col52marking
col52directives
col52directives
col52directives
col52
col52 | IEC60721-3-3,Climatic category,
col52 | Germanisher Lloyd,Environmental category,
col52ambient air temperature for storage | Storage,
col52ambient air temperature for operation | Operation,
col52relative humidity | IEC60068-2-30,Damp heat,XX
col52 | IEC60947-5-1,Cyclic Damp Heat Test,
col52vibration resistance | IEC60068-2-6
col52shock resistance | IEC60068-2-27
col52bump resistance | IEC60068-2-29
col52seismic resistance | IEC60068-3-3
col52IP degree of protection | IEC60529,Terminal Block,
col52IP degree of protection | IEC60529,Housing,
col52IP degree of protection | IEC60529,Front Panel,
col52
col52width | Width,
col52height | Height,
col52depth | Depth,
col52net weight
col52mounting support | IEC/EN 60715,Without socket,
col52mounting support | IEC/EN 60715,With socket,
col52mounting position | In relation to normal vertical mounting plane,
col52Minimum distance to adjacent devices | Horizontal,
col52Minimum distance to adjacent devices | Vertical,
col52connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
col52connections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
col52connections - terminals | IEC60947-1,Solid cable (spring terminal),
col52connections - terminals | IEC60947-1,Flexible cable (spring terminal),
col52tightening torque | IEC60947-1,Tightening torque,
col52cable stripping length | Cable stripping length,
col52duty time
col52
col52electromagnetic compatibility | Generic immunity standard,
col52electromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
col52electromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
col52electromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
col52electromagnetic compatibility | IEC61000-4-5,Surge,
col52electromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
col52electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
col52electromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
col52electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
col52electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
col52electromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
col52electromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
col52electromagnetic compatibility | Generic emission standard,
col52electromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
col52electromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
col52electromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
col52electromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
col52electromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
col52electromagnetic compatibility | Germanisher Lloyd,Conducted emission,
col52
col52pollution degree | IEC60664-1
col52overvoltage category | IEC60664-1
col52circuit group | Supply,Terminal
col52circuit group | Input 1,
col52circuit group | Input 2,
col52circuit group | Input 3,
col52circuit group | Output 1,
col52circuit group | Output 2,
col52 | Supply,Rated
col52 | Input 1,Voltage
col52 | Input 2,Spec
col52 | Input 3,
col52 | Output 1,
col52 | Output 2,
col52[Ui] rated insulation voltage | IEC60664-1,Supply,
col52[Ui] rated insulation voltage | IEC60664-1,Input 1,
col52[Ui] rated insulation voltage | IEC60664-1,Input 2,
col52[Ui] rated insulation voltage | IEC60664-1,Input 3,
col52[Ui] rated insulation voltage | IEC60664-1,Output 1,
col52[Ui] rated insulation voltage | IEC60664-1,Output 2,
col52[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
col52[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
col52[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
col52[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
col52[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
col52[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
col52[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
col52[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
col52[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
col52[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
col52[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
col52[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
col52[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
col52[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
col52[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
col52dielectric strength | IEC60255-27,Supply / Input 1,
col52dielectric strength | IEC60255-27,Supply / Input 2,
col52dielectric strength | IEC60255-27,Supply / Input 3,
col52dielectric strength | IEC60255-27,Supply / Output 1,
col52dielectric strength | IEC60255-27,Supply / Output 2,
col52dielectric strength | IEC60255-27,Output 1 / Output 2,
col52dielectric strength | IEC60255-27,Input 1 / Output 1,
col52dielectric strength | IEC60255-27,Input 1 / Output 2,
col52dielectric strength | IEC60255-27,Input 2 / Output 1,
col52dielectric strength | IEC60255-27,Input 2 / Output 2,
col52dielectric strength | IEC60255-27,Input 3 / Output 1,
col52dielectric strength | IEC60255-27,Input 3 / Output 2,
col52dielectric strength | IEC60255-27,Input 1 / Input 2,
col52dielectric strength | IEC60255-27,Input 2 / Input 3,
col52dielectric strength | IEC60255-27,Input 1 / Input 3,
col52insulation resistance | IEC60255-27,Supply / Input 1,
col52insulation resistance | IEC60255-27,Supply / Input 2,
col52insulation resistance | IEC60255-27,Supply / Input 3,
col52insulation resistance | IEC60255-27,Supply / Output 1,
col52insulation resistance | IEC60255-27,Supply / Output 2,
col52insulation resistance | IEC60255-27,Output 1 / Output 2,
col52insulation resistance | IEC60255-27,Input 1 / Output 1,
col52insulation resistance | IEC60255-27,Input 1 / Output 2,
col52insulation resistance | IEC60255-27,Input 2 / Output 1,
col52insulation resistance | IEC60255-27,Input 2 / Output 2,
col52insulation resistance | IEC60255-27,Input 3 / Output 1,
col52insulation resistance | IEC60255-27,Input 3 / Output 2,
col52insulation resistance | IEC60255-27,Input 1 / Input 2,
col52insulation resistance | IEC60255-27,Input 2 / Input 3,
col52insulation resistance | IEC60255-27,Input 1 / Input 3,
col52
col52[Us] rated supply voltage
col52supply voltage limits
col52polarity
col52supply frequency
col52supply frequency
col52power consumption
col52immunity to microbreaks
col52supply terminal
col52on-load factor
col52release of input voltage
col52
col52monitoring functions | Phase lost ,
col52monitoring functions | Phase sequence,
col52monitoring functions | Over / undervoltage (symmetry windows mode),
col52monitoring functions | Over voltage,
col52monitoring functions | Undervoltage ,
col52monitoring functions | Phase asymmetry,
col52monitoring functions | Disconnection of neutral,
col52monitoring functions | Voltage Regeneration,
col52monitoring functions | Extreme undervoltage,
col52monitoring functions | Extreme overvoltage,
col52monitoring functions | Extreme asymmetry,
col52 | Measurement mode,
col52internal input resistance | Internal input resistance,
col52input terminal | Input terminal,
col52Input nominal voltage selection | Input nominal voltage selection,
col52permissible input overload | permissible input overload,
col52input frequency | Rated frequency,
col52input frequency | Frequency operating range,
col52setting accuracy of the switching threshold | Setting accuracy,
col52repeat accuracy of the switching threshold | Repeat accuracy (constant parameters),
col52measurement method | Measurement method,
col52switching threshold drift | Measurement error with supply voltage variation,
col52switching threshold drift | Measurement error with temperature variation,
col52maximum measuring cycle | Maximum measuring cycles,
col52measurement range | Phase lost ,
col52measurement range | Phase sequence,
col52measurement range | Over / undervoltage (symmetry windows mode),
col52measurement range | Over voltage,
col52measurement range | Undervoltage ,
col52measurement range | Phase asymmetry,
col52measurement range | Disconnection of neutral,
col52measurement range | Voltage Regeneration,
col52measurement range | Extreme undervoltage,
col52measurement range | Extreme Overvoltage,
col52measurement range | Extreme Asymmetry,
col52tripping threshold | Phase cut,
col52tripping threshold | Phase sequence,
col52tripping threshold | Over / undervoltage (symmetry windows mode),
col52tripping threshold | Over voltage,
col52tripping threshold | Undervoltage ,
col52tripping threshold | Phase asymmetry,
col52tripping threshold | Disconnection of neutral,
col52tripping threshold | Voltage Regeneration,
col52tripping threshold | Extreme undervoltage (Phase loss),
col52tripping threshold | Extreme Overvoltage,
col52tripping threshold | Extreme Asymmetry,
col52hysteresis | Phase cut,
col52hysteresis | Phase sequence,
col52hysteresis | Over / undervoltage (symmetry windows mode),
col52hysteresis | Over voltage,
col52hysteresis | Undervoltage ,
col52hysteresis | Phase asymmetry,
col52hysteresis | Disconnection of neutral,
col52hysteresis | Voltage Regeneration,
col52hysteresis | Extreme undervoltage (Phase loss),
col52hysteresis | Extreme Overvoltage,
col52hysteresis | Extreme Asymmetry,
col52
col52output type
col52output terminal
col52output logic | R1 (11-12-14),
col52output logic | R2 (21-22-24),
col52contacts material
col52mechanical durability | IEC61810-1
col52electrical durability | IEC60947-4-1,AC-1,
col52electrical durability | IEC60947-4-1,DC-1,
col52electrical durability | IEC60947-5-1,AC-15,
col52electrical durability | IEC60947-5-1,DC-13,
col52[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col52[Ie] rated operational current | IEC61810-1,Rated switching current,
col52maximum switching capacity | Maximum switching voltage,
col52maximum switching capacity | Maximum switching current,
col52maximum switching capacity | Maximum switching capacity,
col52minimum switching capacity | IEC60947-5-4,Minimum switching voltage,
col52minimum switching capacity | IEC60947-5-4,Minimum switching current,
col52minimum switching capacity | IEC60947-5-4,Minimum switching capacity,
col52maximum voltage drop | IEC62314,Only for solid state output,
col52maximum leakage current | IEC62314,Only for solid state output,
col52thermal current | IEC60947-5-1
col52short circuit protection | IEC60947-5-1,Relay Output by external fuse,
col52short circuit protection | IEC62314,Solid State Output by external fuse,
col52
col52time delay type | "OFF" delay,
col52time delay type | "ON" delay,
col52time delay type | Inhibition,
col52time delay range | "OFF" delay,
col52time delay range | "ON" delay,
col52time delay range | Inhibition,
col52response time | on crossing the threshold,
col52response time
col52response time
col52response time
col52response time
col52power on delay
col52reset time | through Un power reset,
col52reset time | through front panel reset,
col52reset time | through input control reset,
col52setting accuracy of time delay
col52repeat accuracy of time delay
col52time delay drift
col52time delay drift
col52
col52status LED
col52local signalling | Power supply availability,
col52local signalling | Power supply not availability,
col52local signalling | Timing in-progress,
col52local signalling | Output is energized,
col52local signalling | Output is de-energized,
col52local signalling | Range Setting Changes,
col52local signalling | Phase Cut,
col52local signalling | Phase Sequence Swap,
col52local signalling | Undervoltage <U,
col52local signalling | Overvoltage >U,
col52local signalling | Phase Asymmetry,
col52local signalling | Voltage Regeneration,
col52local signalling | Extreme Undervoltage <U (Phase loss),
col52local signalling | Extreme Overvoltage >U,
col52local signalling | Extreme Phase Asymmetry,
col52
col52
col52
col52diagnostic button
col52
col52
col52
col52safety reliability data | MTTF,
col52safety reliability data | B10,
col52 | MTTFd,
col52 | B10d,
col52
col52
Competitor Spec Reference
Competitor Spec Referencestandards
Competitor Spec Referenceproduct certifications
Competitor Spec Referencemarking
Competitor Spec Referencedirectives
Competitor Spec Referencedirectives
Competitor Spec Referencedirectives
Competitor Spec Reference
Competitor Spec Reference | IEC60721-3-3,Climatic category,
Competitor Spec Reference | Germanisher Lloyd,Environmental category,
Competitor Spec Referenceambient air temperature for storage | Storage,
Competitor Spec Referenceambient air temperature for operation | Operation,
Competitor Spec Referencerelative humidity | IEC60068-2-30,Damp heat,XX
Competitor Spec Reference | IEC60947-5-1,Cyclic Damp Heat Test,
Competitor Spec Referencevibration resistance | IEC60068-2-6
Competitor Spec Referenceshock resistance | IEC60068-2-27
Competitor Spec Referencebump resistance | IEC60068-2-29
Competitor Spec Referenceseismic resistance | IEC60068-3-3
Competitor Spec ReferenceIP degree of protection | IEC60529,Terminal Block,
Competitor Spec ReferenceIP degree of protection | IEC60529,Housing,
Competitor Spec ReferenceIP degree of protection | IEC60529,Front Panel,
Competitor Spec Reference
Competitor Spec Referencewidth | Width,
Competitor Spec Referenceheight | Height,
Competitor Spec Referencedepth | Depth,
Competitor Spec Referencenet weight
Competitor Spec Referencemounting support | IEC/EN 60715,Without socket,
Competitor Spec Referencemounting support | IEC/EN 60715,With socket,
Competitor Spec Referencemounting position | In relation to normal vertical mounting plane,
Competitor Spec ReferenceMinimum distance to adjacent devices | Horizontal,
Competitor Spec ReferenceMinimum distance to adjacent devices | Vertical,
Competitor Spec Referenceconnections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
Competitor Spec Referenceconnections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
Competitor Spec Referenceconnections - terminals | IEC60947-1,Solid cable (spring terminal),
Competitor Spec Referenceconnections - terminals | IEC60947-1,Flexible cable (spring terminal),
Competitor Spec Referencetightening torque | IEC60947-1,Tightening torque,
Competitor Spec Referencecable stripping length | Cable stripping length,
Competitor Spec Referenceduty time
Competitor Spec Reference
Competitor Spec Referenceelectromagnetic compatibility | Generic immunity standard,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-5,Surge,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
Competitor Spec Referenceelectromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
Competitor Spec Referenceelectromagnetic compatibility | Generic emission standard,
Competitor Spec Referenceelectromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
Competitor Spec Referenceelectromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
Competitor Spec Referenceelectromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
Competitor Spec Referenceelectromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
Competitor Spec Referenceelectromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
Competitor Spec Referenceelectromagnetic compatibility | Germanisher Lloyd,Conducted emission,
Competitor Spec Reference
Competitor Spec Referencepollution degree | IEC60664-1
Competitor Spec Referenceovervoltage category | IEC60664-1
Competitor Spec Referencecircuit group | Supply,Terminal
Competitor Spec Referencecircuit group | Input 1,
Competitor Spec Referencecircuit group | Input 2,
Competitor Spec Referencecircuit group | Input 3,
Competitor Spec Referencecircuit group | Output 1,
Competitor Spec Referencecircuit group | Output 2,
Competitor Spec Reference | Supply,Rated
Competitor Spec Reference | Input 1,Voltage
Competitor Spec Reference | Input 2,Spec
Competitor Spec Reference | Input 3,
Competitor Spec Reference | Output 1,
Competitor Spec Reference | Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 3,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Input 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Input 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Input 3,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Output 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Output 1 / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 1 / Output 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 1 / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 2 / Output 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 2 / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 3 / Output 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 3 / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 1 / Input 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 2 / Input 3,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 1 / Input 3,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Input 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Input 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Input 3,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Output 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Output 1 / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 1 / Output 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 1 / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 2 / Output 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 2 / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 3 / Output 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 3 / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 1 / Input 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 2 / Input 3,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 1 / Input 3,
Competitor Spec Reference
Competitor Spec Reference[Us] rated supply voltage
Competitor Spec Referencesupply voltage limits
Competitor Spec Referencepolarity
Competitor Spec Referencesupply frequency
Competitor Spec Referencesupply frequency
Competitor Spec Referencepower consumption
Competitor Spec Referenceimmunity to microbreaks
Competitor Spec Referencesupply terminal
Competitor Spec Referenceon-load factor
Competitor Spec Referencerelease of input voltage
Competitor Spec Reference
Competitor Spec Referencemonitoring functions | Phase lost ,
Competitor Spec Referencemonitoring functions | Phase sequence,
Competitor Spec Referencemonitoring functions | Over / undervoltage (symmetry windows mode),
Competitor Spec Referencemonitoring functions | Over voltage,
Competitor Spec Referencemonitoring functions | Undervoltage ,
Competitor Spec Referencemonitoring functions | Phase asymmetry,
Competitor Spec Referencemonitoring functions | Disconnection of neutral,
Competitor Spec Referencemonitoring functions | Voltage Regeneration,
Competitor Spec Referencemonitoring functions | Extreme undervoltage,
Competitor Spec Referencemonitoring functions | Extreme overvoltage,
Competitor Spec Referencemonitoring functions | Extreme asymmetry,
Competitor Spec Reference | Measurement mode,
Competitor Spec Referenceinternal input resistance | Internal input resistance,
Competitor Spec Referenceinput terminal | Input terminal,
Competitor Spec ReferenceInput nominal voltage selection | Input nominal voltage selection,
Competitor Spec Referencepermissible input overload | permissible input overload,
Competitor Spec Referenceinput frequency | Rated frequency,
Competitor Spec Referenceinput frequency | Frequency operating range,
Competitor Spec Referencesetting accuracy of the switching threshold | Setting accuracy,
Competitor Spec Referencerepeat accuracy of the switching threshold | Repeat accuracy (constant parameters),
Competitor Spec Referencemeasurement method | Measurement method,
Competitor Spec Referenceswitching threshold drift | Measurement error with supply voltage variation,
Competitor Spec Referenceswitching threshold drift | Measurement error with temperature variation,
Competitor Spec Referencemaximum measuring cycle | Maximum measuring cycles,
Competitor Spec Referencemeasurement range | Phase lost ,
Competitor Spec Referencemeasurement range | Phase sequence,
Competitor Spec Referencemeasurement range | Over / undervoltage (symmetry windows mode),
Competitor Spec Referencemeasurement range | Over voltage,
Competitor Spec Referencemeasurement range | Undervoltage ,
Competitor Spec Referencemeasurement range | Phase asymmetry,
Competitor Spec Referencemeasurement range | Disconnection of neutral,
Competitor Spec Referencemeasurement range | Voltage Regeneration,
Competitor Spec Referencemeasurement range | Extreme undervoltage,
Competitor Spec Referencemeasurement range | Extreme Overvoltage,
Competitor Spec Referencemeasurement range | Extreme Asymmetry,
Competitor Spec Referencetripping threshold | Phase cut,
Competitor Spec Referencetripping threshold | Phase sequence,
Competitor Spec Referencetripping threshold | Over / undervoltage (symmetry windows mode),
Competitor Spec Referencetripping threshold | Over voltage,
Competitor Spec Referencetripping threshold | Undervoltage ,
Competitor Spec Referencetripping threshold | Phase asymmetry,
Competitor Spec Referencetripping threshold | Disconnection of neutral,
Competitor Spec Referencetripping threshold | Voltage Regeneration,
Competitor Spec Referencetripping threshold | Extreme undervoltage (Phase loss),
Competitor Spec Referencetripping threshold | Extreme Overvoltage,
Competitor Spec Referencetripping threshold | Extreme Asymmetry,
Competitor Spec Referencehysteresis | Phase cut,
Competitor Spec Referencehysteresis | Phase sequence,
Competitor Spec Referencehysteresis | Over / undervoltage (symmetry windows mode),
Competitor Spec Referencehysteresis | Over voltage,
Competitor Spec Referencehysteresis | Undervoltage ,
Competitor Spec Referencehysteresis | Phase asymmetry,
Competitor Spec Referencehysteresis | Disconnection of neutral,
Competitor Spec Referencehysteresis | Voltage Regeneration,
Competitor Spec Referencehysteresis | Extreme undervoltage (Phase loss),
Competitor Spec Referencehysteresis | Extreme Overvoltage,
Competitor Spec Referencehysteresis | Extreme Asymmetry,
Competitor Spec Reference
Competitor Spec Referenceoutput type
Competitor Spec Referenceoutput terminal
Competitor Spec Referenceoutput logic | R1 (11-12-14),
Competitor Spec Referenceoutput logic | R2 (21-22-24),
Competitor Spec Referencecontacts material
Competitor Spec Referencemechanical durability | IEC61810-1
Competitor Spec Referenceelectrical durability | IEC60947-4-1,AC-1,
Competitor Spec Referenceelectrical durability | IEC60947-4-1,DC-1,
Competitor Spec Referenceelectrical durability | IEC60947-5-1,AC-15,
Competitor Spec Referenceelectrical durability | IEC60947-5-1,DC-13,
Competitor Spec Reference[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
Competitor Spec Reference[Ie] rated operational current | IEC61810-1,Rated switching current,
Competitor Spec Referencemaximum switching capacity | Maximum switching voltage,
Competitor Spec Referencemaximum switching capacity | Maximum switching current,
Competitor Spec Referencemaximum switching capacity | Maximum switching capacity,
Competitor Spec Referenceminimum switching capacity | IEC60947-5-4,Minimum switching voltage,
Competitor Spec Referenceminimum switching capacity | IEC60947-5-4,Minimum switching current,
Competitor Spec Referenceminimum switching capacity | IEC60947-5-4,Minimum switching capacity,
Competitor Spec Referencemaximum voltage drop | IEC62314,Only for solid state output,
Competitor Spec Referencemaximum leakage current | IEC62314,Only for solid state output,
Competitor Spec Referencethermal current | IEC60947-5-1
Competitor Spec Referenceshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
Competitor Spec Referenceshort circuit protection | IEC62314,Solid State Output by external fuse,
Competitor Spec Reference
Competitor Spec Referencetime delay type | "OFF" delay,
Competitor Spec Referencetime delay type | "ON" delay,
Competitor Spec Referencetime delay type | Inhibition,
Competitor Spec Referencetime delay range | "OFF" delay,
Competitor Spec Referencetime delay range | "ON" delay,
Competitor Spec Referencetime delay range | Inhibition,
Competitor Spec Referenceresponse time | on crossing the threshold,
Competitor Spec Referenceresponse time
Competitor Spec Referenceresponse time
Competitor Spec Referenceresponse time
Competitor Spec Referenceresponse time
Competitor Spec Referencepower on delay
Competitor Spec Referencereset time | through Un power reset,
Competitor Spec Referencereset time | through front panel reset,
Competitor Spec Referencereset time | through input control reset,
Competitor Spec Referencesetting accuracy of time delay
Competitor Spec Referencerepeat accuracy of time delay
Competitor Spec Referencetime delay drift
Competitor Spec Referencetime delay drift
Competitor Spec Reference
Competitor Spec Referencestatus LED
Competitor Spec Referencelocal signalling | Power supply availability,
Competitor Spec Referencelocal signalling | Power supply not availability,
Competitor Spec Referencelocal signalling | Timing in-progress,
Competitor Spec Referencelocal signalling | Output is energized,
Competitor Spec Referencelocal signalling | Output is de-energized,
Competitor Spec Referencelocal signalling | Range Setting Changes,
Competitor Spec Referencelocal signalling | Phase Cut,
Competitor Spec Referencelocal signalling | Phase Sequence Swap,
Competitor Spec Referencelocal signalling | Undervoltage <U,
Competitor Spec Referencelocal signalling | Overvoltage >U,
Competitor Spec Referencelocal signalling | Phase Asymmetry,
Competitor Spec Referencelocal signalling | Voltage Regeneration,
Competitor Spec Referencelocal signalling | Extreme Undervoltage <U (Phase loss),
Competitor Spec Referencelocal signalling | Extreme Overvoltage >U,
Competitor Spec Referencelocal signalling | Extreme Phase Asymmetry,
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Referencediagnostic button
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Referencesafety reliability data | MTTF,
Competitor Spec Referencesafety reliability data | B10,
Competitor Spec Reference | MTTFd,
Competitor Spec Reference | B10d,
Competitor Spec Reference
Competitor Spec Reference
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual)standards | EN60255-1, IEC60255-1
84873034 (Catch-Up Juret - Actual)product certifications | UL, CSA, CE, EAC
84873034 (Catch-Up Juret - Actual)marking | UL, CSA, CE, EAC
84873034 (Catch-Up Juret - Actual)directives | No 73/23/EEC + 93/68/EEC
84873034 (Catch-Up Juret - Actual)directives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
84873034 (Catch-Up Juret - Actual)directives | 2002/95/EC
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual) | Not specified ¦ IEC60721-3-3,Climatic category,
84873034 (Catch-Up Juret - Actual) | Germanisher Lloyd,Environmental category,
84873034 (Catch-Up Juret - Actual)ambient air temperature for storage | -30…+70 ¦ ,Storage,
84873034 (Catch-Up Juret - Actual)ambient air temperature for operation | -20…+50 ¦ ,Operation,
84873034 (Catch-Up Juret - Actual)relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
84873034 (Catch-Up Juret - Actual) | Not specified ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873034 (Catch-Up Juret - Actual)vibration resistance | ±0.35mm from 5Hz…57.6Hz 1g from 57.6Hz..150Hz ¦ IEC60068-2-6
84873034 (Catch-Up Juret - Actual)shock resistance | 15gn - 11ms ¦ IEC60068-2-27
84873034 (Catch-Up Juret - Actual)bump resistance | IEC60068-2-29
84873034 (Catch-Up Juret - Actual)seismic resistance | IEC60068-3-3
84873034 (Catch-Up Juret - Actual)IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
84873034 (Catch-Up Juret - Actual)IP degree of protection | IP40 ¦ IEC60529,Housing,
84873034 (Catch-Up Juret - Actual)IP degree of protection | IP40 ¦ IEC60529,Front Panel,
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual)width | 22.5 x 90 x 73 ¦ ,Width,
84873034 (Catch-Up Juret - Actual)height | Height,
84873034 (Catch-Up Juret - Actual)depth | Depth,
84873034 (Catch-Up Juret - Actual)net weight | ?
84873034 (Catch-Up Juret - Actual)mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
84873034 (Catch-Up Juret - Actual)mounting support | - ¦ IEC/EN 60715,With socket,
84873034 (Catch-Up Juret - Actual)mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
84873034 (Catch-Up Juret - Actual)Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
84873034 (Catch-Up Juret - Actual)Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
84873034 (Catch-Up Juret - Actual)connections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873034 (Catch-Up Juret - Actual)connections - terminals | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873034 (Catch-Up Juret - Actual)connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
84873034 (Catch-Up Juret - Actual)connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
84873034 (Catch-Up Juret - Actual)tightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
84873034 (Catch-Up Juret - Actual)cable stripping length | Not specified ¦ ,Cable stripping length,
84873034 (Catch-Up Juret - Actual)duty time | Not specified
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | Level III (Supply: 2kV, 5kHx / 100kHz) (I/O: 2kV, 5kHx / 100kHz) ¦ IEC61000-4-4,Fast transient / burst,
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge,
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | - ¦ IEC61000-4-8,Power frequency magnetic field,
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | - ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | Class B, Group 2 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | - ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | Class B, Group 2 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual)pollution degree | IEC60664-1
84873034 (Catch-Up Juret - Actual)overvoltage category | IEC60664-1
84873034 (Catch-Up Juret - Actual)circuit group | Supply,Terminal
84873034 (Catch-Up Juret - Actual)circuit group | Input 1,
84873034 (Catch-Up Juret - Actual)circuit group | Input 2,
84873034 (Catch-Up Juret - Actual)circuit group | Input 3,
84873034 (Catch-Up Juret - Actual)circuit group | Output 1,
84873034 (Catch-Up Juret - Actual)circuit group | Output 2,
84873034 (Catch-Up Juret - Actual) | Supply,Rated
84873034 (Catch-Up Juret - Actual) | Input 1,Voltage
84873034 (Catch-Up Juret - Actual) | Input 2,Spec
84873034 (Catch-Up Juret - Actual) | Input 3,
84873034 (Catch-Up Juret - Actual) | Output 1,
84873034 (Catch-Up Juret - Actual) | Output 2,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Supply,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Input 1,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Input 2,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Input 3,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Output 1,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Output 2,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
84873034 (Catch-Up Juret - Actual)dielectric strength | IEC60255-27,Supply / Input 1,
84873034 (Catch-Up Juret - Actual)dielectric strength | IEC60255-27,Supply / Input 2,
84873034 (Catch-Up Juret - Actual)dielectric strength | IEC60255-27,Supply / Input 3,
84873034 (Catch-Up Juret - Actual)dielectric strength | IEC60255-27,Supply / Output 1,
84873034 (Catch-Up Juret - Actual)dielectric strength | IEC60255-27,Supply / Output 2,
84873034 (Catch-Up Juret - Actual)dielectric strength | IEC60255-27,Output 1 / Output 2,
84873034 (Catch-Up Juret - Actual)dielectric strength | IEC60255-27,Input 1 / Output 1,
84873034 (Catch-Up Juret - Actual)dielectric strength | IEC60255-27,Input 1 / Output 2,
84873034 (Catch-Up Juret - Actual)dielectric strength | IEC60255-27,Input 2 / Output 1,
84873034 (Catch-Up Juret - Actual)dielectric strength | IEC60255-27,Input 2 / Output 2,
84873034 (Catch-Up Juret - Actual)dielectric strength | IEC60255-27,Input 3 / Output 1,
84873034 (Catch-Up Juret - Actual)dielectric strength | IEC60255-27,Input 3 / Output 2,
84873034 (Catch-Up Juret - Actual)dielectric strength | IEC60255-27,Input 1 / Input 2,
84873034 (Catch-Up Juret - Actual)dielectric strength | IEC60255-27,Input 2 / Input 3,
84873034 (Catch-Up Juret - Actual)dielectric strength | IEC60255-27,Input 1 / Input 3,
84873034 (Catch-Up Juret - Actual)insulation resistance | IEC60255-27,Supply / Input 1,
84873034 (Catch-Up Juret - Actual)insulation resistance | IEC60255-27,Supply / Input 2,
84873034 (Catch-Up Juret - Actual)insulation resistance | IEC60255-27,Supply / Input 3,
84873034 (Catch-Up Juret - Actual)insulation resistance | IEC60255-27,Supply / Output 1,
84873034 (Catch-Up Juret - Actual)insulation resistance | IEC60255-27,Supply / Output 2,
84873034 (Catch-Up Juret - Actual)insulation resistance | IEC60255-27,Output 1 / Output 2,
84873034 (Catch-Up Juret - Actual)insulation resistance | IEC60255-27,Input 1 / Output 1,
84873034 (Catch-Up Juret - Actual)insulation resistance | IEC60255-27,Input 1 / Output 2,
84873034 (Catch-Up Juret - Actual)insulation resistance | IEC60255-27,Input 2 / Output 1,
84873034 (Catch-Up Juret - Actual)insulation resistance | IEC60255-27,Input 2 / Output 2,
84873034 (Catch-Up Juret - Actual)insulation resistance | IEC60255-27,Input 3 / Output 1,
84873034 (Catch-Up Juret - Actual)insulation resistance | IEC60255-27,Input 3 / Output 2,
84873034 (Catch-Up Juret - Actual)insulation resistance | IEC60255-27,Input 1 / Input 2,
84873034 (Catch-Up Juret - Actual)insulation resistance | IEC60255-27,Input 2 / Input 3,
84873034 (Catch-Up Juret - Actual)insulation resistance | IEC60255-27,Input 1 / Input 3,
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual)[Us] rated supply voltage | ~ 3 x 208…3 x 480
84873034 (Catch-Up Juret - Actual)supply voltage limits | ~ 3 x 183…3 x 528
84873034 (Catch-Up Juret - Actual)polarity
84873034 (Catch-Up Juret - Actual)supply frequency | 50 / 60
84873034 (Catch-Up Juret - Actual)supply frequency | 45…66
84873034 (Catch-Up Juret - Actual)power consumption | 25
84873034 (Catch-Up Juret - Actual)immunity to microbreaks | 10
84873034 (Catch-Up Juret - Actual)supply terminal | L1-L3
84873034 (Catch-Up Juret - Actual)on-load factor
84873034 (Catch-Up Juret - Actual)release of input voltage
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual)monitoring functions | · ¦ ,Phase lost ,
84873034 (Catch-Up Juret - Actual)monitoring functions | · ¦ ,Phase sequence,
84873034 (Catch-Up Juret - Actual)monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
84873034 (Catch-Up Juret - Actual)monitoring functions | - ¦ ,Over voltage,
84873034 (Catch-Up Juret - Actual)monitoring functions | - ¦ ,Undervoltage ,
84873034 (Catch-Up Juret - Actual)monitoring functions | - ¦ ,Phase asymmetry,
84873034 (Catch-Up Juret - Actual)monitoring functions | - ¦ ,Disconnection of neutral,
84873034 (Catch-Up Juret - Actual)monitoring functions | - ¦ ,Voltage Regeneration,
84873034 (Catch-Up Juret - Actual)monitoring functions | Extreme undervoltage,
84873034 (Catch-Up Juret - Actual)monitoring functions | Extreme overvoltage,
84873034 (Catch-Up Juret - Actual)monitoring functions | Extreme asymmetry,
84873034 (Catch-Up Juret - Actual) | Resistive Voltage Step Down ¦ ,Measurement mode,
84873034 (Catch-Up Juret - Actual)internal input resistance | Not specified ¦ ,Internal input resistance,
84873034 (Catch-Up Juret - Actual)input terminal | L1-L2-L3 ¦ ,Input terminal,
84873034 (Catch-Up Juret - Actual)Input nominal voltage selection | Fixed @ ~ 3 x 183…3 x 528 ¦ ,Input nominal voltage selection,
84873034 (Catch-Up Juret - Actual)permissible input overload | Not specified ¦ ,permissible input overload,
84873034 (Catch-Up Juret - Actual)input frequency | 50 / 60 ¦ ,Rated frequency,
84873034 (Catch-Up Juret - Actual)input frequency | 45…66 ¦ ,Frequency operating range,
84873034 (Catch-Up Juret - Actual)setting accuracy of the switching threshold | - ¦ ,Setting accuracy,
84873034 (Catch-Up Juret - Actual)repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
84873034 (Catch-Up Juret - Actual)measurement method | Not specified ¦ ,Measurement method,
84873034 (Catch-Up Juret - Actual)switching threshold drift | < 1% over whole range ¦ ,Measurement error with supply voltage variation,
84873034 (Catch-Up Juret - Actual)switching threshold drift | 0.05% / oC ¦ ,Measurement error with temperature variation,
84873034 (Catch-Up Juret - Actual)maximum measuring cycle | Not specified ¦ ,Maximum measuring cycles,
84873034 (Catch-Up Juret - Actual)measurement range | Fixed value ¦ ,Phase lost ,
84873034 (Catch-Up Juret - Actual)measurement range | Fixed value ¦ ,Phase sequence,
84873034 (Catch-Up Juret - Actual)measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
84873034 (Catch-Up Juret - Actual)measurement range | - ¦ ,Over voltage,
84873034 (Catch-Up Juret - Actual)measurement range | - ¦ ,Undervoltage ,
84873034 (Catch-Up Juret - Actual)measurement range | - ¦ ,Phase asymmetry,
84873034 (Catch-Up Juret - Actual)measurement range | Disconnection of neutral,
84873034 (Catch-Up Juret - Actual)measurement range | Voltage Regeneration,
84873034 (Catch-Up Juret - Actual)measurement range | Extreme undervoltage,
84873034 (Catch-Up Juret - Actual)measurement range | Extreme Overvoltage,
84873034 (Catch-Up Juret - Actual)measurement range | Extreme Asymmetry,
84873034 (Catch-Up Juret - Actual)tripping threshold | (L2-L1) or (L3-L1) or (L2-L3) < 100 ¦ ,Phase cut,
84873034 (Catch-Up Juret - Actual)tripping threshold | (L2-L1) leads (L3-L1) < 10o or (L2-L1) leads (L3-L1) > 150o ¦ ,Phase sequence,
84873034 (Catch-Up Juret - Actual)tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
84873034 (Catch-Up Juret - Actual)tripping threshold | - ¦ ,Over voltage,
84873034 (Catch-Up Juret - Actual)tripping threshold | - ¦ ,Undervoltage ,
84873034 (Catch-Up Juret - Actual)tripping threshold | - ¦ ,Phase asymmetry,
84873034 (Catch-Up Juret - Actual)tripping threshold | Disconnection of neutral,
84873034 (Catch-Up Juret - Actual)tripping threshold | Voltage Regeneration,
84873034 (Catch-Up Juret - Actual)tripping threshold | Extreme undervoltage (Phase loss),
84873034 (Catch-Up Juret - Actual)tripping threshold | Extreme Overvoltage,
84873034 (Catch-Up Juret - Actual)tripping threshold | Extreme Asymmetry,
84873034 (Catch-Up Juret - Actual)hysteresis | - ¦ ,Phase cut,
84873034 (Catch-Up Juret - Actual)hysteresis | (L2-L1) leads (L3-L1) >=15o or (L2-L1) leads (L3-L1) =< 135o ¦ ,Phase sequence,
84873034 (Catch-Up Juret - Actual)hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
84873034 (Catch-Up Juret - Actual)hysteresis | - ¦ ,Over voltage,
84873034 (Catch-Up Juret - Actual)hysteresis | - ¦ ,Undervoltage ,
84873034 (Catch-Up Juret - Actual)hysteresis | - ¦ ,Phase asymmetry,
84873034 (Catch-Up Juret - Actual)hysteresis | Disconnection of neutral,
84873034 (Catch-Up Juret - Actual)hysteresis | Voltage Regeneration,
84873034 (Catch-Up Juret - Actual)hysteresis | Extreme undervoltage (Phase loss),
84873034 (Catch-Up Juret - Actual)hysteresis | Extreme Overvoltage,
84873034 (Catch-Up Juret - Actual)hysteresis | Extreme Asymmetry,
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual)output type | 2 x C/O relay contacts
84873034 (Catch-Up Juret - Actual)output terminal | 11-12-14, 21-22-24
84873034 (Catch-Up Juret - Actual)output logic | Energized on fault-free ¦ ,R1 (11-12-14),
84873034 (Catch-Up Juret - Actual)output logic | R2 (21-22-24),
84873034 (Catch-Up Juret - Actual)contacts material | Cadmium free
84873034 (Catch-Up Juret - Actual)mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
84873034 (Catch-Up Juret - Actual)electrical durability | 1 x 104 switching cycles ¦ IEC60947-4-1,AC-1,
84873034 (Catch-Up Juret - Actual)electrical durability | IEC60947-4-1,DC-1,
84873034 (Catch-Up Juret - Actual)electrical durability | IEC60947-5-1,AC-15,
84873034 (Catch-Up Juret - Actual)electrical durability | IEC60947-5-1,DC-13,
84873034 (Catch-Up Juret - Actual)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
84873034 (Catch-Up Juret - Actual)[Ie] rated operational current | IEC61810-1,Rated switching current,
84873034 (Catch-Up Juret - Actual)maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
84873034 (Catch-Up Juret - Actual)maximum switching capacity | 8 ¦ ,Maximum switching current,
84873034 (Catch-Up Juret - Actual)maximum switching capacity | 2000 ¦ ,Maximum switching capacity,
84873034 (Catch-Up Juret - Actual)minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
84873034 (Catch-Up Juret - Actual)minimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
84873034 (Catch-Up Juret - Actual)minimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
84873034 (Catch-Up Juret - Actual)maximum voltage drop | IEC62314,Only for solid state output,
84873034 (Catch-Up Juret - Actual)maximum leakage current | IEC62314,Only for solid state output,
84873034 (Catch-Up Juret - Actual)thermal current | IEC60947-5-1
84873034 (Catch-Up Juret - Actual)short circuit protection | IEC60947-5-1,Relay Output by external fuse,
84873034 (Catch-Up Juret - Actual)short circuit protection | IEC62314,Solid State Output by external fuse,
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual)time delay type | - ¦ ,"OFF" delay,
84873034 (Catch-Up Juret - Actual)time delay type | - ¦ ,"ON" delay,
84873034 (Catch-Up Juret - Actual)time delay type | - ¦ ,Inhibition,
84873034 (Catch-Up Juret - Actual)time delay range | - ¦ ,"OFF" delay,
84873034 (Catch-Up Juret - Actual)time delay range | - ¦ ,"ON" delay,
84873034 (Catch-Up Juret - Actual)time delay range | - ¦ ,Inhibition,
84873034 (Catch-Up Juret - Actual)response time | 0
84873034 (Catch-Up Juret - Actual)response time
84873034 (Catch-Up Juret - Actual)response time
84873034 (Catch-Up Juret - Actual)response time
84873034 (Catch-Up Juret - Actual)response time
84873034 (Catch-Up Juret - Actual)power on delay | 0
84873034 (Catch-Up Juret - Actual)reset time | - ¦ ,through Un power reset,
84873034 (Catch-Up Juret - Actual)reset time | through front panel reset,
84873034 (Catch-Up Juret - Actual)reset time | through input control reset,
84873034 (Catch-Up Juret - Actual)setting accuracy of time delay | -
84873034 (Catch-Up Juret - Actual)repeat accuracy of time delay | -
84873034 (Catch-Up Juret - Actual)time delay drift | -
84873034 (Catch-Up Juret - Actual)time delay drift | -
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual)status LED
84873034 (Catch-Up Juret - Actual)local signalling | Power supply availability,
84873034 (Catch-Up Juret - Actual)local signalling | Power supply not availability,
84873034 (Catch-Up Juret - Actual)local signalling | Timing in-progress,
84873034 (Catch-Up Juret - Actual)local signalling | Output is energized,
84873034 (Catch-Up Juret - Actual)local signalling | Output is de-energized,
84873034 (Catch-Up Juret - Actual)local signalling | Range Setting Changes,
84873034 (Catch-Up Juret - Actual)local signalling | Phase Cut,
84873034 (Catch-Up Juret - Actual)local signalling | Phase Sequence Swap,
84873034 (Catch-Up Juret - Actual)local signalling | Undervoltage <U,
84873034 (Catch-Up Juret - Actual)local signalling | Overvoltage >U,
84873034 (Catch-Up Juret - Actual)local signalling | Phase Asymmetry,
84873034 (Catch-Up Juret - Actual)local signalling | Voltage Regeneration,
84873034 (Catch-Up Juret - Actual)local signalling | Extreme Undervoltage <U (Phase loss),
84873034 (Catch-Up Juret - Actual)local signalling | Extreme Overvoltage >U,
84873034 (Catch-Up Juret - Actual)local signalling | Extreme Phase Asymmetry,
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual)diagnostic button
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual)safety reliability data | MTTF,
84873034 (Catch-Up Juret - Actual)safety reliability data | B10,
84873034 (Catch-Up Juret - Actual) | MTTFd,
84873034 (Catch-Up Juret - Actual) | B10d,
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - Actual)
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet)standards | EN60255-1, IEC60255-1
84873034 (Catch-Up Juret - For Crouzet)product certifications | UL, CSA, CE, EAC
84873034 (Catch-Up Juret - For Crouzet)marking | UL, CSA, CE, EAC
84873034 (Catch-Up Juret - For Crouzet)directives | No 73/23/EEC + 93/68/EEC
84873034 (Catch-Up Juret - For Crouzet)directives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
84873034 (Catch-Up Juret - For Crouzet)directives | 2002/95/EC
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet) | Not specified ¦ IEC60721-3-3,Climatic category,
84873034 (Catch-Up Juret - For Crouzet) | Germanisher Lloyd,Environmental category,
84873034 (Catch-Up Juret - For Crouzet)ambient air temperature for storage | -30…+70 ¦ ,Storage,
84873034 (Catch-Up Juret - For Crouzet)ambient air temperature for operation | -20…+50 ¦ ,Operation,
84873034 (Catch-Up Juret - For Crouzet)relative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,XX
84873034 (Catch-Up Juret - For Crouzet) | Not specified ¦ IEC60947-5-1,Cyclic Damp Heat Test,
84873034 (Catch-Up Juret - For Crouzet)vibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
84873034 (Catch-Up Juret - For Crouzet)shock resistance | 5 gn ¦ IEC60068-2-27
84873034 (Catch-Up Juret - For Crouzet)bump resistance | IEC60068-2-29
84873034 (Catch-Up Juret - For Crouzet)seismic resistance | IEC60068-3-3
84873034 (Catch-Up Juret - For Crouzet)IP degree of protection | IP40 ¦ IEC60529,Terminal Block,
84873034 (Catch-Up Juret - For Crouzet)IP degree of protection | IP20 ¦ IEC60529,Housing,
84873034 (Catch-Up Juret - For Crouzet)IP degree of protection | Not specified ¦ IEC60529,Front Panel,
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet)width | 22.5 x 90 x 73 ¦ ,Width,
84873034 (Catch-Up Juret - For Crouzet)height | Height,
84873034 (Catch-Up Juret - For Crouzet)depth | Depth,
84873034 (Catch-Up Juret - For Crouzet)net weight | To be updated
84873034 (Catch-Up Juret - For Crouzet)mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
84873034 (Catch-Up Juret - For Crouzet)mounting support | - ¦ IEC/EN 60715,With socket,
84873034 (Catch-Up Juret - For Crouzet)mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
84873034 (Catch-Up Juret - For Crouzet)Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
84873034 (Catch-Up Juret - For Crouzet)Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
84873034 (Catch-Up Juret - For Crouzet)connections - terminals | 1 conductor:0.5…4 2 conductor:0.5…2.5 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873034 (Catch-Up Juret - For Crouzet)connections - terminals | 1 conductor:0.2…2.5 2 conductor:0.2…1.5 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873034 (Catch-Up Juret - For Crouzet)connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
84873034 (Catch-Up Juret - For Crouzet)connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
84873034 (Catch-Up Juret - For Crouzet)tightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
84873034 (Catch-Up Juret - For Crouzet)cable stripping length | Not specified ¦ ,Cable stripping length,
84873034 (Catch-Up Juret - For Crouzet)duty time | Not specified
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard,
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | - ¦ IEC61000-4-8,Power frequency magnetic field,
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | - ¦ IEC61000-4-18,1 MHz oscillation wave,
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet)pollution degree | IEC60664-1
84873034 (Catch-Up Juret - For Crouzet)overvoltage category | IEC60664-1
84873034 (Catch-Up Juret - For Crouzet)circuit group | Supply,Terminal
84873034 (Catch-Up Juret - For Crouzet)circuit group | Input 1,
84873034 (Catch-Up Juret - For Crouzet)circuit group | Input 2,
84873034 (Catch-Up Juret - For Crouzet)circuit group | Input 3,
84873034 (Catch-Up Juret - For Crouzet)circuit group | Output 1,
84873034 (Catch-Up Juret - For Crouzet)circuit group | Output 2,
84873034 (Catch-Up Juret - For Crouzet) | Supply,Rated
84873034 (Catch-Up Juret - For Crouzet) | Input 1,Voltage
84873034 (Catch-Up Juret - For Crouzet) | Input 2,Spec
84873034 (Catch-Up Juret - For Crouzet) | Input 3,
84873034 (Catch-Up Juret - For Crouzet) | Output 1,
84873034 (Catch-Up Juret - For Crouzet) | Output 2,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Supply,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Input 1,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Input 2,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Input 3,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Output 1,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Output 2,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
84873034 (Catch-Up Juret - For Crouzet)dielectric strength | IEC60255-27,Supply / Input 1,
84873034 (Catch-Up Juret - For Crouzet)dielectric strength | IEC60255-27,Supply / Input 2,
84873034 (Catch-Up Juret - For Crouzet)dielectric strength | IEC60255-27,Supply / Input 3,
84873034 (Catch-Up Juret - For Crouzet)dielectric strength | IEC60255-27,Supply / Output 1,
84873034 (Catch-Up Juret - For Crouzet)dielectric strength | IEC60255-27,Supply / Output 2,
84873034 (Catch-Up Juret - For Crouzet)dielectric strength | IEC60255-27,Output 1 / Output 2,
84873034 (Catch-Up Juret - For Crouzet)dielectric strength | IEC60255-27,Input 1 / Output 1,
84873034 (Catch-Up Juret - For Crouzet)dielectric strength | IEC60255-27,Input 1 / Output 2,
84873034 (Catch-Up Juret - For Crouzet)dielectric strength | IEC60255-27,Input 2 / Output 1,
84873034 (Catch-Up Juret - For Crouzet)dielectric strength | IEC60255-27,Input 2 / Output 2,
84873034 (Catch-Up Juret - For Crouzet)dielectric strength | IEC60255-27,Input 3 / Output 1,
84873034 (Catch-Up Juret - For Crouzet)dielectric strength | IEC60255-27,Input 3 / Output 2,
84873034 (Catch-Up Juret - For Crouzet)dielectric strength | IEC60255-27,Input 1 / Input 2,
84873034 (Catch-Up Juret - For Crouzet)dielectric strength | IEC60255-27,Input 2 / Input 3,
84873034 (Catch-Up Juret - For Crouzet)dielectric strength | IEC60255-27,Input 1 / Input 3,
84873034 (Catch-Up Juret - For Crouzet)insulation resistance | IEC60255-27,Supply / Input 1,
84873034 (Catch-Up Juret - For Crouzet)insulation resistance | IEC60255-27,Supply / Input 2,
84873034 (Catch-Up Juret - For Crouzet)insulation resistance | IEC60255-27,Supply / Input 3,
84873034 (Catch-Up Juret - For Crouzet)insulation resistance | IEC60255-27,Supply / Output 1,
84873034 (Catch-Up Juret - For Crouzet)insulation resistance | IEC60255-27,Supply / Output 2,
84873034 (Catch-Up Juret - For Crouzet)insulation resistance | IEC60255-27,Output 1 / Output 2,
84873034 (Catch-Up Juret - For Crouzet)insulation resistance | IEC60255-27,Input 1 / Output 1,
84873034 (Catch-Up Juret - For Crouzet)insulation resistance | IEC60255-27,Input 1 / Output 2,
84873034 (Catch-Up Juret - For Crouzet)insulation resistance | IEC60255-27,Input 2 / Output 1,
84873034 (Catch-Up Juret - For Crouzet)insulation resistance | IEC60255-27,Input 2 / Output 2,
84873034 (Catch-Up Juret - For Crouzet)insulation resistance | IEC60255-27,Input 3 / Output 1,
84873034 (Catch-Up Juret - For Crouzet)insulation resistance | IEC60255-27,Input 3 / Output 2,
84873034 (Catch-Up Juret - For Crouzet)insulation resistance | IEC60255-27,Input 1 / Input 2,
84873034 (Catch-Up Juret - For Crouzet)insulation resistance | IEC60255-27,Input 2 / Input 3,
84873034 (Catch-Up Juret - For Crouzet)insulation resistance | IEC60255-27,Input 1 / Input 3,
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet)[Us] rated supply voltage | ~ 3 x 230…3 x 440
84873034 (Catch-Up Juret - For Crouzet)supply voltage limits | ~ 3 x 207…3 x 484
84873034 (Catch-Up Juret - For Crouzet)polarity
84873034 (Catch-Up Juret - For Crouzet)supply frequency | 50 / 60
84873034 (Catch-Up Juret - For Crouzet)supply frequency | 49…61
84873034 (Catch-Up Juret - For Crouzet)power consumption | 25
84873034 (Catch-Up Juret - For Crouzet)immunity to microbreaks
84873034 (Catch-Up Juret - For Crouzet)supply terminal | L1-L3
84873034 (Catch-Up Juret - For Crouzet)on-load factor | Not specified
84873034 (Catch-Up Juret - For Crouzet)release of input voltage | Not specified
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet)monitoring functions | · ¦ ,Phase lost ,
84873034 (Catch-Up Juret - For Crouzet)monitoring functions | · ¦ ,Phase sequence,
84873034 (Catch-Up Juret - For Crouzet)monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
84873034 (Catch-Up Juret - For Crouzet)monitoring functions | - ¦ ,Over voltage,
84873034 (Catch-Up Juret - For Crouzet)monitoring functions | - ¦ ,Undervoltage ,
84873034 (Catch-Up Juret - For Crouzet)monitoring functions | - ¦ ,Phase asymmetry,
84873034 (Catch-Up Juret - For Crouzet)monitoring functions | - ¦ ,Disconnection of neutral,
84873034 (Catch-Up Juret - For Crouzet)monitoring functions | - ¦ ,Voltage Regeneration,
84873034 (Catch-Up Juret - For Crouzet)monitoring functions | Extreme undervoltage,
84873034 (Catch-Up Juret - For Crouzet)monitoring functions | Extreme overvoltage,
84873034 (Catch-Up Juret - For Crouzet)monitoring functions | Extreme asymmetry,
84873034 (Catch-Up Juret - For Crouzet) | Resistive Voltage Step Down ¦ ,Measurement mode,
84873034 (Catch-Up Juret - For Crouzet)internal input resistance | - ¦ ,Internal input resistance,
84873034 (Catch-Up Juret - For Crouzet)input terminal | L1-L2-L3 ¦ ,Input terminal,
84873034 (Catch-Up Juret - For Crouzet)Input nominal voltage selection | Fixed @ ~ 3 x 230…3 x 440 ¦ ,Input nominal voltage selection,
84873034 (Catch-Up Juret - For Crouzet)permissible input overload | Not specified ¦ ,permissible input overload,
84873034 (Catch-Up Juret - For Crouzet)input frequency | 50 / 60 ¦ ,Rated frequency,
84873034 (Catch-Up Juret - For Crouzet)input frequency | 49…61 ¦ ,Frequency operating range,
84873034 (Catch-Up Juret - For Crouzet)setting accuracy of the switching threshold | - ¦ ,Setting accuracy,
84873034 (Catch-Up Juret - For Crouzet)repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
84873034 (Catch-Up Juret - For Crouzet)measurement method | Not specified ¦ ,Measurement method,
84873034 (Catch-Up Juret - For Crouzet)switching threshold drift | < 1% over whole range ¦ ,Measurement error with supply voltage variation,
84873034 (Catch-Up Juret - For Crouzet)switching threshold drift | 0.05% / oC ¦ ,Measurement error with temperature variation,
84873034 (Catch-Up Juret - For Crouzet)maximum measuring cycle | Not specified ¦ ,Maximum measuring cycles,
84873034 (Catch-Up Juret - For Crouzet)measurement range | - ¦ ,Phase lost ,
84873034 (Catch-Up Juret - For Crouzet)measurement range | - ¦ ,Phase sequence,
84873034 (Catch-Up Juret - For Crouzet)measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
84873034 (Catch-Up Juret - For Crouzet)measurement range | - ¦ ,Over voltage,
84873034 (Catch-Up Juret - For Crouzet)measurement range | - ¦ ,Undervoltage ,
84873034 (Catch-Up Juret - For Crouzet)measurement range | - ¦ ,Phase asymmetry,
84873034 (Catch-Up Juret - For Crouzet)measurement range | Disconnection of neutral,
84873034 (Catch-Up Juret - For Crouzet)measurement range | Voltage Regeneration,
84873034 (Catch-Up Juret - For Crouzet)measurement range | Extreme undervoltage,
84873034 (Catch-Up Juret - For Crouzet)measurement range | Extreme Overvoltage,
84873034 (Catch-Up Juret - For Crouzet)measurement range | Extreme Asymmetry,
84873034 (Catch-Up Juret - For Crouzet)tripping threshold | (L2-L1) or (L3-L1) or (L2-L3) < 100 ¦ ,Phase cut,
84873034 (Catch-Up Juret - For Crouzet)tripping threshold | (L2-L1) leads (L3-L1) < 10o or (L2-L1) leads (L3-L1) > 150o ¦ ,Phase sequence,
84873034 (Catch-Up Juret - For Crouzet)tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
84873034 (Catch-Up Juret - For Crouzet)tripping threshold | - ¦ ,Over voltage,
84873034 (Catch-Up Juret - For Crouzet)tripping threshold | - ¦ ,Undervoltage ,
84873034 (Catch-Up Juret - For Crouzet)tripping threshold | - ¦ ,Phase asymmetry,
84873034 (Catch-Up Juret - For Crouzet)tripping threshold | Disconnection of neutral,
84873034 (Catch-Up Juret - For Crouzet)tripping threshold | Voltage Regeneration,
84873034 (Catch-Up Juret - For Crouzet)tripping threshold | Extreme undervoltage (Phase loss),
84873034 (Catch-Up Juret - For Crouzet)tripping threshold | Extreme Overvoltage,
84873034 (Catch-Up Juret - For Crouzet)tripping threshold | Extreme Asymmetry,
84873034 (Catch-Up Juret - For Crouzet)hysteresis | Not specified ¦ ,Phase cut,
84873034 (Catch-Up Juret - For Crouzet)hysteresis | (L2-L1) leads (L3-L1) >=15o or (L2-L1) leads (L3-L1) =< 135o ¦ ,Phase sequence,
84873034 (Catch-Up Juret - For Crouzet)hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
84873034 (Catch-Up Juret - For Crouzet)hysteresis | - ¦ ,Over voltage,
84873034 (Catch-Up Juret - For Crouzet)hysteresis | - ¦ ,Undervoltage ,
84873034 (Catch-Up Juret - For Crouzet)hysteresis | - ¦ ,Phase asymmetry,
84873034 (Catch-Up Juret - For Crouzet)hysteresis | Disconnection of neutral,
84873034 (Catch-Up Juret - For Crouzet)hysteresis | Voltage Regeneration,
84873034 (Catch-Up Juret - For Crouzet)hysteresis | Extreme undervoltage (Phase loss),
84873034 (Catch-Up Juret - For Crouzet)hysteresis | Extreme Overvoltage,
84873034 (Catch-Up Juret - For Crouzet)hysteresis | Extreme Asymmetry,
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet)output type | 2 x C/O relay contacts
84873034 (Catch-Up Juret - For Crouzet)output terminal | 11-12-14, 21-22-24
84873034 (Catch-Up Juret - For Crouzet)output logic | Energized on fault-free ¦ ,R1 (11-12-14),
84873034 (Catch-Up Juret - For Crouzet)output logic | - ¦ ,R2 (21-22-24),
84873034 (Catch-Up Juret - For Crouzet)contacts material | Cadmium free
84873034 (Catch-Up Juret - For Crouzet)mechanical durability | 20 x 106 switching cycles ¦ IEC61810-1
84873034 (Catch-Up Juret - For Crouzet)electrical durability | 1 x 104 switching cycles ¦ IEC60947-4-1,AC-1,
84873034 (Catch-Up Juret - For Crouzet)electrical durability | IEC60947-4-1,DC-1,
84873034 (Catch-Up Juret - For Crouzet)electrical durability | IEC60947-5-1,AC-15,
84873034 (Catch-Up Juret - For Crouzet)electrical durability | IEC60947-5-1,DC-13,
84873034 (Catch-Up Juret - For Crouzet)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
84873034 (Catch-Up Juret - For Crouzet)[Ie] rated operational current | IEC61810-1,Rated switching current,
84873034 (Catch-Up Juret - For Crouzet)maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
84873034 (Catch-Up Juret - For Crouzet)maximum switching capacity | 8 ¦ ,Maximum switching current,
84873034 (Catch-Up Juret - For Crouzet)maximum switching capacity | 2000 ¦ ,Maximum switching capacity,
84873034 (Catch-Up Juret - For Crouzet)minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
84873034 (Catch-Up Juret - For Crouzet)minimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
84873034 (Catch-Up Juret - For Crouzet)minimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
84873034 (Catch-Up Juret - For Crouzet)maximum voltage drop | - ¦ IEC62314,Only for solid state output,
84873034 (Catch-Up Juret - For Crouzet)maximum leakage current | - ¦ IEC62314,Only for solid state output,
84873034 (Catch-Up Juret - For Crouzet)thermal current | - ¦ IEC60947-5-1
84873034 (Catch-Up Juret - For Crouzet)short circuit protection | - ¦ IEC60947-5-1,Relay Output by external fuse,
84873034 (Catch-Up Juret - For Crouzet)short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet)time delay type | - ¦ ,"OFF" delay,
84873034 (Catch-Up Juret - For Crouzet)time delay type | - ¦ ,"ON" delay,
84873034 (Catch-Up Juret - For Crouzet)time delay type | - ¦ ,Inhibition,
84873034 (Catch-Up Juret - For Crouzet)time delay range | - ¦ ,"OFF" delay,
84873034 (Catch-Up Juret - For Crouzet)time delay range | - ¦ ,"ON" delay,
84873034 (Catch-Up Juret - For Crouzet)time delay range | - ¦ ,Inhibition,
84873034 (Catch-Up Juret - For Crouzet)response time | 0
84873034 (Catch-Up Juret - For Crouzet)response time
84873034 (Catch-Up Juret - For Crouzet)response time
84873034 (Catch-Up Juret - For Crouzet)response time
84873034 (Catch-Up Juret - For Crouzet)response time
84873034 (Catch-Up Juret - For Crouzet)power on delay | 0
84873034 (Catch-Up Juret - For Crouzet)reset time | - ¦ ,through Un power reset,
84873034 (Catch-Up Juret - For Crouzet)reset time | through front panel reset,
84873034 (Catch-Up Juret - For Crouzet)reset time | through input control reset,
84873034 (Catch-Up Juret - For Crouzet)setting accuracy of time delay | -
84873034 (Catch-Up Juret - For Crouzet)repeat accuracy of time delay | -
84873034 (Catch-Up Juret - For Crouzet)time delay drift | -
84873034 (Catch-Up Juret - For Crouzet)time delay drift | -
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet)status LED
84873034 (Catch-Up Juret - For Crouzet)local signalling | Power supply availability,
84873034 (Catch-Up Juret - For Crouzet)local signalling | Power supply not availability,
84873034 (Catch-Up Juret - For Crouzet)local signalling | Timing in-progress,
84873034 (Catch-Up Juret - For Crouzet)local signalling | Output is energized,
84873034 (Catch-Up Juret - For Crouzet)local signalling | Output is de-energized,
84873034 (Catch-Up Juret - For Crouzet)local signalling | Range Setting Changes,
84873034 (Catch-Up Juret - For Crouzet)local signalling | Phase Cut,
84873034 (Catch-Up Juret - For Crouzet)local signalling | Phase Sequence Swap,
84873034 (Catch-Up Juret - For Crouzet)local signalling | Undervoltage <U,
84873034 (Catch-Up Juret - For Crouzet)local signalling | Overvoltage >U,
84873034 (Catch-Up Juret - For Crouzet)local signalling | Phase Asymmetry,
84873034 (Catch-Up Juret - For Crouzet)local signalling | Voltage Regeneration,
84873034 (Catch-Up Juret - For Crouzet)local signalling | Extreme Undervoltage <U (Phase loss),
84873034 (Catch-Up Juret - For Crouzet)local signalling | Extreme Overvoltage >U,
84873034 (Catch-Up Juret - For Crouzet)local signalling | Extreme Phase Asymmetry,
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet)diagnostic button
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet)safety reliability data | MTTF,
84873034 (Catch-Up Juret - For Crouzet)safety reliability data | B10,
84873034 (Catch-Up Juret - For Crouzet) | MTTFd,
84873034 (Catch-Up Juret - For Crouzet) | B10d,
84873034 (Catch-Up Juret - For Crouzet)
84873034 (Catch-Up Juret - For Crouzet)
RM4TR
RM4TRstandards | EN60255-6, IEC60255-6
RM4TRproduct certifications | UL, CSA, GL, C-Tick, GOST
RM4TRmarking | UL, CSA, GL, C-Tick, GOST
RM4TRdirectives | 2006/95/EC
RM4TRdirectives | 2004/108/EC
RM4TRdirectives | 2002/95/EC
RM4TR
RM4TR | 3K3 ¦ IEC60721-3-3,Climatic category,
RM4TR | Germanisher Lloyd,Environmental category,
RM4TRambient air temperature for storage | -40…+85 ¦ ,Storage,
RM4TRambient air temperature for operation | -20…+65 ¦ ,Operation,
RM4TRrelative humidity | 15%...85% ¦ IEC60068-2-30,Damp heat,XX
RM4TR | IEC60947-5-1,Cyclic Damp Heat Test,
RM4TRvibration resistance | a=0.35ms from 10Hz…55Hz ¦ IEC60068-2-6
RM4TRshock resistance | 15 gn ¦ IEC60068-2-27
RM4TRbump resistance | IEC60068-2-29
RM4TRseismic resistance | IEC60068-3-3
RM4TRIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM4TRIP degree of protection | IP50 ¦ IEC60529,Housing,
RM4TRIP degree of protection | Not specified ¦ IEC60529,Front Panel,
RM4TR
RM4TRwidth | 22.5 x 78 x 80 ¦ ,Width,
RM4TRheight | Height,
RM4TRdepth | Depth,
RM4TRnet weight | 110
RM4TRmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM4TRmounting support | - ¦ IEC/EN 60715,With socket,
RM4TRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM4TRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM4TRMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM4TRconnections - terminals | 2 conductor: 2.5 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM4TRconnections - terminals | 2 conductor: 1.5 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM4TRconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM4TRconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4TRtightening torque | 0.6…1.1 ¦ IEC60947-1,Tightening torque,
RM4TRcable stripping length | Not specified ¦ ,Cable stripping length,
RM4TRduty time | Not specified
RM4TR
RM4TRelectromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard,
RM4TRelectromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM4TRelectromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM4TRelectromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM4TRelectromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM4TRelectromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM4TRelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM4TRelectromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM4TRelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM4TRelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM4TRelectromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM4TRelectromagnetic compatibility | ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM4TRelectromagnetic compatibility | IEC50081-1, IEC50081-2 ¦ ,Generic emission standard,
RM4TRelectromagnetic compatibility | Class B Group 1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM4TRelectromagnetic compatibility | Class B Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM4TRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM4TRelectromagnetic compatibility | Class B Group 1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM4TRelectromagnetic compatibility | Class B Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM4TRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4TR
RM4TRpollution degree | IEC60664-1
RM4TRovervoltage category | IEC60664-1
RM4TRcircuit group | Supply,Terminal
RM4TRcircuit group | Input 1,
RM4TRcircuit group | Input 2,
RM4TRcircuit group | Input 3,
RM4TRcircuit group | Output 1,
RM4TRcircuit group | Output 2,
RM4TR | Supply,Rated
RM4TR | Input 1,Voltage
RM4TR | Input 2,Spec
RM4TR | Input 3,
RM4TR | Output 1,
RM4TR | Output 2,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Supply,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Output 1,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4TR[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM4TR[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM4TR[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM4TRdielectric strength | IEC60255-27,Supply / Input 1,
RM4TRdielectric strength | IEC60255-27,Supply / Input 2,
RM4TRdielectric strength | IEC60255-27,Supply / Input 3,
RM4TRdielectric strength | IEC60255-27,Supply / Output 1,
RM4TRdielectric strength | IEC60255-27,Supply / Output 2,
RM4TRdielectric strength | IEC60255-27,Output 1 / Output 2,
RM4TRdielectric strength | IEC60255-27,Input 1 / Output 1,
RM4TRdielectric strength | IEC60255-27,Input 1 / Output 2,
RM4TRdielectric strength | IEC60255-27,Input 2 / Output 1,
RM4TRdielectric strength | IEC60255-27,Input 2 / Output 2,
RM4TRdielectric strength | IEC60255-27,Input 3 / Output 1,
RM4TRdielectric strength | IEC60255-27,Input 3 / Output 2,
RM4TRdielectric strength | IEC60255-27,Input 1 / Input 2,
RM4TRdielectric strength | IEC60255-27,Input 2 / Input 3,
RM4TRdielectric strength | IEC60255-27,Input 1 / Input 3,
RM4TRinsulation resistance | IEC60255-27,Supply / Input 1,
RM4TRinsulation resistance | IEC60255-27,Supply / Input 2,
RM4TRinsulation resistance | IEC60255-27,Supply / Input 3,
RM4TRinsulation resistance | IEC60255-27,Supply / Output 1,
RM4TRinsulation resistance | IEC60255-27,Supply / Output 2,
RM4TRinsulation resistance | IEC60255-27,Output 1 / Output 2,
RM4TRinsulation resistance | IEC60255-27,Input 1 / Output 1,
RM4TRinsulation resistance | IEC60255-27,Input 1 / Output 2,
RM4TRinsulation resistance | IEC60255-27,Input 2 / Output 1,
RM4TRinsulation resistance | IEC60255-27,Input 2 / Output 2,
RM4TRinsulation resistance | IEC60255-27,Input 3 / Output 1,
RM4TRinsulation resistance | IEC60255-27,Input 3 / Output 2,
RM4TRinsulation resistance | IEC60255-27,Input 1 / Input 2,
RM4TRinsulation resistance | IEC60255-27,Input 2 / Input 3,
RM4TRinsulation resistance | IEC60255-27,Input 1 / Input 3,
RM4TR
RM4TR[Us] rated supply voltage | RM4TR31: ~ 3 x 200…3 x 240 RM4TR32: ~ 3 x 300…3 x 500 RM4TR33: ~ 3 x 220 RM4TR33: ~ 3 x 400
RM4TRsupply voltage limits | RM4TR31/33: ~ 3 x 160…3 x 300 RM4TR32/34: ~ 3 x 290…3 x 580
RM4TRpolarity
RM4TRsupply frequency | 50 / 60
RM4TRsupply frequency | 47.5…63
RM4TRpower consumption | Not specified
RM4TRimmunity to microbreaks | Not specified
RM4TRsupply terminal | L1-L2-L3
RM4TRon-load factor
RM4TRrelease of input voltage
RM4TR
RM4TRmonitoring functions | · ¦ ,Phase lost ,
RM4TRmonitoring functions | · ¦ ,Phase sequence,
RM4TRmonitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4TRmonitoring functions | · ¦ ,Over voltage,
RM4TRmonitoring functions | · ¦ ,Undervoltage ,
RM4TRmonitoring functions | - ¦ ,Phase asymmetry,
RM4TRmonitoring functions | - ¦ ,Disconnection of neutral,
RM4TRmonitoring functions | - ¦ ,Voltage Regeneration,
RM4TRmonitoring functions | Extreme undervoltage,
RM4TRmonitoring functions | Extreme overvoltage,
RM4TRmonitoring functions | Extreme asymmetry,
RM4TR | Resistive Voltage Step Down ¦ ,Measurement mode,
RM4TRinternal input resistance | Not specified ¦ ,Internal input resistance,
RM4TRinput terminal | L1-L2-L3 ¦ ,Input terminal,
RM4TRInput nominal voltage selection | RM4TR31/33: ~ 3 x 160…3 x 300 RM4TR32/34: ~ 3 x 290…3 x 580 ¦ ,Input nominal voltage selection,
RM4TRpermissible input overload | Not specified ¦ ,permissible input overload,
RM4TRinput frequency | 50 / 60 ¦ ,Rated frequency,
RM4TRinput frequency | 47.5…63 ¦ ,Frequency operating range,
RM4TRsetting accuracy of the switching threshold | +/- 3% of set value ¦ ,Setting accuracy,
RM4TRrepeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM4TRmeasurement method | Voltage Peak Detection ¦ ,Measurement method,
RM4TRswitching threshold drift | < 0.5% ¦ ,Measurement error with supply voltage variation,
RM4TRswitching threshold drift | =< 0.06% / oC ¦ ,Measurement error with temperature variation,
RM4TRmaximum measuring cycle | 80 ¦ ,Maximum measuring cycles,
RM4TRmeasurement range | Fixed value ¦ ,Phase lost ,
RM4TRmeasurement range | Fixed value ¦ ,Phase sequence,
RM4TRmeasurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4TRmeasurement range | RM4TR31: ~ 3 x 160…3 x 300 RM4TR32: ~ 3 x 420…3 x 480 RM4TR33: ~ 3 x 198 RM4TR34: ~ 3 x 360 ¦ ,Over voltage,
RM4TRmeasurement range | RM4TR31: ~ 3 x 220…3 x 300 RM4TR32: ~ 3 x 300…3 x 430 RM4TR33: ~ 3 x 242 RM4TR34: ~ 3 x 440 ¦ ,Undervoltage ,
RM4TRmeasurement range | - ¦ ,Phase asymmetry,
RM4TRmeasurement range | Disconnection of neutral,
RM4TRmeasurement range | Voltage Regeneration,
RM4TRmeasurement range | Extreme undervoltage,
RM4TRmeasurement range | Extreme Overvoltage,
RM4TRmeasurement range | Extreme Asymmetry,
RM4TRtripping threshold | RM4TR32: (L2-L1) or (L3-L1) or (L2-L3) < 290 or Differences of (L2-L1) / (L3-L1) /(L2-L3) > 105V Other: Unknown ¦ ,Phase cut,
RM4TRtripping threshold | Total swap of phase ¦ ,Phase sequence,
RM4TRtripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4TRtripping threshold | Adjustable within measurement range ¦ ,Over voltage,
RM4TRtripping threshold | Adjustable within measurement range ¦ ,Undervoltage ,
RM4TRtripping threshold | - ¦ ,Phase asymmetry,
RM4TRtripping threshold | Disconnection of neutral,
RM4TRtripping threshold | Voltage Regeneration,
RM4TRtripping threshold | Extreme undervoltage (Phase loss),
RM4TRtripping threshold | Extreme Overvoltage,
RM4TRtripping threshold | Extreme Asymmetry,
RM4TRhysteresis | - ¦ ,Phase cut,
RM4TRhysteresis | - ¦ ,Phase sequence,
RM4TRhysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4TRhysteresis | Fixed 5% of de-energization threshold ¦ ,Over voltage,
RM4TRhysteresis | Fixed 5% of de-energization threshold ¦ ,Undervoltage ,
RM4TRhysteresis | - ¦ ,Phase asymmetry,
RM4TRhysteresis | Disconnection of neutral,
RM4TRhysteresis | Voltage Regeneration,
RM4TRhysteresis | Extreme undervoltage (Phase loss),
RM4TRhysteresis | Extreme Overvoltage,
RM4TRhysteresis | Extreme Asymmetry,
RM4TR
RM4TRoutput type | 2 x C/O relay contacts
RM4TRoutput terminal | 15-16-18, 25-26-28
RM4TRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM4TRoutput logic | R2 (21-22-24),
RM4TRcontacts material | 90/10 Nickel Silver
RM4TRmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM4TRelectrical durability | Not specified ¦ IEC60947-4-1,AC-1,
RM4TRelectrical durability | IEC60947-4-1,DC-1,
RM4TRelectrical durability | IEC60947-5-1,AC-15,
RM4TRelectrical durability | IEC60947-5-1,DC-13,
RM4TR[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4TR[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4TRmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM4TRmaximum switching capacity | 8 ¦ ,Maximum switching current,
RM4TRmaximum switching capacity | 2000 ¦ ,Maximum switching capacity,
RM4TRminimum switching capacity | 12 ¦ IEC60947-5-4,Minimum switching voltage,
RM4TRminimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM4TRminimum switching capacity | 120 ¦ IEC60947-5-4,Minimum switching capacity,
RM4TRmaximum voltage drop | IEC62314,Only for solid state output,
RM4TRmaximum leakage current | IEC62314,Only for solid state output,
RM4TRthermal current | IEC60947-5-1
RM4TRshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM4TRshort circuit protection | IEC62314,Solid State Output by external fuse,
RM4TR
RM4TRtime delay type | · ¦ ,"OFF" delay,
RM4TRtime delay type | · ¦ ,"ON" delay,
RM4TRtime delay type | - ¦ ,Inhibition,
RM4TRtime delay range | Adjustable 0.1…10 ¦ ,"OFF" delay,
RM4TRtime delay range | - ¦ ,"ON" delay,
RM4TRtime delay range | - ¦ ,Inhibition,
RM4TRresponse time | Not specified ¦ ,on crossing the threshold,
RM4TRresponse time
RM4TRresponse time
RM4TRresponse time
RM4TRresponse time
RM4TRpower on delay | Not specified
RM4TRreset time | Not specified ¦ ,through Un power reset,
RM4TRreset time | through front panel reset,
RM4TRreset time | through input control reset,
RM4TRsetting accuracy of time delay | +/- 10% of full scales value
RM4TRrepeat accuracy of time delay | Not specified
RM4TRtime delay drift | < 0.5%
RM4TRtime delay drift | =< 0.07% / oC
RM4TR
RM4TRstatus LED
RM4TRlocal signalling | Power supply availability,
RM4TRlocal signalling | Power supply not availability,
RM4TRlocal signalling | Timing in-progress,
RM4TRlocal signalling | Output is energized,
RM4TRlocal signalling | Output is de-energized,
RM4TRlocal signalling | Range Setting Changes,
RM4TRlocal signalling | Phase Cut,
RM4TRlocal signalling | Phase Sequence Swap,
RM4TRlocal signalling | Undervoltage <U,
RM4TRlocal signalling | Overvoltage >U,
RM4TRlocal signalling | Phase Asymmetry,
RM4TRlocal signalling | Voltage Regeneration,
RM4TRlocal signalling | Extreme Undervoltage <U (Phase loss),
RM4TRlocal signalling | Extreme Overvoltage >U,
RM4TRlocal signalling | Extreme Phase Asymmetry,
RM4TR
RM4TR
RM4TR
RM4TRdiagnostic button
RM4TR
RM4TR
RM4TR
RM4TRsafety reliability data | MTTF,
RM4TRsafety reliability data | B10,
RM4TR | MTTFd,
RM4TR | B10d,
RM4TR
RM4TR
RM4TG20
RM4TG20standards | EN60255-6, IEC60255-6
RM4TG20product certifications | UL, CSA, GL, C-Tick, GOST
RM4TG20marking | UL, CSA, GL, C-Tick, GOST
RM4TG20directives | 2006/95/EC
RM4TG20directives | 2004/108/EC
RM4TG20directives | 2002/95/EC
RM4TG20
RM4TG20 | 3K3 ¦ IEC60721-3-3,Climatic category,
RM4TG20 | Germanisher Lloyd,Environmental category,
RM4TG20ambient air temperature for storage | -40…+85 ¦ ,Storage,
RM4TG20ambient air temperature for operation | -20…+65 ¦ ,Operation,
RM4TG20relative humidity | 15%...85% ¦ IEC60068-2-30,Damp heat,XX
RM4TG20 | IEC60947-5-1,Cyclic Damp Heat Test,
RM4TG20vibration resistance | a=0.35ms from 10Hz…55Hz ¦ IEC60068-2-6
RM4TG20shock resistance | 15 gn ¦ IEC60068-2-27
RM4TG20bump resistance | IEC60068-2-29
RM4TG20seismic resistance | IEC60068-3-3
RM4TG20IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM4TG20IP degree of protection | IP50 ¦ IEC60529,Housing,
RM4TG20IP degree of protection | Not specified ¦ IEC60529,Front Panel,
RM4TG20
RM4TG20width | 22.5 x 78 x 80 ¦ ,Width,
RM4TG20height | Height,
RM4TG20depth | Depth,
RM4TG20net weight | 110
RM4TG20mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM4TG20mounting support | - ¦ IEC/EN 60715,With socket,
RM4TG20mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM4TG20Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM4TG20Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM4TG20connections - terminals | 2 conductor: 2.5 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM4TG20connections - terminals | 2 conductor: 1.5 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM4TG20connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM4TG20connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4TG20tightening torque | 0.6…1.1 ¦ IEC60947-1,Tightening torque,
RM4TG20cable stripping length | Not specified ¦ ,Cable stripping length,
RM4TG20duty time | Not specified
RM4TG20
RM4TG20electromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard,
RM4TG20electromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM4TG20electromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM4TG20electromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM4TG20electromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM4TG20electromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM4TG20electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM4TG20electromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM4TG20electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM4TG20electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM4TG20electromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM4TG20electromagnetic compatibility | ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM4TG20electromagnetic compatibility | IEC50081-1, IEC50081-2 ¦ ,Generic emission standard,
RM4TG20electromagnetic compatibility | Class B Group 1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM4TG20electromagnetic compatibility | Class B Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM4TG20electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM4TG20electromagnetic compatibility | Class B Group 1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM4TG20electromagnetic compatibility | Class B Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM4TG20electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4TG20
RM4TG20pollution degree | IEC60664-1
RM4TG20overvoltage category | IEC60664-1
RM4TG20circuit group | Supply,Terminal
RM4TG20circuit group | Input 1,
RM4TG20circuit group | Input 2,
RM4TG20circuit group | Input 3,
RM4TG20circuit group | Output 1,
RM4TG20circuit group | Output 2,
RM4TG20 | Supply,Rated
RM4TG20 | Input 1,Voltage
RM4TG20 | Input 2,Spec
RM4TG20 | Input 3,
RM4TG20 | Output 1,
RM4TG20 | Output 2,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Supply,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Output 1,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM4TG20dielectric strength | IEC60255-27,Supply / Input 1,
RM4TG20dielectric strength | IEC60255-27,Supply / Input 2,
RM4TG20dielectric strength | IEC60255-27,Supply / Input 3,
RM4TG20dielectric strength | IEC60255-27,Supply / Output 1,
RM4TG20dielectric strength | IEC60255-27,Supply / Output 2,
RM4TG20dielectric strength | IEC60255-27,Output 1 / Output 2,
RM4TG20dielectric strength | IEC60255-27,Input 1 / Output 1,
RM4TG20dielectric strength | IEC60255-27,Input 1 / Output 2,
RM4TG20dielectric strength | IEC60255-27,Input 2 / Output 1,
RM4TG20dielectric strength | IEC60255-27,Input 2 / Output 2,
RM4TG20dielectric strength | IEC60255-27,Input 3 / Output 1,
RM4TG20dielectric strength | IEC60255-27,Input 3 / Output 2,
RM4TG20dielectric strength | IEC60255-27,Input 1 / Input 2,
RM4TG20dielectric strength | IEC60255-27,Input 2 / Input 3,
RM4TG20dielectric strength | IEC60255-27,Input 1 / Input 3,
RM4TG20insulation resistance | IEC60255-27,Supply / Input 1,
RM4TG20insulation resistance | IEC60255-27,Supply / Input 2,
RM4TG20insulation resistance | IEC60255-27,Supply / Input 3,
RM4TG20insulation resistance | IEC60255-27,Supply / Output 1,
RM4TG20insulation resistance | IEC60255-27,Supply / Output 2,
RM4TG20insulation resistance | IEC60255-27,Output 1 / Output 2,
RM4TG20insulation resistance | IEC60255-27,Input 1 / Output 1,
RM4TG20insulation resistance | IEC60255-27,Input 1 / Output 2,
RM4TG20insulation resistance | IEC60255-27,Input 2 / Output 1,
RM4TG20insulation resistance | IEC60255-27,Input 2 / Output 2,
RM4TG20insulation resistance | IEC60255-27,Input 3 / Output 1,
RM4TG20insulation resistance | IEC60255-27,Input 3 / Output 2,
RM4TG20insulation resistance | IEC60255-27,Input 1 / Input 2,
RM4TG20insulation resistance | IEC60255-27,Input 2 / Input 3,
RM4TG20insulation resistance | IEC60255-27,Input 1 / Input 3,
RM4TG20
RM4TG20[Us] rated supply voltage | ~ 3 x 200…3 x 500
RM4TG20supply voltage limits | ~ 3 x 140…3 x 580
RM4TG20polarity
RM4TG20supply frequency | 50 / 60
RM4TG20supply frequency | 47.5…63
RM4TG20power consumption | Not specified
RM4TG20immunity to microbreaks | Not specified
RM4TG20supply terminal | L1-L2-L3
RM4TG20on-load factor
RM4TG20release of input voltage
RM4TG20
RM4TG20monitoring functions | · ¦ ,Phase lost ,
RM4TG20monitoring functions | · ¦ ,Phase sequence,
RM4TG20monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4TG20monitoring functions | - ¦ ,Over voltage,
RM4TG20monitoring functions | - ¦ ,Undervoltage ,
RM4TG20monitoring functions | - ¦ ,Phase asymmetry,
RM4TG20monitoring functions | - ¦ ,Disconnection of neutral,
RM4TG20monitoring functions | - ¦ ,Voltage Regeneration,
RM4TG20monitoring functions | Extreme undervoltage,
RM4TG20monitoring functions | Extreme overvoltage,
RM4TG20monitoring functions | Extreme asymmetry,
RM4TG20 | Resistive Voltage Step Down ¦ ,Measurement mode,
RM4TG20internal input resistance | Not specified ¦ ,Internal input resistance,
RM4TG20input terminal | L1-L2-L3 ¦ ,Input terminal,
RM4TG20Input nominal voltage selection | Fixed @ ~ 3 x 140…3 x 580 ¦ ,Input nominal voltage selection,
RM4TG20permissible input overload | Not specified ¦ ,permissible input overload,
RM4TG20input frequency | 50 / 60 ¦ ,Rated frequency,
RM4TG20input frequency | 47.5…63 ¦ ,Frequency operating range,
RM4TG20setting accuracy of the switching threshold | +/- 3% of set value ¦ ,Setting accuracy,
RM4TG20repeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM4TG20measurement method | Voltage Peak Detection ¦ ,Measurement method,
RM4TG20switching threshold drift | < 0.5% ¦ ,Measurement error with supply voltage variation,
RM4TG20switching threshold drift | =< 0.06% / oC ¦ ,Measurement error with temperature variation,
RM4TG20maximum measuring cycle | 80 ¦ ,Maximum measuring cycles,
RM4TG20measurement range | Fixed value ¦ ,Phase lost ,
RM4TG20measurement range | Fixed value ¦ ,Phase sequence,
RM4TG20measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4TG20measurement range | - ¦ ,Over voltage,
RM4TG20measurement range | - ¦ ,Undervoltage ,
RM4TG20measurement range | - ¦ ,Phase asymmetry,
RM4TG20measurement range | Disconnection of neutral,
RM4TG20measurement range | Voltage Regeneration,
RM4TG20measurement range | Extreme undervoltage,
RM4TG20measurement range | Extreme Overvoltage,
RM4TG20measurement range | Extreme Asymmetry,
RM4TG20tripping threshold | Unknown ¦ ,Phase cut,
RM4TG20tripping threshold | Total swap of phase ¦ ,Phase sequence,
RM4TG20tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4TG20tripping threshold | - ¦ ,Over voltage,
RM4TG20tripping threshold | - ¦ ,Undervoltage ,
RM4TG20tripping threshold | - ¦ ,Phase asymmetry,
RM4TG20tripping threshold | Disconnection of neutral,
RM4TG20tripping threshold | Voltage Regeneration,
RM4TG20tripping threshold | Extreme undervoltage (Phase loss),
RM4TG20tripping threshold | Extreme Overvoltage,
RM4TG20tripping threshold | Extreme Asymmetry,
RM4TG20hysteresis | - ¦ ,Phase cut,
RM4TG20hysteresis | - ¦ ,Phase sequence,
RM4TG20hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4TG20hysteresis | Fixed 5% of de-energization threshold ¦ ,Over voltage,
RM4TG20hysteresis | Fixed 5% of de-energization threshold ¦ ,Undervoltage ,
RM4TG20hysteresis | - ¦ ,Phase asymmetry,
RM4TG20hysteresis | Disconnection of neutral,
RM4TG20hysteresis | Voltage Regeneration,
RM4TG20hysteresis | Extreme undervoltage (Phase loss),
RM4TG20hysteresis | Extreme Overvoltage,
RM4TG20hysteresis | Extreme Asymmetry,
RM4TG20
RM4TG20output type | 2 x C/O relay contacts
RM4TG20output terminal | 15-16-18, 25-26-28
RM4TG20output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM4TG20output logic | R2 (21-22-24),
RM4TG20contacts material | 90/10 Nickel Silver
RM4TG20mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM4TG20electrical durability | Not specified ¦ IEC60947-4-1,AC-1,
RM4TG20electrical durability | IEC60947-4-1,DC-1,
RM4TG20electrical durability | IEC60947-5-1,AC-15,
RM4TG20electrical durability | IEC60947-5-1,DC-13,
RM4TG20[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4TG20[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4TG20maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM4TG20maximum switching capacity | 8 ¦ ,Maximum switching current,
RM4TG20maximum switching capacity | 2000 ¦ ,Maximum switching capacity,
RM4TG20minimum switching capacity | 12 ¦ IEC60947-5-4,Minimum switching voltage,
RM4TG20minimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM4TG20minimum switching capacity | 120 ¦ IEC60947-5-4,Minimum switching capacity,
RM4TG20maximum voltage drop | IEC62314,Only for solid state output,
RM4TG20maximum leakage current | IEC62314,Only for solid state output,
RM4TG20thermal current | IEC60947-5-1
RM4TG20short circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM4TG20short circuit protection | IEC62314,Solid State Output by external fuse,
RM4TG20
RM4TG20time delay type | · ¦ ,"OFF" delay,
RM4TG20time delay type | · ¦ ,"ON" delay,
RM4TG20time delay type | - ¦ ,Inhibition,
RM4TG20time delay range | Adjustable 0.1…10 ¦ ,"OFF" delay,
RM4TG20time delay range | - ¦ ,"ON" delay,
RM4TG20time delay range | - ¦ ,Inhibition,
RM4TG20response time | Not specified ¦ ,on crossing the threshold,
RM4TG20response time
RM4TG20response time
RM4TG20response time
RM4TG20response time
RM4TG20power on delay | Not specified
RM4TG20reset time | Not specified ¦ ,through Un power reset,
RM4TG20reset time | through front panel reset,
RM4TG20reset time | through input control reset,
RM4TG20setting accuracy of time delay | +/- 10% of full scales value
RM4TG20repeat accuracy of time delay | Not specified
RM4TG20time delay drift | < 0.5%
RM4TG20time delay drift | =< 0.07% / oC
RM4TG20
RM4TG20status LED
RM4TG20local signalling | Power supply availability,
RM4TG20local signalling | Power supply not availability,
RM4TG20local signalling | Timing in-progress,
RM4TG20local signalling | Output is energized,
RM4TG20local signalling | Output is de-energized,
RM4TG20local signalling | Range Setting Changes,
RM4TG20local signalling | Phase Cut,
RM4TG20local signalling | Phase Sequence Swap,
RM4TG20local signalling | Undervoltage <U,
RM4TG20local signalling | Overvoltage >U,
RM4TG20local signalling | Phase Asymmetry,
RM4TG20local signalling | Voltage Regeneration,
RM4TG20local signalling | Extreme Undervoltage <U (Phase loss),
RM4TG20local signalling | Extreme Overvoltage >U,
RM4TG20local signalling | Extreme Phase Asymmetry,
RM4TG20
RM4TG20
RM4TG20
RM4TG20diagnostic button
RM4TG20
RM4TG20
RM4TG20
RM4TG20safety reliability data | MTTF,
RM4TG20safety reliability data | B10,
RM4TG20 | MTTFd,
RM4TG20 | B10d,
RM4TG20
RM4TG20
RM4TU
RM4TUstandards | EN60255-6, IEC60255-6
RM4TUproduct certifications | UL, CSA, GL, C-Tick, GOST
RM4TUmarking | UL, CSA, GL, C-Tick, GOST
RM4TUdirectives | 2006/95/EC
RM4TUdirectives | 2004/108/EC
RM4TUdirectives | 2002/95/EC
RM4TU
RM4TU | 3K3 ¦ IEC60721-3-3,Climatic category,
RM4TU | Germanisher Lloyd,Environmental category,
RM4TUambient air temperature for storage | -40…+85 ¦ ,Storage,
RM4TUambient air temperature for operation | -20…+65 ¦ ,Operation,
RM4TUrelative humidity | 15%...85% ¦ IEC60068-2-30,Damp heat,XX
RM4TU | IEC60947-5-1,Cyclic Damp Heat Test,
RM4TUvibration resistance | a=0.35ms from 10Hz…55Hz ¦ IEC60068-2-6
RM4TUshock resistance | 15 gn ¦ IEC60068-2-27
RM4TUbump resistance | IEC60068-2-29
RM4TUseismic resistance | IEC60068-3-3
RM4TUIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM4TUIP degree of protection | IP50 ¦ IEC60529,Housing,
RM4TUIP degree of protection | Not specified ¦ IEC60529,Front Panel,
RM4TU
RM4TUwidth | 22.5 x 78 x 80 ¦ ,Width,
RM4TUheight | Height,
RM4TUdepth | Depth,
RM4TUnet weight | 110
RM4TUmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM4TUmounting support | - ¦ IEC/EN 60715,With socket,
RM4TUmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM4TUMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM4TUMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM4TUconnections - terminals | 2 conductor: 2.5 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM4TUconnections - terminals | 2 conductor: 1.5 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM4TUconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM4TUconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4TUtightening torque | 0.6…1.1 ¦ IEC60947-1,Tightening torque,
RM4TUcable stripping length | Not specified ¦ ,Cable stripping length,
RM4TUduty time | Not specified
RM4TU
RM4TUelectromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard,
RM4TUelectromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM4TUelectromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM4TUelectromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM4TUelectromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM4TUelectromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM4TUelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM4TUelectromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM4TUelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM4TUelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM4TUelectromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM4TUelectromagnetic compatibility | ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM4TUelectromagnetic compatibility | IEC50081-1, IEC50081-2 ¦ ,Generic emission standard,
RM4TUelectromagnetic compatibility | Class B Group 1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM4TUelectromagnetic compatibility | Class B Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM4TUelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM4TUelectromagnetic compatibility | Class B Group 1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM4TUelectromagnetic compatibility | Class B Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM4TUelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4TU
RM4TUpollution degree | IEC60664-1
RM4TUovervoltage category | IEC60664-1
RM4TUcircuit group | Supply,Terminal
RM4TUcircuit group | Input 1,
RM4TUcircuit group | Input 2,
RM4TUcircuit group | Input 3,
RM4TUcircuit group | Output 1,
RM4TUcircuit group | Output 2,
RM4TU | Supply,Rated
RM4TU | Input 1,Voltage
RM4TU | Input 2,Spec
RM4TU | Input 3,
RM4TU | Output 1,
RM4TU | Output 2,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Supply,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Output 1,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4TU[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM4TU[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM4TU[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM4TUdielectric strength | IEC60255-27,Supply / Input 1,
RM4TUdielectric strength | IEC60255-27,Supply / Input 2,
RM4TUdielectric strength | IEC60255-27,Supply / Input 3,
RM4TUdielectric strength | IEC60255-27,Supply / Output 1,
RM4TUdielectric strength | IEC60255-27,Supply / Output 2,
RM4TUdielectric strength | IEC60255-27,Output 1 / Output 2,
RM4TUdielectric strength | IEC60255-27,Input 1 / Output 1,
RM4TUdielectric strength | IEC60255-27,Input 1 / Output 2,
RM4TUdielectric strength | IEC60255-27,Input 2 / Output 1,
RM4TUdielectric strength | IEC60255-27,Input 2 / Output 2,
RM4TUdielectric strength | IEC60255-27,Input 3 / Output 1,
RM4TUdielectric strength | IEC60255-27,Input 3 / Output 2,
RM4TUdielectric strength | IEC60255-27,Input 1 / Input 2,
RM4TUdielectric strength | IEC60255-27,Input 2 / Input 3,
RM4TUdielectric strength | IEC60255-27,Input 1 / Input 3,
RM4TUinsulation resistance | IEC60255-27,Supply / Input 1,
RM4TUinsulation resistance | IEC60255-27,Supply / Input 2,
RM4TUinsulation resistance | IEC60255-27,Supply / Input 3,
RM4TUinsulation resistance | IEC60255-27,Supply / Output 1,
RM4TUinsulation resistance | IEC60255-27,Supply / Output 2,
RM4TUinsulation resistance | IEC60255-27,Output 1 / Output 2,
RM4TUinsulation resistance | IEC60255-27,Input 1 / Output 1,
RM4TUinsulation resistance | IEC60255-27,Input 1 / Output 2,
RM4TUinsulation resistance | IEC60255-27,Input 2 / Output 1,
RM4TUinsulation resistance | IEC60255-27,Input 2 / Output 2,
RM4TUinsulation resistance | IEC60255-27,Input 3 / Output 1,
RM4TUinsulation resistance | IEC60255-27,Input 3 / Output 2,
RM4TUinsulation resistance | IEC60255-27,Input 1 / Input 2,
RM4TUinsulation resistance | IEC60255-27,Input 2 / Input 3,
RM4TUinsulation resistance | IEC60255-27,Input 1 / Input 3,
RM4TU
RM4TU[Us] rated supply voltage | RM4TU01: ~ 3 x 200…3 x 240 RM4TU02: ~ 3 x 380…3 x 500
RM4TUsupply voltage limits | RM4TU01: ~ 3 x 160…3 x 300 RM4TU01: ~ 3 x 290…3 x 580
RM4TUpolarity
RM4TUsupply frequency | 50 / 60
RM4TUsupply frequency | 47.5…63
RM4TUpower consumption | Not specified
RM4TUimmunity to microbreaks | Not specified
RM4TUsupply terminal | L1-L2-L3
RM4TUon-load factor
RM4TUrelease of input voltage
RM4TU
RM4TUmonitoring functions | · ¦ ,Phase lost ,
RM4TUmonitoring functions | · ¦ ,Phase sequence,
RM4TUmonitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4TUmonitoring functions | - ¦ ,Over voltage,
RM4TUmonitoring functions | · ¦ ,Undervoltage ,
RM4TUmonitoring functions | - ¦ ,Phase asymmetry,
RM4TUmonitoring functions | - ¦ ,Disconnection of neutral,
RM4TUmonitoring functions | - ¦ ,Voltage Regeneration,
RM4TUmonitoring functions | Extreme undervoltage,
RM4TUmonitoring functions | Extreme overvoltage,
RM4TUmonitoring functions | Extreme asymmetry,
RM4TU | Resistive Voltage Step Down ¦ ,Measurement mode,
RM4TUinternal input resistance | Not specified ¦ ,Internal input resistance,
RM4TUinput terminal | L1-L2-L3 ¦ ,Input terminal,
RM4TUInput nominal voltage selection | RM4TU01: ~ 3 x 160…3 x 300 RM4TU01: ~ 3 x 290…3 x 580 ¦ ,Input nominal voltage selection,
RM4TUpermissible input overload | Not specified ¦ ,permissible input overload,
RM4TUinput frequency | 50 / 60 ¦ ,Rated frequency,
RM4TUinput frequency | 47.5…63 ¦ ,Frequency operating range,
RM4TUsetting accuracy of the switching threshold | +/- 3% of set value ¦ ,Setting accuracy,
RM4TUrepeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM4TUmeasurement method | Voltage Peak Detection ¦ ,Measurement method,
RM4TUswitching threshold drift | < 0.5% ¦ ,Measurement error with supply voltage variation,
RM4TUswitching threshold drift | =< 0.06% / oC ¦ ,Measurement error with temperature variation,
RM4TUmaximum measuring cycle | 80 ¦ ,Maximum measuring cycles,
RM4TUmeasurement range | Fixed value ¦ ,Phase lost ,
RM4TUmeasurement range | Fixed value ¦ ,Phase sequence,
RM4TUmeasurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4TUmeasurement range | - ¦ ,Over voltage,
RM4TUmeasurement range | RM4TU01: ~ 3 x 160…3 x 220 RM4TU02: ~ 3 x 300…3 x 430 ¦ ,Undervoltage ,
RM4TUmeasurement range | - ¦ ,Phase asymmetry,
RM4TUmeasurement range | Disconnection of neutral,
RM4TUmeasurement range | Voltage Regeneration,
RM4TUmeasurement range | Extreme undervoltage,
RM4TUmeasurement range | Extreme Overvoltage,
RM4TUmeasurement range | Extreme Asymmetry,
RM4TUtripping threshold | Unknown ¦ ,Phase cut,
RM4TUtripping threshold | Total swap of phase ¦ ,Phase sequence,
RM4TUtripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4TUtripping threshold | - ¦ ,Over voltage,
RM4TUtripping threshold | Adjustable within measurement range ¦ ,Undervoltage ,
RM4TUtripping threshold | - ¦ ,Phase asymmetry,
RM4TUtripping threshold | Disconnection of neutral,
RM4TUtripping threshold | Voltage Regeneration,
RM4TUtripping threshold | Extreme undervoltage (Phase loss),
RM4TUtripping threshold | Extreme Overvoltage,
RM4TUtripping threshold | Extreme Asymmetry,
RM4TUhysteresis | - ¦ ,Phase cut,
RM4TUhysteresis | - ¦ ,Phase sequence,
RM4TUhysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4TUhysteresis | Fixed 5% of de-energization threshold ¦ ,Over voltage,
RM4TUhysteresis | Fixed 5% of de-energization threshold ¦ ,Undervoltage ,
RM4TUhysteresis | - ¦ ,Phase asymmetry,
RM4TUhysteresis | Disconnection of neutral,
RM4TUhysteresis | Voltage Regeneration,
RM4TUhysteresis | Extreme undervoltage (Phase loss),
RM4TUhysteresis | Extreme Overvoltage,
RM4TUhysteresis | Extreme Asymmetry,
RM4TU
RM4TUoutput type | 2 x C/O relay contacts
RM4TUoutput terminal | 15-16-18, 25-26-28
RM4TUoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM4TUoutput logic | R2 (21-22-24),
RM4TUcontacts material | 90/10 Nickel Silver
RM4TUmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM4TUelectrical durability | Not specified ¦ IEC60947-4-1,AC-1,
RM4TUelectrical durability | IEC60947-4-1,DC-1,
RM4TUelectrical durability | IEC60947-5-1,AC-15,
RM4TUelectrical durability | IEC60947-5-1,DC-13,
RM4TU[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4TU[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4TUmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM4TUmaximum switching capacity | 8 ¦ ,Maximum switching current,
RM4TUmaximum switching capacity | 2000 ¦ ,Maximum switching capacity,
RM4TUminimum switching capacity | 12 ¦ IEC60947-5-4,Minimum switching voltage,
RM4TUminimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM4TUminimum switching capacity | 120 ¦ IEC60947-5-4,Minimum switching capacity,
RM4TUmaximum voltage drop | IEC62314,Only for solid state output,
RM4TUmaximum leakage current | IEC62314,Only for solid state output,
RM4TUthermal current | IEC60947-5-1
RM4TUshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM4TUshort circuit protection | IEC62314,Solid State Output by external fuse,
RM4TU
RM4TUtime delay type | · ¦ ,"OFF" delay,
RM4TUtime delay type | · ¦ ,"ON" delay,
RM4TUtime delay type | - ¦ ,Inhibition,
RM4TUtime delay range | Adjustable 0.1…10 ¦ ,"OFF" delay,
RM4TUtime delay range | - ¦ ,"ON" delay,
RM4TUtime delay range | - ¦ ,Inhibition,
RM4TUresponse time | Not specified ¦ ,on crossing the threshold,
RM4TUresponse time
RM4TUresponse time
RM4TUresponse time
RM4TUresponse time
RM4TUpower on delay | Not specified
RM4TUreset time | Not specified ¦ ,through Un power reset,
RM4TUreset time | through front panel reset,
RM4TUreset time | through input control reset,
RM4TUsetting accuracy of time delay | +/- 10% of full scales value
RM4TUrepeat accuracy of time delay | Not specified
RM4TUtime delay drift | < 0.5%
RM4TUtime delay drift | =< 0.07% / oC
RM4TU
RM4TUstatus LED
RM4TUlocal signalling | Power supply availability,
RM4TUlocal signalling | Power supply not availability,
RM4TUlocal signalling | Timing in-progress,
RM4TUlocal signalling | Output is energized,
RM4TUlocal signalling | Output is de-energized,
RM4TUlocal signalling | Range Setting Changes,
RM4TUlocal signalling | Phase Cut,
RM4TUlocal signalling | Phase Sequence Swap,
RM4TUlocal signalling | Undervoltage <U,
RM4TUlocal signalling | Overvoltage >U,
RM4TUlocal signalling | Phase Asymmetry,
RM4TUlocal signalling | Voltage Regeneration,
RM4TUlocal signalling | Extreme Undervoltage <U (Phase loss),
RM4TUlocal signalling | Extreme Overvoltage >U,
RM4TUlocal signalling | Extreme Phase Asymmetry,
RM4TU
RM4TU
RM4TU
RM4TUdiagnostic button
RM4TU
RM4TU
RM4TU
RM4TUsafety reliability data | MTTF,
RM4TUsafety reliability data | B10,
RM4TU | MTTFd,
RM4TU | B10d,
RM4TU
RM4TU
RM4TA
RM4TAstandards | EN60255-6, IEC60255-6
RM4TAproduct certifications | UL, CSA, GL, C-Tick, GOST
RM4TAmarking | UL, CSA, GL, C-Tick, GOST
RM4TAdirectives | 2006/95/EC
RM4TAdirectives | 2004/108/EC
RM4TAdirectives | 2002/95/EC
RM4TA
RM4TA | 3K3 ¦ IEC60721-3-3,Climatic category,
RM4TA | Germanisher Lloyd,Environmental category,
RM4TAambient air temperature for storage | -40…+85 ¦ ,Storage,
RM4TAambient air temperature for operation | -20…+65 ¦ ,Operation,
RM4TArelative humidity | 15%...85% ¦ IEC60068-2-30,Damp heat,XX
RM4TA | IEC60947-5-1,Cyclic Damp Heat Test,
RM4TAvibration resistance | a=0.35ms from 10Hz…55Hz ¦ IEC60068-2-6
RM4TAshock resistance | 15 gn ¦ IEC60068-2-27
RM4TAbump resistance | IEC60068-2-29
RM4TAseismic resistance | IEC60068-3-3
RM4TAIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM4TAIP degree of protection | IP50 ¦ IEC60529,Housing,
RM4TAIP degree of protection | Not specified ¦ IEC60529,Front Panel,
RM4TA
RM4TAwidth | 22.5 x 78 x 80 ¦ ,Width,
RM4TAheight | Height,
RM4TAdepth | Depth,
RM4TAnet weight | 110
RM4TAmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM4TAmounting support | - ¦ IEC/EN 60715,With socket,
RM4TAmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM4TAMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM4TAMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM4TAconnections - terminals | 2 conductor: 2.5 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM4TAconnections - terminals | 2 conductor: 1.5 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM4TAconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM4TAconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4TAtightening torque | 0.6…1.1 ¦ IEC60947-1,Tightening torque,
RM4TAcable stripping length | Not specified ¦ ,Cable stripping length,
RM4TAduty time | Not specified
RM4TA
RM4TAelectromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard,
RM4TAelectromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM4TAelectromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM4TAelectromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM4TAelectromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM4TAelectromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM4TAelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM4TAelectromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM4TAelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM4TAelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM4TAelectromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM4TAelectromagnetic compatibility | ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM4TAelectromagnetic compatibility | IEC50081-1, IEC50081-2 ¦ ,Generic emission standard,
RM4TAelectromagnetic compatibility | Class B Group 1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM4TAelectromagnetic compatibility | Class B Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM4TAelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM4TAelectromagnetic compatibility | Class B Group 1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM4TAelectromagnetic compatibility | Class B Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM4TAelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4TA
RM4TApollution degree | IEC60664-1
RM4TAovervoltage category | IEC60664-1
RM4TAcircuit group | Supply,Terminal
RM4TAcircuit group | Input 1,
RM4TAcircuit group | Input 2,
RM4TAcircuit group | Input 3,
RM4TAcircuit group | Output 1,
RM4TAcircuit group | Output 2,
RM4TA | Supply,Rated
RM4TA | Input 1,Voltage
RM4TA | Input 2,Spec
RM4TA | Input 3,
RM4TA | Output 1,
RM4TA | Output 2,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Supply,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Output 1,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4TA[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM4TA[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM4TA[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM4TAdielectric strength | IEC60255-27,Supply / Input 1,
RM4TAdielectric strength | IEC60255-27,Supply / Input 2,
RM4TAdielectric strength | IEC60255-27,Supply / Input 3,
RM4TAdielectric strength | IEC60255-27,Supply / Output 1,
RM4TAdielectric strength | IEC60255-27,Supply / Output 2,
RM4TAdielectric strength | IEC60255-27,Output 1 / Output 2,
RM4TAdielectric strength | IEC60255-27,Input 1 / Output 1,
RM4TAdielectric strength | IEC60255-27,Input 1 / Output 2,
RM4TAdielectric strength | IEC60255-27,Input 2 / Output 1,
RM4TAdielectric strength | IEC60255-27,Input 2 / Output 2,
RM4TAdielectric strength | IEC60255-27,Input 3 / Output 1,
RM4TAdielectric strength | IEC60255-27,Input 3 / Output 2,
RM4TAdielectric strength | IEC60255-27,Input 1 / Input 2,
RM4TAdielectric strength | IEC60255-27,Input 2 / Input 3,
RM4TAdielectric strength | IEC60255-27,Input 1 / Input 3,
RM4TAinsulation resistance | IEC60255-27,Supply / Input 1,
RM4TAinsulation resistance | IEC60255-27,Supply / Input 2,
RM4TAinsulation resistance | IEC60255-27,Supply / Input 3,
RM4TAinsulation resistance | IEC60255-27,Supply / Output 1,
RM4TAinsulation resistance | IEC60255-27,Supply / Output 2,
RM4TAinsulation resistance | IEC60255-27,Output 1 / Output 2,
RM4TAinsulation resistance | IEC60255-27,Input 1 / Output 1,
RM4TAinsulation resistance | IEC60255-27,Input 1 / Output 2,
RM4TAinsulation resistance | IEC60255-27,Input 2 / Output 1,
RM4TAinsulation resistance | IEC60255-27,Input 2 / Output 2,
RM4TAinsulation resistance | IEC60255-27,Input 3 / Output 1,
RM4TAinsulation resistance | IEC60255-27,Input 3 / Output 2,
RM4TAinsulation resistance | IEC60255-27,Input 1 / Input 2,
RM4TAinsulation resistance | IEC60255-27,Input 2 / Input 3,
RM4TAinsulation resistance | IEC60255-27,Input 1 / Input 3,
RM4TA
RM4TA[Us] rated supply voltage | RM4TA01/31: ~ 3 x 200…3 x 240 RM4TA02/32: ~ 3 x 380…3 x 500
RM4TAsupply voltage limits | RM4TA01/31: ~ 3 x 160…3 x 300 RM4TA02/32: ~ 3 x 290…3 x 580
RM4TApolarity
RM4TAsupply frequency | 50 / 60
RM4TAsupply frequency | 47.5…63
RM4TApower consumption | Not specified
RM4TAimmunity to microbreaks | Not specified
RM4TAsupply terminal | L1-L2-L3
RM4TAon-load factor
RM4TArelease of input voltage
RM4TA
RM4TAmonitoring functions | · ¦ ,Phase lost ,
RM4TAmonitoring functions | · ¦ ,Phase sequence,
RM4TAmonitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4TAmonitoring functions | - ¦ ,Over voltage,
RM4TAmonitoring functions | - ¦ ,Undervoltage ,
RM4TAmonitoring functions | · ¦ ,Phase asymmetry,
RM4TAmonitoring functions | - ¦ ,Disconnection of neutral,
RM4TAmonitoring functions | - ¦ ,Voltage Regeneration,
RM4TAmonitoring functions | Extreme undervoltage,
RM4TAmonitoring functions | Extreme overvoltage,
RM4TAmonitoring functions | Extreme asymmetry,
RM4TA | Resistive Voltage Step Down ¦ ,Measurement mode,
RM4TAinternal input resistance | Not specified ¦ ,Internal input resistance,
RM4TAinput terminal | L1-L2-L3 ¦ ,Input terminal,
RM4TAInput nominal voltage selection | RM4TU0131: ~ 3 x 160…3 x 300 RM4TU02/32: ~ 3 x 290…3 x 580 ¦ ,Input nominal voltage selection,
RM4TApermissible input overload | Not specified ¦ ,permissible input overload,
RM4TAinput frequency | 50 / 60 ¦ ,Rated frequency,
RM4TAinput frequency | 47.5…63 ¦ ,Frequency operating range,
RM4TAsetting accuracy of the switching threshold | +/- 3% of set value ¦ ,Setting accuracy,
RM4TArepeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM4TAmeasurement method | Voltage Peak Detection ¦ ,Measurement method,
RM4TAswitching threshold drift | < 0.5% ¦ ,Measurement error with supply voltage variation,
RM4TAswitching threshold drift | =< 0.06% / oC ¦ ,Measurement error with temperature variation,
RM4TAmaximum measuring cycle | 80 ¦ ,Maximum measuring cycles,
RM4TAmeasurement range | Fixed value ¦ ,Phase lost ,
RM4TAmeasurement range | Fixed value ¦ ,Phase sequence,
RM4TAmeasurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4TAmeasurement range | - ¦ ,Over voltage,
RM4TAmeasurement range | - ¦ ,Undervoltage ,
RM4TAmeasurement range | Not specified ¦ ,Phase asymmetry,
RM4TAmeasurement range | Disconnection of neutral,
RM4TAmeasurement range | Voltage Regeneration,
RM4TAmeasurement range | Extreme undervoltage,
RM4TAmeasurement range | Extreme Overvoltage,
RM4TAmeasurement range | Extreme Asymmetry,
RM4TAtripping threshold | Unknown ¦ ,Phase cut,
RM4TAtripping threshold | Total swap of phase ¦ ,Phase sequence,
RM4TAtripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4TAtripping threshold | - ¦ ,Over voltage,
RM4TAtripping threshold | - ¦ ,Undervoltage ,
RM4TAtripping threshold | Adjustable 5%...15% of selected Un ¦ ,Phase asymmetry,
RM4TAtripping threshold | Disconnection of neutral,
RM4TAtripping threshold | Voltage Regeneration,
RM4TAtripping threshold | Extreme undervoltage (Phase loss),
RM4TAtripping threshold | Extreme Overvoltage,
RM4TAtripping threshold | Extreme Asymmetry,
RM4TAhysteresis | - ¦ ,Phase cut,
RM4TAhysteresis | - ¦ ,Phase sequence,
RM4TAhysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4TAhysteresis | Fixed 5% of de-energization threshold ¦ ,Over voltage,
RM4TAhysteresis | Fixed 5% of de-energization threshold ¦ ,Undervoltage ,
RM4TAhysteresis | - ¦ ,Phase asymmetry,
RM4TAhysteresis | Disconnection of neutral,
RM4TAhysteresis | Voltage Regeneration,
RM4TAhysteresis | Extreme undervoltage (Phase loss),
RM4TAhysteresis | Extreme Overvoltage,
RM4TAhysteresis | Extreme Asymmetry,
RM4TA
RM4TAoutput type | 2 x C/O relay contacts
RM4TAoutput terminal | 15-16-18, 25-26-28
RM4TAoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM4TAoutput logic | R2 (21-22-24),
RM4TAcontacts material | 90/10 Nickel Silver
RM4TAmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM4TAelectrical durability | Not specified ¦ IEC60947-4-1,AC-1,
RM4TAelectrical durability | IEC60947-4-1,DC-1,
RM4TAelectrical durability | IEC60947-5-1,AC-15,
RM4TAelectrical durability | IEC60947-5-1,DC-13,
RM4TA[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4TA[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4TAmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM4TAmaximum switching capacity | 8 ¦ ,Maximum switching current,
RM4TAmaximum switching capacity | 2000 ¦ ,Maximum switching capacity,
RM4TAminimum switching capacity | 12 ¦ IEC60947-5-4,Minimum switching voltage,
RM4TAminimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM4TAminimum switching capacity | 120 ¦ IEC60947-5-4,Minimum switching capacity,
RM4TAmaximum voltage drop | IEC62314,Only for solid state output,
RM4TAmaximum leakage current | IEC62314,Only for solid state output,
RM4TAthermal current | IEC60947-5-1
RM4TAshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM4TAshort circuit protection | IEC62314,Solid State Output by external fuse,
RM4TA
RM4TAtime delay type | · ¦ ,"OFF" delay,
RM4TAtime delay type | · ¦ ,"ON" delay,
RM4TAtime delay type | - ¦ ,Inhibition,
RM4TAtime delay range | Adjustable 0.1…10 ¦ ,"OFF" delay,
RM4TAtime delay range | - ¦ ,"ON" delay,
RM4TAtime delay range | - ¦ ,Inhibition,
RM4TAresponse time | Not specified ¦ ,on crossing the threshold,
RM4TAresponse time
RM4TAresponse time
RM4TAresponse time
RM4TAresponse time
RM4TApower on delay | Not specified
RM4TAreset time | Not specified ¦ ,through Un power reset,
RM4TAreset time | through front panel reset,
RM4TAreset time | through input control reset,
RM4TAsetting accuracy of time delay | +/- 10% of full scales value
RM4TArepeat accuracy of time delay | Not specified
RM4TAtime delay drift | < 0.5%
RM4TAtime delay drift | =< 0.07% / oC
RM4TA
RM4TAstatus LED
RM4TAlocal signalling | Power supply availability,
RM4TAlocal signalling | Power supply not availability,
RM4TAlocal signalling | Timing in-progress,
RM4TAlocal signalling | Output is energized,
RM4TAlocal signalling | Output is de-energized,
RM4TAlocal signalling | Range Setting Changes,
RM4TAlocal signalling | Phase Cut,
RM4TAlocal signalling | Phase Sequence Swap,
RM4TAlocal signalling | Undervoltage <U,
RM4TAlocal signalling | Overvoltage >U,
RM4TAlocal signalling | Phase Asymmetry,
RM4TAlocal signalling | Voltage Regeneration,
RM4TAlocal signalling | Extreme Undervoltage <U (Phase loss),
RM4TAlocal signalling | Extreme Overvoltage >U,
RM4TAlocal signalling | Extreme Phase Asymmetry,
RM4TA
RM4TA
RM4TA
RM4TAdiagnostic button
RM4TA
RM4TA
RM4TA
RM4TAsafety reliability data | MTTF,
RM4TAsafety reliability data | B10,
RM4TA | MTTFd,
RM4TA | B10d,
RM4TA
RM4TA
RM4UB
RM4UBstandards | EN60255-6, IEC60255-6
RM4UBproduct certifications | UL, CSA, GL, C-Tick, GOST
RM4UBmarking | UL, CSA, GL, C-Tick, GOST
RM4UBdirectives | 2006/95/EC
RM4UBdirectives | 2004/108/EC
RM4UBdirectives | 2002/95/EC
RM4UB
RM4UB | 3K3 ¦ IEC60721-3-3,Climatic category,
RM4UB | Germanisher Lloyd,Environmental category,
RM4UBambient air temperature for storage | -40…+85 ¦ ,Storage,
RM4UBambient air temperature for operation | -20…+65 ¦ ,Operation,
RM4UBrelative humidity | 15%...85% ¦ IEC60068-2-30,Damp heat,XX
RM4UB | IEC60947-5-1,Cyclic Damp Heat Test,
RM4UBvibration resistance | a=0.35ms from 10Hz…55Hz ¦ IEC60068-2-6
RM4UBshock resistance | 15 gn ¦ IEC60068-2-27
RM4UBbump resistance | IEC60068-2-29
RM4UBseismic resistance | IEC60068-3-3
RM4UBIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM4UBIP degree of protection | IP50 ¦ IEC60529,Housing,
RM4UBIP degree of protection | Not specified ¦ IEC60529,Front Panel,
RM4UB
RM4UBwidth | 22.5 x 78 x 80 ¦ ,Width,
RM4UBheight | Height,
RM4UBdepth | Depth,
RM4UBnet weight | 110
RM4UBmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM4UBmounting support | - ¦ IEC/EN 60715,With socket,
RM4UBmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM4UBMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM4UBMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM4UBconnections - terminals | 2 conductor: 2.5 ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM4UBconnections - terminals | 2 conductor: 1.5 ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM4UBconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM4UBconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4UBtightening torque | 0.6…1.1 ¦ IEC60947-1,Tightening torque,
RM4UBcable stripping length | Not specified ¦ ,Cable stripping length,
RM4UBduty time | Not specified
RM4UB
RM4UBelectromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard,
RM4UBelectromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM4UBelectromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM4UBelectromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM4UBelectromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM4UBelectromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM4UBelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM4UBelectromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM4UBelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM4UBelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM4UBelectromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM4UBelectromagnetic compatibility | ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM4UBelectromagnetic compatibility | IEC50081-1, IEC50081-2 ¦ ,Generic emission standard,
RM4UBelectromagnetic compatibility | Class B Group 1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM4UBelectromagnetic compatibility | Class B Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM4UBelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM4UBelectromagnetic compatibility | Class B Group 1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM4UBelectromagnetic compatibility | Class B Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM4UBelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4UB
RM4UBpollution degree | IEC60664-1
RM4UBovervoltage category | IEC60664-1
RM4UBcircuit group | Supply,Terminal
RM4UBcircuit group | Input 1,
RM4UBcircuit group | Input 2,
RM4UBcircuit group | Input 3,
RM4UBcircuit group | Output 1,
RM4UBcircuit group | Output 2,
RM4UB | Supply,Rated
RM4UB | Input 1,Voltage
RM4UB | Input 2,Spec
RM4UB | Input 3,
RM4UB | Output 1,
RM4UB | Output 2,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Supply,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Output 1,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4UB[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM4UB[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM4UB[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM4UBdielectric strength | IEC60255-27,Supply / Input 1,
RM4UBdielectric strength | IEC60255-27,Supply / Input 2,
RM4UBdielectric strength | IEC60255-27,Supply / Input 3,
RM4UBdielectric strength | IEC60255-27,Supply / Output 1,
RM4UBdielectric strength | IEC60255-27,Supply / Output 2,
RM4UBdielectric strength | IEC60255-27,Output 1 / Output 2,
RM4UBdielectric strength | IEC60255-27,Input 1 / Output 1,
RM4UBdielectric strength | IEC60255-27,Input 1 / Output 2,
RM4UBdielectric strength | IEC60255-27,Input 2 / Output 1,
RM4UBdielectric strength | IEC60255-27,Input 2 / Output 2,
RM4UBdielectric strength | IEC60255-27,Input 3 / Output 1,
RM4UBdielectric strength | IEC60255-27,Input 3 / Output 2,
RM4UBdielectric strength | IEC60255-27,Input 1 / Input 2,
RM4UBdielectric strength | IEC60255-27,Input 2 / Input 3,
RM4UBdielectric strength | IEC60255-27,Input 1 / Input 3,
RM4UBinsulation resistance | IEC60255-27,Supply / Input 1,
RM4UBinsulation resistance | IEC60255-27,Supply / Input 2,
RM4UBinsulation resistance | IEC60255-27,Supply / Input 3,
RM4UBinsulation resistance | IEC60255-27,Supply / Output 1,
RM4UBinsulation resistance | IEC60255-27,Supply / Output 2,
RM4UBinsulation resistance | IEC60255-27,Output 1 / Output 2,
RM4UBinsulation resistance | IEC60255-27,Input 1 / Output 1,
RM4UBinsulation resistance | IEC60255-27,Input 1 / Output 2,
RM4UBinsulation resistance | IEC60255-27,Input 2 / Output 1,
RM4UBinsulation resistance | IEC60255-27,Input 2 / Output 2,
RM4UBinsulation resistance | IEC60255-27,Input 3 / Output 1,
RM4UBinsulation resistance | IEC60255-27,Input 3 / Output 2,
RM4UBinsulation resistance | IEC60255-27,Input 1 / Input 2,
RM4UBinsulation resistance | IEC60255-27,Input 2 / Input 3,
RM4UBinsulation resistance | IEC60255-27,Input 1 / Input 3,
RM4UB
RM4UB[Us] rated supply voltage | RM4UB34: ~80…220 RM4UB35: ~160…300
RM4UBsupply voltage limits | RM4UB34: ~60…300 RM4UB35: ~160…300
RM4UBpolarity
RM4UBsupply frequency | 50 / 60
RM4UBsupply frequency | 47.5…63
RM4UBpower consumption | Not specified
RM4UBimmunity to microbreaks | Not specified
RM4UBsupply terminal | L1-L3
RM4UBon-load factor
RM4UBrelease of input voltage
RM4UB
RM4UBmonitoring functions | - ¦ ,Phase lost ,
RM4UBmonitoring functions | - ¦ ,Phase sequence,
RM4UBmonitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4UBmonitoring functions | - ¦ ,Over voltage,
RM4UBmonitoring functions | - ¦ ,Undervoltage ,
RM4UBmonitoring functions | - ¦ ,Phase asymmetry,
RM4UBmonitoring functions | - ¦ ,Disconnection of neutral,
RM4UBmonitoring functions | - ¦ ,Voltage Regeneration,
RM4UBmonitoring functions | Extreme undervoltage,
RM4UBmonitoring functions | Extreme overvoltage,
RM4UBmonitoring functions | Extreme asymmetry,
RM4UB | Resistive Voltage Step Down ¦ ,Measurement mode,
RM4UBinternal input resistance | Not specified ¦ ,Internal input resistance,
RM4UBinput terminal | L1-L3 ¦ ,Input terminal,
RM4UBInput nominal voltage selection | RM4UB34: ~ 160…300 RM4UB35: ~ 160…300 ¦ ,Input nominal voltage selection,
RM4UBpermissible input overload | Not specified ¦ ,permissible input overload,
RM4UBinput frequency | 50 / 60 ¦ ,Rated frequency,
RM4UBinput frequency | 47.5…63 ¦ ,Frequency operating range,
RM4UBsetting accuracy of the switching threshold | +/- 3% of set value ¦ ,Setting accuracy,
RM4UBrepeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM4UBmeasurement method | Voltage Peak Detection ¦ ,Measurement method,
RM4UBswitching threshold drift | < 0.5% ¦ ,Measurement error with supply voltage variation,
RM4UBswitching threshold drift | =< 0.06% / oC ¦ ,Measurement error with temperature variation,
RM4UBmaximum measuring cycle | 80 ¦ ,Maximum measuring cycles,
RM4UBmeasurement range | Fixed value ¦ ,Phase lost ,
RM4UBmeasurement range | Fixed value ¦ ,Phase sequence,
RM4UBmeasurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4UBmeasurement range | RM4UB34: ~ 160…220 RM4UB34: ~ 220…300 ¦ ,Over voltage,
RM4UBmeasurement range | RM4UB34: ~ 80…120 RM4UB34: ~ 160…220 ¦ ,Undervoltage ,
RM4UBmeasurement range | - ¦ ,Phase asymmetry,
RM4UBmeasurement range | Disconnection of neutral,
RM4UBmeasurement range | Voltage Regeneration,
RM4UBmeasurement range | Extreme undervoltage,
RM4UBmeasurement range | Extreme Overvoltage,
RM4UBmeasurement range | Extreme Asymmetry,
RM4UBtripping threshold | - ¦ ,Phase cut,
RM4UBtripping threshold | - ¦ ,Phase sequence,
RM4UBtripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4UBtripping threshold | Adjustable within measurement range ¦ ,Over voltage,
RM4UBtripping threshold | Adjustable within measurement range ¦ ,Undervoltage ,
RM4UBtripping threshold | - ¦ ,Phase asymmetry,
RM4UBtripping threshold | Disconnection of neutral,
RM4UBtripping threshold | Voltage Regeneration,
RM4UBtripping threshold | Extreme undervoltage (Phase loss),
RM4UBtripping threshold | Extreme Overvoltage,
RM4UBtripping threshold | Extreme Asymmetry,
RM4UBhysteresis | - ¦ ,Phase cut,
RM4UBhysteresis | - ¦ ,Phase sequence,
RM4UBhysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
RM4UBhysteresis | Fixed 5% of de-energization threshold ¦ ,Over voltage,
RM4UBhysteresis | Fixed 5% of de-energization threshold ¦ ,Undervoltage ,
RM4UBhysteresis | - ¦ ,Phase asymmetry,
RM4UBhysteresis | Disconnection of neutral,
RM4UBhysteresis | Voltage Regeneration,
RM4UBhysteresis | Extreme undervoltage (Phase loss),
RM4UBhysteresis | Extreme Overvoltage,
RM4UBhysteresis | Extreme Asymmetry,
RM4UB
RM4UBoutput type | 2 x C/O relay contacts
RM4UBoutput terminal | 15-16-18, 25-26-28
RM4UBoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM4UBoutput logic | R2 (21-22-24),
RM4UBcontacts material | 90/10 Nickel Silver
RM4UBmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM4UBelectrical durability | Not specified ¦ IEC60947-4-1,AC-1,
RM4UBelectrical durability | IEC60947-4-1,DC-1,
RM4UBelectrical durability | IEC60947-5-1,AC-15,
RM4UBelectrical durability | IEC60947-5-1,DC-13,
RM4UB[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4UB[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4UBmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM4UBmaximum switching capacity | 8 ¦ ,Maximum switching current,
RM4UBmaximum switching capacity | 2000 ¦ ,Maximum switching capacity,
RM4UBminimum switching capacity | 12 ¦ IEC60947-5-4,Minimum switching voltage,
RM4UBminimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM4UBminimum switching capacity | 120 ¦ IEC60947-5-4,Minimum switching capacity,
RM4UBmaximum voltage drop | IEC62314,Only for solid state output,
RM4UBmaximum leakage current | IEC62314,Only for solid state output,
RM4UBthermal current | IEC60947-5-1
RM4UBshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM4UBshort circuit protection | IEC62314,Solid State Output by external fuse,
RM4UB
RM4UBtime delay type | · ¦ ,"OFF" delay,
RM4UBtime delay type | · ¦ ,"ON" delay,
RM4UBtime delay type | - ¦ ,Inhibition,
RM4UBtime delay range | Adjustable 0.1…10 ¦ ,"OFF" delay,
RM4UBtime delay range | - ¦ ,"ON" delay,
RM4UBtime delay range | - ¦ ,Inhibition,
RM4UBresponse time | Not specified ¦ ,on crossing the threshold,
RM4UBresponse time
RM4UBresponse time
RM4UBresponse time
RM4UBresponse time
RM4UBpower on delay | Not specified
RM4UBreset time | Not specified ¦ ,through Un power reset,
RM4UBreset time | through front panel reset,
RM4UBreset time | through input control reset,
RM4UBsetting accuracy of time delay | +/- 10% of full scales value
RM4UBrepeat accuracy of time delay | Not specified
RM4UBtime delay drift | < 0.5%
RM4UBtime delay drift | =< 0.07% / oC
RM4UB
RM4UBstatus LED
RM4UBlocal signalling | Power supply availability,
RM4UBlocal signalling | Power supply not availability,
RM4UBlocal signalling | Timing in-progress,
RM4UBlocal signalling | Output is energized,
RM4UBlocal signalling | Output is de-energized,
RM4UBlocal signalling | Range Setting Changes,
RM4UBlocal signalling | Phase Cut,
RM4UBlocal signalling | Phase Sequence Swap,
RM4UBlocal signalling | Undervoltage <U,
RM4UBlocal signalling | Overvoltage >U,
RM4UBlocal signalling | Phase Asymmetry,
RM4UBlocal signalling | Voltage Regeneration,
RM4UBlocal signalling | Extreme Undervoltage <U (Phase loss),
RM4UBlocal signalling | Extreme Overvoltage >U,
RM4UBlocal signalling | Extreme Phase Asymmetry,
RM4UB
RM4UB
RM4UB
RM4UBdiagnostic button
RM4UB
RM4UB
RM4UB
RM4UBsafety reliability data | MTTF,
RM4UBsafety reliability data | B10,
RM4UB | MTTFd,
RM4UB | B10d,
RM4UB
RM4UB
84873004
84873004standards | Not specified
84873004product certifications | cULus, CE
84873004marking | cULus, CE
84873004directives | Not specified
84873004directives | Not specified
84873004directives | Not specified
84873004
84873004 | Not specified ¦ IEC60721-3-3,Climatic category,
84873004 | Germanisher Lloyd,Environmental category,
84873004ambient air temperature for storage | -30…+70 ¦ ,Storage,
84873004ambient air temperature for operation | Not specified ¦ ,Operation,
84873004relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,XX
84873004 | IEC60947-5-1,Cyclic Damp Heat Test,
84873004vibration resistance | Not specified ¦ IEC60068-2-6
84873004shock resistance | Not specified ¦ IEC60068-2-27
84873004bump resistance | IEC60068-2-29
84873004seismic resistance | IEC60068-3-3
84873004IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
84873004IP degree of protection | IP40 ¦ IEC60529,Housing,
84873004IP degree of protection | Not specified ¦ IEC60529,Front Panel,
84873004
84873004width | 22.5 x 78.5 x 100 ¦ ,Width,
84873004height | Height,
84873004depth | Depth,
84873004net weight | 110
84873004mounting support | IEC/EN 60715,Without socket,
84873004mounting support | - ¦ IEC/EN 60715,With socket,
84873004mounting position | In relation to normal vertical mounting plane,
84873004Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
84873004Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
84873004connections - terminals | 1 conductor: 4 (AWG11) 2 conductor:2.5 (AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84873004connections - terminals | 2 conductor: 1.5 (AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84873004connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
84873004connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
84873004tightening torque | Max 1 ¦ IEC60947-1,Tightening torque,
84873004cable stripping length | Cable stripping length,
84873004duty time
84873004
84873004electromagnetic compatibility | Not specified ¦ ,Generic immunity standard,
84873004electromagnetic compatibility | Not specified ¦ IEC61000-4-2,Electrostatic discharge,
84873004electromagnetic compatibility | Not specified ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84873004electromagnetic compatibility | Not specified ¦ IEC61000-4-4,Fast transient / burst,
84873004electromagnetic compatibility | Not specified ¦ IEC61000-4-5,Surge,
84873004electromagnetic compatibility | Not specified ¦ IEC61000-4-6,Conducted RF disturbance,
84873004electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
84873004electromagnetic compatibility | Not specified ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84873004electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
84873004electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
84873004electromagnetic compatibility | Not specified ¦ IEC61000-4-13,Low frequency harmonics,
84873004electromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84873004electromagnetic compatibility | Not specified ¦ ,Generic emission standard,
84873004electromagnetic compatibility | Not specified ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84873004electromagnetic compatibility | Not specified ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84873004electromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84873004electromagnetic compatibility | Not specified ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84873004electromagnetic compatibility | Not specified ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84873004electromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Conducted emission,
84873004
84873004pollution degree | IEC60664-1
84873004overvoltage category | IEC60664-1
84873004circuit group | Supply,Terminal
84873004circuit group | Input 1,
84873004circuit group | Input 2,
84873004circuit group | Input 3,
84873004circuit group | Output 1,
84873004circuit group | Output 2,
84873004 | Supply,Rated
84873004 | Input 1,Voltage
84873004 | Input 2,Spec
84873004 | Input 3,
84873004 | Output 1,
84873004 | Output 2,
84873004[Ui] rated insulation voltage | IEC60664-1,Supply,
84873004[Ui] rated insulation voltage | IEC60664-1,Input 1,
84873004[Ui] rated insulation voltage | IEC60664-1,Input 2,
84873004[Ui] rated insulation voltage | IEC60664-1,Input 3,
84873004[Ui] rated insulation voltage | IEC60664-1,Output 1,
84873004[Ui] rated insulation voltage | IEC60664-1,Output 2,
84873004[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
84873004[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
84873004[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
84873004[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
84873004[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
84873004[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
84873004[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
84873004[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
84873004[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
84873004[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
84873004[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
84873004[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
84873004[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
84873004[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
84873004[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
84873004dielectric strength | IEC60255-27,Supply / Input 1,
84873004dielectric strength | IEC60255-27,Supply / Input 2,
84873004dielectric strength | IEC60255-27,Supply / Input 3,
84873004dielectric strength | IEC60255-27,Supply / Output 1,
84873004dielectric strength | IEC60255-27,Supply / Output 2,
84873004dielectric strength | IEC60255-27,Output 1 / Output 2,
84873004dielectric strength | IEC60255-27,Input 1 / Output 1,
84873004dielectric strength | IEC60255-27,Input 1 / Output 2,
84873004dielectric strength | IEC60255-27,Input 2 / Output 1,
84873004dielectric strength | IEC60255-27,Input 2 / Output 2,
84873004dielectric strength | IEC60255-27,Input 3 / Output 1,
84873004dielectric strength | IEC60255-27,Input 3 / Output 2,
84873004dielectric strength | IEC60255-27,Input 1 / Input 2,
84873004dielectric strength | IEC60255-27,Input 2 / Input 3,
84873004dielectric strength | IEC60255-27,Input 1 / Input 3,
84873004insulation resistance | IEC60255-27,Supply / Input 1,
84873004insulation resistance | IEC60255-27,Supply / Input 2,
84873004insulation resistance | IEC60255-27,Supply / Input 3,
84873004insulation resistance | IEC60255-27,Supply / Output 1,
84873004insulation resistance | IEC60255-27,Supply / Output 2,
84873004insulation resistance | IEC60255-27,Output 1 / Output 2,
84873004insulation resistance | IEC60255-27,Input 1 / Output 1,
84873004insulation resistance | IEC60255-27,Input 1 / Output 2,
84873004insulation resistance | IEC60255-27,Input 2 / Output 1,
84873004insulation resistance | IEC60255-27,Input 2 / Output 2,
84873004insulation resistance | IEC60255-27,Input 3 / Output 1,
84873004insulation resistance | IEC60255-27,Input 3 / Output 2,
84873004insulation resistance | IEC60255-27,Input 1 / Input 2,
84873004insulation resistance | IEC60255-27,Input 2 / Input 3,
84873004insulation resistance | IEC60255-27,Input 1 / Input 3,
84873004
84873004[Us] rated supply voltage | ~ 3 x 230…3 x 440
84873004supply voltage limits | Not specified
84873004polarity
84873004supply frequency | 50 / 60
84873004supply frequency | 49…61
84873004power consumption | 25
84873004immunity to microbreaks | Not specified
84873004supply terminal | Not specified
84873004on-load factor
84873004release of input voltage
84873004
84873004monitoring functions | · ¦ ,Phase lost ,
84873004monitoring functions | · ¦ ,Phase sequence,
84873004monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
84873004monitoring functions | - ¦ ,Over voltage,
84873004monitoring functions | - ¦ ,Undervoltage ,
84873004monitoring functions | - ¦ ,Phase asymmetry,
84873004monitoring functions | - ¦ ,Disconnection of neutral,
84873004monitoring functions | - ¦ ,Voltage Regeneration,
84873004monitoring functions | Extreme undervoltage,
84873004monitoring functions | Extreme overvoltage,
84873004monitoring functions | Extreme asymmetry,
84873004 | Measurement mode,
84873004internal input resistance | Not specified ¦ ,Internal input resistance,
84873004input terminal | L1-L2-L3 ¦ ,Input terminal,
84873004Input nominal voltage selection | Fixed @ ~ 3 x 230…3 x 440 ¦ ,Input nominal voltage selection,
84873004permissible input overload | Not specified ¦ ,permissible input overload,
84873004input frequency | 50 / 60 ¦ ,Rated frequency,
84873004input frequency | 49…61 ¦ ,Frequency operating range,
84873004setting accuracy of the switching threshold | - ¦ ,Setting accuracy,
84873004repeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
84873004measurement method | Not specified ¦ ,Measurement method,
84873004switching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation,
84873004switching threshold drift | Not specified ¦ ,Measurement error with temperature variation,
84873004maximum measuring cycle | Not specified ¦ ,Maximum measuring cycles,
84873004measurement range | Not specified ¦ ,Phase lost ,
84873004measurement range | Not specified ¦ ,Phase sequence,
84873004measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
84873004measurement range | - ¦ ,Over voltage,
84873004measurement range | - ¦ ,Undervoltage ,
84873004measurement range | - ¦ ,Phase asymmetry,
84873004measurement range | Disconnection of neutral,
84873004measurement range | Voltage Regeneration,
84873004measurement range | Extreme undervoltage,
84873004measurement range | Extreme Overvoltage,
84873004measurement range | Extreme Asymmetry,
84873004tripping threshold | Not specified ¦ ,Phase cut,
84873004tripping threshold | Not specified ¦ ,Phase sequence,
84873004tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
84873004tripping threshold | - ¦ ,Over voltage,
84873004tripping threshold | - ¦ ,Undervoltage ,
84873004tripping threshold | - ¦ ,Phase asymmetry,
84873004tripping threshold | Disconnection of neutral,
84873004tripping threshold | Voltage Regeneration,
84873004tripping threshold | Extreme undervoltage (Phase loss),
84873004tripping threshold | Extreme Overvoltage,
84873004tripping threshold | Extreme Asymmetry,
84873004hysteresis | Not specified ¦ ,Phase cut,
84873004hysteresis | Not specified ¦ ,Phase sequence,
84873004hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
84873004hysteresis | - ¦ ,Over voltage,
84873004hysteresis | - ¦ ,Undervoltage ,
84873004hysteresis | - ¦ ,Phase asymmetry,
84873004hysteresis | Disconnection of neutral,
84873004hysteresis | Voltage Regeneration,
84873004hysteresis | Extreme undervoltage (Phase loss),
84873004hysteresis | Extreme Overvoltage,
84873004hysteresis | Extreme Asymmetry,
84873004
84873004output type | 2 x C/O relay contacts
84873004output terminal | 11-12-14, 21-22-24
84873004output logic | Energized on fault-free ¦ ,R1 (11-12-14),
84873004output logic | R2 (21-22-24),
84873004contacts material | Cadmium free
84873004mechanical durability | 20 x 106 switching cycles ¦ IEC61810-1
84873004electrical durability | Not specified ¦ IEC60947-4-1,AC-1,
84873004electrical durability | IEC60947-4-1,DC-1,
84873004electrical durability | IEC60947-5-1,AC-15,
84873004electrical durability | IEC60947-5-1,DC-13,
84873004[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
84873004[Ie] rated operational current | IEC61810-1,Rated switching current,
84873004maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
84873004maximum switching capacity | 8 ¦ ,Maximum switching current,
84873004maximum switching capacity | 2000 ¦ ,Maximum switching capacity,
84873004minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
84873004minimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
84873004minimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
84873004maximum voltage drop | IEC62314,Only for solid state output,
84873004maximum leakage current | IEC62314,Only for solid state output,
84873004thermal current | IEC60947-5-1
84873004short circuit protection | IEC60947-5-1,Relay Output by external fuse,
84873004short circuit protection | IEC62314,Solid State Output by external fuse,
84873004
84873004time delay type | - ¦ ,"OFF" delay,
84873004time delay type | - ¦ ,"ON" delay,
84873004time delay type | - ¦ ,Inhibition,
84873004time delay range | - ¦ ,"OFF" delay,
84873004time delay range | - ¦ ,"ON" delay,
84873004time delay range | - ¦ ,Inhibition,
84873004response time | 0
84873004response time
84873004response time
84873004response time
84873004response time
84873004power on delay | 0
84873004reset time | - ¦ ,through Un power reset,
84873004reset time | through front panel reset,
84873004reset time | through input control reset,
84873004setting accuracy of time delay | -
84873004repeat accuracy of time delay | -
84873004time delay drift | -
84873004time delay drift | -
84873004
84873004status LED
84873004local signalling | Power supply availability,
84873004local signalling | Power supply not availability,
84873004local signalling | Timing in-progress,
84873004local signalling | Output is energized,
84873004local signalling | Output is de-energized,
84873004local signalling | Range Setting Changes,
84873004local signalling | Phase Cut,
84873004local signalling | Phase Sequence Swap,
84873004local signalling | Undervoltage <U,
84873004local signalling | Overvoltage >U,
84873004local signalling | Phase Asymmetry,
84873004local signalling | Voltage Regeneration,
84873004local signalling | Extreme Undervoltage <U (Phase loss),
84873004local signalling | Extreme Overvoltage >U,
84873004local signalling | Extreme Phase Asymmetry,
84873004
84873004
84873004
84873004diagnostic button
84873004
84873004
84873004
84873004safety reliability data | MTTF,
84873004safety reliability data | B10,
84873004 | MTTFd,
84873004 | B10d,
84873004
84873004
848792299
848792299standards | Not specified
848792299product certifications | cULus, CE
848792299marking | cULus, CE
848792299directives | Not specified
848792299directives | Not specified
848792299directives | Not specified
848792299
848792299 | Not specified ¦ IEC60721-3-3,Climatic category,
848792299 | Germanisher Lloyd,Environmental category,
848792299ambient air temperature for storage | -30…+70 ¦ ,Storage,
848792299ambient air temperature for operation | Not specified ¦ ,Operation,
848792299relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,XX
848792299 | IEC60947-5-1,Cyclic Damp Heat Test,
848792299vibration resistance | Not specified ¦ IEC60068-2-6
848792299shock resistance | Not specified ¦ IEC60068-2-27
848792299bump resistance | IEC60068-2-29
848792299seismic resistance | IEC60068-3-3
848792299IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
848792299IP degree of protection | IP40 ¦ IEC60529,Housing,
848792299IP degree of protection | Not specified ¦ IEC60529,Front Panel,
848792299
848792299width | 22.5 x 78.5 x 100 ¦ ,Width,
848792299height | Height,
848792299depth | Depth,
848792299net weight | 110
848792299mounting support | IEC/EN 60715,Without socket,
848792299mounting support | - ¦ IEC/EN 60715,With socket,
848792299mounting position | In relation to normal vertical mounting plane,
848792299Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
848792299Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
848792299connections - terminals | 1 conductor: 4 (AWG11) 2 conductor:2.5 (AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
848792299connections - terminals | 2 conductor: 1.5 (AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
848792299connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
848792299connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
848792299tightening torque | Max 1 ¦ IEC60947-1,Tightening torque,
848792299cable stripping length | Cable stripping length,
848792299duty time
848792299
848792299electromagnetic compatibility | Not specified ¦ ,Generic immunity standard,
848792299electromagnetic compatibility | Not specified ¦ IEC61000-4-2,Electrostatic discharge,
848792299electromagnetic compatibility | Not specified ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
848792299electromagnetic compatibility | Not specified ¦ IEC61000-4-4,Fast transient / burst,
848792299electromagnetic compatibility | Not specified ¦ IEC61000-4-5,Surge,
848792299electromagnetic compatibility | Not specified ¦ IEC61000-4-6,Conducted RF disturbance,
848792299electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
848792299electromagnetic compatibility | Not specified ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
848792299electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
848792299electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
848792299electromagnetic compatibility | Not specified ¦ IEC61000-4-13,Low frequency harmonics,
848792299electromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
848792299electromagnetic compatibility | Not specified ¦ ,Generic emission standard,
848792299electromagnetic compatibility | Not specified ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
848792299electromagnetic compatibility | Not specified ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
848792299electromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Radiated emission from enclosure port,
848792299electromagnetic compatibility | Not specified ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
848792299electromagnetic compatibility | Not specified ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
848792299electromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Conducted emission,
848792299
848792299pollution degree | IEC60664-1
848792299overvoltage category | IEC60664-1
848792299circuit group | Supply,Terminal
848792299circuit group | Input 1,
848792299circuit group | Input 2,
848792299circuit group | Input 3,
848792299circuit group | Output 1,
848792299circuit group | Output 2,
848792299 | Supply,Rated
848792299 | Input 1,Voltage
848792299 | Input 2,Spec
848792299 | Input 3,
848792299 | Output 1,
848792299 | Output 2,
848792299[Ui] rated insulation voltage | IEC60664-1,Supply,
848792299[Ui] rated insulation voltage | IEC60664-1,Input 1,
848792299[Ui] rated insulation voltage | IEC60664-1,Input 2,
848792299[Ui] rated insulation voltage | IEC60664-1,Input 3,
848792299[Ui] rated insulation voltage | IEC60664-1,Output 1,
848792299[Ui] rated insulation voltage | IEC60664-1,Output 2,
848792299[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
848792299[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
848792299[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
848792299[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
848792299[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
848792299[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
848792299[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
848792299[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
848792299[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
848792299[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
848792299[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
848792299[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
848792299[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
848792299[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
848792299[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
848792299dielectric strength | IEC60255-27,Supply / Input 1,
848792299dielectric strength | IEC60255-27,Supply / Input 2,
848792299dielectric strength | IEC60255-27,Supply / Input 3,
848792299dielectric strength | IEC60255-27,Supply / Output 1,
848792299dielectric strength | IEC60255-27,Supply / Output 2,
848792299dielectric strength | IEC60255-27,Output 1 / Output 2,
848792299dielectric strength | IEC60255-27,Input 1 / Output 1,
848792299dielectric strength | IEC60255-27,Input 1 / Output 2,
848792299dielectric strength | IEC60255-27,Input 2 / Output 1,
848792299dielectric strength | IEC60255-27,Input 2 / Output 2,
848792299dielectric strength | IEC60255-27,Input 3 / Output 1,
848792299dielectric strength | IEC60255-27,Input 3 / Output 2,
848792299dielectric strength | IEC60255-27,Input 1 / Input 2,
848792299dielectric strength | IEC60255-27,Input 2 / Input 3,
848792299dielectric strength | IEC60255-27,Input 1 / Input 3,
848792299insulation resistance | IEC60255-27,Supply / Input 1,
848792299insulation resistance | IEC60255-27,Supply / Input 2,
848792299insulation resistance | IEC60255-27,Supply / Input 3,
848792299insulation resistance | IEC60255-27,Supply / Output 1,
848792299insulation resistance | IEC60255-27,Supply / Output 2,
848792299insulation resistance | IEC60255-27,Output 1 / Output 2,
848792299insulation resistance | IEC60255-27,Input 1 / Output 1,
848792299insulation resistance | IEC60255-27,Input 1 / Output 2,
848792299insulation resistance | IEC60255-27,Input 2 / Output 1,
848792299insulation resistance | IEC60255-27,Input 2 / Output 2,
848792299insulation resistance | IEC60255-27,Input 3 / Output 1,
848792299insulation resistance | IEC60255-27,Input 3 / Output 2,
848792299insulation resistance | IEC60255-27,Input 1 / Input 2,
848792299insulation resistance | IEC60255-27,Input 2 / Input 3,
848792299insulation resistance | IEC60255-27,Input 1 / Input 3,
848792299
848792299[Us] rated supply voltage | ~ 3 x 230…3 x 440
848792299supply voltage limits | Not specified
848792299polarity
848792299supply frequency | 50 / 60
848792299supply frequency | 49…61
848792299power consumption | 25
848792299immunity to microbreaks | Not specified
848792299supply terminal | Not specified
848792299on-load factor
848792299release of input voltage
848792299
848792299monitoring functions | · ¦ ,Phase lost ,
848792299monitoring functions | · ¦ ,Phase sequence,
848792299monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
848792299monitoring functions | - ¦ ,Over voltage,
848792299monitoring functions | - ¦ ,Undervoltage ,
848792299monitoring functions | - ¦ ,Phase asymmetry,
848792299monitoring functions | - ¦ ,Disconnection of neutral,
848792299monitoring functions | - ¦ ,Voltage Regeneration,
848792299monitoring functions | Extreme undervoltage,
848792299monitoring functions | Extreme overvoltage,
848792299monitoring functions | Extreme asymmetry,
848792299 | Measurement mode,
848792299internal input resistance | Not specified ¦ ,Internal input resistance,
848792299input terminal | L1-L2-L3 ¦ ,Input terminal,
848792299Input nominal voltage selection | Fixed @ ~ 3 x 230…3 x 440 ¦ ,Input nominal voltage selection,
848792299permissible input overload | Not specified ¦ ,permissible input overload,
848792299input frequency | 50 / 60 ¦ ,Rated frequency,
848792299input frequency | 49…61 ¦ ,Frequency operating range,
848792299setting accuracy of the switching threshold | - ¦ ,Setting accuracy,
848792299repeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
848792299measurement method | Not specified ¦ ,Measurement method,
848792299switching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation,
848792299switching threshold drift | Not specified ¦ ,Measurement error with temperature variation,
848792299maximum measuring cycle | Not specified ¦ ,Maximum measuring cycles,
848792299measurement range | Not specified ¦ ,Phase lost ,
848792299measurement range | Not specified ¦ ,Phase sequence,
848792299measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
848792299measurement range | - ¦ ,Over voltage,
848792299measurement range | - ¦ ,Undervoltage ,
848792299measurement range | - ¦ ,Phase asymmetry,
848792299measurement range | Disconnection of neutral,
848792299measurement range | Voltage Regeneration,
848792299measurement range | Extreme undervoltage,
848792299measurement range | Extreme Overvoltage,
848792299measurement range | Extreme Asymmetry,
848792299tripping threshold | Not specified ¦ ,Phase cut,
848792299tripping threshold | Not specified ¦ ,Phase sequence,
848792299tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
848792299tripping threshold | - ¦ ,Over voltage,
848792299tripping threshold | - ¦ ,Undervoltage ,
848792299tripping threshold | - ¦ ,Phase asymmetry,
848792299tripping threshold | Disconnection of neutral,
848792299tripping threshold | Voltage Regeneration,
848792299tripping threshold | Extreme undervoltage (Phase loss),
848792299tripping threshold | Extreme Overvoltage,
848792299tripping threshold | Extreme Asymmetry,
848792299hysteresis | Not specified ¦ ,Phase cut,
848792299hysteresis | Not specified ¦ ,Phase sequence,
848792299hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
848792299hysteresis | - ¦ ,Over voltage,
848792299hysteresis | - ¦ ,Undervoltage ,
848792299hysteresis | - ¦ ,Phase asymmetry,
848792299hysteresis | Disconnection of neutral,
848792299hysteresis | Voltage Regeneration,
848792299hysteresis | Extreme undervoltage (Phase loss),
848792299hysteresis | Extreme Overvoltage,
848792299hysteresis | Extreme Asymmetry,
848792299
848792299output type | 1 x C/O relay contacts
848792299output terminal | 2014-11-12 00:00:00
848792299output logic | Energized on fault-free ¦ ,R1 (11-12-14),
848792299output logic | R2 (21-22-24),
848792299contacts material | Cadmium free
848792299mechanical durability | 20 x 106 switching cycles ¦ IEC61810-1
848792299electrical durability | Not specified ¦ IEC60947-4-1,AC-1,
848792299electrical durability | IEC60947-4-1,DC-1,
848792299electrical durability | IEC60947-5-1,AC-15,
848792299electrical durability | IEC60947-5-1,DC-13,
848792299[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
848792299[Ie] rated operational current | IEC61810-1,Rated switching current,
848792299maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
848792299maximum switching capacity | 8 ¦ ,Maximum switching current,
848792299maximum switching capacity | 2000 ¦ ,Maximum switching capacity,
848792299minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
848792299minimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
848792299minimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
848792299maximum voltage drop | IEC62314,Only for solid state output,
848792299maximum leakage current | IEC62314,Only for solid state output,
848792299thermal current | IEC60947-5-1
848792299short circuit protection | IEC60947-5-1,Relay Output by external fuse,
848792299short circuit protection | IEC62314,Solid State Output by external fuse,
848792299
848792299time delay type | - ¦ ,"OFF" delay,
848792299time delay type | - ¦ ,"ON" delay,
848792299time delay type | - ¦ ,Inhibition,
848792299time delay range | - ¦ ,"OFF" delay,
848792299time delay range | - ¦ ,"ON" delay,
848792299time delay range | - ¦ ,Inhibition,
848792299response time | 0
848792299response time
848792299response time
848792299response time
848792299response time
848792299power on delay | 0
848792299reset time | - ¦ ,through Un power reset,
848792299reset time | through front panel reset,
848792299reset time | through input control reset,
848792299setting accuracy of time delay | -
848792299repeat accuracy of time delay | -
848792299time delay drift | -
848792299time delay drift | -
848792299
848792299status LED
848792299local signalling | Power supply availability,
848792299local signalling | Power supply not availability,
848792299local signalling | Timing in-progress,
848792299local signalling | Output is energized,
848792299local signalling | Output is de-energized,
848792299local signalling | Range Setting Changes,
848792299local signalling | Phase Cut,
848792299local signalling | Phase Sequence Swap,
848792299local signalling | Undervoltage <U,
848792299local signalling | Overvoltage >U,
848792299local signalling | Phase Asymmetry,
848792299local signalling | Voltage Regeneration,
848792299local signalling | Extreme Undervoltage <U (Phase loss),
848792299local signalling | Extreme Overvoltage >U,
848792299local signalling | Extreme Phase Asymmetry,
848792299
848792299
848792299
848792299diagnostic button
848792299
848792299
848792299
848792299safety reliability data | MTTF,
848792299safety reliability data | B10,
848792299 | MTTFd,
848792299 | B10d,
848792299
848792299
1SVR 630 794 R3300
1SVR 630 794 R3300standards | EN60255-6, IEC60255-6, EN50178
1SVR 630 794 R3300product certifications | cULus, CSA, GL, C-Tick, GOST, CCC, CB
1SVR 630 794 R3300marking | cULus, CSA, GL, C-Tick, GOST, CCC, CB, CE
1SVR 630 794 R3300directives | 2006/95/EG
1SVR 630 794 R3300directives | 2004/108/EG
1SVR 630 794 R3300directives | 2002/95/EC
1SVR 630 794 R3300
1SVR 630 794 R3300 | 3K3 ¦ IEC60721-3-3,Climatic category,
1SVR 630 794 R3300 | Germanisher Lloyd,Environmental category,
1SVR 630 794 R3300ambient air temperature for storage | -40…+85 ¦ ,Storage,
1SVR 630 794 R3300ambient air temperature for operation | -25…+60 ¦ ,Operation,
1SVR 630 794 R3300relative humidity | +55°C, 6 cycles ¦ IEC60068-2-30,Damp heat,XX
1SVR 630 794 R3300 | IEC60947-5-1,Cyclic Damp Heat Test,
1SVR 630 794 R3300vibration resistance | Class 2 ¦ IEC60068-2-6
1SVR 630 794 R3300shock resistance | Class 2 ¦ IEC60068-2-27
1SVR 630 794 R3300bump resistance | IEC60068-2-29
1SVR 630 794 R3300seismic resistance | IEC60068-3-3
1SVR 630 794 R3300IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
1SVR 630 794 R3300IP degree of protection | IP50 ¦ IEC60529,Housing,
1SVR 630 794 R3300IP degree of protection | Not specified ¦ IEC60529,Front Panel,
1SVR 630 794 R3300
1SVR 630 794 R3300width | 22.5 x 78 x 100 ¦ ,Width,
1SVR 630 794 R3300height | Height,
1SVR 630 794 R3300depth | Depth,
1SVR 630 794 R3300net weight | 130
1SVR 630 794 R3300mounting support | DIN rail snap-on mounting without any tool ¦ IEC/EN 60715,Without socket,
1SVR 630 794 R3300mounting support | - ¦ IEC/EN 60715,With socket,
1SVR 630 794 R3300mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
1SVR 630 794 R3300Minimum distance to adjacent devices | None ¦ ,Horizontal,
1SVR 630 794 R3300Minimum distance to adjacent devices | None ¦ ,Vertical,
1SVR 630 794 R3300connections - terminals | 2 conductor:0.75…2.5 (AWG18…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
1SVR 630 794 R3300connections - terminals | 2 conductor:0.5…4 (AWG20…AWG12) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
1SVR 630 794 R3300connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
1SVR 630 794 R3300connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
1SVR 630 794 R3300tightening torque | 0.6…0.8 ¦ IEC60947-1,Tightening torque,
1SVR 630 794 R3300cable stripping length | 7 ¦ ,Cable stripping length,
1SVR 630 794 R3300duty time | 100
1SVR 630 794 R3300
1SVR 630 794 R3300electromagnetic compatibility | IEC61000-6-1, IEC61000-6-2 ¦ ,Generic immunity standard,
1SVR 630 794 R3300electromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
1SVR 630 794 R3300electromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
1SVR 630 794 R3300electromagnetic compatibility | Level 3 (2kV / 2kHz) ¦ IEC61000-4-4,Fast transient / burst,
1SVR 630 794 R3300electromagnetic compatibility | Level 3 (2kV phase-phase) ¦ IEC61000-4-5,Surge,
1SVR 630 794 R3300electromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
1SVR 630 794 R3300electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
1SVR 630 794 R3300electromagnetic compatibility | Not specified ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
1SVR 630 794 R3300electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
1SVR 630 794 R3300electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
1SVR 630 794 R3300electromagnetic compatibility | Class 3 ¦ IEC61000-4-13,Low frequency harmonics,
1SVR 630 794 R3300electromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
1SVR 630 794 R3300electromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
1SVR 630 794 R3300electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
1SVR 630 794 R3300electromagnetic compatibility | - ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
1SVR 630 794 R3300electromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Radiated emission from enclosure port,
1SVR 630 794 R3300electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
1SVR 630 794 R3300electromagnetic compatibility | - ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
1SVR 630 794 R3300electromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Conducted emission,
1SVR 630 794 R3300
1SVR 630 794 R3300pollution degree | IEC60664-1
1SVR 630 794 R3300overvoltage category | IEC60664-1
1SVR 630 794 R3300circuit group | Supply,Terminal
1SVR 630 794 R3300circuit group | Input 1,
1SVR 630 794 R3300circuit group | Input 2,
1SVR 630 794 R3300circuit group | Input 3,
1SVR 630 794 R3300circuit group | Output 1,
1SVR 630 794 R3300circuit group | Output 2,
1SVR 630 794 R3300 | Supply,Rated
1SVR 630 794 R3300 | Input 1,Voltage
1SVR 630 794 R3300 | Input 2,Spec
1SVR 630 794 R3300 | Input 3,
1SVR 630 794 R3300 | Output 1,
1SVR 630 794 R3300 | Output 2,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Supply,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Input 1,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Input 2,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Input 3,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Output 1,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Output 2,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
1SVR 630 794 R3300dielectric strength | IEC60255-27,Supply / Input 1,
1SVR 630 794 R3300dielectric strength | IEC60255-27,Supply / Input 2,
1SVR 630 794 R3300dielectric strength | IEC60255-27,Supply / Input 3,
1SVR 630 794 R3300dielectric strength | IEC60255-27,Supply / Output 1,
1SVR 630 794 R3300dielectric strength | IEC60255-27,Supply / Output 2,
1SVR 630 794 R3300dielectric strength | IEC60255-27,Output 1 / Output 2,
1SVR 630 794 R3300dielectric strength | IEC60255-27,Input 1 / Output 1,
1SVR 630 794 R3300dielectric strength | IEC60255-27,Input 1 / Output 2,
1SVR 630 794 R3300dielectric strength | IEC60255-27,Input 2 / Output 1,
1SVR 630 794 R3300dielectric strength | IEC60255-27,Input 2 / Output 2,
1SVR 630 794 R3300dielectric strength | IEC60255-27,Input 3 / Output 1,
1SVR 630 794 R3300dielectric strength | IEC60255-27,Input 3 / Output 2,
1SVR 630 794 R3300dielectric strength | IEC60255-27,Input 1 / Input 2,
1SVR 630 794 R3300dielectric strength | IEC60255-27,Input 2 / Input 3,
1SVR 630 794 R3300dielectric strength | IEC60255-27,Input 1 / Input 3,
1SVR 630 794 R3300insulation resistance | IEC60255-27,Supply / Input 1,
1SVR 630 794 R3300insulation resistance | IEC60255-27,Supply / Input 2,
1SVR 630 794 R3300insulation resistance | IEC60255-27,Supply / Input 3,
1SVR 630 794 R3300insulation resistance | IEC60255-27,Supply / Output 1,
1SVR 630 794 R3300insulation resistance | IEC60255-27,Supply / Output 2,
1SVR 630 794 R3300insulation resistance | IEC60255-27,Output 1 / Output 2,
1SVR 630 794 R3300insulation resistance | IEC60255-27,Input 1 / Output 1,
1SVR 630 794 R3300insulation resistance | IEC60255-27,Input 1 / Output 2,
1SVR 630 794 R3300insulation resistance | IEC60255-27,Input 2 / Output 1,
1SVR 630 794 R3300insulation resistance | IEC60255-27,Input 2 / Output 2,
1SVR 630 794 R3300insulation resistance | IEC60255-27,Input 3 / Output 1,
1SVR 630 794 R3300insulation resistance | IEC60255-27,Input 3 / Output 2,
1SVR 630 794 R3300insulation resistance | IEC60255-27,Input 1 / Input 2,
1SVR 630 794 R3300insulation resistance | IEC60255-27,Input 2 / Input 3,
1SVR 630 794 R3300insulation resistance | IEC60255-27,Input 1 / Input 3,
1SVR 630 794 R3300
1SVR 630 794 R3300[Us] rated supply voltage | ~ 3 x 300…3 x 500
1SVR 630 794 R3300supply voltage limits | ~ 3 x 255…3 x 550
1SVR 630 794 R3300polarity
1SVR 630 794 R3300supply frequency | 50 / 60
1SVR 630 794 R3300supply frequency | 45…66
1SVR 630 794 R3300power consumption | 25mA / 18VA (400VAC)
1SVR 630 794 R3300immunity to microbreaks | -
1SVR 630 794 R3300supply terminal | L1-L2-L3
1SVR 630 794 R3300on-load factor
1SVR 630 794 R3300release of input voltage
1SVR 630 794 R3300
1SVR 630 794 R3300monitoring functions | · ¦ ,Phase lost ,
1SVR 630 794 R3300monitoring functions | can be switched off ¦ ,Phase sequence,
1SVR 630 794 R3300monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
1SVR 630 794 R3300monitoring functions | · ¦ ,Over voltage,
1SVR 630 794 R3300monitoring functions | · ¦ ,Undervoltage ,
1SVR 630 794 R3300monitoring functions | - ¦ ,Phase asymmetry,
1SVR 630 794 R3300monitoring functions | - ¦ ,Disconnection of neutral,
1SVR 630 794 R3300monitoring functions | - ¦ ,Voltage Regeneration,
1SVR 630 794 R3300monitoring functions | Extreme undervoltage,
1SVR 630 794 R3300monitoring functions | Extreme overvoltage,
1SVR 630 794 R3300monitoring functions | Extreme asymmetry,
1SVR 630 794 R3300 | Resistive Voltage Step Down ¦ ,Measurement mode,
1SVR 630 794 R3300internal input resistance | Not specified ¦ ,Internal input resistance,
1SVR 630 794 R3300input terminal | L1-L2-L3 ¦ ,Input terminal,
1SVR 630 794 R3300Input nominal voltage selection | Fixed @ ~ 3 x 255…3 x 550 ¦ ,Input nominal voltage selection,
1SVR 630 794 R3300permissible input overload | Not specified ¦ ,permissible input overload,
1SVR 630 794 R3300input frequency | 50 / 60 ¦ ,Rated frequency,
1SVR 630 794 R3300input frequency | 45…66 ¦ ,Frequency operating range,
1SVR 630 794 R3300setting accuracy of the switching threshold | Not specified ¦ ,Setting accuracy,
1SVR 630 794 R3300repeat accuracy of the switching threshold | < +/- 0.2% ¦ ,Repeat accuracy (constant parameters),
1SVR 630 794 R3300measurement method | True RMS ¦ ,Measurement method,
1SVR 630 794 R3300switching threshold drift | < 0.5% ¦ ,Measurement error with supply voltage variation,
1SVR 630 794 R3300switching threshold drift | =< 0.06% / oC ¦ ,Measurement error with temperature variation,
1SVR 630 794 R3300maximum measuring cycle | 100 ¦ ,Maximum measuring cycles,
1SVR 630 794 R3300measurement range | Not specified ¦ ,Phase lost ,
1SVR 630 794 R3300measurement range | Not specified ¦ ,Phase sequence,
1SVR 630 794 R3300measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
1SVR 630 794 R3300measurement range | ~ 3 x 420…3 x 500 ¦ ,Over voltage,
1SVR 630 794 R3300measurement range | ~ 3 x 300…3 x 380 ¦ ,Undervoltage ,
1SVR 630 794 R3300measurement range | - ¦ ,Phase asymmetry,
1SVR 630 794 R3300measurement range | Disconnection of neutral,
1SVR 630 794 R3300measurement range | Voltage Regeneration,
1SVR 630 794 R3300measurement range | Extreme undervoltage,
1SVR 630 794 R3300measurement range | Extreme Overvoltage,
1SVR 630 794 R3300measurement range | Extreme Asymmetry,
1SVR 630 794 R3300tripping threshold | - ¦ ,Phase cut,
1SVR 630 794 R3300tripping threshold | - ¦ ,Phase sequence,
1SVR 630 794 R3300tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
1SVR 630 794 R3300tripping threshold | Adjustable within measurement range ¦ ,Over voltage,
1SVR 630 794 R3300tripping threshold | Adjustable within measurement range ¦ ,Undervoltage ,
1SVR 630 794 R3300tripping threshold | - ¦ ,Phase asymmetry,
1SVR 630 794 R3300tripping threshold | Disconnection of neutral,
1SVR 630 794 R3300tripping threshold | Voltage Regeneration,
1SVR 630 794 R3300tripping threshold | Extreme undervoltage (Phase loss),
1SVR 630 794 R3300tripping threshold | Extreme Overvoltage,
1SVR 630 794 R3300tripping threshold | Extreme Asymmetry,
1SVR 630 794 R3300hysteresis | - ¦ ,Phase cut,
1SVR 630 794 R3300hysteresis | - ¦ ,Phase sequence,
1SVR 630 794 R3300hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
1SVR 630 794 R3300hysteresis | Fixed 5% ¦ ,Over voltage,
1SVR 630 794 R3300hysteresis | Fixed 5% ¦ ,Undervoltage ,
1SVR 630 794 R3300hysteresis | - ¦ ,Phase asymmetry,
1SVR 630 794 R3300hysteresis | Disconnection of neutral,
1SVR 630 794 R3300hysteresis | Voltage Regeneration,
1SVR 630 794 R3300hysteresis | Extreme undervoltage (Phase loss),
1SVR 630 794 R3300hysteresis | Extreme Overvoltage,
1SVR 630 794 R3300hysteresis | Extreme Asymmetry,
1SVR 630 794 R3300
1SVR 630 794 R3300output type | 2 x C/O relay contacts
1SVR 630 794 R3300output terminal
1SVR 630 794 R3300output logic | Energized on fault-free ¦ ,R1 (11-12-14),
1SVR 630 794 R3300output logic | R2 (21-22-24),
1SVR 630 794 R3300contacts material | AgNi alloy, Cadmium free
1SVR 630 794 R3300mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
1SVR 630 794 R3300electrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1,
1SVR 630 794 R3300electrical durability | IEC60947-4-1,DC-1,
1SVR 630 794 R3300electrical durability | IEC60947-5-1,AC-15,
1SVR 630 794 R3300electrical durability | IEC60947-5-1,DC-13,
1SVR 630 794 R3300[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
1SVR 630 794 R3300[Ie] rated operational current | IEC61810-1,Rated switching current,
1SVR 630 794 R3300maximum switching capacity | ~/-- 250 ¦ ,Maximum switching voltage,
1SVR 630 794 R3300maximum switching capacity | - ¦ ,Maximum switching current,
1SVR 630 794 R3300maximum switching capacity | Maximum switching capacity,
1SVR 630 794 R3300minimum switching capacity | 24 ¦ IEC60947-5-4,Minimum switching voltage,
1SVR 630 794 R3300minimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
1SVR 630 794 R3300minimum switching capacity | 240 ¦ IEC60947-5-4,Minimum switching capacity,
1SVR 630 794 R3300maximum voltage drop | IEC62314,Only for solid state output,
1SVR 630 794 R3300maximum leakage current | IEC62314,Only for solid state output,
1SVR 630 794 R3300thermal current | IEC60947-5-1
1SVR 630 794 R3300short circuit protection | IEC60947-5-1,Relay Output by external fuse,
1SVR 630 794 R3300short circuit protection | IEC62314,Solid State Output by external fuse,
1SVR 630 794 R3300
1SVR 630 794 R3300time delay type | · ¦ ,"OFF" delay,
1SVR 630 794 R3300time delay type | · ¦ ,"ON" delay,
1SVR 630 794 R3300time delay type | - ¦ ,Inhibition,
1SVR 630 794 R3300time delay range | Adjustable 0.1…30 ¦ ,"OFF" delay,
1SVR 630 794 R3300time delay range | - ¦ ,"ON" delay,
1SVR 630 794 R3300time delay range | - ¦ ,Inhibition,
1SVR 630 794 R3300response time | - ¦ ,on crossing the threshold,
1SVR 630 794 R3300response time
1SVR 630 794 R3300response time
1SVR 630 794 R3300response time
1SVR 630 794 R3300response time
1SVR 630 794 R3300power on delay | Fixed 200
1SVR 630 794 R3300reset time | - ¦ ,through Un power reset,
1SVR 630 794 R3300reset time | through front panel reset,
1SVR 630 794 R3300reset time | through input control reset,
1SVR 630 794 R3300setting accuracy of time delay | -
1SVR 630 794 R3300repeat accuracy of time delay | < +/- 0.2%
1SVR 630 794 R3300time delay drift | < 0.5%
1SVR 630 794 R3300time delay drift | =< 0.06% / oC
1SVR 630 794 R3300
1SVR 630 794 R3300status LED
1SVR 630 794 R3300local signalling | Power supply availability,
1SVR 630 794 R3300local signalling | Power supply not availability,
1SVR 630 794 R3300local signalling | Timing in-progress,
1SVR 630 794 R3300local signalling | Output is energized,
1SVR 630 794 R3300local signalling | Output is de-energized,
1SVR 630 794 R3300local signalling | Range Setting Changes,
1SVR 630 794 R3300local signalling | Phase Cut,
1SVR 630 794 R3300local signalling | Phase Sequence Swap,
1SVR 630 794 R3300local signalling | Undervoltage <U,
1SVR 630 794 R3300local signalling | Overvoltage >U,
1SVR 630 794 R3300local signalling | Phase Asymmetry,
1SVR 630 794 R3300local signalling | Voltage Regeneration,
1SVR 630 794 R3300local signalling | Extreme Undervoltage <U (Phase loss),
1SVR 630 794 R3300local signalling | Extreme Overvoltage >U,
1SVR 630 794 R3300local signalling | Extreme Phase Asymmetry,
1SVR 630 794 R3300
1SVR 630 794 R3300
1SVR 630 794 R3300
1SVR 630 794 R3300diagnostic button
1SVR 630 794 R3300
1SVR 630 794 R3300
1SVR 630 794 R3300
1SVR 630 794 R3300safety reliability data | MTTF,
1SVR 630 794 R3300safety reliability data | B10,
1SVR 630 794 R3300 | MTTFd,
1SVR 630 794 R3300 | B10d,
1SVR 630 794 R3300
1SVR 630 794 R3300
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)standards | EN60947-5-1
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)product certifications
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)marking
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)directives
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)directives
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)directives
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O) | IEC60721-3-3,Climatic category,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O) | Germanisher Lloyd,Environmental category,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)ambient air temperature for storage | -25…+65 ¦ ,Storage,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)ambient air temperature for operation | -20…+60 ¦ ,Operation,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)relative humidity | IEC60068-2-30,Damp heat,XX
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O) | IEC60947-5-1,Cyclic Damp Heat Test,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)vibration resistance | IEC60068-2-6
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)shock resistance | IEC60068-2-27
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)bump resistance | IEC60068-2-29
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)seismic resistance | IEC60068-3-3
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)IP degree of protection | IEC60529,Terminal Block,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)IP degree of protection | IEC60529,Housing,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)IP degree of protection | IEC60529,Front Panel,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)width | Width,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)height | Height,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)depth | Depth,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)net weight
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)mounting support | IEC/EN 60715,Without socket,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)mounting support | IEC/EN 60715,With socket,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)mounting position | In relation to normal vertical mounting plane,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)Minimum distance to adjacent devices | Horizontal,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)Minimum distance to adjacent devices | Vertical,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)connections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)connections - terminals | IEC60947-1,Solid cable (spring terminal),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)connections - terminals | IEC60947-1,Flexible cable (spring terminal),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)tightening torque | 0.54Nm (Rec) 0.59Nm (Max) ¦ IEC60947-1,Tightening torque,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)cable stripping length | Cable stripping length,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)duty time
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | Generic immunity standard,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | IEC61000-4-5,Surge,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | Generic emission standard,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | Germanisher Lloyd,Conducted emission,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)pollution degree | IEC60664-1
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)overvoltage category | IEC60664-1
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)circuit group | Supply,Terminal
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)circuit group | Input 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)circuit group | Input 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)circuit group | Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)circuit group | Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)circuit group | Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O) | Supply,Rated
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O) | Input 1,Voltage
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O) | Input 2,Spec
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O) | Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O) | Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O) | Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Supply,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Input 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Input 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)dielectric strength | IEC60255-27,Supply / Input 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)dielectric strength | IEC60255-27,Supply / Input 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)dielectric strength | IEC60255-27,Supply / Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)dielectric strength | IEC60255-27,Supply / Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)dielectric strength | IEC60255-27,Supply / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)dielectric strength | IEC60255-27,Output 1 / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)dielectric strength | IEC60255-27,Input 1 / Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)dielectric strength | IEC60255-27,Input 1 / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)dielectric strength | IEC60255-27,Input 2 / Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)dielectric strength | IEC60255-27,Input 2 / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)dielectric strength | IEC60255-27,Input 3 / Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)dielectric strength | IEC60255-27,Input 3 / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)dielectric strength | IEC60255-27,Input 1 / Input 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)dielectric strength | IEC60255-27,Input 2 / Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)dielectric strength | IEC60255-27,Input 1 / Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)insulation resistance | IEC60255-27,Supply / Input 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)insulation resistance | IEC60255-27,Supply / Input 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)insulation resistance | IEC60255-27,Supply / Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)insulation resistance | IEC60255-27,Supply / Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)insulation resistance | IEC60255-27,Supply / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)insulation resistance | IEC60255-27,Output 1 / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)insulation resistance | IEC60255-27,Input 1 / Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)insulation resistance | IEC60255-27,Input 1 / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)insulation resistance | IEC60255-27,Input 2 / Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)insulation resistance | IEC60255-27,Input 2 / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)insulation resistance | IEC60255-27,Input 3 / Output 1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)insulation resistance | IEC60255-27,Input 3 / Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)insulation resistance | IEC60255-27,Input 1 / Input 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)insulation resistance | IEC60255-27,Input 2 / Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)insulation resistance | IEC60255-27,Input 1 / Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Us] rated supply voltage
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)supply voltage limits
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)polarity
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)supply frequency
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)supply frequency
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)power consumption
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)immunity to microbreaks
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)supply terminal
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)on-load factor
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)release of input voltage
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)monitoring functions | Phase lost ,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)monitoring functions | Phase sequence,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)monitoring functions | Over / undervoltage (symmetry windows mode),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)monitoring functions | Over voltage,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)monitoring functions | Undervoltage ,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)monitoring functions | Phase asymmetry,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)monitoring functions | Disconnection of neutral,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)monitoring functions | Voltage Regeneration,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)monitoring functions | Extreme undervoltage,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)monitoring functions | Extreme overvoltage,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)monitoring functions | Extreme asymmetry,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O) | Measurement mode,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)internal input resistance | Internal input resistance,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)input terminal | Input terminal,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)Input nominal voltage selection | Input nominal voltage selection,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)permissible input overload | permissible input overload,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)input frequency | Rated frequency,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)input frequency | Frequency operating range,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)setting accuracy of the switching threshold | Setting accuracy,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)repeat accuracy of the switching threshold | Repeat accuracy (constant parameters),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)measurement method | Measurement method,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)switching threshold drift | Measurement error with supply voltage variation,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)switching threshold drift | Measurement error with temperature variation,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)maximum measuring cycle | Maximum measuring cycles,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)measurement range | Phase lost ,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)measurement range | Phase sequence,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)measurement range | Over / undervoltage (symmetry windows mode),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)measurement range | Over voltage,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)measurement range | Undervoltage ,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)measurement range | Phase asymmetry,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)measurement range | Disconnection of neutral,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)measurement range | Voltage Regeneration,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)measurement range | Extreme undervoltage,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)measurement range | Extreme Overvoltage,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)measurement range | Extreme Asymmetry,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)tripping threshold | Phase cut,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)tripping threshold | Phase sequence,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)tripping threshold | Over / undervoltage (symmetry windows mode),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)tripping threshold | Over voltage,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)tripping threshold | Undervoltage ,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)tripping threshold | Phase asymmetry,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)tripping threshold | Disconnection of neutral,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)tripping threshold | Voltage Regeneration,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)tripping threshold | Extreme undervoltage (Phase loss),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)tripping threshold | Extreme Overvoltage,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)tripping threshold | Extreme Asymmetry,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)hysteresis | Phase cut,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)hysteresis | Phase sequence,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)hysteresis | Over / undervoltage (symmetry windows mode),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)hysteresis | Over voltage,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)hysteresis | Undervoltage ,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)hysteresis | Phase asymmetry,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)hysteresis | Disconnection of neutral,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)hysteresis | Voltage Regeneration,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)hysteresis | Extreme undervoltage (Phase loss),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)hysteresis | Extreme Overvoltage,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)hysteresis | Extreme Asymmetry,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)output type
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)output terminal
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)output logic | R1 (11-12-14),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)output logic | R2 (21-22-24),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)contacts material
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)mechanical durability | IEC61810-1
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electrical durability | - ¦ IEC60947-4-1,AC-1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electrical durability | - ¦ IEC60947-4-1,DC-1,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electrical durability | - ¦ IEC60947-5-1,AC-15,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electrical durability | - ¦ IEC60947-5-1,DC-13,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ie] rated operational current | IEC61810-1,Rated switching current,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)maximum switching capacity | Maximum switching voltage,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)maximum switching capacity | Maximum switching current,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)maximum switching capacity | Maximum switching capacity,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)minimum switching capacity | IEC60947-5-4,Minimum switching voltage,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)minimum switching capacity | IEC60947-5-4,Minimum switching current,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)minimum switching capacity | IEC60947-5-4,Minimum switching capacity,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)maximum voltage drop | IEC62314,Only for solid state output,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)maximum leakage current | IEC62314,Only for solid state output,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)thermal current | IEC60947-5-1
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)short circuit protection | IEC60947-5-1,Relay Output by external fuse,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)short circuit protection | IEC62314,Solid State Output by external fuse,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)time delay type | "OFF" delay,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)time delay type | "ON" delay,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)time delay type | Inhibition,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)time delay range | "OFF" delay,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)time delay range | "ON" delay,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)time delay range | Inhibition,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)response time | on crossing the threshold,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)response time
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)response time
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)response time
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)response time
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)power on delay
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)reset time | through Un power reset,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)reset time | through front panel reset,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)reset time | through input control reset,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)setting accuracy of time delay
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)repeat accuracy of time delay
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)time delay drift
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)time delay drift
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)status LED
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)local signalling | Power supply availability,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)local signalling | Power supply not availability,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)local signalling | Timing in-progress,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)local signalling | Output is energized,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)local signalling | Output is de-energized,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)local signalling | Range Setting Changes,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)local signalling | Phase Cut,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)local signalling | Phase Sequence Swap,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)local signalling | Undervoltage <U,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)local signalling | Overvoltage >U,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)local signalling | Phase Asymmetry,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)local signalling | Voltage Regeneration,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)local signalling | Extreme Undervoltage <U (Phase loss),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)local signalling | Extreme Overvoltage >U,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)local signalling | Extreme Phase Asymmetry,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)diagnostic button
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)safety reliability data | MTTF,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)safety reliability data | B10,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O) | MTTFd,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O) | B10d,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)
DPA51CM44
DPA51CM44standards | Not specified
DPA51CM44product certifications | UL, CSA
DPA51CM44marking | UL, CSA, CE
DPA51CM44directives | Not specified
DPA51CM44directives | Not specified
DPA51CM44directives | Not specified
DPA51CM44
DPA51CM44 | Not specified ¦ IEC60721-3-3,Climatic category,
DPA51CM44 | Germanisher Lloyd,Environmental category,
DPA51CM44ambient air temperature for storage | -30…+80, R.H. < 95% ¦ ,Storage,
DPA51CM44ambient air temperature for operation | -20…+50, R.H. < 95% ¦ ,Operation,
DPA51CM44relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,XX
DPA51CM44 | IEC60947-5-1,Cyclic Damp Heat Test,
DPA51CM44vibration resistance | Not specified ¦ IEC60068-2-6
DPA51CM44shock resistance | Not specified ¦ IEC60068-2-27
DPA51CM44bump resistance | IEC60068-2-29
DPA51CM44seismic resistance | IEC60068-3-3
DPA51CM44IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
DPA51CM44IP degree of protection | Not specified ¦ IEC60529,Housing,
DPA51CM44IP degree of protection | Not specified ¦ IEC60529,Front Panel,
DPA51CM44
DPA51CM44width | 17.5 x 81 x 67.2 ¦ ,Width,
DPA51CM44height | Height,
DPA51CM44depth | Depth,
DPA51CM44net weight | 75
DPA51CM44mounting support | Mounting in DIN rail according EN50022 ¦ IEC/EN 60715,Without socket,
DPA51CM44mounting support | - ¦ IEC/EN 60715,With socket,
DPA51CM44mounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
DPA51CM44Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
DPA51CM44Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
DPA51CM44connections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal),
DPA51CM44connections - terminals | Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
DPA51CM44connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
DPA51CM44connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
DPA51CM44tightening torque | 0.5Nm (Max) ¦ IEC60947-1,Tightening torque,
DPA51CM44cable stripping length | Not specified ¦ ,Cable stripping length,
DPA51CM44duty time | Not specified
DPA51CM44
DPA51CM44electromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard,
DPA51CM44electromagnetic compatibility | Not specified ¦ IEC61000-4-2,Electrostatic discharge,
DPA51CM44electromagnetic compatibility | Not specified ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
DPA51CM44electromagnetic compatibility | Not specified ¦ IEC61000-4-4,Fast transient / burst,
DPA51CM44electromagnetic compatibility | Not specified ¦ IEC61000-4-5,Surge,
DPA51CM44electromagnetic compatibility | Not specified ¦ IEC61000-4-6,Conducted RF disturbance,
DPA51CM44electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
DPA51CM44electromagnetic compatibility | Not specified ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
DPA51CM44electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
DPA51CM44electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
DPA51CM44electromagnetic compatibility | Not specified ¦ IEC61000-4-13,Low frequency harmonics,
DPA51CM44electromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
DPA51CM44electromagnetic compatibility | IEC50081-1 ¦ ,Generic emission standard,
DPA51CM44electromagnetic compatibility | Not specified ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
DPA51CM44electromagnetic compatibility | Not specified ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
DPA51CM44electromagnetic compatibility | - ¦ Germanisher Lloyd,Radiated emission from enclosure port,
DPA51CM44electromagnetic compatibility | Not specified ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
DPA51CM44electromagnetic compatibility | Not specified ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
DPA51CM44electromagnetic compatibility | - ¦ Germanisher Lloyd,Conducted emission,
DPA51CM44
DPA51CM44pollution degree | IEC60664-1
DPA51CM44overvoltage category | IEC60664-1
DPA51CM44circuit group | Supply,Terminal
DPA51CM44circuit group | Input 1,
DPA51CM44circuit group | Input 2,
DPA51CM44circuit group | Input 3,
DPA51CM44circuit group | Output 1,
DPA51CM44circuit group | Output 2,
DPA51CM44 | Supply,Rated
DPA51CM44 | Input 1,Voltage
DPA51CM44 | Input 2,Spec
DPA51CM44 | Input 3,
DPA51CM44 | Output 1,
DPA51CM44 | Output 2,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Supply,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Input 1,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Input 2,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Input 3,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Output 1,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Output 2,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
DPA51CM44dielectric strength | IEC60255-27,Supply / Input 1,
DPA51CM44dielectric strength | IEC60255-27,Supply / Input 2,
DPA51CM44dielectric strength | IEC60255-27,Supply / Input 3,
DPA51CM44dielectric strength | IEC60255-27,Supply / Output 1,
DPA51CM44dielectric strength | IEC60255-27,Supply / Output 2,
DPA51CM44dielectric strength | IEC60255-27,Output 1 / Output 2,
DPA51CM44dielectric strength | IEC60255-27,Input 1 / Output 1,
DPA51CM44dielectric strength | IEC60255-27,Input 1 / Output 2,
DPA51CM44dielectric strength | IEC60255-27,Input 2 / Output 1,
DPA51CM44dielectric strength | IEC60255-27,Input 2 / Output 2,
DPA51CM44dielectric strength | IEC60255-27,Input 3 / Output 1,
DPA51CM44dielectric strength | IEC60255-27,Input 3 / Output 2,
DPA51CM44dielectric strength | IEC60255-27,Input 1 / Input 2,
DPA51CM44dielectric strength | IEC60255-27,Input 2 / Input 3,
DPA51CM44dielectric strength | IEC60255-27,Input 1 / Input 3,
DPA51CM44insulation resistance | IEC60255-27,Supply / Input 1,
DPA51CM44insulation resistance | IEC60255-27,Supply / Input 2,
DPA51CM44insulation resistance | IEC60255-27,Supply / Input 3,
DPA51CM44insulation resistance | IEC60255-27,Supply / Output 1,
DPA51CM44insulation resistance | IEC60255-27,Supply / Output 2,
DPA51CM44insulation resistance | IEC60255-27,Output 1 / Output 2,
DPA51CM44insulation resistance | IEC60255-27,Input 1 / Output 1,
DPA51CM44insulation resistance | IEC60255-27,Input 1 / Output 2,
DPA51CM44insulation resistance | IEC60255-27,Input 2 / Output 1,
DPA51CM44insulation resistance | IEC60255-27,Input 2 / Output 2,
DPA51CM44insulation resistance | IEC60255-27,Input 3 / Output 1,
DPA51CM44insulation resistance | IEC60255-27,Input 3 / Output 2,
DPA51CM44insulation resistance | IEC60255-27,Input 1 / Input 2,
DPA51CM44insulation resistance | IEC60255-27,Input 2 / Input 3,
DPA51CM44insulation resistance | IEC60255-27,Input 1 / Input 3,
DPA51CM44
DPA51CM44[Us] rated supply voltage | ~ 3 x 208…3 x 480
DPA51CM44supply voltage limits | ~ 3 x 177…3 x 550
DPA51CM44polarity
DPA51CM44supply frequency | 50 / 60
DPA51CM44supply frequency | 45…66
DPA51CM44power consumption | 13VA (400VAC, 50Hz) by L2, L3
DPA51CM44immunity to microbreaks | -
DPA51CM44supply terminal | L1-L2-L3
DPA51CM44on-load factor
DPA51CM44release of input voltage
DPA51CM44
DPA51CM44monitoring functions | · ¦ ,Phase lost ,
DPA51CM44monitoring functions | · ¦ ,Phase sequence,
DPA51CM44monitoring functions | - ¦ ,Over / undervoltage (symmetry windows mode),
DPA51CM44monitoring functions | - ¦ ,Over voltage,
DPA51CM44monitoring functions | - ¦ ,Undervoltage ,
DPA51CM44monitoring functions | - ¦ ,Phase asymmetry,
DPA51CM44monitoring functions | - ¦ ,Disconnection of neutral,
DPA51CM44monitoring functions | - ¦ ,Voltage Regeneration,
DPA51CM44monitoring functions | Extreme undervoltage,
DPA51CM44monitoring functions | Extreme overvoltage,
DPA51CM44monitoring functions | Extreme asymmetry,
DPA51CM44 | Resistive Voltage Step Down ¦ ,Measurement mode,
DPA51CM44internal input resistance | Not specified ¦ ,Internal input resistance,
DPA51CM44input terminal | L1-L2-L3 ¦ ,Input terminal,
DPA51CM44Input nominal voltage selection | Fixed @ ~ 3 x 177…3 x 550 ¦ ,Input nominal voltage selection,
DPA51CM44permissible input overload | Not specified ¦ ,permissible input overload,
DPA51CM44input frequency | 50 / 60 ¦ ,Rated frequency,
DPA51CM44input frequency | 45…66 ¦ ,Frequency operating range,
DPA51CM44setting accuracy of the switching threshold | - ¦ ,Setting accuracy,
DPA51CM44repeat accuracy of the switching threshold | +/- 0.5% on full scale ¦ ,Repeat accuracy (constant parameters),
DPA51CM44measurement method | Not specified ¦ ,Measurement method,
DPA51CM44switching threshold drift | - ¦ ,Measurement error with supply voltage variation,
DPA51CM44switching threshold drift | 0.1% / oC ¦ ,Measurement error with temperature variation,
DPA51CM44maximum measuring cycle | - ¦ ,Maximum measuring cycles,
DPA51CM44measurement range | Not specified ¦ ,Phase lost ,
DPA51CM44measurement range | Not specified ¦ ,Phase sequence,
DPA51CM44measurement range | - ¦ ,Over / undervoltage (symmetry windows mode),
DPA51CM44measurement range | - ¦ ,Over voltage,
DPA51CM44measurement range | - ¦ ,Undervoltage ,
DPA51CM44measurement range | - ¦ ,Phase asymmetry,
DPA51CM44measurement range | Disconnection of neutral,
DPA51CM44measurement range | Voltage Regeneration,
DPA51CM44measurement range | Extreme undervoltage,
DPA51CM44measurement range | Extreme Overvoltage,
DPA51CM44measurement range | Extreme Asymmetry,
DPA51CM44tripping threshold | 1 phase below 85% of other phase ¦ ,Phase cut,
DPA51CM44tripping threshold | - ¦ ,Phase sequence,
DPA51CM44tripping threshold | - ¦ ,Over / undervoltage (symmetry windows mode),
DPA51CM44tripping threshold | - ¦ ,Over voltage,
DPA51CM44tripping threshold | - ¦ ,Undervoltage ,
DPA51CM44tripping threshold | - ¦ ,Phase asymmetry,
DPA51CM44tripping threshold | Disconnection of neutral,
DPA51CM44tripping threshold | Voltage Regeneration,
DPA51CM44tripping threshold | Extreme undervoltage (Phase loss),
DPA51CM44tripping threshold | Extreme Overvoltage,
DPA51CM44tripping threshold | Extreme Asymmetry,
DPA51CM44hysteresis | - ¦ ,Phase cut,
DPA51CM44hysteresis | - ¦ ,Phase sequence,
DPA51CM44hysteresis | - ¦ ,Over / undervoltage (symmetry windows mode),
DPA51CM44hysteresis | - ¦ ,Over voltage,
DPA51CM44hysteresis | - ¦ ,Undervoltage ,
DPA51CM44hysteresis | - ¦ ,Phase asymmetry,
DPA51CM44hysteresis | Disconnection of neutral,
DPA51CM44hysteresis | Voltage Regeneration,
DPA51CM44hysteresis | Extreme undervoltage (Phase loss),
DPA51CM44hysteresis | Extreme Overvoltage,
DPA51CM44hysteresis | Extreme Asymmetry,
DPA51CM44
DPA51CM44output type | 1 x C/O relay contact
DPA51CM44output terminal
DPA51CM44output logic | - ¦ ,R1 (11-12-14),
DPA51CM44output logic | R2 (21-22-24),
DPA51CM44contacts material | AgSnO2
DPA51CM44mechanical durability | >= 30 x 106 switching cycles ¦ IEC61810-1
DPA51CM44electrical durability | >= 1 x 105 switching cycles @ 5A, 250VAC ¦ IEC60947-4-1,AC-1,
DPA51CM44electrical durability | IEC60947-4-1,DC-1,
DPA51CM44electrical durability | IEC60947-5-1,AC-15,
DPA51CM44electrical durability | IEC60947-5-1,DC-13,
DPA51CM44[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
DPA51CM44[Ie] rated operational current | IEC61810-1,Rated switching current,
DPA51CM44maximum switching capacity | - ¦ ,Maximum switching voltage,
DPA51CM44maximum switching capacity | - ¦ ,Maximum switching current,
DPA51CM44maximum switching capacity | Maximum switching capacity,
DPA51CM44minimum switching capacity | IEC60947-5-4,Minimum switching voltage,
DPA51CM44minimum switching capacity | IEC60947-5-4,Minimum switching current,
DPA51CM44minimum switching capacity | IEC60947-5-4,Minimum switching capacity,
DPA51CM44maximum voltage drop | IEC62314,Only for solid state output,
DPA51CM44maximum leakage current | IEC62314,Only for solid state output,
DPA51CM44thermal current | IEC60947-5-1
DPA51CM44short circuit protection | IEC60947-5-1,Relay Output by external fuse,
DPA51CM44short circuit protection | IEC62314,Solid State Output by external fuse,
DPA51CM44
DPA51CM44time delay type | - ¦ ,"OFF" delay,
DPA51CM44time delay type | - ¦ ,"ON" delay,
DPA51CM44time delay type | - ¦ ,Inhibition,
DPA51CM44time delay range | - ¦ ,"OFF" delay,
DPA51CM44time delay range | - ¦ ,"ON" delay,
DPA51CM44time delay range | - ¦ ,Inhibition,
DPA51CM44response time | < 100 for ON delay ; < 300 for OFF delay ¦ ,on crossing the threshold,
DPA51CM44response time
DPA51CM44response time
DPA51CM44response time
DPA51CM44response time
DPA51CM44power on delay | -
DPA51CM44reset time | - ¦ ,through Un power reset,
DPA51CM44reset time | through front panel reset,
DPA51CM44reset time | through input control reset,
DPA51CM44setting accuracy of time delay | -
DPA51CM44repeat accuracy of time delay | -
DPA51CM44time delay drift | -
DPA51CM44time delay drift | -
DPA51CM44
DPA51CM44status LED
DPA51CM44local signalling | Power supply availability,
DPA51CM44local signalling | Power supply not availability,
DPA51CM44local signalling | Timing in-progress,
DPA51CM44local signalling | Output is energized,
DPA51CM44local signalling | Output is de-energized,
DPA51CM44local signalling | Range Setting Changes,
DPA51CM44local signalling | Phase Cut,
DPA51CM44local signalling | Phase Sequence Swap,
DPA51CM44local signalling | Undervoltage <U,
DPA51CM44local signalling | Overvoltage >U,
DPA51CM44local signalling | Phase Asymmetry,
DPA51CM44local signalling | Voltage Regeneration,
DPA51CM44local signalling | Extreme Undervoltage <U (Phase loss),
DPA51CM44local signalling | Extreme Overvoltage >U,
DPA51CM44local signalling | Extreme Phase Asymmetry,
DPA51CM44
DPA51CM44
DPA51CM44
DPA51CM44diagnostic button
DPA51CM44
DPA51CM44
DPA51CM44
DPA51CM44safety reliability data | MTTF,
DPA51CM44safety reliability data | B10,
DPA51CM44 | MTTFd,
DPA51CM44 | B10d,
DPA51CM44
DPA51CM44
RM22LG11MR
RM22LG11MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22LG11MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22LG11MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22LG11MRdirectives | 2014/35/EU
RM22LG11MRdirectives | 2014/30/EU
RM22LG11MRdirectives | 2011/65/EU
RM22LG11MR
RM22LG11MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category,
RM22LG11MR | Class C ¦ Germanisher Lloyd,Environmental category,
RM22LG11MRambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22LG11MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22LG11MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22LG11MR | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22LG11MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22LG11MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22LG11MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22LG11MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22LG11MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22LG11MRIP degree of protection | IP40 ¦ IEC60529,Housing,
RM22LG11MRIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22LG11MR
RM22LG11MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22LG11MRheight | Height,
RM22LG11MRdepth | Depth,
RM22LG11MRnet weight | 100
RM22LG11MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22LG11MRmounting support | - ¦ IEC/EN 60715,With socket,
RM22LG11MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22LG11MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22LG11MRMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22LG11MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22LG11MRconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22LG11MRconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22LG11MRconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22LG11MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22LG11MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22LG11MRduty time | 1
RM22LG11MR
RM22LG11MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22LG11MRelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22LG11MRelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22LG11MRelectromagnetic compatibility | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22LG11MRelectromagnetic compatibility | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22LG11MRelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22LG11MRelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22LG11MRelectromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22LG11MRelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22LG11MRelectromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
RM22LG11MRelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22LG11MRelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22LG11MRelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22LG11MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22LG11MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22LG11MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22LG11MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22LG11MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22LG11MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22LG11MR
RM22LG11MRpollution degree | 3 ¦ IEC60664-1
RM22LG11MRovervoltage category | 3 ¦ IEC60664-1
RM22LG11MRcircuit group | A1, A2 ¦ ,Supply,Terminal
RM22LG11MRcircuit group | Min, Max, C ¦ ,Input 1,
RM22LG11MRcircuit group | - ¦ ,Input 2,
RM22LG11MRcircuit group | - ¦ ,Input 3,
RM22LG11MRcircuit group | 11,12,14 ¦ ,Output 1,
RM22LG11MRcircuit group | - ¦ ,Output 2,
RM22LG11MR | 24…240 AC/DC ¦ ,Supply,Rated
RM22LG11MR | Level probe ¦ ,Input 1,Voltage
RM22LG11MR | - ¦ ,Input 2,Spec
RM22LG11MR | - ¦ ,Input 3,
RM22LG11MR | 250V ¦ ,Output 1,
RM22LG11MR | - ¦ ,Output 2,
RM22LG11MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply,
RM22LG11MR[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 1,
RM22LG11MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM22LG11MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM22LG11MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22LG11MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Output 2,
RM22LG11MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22LG11MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22LG11MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22LG11MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 1,
RM22LG11MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Output 2,
RM22LG11MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Output 1 / Output 2,
RM22LG11MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 1,
RM22LG11MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22LG11MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22LG11MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22LG11MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22LG11MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22LG11MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22LG11MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22LG11MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22LG11MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22LG11MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22LG11MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Output 2,
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1 / Output 2,
RM22LG11MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22LG11MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22LG11MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM22LG11MRdielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM22LG11MRdielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM22LG11MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22LG11MRdielectric strength | - ¦ IEC60255-27,Supply / Output 2,
RM22LG11MRdielectric strength | - ¦ IEC60255-27,Output 1 / Output 2,
RM22LG11MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM22LG11MRdielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM22LG11MRdielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM22LG11MRdielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM22LG11MRdielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM22LG11MRdielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM22LG11MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22LG11MRdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22LG11MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22LG11MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM22LG11MRinsulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM22LG11MRinsulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM22LG11MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22LG11MRinsulation resistance | - ¦ IEC60255-27,Supply / Output 2,
RM22LG11MRinsulation resistance | - ¦ IEC60255-27,Output 1 / Output 2,
RM22LG11MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM22LG11MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM22LG11MRinsulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM22LG11MRinsulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM22LG11MRinsulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM22LG11MRinsulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM22LG11MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22LG11MRinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22LG11MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22LG11MR
RM22LG11MR[Us] rated supply voltage | ~/-- 24…240
RM22LG11MRsupply voltage limits | ~/-- 20.4…264
RM22LG11MRpolarity
RM22LG11MRsupply frequency | 50 / 60
RM22LG11MRsupply frequency | 45…66
RM22LG11MRpower consumption | ~ 3.5VA, ~5VA, 1.5W
RM22LG11MRimmunity to microbreaks | ~ 90, -- 100
RM22LG11MRsupply terminal | A1-A2
RM22LG11MRon-load factor | 1
RM22LG11MRrelease of input voltage | -
RM22LG11MR
RM22LG11MRmonitoring functions | - governed by response time - status reflects to both R1 & R2 ¦ ,1 level - Fill operation,
RM22LG11MRmonitoring functions | - governed by response time - status reflects to both R1 & R2 ¦ ,1 level - Empty operation,
RM22LG11MRmonitoring functions | - governed by response time - status reflects to both R1 & R2 ¦ ,2 level - Fill operation,
RM22LG11MRmonitoring functions | - governed by response time - status reflects to both R1 & R2 ¦ ,2 level - Empty operation,
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR | Measurement mode,
RM22LG11MRinternal input resistance | - ¦ ,Internal input resistance,
RM22LG11MRinput terminal | Min-Max-C ¦ ,Input terminal,
RM22LG11MRMaximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage,
RM22LG11MRMaximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
RM22LG11MRMaximum length of probes cable | 100 ¦ ,Maximum length of probes cable,
RM22LG11MRinput frequency | 1 for LS 2.2 for St 4.7 for HS ¦ ,Maximum cable capacitance,
RM22LG11MRsetting accuracy of the switching threshold | +/- 10% of full scale value ¦ ,Setting accuracy,
RM22LG11MRrepeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22LG11MRmeasurement method | Liquid level resistive probe ¦ ,Measurement method,
RM22LG11MRswitching threshold drift | < 1% over whole range ¦ ,Measurement error with supply voltage variation,
RM22LG11MRswitching threshold drift | 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22LG11MRmaximum measuring cycle | Maximum measuring cycles,
RM22LG11MRmeasurement range | 5kW…100kW ¦ ,1 level - Fill operation,
RM22LG11MRmeasurement range | 5kW…100kW ¦ ,1 level - Empty operation,
RM22LG11MRmeasurement range | 5kW…100kW ¦ ,2 level - Fill operation,
RM22LG11MRmeasurement range | 5kW…100kW ¦ ,2 level - Empty operation,
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MRtripping threshold | Adjustable 5%...100% of 100kW ¦ ,1 level - Fill operation,
RM22LG11MRtripping threshold | Adjustable 5%...100% of 100kW ¦ ,1 level - Empty operation,
RM22LG11MRtripping threshold | Adjustable 5%...100% of 100kW ¦ ,2 level - Fill operation,
RM22LG11MRtripping threshold | Adjustable 5%...100% of 100kW ¦ ,2 level - Empty operation,
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MRhysteresis | - ¦ ,1 level - Fill operation,
RM22LG11MRhysteresis | - ¦ ,1 level - Empty operation,
RM22LG11MRhysteresis | - ¦ ,2 level - Fill operation,
RM22LG11MRhysteresis | - ¦ ,2 level - Empty operation,
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MR
RM22LG11MRoutput type | 1 x C/O relay contacts
RM22LG11MRoutput terminal | 11/12/14,
RM22LG11MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22LG11MRoutput logic | - ¦ ,R2 (21-22-24),
RM22LG11MRcontacts material | Cadmium free
RM22LG11MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22LG11MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22LG11MRelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22LG11MRelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22LG11MRelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22LG11MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22LG11MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22LG11MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22LG11MRmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM22LG11MRmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM22LG11MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22LG11MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22LG11MRminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22LG11MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22LG11MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22LG11MRthermal current | 8A ¦ IEC60947-5-1
RM22LG11MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22LG11MRshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22LG11MR
RM22LG11MRtime delay type | - ¦ ,"OFF" delay,
RM22LG11MRtime delay type | Yes ¦ ,"ON" delay,
RM22LG11MRtime delay type | - ¦ ,Inhibition,
RM22LG11MRtime delay range | - ¦ ,"OFF" delay,
RM22LG11MRtime delay range | - ¦ ,"ON" delay,
RM22LG11MRtime delay range | - ¦ ,Inhibition,
RM22LG11MRresponse time | 0
RM22LG11MRresponse time
RM22LG11MRresponse time
RM22LG11MRresponse time
RM22LG11MRresponse time
RM22LG11MRpower on delay | 0
RM22LG11MRreset time | 0
RM22LG11MRreset time | through front panel reset,
RM22LG11MRreset time | through input control reset,
RM22LG11MRsetting accuracy of time delay | +/- 10% of full scales
RM22LG11MRrepeat accuracy of time delay | +/- 2%
RM22LG11MRtime delay drift | < 1
RM22LG11MRtime delay drift | < 0.05
RM22LG11MR
RM22LG11MRstatus LED | R (Amber)
RM22LG11MRlocal signalling | - ¦ ,Power supply availability,
RM22LG11MRlocal signalling | - ¦ ,Power supply not availability,
RM22LG11MRlocal signalling | - ¦ ,Timing in-progress,
RM22LG11MRlocal signalling | R - ON ¦ ,Output is energized,
RM22LG11MRlocal signalling | R - OFF ¦ ,Output is de-energized,
RM22LG11MRlocal signalling | - ¦ ,Range Setting Changes,
RM22LG11MRlocal signalling
RM22LG11MRlocal signalling
RM22LG11MRlocal signalling
RM22LG11MRlocal signalling
RM22LG11MRlocal signalling
RM22LG11MRlocal signalling
RM22LG11MRlocal signalling
RM22LG11MRlocal signalling
RM22LG11MRlocal signalling
RM22LG11MR
RM22LG11MR | -
RM22LG11MR | 1) Will always illuminated when power is supplied to the product
RM22LG11MRdiagnostic button | Output will be de-energized when activated
RM22LG11MR | -
RM22LG11MR | 1) Output is energized/ de-energized according to function diagram 2) When input monitored @ fault condition, output is always de-energized
RM22LG11MR
RM22LG11MRsafety reliability data | 1,100,000 hours ¦ ,MTTF,
RM22LG11MRsafety reliability data | 120,000 hours ¦ ,B10,
RM22LG11MR | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22LG11MR | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22LG11MR
RM22LG11MT
RM22LG11MTstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22LG11MTproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22LG11MTmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22LG11MTdirectives | 2014/35/EU
RM22LG11MTdirectives | 2014/30/EU
RM22LG11MTdirectives | 2011/65/EU
RM22LG11MT
RM22LG11MT | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category,
RM22LG11MT | Class C ¦ Germanisher Lloyd,Environmental category,
RM22LG11MTambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22LG11MTambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22LG11MTrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22LG11MT | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22LG11MTvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22LG11MTshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22LG11MTbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22LG11MTseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22LG11MTIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22LG11MTIP degree of protection | IP40 ¦ IEC60529,Housing,
RM22LG11MTIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22LG11MT
RM22LG11MTwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22LG11MTheight | Height,
RM22LG11MTdepth | Depth,
RM22LG11MTnet weight | 100
RM22LG11MTmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22LG11MTmounting support | - ¦ IEC/EN 60715,With socket,
RM22LG11MTmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22LG11MTMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22LG11MTMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22LG11MTconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22LG11MTconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22LG11MTconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22LG11MTconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22LG11MTtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22LG11MTcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22LG11MTduty time | 1
RM22LG11MT
RM22LG11MTelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22LG11MTelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22LG11MTelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22LG11MTelectromagnetic compatibility | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22LG11MTelectromagnetic compatibility | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22LG11MTelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22LG11MTelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22LG11MTelectromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22LG11MTelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22LG11MTelectromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
RM22LG11MTelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22LG11MTelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22LG11MTelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22LG11MTelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22LG11MTelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22LG11MTelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22LG11MTelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22LG11MTelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22LG11MTelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22LG11MT
RM22LG11MTpollution degree | 3 ¦ IEC60664-1
RM22LG11MTovervoltage category | 3 ¦ IEC60664-1
RM22LG11MTcircuit group | A1, A2 ¦ ,Supply,Terminal
RM22LG11MTcircuit group | Min, Max, C ¦ ,Input 1,
RM22LG11MTcircuit group | - ¦ ,Input 2,
RM22LG11MTcircuit group | - ¦ ,Input 3,
RM22LG11MTcircuit group | 11,12,14 ¦ ,Output 1,
RM22LG11MTcircuit group | - ¦ ,Output 2,
RM22LG11MT | 380…415 AC ¦ ,Supply,Rated
RM22LG11MT | Level probe ¦ ,Input 1,Voltage
RM22LG11MT | - ¦ ,Input 2,Spec
RM22LG11MT | - ¦ ,Input 3,
RM22LG11MT | 250V ¦ ,Output 1,
RM22LG11MT | - ¦ ,Output 2,
RM22LG11MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply,
RM22LG11MT[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 1,
RM22LG11MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM22LG11MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM22LG11MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22LG11MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Output 2,
RM22LG11MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22LG11MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22LG11MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22LG11MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply / Output 1,
RM22LG11MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Output 2,
RM22LG11MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Output 1 / Output 2,
RM22LG11MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 1,
RM22LG11MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22LG11MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22LG11MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22LG11MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22LG11MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22LG11MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22LG11MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22LG11MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22LG11MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22LG11MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22LG11MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Output 2,
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1 / Output 2,
RM22LG11MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22LG11MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22LG11MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM22LG11MTdielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM22LG11MTdielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM22LG11MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22LG11MTdielectric strength | - ¦ IEC60255-27,Supply / Output 2,
RM22LG11MTdielectric strength | - ¦ IEC60255-27,Output 1 / Output 2,
RM22LG11MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM22LG11MTdielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM22LG11MTdielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM22LG11MTdielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM22LG11MTdielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM22LG11MTdielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM22LG11MTdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22LG11MTdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22LG11MTdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22LG11MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM22LG11MTinsulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM22LG11MTinsulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM22LG11MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22LG11MTinsulation resistance | - ¦ IEC60255-27,Supply / Output 2,
RM22LG11MTinsulation resistance | - ¦ IEC60255-27,Output 1 / Output 2,
RM22LG11MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM22LG11MTinsulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM22LG11MTinsulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM22LG11MTinsulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM22LG11MTinsulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM22LG11MTinsulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM22LG11MTinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22LG11MTinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22LG11MTinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22LG11MT
RM22LG11MT[Us] rated supply voltage | ~380…415
RM22LG11MTsupply voltage limits | ~323…456.5
RM22LG11MTpolarity
RM22LG11MTsupply frequency | 50 / 60
RM22LG11MTsupply frequency | 45…66
RM22LG11MTpower consumption | ~ 10VA ~ 8VA
RM22LG11MTimmunity to microbreaks | ~ 90, -- 100
RM22LG11MTsupply terminal | A1-A2
RM22LG11MTon-load factor | 1
RM22LG11MTrelease of input voltage | -
RM22LG11MT
RM22LG11MTmonitoring functions | - governed by response time - status reflects to both R1 & R2 ¦ ,1 level - Fill operation,
RM22LG11MTmonitoring functions | - governed by response time - status reflects to both R1 & R2 ¦ ,1 level - Empty operation,
RM22LG11MTmonitoring functions | - governed by response time - status reflects to both R1 & R2 ¦ ,2 level - Fill operation,
RM22LG11MTmonitoring functions | - governed by response time - status reflects to both R1 & R2 ¦ ,2 level - Empty operation,
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT | Measurement mode,
RM22LG11MTinternal input resistance | - ¦ ,Internal input resistance,
RM22LG11MTinput terminal | Min-Max-C ¦ ,Input terminal,
RM22LG11MTMaximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage,
RM22LG11MTMaximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
RM22LG11MTMaximum length of probes cable | 100 ¦ ,Maximum length of probes cable,
RM22LG11MTinput frequency | 1 for LS 2.2 for St 4.7 for HS ¦ ,Maximum cable capacitance,
RM22LG11MTsetting accuracy of the switching threshold | +/- 10% of full scale value ¦ ,Setting accuracy,
RM22LG11MTrepeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22LG11MTmeasurement method | Liquid level resistive probe ¦ ,Measurement method,
RM22LG11MTswitching threshold drift | < 1% over whole range ¦ ,Measurement error with supply voltage variation,
RM22LG11MTswitching threshold drift | 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22LG11MTmaximum measuring cycle | Maximum measuring cycles,
RM22LG11MTmeasurement range | 5kW…100kW ¦ ,1 level - Fill operation,
RM22LG11MTmeasurement range | 5kW…100kW ¦ ,1 level - Empty operation,
RM22LG11MTmeasurement range | 5kW…100kW ¦ ,2 level - Fill operation,
RM22LG11MTmeasurement range | 5kW…100kW ¦ ,2 level - Empty operation,
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MTtripping threshold | Adjustable 5%...100% of 100kW ¦ ,1 level - Fill operation,
RM22LG11MTtripping threshold | Adjustable 5%...100% of 100kW ¦ ,1 level - Empty operation,
RM22LG11MTtripping threshold | Adjustable 5%...100% of 100kW ¦ ,2 level - Fill operation,
RM22LG11MTtripping threshold | Adjustable 5%...100% of 100kW ¦ ,2 level - Empty operation,
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MThysteresis | - ¦ ,1 level - Fill operation,
RM22LG11MThysteresis | - ¦ ,1 level - Empty operation,
RM22LG11MThysteresis | - ¦ ,2 level - Fill operation,
RM22LG11MThysteresis | - ¦ ,2 level - Empty operation,
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MT
RM22LG11MToutput type | 1 x C/O relay contacts
RM22LG11MToutput terminal | 11/12/14,
RM22LG11MToutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22LG11MToutput logic | - ¦ ,R2 (21-22-24),
RM22LG11MTcontacts material | Cadmium free
RM22LG11MTmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22LG11MTelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22LG11MTelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22LG11MTelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22LG11MTelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22LG11MT[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22LG11MT[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22LG11MTmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22LG11MTmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM22LG11MTmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM22LG11MTminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22LG11MTminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22LG11MTminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22LG11MTmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22LG11MTmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22LG11MTthermal current | 8A ¦ IEC60947-5-1
RM22LG11MTshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22LG11MTshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22LG11MT
RM22LG11MTtime delay type | - ¦ ,"OFF" delay,
RM22LG11MTtime delay type | Yes ¦ ,"ON" delay,
RM22LG11MTtime delay type | - ¦ ,Inhibition,
RM22LG11MTtime delay range | - ¦ ,"OFF" delay,
RM22LG11MTtime delay range | - ¦ ,"ON" delay,
RM22LG11MTtime delay range | - ¦ ,Inhibition,
RM22LG11MTresponse time | 0
RM22LG11MTresponse time
RM22LG11MTresponse time
RM22LG11MTresponse time
RM22LG11MTresponse time
RM22LG11MTpower on delay | 0
RM22LG11MTreset time | 0
RM22LG11MTreset time | through front panel reset,
RM22LG11MTreset time | through input control reset,
RM22LG11MTsetting accuracy of time delay | +/- 10% of full scales
RM22LG11MTrepeat accuracy of time delay | +/- 2%
RM22LG11MTtime delay drift | < 1
RM22LG11MTtime delay drift | < 0.05
RM22LG11MT
RM22LG11MTstatus LED | R (Amber)
RM22LG11MTlocal signalling | - ¦ ,Power supply availability,
RM22LG11MTlocal signalling | - ¦ ,Power supply not availability,
RM22LG11MTlocal signalling | - ¦ ,Timing in-progress,
RM22LG11MTlocal signalling | R - ON ¦ ,Output is energized,
RM22LG11MTlocal signalling | R - OFF ¦ ,Output is de-energized,
RM22LG11MTlocal signalling | - ¦ ,Range Setting Changes,
RM22LG11MTlocal signalling
RM22LG11MTlocal signalling
RM22LG11MTlocal signalling
RM22LG11MTlocal signalling
RM22LG11MTlocal signalling
RM22LG11MTlocal signalling
RM22LG11MTlocal signalling
RM22LG11MTlocal signalling
RM22LG11MTlocal signalling
RM22LG11MT
RM22LG11MT | -
RM22LG11MT | 1) Will always illuminated when power is supplied to the product
RM22LG11MTdiagnostic button | Output will be de-energized when activated
RM22LG11MT | -
RM22LG11MT | 1) Output is energized/ de-energized according to function diagram 2) When input monitored @ fault condition, output is always de-energized
RM22LG11MT
RM22LG11MTsafety reliability data | 1,100,000 hours ¦ ,MTTF,
RM22LG11MTsafety reliability data | 120,000 hours ¦ ,B10,
RM22LG11MT | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22LG11MT | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22LG11MT
RM22LA32MR
RM22LA32MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22LA32MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22LA32MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22LA32MRdirectives | 2014/35/EU
RM22LA32MRdirectives | 2014/30/EU
RM22LA32MRdirectives | 2011/65/EU
RM22LA32MR
RM22LA32MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category,
RM22LA32MR | Class C ¦ Germanisher Lloyd,Environmental category,
RM22LA32MRambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22LA32MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22LA32MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22LA32MR | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22LA32MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22LA32MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22LA32MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22LA32MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22LA32MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22LA32MRIP degree of protection | IP40 ¦ IEC60529,Housing,
RM22LA32MRIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22LA32MR
RM22LA32MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22LA32MRheight | Height,
RM22LA32MRdepth | Depth,
RM22LA32MRnet weight | 110
RM22LA32MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22LA32MRmounting support | - ¦ IEC/EN 60715,With socket,
RM22LA32MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22LA32MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22LA32MRMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22LA32MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22LA32MRconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22LA32MRconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22LA32MRconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22LA32MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22LA32MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22LA32MRduty time | 1
RM22LA32MR
RM22LA32MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22LA32MRelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22LA32MRelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22LA32MRelectromagnetic compatibility | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22LA32MRelectromagnetic compatibility | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22LA32MRelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22LA32MRelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22LA32MRelectromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22LA32MRelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22LA32MRelectromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
RM22LA32MRelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22LA32MRelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22LA32MRelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22LA32MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22LA32MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22LA32MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22LA32MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22LA32MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22LA32MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22LA32MR
RM22LA32MRpollution degree | 3 ¦ IEC60664-1
RM22LA32MRovervoltage category | 3 ¦ IEC60664-1
RM22LA32MRcircuit group | A1, A2 ¦ ,Supply,Terminal
RM22LA32MRcircuit group | Min, Max, C ¦ ,Input 1,
RM22LA32MRcircuit group | - ¦ ,Input 2,
RM22LA32MRcircuit group | - ¦ ,Input 3,
RM22LA32MRcircuit group | 11,12,14 ¦ ,Output 1,
RM22LA32MRcircuit group | 21,22,24 ¦ ,Output 2,
RM22LA32MR | 24…240 AC/DC ¦ ,Supply,Rated
RM22LA32MR | Level probe ¦ ,Input 1,Voltage
RM22LA32MR | - ¦ ,Input 2,Spec
RM22LA32MR | - ¦ ,Input 3,
RM22LA32MR | 250V ¦ ,Output 1,
RM22LA32MR | 250V ¦ ,Output 2,
RM22LA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply,
RM22LA32MR[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 1,
RM22LA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM22LA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM22LA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22LA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22LA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22LA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22LA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22LA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 1,
RM22LA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 2,
RM22LA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22LA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 1,
RM22LA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 2,
RM22LA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22LA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22LA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22LA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22LA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22LA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22LA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22LA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22LA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM22LA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM22LA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM22LA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22LA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22LA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22LA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22LA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22LA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22LA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22LA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22LA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM22LA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2,
RM22LA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22LA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22LA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22LA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22LA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22LA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22LA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22LA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM22LA32MRdielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM22LA32MRdielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM22LA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22LA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22LA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22LA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM22LA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2,
RM22LA32MRdielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM22LA32MRdielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM22LA32MRdielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM22LA32MRdielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM22LA32MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22LA32MRdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22LA32MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22LA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM22LA32MRinsulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM22LA32MRinsulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM22LA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22LA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22LA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22LA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM22LA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2,
RM22LA32MRinsulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM22LA32MRinsulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM22LA32MRinsulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM22LA32MRinsulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM22LA32MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22LA32MRinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22LA32MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22LA32MR
RM22LA32MR[Us] rated supply voltage | ~/-- 24…240
RM22LA32MRsupply voltage limits | ~/-- 20.4…264
RM22LA32MRpolarity
RM22LA32MRsupply frequency | 50 / 60
RM22LA32MRsupply frequency | 45…66
RM22LA32MRpower consumption | ~ 3.5VA, ~5VA, 1.5W
RM22LA32MRimmunity to microbreaks | ~ 90, -- 100
RM22LA32MRsupply terminal | A1-A2
RM22LA32MRon-load factor | 1
RM22LA32MRrelease of input voltage | -
RM22LA32MR
RM22LA32MRmonitoring functions | - governed by time delay - status reflects to both R1 & R2 ¦ ,1 level - Fill operation,
RM22LA32MRmonitoring functions | - governed by time delay - status reflects to both R1 & R2 ¦ ,1 level - Empty operation,
RM22LA32MRmonitoring functions | - governed by time delay - status reflects to both R1 & R2 ¦ ,2 level - Fill operation,
RM22LA32MRmonitoring functions | - governed by time delay - status reflects to both R1 & R2 ¦ ,2 level - Empty operation,
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR | Measurement mode,
RM22LA32MRinternal input resistance | - ¦ ,Internal input resistance,
RM22LA32MRinput terminal | Min-Max-C ¦ ,Input terminal,
RM22LA32MRMaximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage,
RM22LA32MRMaximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
RM22LA32MRMaximum length of probes cable | 100 ¦ ,Maximum length of probes cable,
RM22LA32MRinput frequency | 1 for LS 2.2 for St 4.7 for HS ¦ ,Maximum cable capacitance,
RM22LA32MRsetting accuracy of the switching threshold | +/- 10% of full scale value for LS '+/- 10% of full scale value for St '+/- 35% of full scale value for HS ¦ ,Setting accuracy,
RM22LA32MRrepeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22LA32MRmeasurement method | Liquid level resistive probe ¦ ,Measurement method,
RM22LA32MRswitching threshold drift | < 1% over whole range ¦ ,Measurement error with supply voltage variation,
RM22LA32MRswitching threshold drift | 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22LA32MRmaximum measuring cycle | Maximum measuring cycles,
RM22LA32MRmeasurement range | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS ¦ ,1 level - Fill operation,
RM22LA32MRmeasurement range | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS ¦ ,1 level - Empty operation,
RM22LA32MRmeasurement range | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS ¦ ,2 level - Fill operation,
RM22LA32MRmeasurement range | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS ¦ ,2 level - Empty operation,
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MRtripping threshold | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS ¦ ,1 level - Fill operation,
RM22LA32MRtripping threshold | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS ¦ ,1 level - Empty operation,
RM22LA32MRtripping threshold | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS ¦ ,2 level - Fill operation,
RM22LA32MRtripping threshold | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS ¦ ,2 level - Empty operation,
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MRhysteresis | - ¦ ,1 level - Fill operation,
RM22LA32MRhysteresis | - ¦ ,1 level - Empty operation,
RM22LA32MRhysteresis | - ¦ ,2 level - Fill operation,
RM22LA32MRhysteresis | - ¦ ,2 level - Empty operation,
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MR
RM22LA32MRoutput type | 2 x C/O relay contacts
RM22LA32MRoutput terminal | 11-12-14, 21-22-24
RM22LA32MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22LA32MRoutput logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22LA32MRcontacts material | Cadmium free
RM22LA32MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22LA32MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22LA32MRelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22LA32MRelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22LA32MRelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22LA32MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22LA32MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22LA32MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22LA32MRmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM22LA32MRmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM22LA32MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22LA32MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22LA32MRminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22LA32MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22LA32MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22LA32MRthermal current | 8A ¦ IEC60947-5-1
RM22LA32MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22LA32MRshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22LA32MR
RM22LA32MRtime delay type | Yes ¦ ,"OFF" delay,
RM22LA32MRtime delay type | Yes ¦ ,"ON" delay,
RM22LA32MRtime delay type | - ¦ ,Inhibition,
RM22LA32MRtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay,
RM22LA32MRtime delay range | Adjustable 0.1…30 ¦ ,"ON" delay,
RM22LA32MRtime delay range | - ¦ ,Inhibition,
RM22LA32MRresponse time | 0
RM22LA32MRresponse time
RM22LA32MRresponse time
RM22LA32MRresponse time
RM22LA32MRresponse time
RM22LA32MRpower on delay | 0
RM22LA32MRreset time | 0
RM22LA32MRreset time | through front panel reset,
RM22LA32MRreset time | through input control reset,
RM22LA32MRsetting accuracy of time delay | +/- 10% of full scales
RM22LA32MRrepeat accuracy of time delay | +/- 2%
RM22LA32MRtime delay drift | < 1
RM22LA32MRtime delay drift | < 0.05
RM22LA32MR
RM22LA32MRstatus LED | Dial pointer (Green) R (Amber)
RM22LA32MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22LA32MRlocal signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22LA32MRlocal signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22LA32MRlocal signalling | R - ON ¦ ,Output is energized,
RM22LA32MRlocal signalling | R - OFF ¦ ,Output is de-energized,
RM22LA32MRlocal signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22LA32MRlocal signalling
RM22LA32MRlocal signalling
RM22LA32MRlocal signalling
RM22LA32MRlocal signalling
RM22LA32MRlocal signalling
RM22LA32MRlocal signalling
RM22LA32MRlocal signalling
RM22LA32MRlocal signalling
RM22LA32MRlocal signalling
RM22LA32MR
RM22LA32MR | -
RM22LA32MR | 1) Will always illuminated when power is supplied to the product
RM22LA32MRdiagnostic button | Output will be de-energized when activated
RM22LA32MR | -
RM22LA32MR | 1) Output is energized/ de-energized according to function diagram 2) When input monitored @ fault condition, output is always de-energized
RM22LA32MR
RM22LA32MRsafety reliability data | 1,600,000 hours ¦ ,MTTF,
RM22LA32MRsafety reliability data | 170,000 hours ¦ ,B10,
RM22LA32MR | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22LA32MR | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22LA32MR
RM22LA32MT
RM22LA32MTstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22LA32MTproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22LA32MTmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22LA32MTdirectives | 2014/35/EU
RM22LA32MTdirectives | 2014/30/EU
RM22LA32MTdirectives | 2011/65/EU
RM22LA32MT
RM22LA32MT | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category,
RM22LA32MT | Class C ¦ Germanisher Lloyd,Environmental category,
RM22LA32MTambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22LA32MTambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22LA32MTrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22LA32MT | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22LA32MTvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22LA32MTshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22LA32MTbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22LA32MTseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22LA32MTIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22LA32MTIP degree of protection | IP40 ¦ IEC60529,Housing,
RM22LA32MTIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22LA32MT
RM22LA32MTwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22LA32MTheight | Height,
RM22LA32MTdepth | Depth,
RM22LA32MTnet weight | 110
RM22LA32MTmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22LA32MTmounting support | - ¦ IEC/EN 60715,With socket,
RM22LA32MTmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22LA32MTMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22LA32MTMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22LA32MTconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22LA32MTconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22LA32MTconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22LA32MTconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22LA32MTtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22LA32MTcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22LA32MTduty time | 1
RM22LA32MT
RM22LA32MTelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22LA32MTelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22LA32MTelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22LA32MTelectromagnetic compatibility | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22LA32MTelectromagnetic compatibility | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22LA32MTelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22LA32MTelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22LA32MTelectromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22LA32MTelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22LA32MTelectromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
RM22LA32MTelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22LA32MTelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22LA32MTelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22LA32MTelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22LA32MTelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22LA32MTelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22LA32MTelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22LA32MTelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22LA32MTelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22LA32MT
RM22LA32MTpollution degree | 3 ¦ IEC60664-1
RM22LA32MTovervoltage category | 3 ¦ IEC60664-1
RM22LA32MTcircuit group | A1, A2 ¦ ,Supply,Terminal
RM22LA32MTcircuit group | Min, Max, C ¦ ,Input 1,
RM22LA32MTcircuit group | - ¦ ,Input 2,
RM22LA32MTcircuit group | - ¦ ,Input 3,
RM22LA32MTcircuit group | 11,12,14 ¦ ,Output 1,
RM22LA32MTcircuit group | 21,22,24 ¦ ,Output 2,
RM22LA32MT | 380…415 AC ¦ ,Supply,Rated
RM22LA32MT | Level probe ¦ ,Input 1,Voltage
RM22LA32MT | - ¦ ,Input 2,Spec
RM22LA32MT | - ¦ ,Input 3,
RM22LA32MT | 250V ¦ ,Output 1,
RM22LA32MT | 250V ¦ ,Output 2,
RM22LA32MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply,
RM22LA32MT[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 1,
RM22LA32MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM22LA32MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM22LA32MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22LA32MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22LA32MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22LA32MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22LA32MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22LA32MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply / Output 1,
RM22LA32MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply / Output 2,
RM22LA32MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22LA32MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 1,
RM22LA32MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 2,
RM22LA32MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22LA32MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22LA32MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22LA32MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22LA32MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22LA32MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22LA32MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22LA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22LA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM22LA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM22LA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM22LA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22LA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22LA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22LA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22LA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22LA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22LA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22LA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22LA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM22LA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2,
RM22LA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22LA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22LA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22LA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22LA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22LA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22LA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22LA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM22LA32MTdielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM22LA32MTdielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM22LA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22LA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22LA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22LA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM22LA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2,
RM22LA32MTdielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM22LA32MTdielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM22LA32MTdielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM22LA32MTdielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM22LA32MTdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22LA32MTdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22LA32MTdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22LA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM22LA32MTinsulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM22LA32MTinsulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM22LA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22LA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22LA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22LA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM22LA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2,
RM22LA32MTinsulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM22LA32MTinsulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM22LA32MTinsulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM22LA32MTinsulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM22LA32MTinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22LA32MTinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22LA32MTinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22LA32MT
RM22LA32MT[Us] rated supply voltage | ~380…415
RM22LA32MTsupply voltage limits | ~323…456.5
RM22LA32MTpolarity
RM22LA32MTsupply frequency | 50 / 60
RM22LA32MTsupply frequency | 45…66
RM22LA32MTpower consumption | ~ 10VA ~ 8VA
RM22LA32MTimmunity to microbreaks | ~ 90, -- 100
RM22LA32MTsupply terminal | A1-A2
RM22LA32MTon-load factor | 1
RM22LA32MTrelease of input voltage | -
RM22LA32MT
RM22LA32MTmonitoring functions | - governed by time delay - status reflects to both R1 & R2 ¦ ,1 level - Fill operation,
RM22LA32MTmonitoring functions | - governed by time delay - status reflects to both R1 & R2 ¦ ,1 level - Empty operation,
RM22LA32MTmonitoring functions | - governed by time delay - status reflects to both R1 & R2 ¦ ,2 level - Fill operation,
RM22LA32MTmonitoring functions | - governed by time delay - status reflects to both R1 & R2 ¦ ,2 level - Empty operation,
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT | Measurement mode,
RM22LA32MTinternal input resistance | - ¦ ,Internal input resistance,
RM22LA32MTinput terminal | Min-Max-C ¦ ,Input terminal,
RM22LA32MTMaximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage,
RM22LA32MTMaximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
RM22LA32MTMaximum length of probes cable | 100 ¦ ,Maximum length of probes cable,
RM22LA32MTinput frequency | 1 for LS 2.2 for St 4.7 for HS ¦ ,Maximum cable capacitance,
RM22LA32MTsetting accuracy of the switching threshold | +/- 10% of full scale value for LS '+/- 10% of full scale value for St '+/- 35% of full scale value for HS ¦ ,Setting accuracy,
RM22LA32MTrepeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22LA32MTmeasurement method | Liquid level resistive probe ¦ ,Measurement method,
RM22LA32MTswitching threshold drift | < 1% over whole range ¦ ,Measurement error with supply voltage variation,
RM22LA32MTswitching threshold drift | 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22LA32MTmaximum measuring cycle | Maximum measuring cycles,
RM22LA32MTmeasurement range | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS ¦ ,1 level - Fill operation,
RM22LA32MTmeasurement range | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS ¦ ,1 level - Empty operation,
RM22LA32MTmeasurement range | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS ¦ ,2 level - Fill operation,
RM22LA32MTmeasurement range | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS ¦ ,2 level - Empty operation,
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MTtripping threshold | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS ¦ ,1 level - Fill operation,
RM22LA32MTtripping threshold | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS ¦ ,1 level - Empty operation,
RM22LA32MTtripping threshold | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS ¦ ,2 level - Fill operation,
RM22LA32MTtripping threshold | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS ¦ ,2 level - Empty operation,
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MThysteresis | - ¦ ,1 level - Fill operation,
RM22LA32MThysteresis | - ¦ ,1 level - Empty operation,
RM22LA32MThysteresis | - ¦ ,2 level - Fill operation,
RM22LA32MThysteresis | - ¦ ,2 level - Empty operation,
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MT
RM22LA32MToutput type | 2 x C/O relay contacts
RM22LA32MToutput terminal | 11-12-14, 21-22-24
RM22LA32MToutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22LA32MToutput logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22LA32MTcontacts material | Cadmium free
RM22LA32MTmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22LA32MTelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22LA32MTelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22LA32MTelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22LA32MTelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22LA32MT[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22LA32MT[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22LA32MTmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22LA32MTmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM22LA32MTmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM22LA32MTminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22LA32MTminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22LA32MTminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22LA32MTmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22LA32MTmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22LA32MTthermal current | 8A ¦ IEC60947-5-1
RM22LA32MTshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22LA32MTshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22LA32MT
RM22LA32MTtime delay type | Yes ¦ ,"OFF" delay,
RM22LA32MTtime delay type | Yes ¦ ,"ON" delay,
RM22LA32MTtime delay type | - ¦ ,Inhibition,
RM22LA32MTtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay,
RM22LA32MTtime delay range | Adjustable 0.1…30 ¦ ,"ON" delay,
RM22LA32MTtime delay range | - ¦ ,Inhibition,
RM22LA32MTresponse time | 0
RM22LA32MTresponse time
RM22LA32MTresponse time
RM22LA32MTresponse time
RM22LA32MTresponse time
RM22LA32MTpower on delay | 0
RM22LA32MTreset time | 0
RM22LA32MTreset time | through front panel reset,
RM22LA32MTreset time | through input control reset,
RM22LA32MTsetting accuracy of time delay | +/- 10% of full scales
RM22LA32MTrepeat accuracy of time delay | +/- 2%
RM22LA32MTtime delay drift | < 1
RM22LA32MTtime delay drift | < 0.05
RM22LA32MT
RM22LA32MTstatus LED | Dial pointer (Green) R (Amber)
RM22LA32MTlocal signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22LA32MTlocal signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22LA32MTlocal signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22LA32MTlocal signalling | R - ON ¦ ,Output is energized,
RM22LA32MTlocal signalling | R - OFF ¦ ,Output is de-energized,
RM22LA32MTlocal signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22LA32MTlocal signalling
RM22LA32MTlocal signalling
RM22LA32MTlocal signalling
RM22LA32MTlocal signalling
RM22LA32MTlocal signalling
RM22LA32MTlocal signalling
RM22LA32MTlocal signalling
RM22LA32MTlocal signalling
RM22LA32MTlocal signalling
RM22LA32MT
RM22LA32MT | -
RM22LA32MT | 1) Will always illuminated when power is supplied to the product
RM22LA32MTdiagnostic button | Output will be de-energized when activated
RM22LA32MT | -
RM22LA32MT | 1) Output is energized/ de-energized according to function diagram 2) When input monitored @ fault condition, output is always de-energized
RM22LA32MT
RM22LA32MTsafety reliability data | 1,600,000 hours ¦ ,MTTF,
RM22LA32MTsafety reliability data | 170,000 hours ¦ ,B10,
RM22LA32MT | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22LA32MT | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22LA32MT
RM35LM33MW
RM35LM33MWstandards | NF EN 60255-6 and IEC 60255-6
RM35LM33MWproduct certifications | UL, CSA, GL, C-Tick, GOST
RM35LM33MWmarking | 1: 73/23/EEC and EMC 89/336/EEC
RM35LM33MWdirectives
RM35LM33MWdirectives
RM35LM33MWdirectives
RM35LM33MW
RM35LM33MW | IEC60721-3-3,Climatic category,
RM35LM33MW | Germanisher Lloyd,Environmental category,
RM35LM33MWambient air temperature for storage | - 40…+ 70 ¦ ,Storage,
RM35LM33MWambient air temperature for operation | - 20…+ 50 ¦ ,Operation,
RM35LM33MWrelative humidity | 2 x 24 hours…+ 95 % RH at + 55 °C (without condensation) ¦ IEC60068-2-30,Damp heat,
RM35LM33MW | IEC60947-5-1,Cyclic Damp Heat Test,
RM35LM33MWvibration resistance | 0.035 mm from 10…150 Hz ¦ IEC60068-2-6
RM35LM33MWshock resistance | 5 gn ¦ IEC60068-2-27
RM35LM33MWbump resistance | IEC60068-2-29
RM35LM33MWseismic resistance | IEC60068-3-3
RM35LM33MWIP degree of protection | IP 20 ¦ IEC60529,Terminal Block,
RM35LM33MWIP degree of protection | IP 30 ¦ IEC60529,Housing,
RM35LM33MWIP degree of protection | IEC60529,Front Panel,
RM35LM33MW
RM35LM33MWwidth | Width,
RM35LM33MWheight | Height,
RM35LM33MWdepth | Depth,
RM35LM33MWnet weight
RM35LM33MWmounting support | On 4 rail ¦ IEC/EN 60715,Without socket,
RM35LM33MWmounting support | IEC/EN 60715,With socket,
RM35LM33MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35LM33MWMinimum distance to adjacent devices | Horizontal,
RM35LM33MWMinimum distance to adjacent devices | Vertical,
RM35LM33MWconnections - terminals | 1 conductor: 0.5…4 (AWG 20…AWG 11) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35LM33MWconnections - terminals | 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35LM33MWconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 12) ¦ IEC60947-1,Solid cable (spring terminal),
RM35LM33MWconnections - terminals | 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable (spring terminal),
RM35LM33MWtightening torque | 0.6…1N.m / 5.3…8.8 Lbf.In ¦ IEC60947-1,Tightening torque,
RM35LM33MWcable stripping length | Cable stripping length,
RM35LM33MWduty time
RM35LM33MW
RM35LM33MWelectromagnetic compatibility | Immunity NF EN 61000-6-2 2002 / IEC 61000-6-2 ¦ ,Generic immunity standard,
RM35LM33MWelectromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
RM35LM33MWelectromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
RM35LM33MWelectromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
RM35LM33MWelectromagnetic compatibility | IEC61000-4-5,Surge,
RM35LM33MWelectromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
RM35LM33MWelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM35LM33MWelectromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35LM33MWelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM35LM33MWelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM35LM33MWelectromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
RM35LM33MWelectromagnetic compatibility | Emission NF EN 61000-6-4, NF EN 61000-6-3, IEC 61000-6-4, IEC 61000-6-3 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35LM33MWelectromagnetic compatibility | Generic emission standard,
RM35LM33MWelectromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35LM33MWelectromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35LM33MWelectromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
RM35LM33MWelectromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35LM33MWelectromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35LM33MWelectromagnetic compatibility | Germanisher Lloyd,Conducted emission,
RM35LM33MW
RM35LM33MWpollution degree | 3 ¦ IEC60664-1
RM35LM33MWovervoltage category | III ¦ IEC60664-1
RM35LM33MWcircuit group | Supply,Terminal
RM35LM33MWcircuit group | Input 1,
RM35LM33MWcircuit group | Input 2,
RM35LM33MWcircuit group | Input 3,
RM35LM33MWcircuit group | Output 1,
RM35LM33MWcircuit group | Output 2,
RM35LM33MW | Supply,Rated
RM35LM33MW | Input 1,Voltage
RM35LM33MW | Input 2,Spec
RM35LM33MW | Input 3,
RM35LM33MW | Output 1,
RM35LM33MW | Output 2,
RM35LM33MW[Ui] rated insulation voltage | 250 ¦ IEC60664-1,Supply,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Output 1,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM35LM33MW[Uimp] rated impulse withstand voltage | 4 (1.2/50 µs) ¦ IEC60664-1,Supply,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM35LM33MWdielectric strength | 2, 1 50 Hz, 1 min. ¦ IEC60255-27,Supply / Input 1,
RM35LM33MWdielectric strength | IEC60255-27,Supply / Input 2,
RM35LM33MWdielectric strength | IEC60255-27,Supply / Input 3,
RM35LM33MWdielectric strength | IEC60255-27,Supply / Output 1,
RM35LM33MWdielectric strength | IEC60255-27,Supply / Output 2,
RM35LM33MWdielectric strength | IEC60255-27,Output 1 / Output 2,
RM35LM33MWdielectric strength | IEC60255-27,Input 1 / Output 1,
RM35LM33MWdielectric strength | IEC60255-27,Input 1 / Output 2,
RM35LM33MWdielectric strength | IEC60255-27,Input 2 / Output 1,
RM35LM33MWdielectric strength | IEC60255-27,Input 2 / Output 2,
RM35LM33MWdielectric strength | IEC60255-27,Input 3 / Output 1,
RM35LM33MWdielectric strength | IEC60255-27,Input 3 / Output 2,
RM35LM33MWdielectric strength | IEC60255-27,Input 1 / Input 2,
RM35LM33MWdielectric strength | IEC60255-27,Input 2 / Input 3,
RM35LM33MWdielectric strength | IEC60255-27,Input 1 / Input 3,
RM35LM33MWinsulation resistance | > 500 MΩ, 2 500 V ¦ IEC60255-27,Supply / Input 1,
RM35LM33MWinsulation resistance | IEC60255-27,Supply / Input 2,
RM35LM33MWinsulation resistance | IEC60255-27,Supply / Input 3,
RM35LM33MWinsulation resistance | IEC60255-27,Supply / Output 1,
RM35LM33MWinsulation resistance | IEC60255-27,Supply / Output 2,
RM35LM33MWinsulation resistance | IEC60255-27,Output 1 / Output 2,
RM35LM33MWinsulation resistance | IEC60255-27,Input 1 / Output 1,
RM35LM33MWinsulation resistance | IEC60255-27,Input 1 / Output 2,
RM35LM33MWinsulation resistance | IEC60255-27,Input 2 / Output 1,
RM35LM33MWinsulation resistance | IEC60255-27,Input 2 / Output 2,
RM35LM33MWinsulation resistance | IEC60255-27,Input 3 / Output 1,
RM35LM33MWinsulation resistance | IEC60255-27,Input 3 / Output 2,
RM35LM33MWinsulation resistance | IEC60255-27,Input 1 / Input 2,
RM35LM33MWinsulation resistance | IEC60255-27,Input 2 / Input 3,
RM35LM33MWinsulation resistance | IEC60255-27,Input 1 / Input 3,
RM35LM33MW
RM35LM33MW[Us] rated supply voltage | ~/-- 24…240
RM35LM33MWsupply voltage limits | ~/-- 20.4…264
RM35LM33MWpolarity
RM35LM33MWsupply frequency | 50/60 Hz ± 10 %
RM35LM33MWsupply frequency
RM35LM33MWpower consumption | 5VA / 1.5W
RM35LM33MWimmunity to microbreaks | ~ 90, -- 100
RM35LM33MWsupply terminal
RM35LM33MWon-load factor
RM35LM33MWrelease of input voltage
RM35LM33MW
RM35LM33MWmonitoring functions | 1 level - Fill operation,
RM35LM33MWmonitoring functions | 1 level - Empty operation,
RM35LM33MWmonitoring functions | 2 level - Fill operation,
RM35LM33MWmonitoring functions | 2 level - Empty operation,
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW | Measurement mode,
RM35LM33MWinternal input resistance | Internal input resistance,
RM35LM33MWinput terminal | Input terminal,
RM35LM33MWMaximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage,
RM35LM33MWMaximum probe supplied current | < 1 ¦ ,Maximum probe supplied current,
RM35LM33MWMaximum length of probes cable | 100 ¦ ,Maximum length of probes cable,
RM35LM33MWinput frequency | 1 for LS 2.2 for St 4.7 pour HS ¦ ,Maximum cable capacitance,
RM35LM33MWsetting accuracy of the switching threshold | ± 10 % of the full scale ± 20 % for the HS range ¦ ,Setting accuracy,
RM35LM33MWrepeat accuracy of the switching threshold | Repeat accuracy (constant parameters),
RM35LM33MWmeasurement method | Measurement method,
RM35LM33MWswitching threshold drift | Measurement error with supply voltage variation,
RM35LM33MWswitching threshold drift | 0.5 % / °C ¦ ,Measurement error with temperature variation,
RM35LM33MWmaximum measuring cycle | Maximum measuring cycles,
RM35LM33MWmeasurement range | 250 Ω…5 kΩ ¦ ,1 level - Fill operation,
RM35LM33MWmeasurement range | 5 kΩ…100 kΩ ¦ ,1 level - Empty operation,
RM35LM33MWmeasurement range | 50 kΩ…1 MΩ ¦ ,2 level - Fill operation,
RM35LM33MWmeasurement range | 2 level - Empty operation,
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MWtripping threshold | 5…100 % of the range ¦ ,1 level - Fill operation,
RM35LM33MWtripping threshold | 1 level - Empty operation,
RM35LM33MWtripping threshold | 2 level - Fill operation,
RM35LM33MWtripping threshold | 2 level - Empty operation,
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MWhysteresis | 1 level - Fill operation,
RM35LM33MWhysteresis | 1 level - Empty operation,
RM35LM33MWhysteresis | 2 level - Fill operation,
RM35LM33MWhysteresis | 2 level - Empty operation,
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MWoutput type | 2 C/O contacts
RM35LM33MWoutput terminal
RM35LM33MWoutput logic | R1 (11-12-14),
RM35LM33MWoutput logic | R2 (21-22-24),
RM35LM33MWcontacts material | Cadmium free
RM35LM33MWmechanical durability | 30 x 106 operating cycles ¦ IEC61810-1
RM35LM33MWelectrical durability | 1 x 105 operating cycles ¦ IEC60947-4-1,AC-1,
RM35LM33MWelectrical durability | AC-12, AC-13, AC-14, AC-15, DC-12, DC-13 ¦ IEC60947-4-1,DC-1,
RM35LM33MWelectrical durability | IEC60947-5-1,AC-15,
RM35LM33MWelectrical durability | IEC60947-5-1,DC-13,
RM35LM33MW[Ue] rated operational voltage | 1250 ¦ IEC61810-1,Rated switching voltage,
RM35LM33MW[Ie] rated operational current | 5 ¦ IEC61810-1,Rated switching current,
RM35LM33MWmaximum switching capacity | 1/2 250 ¦ ,Maximum switching voltage,
RM35LM33MWmaximum switching capacity | 1/2 5 ¦ ,Maximum switching current,
RM35LM33MWmaximum switching capacity | Maximum switching capacity,
RM35LM33MWminimum switching capacity | IEC60947-5-4,Minimum switching voltage,
RM35LM33MWminimum switching capacity | IEC60947-5-4,Minimum switching current,
RM35LM33MWminimum switching capacity | 10/ 2 5 V ¦ IEC60947-5-4,Minimum switching capacity,
RM35LM33MWmaximum voltage drop | IEC62314,Only for solid state output,
RM35LM33MWmaximum leakage current | IEC62314,Only for solid state output,
RM35LM33MWthermal current | IEC60947-5-1
RM35LM33MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM35LM33MWshort circuit protection | IEC62314,Solid State Output by external fuse,
RM35LM33MW
RM35LM33MWtime delay type | "OFF" delay,
RM35LM33MWtime delay type | "ON" delay,
RM35LM33MWtime delay type | Inhibition,
RM35LM33MWtime delay range | 0.1…5, 0 + 10 % ¦ ,"OFF" delay,
RM35LM33MWtime delay range | "ON" delay,
RM35LM33MWtime delay range | Inhibition,
RM35LM33MWresponse time | on crossing the threshold,
RM35LM33MWresponse time
RM35LM33MWresponse time
RM35LM33MWresponse time
RM35LM33MWresponse time
RM35LM33MWpower on delay | 600
RM35LM33MWreset time | 1.75 ¦ ,through Un power reset,
RM35LM33MWreset time | through front panel reset,
RM35LM33MWreset time | through input control reset,
RM35LM33MWsetting accuracy of time delay
RM35LM33MWrepeat accuracy of time delay | ± 2 %
RM35LM33MWtime delay drift
RM35LM33MWtime delay drift
RM35LM33MW
RM35LM33MWstatus LED
RM35LM33MWlocal signalling | Green LED ¦ ,Power supply availability,
RM35LM33MWlocal signalling | Power supply not availability,
RM35LM33MWlocal signalling | Timing in-progress,
RM35LM33MWlocal signalling | Yellow LED ¦ ,Output is energized,
RM35LM33MWlocal signalling | Yellow LED ¦ ,Output is de-energized,
RM35LM33MWlocal signalling | Range Setting Changes,
RM35LM33MWlocal signalling
RM35LM33MWlocal signalling
RM35LM33MWlocal signalling
RM35LM33MWlocal signalling
RM35LM33MWlocal signalling
RM35LM33MWlocal signalling
RM35LM33MWlocal signalling
RM35LM33MWlocal signalling
RM35LM33MWlocal signalling
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MWdiagnostic button
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MWsafety reliability data | MTTF,
RM35LM33MWsafety reliability data | B10,
RM35LM33MW | MTTFd,
RM35LM33MW | B10d,
RM35LM33MW
RM35LV14MW
RM35LV14MWstandards | NF EN 60255-6 and IEC 60255-6
RM35LV14MWproduct certifications | UL, CSA, GL, C-Tick, GOST
RM35LV14MWmarking | 1: 73/23/EEC and EMC 89/336/EEC
RM35LV14MWdirectives
RM35LV14MWdirectives
RM35LV14MWdirectives
RM35LV14MW
RM35LV14MW | IEC60721-3-3,Climatic category,
RM35LV14MW | Germanisher Lloyd,Environmental category,
RM35LV14MWambient air temperature for storage | - 40…+ 70 ¦ ,Storage,
RM35LV14MWambient air temperature for operation | - 20…+ 50 ¦ ,Operation,
RM35LV14MWrelative humidity | 2 x 24 hours…+ 95 % RH at + 55 °C (without condensation) ¦ IEC60068-2-30,Damp heat,
RM35LV14MW | IEC60947-5-1,Cyclic Damp Heat Test,
RM35LV14MWvibration resistance | 0.035 mm from 10…150 Hz ¦ IEC60068-2-6
RM35LV14MWshock resistance | 5 gn ¦ IEC60068-2-27
RM35LV14MWbump resistance | IEC60068-2-29
RM35LV14MWseismic resistance | IEC60068-3-3
RM35LV14MWIP degree of protection | IP 20 ¦ IEC60529,Terminal Block,
RM35LV14MWIP degree of protection | IP 30 ¦ IEC60529,Housing,
RM35LV14MWIP degree of protection | IEC60529,Front Panel,
RM35LV14MW
RM35LV14MWwidth | Width,
RM35LV14MWheight | Height,
RM35LV14MWdepth | Depth,
RM35LV14MWnet weight
RM35LV14MWmounting support | On 4 rail ¦ IEC/EN 60715,Without socket,
RM35LV14MWmounting support | IEC/EN 60715,With socket,
RM35LV14MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35LV14MWMinimum distance to adjacent devices | Horizontal,
RM35LV14MWMinimum distance to adjacent devices | Vertical,
RM35LV14MWconnections - terminals | 1 conductor: 0.5…4 (AWG 20…AWG 11) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35LV14MWconnections - terminals | 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35LV14MWconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 12) ¦ IEC60947-1,Solid cable (spring terminal),
RM35LV14MWconnections - terminals | 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable (spring terminal),
RM35LV14MWtightening torque | 0.6…1N.m / 5.3…8.8 Lbf.In ¦ IEC60947-1,Tightening torque,
RM35LV14MWcable stripping length | Cable stripping length,
RM35LV14MWduty time
RM35LV14MW
RM35LV14MWelectromagnetic compatibility | Immunity NF EN 61000-6-2 2002 / IEC 61000-6-2 ¦ ,Generic immunity standard,
RM35LV14MWelectromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
RM35LV14MWelectromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
RM35LV14MWelectromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
RM35LV14MWelectromagnetic compatibility | IEC61000-4-5,Surge,
RM35LV14MWelectromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
RM35LV14MWelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM35LV14MWelectromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35LV14MWelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM35LV14MWelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM35LV14MWelectromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
RM35LV14MWelectromagnetic compatibility | Emission NF EN 61000-6-4, NF EN 61000-6-3, IEC 61000-6-4, IEC 61000-6-3 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35LV14MWelectromagnetic compatibility | Generic emission standard,
RM35LV14MWelectromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35LV14MWelectromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35LV14MWelectromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
RM35LV14MWelectromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35LV14MWelectromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35LV14MWelectromagnetic compatibility | Germanisher Lloyd,Conducted emission,
RM35LV14MW
RM35LV14MWpollution degree | 3 ¦ IEC60664-1
RM35LV14MWovervoltage category | III ¦ IEC60664-1
RM35LV14MWcircuit group | Supply,Terminal
RM35LV14MWcircuit group | Input 1,
RM35LV14MWcircuit group | Input 2,
RM35LV14MWcircuit group | Input 3,
RM35LV14MWcircuit group | Output 1,
RM35LV14MWcircuit group | Output 2,
RM35LV14MW | Supply,Rated
RM35LV14MW | Input 1,Voltage
RM35LV14MW | Input 2,Spec
RM35LV14MW | Input 3,
RM35LV14MW | Output 1,
RM35LV14MW | Output 2,
RM35LV14MW[Ui] rated insulation voltage | 250 ¦ IEC60664-1,Supply,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Output 1,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM35LV14MW[Uimp] rated impulse withstand voltage | 4 (1.2/50 µs) ¦ IEC60664-1,Supply,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM35LV14MWdielectric strength | 2, 1 50 Hz, 1 min. ¦ IEC60255-27,Supply / Input 1,
RM35LV14MWdielectric strength | IEC60255-27,Supply / Input 2,
RM35LV14MWdielectric strength | IEC60255-27,Supply / Input 3,
RM35LV14MWdielectric strength | IEC60255-27,Supply / Output 1,
RM35LV14MWdielectric strength | IEC60255-27,Supply / Output 2,
RM35LV14MWdielectric strength | IEC60255-27,Output 1 / Output 2,
RM35LV14MWdielectric strength | IEC60255-27,Input 1 / Output 1,
RM35LV14MWdielectric strength | IEC60255-27,Input 1 / Output 2,
RM35LV14MWdielectric strength | IEC60255-27,Input 2 / Output 1,
RM35LV14MWdielectric strength | IEC60255-27,Input 2 / Output 2,
RM35LV14MWdielectric strength | IEC60255-27,Input 3 / Output 1,
RM35LV14MWdielectric strength | IEC60255-27,Input 3 / Output 2,
RM35LV14MWdielectric strength | IEC60255-27,Input 1 / Input 2,
RM35LV14MWdielectric strength | IEC60255-27,Input 2 / Input 3,
RM35LV14MWdielectric strength | IEC60255-27,Input 1 / Input 3,
RM35LV14MWinsulation resistance | > 500 MΩ, 2 500 V ¦ IEC60255-27,Supply / Input 1,
RM35LV14MWinsulation resistance | IEC60255-27,Supply / Input 2,
RM35LV14MWinsulation resistance | IEC60255-27,Supply / Input 3,
RM35LV14MWinsulation resistance | IEC60255-27,Supply / Output 1,
RM35LV14MWinsulation resistance | IEC60255-27,Supply / Output 2,
RM35LV14MWinsulation resistance | IEC60255-27,Output 1 / Output 2,
RM35LV14MWinsulation resistance | IEC60255-27,Input 1 / Output 1,
RM35LV14MWinsulation resistance | IEC60255-27,Input 1 / Output 2,
RM35LV14MWinsulation resistance | IEC60255-27,Input 2 / Output 1,
RM35LV14MWinsulation resistance | IEC60255-27,Input 2 / Output 2,
RM35LV14MWinsulation resistance | IEC60255-27,Input 3 / Output 1,
RM35LV14MWinsulation resistance | IEC60255-27,Input 3 / Output 2,
RM35LV14MWinsulation resistance | IEC60255-27,Input 1 / Input 2,
RM35LV14MWinsulation resistance | IEC60255-27,Input 2 / Input 3,
RM35LV14MWinsulation resistance | IEC60255-27,Input 1 / Input 3,
RM35LV14MW
RM35LV14MW[Us] rated supply voltage | 1/2 24…240
RM35LV14MWsupply voltage limits | 1/2 20.4…264
RM35LV14MWpolarity
RM35LV14MWsupply frequency | 50/60 Hz ± 10 %
RM35LV14MWsupply frequency
RM35LV14MWpower consumption | 5VA / 1.5W
RM35LV14MWimmunity to microbreaks | ~ 90, -- 100
RM35LV14MWsupply terminal
RM35LV14MWon-load factor
RM35LV14MWrelease of input voltage
RM35LV14MW
RM35LV14MWmonitoring functions | 1 level - Fill operation,
RM35LV14MWmonitoring functions | 1 level - Empty operation,
RM35LV14MWmonitoring functions | 2 level - Fill operation,
RM35LV14MWmonitoring functions | 2 level - Empty operation,
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW | Measurement mode,
RM35LV14MWinternal input resistance | Internal input resistance,
RM35LV14MWinput terminal | Input terminal,
RM35LV14MWMaximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage,
RM35LV14MWMaximum probe supplied current | 40 ¦ ,Maximum probe supplied current,
RM35LV14MWMaximum length of probes cable | 100 ¦ ,Maximum length of probes cable,
RM35LV14MWinput frequency | 10 ¦ ,Maximum cable capacitance,
RM35LV14MWsetting accuracy of the switching threshold | ± 10 % of the full scale ± 20 % for the HS range ¦ ,Setting accuracy,
RM35LV14MWrepeat accuracy of the switching threshold | Repeat accuracy (constant parameters),
RM35LV14MWmeasurement method | Measurement method,
RM35LV14MWswitching threshold drift | Measurement error with supply voltage variation,
RM35LV14MWswitching threshold drift | 0.5 % / °C ¦ ,Measurement error with temperature variation,
RM35LV14MWmaximum measuring cycle | Maximum measuring cycles,
RM35LV14MWmeasurement range | – ¦ ,1 level - Fill operation,
RM35LV14MWmeasurement range | – ¦ ,1 level - Empty operation,
RM35LV14MWmeasurement range | – ¦ ,2 level - Fill operation,
RM35LV14MWmeasurement range | 2 level - Empty operation,
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MWtripping threshold | – ¦ ,1 level - Fill operation,
RM35LV14MWtripping threshold | 1 level - Empty operation,
RM35LV14MWtripping threshold | 2 level - Fill operation,
RM35LV14MWtripping threshold | 2 level - Empty operation,
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MWhysteresis | 1 level - Fill operation,
RM35LV14MWhysteresis | 1 level - Empty operation,
RM35LV14MWhysteresis | 2 level - Fill operation,
RM35LV14MWhysteresis | 2 level - Empty operation,
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MWoutput type | 1 C/O contact
RM35LV14MWoutput terminal
RM35LV14MWoutput logic | R1 (11-12-14),
RM35LV14MWoutput logic | R2 (21-22-24),
RM35LV14MWcontacts material | Cadmium free
RM35LV14MWmechanical durability | 30 x 106 operating cycles ¦ IEC61810-1
RM35LV14MWelectrical durability | 1 x 105 operating cycles ¦ IEC60947-4-1,AC-1,
RM35LV14MWelectrical durability | AC-12, AC-13, AC-14, AC-15, DC-12, DC-13 ¦ IEC60947-4-1,DC-1,
RM35LV14MWelectrical durability | IEC60947-5-1,AC-15,
RM35LV14MWelectrical durability | IEC60947-5-1,DC-13,
RM35LV14MW[Ue] rated operational voltage | 1250 ¦ IEC61810-1,Rated switching voltage,
RM35LV14MW[Ie] rated operational current | 5 ¦ IEC61810-1,Rated switching current,
RM35LV14MWmaximum switching capacity | 1/2 250 ¦ ,Maximum switching voltage,
RM35LV14MWmaximum switching capacity | 1/2 5 ¦ ,Maximum switching current,
RM35LV14MWmaximum switching capacity | Maximum switching capacity,
RM35LV14MWminimum switching capacity | IEC60947-5-4,Minimum switching voltage,
RM35LV14MWminimum switching capacity | IEC60947-5-4,Minimum switching current,
RM35LV14MWminimum switching capacity | 10/ 2 5 V ¦ IEC60947-5-4,Minimum switching capacity,
RM35LV14MWmaximum voltage drop | IEC62314,Only for solid state output,
RM35LV14MWmaximum leakage current | IEC62314,Only for solid state output,
RM35LV14MWthermal current | IEC60947-5-1
RM35LV14MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM35LV14MWshort circuit protection | IEC62314,Solid State Output by external fuse,
RM35LV14MW
RM35LV14MWtime delay type | "OFF" delay,
RM35LV14MWtime delay type | "ON" delay,
RM35LV14MWtime delay type | Inhibition,
RM35LV14MWtime delay range | 0.1…5, 0 + 10 % ¦ ,"OFF" delay,
RM35LV14MWtime delay range | "ON" delay,
RM35LV14MWtime delay range | Inhibition,
RM35LV14MWresponse time | on crossing the threshold,
RM35LV14MWresponse time
RM35LV14MWresponse time
RM35LV14MWresponse time
RM35LV14MWresponse time
RM35LV14MWpower on delay | 500
RM35LV14MWreset time | 4 if 1 line broken / 1 if 2 lines broken ¦ ,through Un power reset,
RM35LV14MWreset time | through front panel reset,
RM35LV14MWreset time | through input control reset,
RM35LV14MWsetting accuracy of time delay
RM35LV14MWrepeat accuracy of time delay | ± 2 %
RM35LV14MWtime delay drift
RM35LV14MWtime delay drift
RM35LV14MW
RM35LV14MWstatus LED
RM35LV14MWlocal signalling | Green LED ¦ ,Power supply availability,
RM35LV14MWlocal signalling | Power supply not availability,
RM35LV14MWlocal signalling | Timing in-progress,
RM35LV14MWlocal signalling | Yellow LED ¦ ,Output is energized,
RM35LV14MWlocal signalling | Yellow LED ¦ ,Output is de-energized,
RM35LV14MWlocal signalling | Range Setting Changes,
RM35LV14MWlocal signalling
RM35LV14MWlocal signalling
RM35LV14MWlocal signalling
RM35LV14MWlocal signalling
RM35LV14MWlocal signalling
RM35LV14MWlocal signalling
RM35LV14MWlocal signalling
RM35LV14MWlocal signalling
RM35LV14MWlocal signalling
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MWdiagnostic button
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MWsafety reliability data | MTTF,
RM35LV14MWsafety reliability data | B10,
RM35LV14MW | MTTFd,
RM35LV14MW | B10d,
RM35LV14MW
col15
col15standards
col15product certifications
col15marking
col15directives
col15directives
col15directives
col15
col15 | IEC60721-3-3,Climatic category,
col15 | Germanisher Lloyd,Environmental category,
col15ambient air temperature for storage | Storage,
col15ambient air temperature for operation | Operation,
col15relative humidity | IEC60068-2-30,Damp heat,
col15 | IEC60947-5-1,Cyclic Damp Heat Test,
col15vibration resistance | IEC60068-2-6
col15shock resistance | IEC60068-2-27
col15bump resistance | IEC60068-2-29
col15seismic resistance | IEC60068-3-3
col15IP degree of protection | IEC60529,Terminal Block,
col15IP degree of protection | IEC60529,Housing,
col15IP degree of protection | IEC60529,Front Panel,
col15
col15width | Width,
col15height | Height,
col15depth | Depth,
col15net weight
col15mounting support | IEC/EN 60715,Without socket,
col15mounting support | IEC/EN 60715,With socket,
col15mounting position | In relation to normal vertical mounting plane,
col15Minimum distance to adjacent devices | Horizontal,
col15Minimum distance to adjacent devices | Vertical,
col15connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
col15connections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
col15connections - terminals | IEC60947-1,Solid cable (spring terminal),
col15connections - terminals | IEC60947-1,Flexible cable (spring terminal),
col15tightening torque | IEC60947-1,Tightening torque,
col15cable stripping length | Cable stripping length,
col15duty time
col15
col15electromagnetic compatibility | Generic immunity standard,
col15electromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
col15electromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
col15electromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
col15electromagnetic compatibility | IEC61000-4-5,Surge,
col15electromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
col15electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
col15electromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
col15electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
col15electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
col15electromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
col15electromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
col15electromagnetic compatibility | Generic emission standard,
col15electromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
col15electromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
col15electromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
col15electromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
col15electromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
col15electromagnetic compatibility | Germanisher Lloyd,Conducted emission,
col15
col15pollution degree | IEC60664-1
col15overvoltage category | IEC60664-1
col15circuit group | Supply,Terminal
col15circuit group | Input 1,
col15circuit group | Input 2,
col15circuit group | Input 3,
col15circuit group | Output 1,
col15circuit group | Output 2,
col15 | Supply,Rated
col15 | Input 1,Voltage
col15 | Input 2,Spec
col15 | Input 3,
col15 | Output 1,
col15 | Output 2,
col15[Ui] rated insulation voltage | IEC60664-1,Supply,
col15[Ui] rated insulation voltage | IEC60664-1,Input 1,
col15[Ui] rated insulation voltage | IEC60664-1,Input 2,
col15[Ui] rated insulation voltage | IEC60664-1,Input 3,
col15[Ui] rated insulation voltage | IEC60664-1,Output 1,
col15[Ui] rated insulation voltage | IEC60664-1,Output 2,
col15[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
col15[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
col15[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
col15[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
col15[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
col15[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
col15[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
col15[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
col15[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
col15[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
col15[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
col15[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
col15[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
col15[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
col15[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
col15dielectric strength | IEC60255-27,Supply / Input 1,
col15dielectric strength | IEC60255-27,Supply / Input 2,
col15dielectric strength | IEC60255-27,Supply / Input 3,
col15dielectric strength | IEC60255-27,Supply / Output 1,
col15dielectric strength | IEC60255-27,Supply / Output 2,
col15dielectric strength | IEC60255-27,Output 1 / Output 2,
col15dielectric strength | IEC60255-27,Input 1 / Output 1,
col15dielectric strength | IEC60255-27,Input 1 / Output 2,
col15dielectric strength | IEC60255-27,Input 2 / Output 1,
col15dielectric strength | IEC60255-27,Input 2 / Output 2,
col15dielectric strength | IEC60255-27,Input 3 / Output 1,
col15dielectric strength | IEC60255-27,Input 3 / Output 2,
col15dielectric strength | IEC60255-27,Input 1 / Input 2,
col15dielectric strength | IEC60255-27,Input 2 / Input 3,
col15dielectric strength | IEC60255-27,Input 1 / Input 3,
col15insulation resistance | IEC60255-27,Supply / Input 1,
col15insulation resistance | IEC60255-27,Supply / Input 2,
col15insulation resistance | IEC60255-27,Supply / Input 3,
col15insulation resistance | IEC60255-27,Supply / Output 1,
col15insulation resistance | IEC60255-27,Supply / Output 2,
col15insulation resistance | IEC60255-27,Output 1 / Output 2,
col15insulation resistance | IEC60255-27,Input 1 / Output 1,
col15insulation resistance | IEC60255-27,Input 1 / Output 2,
col15insulation resistance | IEC60255-27,Input 2 / Output 1,
col15insulation resistance | IEC60255-27,Input 2 / Output 2,
col15insulation resistance | IEC60255-27,Input 3 / Output 1,
col15insulation resistance | IEC60255-27,Input 3 / Output 2,
col15insulation resistance | IEC60255-27,Input 1 / Input 2,
col15insulation resistance | IEC60255-27,Input 2 / Input 3,
col15insulation resistance | IEC60255-27,Input 1 / Input 3,
col15
col15[Us] rated supply voltage
col15supply voltage limits
col15polarity
col15supply frequency
col15supply frequency
col15power consumption
col15immunity to microbreaks
col15supply terminal
col15on-load factor
col15release of input voltage
col15
col15monitoring functions | 1 level - Fill operation,
col15monitoring functions | 1 level - Empty operation,
col15monitoring functions | 2 level - Fill operation,
col15monitoring functions | 2 level - Empty operation,
col15
col15
col15
col15
col15
col15
col15
col15 | Measurement mode,
col15internal input resistance | Internal input resistance,
col15input terminal | Input terminal,
col15Maximum probe supplied voltage | Maximum probe supplied voltage,
col15Maximum probe supplied current | Maximum probe supplied current,
col15Maximum length of probes cable | Maximum length of probes cable,
col15input frequency | Maximum cable capacitance,
col15setting accuracy of the switching threshold | Setting accuracy,
col15repeat accuracy of the switching threshold | Repeat accuracy (constant parameters),
col15measurement method | Measurement method,
col15switching threshold drift | Measurement error with supply voltage variation,
col15switching threshold drift | Measurement error with temperature variation,
col15maximum measuring cycle | Maximum measuring cycles,
col15measurement range | 1 level - Fill operation,
col15measurement range | 1 level - Empty operation,
col15measurement range | 2 level - Fill operation,
col15measurement range | 2 level - Empty operation,
col15
col15
col15
col15
col15
col15
col15
col15tripping threshold | 1 level - Fill operation,
col15tripping threshold | 1 level - Empty operation,
col15tripping threshold | 2 level - Fill operation,
col15tripping threshold | 2 level - Empty operation,
col15
col15
col15
col15
col15
col15
col15
col15hysteresis | 1 level - Fill operation,
col15hysteresis | 1 level - Empty operation,
col15hysteresis | 2 level - Fill operation,
col15hysteresis | 2 level - Empty operation,
col15
col15
col15
col15
col15
col15
col15
col15
col15output type
col15output terminal
col15output logic | R1 (11-12-14),
col15output logic | R2 (21-22-24),
col15contacts material
col15mechanical durability | IEC61810-1
col15electrical durability | IEC60947-4-1,AC-1,
col15electrical durability | IEC60947-4-1,DC-1,
col15electrical durability | IEC60947-5-1,AC-15,
col15electrical durability | IEC60947-5-1,DC-13,
col15[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col15[Ie] rated operational current | IEC61810-1,Rated switching current,
col15maximum switching capacity | Maximum switching voltage,
col15maximum switching capacity | Maximum switching current,
col15maximum switching capacity | Maximum switching capacity,
col15minimum switching capacity | IEC60947-5-4,Minimum switching voltage,
col15minimum switching capacity | IEC60947-5-4,Minimum switching current,
col15minimum switching capacity | IEC60947-5-4,Minimum switching capacity,
col15maximum voltage drop | IEC62314,Only for solid state output,
col15maximum leakage current | IEC62314,Only for solid state output,
col15thermal current | IEC60947-5-1
col15short circuit protection | IEC60947-5-1,Relay Output by external fuse,
col15short circuit protection | IEC62314,Solid State Output by external fuse,
col15
col15time delay type | "OFF" delay,
col15time delay type | "ON" delay,
col15time delay type | Inhibition,
col15time delay range | "OFF" delay,
col15time delay range | "ON" delay,
col15time delay range | Inhibition,
col15response time | on crossing the threshold,
col15response time
col15response time
col15response time
col15response time
col15power on delay
col15reset time | through Un power reset,
col15reset time | through front panel reset,
col15reset time | through input control reset,
col15setting accuracy of time delay
col15repeat accuracy of time delay
col15time delay drift
col15time delay drift
col15
col15status LED
col15local signalling | Power supply availability,
col15local signalling | Power supply not availability,
col15local signalling | Timing in-progress,
col15local signalling | Output is energized,
col15local signalling | Output is de-energized,
col15local signalling | Range Setting Changes,
col15local signalling
col15local signalling
col15local signalling
col15local signalling
col15local signalling
col15local signalling
col15local signalling
col15local signalling
col15local signalling
col15
col15
col15
col15diagnostic button
col15
col15
col15
col15safety reliability data | MTTF,
col15safety reliability data | B10,
col15 | MTTFd,
col15 | B10d,
col15
col16
col16standards
col16product certifications
col16marking
col16directives
col16directives
col16directives
col16
col16 | IEC60721-3-3,Climatic category,
col16 | Germanisher Lloyd,Environmental category,
col16ambient air temperature for storage | Storage,
col16ambient air temperature for operation | Operation,
col16relative humidity | IEC60068-2-30,Damp heat,
col16 | IEC60947-5-1,Cyclic Damp Heat Test,
col16vibration resistance | IEC60068-2-6
col16shock resistance | IEC60068-2-27
col16bump resistance | IEC60068-2-29
col16seismic resistance | IEC60068-3-3
col16IP degree of protection | IEC60529,Terminal Block,
col16IP degree of protection | IEC60529,Housing,
col16IP degree of protection | IEC60529,Front Panel,
col16
col16width | Width,
col16height | Height,
col16depth | Depth,
col16net weight
col16mounting support | IEC/EN 60715,Without socket,
col16mounting support | IEC/EN 60715,With socket,
col16mounting position | In relation to normal vertical mounting plane,
col16Minimum distance to adjacent devices | Horizontal,
col16Minimum distance to adjacent devices | Vertical,
col16connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
col16connections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
col16connections - terminals | IEC60947-1,Solid cable (spring terminal),
col16connections - terminals | IEC60947-1,Flexible cable (spring terminal),
col16tightening torque | IEC60947-1,Tightening torque,
col16cable stripping length | Cable stripping length,
col16duty time
col16
col16electromagnetic compatibility | Generic immunity standard,
col16electromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
col16electromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
col16electromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
col16electromagnetic compatibility | IEC61000-4-5,Surge,
col16electromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
col16electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
col16electromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
col16electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
col16electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
col16electromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
col16electromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
col16electromagnetic compatibility | Generic emission standard,
col16electromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
col16electromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
col16electromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
col16electromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
col16electromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
col16electromagnetic compatibility | Germanisher Lloyd,Conducted emission,
col16
col16pollution degree | IEC60664-1
col16overvoltage category | IEC60664-1
col16circuit group | Supply,Terminal
col16circuit group | Input 1,
col16circuit group | Input 2,
col16circuit group | Input 3,
col16circuit group | Output 1,
col16circuit group | Output 2,
col16 | Supply,Rated
col16 | Input 1,Voltage
col16 | Input 2,Spec
col16 | Input 3,
col16 | Output 1,
col16 | Output 2,
col16[Ui] rated insulation voltage | IEC60664-1,Supply,
col16[Ui] rated insulation voltage | IEC60664-1,Input 1,
col16[Ui] rated insulation voltage | IEC60664-1,Input 2,
col16[Ui] rated insulation voltage | IEC60664-1,Input 3,
col16[Ui] rated insulation voltage | IEC60664-1,Output 1,
col16[Ui] rated insulation voltage | IEC60664-1,Output 2,
col16[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
col16[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
col16[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
col16[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
col16[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
col16[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
col16[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
col16[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
col16[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
col16[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
col16[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
col16[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
col16[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
col16[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
col16[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
col16dielectric strength | IEC60255-27,Supply / Input 1,
col16dielectric strength | IEC60255-27,Supply / Input 2,
col16dielectric strength | IEC60255-27,Supply / Input 3,
col16dielectric strength | IEC60255-27,Supply / Output 1,
col16dielectric strength | IEC60255-27,Supply / Output 2,
col16dielectric strength | IEC60255-27,Output 1 / Output 2,
col16dielectric strength | IEC60255-27,Input 1 / Output 1,
col16dielectric strength | IEC60255-27,Input 1 / Output 2,
col16dielectric strength | IEC60255-27,Input 2 / Output 1,
col16dielectric strength | IEC60255-27,Input 2 / Output 2,
col16dielectric strength | IEC60255-27,Input 3 / Output 1,
col16dielectric strength | IEC60255-27,Input 3 / Output 2,
col16dielectric strength | IEC60255-27,Input 1 / Input 2,
col16dielectric strength | IEC60255-27,Input 2 / Input 3,
col16dielectric strength | IEC60255-27,Input 1 / Input 3,
col16insulation resistance | IEC60255-27,Supply / Input 1,
col16insulation resistance | IEC60255-27,Supply / Input 2,
col16insulation resistance | IEC60255-27,Supply / Input 3,
col16insulation resistance | IEC60255-27,Supply / Output 1,
col16insulation resistance | IEC60255-27,Supply / Output 2,
col16insulation resistance | IEC60255-27,Output 1 / Output 2,
col16insulation resistance | IEC60255-27,Input 1 / Output 1,
col16insulation resistance | IEC60255-27,Input 1 / Output 2,
col16insulation resistance | IEC60255-27,Input 2 / Output 1,
col16insulation resistance | IEC60255-27,Input 2 / Output 2,
col16insulation resistance | IEC60255-27,Input 3 / Output 1,
col16insulation resistance | IEC60255-27,Input 3 / Output 2,
col16insulation resistance | IEC60255-27,Input 1 / Input 2,
col16insulation resistance | IEC60255-27,Input 2 / Input 3,
col16insulation resistance | IEC60255-27,Input 1 / Input 3,
col16
col16[Us] rated supply voltage
col16supply voltage limits
col16polarity
col16supply frequency
col16supply frequency
col16power consumption
col16immunity to microbreaks
col16supply terminal
col16on-load factor
col16release of input voltage
col16
col16monitoring functions | 1 level - Fill operation,
col16monitoring functions | 1 level - Empty operation,
col16monitoring functions | 2 level - Fill operation,
col16monitoring functions | 2 level - Empty operation,
col16
col16
col16
col16
col16
col16
col16
col16 | Measurement mode,
col16internal input resistance | Internal input resistance,
col16input terminal | Input terminal,
col16Maximum probe supplied voltage | Maximum probe supplied voltage,
col16Maximum probe supplied current | Maximum probe supplied current,
col16Maximum length of probes cable | Maximum length of probes cable,
col16input frequency | Maximum cable capacitance,
col16setting accuracy of the switching threshold | Setting accuracy,
col16repeat accuracy of the switching threshold | Repeat accuracy (constant parameters),
col16measurement method | Measurement method,
col16switching threshold drift | Measurement error with supply voltage variation,
col16switching threshold drift | Measurement error with temperature variation,
col16maximum measuring cycle | Maximum measuring cycles,
col16measurement range | 1 level - Fill operation,
col16measurement range | 1 level - Empty operation,
col16measurement range | 2 level - Fill operation,
col16measurement range | 2 level - Empty operation,
col16
col16
col16
col16
col16
col16
col16
col16tripping threshold | 1 level - Fill operation,
col16tripping threshold | 1 level - Empty operation,
col16tripping threshold | 2 level - Fill operation,
col16tripping threshold | 2 level - Empty operation,
col16
col16
col16
col16
col16
col16
col16
col16hysteresis | 1 level - Fill operation,
col16hysteresis | 1 level - Empty operation,
col16hysteresis | 2 level - Fill operation,
col16hysteresis | 2 level - Empty operation,
col16
col16
col16
col16
col16
col16
col16
col16
col16output type
col16output terminal
col16output logic | R1 (11-12-14),
col16output logic | R2 (21-22-24),
col16contacts material
col16mechanical durability | IEC61810-1
col16electrical durability | IEC60947-4-1,AC-1,
col16electrical durability | IEC60947-4-1,DC-1,
col16electrical durability | IEC60947-5-1,AC-15,
col16electrical durability | IEC60947-5-1,DC-13,
col16[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col16[Ie] rated operational current | IEC61810-1,Rated switching current,
col16maximum switching capacity | Maximum switching voltage,
col16maximum switching capacity | Maximum switching current,
col16maximum switching capacity | Maximum switching capacity,
col16minimum switching capacity | IEC60947-5-4,Minimum switching voltage,
col16minimum switching capacity | IEC60947-5-4,Minimum switching current,
col16minimum switching capacity | IEC60947-5-4,Minimum switching capacity,
col16maximum voltage drop | IEC62314,Only for solid state output,
col16maximum leakage current | IEC62314,Only for solid state output,
col16thermal current | IEC60947-5-1
col16short circuit protection | IEC60947-5-1,Relay Output by external fuse,
col16short circuit protection | IEC62314,Solid State Output by external fuse,
col16
col16time delay type | "OFF" delay,
col16time delay type | "ON" delay,
col16time delay type | Inhibition,
col16time delay range | "OFF" delay,
col16time delay range | "ON" delay,
col16time delay range | Inhibition,
col16response time | on crossing the threshold,
col16response time
col16response time
col16response time
col16response time
col16power on delay
col16reset time | through Un power reset,
col16reset time | through front panel reset,
col16reset time | through input control reset,
col16setting accuracy of time delay
col16repeat accuracy of time delay
col16time delay drift
col16time delay drift
col16
col16status LED
col16local signalling | Power supply availability,
col16local signalling | Power supply not availability,
col16local signalling | Timing in-progress,
col16local signalling | Output is energized,
col16local signalling | Output is de-energized,
col16local signalling | Range Setting Changes,
col16local signalling
col16local signalling
col16local signalling
col16local signalling
col16local signalling
col16local signalling
col16local signalling
col16local signalling
col16local signalling
col16
col16
col16
col16diagnostic button
col16
col16
col16
col16safety reliability data | MTTF,
col16safety reliability data | B10,
col16 | MTTFd,
col16 | B10d,
col16
Competitor Spec Reference
Competitor Spec Referencestandards
Competitor Spec Referenceproduct certifications
Competitor Spec Referencemarking
Competitor Spec Referencedirectives
Competitor Spec Referencedirectives
Competitor Spec Referencedirectives
Competitor Spec Reference
Competitor Spec Reference | IEC60721-3-3,Climatic category,
Competitor Spec Reference | Germanisher Lloyd,Environmental category,
Competitor Spec Referenceambient air temperature for storage | Storage,
Competitor Spec Referenceambient air temperature for operation | Operation,
Competitor Spec Referencerelative humidity | IEC60068-2-30,Damp heat,
Competitor Spec Reference | IEC60947-5-1,Cyclic Damp Heat Test,
Competitor Spec Referencevibration resistance | IEC60068-2-6
Competitor Spec Referenceshock resistance | IEC60068-2-27
Competitor Spec Referencebump resistance | IEC60068-2-29
Competitor Spec Referenceseismic resistance | IEC60068-3-3
Competitor Spec ReferenceIP degree of protection | IEC60529,Terminal Block,
Competitor Spec ReferenceIP degree of protection | IEC60529,Housing,
Competitor Spec ReferenceIP degree of protection | IEC60529,Front Panel,
Competitor Spec Reference
Competitor Spec Referencewidth | Width,
Competitor Spec Referenceheight | Height,
Competitor Spec Referencedepth | Depth,
Competitor Spec Referencenet weight
Competitor Spec Referencemounting support | IEC/EN 60715,Without socket,
Competitor Spec Referencemounting support | IEC/EN 60715,With socket,
Competitor Spec Referencemounting position | In relation to normal vertical mounting plane,
Competitor Spec ReferenceMinimum distance to adjacent devices | Horizontal,
Competitor Spec ReferenceMinimum distance to adjacent devices | Vertical,
Competitor Spec Referenceconnections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
Competitor Spec Referenceconnections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
Competitor Spec Referenceconnections - terminals | IEC60947-1,Solid cable (spring terminal),
Competitor Spec Referenceconnections - terminals | IEC60947-1,Flexible cable (spring terminal),
Competitor Spec Referencetightening torque | IEC60947-1,Tightening torque,
Competitor Spec Referencecable stripping length | Cable stripping length,
Competitor Spec Referenceduty time
Competitor Spec Reference
Competitor Spec Referenceelectromagnetic compatibility | Generic immunity standard,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-5,Surge,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
Competitor Spec Referenceelectromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
Competitor Spec Referenceelectromagnetic compatibility | Generic emission standard,
Competitor Spec Referenceelectromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
Competitor Spec Referenceelectromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
Competitor Spec Referenceelectromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
Competitor Spec Referenceelectromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
Competitor Spec Referenceelectromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
Competitor Spec Referenceelectromagnetic compatibility | Germanisher Lloyd,Conducted emission,
Competitor Spec Reference
Competitor Spec Referencepollution degree | IEC60664-1
Competitor Spec Referenceovervoltage category | IEC60664-1
Competitor Spec Referencecircuit group | Supply,Terminal
Competitor Spec Referencecircuit group | Input 1,
Competitor Spec Referencecircuit group | Input 2,
Competitor Spec Referencecircuit group | Input 3,
Competitor Spec Referencecircuit group | Output 1,
Competitor Spec Referencecircuit group | Output 2,
Competitor Spec Reference | Supply,Rated
Competitor Spec Reference | Input 1,Voltage
Competitor Spec Reference | Input 2,Spec
Competitor Spec Reference | Input 3,
Competitor Spec Reference | Output 1,
Competitor Spec Reference | Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 3,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Input 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Input 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Input 3,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Output 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Output 1 / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 1 / Output 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 1 / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 2 / Output 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 2 / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 3 / Output 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 3 / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 1 / Input 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 2 / Input 3,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 1 / Input 3,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Input 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Input 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Input 3,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Output 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Output 1 / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 1 / Output 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 1 / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 2 / Output 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 2 / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 3 / Output 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 3 / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 1 / Input 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 2 / Input 3,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 1 / Input 3,
Competitor Spec Reference
Competitor Spec Reference[Us] rated supply voltage
Competitor Spec Referencesupply voltage limits
Competitor Spec Referencepolarity
Competitor Spec Referencesupply frequency
Competitor Spec Referencesupply frequency
Competitor Spec Referencepower consumption
Competitor Spec Referenceimmunity to microbreaks
Competitor Spec Referencesupply terminal
Competitor Spec Referenceon-load factor
Competitor Spec Referencerelease of input voltage
Competitor Spec Reference
Competitor Spec Referencemonitoring functions | 1 level - Fill operation,
Competitor Spec Referencemonitoring functions | 1 level - Empty operation,
Competitor Spec Referencemonitoring functions | 2 level - Fill operation,
Competitor Spec Referencemonitoring functions | 2 level - Empty operation,
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference | Measurement mode,
Competitor Spec Referenceinternal input resistance | Internal input resistance,
Competitor Spec Referenceinput terminal | Input terminal,
Competitor Spec ReferenceMaximum probe supplied voltage | Maximum probe supplied voltage,
Competitor Spec ReferenceMaximum probe supplied current | Maximum probe supplied current,
Competitor Spec ReferenceMaximum length of probes cable | Maximum length of probes cable,
Competitor Spec Referenceinput frequency | Maximum cable capacitance,
Competitor Spec Referencesetting accuracy of the switching threshold | Setting accuracy,
Competitor Spec Referencerepeat accuracy of the switching threshold | Repeat accuracy (constant parameters),
Competitor Spec Referencemeasurement method | Measurement method,
Competitor Spec Referenceswitching threshold drift | Measurement error with supply voltage variation,
Competitor Spec Referenceswitching threshold drift | Measurement error with temperature variation,
Competitor Spec Referencemaximum measuring cycle | Maximum measuring cycles,
Competitor Spec Referencemeasurement range | 1 level - Fill operation,
Competitor Spec Referencemeasurement range | 1 level - Empty operation,
Competitor Spec Referencemeasurement range | 2 level - Fill operation,
Competitor Spec Referencemeasurement range | 2 level - Empty operation,
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Referencetripping threshold | 1 level - Fill operation,
Competitor Spec Referencetripping threshold | 1 level - Empty operation,
Competitor Spec Referencetripping threshold | 2 level - Fill operation,
Competitor Spec Referencetripping threshold | 2 level - Empty operation,
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Referencehysteresis | 1 level - Fill operation,
Competitor Spec Referencehysteresis | 1 level - Empty operation,
Competitor Spec Referencehysteresis | 2 level - Fill operation,
Competitor Spec Referencehysteresis | 2 level - Empty operation,
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Referenceoutput type
Competitor Spec Referenceoutput terminal
Competitor Spec Referenceoutput logic | R1 (11-12-14),
Competitor Spec Referenceoutput logic | R2 (21-22-24),
Competitor Spec Referencecontacts material
Competitor Spec Referencemechanical durability | IEC61810-1
Competitor Spec Referenceelectrical durability | IEC60947-4-1,AC-1,
Competitor Spec Referenceelectrical durability | IEC60947-4-1,DC-1,
Competitor Spec Referenceelectrical durability | IEC60947-5-1,AC-15,
Competitor Spec Referenceelectrical durability | IEC60947-5-1,DC-13,
Competitor Spec Reference[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
Competitor Spec Reference[Ie] rated operational current | IEC61810-1,Rated switching current,
Competitor Spec Referencemaximum switching capacity | Maximum switching voltage,
Competitor Spec Referencemaximum switching capacity | Maximum switching current,
Competitor Spec Referencemaximum switching capacity | Maximum switching capacity,
Competitor Spec Referenceminimum switching capacity | IEC60947-5-4,Minimum switching voltage,
Competitor Spec Referenceminimum switching capacity | IEC60947-5-4,Minimum switching current,
Competitor Spec Referenceminimum switching capacity | IEC60947-5-4,Minimum switching capacity,
Competitor Spec Referencemaximum voltage drop | IEC62314,Only for solid state output,
Competitor Spec Referencemaximum leakage current | IEC62314,Only for solid state output,
Competitor Spec Referencethermal current | IEC60947-5-1
Competitor Spec Referenceshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
Competitor Spec Referenceshort circuit protection | IEC62314,Solid State Output by external fuse,
Competitor Spec Reference
Competitor Spec Referencetime delay type | "OFF" delay,
Competitor Spec Referencetime delay type | "ON" delay,
Competitor Spec Referencetime delay type | Inhibition,
Competitor Spec Referencetime delay range | "OFF" delay,
Competitor Spec Referencetime delay range | "ON" delay,
Competitor Spec Referencetime delay range | Inhibition,
Competitor Spec Referenceresponse time | on crossing the threshold,
Competitor Spec Referenceresponse time
Competitor Spec Referenceresponse time
Competitor Spec Referenceresponse time
Competitor Spec Referenceresponse time
Competitor Spec Referencepower on delay
Competitor Spec Referencereset time | through Un power reset,
Competitor Spec Referencereset time | through front panel reset,
Competitor Spec Referencereset time | through input control reset,
Competitor Spec Referencesetting accuracy of time delay
Competitor Spec Referencerepeat accuracy of time delay
Competitor Spec Referencetime delay drift
Competitor Spec Referencetime delay drift
Competitor Spec Reference
Competitor Spec Referencestatus LED
Competitor Spec Referencelocal signalling | Power supply availability,
Competitor Spec Referencelocal signalling | Power supply not availability,
Competitor Spec Referencelocal signalling | Timing in-progress,
Competitor Spec Referencelocal signalling | Output is energized,
Competitor Spec Referencelocal signalling | Output is de-energized,
Competitor Spec Referencelocal signalling | Range Setting Changes,
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Referencediagnostic button
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Referencesafety reliability data | MTTF,
Competitor Spec Referencesafety reliability data | B10,
Competitor Spec Reference | MTTFd,
Competitor Spec Reference | B10d,
Competitor Spec Reference
RM35LM33MW
RM35LM33MWstandards | EN60255-6, IEC60255-6
RM35LM33MWproduct certifications | UL, CSA, GL, C-Tick, GOST
RM35LM33MWmarking | UL, CSA, GL, C-Tick, GOST, CE
RM35LM33MWdirectives | No 73/23/EEC + 93/68/EEC
RM35LM33MWdirectives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
RM35LM33MWdirectives | 2002/95/EC
RM35LM33MW
RM35LM33MW | Not specified ¦ IEC60721-3-3,Climatic category,
RM35LM33MW | Germanisher Lloyd,Environmental category,
RM35LM33MWambient air temperature for storage | -40…+70 ¦ ,Storage,
RM35LM33MWambient air temperature for operation | -20…+50 ¦ ,Operation,
RM35LM33MWrelative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM35LM33MW | IEC60947-5-1,Cyclic Damp Heat Test,
RM35LM33MWvibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM35LM33MWshock resistance | 5 gn ¦ IEC60068-2-27
RM35LM33MWbump resistance | IEC60068-2-29
RM35LM33MWseismic resistance | IEC60068-3-3
RM35LM33MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM35LM33MWIP degree of protection | IP30 ¦ IEC60529,Housing,
RM35LM33MWIP degree of protection | IEC60529,Front Panel,
RM35LM33MW
RM35LM33MWwidth | 35 x 90 x 72 ¦ ,Width,
RM35LM33MWheight | Height,
RM35LM33MWdepth | Depth,
RM35LM33MWnet weight | 130
RM35LM33MWmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM35LM33MWmounting support | - ¦ IEC/EN 60715,With socket,
RM35LM33MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35LM33MWMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM35LM33MWMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM35LM33MWconnections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35LM33MWconnections - terminals | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35LM33MWconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM35LM33MWconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35LM33MWtightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM35LM33MWcable stripping length | Not specified ¦ ,Cable stripping length,
RM35LM33MWduty time | Not specified
RM35LM33MW
RM35LM33MWelectromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard,
RM35LM33MWelectromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM35LM33MWelectromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM35LM33MWelectromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM35LM33MWelectromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM35LM33MWelectromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM35LM33MWelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM35LM33MWelectromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35LM33MWelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM35LM33MWelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM35LM33MWelectromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM35LM33MWelectromagnetic compatibility | · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35LM33MWelectromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM35LM33MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35LM33MWelectromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35LM33MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM35LM33MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35LM33MWelectromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35LM33MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35LM33MW
RM35LM33MWpollution degree | 3 ¦ IEC60664-1
RM35LM33MWovervoltage category | III ¦ IEC60664-1
RM35LM33MWcircuit group | Supply,Terminal
RM35LM33MWcircuit group | Input 1,
RM35LM33MWcircuit group | Input 2,
RM35LM33MWcircuit group | Input 3,
RM35LM33MWcircuit group | Output 1,
RM35LM33MWcircuit group | 600 ¦ ,Output 2,
RM35LM33MW | 600 ¦ ,Supply,Rated
RM35LM33MW | 600 ¦ ,Input 1,Voltage
RM35LM33MW | Input 2,Spec
RM35LM33MW | Input 3,
RM35LM33MW | Output 1,
RM35LM33MW | Output 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Supply,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM35LM33MW[Ui] rated insulation voltage | 4 ¦ IEC60664-1,Output 1,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM35LM33MW[Ui] rated insulation voltage | 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM35LM33MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM35LM33MW[Uimp] rated impulse withstand voltage | > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM35LM33MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM35LM33MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM35LM33MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM35LM33MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM35LM33MWdielectric strength | IEC60255-27,Supply / Output 1,
RM35LM33MWdielectric strength | IEC60255-27,Supply / Output 2,
RM35LM33MWdielectric strength | IEC60255-27,Output 1 / Output 2,
RM35LM33MWdielectric strength | IEC60255-27,Input 1 / Output 1,
RM35LM33MWdielectric strength | IEC60255-27,Input 1 / Output 2,
RM35LM33MWdielectric strength | IEC60255-27,Input 2 / Output 1,
RM35LM33MWdielectric strength | IEC60255-27,Input 2 / Output 2,
RM35LM33MWdielectric strength | IEC60255-27,Input 3 / Output 1,
RM35LM33MWdielectric strength | IEC60255-27,Input 3 / Output 2,
RM35LM33MWdielectric strength | IEC60255-27,Input 1 / Input 2,
RM35LM33MWdielectric strength | IEC60255-27,Input 2 / Input 3,
RM35LM33MWdielectric strength | IEC60255-27,Input 1 / Input 3,
RM35LM33MWinsulation resistance | IEC60255-27,Supply / Input 1,
RM35LM33MWinsulation resistance | IEC60255-27,Supply / Input 2,
RM35LM33MWinsulation resistance | IEC60255-27,Supply / Input 3,
RM35LM33MWinsulation resistance | IEC60255-27,Supply / Output 1,
RM35LM33MWinsulation resistance | IEC60255-27,Supply / Output 2,
RM35LM33MWinsulation resistance | IEC60255-27,Output 1 / Output 2,
RM35LM33MWinsulation resistance | IEC60255-27,Input 1 / Output 1,
RM35LM33MWinsulation resistance | IEC60255-27,Input 1 / Output 2,
RM35LM33MWinsulation resistance | IEC60255-27,Input 2 / Output 1,
RM35LM33MWinsulation resistance | IEC60255-27,Input 2 / Output 2,
RM35LM33MWinsulation resistance | IEC60255-27,Input 3 / Output 1,
RM35LM33MWinsulation resistance | IEC60255-27,Input 3 / Output 2,
RM35LM33MWinsulation resistance | IEC60255-27,Input 1 / Input 2,
RM35LM33MWinsulation resistance | IEC60255-27,Input 2 / Input 3,
RM35LM33MWinsulation resistance | IEC60255-27,Input 1 / Input 3,
RM35LM33MW
RM35LM33MW[Us] rated supply voltage | ~/-- 24…240
RM35LM33MWsupply voltage limits | ~/-- 20.4…264
RM35LM33MWpolarity
RM35LM33MWsupply frequency | 50 / 60
RM35LM33MWsupply frequency | 45…66
RM35LM33MWpower consumption | ~ 5VA, -- 1.5W
RM35LM33MWimmunity to microbreaks | 90 (AC), 100 (DC)
RM35LM33MWsupply terminal | A1-A2
RM35LM33MWon-load factor
RM35LM33MWrelease of input voltage
RM35LM33MW
RM35LM33MWmonitoring functions | 1 level - Fill operation,
RM35LM33MWmonitoring functions | 1 level - Empty operation,
RM35LM33MWmonitoring functions | 2 level - Fill operation,
RM35LM33MWmonitoring functions | 2 level - Empty operation,
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW | Measurement mode,
RM35LM33MWinternal input resistance | Internal input resistance,
RM35LM33MWinput terminal | Input terminal,
RM35LM33MWMaximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage,
RM35LM33MWMaximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
RM35LM33MWMaximum length of probes cable | 100 ¦ ,Maximum length of probes cable,
RM35LM33MWinput frequency | Maximum cable capacitance,
RM35LM33MWsetting accuracy of the switching threshold | +/- 10% of full scale value, +/- 20% for HS range ¦ ,Setting accuracy,
RM35LM33MWrepeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM35LM33MWmeasurement method | Liquid level probe ¦ ,Measurement method,
RM35LM33MWswitching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation,
RM35LM33MWswitching threshold drift | 0.5% / oC ¦ ,Measurement error with temperature variation,
RM35LM33MWmaximum measuring cycle | Maximum measuring cycles,
RM35LM33MWmeasurement range | 1 level - Fill operation,
RM35LM33MWmeasurement range | 1 level - Empty operation,
RM35LM33MWmeasurement range | 2 level - Fill operation,
RM35LM33MWmeasurement range | 2 level - Empty operation,
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MWtripping threshold | 1 level - Fill operation,
RM35LM33MWtripping threshold | 1 level - Empty operation,
RM35LM33MWtripping threshold | 2 level - Fill operation,
RM35LM33MWtripping threshold | 2 level - Empty operation,
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MWhysteresis | 1 level - Fill operation,
RM35LM33MWhysteresis | 1 level - Empty operation,
RM35LM33MWhysteresis | 2 level - Fill operation,
RM35LM33MWhysteresis | 2 level - Empty operation,
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MWoutput type | 2 x C/O relay contacts
RM35LM33MWoutput terminal | 11-12-14, 21-22-24
RM35LM33MWoutput logic | Not specified ¦ ,R1 (11-12-14),
RM35LM33MWoutput logic | R2 (21-22-24),
RM35LM33MWcontacts material | Cadmium free
RM35LM33MWmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM35LM33MWelectrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1,
RM35LM33MWelectrical durability | IEC60947-4-1,DC-1,
RM35LM33MWelectrical durability | IEC60947-5-1,AC-15,
RM35LM33MWelectrical durability | IEC60947-5-1,DC-13,
RM35LM33MW[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM35LM33MW[Ie] rated operational current | IEC61810-1,Rated switching current,
RM35LM33MWmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM35LM33MWmaximum switching capacity | ~ 5 ¦ ,Maximum switching current,
RM35LM33MWmaximum switching capacity | 1250 ¦ ,Maximum switching capacity,
RM35LM33MWminimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
RM35LM33MWminimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM35LM33MWminimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM35LM33MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35LM33MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35LM33MWthermal current | 5 ¦ IEC60947-5-1
RM35LM33MWshort circuit protection | 8 ¦ IEC60947-5-1,Relay Output by external fuse,
RM35LM33MWshort circuit protection | IEC62314,Solid State Output by external fuse,
RM35LM33MW
RM35LM33MWtime delay type | · ¦ ,"OFF" delay,
RM35LM33MWtime delay type | · ¦ ,"ON" delay,
RM35LM33MWtime delay type | - ¦ ,Inhibition,
RM35LM33MWtime delay range | Adjustable 0.1…5 ¦ ,"OFF" delay,
RM35LM33MWtime delay range | Adjustable 0.1…5 ¦ ,"ON" delay,
RM35LM33MWtime delay range | - ¦ ,Inhibition,
RM35LM33MWresponse time | Not specified ¦ ,on crossing the threshold,
RM35LM33MWresponse time
RM35LM33MWresponse time
RM35LM33MWresponse time
RM35LM33MWresponse time
RM35LM33MWpower on delay | 0
RM35LM33MWreset time | 0
RM35LM33MWreset time | through front panel reset,
RM35LM33MWreset time | through input control reset,
RM35LM33MWsetting accuracy of time delay | +/- 10% of full scales
RM35LM33MWrepeat accuracy of time delay | +/- 2%
RM35LM33MWtime delay drift | Not specified
RM35LM33MWtime delay drift | Not specified
RM35LM33MW
RM35LM33MWstatus LED
RM35LM33MWlocal signalling | Power supply availability,
RM35LM33MWlocal signalling | Power supply not availability,
RM35LM33MWlocal signalling | Timing in-progress,
RM35LM33MWlocal signalling | Output is energized,
RM35LM33MWlocal signalling | Output is de-energized,
RM35LM33MWlocal signalling | Range Setting Changes,
RM35LM33MWlocal signalling
RM35LM33MWlocal signalling
RM35LM33MWlocal signalling
RM35LM33MWlocal signalling
RM35LM33MWlocal signalling
RM35LM33MWlocal signalling
RM35LM33MWlocal signalling
RM35LM33MWlocal signalling
RM35LM33MWlocal signalling
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MWdiagnostic button
RM35LM33MW
RM35LM33MW
RM35LM33MW
RM35LM33MWsafety reliability data | MTTF,
RM35LM33MWsafety reliability data | B10,
RM35LM33MW | MTTFd,
RM35LM33MW | B10d,
RM35LM33MW
RM35LV14MW
RM35LV14MWstandards | EN60255-6, IEC60255-6
RM35LV14MWproduct certifications | UL, CSA, GL, C-Tick, GOST
RM35LV14MWmarking | UL, CSA, GL, C-Tick, GOST, CE
RM35LV14MWdirectives | No 73/23/EEC + 93/68/EEC
RM35LV14MWdirectives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
RM35LV14MWdirectives | 2002/95/EC
RM35LV14MW
RM35LV14MW | Not specified ¦ IEC60721-3-3,Climatic category,
RM35LV14MW | Germanisher Lloyd,Environmental category,
RM35LV14MWambient air temperature for storage | -40…+70 ¦ ,Storage,
RM35LV14MWambient air temperature for operation | -20…+50 ¦ ,Operation,
RM35LV14MWrelative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM35LV14MW | IEC60947-5-1,Cyclic Damp Heat Test,
RM35LV14MWvibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM35LV14MWshock resistance | 5 gn ¦ IEC60068-2-27
RM35LV14MWbump resistance | IEC60068-2-29
RM35LV14MWseismic resistance | IEC60068-3-3
RM35LV14MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM35LV14MWIP degree of protection | IP30 ¦ IEC60529,Housing,
RM35LV14MWIP degree of protection | IEC60529,Front Panel,
RM35LV14MW
RM35LV14MWwidth | 35 x 90 x 72 ¦ ,Width,
RM35LV14MWheight | Height,
RM35LV14MWdepth | Depth,
RM35LV14MWnet weight | 130
RM35LV14MWmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM35LV14MWmounting support | - ¦ IEC/EN 60715,With socket,
RM35LV14MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35LV14MWMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM35LV14MWMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM35LV14MWconnections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35LV14MWconnections - terminals | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35LV14MWconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM35LV14MWconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35LV14MWtightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM35LV14MWcable stripping length | Not specified ¦ ,Cable stripping length,
RM35LV14MWduty time | Not specified
RM35LV14MW
RM35LV14MWelectromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard,
RM35LV14MWelectromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM35LV14MWelectromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM35LV14MWelectromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM35LV14MWelectromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM35LV14MWelectromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM35LV14MWelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM35LV14MWelectromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35LV14MWelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM35LV14MWelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM35LV14MWelectromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM35LV14MWelectromagnetic compatibility | · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35LV14MWelectromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM35LV14MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35LV14MWelectromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35LV14MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM35LV14MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35LV14MWelectromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35LV14MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35LV14MW
RM35LV14MWpollution degree | 3 ¦ IEC60664-1
RM35LV14MWovervoltage category | III ¦ IEC60664-1
RM35LV14MWcircuit group | Supply,Terminal
RM35LV14MWcircuit group | Input 1,
RM35LV14MWcircuit group | Input 2,
RM35LV14MWcircuit group | Input 3,
RM35LV14MWcircuit group | Output 1,
RM35LV14MWcircuit group | 600 ¦ ,Output 2,
RM35LV14MW | 600 ¦ ,Supply,Rated
RM35LV14MW | 600 ¦ ,Input 1,Voltage
RM35LV14MW | Input 2,Spec
RM35LV14MW | Input 3,
RM35LV14MW | Output 1,
RM35LV14MW | Output 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Supply,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM35LV14MW[Ui] rated insulation voltage | 4 ¦ IEC60664-1,Output 1,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM35LV14MW[Ui] rated insulation voltage | 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM35LV14MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM35LV14MW[Uimp] rated impulse withstand voltage | > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM35LV14MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM35LV14MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM35LV14MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM35LV14MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM35LV14MWdielectric strength | IEC60255-27,Supply / Output 1,
RM35LV14MWdielectric strength | IEC60255-27,Supply / Output 2,
RM35LV14MWdielectric strength | IEC60255-27,Output 1 / Output 2,
RM35LV14MWdielectric strength | IEC60255-27,Input 1 / Output 1,
RM35LV14MWdielectric strength | IEC60255-27,Input 1 / Output 2,
RM35LV14MWdielectric strength | IEC60255-27,Input 2 / Output 1,
RM35LV14MWdielectric strength | IEC60255-27,Input 2 / Output 2,
RM35LV14MWdielectric strength | IEC60255-27,Input 3 / Output 1,
RM35LV14MWdielectric strength | IEC60255-27,Input 3 / Output 2,
RM35LV14MWdielectric strength | IEC60255-27,Input 1 / Input 2,
RM35LV14MWdielectric strength | IEC60255-27,Input 2 / Input 3,
RM35LV14MWdielectric strength | IEC60255-27,Input 1 / Input 3,
RM35LV14MWinsulation resistance | IEC60255-27,Supply / Input 1,
RM35LV14MWinsulation resistance | IEC60255-27,Supply / Input 2,
RM35LV14MWinsulation resistance | IEC60255-27,Supply / Input 3,
RM35LV14MWinsulation resistance | IEC60255-27,Supply / Output 1,
RM35LV14MWinsulation resistance | IEC60255-27,Supply / Output 2,
RM35LV14MWinsulation resistance | IEC60255-27,Output 1 / Output 2,
RM35LV14MWinsulation resistance | IEC60255-27,Input 1 / Output 1,
RM35LV14MWinsulation resistance | IEC60255-27,Input 1 / Output 2,
RM35LV14MWinsulation resistance | IEC60255-27,Input 2 / Output 1,
RM35LV14MWinsulation resistance | IEC60255-27,Input 2 / Output 2,
RM35LV14MWinsulation resistance | IEC60255-27,Input 3 / Output 1,
RM35LV14MWinsulation resistance | IEC60255-27,Input 3 / Output 2,
RM35LV14MWinsulation resistance | IEC60255-27,Input 1 / Input 2,
RM35LV14MWinsulation resistance | IEC60255-27,Input 2 / Input 3,
RM35LV14MWinsulation resistance | IEC60255-27,Input 1 / Input 3,
RM35LV14MW
RM35LV14MW[Us] rated supply voltage | ~/-- 24…240
RM35LV14MWsupply voltage limits | ~/-- 20.4…264
RM35LV14MWpolarity
RM35LV14MWsupply frequency | 50 / 60
RM35LV14MWsupply frequency | 45…66
RM35LV14MWpower consumption | ~ 5VA, -- 1.5W
RM35LV14MWimmunity to microbreaks | 90 (AC), 100 (DC)
RM35LV14MWsupply terminal | A1-A2
RM35LV14MWon-load factor
RM35LV14MWrelease of input voltage
RM35LV14MW
RM35LV14MWmonitoring functions | 1 level - Fill operation,
RM35LV14MWmonitoring functions | 1 level - Empty operation,
RM35LV14MWmonitoring functions | 2 level - Fill operation,
RM35LV14MWmonitoring functions | 2 level - Empty operation,
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW | Measurement mode,
RM35LV14MWinternal input resistance | Internal input resistance,
RM35LV14MWinput terminal | Input terminal,
RM35LV14MWMaximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage,
RM35LV14MWMaximum probe supplied current | 40 ¦ ,Maximum probe supplied current,
RM35LV14MWMaximum length of probes cable | 100 ¦ ,Maximum length of probes cable,
RM35LV14MWinput frequency | Maximum cable capacitance,
RM35LV14MWsetting accuracy of the switching threshold | +/- 10% of full scale value ¦ ,Setting accuracy,
RM35LV14MWrepeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM35LV14MWmeasurement method | 12V NPN/PNP ultrasonics sensor ¦ ,Measurement method,
RM35LV14MWswitching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation,
RM35LV14MWswitching threshold drift | 0.5% / oC ¦ ,Measurement error with temperature variation,
RM35LV14MWmaximum measuring cycle | Maximum measuring cycles,
RM35LV14MWmeasurement range | 1 level - Fill operation,
RM35LV14MWmeasurement range | 1 level - Empty operation,
RM35LV14MWmeasurement range | 2 level - Fill operation,
RM35LV14MWmeasurement range | 2 level - Empty operation,
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MWtripping threshold | 1 level - Fill operation,
RM35LV14MWtripping threshold | 1 level - Empty operation,
RM35LV14MWtripping threshold | 2 level - Fill operation,
RM35LV14MWtripping threshold | 2 level - Empty operation,
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MWhysteresis | 1 level - Fill operation,
RM35LV14MWhysteresis | 1 level - Empty operation,
RM35LV14MWhysteresis | 2 level - Fill operation,
RM35LV14MWhysteresis | 2 level - Empty operation,
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MWoutput type | 1 x C/O relay contacts
RM35LV14MWoutput terminal | 11-12-14
RM35LV14MWoutput logic | Not specified ¦ ,R1 (11-12-14),
RM35LV14MWoutput logic | R2 (21-22-24),
RM35LV14MWcontacts material | Cadmium free
RM35LV14MWmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM35LV14MWelectrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1,
RM35LV14MWelectrical durability | IEC60947-4-1,DC-1,
RM35LV14MWelectrical durability | IEC60947-5-1,AC-15,
RM35LV14MWelectrical durability | IEC60947-5-1,DC-13,
RM35LV14MW[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM35LV14MW[Ie] rated operational current | IEC61810-1,Rated switching current,
RM35LV14MWmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM35LV14MWmaximum switching capacity | ~ 5 ¦ ,Maximum switching current,
RM35LV14MWmaximum switching capacity | 1250 ¦ ,Maximum switching capacity,
RM35LV14MWminimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
RM35LV14MWminimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM35LV14MWminimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM35LV14MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35LV14MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35LV14MWthermal current | 5 ¦ IEC60947-5-1
RM35LV14MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM35LV14MWshort circuit protection | IEC62314,Solid State Output by external fuse,
RM35LV14MW
RM35LV14MWtime delay type | · ¦ ,"OFF" delay,
RM35LV14MWtime delay type | · ¦ ,"ON" delay,
RM35LV14MWtime delay type | - ¦ ,Inhibition,
RM35LV14MWtime delay range | Adjustable 0.1…5 ¦ ,"OFF" delay,
RM35LV14MWtime delay range | Adjustable 0.1…5 ¦ ,"ON" delay,
RM35LV14MWtime delay range | - ¦ ,Inhibition,
RM35LV14MWresponse time | Not specified ¦ ,on crossing the threshold,
RM35LV14MWresponse time
RM35LV14MWresponse time
RM35LV14MWresponse time
RM35LV14MWresponse time
RM35LV14MWpower on delay | 0
RM35LV14MWreset time | 0
RM35LV14MWreset time | through front panel reset,
RM35LV14MWreset time | through input control reset,
RM35LV14MWsetting accuracy of time delay | +/- 10% of full scales
RM35LV14MWrepeat accuracy of time delay | +/- 2%
RM35LV14MWtime delay drift | Not specified
RM35LV14MWtime delay drift | Not specified
RM35LV14MW
RM35LV14MWstatus LED
RM35LV14MWlocal signalling | Power supply availability,
RM35LV14MWlocal signalling | Power supply not availability,
RM35LV14MWlocal signalling | Timing in-progress,
RM35LV14MWlocal signalling | Output is energized,
RM35LV14MWlocal signalling | Output is de-energized,
RM35LV14MWlocal signalling | Range Setting Changes,
RM35LV14MWlocal signalling
RM35LV14MWlocal signalling
RM35LV14MWlocal signalling
RM35LV14MWlocal signalling
RM35LV14MWlocal signalling
RM35LV14MWlocal signalling
RM35LV14MWlocal signalling
RM35LV14MWlocal signalling
RM35LV14MWlocal signalling
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MWdiagnostic button
RM35LV14MW
RM35LV14MW
RM35LV14MW
RM35LV14MWsafety reliability data | MTTF,
RM35LV14MWsafety reliability data | B10,
RM35LV14MW | MTTFd,
RM35LV14MW | B10d,
RM35LV14MW
RM4LA32
RM4LA32standards | EN60255-6, IEC60255-6
RM4LA32product certifications | UL, CSA, GL, C-Tick, GOST
RM4LA32marking | UL, CSA, GL, C-Tick, GOST, CE
RM4LA32directives | No 73/23/EEC + 93/68/EEC
RM4LA32directives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
RM4LA32directives | 2002/95/EC
RM4LA32
RM4LA32 | Not specified ¦ IEC60721-3-3,Climatic category,
RM4LA32 | Germanisher Lloyd,Environmental category,
RM4LA32ambient air temperature for storage | Not specified ¦ ,Storage,
RM4LA32ambient air temperature for operation | Not specified ¦ ,Operation,
RM4LA32relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
RM4LA32 | IEC60947-5-1,Cyclic Damp Heat Test,
RM4LA32vibration resistance | Not specified ¦ IEC60068-2-6
RM4LA32shock resistance | Not specified ¦ IEC60068-2-27
RM4LA32bump resistance | IEC60068-2-29
RM4LA32seismic resistance | IEC60068-3-3
RM4LA32IP degree of protection | Not specified ¦ IEC60529,Terminal Block,
RM4LA32IP degree of protection | Not specified ¦ IEC60529,Housing,
RM4LA32IP degree of protection | IEC60529,Front Panel,
RM4LA32
RM4LA32width | 22.5 x 78 x 80 ¦ ,Width,
RM4LA32height | Height,
RM4LA32depth | Depth,
RM4LA32net weight | 168
RM4LA32mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM4LA32mounting support | - ¦ IEC/EN 60715,With socket,
RM4LA32mounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
RM4LA32Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM4LA32Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM4LA32connections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM4LA32connections - terminals | Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM4LA32connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM4LA32connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4LA32tightening torque | Not specified ¦ IEC60947-1,Tightening torque,
RM4LA32cable stripping length | Not specified ¦ ,Cable stripping length,
RM4LA32duty time | Not specified
RM4LA32
RM4LA32electromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard,
RM4LA32electromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM4LA32electromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM4LA32electromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM4LA32electromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM4LA32electromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM4LA32electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM4LA32electromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM4LA32electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM4LA32electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM4LA32electromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM4LA32electromagnetic compatibility | ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM4LA32electromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM4LA32electromagnetic compatibility | Class B Group1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM4LA32electromagnetic compatibility | Class B Group1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM4LA32electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM4LA32electromagnetic compatibility | Class B Group1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM4LA32electromagnetic compatibility | Class B Group1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM4LA32electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4LA32
RM4LA32pollution degree | Not specified ¦ IEC60664-1
RM4LA32overvoltage category | Not specified ¦ IEC60664-1
RM4LA32circuit group | Supply,Terminal
RM4LA32circuit group | Input 1,
RM4LA32circuit group | Input 2,
RM4LA32circuit group | Input 3,
RM4LA32circuit group | Output 1,
RM4LA32circuit group | Not specified ¦ ,Output 2,
RM4LA32 | Not specified ¦ ,Supply,Rated
RM4LA32 | Not specified ¦ ,Input 1,Voltage
RM4LA32 | Input 2,Spec
RM4LA32 | Input 3,
RM4LA32 | Output 1,
RM4LA32 | Output 2,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Supply,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM4LA32[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Output 1,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM4LA32[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM4LA32[Uimp] rated impulse withstand voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM4LA32dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM4LA32dielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM4LA32dielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM4LA32dielectric strength | IEC60255-27,Supply / Output 1,
RM4LA32dielectric strength | IEC60255-27,Supply / Output 2,
RM4LA32dielectric strength | IEC60255-27,Output 1 / Output 2,
RM4LA32dielectric strength | IEC60255-27,Input 1 / Output 1,
RM4LA32dielectric strength | IEC60255-27,Input 1 / Output 2,
RM4LA32dielectric strength | IEC60255-27,Input 2 / Output 1,
RM4LA32dielectric strength | IEC60255-27,Input 2 / Output 2,
RM4LA32dielectric strength | IEC60255-27,Input 3 / Output 1,
RM4LA32dielectric strength | IEC60255-27,Input 3 / Output 2,
RM4LA32dielectric strength | IEC60255-27,Input 1 / Input 2,
RM4LA32dielectric strength | IEC60255-27,Input 2 / Input 3,
RM4LA32dielectric strength | IEC60255-27,Input 1 / Input 3,
RM4LA32insulation resistance | IEC60255-27,Supply / Input 1,
RM4LA32insulation resistance | IEC60255-27,Supply / Input 2,
RM4LA32insulation resistance | IEC60255-27,Supply / Input 3,
RM4LA32insulation resistance | IEC60255-27,Supply / Output 1,
RM4LA32insulation resistance | IEC60255-27,Supply / Output 2,
RM4LA32insulation resistance | IEC60255-27,Output 1 / Output 2,
RM4LA32insulation resistance | IEC60255-27,Input 1 / Output 1,
RM4LA32insulation resistance | IEC60255-27,Input 1 / Output 2,
RM4LA32insulation resistance | IEC60255-27,Input 2 / Output 1,
RM4LA32insulation resistance | IEC60255-27,Input 2 / Output 2,
RM4LA32insulation resistance | IEC60255-27,Input 3 / Output 1,
RM4LA32insulation resistance | IEC60255-27,Input 3 / Output 2,
RM4LA32insulation resistance | IEC60255-27,Input 1 / Input 2,
RM4LA32insulation resistance | IEC60255-27,Input 2 / Input 3,
RM4LA32insulation resistance | IEC60255-27,Input 1 / Input 3,
RM4LA32
RM4LA32[Us] rated supply voltage | RM4LA32B: ~ 24 RM4LA32F: ~110…130 RM4LA32M: ~220…240 RM4LA32MW: ~/-- 24…240 RM4LA32Q: ~380…415
RM4LA32supply voltage limits | Not specified
RM4LA32polarity
RM4LA32supply frequency | 50 / 60
RM4LA32supply frequency | Not specified
RM4LA32power consumption | RM4LA32B: 3.1VA RM4LA32F: 2.7VA RM4LA32M: 2.6VA RM4LA32MW: 2.7VA, 2.4W RM4LA32Q: 3.4VA
RM4LA32immunity to microbreaks | Not specified
RM4LA32supply terminal | A1-A2
RM4LA32on-load factor
RM4LA32release of input voltage
RM4LA32
RM4LA32monitoring functions | 1 level - Fill operation,
RM4LA32monitoring functions | 1 level - Empty operation,
RM4LA32monitoring functions | 2 level - Fill operation,
RM4LA32monitoring functions | 2 level - Empty operation,
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32 | Measurement mode,
RM4LA32internal input resistance | Internal input resistance,
RM4LA32input terminal | Input terminal,
RM4LA32Maximum probe supplied voltage | 24 ¦ ,Maximum probe supplied voltage,
RM4LA32Maximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
RM4LA32Maximum length of probes cable | 1000 ¦ ,Maximum length of probes cable,
RM4LA32input frequency | Maximum cable capacitance,
RM4LA32setting accuracy of the switching threshold | Not specified ¦ ,Setting accuracy,
RM4LA32repeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM4LA32measurement method | Liquid level probe ¦ ,Measurement method,
RM4LA32switching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation,
RM4LA32switching threshold drift | Not specified ¦ ,Measurement error with temperature variation,
RM4LA32maximum measuring cycle | Maximum measuring cycles,
RM4LA32measurement range | 1 level - Fill operation,
RM4LA32measurement range | 1 level - Empty operation,
RM4LA32measurement range | 2 level - Fill operation,
RM4LA32measurement range | 2 level - Empty operation,
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32tripping threshold | 1 level - Fill operation,
RM4LA32tripping threshold | 1 level - Empty operation,
RM4LA32tripping threshold | 2 level - Fill operation,
RM4LA32tripping threshold | 2 level - Empty operation,
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32hysteresis | 1 level - Fill operation,
RM4LA32hysteresis | 1 level - Empty operation,
RM4LA32hysteresis | 2 level - Fill operation,
RM4LA32hysteresis | 2 level - Empty operation,
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32
RM4LA32output type | 2 x C/O relay contacts
RM4LA32output terminal | 15-16-18, 25-26-28
RM4LA32output logic | Not specified ¦ ,R1 (11-12-14),
RM4LA32output logic | R2 (21-22-24),
RM4LA32contacts material | Not specified
RM4LA32mechanical durability | Not specified ¦ IEC61810-1
RM4LA32electrical durability | Not specified ¦ IEC60947-4-1,AC-1,
RM4LA32electrical durability | IEC60947-4-1,DC-1,
RM4LA32electrical durability | IEC60947-5-1,AC-15,
RM4LA32electrical durability | IEC60947-5-1,DC-13,
RM4LA32[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4LA32[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4LA32maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM4LA32maximum switching capacity | 8 ¦ ,Maximum switching current,
RM4LA32maximum switching capacity | 2000VA ¦ ,Maximum switching capacity,
RM4LA32minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching voltage,
RM4LA32minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching current,
RM4LA32minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching capacity,
RM4LA32maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM4LA32maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM4LA32thermal current | 8 ¦ IEC60947-5-1
RM4LA32short circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM4LA32short circuit protection | IEC62314,Solid State Output by external fuse,
RM4LA32
RM4LA32time delay type | · ¦ ,"OFF" delay,
RM4LA32time delay type | · ¦ ,"ON" delay,
RM4LA32time delay type | - ¦ ,Inhibition,
RM4LA32time delay range | Adjustable 0.1…10 ¦ ,"OFF" delay,
RM4LA32time delay range | Adjustable 0.1…10 ¦ ,"ON" delay,
RM4LA32time delay range | - ¦ ,Inhibition,
RM4LA32response time | Not specified ¦ ,on crossing the threshold,
RM4LA32response time
RM4LA32response time
RM4LA32response time
RM4LA32response time
RM4LA32power on delay | Not specified
RM4LA32reset time | Not specified ¦ ,through Un power reset,
RM4LA32reset time | through front panel reset,
RM4LA32reset time | through input control reset,
RM4LA32setting accuracy of time delay | Not specified
RM4LA32repeat accuracy of time delay | Not specified
RM4LA32time delay drift | Not specified
RM4LA32time delay drift | Not specified
RM4LA32
RM4LA32status LED
RM4LA32local signalling | Power supply availability,
RM4LA32local signalling | Power supply not availability,
RM4LA32local signalling | Timing in-progress,
RM4LA32local signalling | Output is energized,
RM4LA32local signalling | Output is de-energized,
RM4LA32local signalling | Range Setting Changes,
RM4LA32local signalling
RM4LA32local signalling
RM4LA32local signalling
RM4LA32local signalling
RM4LA32local signalling
RM4LA32local signalling
RM4LA32local signalling
RM4LA32local signalling
RM4LA32local signalling
RM4LA32
RM4LA32
RM4LA32
RM4LA32diagnostic button
RM4LA32
RM4LA32
RM4LA32
RM4LA32safety reliability data | MTTF,
RM4LA32safety reliability data | B10,
RM4LA32 | MTTFd,
RM4LA32 | B10d,
RM4LA32
RM4LG01
RM4LG01standards | EN60255-6, IEC60255-6
RM4LG01product certifications | UL, CSA, GL, C-Tick, GOST
RM4LG01marking | UL, CSA, GL, C-Tick, GOST, CE
RM4LG01directives | No 73/23/EEC + 93/68/EEC
RM4LG01directives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
RM4LG01directives | 2002/95/EC
RM4LG01
RM4LG01 | Not specified ¦ IEC60721-3-3,Climatic category,
RM4LG01 | Germanisher Lloyd,Environmental category,
RM4LG01ambient air temperature for storage | Not specified ¦ ,Storage,
RM4LG01ambient air temperature for operation | Not specified ¦ ,Operation,
RM4LG01relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
RM4LG01 | IEC60947-5-1,Cyclic Damp Heat Test,
RM4LG01vibration resistance | Not specified ¦ IEC60068-2-6
RM4LG01shock resistance | Not specified ¦ IEC60068-2-27
RM4LG01bump resistance | IEC60068-2-29
RM4LG01seismic resistance | IEC60068-3-3
RM4LG01IP degree of protection | Not specified ¦ IEC60529,Terminal Block,
RM4LG01IP degree of protection | Not specified ¦ IEC60529,Housing,
RM4LG01IP degree of protection | IEC60529,Front Panel,
RM4LG01
RM4LG01width | 22.5 x 78 x 80 ¦ ,Width,
RM4LG01height | Height,
RM4LG01depth | Depth,
RM4LG01net weight | 168
RM4LG01mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM4LG01mounting support | - ¦ IEC/EN 60715,With socket,
RM4LG01mounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
RM4LG01Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM4LG01Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM4LG01connections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM4LG01connections - terminals | Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM4LG01connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM4LG01connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4LG01tightening torque | Not specified ¦ IEC60947-1,Tightening torque,
RM4LG01cable stripping length | Not specified ¦ ,Cable stripping length,
RM4LG01duty time | Not specified
RM4LG01
RM4LG01electromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard,
RM4LG01electromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM4LG01electromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM4LG01electromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM4LG01electromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM4LG01electromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM4LG01electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM4LG01electromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM4LG01electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM4LG01electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM4LG01electromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM4LG01electromagnetic compatibility | ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM4LG01electromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM4LG01electromagnetic compatibility | Class B Group1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM4LG01electromagnetic compatibility | Class B Group1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM4LG01electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM4LG01electromagnetic compatibility | Class B Group1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM4LG01electromagnetic compatibility | Class B Group1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM4LG01electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4LG01
RM4LG01pollution degree | Not specified ¦ IEC60664-1
RM4LG01overvoltage category | Not specified ¦ IEC60664-1
RM4LG01circuit group | Supply,Terminal
RM4LG01circuit group | Input 1,
RM4LG01circuit group | Input 2,
RM4LG01circuit group | Input 3,
RM4LG01circuit group | Output 1,
RM4LG01circuit group | Not specified ¦ ,Output 2,
RM4LG01 | Not specified ¦ ,Supply,Rated
RM4LG01 | Not specified ¦ ,Input 1,Voltage
RM4LG01 | Input 2,Spec
RM4LG01 | Input 3,
RM4LG01 | Output 1,
RM4LG01 | Output 2,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Supply,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM4LG01[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Output 1,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM4LG01[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM4LG01[Uimp] rated impulse withstand voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM4LG01dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM4LG01dielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM4LG01dielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM4LG01dielectric strength | IEC60255-27,Supply / Output 1,
RM4LG01dielectric strength | IEC60255-27,Supply / Output 2,
RM4LG01dielectric strength | IEC60255-27,Output 1 / Output 2,
RM4LG01dielectric strength | IEC60255-27,Input 1 / Output 1,
RM4LG01dielectric strength | IEC60255-27,Input 1 / Output 2,
RM4LG01dielectric strength | IEC60255-27,Input 2 / Output 1,
RM4LG01dielectric strength | IEC60255-27,Input 2 / Output 2,
RM4LG01dielectric strength | IEC60255-27,Input 3 / Output 1,
RM4LG01dielectric strength | IEC60255-27,Input 3 / Output 2,
RM4LG01dielectric strength | IEC60255-27,Input 1 / Input 2,
RM4LG01dielectric strength | IEC60255-27,Input 2 / Input 3,
RM4LG01dielectric strength | IEC60255-27,Input 1 / Input 3,
RM4LG01insulation resistance | IEC60255-27,Supply / Input 1,
RM4LG01insulation resistance | IEC60255-27,Supply / Input 2,
RM4LG01insulation resistance | IEC60255-27,Supply / Input 3,
RM4LG01insulation resistance | IEC60255-27,Supply / Output 1,
RM4LG01insulation resistance | IEC60255-27,Supply / Output 2,
RM4LG01insulation resistance | IEC60255-27,Output 1 / Output 2,
RM4LG01insulation resistance | IEC60255-27,Input 1 / Output 1,
RM4LG01insulation resistance | IEC60255-27,Input 1 / Output 2,
RM4LG01insulation resistance | IEC60255-27,Input 2 / Output 1,
RM4LG01insulation resistance | IEC60255-27,Input 2 / Output 2,
RM4LG01insulation resistance | IEC60255-27,Input 3 / Output 1,
RM4LG01insulation resistance | IEC60255-27,Input 3 / Output 2,
RM4LG01insulation resistance | IEC60255-27,Input 1 / Input 2,
RM4LG01insulation resistance | IEC60255-27,Input 2 / Input 3,
RM4LG01insulation resistance | IEC60255-27,Input 1 / Input 3,
RM4LG01
RM4LG01[Us] rated supply voltage | RM4LA32B: ~ 24 RM4LA32F: ~110…130 RM4LA32M: ~220…240 RM4LA32Q: ~380…415
RM4LG01supply voltage limits | Not specified
RM4LG01polarity
RM4LG01supply frequency | 50 / 60
RM4LG01supply frequency | Not specified
RM4LG01power consumption | RM4LG01B: 1.9VA RM4LG01F: 2.6VA RM4LG01M: 2.4VA RM4LG01Q: 2.9VA
RM4LG01immunity to microbreaks | Not specified
RM4LG01supply terminal | A1-A2
RM4LG01on-load factor
RM4LG01release of input voltage
RM4LG01
RM4LG01monitoring functions | 1 level - Fill operation,
RM4LG01monitoring functions | 1 level - Empty operation,
RM4LG01monitoring functions | 2 level - Fill operation,
RM4LG01monitoring functions | 2 level - Empty operation,
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01 | Measurement mode,
RM4LG01internal input resistance | Internal input resistance,
RM4LG01input terminal | Input terminal,
RM4LG01Maximum probe supplied voltage | 24 ¦ ,Maximum probe supplied voltage,
RM4LG01Maximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
RM4LG01Maximum length of probes cable | 1000 ¦ ,Maximum length of probes cable,
RM4LG01input frequency | Maximum cable capacitance,
RM4LG01setting accuracy of the switching threshold | Not specified ¦ ,Setting accuracy,
RM4LG01repeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM4LG01measurement method | Liquid level probe ¦ ,Measurement method,
RM4LG01switching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation,
RM4LG01switching threshold drift | Not specified ¦ ,Measurement error with temperature variation,
RM4LG01maximum measuring cycle | Maximum measuring cycles,
RM4LG01measurement range | 1 level - Fill operation,
RM4LG01measurement range | 1 level - Empty operation,
RM4LG01measurement range | 2 level - Fill operation,
RM4LG01measurement range | 2 level - Empty operation,
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01tripping threshold | 1 level - Fill operation,
RM4LG01tripping threshold | 1 level - Empty operation,
RM4LG01tripping threshold | 2 level - Fill operation,
RM4LG01tripping threshold | 2 level - Empty operation,
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01hysteresis | 1 level - Fill operation,
RM4LG01hysteresis | 1 level - Empty operation,
RM4LG01hysteresis | 2 level - Fill operation,
RM4LG01hysteresis | 2 level - Empty operation,
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01
RM4LG01output type | 1 x C/O relay contacts
RM4LG01output terminal | 15-16-18
RM4LG01output logic | Not specified ¦ ,R1 (11-12-14),
RM4LG01output logic | R2 (21-22-24),
RM4LG01contacts material | Not specified
RM4LG01mechanical durability | Not specified ¦ IEC61810-1
RM4LG01electrical durability | Not specified ¦ IEC60947-4-1,AC-1,
RM4LG01electrical durability | IEC60947-4-1,DC-1,
RM4LG01electrical durability | IEC60947-5-1,AC-15,
RM4LG01electrical durability | IEC60947-5-1,DC-13,
RM4LG01[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4LG01[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4LG01maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM4LG01maximum switching capacity | 8 ¦ ,Maximum switching current,
RM4LG01maximum switching capacity | 2000VA ¦ ,Maximum switching capacity,
RM4LG01minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching voltage,
RM4LG01minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching current,
RM4LG01minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching capacity,
RM4LG01maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM4LG01maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM4LG01thermal current | 8 ¦ IEC60947-5-1
RM4LG01short circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM4LG01short circuit protection | IEC62314,Solid State Output by external fuse,
RM4LG01
RM4LG01time delay type | - ¦ ,"OFF" delay,
RM4LG01time delay type | - ¦ ,"ON" delay,
RM4LG01time delay type | - ¦ ,Inhibition,
RM4LG01time delay range | - ¦ ,"OFF" delay,
RM4LG01time delay range | - ¦ ,"ON" delay,
RM4LG01time delay range | - ¦ ,Inhibition,
RM4LG01response time | Not specified ¦ ,on crossing the threshold,
RM4LG01response time
RM4LG01response time
RM4LG01response time
RM4LG01response time
RM4LG01power on delay | Not specified
RM4LG01reset time | Not specified ¦ ,through Un power reset,
RM4LG01reset time | through front panel reset,
RM4LG01reset time | through input control reset,
RM4LG01setting accuracy of time delay | Not specified
RM4LG01repeat accuracy of time delay | Not specified
RM4LG01time delay drift | Not specified
RM4LG01time delay drift | Not specified
RM4LG01
RM4LG01status LED
RM4LG01local signalling | Power supply availability,
RM4LG01local signalling | Power supply not availability,
RM4LG01local signalling | Timing in-progress,
RM4LG01local signalling | Output is energized,
RM4LG01local signalling | Output is de-energized,
RM4LG01local signalling | Range Setting Changes,
RM4LG01local signalling
RM4LG01local signalling
RM4LG01local signalling
RM4LG01local signalling
RM4LG01local signalling
RM4LG01local signalling
RM4LG01local signalling
RM4LG01local signalling
RM4LG01local signalling
RM4LG01
RM4LG01
RM4LG01
RM4LG01diagnostic button
RM4LG01
RM4LG01
RM4LG01
RM4LG01safety reliability data | MTTF,
RM4LG01safety reliability data | B10,
RM4LG01 | MTTFd,
RM4LG01 | B10d,
RM4LG01
RM22 (Catch Up)
RM22 (Catch Up)standards | EN60255-6, IEC60255-6
RM22 (Catch Up)product certifications | UL, CSA, GL, C-Tick, GOST
RM22 (Catch Up)marking | UL, CSA, GL, C-Tick, GOST, CE
RM22 (Catch Up)directives | No 73/23/EEC + 93/68/EEC
RM22 (Catch Up)directives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
RM22 (Catch Up)directives | 2002/95/EC
RM22 (Catch Up)
RM22 (Catch Up) | Not specified ¦ IEC60721-3-3,Climatic category,
RM22 (Catch Up) | Germanisher Lloyd,Environmental category,
RM22 (Catch Up)ambient air temperature for storage | -40…+70 ¦ ,Storage,
RM22 (Catch Up)ambient air temperature for operation | -20…+50 ¦ ,Operation,
RM22 (Catch Up)relative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM22 (Catch Up) | IEC60947-5-1,Cyclic Damp Heat Test,
RM22 (Catch Up)vibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM22 (Catch Up)shock resistance | 5 gn ¦ IEC60068-2-27
RM22 (Catch Up)bump resistance | IEC60068-2-29
RM22 (Catch Up)seismic resistance | IEC60068-3-3
RM22 (Catch Up)IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22 (Catch Up)IP degree of protection | IP30 ¦ IEC60529,Housing,
RM22 (Catch Up)IP degree of protection | IEC60529,Front Panel,
RM22 (Catch Up)
RM22 (Catch Up)width | 22.5 x ? x ? ¦ ,Width,
RM22 (Catch Up)height | Height,
RM22 (Catch Up)depth | Depth,
RM22 (Catch Up)net weight | ?
RM22 (Catch Up)mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22 (Catch Up)mounting support | - ¦ IEC/EN 60715,With socket,
RM22 (Catch Up)mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22 (Catch Up)Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22 (Catch Up)Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22 (Catch Up)connections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22 (Catch Up)connections - terminals | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22 (Catch Up)connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22 (Catch Up)connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22 (Catch Up)tightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM22 (Catch Up)cable stripping length | Not specified ¦ ,Cable stripping length,
RM22 (Catch Up)duty time | Not specified
RM22 (Catch Up)
RM22 (Catch Up)electromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard,
RM22 (Catch Up)electromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22 (Catch Up)electromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22 (Catch Up)electromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM22 (Catch Up)electromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM22 (Catch Up)electromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22 (Catch Up)electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM22 (Catch Up)electromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22 (Catch Up)electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM22 (Catch Up)electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM22 (Catch Up)electromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM22 (Catch Up)electromagnetic compatibility | · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22 (Catch Up)electromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM22 (Catch Up)electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22 (Catch Up)electromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22 (Catch Up)electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22 (Catch Up)electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22 (Catch Up)electromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22 (Catch Up)electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22 (Catch Up)
RM22 (Catch Up)pollution degree | 3 ¦ IEC60664-1
RM22 (Catch Up)overvoltage category | III ¦ IEC60664-1
RM22 (Catch Up)circuit group | Supply,Terminal
RM22 (Catch Up)circuit group | Input 1,
RM22 (Catch Up)circuit group | Input 2,
RM22 (Catch Up)circuit group | Input 3,
RM22 (Catch Up)circuit group | Output 1,
RM22 (Catch Up)circuit group | 600 ¦ ,Output 2,
RM22 (Catch Up) | 600 ¦ ,Supply,Rated
RM22 (Catch Up) | 600 ¦ ,Input 1,Voltage
RM22 (Catch Up) | Input 2,Spec
RM22 (Catch Up) | Input 3,
RM22 (Catch Up) | Output 1,
RM22 (Catch Up) | Output 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM22 (Catch Up)[Ui] rated insulation voltage | 4 ¦ IEC60664-1,Output 1,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM22 (Catch Up)[Ui] rated insulation voltage | 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM22 (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM22 (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM22 (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM22 (Catch Up)dielectric strength | IEC60255-27,Supply / Output 1,
RM22 (Catch Up)dielectric strength | IEC60255-27,Supply / Output 2,
RM22 (Catch Up)dielectric strength | IEC60255-27,Output 1 / Output 2,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 1 / Output 1,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 1 / Output 2,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 2 / Output 1,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 2 / Output 2,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 3 / Output 1,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 3 / Output 2,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 1 / Input 2,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 2 / Input 3,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 1 / Input 3,
RM22 (Catch Up)insulation resistance | IEC60255-27,Supply / Input 1,
RM22 (Catch Up)insulation resistance | IEC60255-27,Supply / Input 2,
RM22 (Catch Up)insulation resistance | IEC60255-27,Supply / Input 3,
RM22 (Catch Up)insulation resistance | IEC60255-27,Supply / Output 1,
RM22 (Catch Up)insulation resistance | IEC60255-27,Supply / Output 2,
RM22 (Catch Up)insulation resistance | IEC60255-27,Output 1 / Output 2,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 1 / Output 1,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 1 / Output 2,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 2 / Output 1,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 2 / Output 2,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 3 / Output 1,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 3 / Output 2,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 1 / Input 2,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 2 / Input 3,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 1 / Input 3,
RM22 (Catch Up)
RM22 (Catch Up)[Us] rated supply voltage | ~/-- 24…240
RM22 (Catch Up)supply voltage limits | ~/-- 20.4…264
RM22 (Catch Up)polarity
RM22 (Catch Up)supply frequency | 50 / 60
RM22 (Catch Up)supply frequency | 45…66
RM22 (Catch Up)power consumption | ~ 5VA, -- 1.5W
RM22 (Catch Up)immunity to microbreaks | 90 (AC), 100 (DC)
RM22 (Catch Up)supply terminal | A1-A2
RM22 (Catch Up)on-load factor
RM22 (Catch Up)release of input voltage
RM22 (Catch Up)
RM22 (Catch Up)monitoring functions | 1 level - Fill operation,
RM22 (Catch Up)monitoring functions | 1 level - Empty operation,
RM22 (Catch Up)monitoring functions | 2 level - Fill operation,
RM22 (Catch Up)monitoring functions | 2 level - Empty operation,
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up) | Measurement mode,
RM22 (Catch Up)internal input resistance | Internal input resistance,
RM22 (Catch Up)input terminal | Input terminal,
RM22 (Catch Up)Maximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage,
RM22 (Catch Up)Maximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
RM22 (Catch Up)Maximum length of probes cable | 100 ¦ ,Maximum length of probes cable,
RM22 (Catch Up)input frequency | Maximum cable capacitance,
RM22 (Catch Up)setting accuracy of the switching threshold | +/- 10% of full scale value, +/- 20% for HS range ¦ ,Setting accuracy,
RM22 (Catch Up)repeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM22 (Catch Up)measurement method | Liquid level probe ¦ ,Measurement method,
RM22 (Catch Up)switching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation,
RM22 (Catch Up)switching threshold drift | 0.5% / oC ¦ ,Measurement error with temperature variation,
RM22 (Catch Up)maximum measuring cycle | Maximum measuring cycles,
RM22 (Catch Up)measurement range | 1 level - Fill operation,
RM22 (Catch Up)measurement range | 1 level - Empty operation,
RM22 (Catch Up)measurement range | 2 level - Fill operation,
RM22 (Catch Up)measurement range | 2 level - Empty operation,
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)tripping threshold | 1 level - Fill operation,
RM22 (Catch Up)tripping threshold | 1 level - Empty operation,
RM22 (Catch Up)tripping threshold | 2 level - Fill operation,
RM22 (Catch Up)tripping threshold | 2 level - Empty operation,
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)hysteresis | 1 level - Fill operation,
RM22 (Catch Up)hysteresis | 1 level - Empty operation,
RM22 (Catch Up)hysteresis | 2 level - Fill operation,
RM22 (Catch Up)hysteresis | 2 level - Empty operation,
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)output type | 1 x C/O relay contacts
RM22 (Catch Up)output terminal | 11-12-14
RM22 (Catch Up)output logic | Not specified ¦ ,R1 (11-12-14),
RM22 (Catch Up)output logic | R2 (21-22-24),
RM22 (Catch Up)contacts material | Cadmium free
RM22 (Catch Up)mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM22 (Catch Up)electrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1,
RM22 (Catch Up)electrical durability | IEC60947-4-1,DC-1,
RM22 (Catch Up)electrical durability | IEC60947-5-1,AC-15,
RM22 (Catch Up)electrical durability | IEC60947-5-1,DC-13,
RM22 (Catch Up)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM22 (Catch Up)[Ie] rated operational current | IEC61810-1,Rated switching current,
RM22 (Catch Up)maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM22 (Catch Up)maximum switching capacity | ~ 8 ¦ ,Maximum switching current,
RM22 (Catch Up)maximum switching capacity | 2000 ¦ ,Maximum switching capacity,
RM22 (Catch Up)minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
RM22 (Catch Up)minimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM22 (Catch Up)minimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM22 (Catch Up)maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22 (Catch Up)maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22 (Catch Up)thermal current | 8 ¦ IEC60947-5-1
RM22 (Catch Up)short circuit protection | 8 ¦ IEC60947-5-1,Relay Output by external fuse,
RM22 (Catch Up)short circuit protection | IEC62314,Solid State Output by external fuse,
RM22 (Catch Up)
RM22 (Catch Up)time delay type | - ¦ ,"OFF" delay,
RM22 (Catch Up)time delay type | - ¦ ,"ON" delay,
RM22 (Catch Up)time delay type | - ¦ ,Inhibition,
RM22 (Catch Up)time delay range | - ¦ ,"OFF" delay,
RM22 (Catch Up)time delay range | - ¦ ,"ON" delay,
RM22 (Catch Up)time delay range | - ¦ ,Inhibition,
RM22 (Catch Up)response time | Not specified ¦ ,on crossing the threshold,
RM22 (Catch Up)response time
RM22 (Catch Up)response time
RM22 (Catch Up)response time
RM22 (Catch Up)response time
RM22 (Catch Up)power on delay | 0
RM22 (Catch Up)reset time | 0
RM22 (Catch Up)reset time | through front panel reset,
RM22 (Catch Up)reset time | through input control reset,
RM22 (Catch Up)setting accuracy of time delay | +/- 10% of full scales
RM22 (Catch Up)repeat accuracy of time delay | +/- 2%
RM22 (Catch Up)time delay drift | Not specified
RM22 (Catch Up)time delay drift | Not specified
RM22 (Catch Up)
RM22 (Catch Up)status LED
RM22 (Catch Up)local signalling | Power supply availability,
RM22 (Catch Up)local signalling | Power supply not availability,
RM22 (Catch Up)local signalling | Timing in-progress,
RM22 (Catch Up)local signalling | Output is energized,
RM22 (Catch Up)local signalling | Output is de-energized,
RM22 (Catch Up)local signalling | Range Setting Changes,
RM22 (Catch Up)local signalling
RM22 (Catch Up)local signalling
RM22 (Catch Up)local signalling
RM22 (Catch Up)local signalling
RM22 (Catch Up)local signalling
RM22 (Catch Up)local signalling
RM22 (Catch Up)local signalling
RM22 (Catch Up)local signalling
RM22 (Catch Up)local signalling
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)diagnostic button
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)safety reliability data | MTTF,
RM22 (Catch Up)safety reliability data | B10,
RM22 (Catch Up) | MTTFd,
RM22 (Catch Up) | B10d,
RM22 (Catch Up)
8487020x
8487020xstandards | Not specified
8487020xproduct certifications | cULus, CE, CSA
8487020xmarking | cULus, CE, CSA
8487020xdirectives | Not specified
8487020xdirectives | Not specified
8487020xdirectives | Not specified
8487020x
8487020x | Not specified ¦ IEC60721-3-3,Climatic category,
8487020x | Germanisher Lloyd,Environmental category,
8487020xambient air temperature for storage | -40…+70 ¦ ,Storage,
8487020xambient air temperature for operation | -20…+50 ¦ ,Operation,
8487020xrelative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
8487020x | IEC60947-5-1,Cyclic Damp Heat Test,
8487020xvibration resistance | Not specified ¦ IEC60068-2-6
8487020xshock resistance | Not specified ¦ IEC60068-2-27
8487020xbump resistance | IEC60068-2-29
8487020xseismic resistance | IEC60068-3-3
8487020xIP degree of protection | Not specified ¦ IEC60529,Terminal Block,
8487020xIP degree of protection | Not specified ¦ IEC60529,Housing,
8487020xIP degree of protection | IEC60529,Front Panel,
8487020x
8487020xwidth | 22.5 x 78.5 x 100 ¦ ,Width,
8487020xheight | Height,
8487020xdepth | Depth,
8487020xnet weight | 150
8487020xmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
8487020xmounting support | - ¦ IEC/EN 60715,With socket,
8487020xmounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
8487020xMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
8487020xMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
8487020xconnections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal),
8487020xconnections - terminals | Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
8487020xconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
8487020xconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
8487020xtightening torque | Not specified ¦ IEC60947-1,Tightening torque,
8487020xcable stripping length | Not specified ¦ ,Cable stripping length,
8487020xduty time | Not specified
8487020x
8487020xelectromagnetic compatibility | Not specified ¦ ,Generic immunity standard,
8487020xelectromagnetic compatibility | Not specified ¦ IEC61000-4-2,Electrostatic discharge,
8487020xelectromagnetic compatibility | Not specified ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
8487020xelectromagnetic compatibility | Not specified ¦ IEC61000-4-4,Fast transient / burst,
8487020xelectromagnetic compatibility | Not specified ¦ IEC61000-4-5,Surge,
8487020xelectromagnetic compatibility | Not specified ¦ IEC61000-4-6,Conducted RF disturbance,
8487020xelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
8487020xelectromagnetic compatibility | Not specified ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
8487020xelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
8487020xelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
8487020xelectromagnetic compatibility | Not specified ¦ IEC61000-4-13,Low frequency harmonics,
8487020xelectromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
8487020xelectromagnetic compatibility | Not specified ¦ ,Generic emission standard,
8487020xelectromagnetic compatibility | Not specified ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
8487020xelectromagnetic compatibility | Not specified ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
8487020xelectromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Radiated emission from enclosure port,
8487020xelectromagnetic compatibility | Not specified ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
8487020xelectromagnetic compatibility | Not specified ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
8487020xelectromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Conducted emission,
8487020x
8487020xpollution degree | Not specified ¦ IEC60664-1
8487020xovervoltage category | Not specified ¦ IEC60664-1
8487020xcircuit group | Supply,Terminal
8487020xcircuit group | Input 1,
8487020xcircuit group | Input 2,
8487020xcircuit group | Input 3,
8487020xcircuit group | Output 1,
8487020xcircuit group | Not specified ¦ ,Output 2,
8487020x | Not specified ¦ ,Supply,Rated
8487020x | Not specified ¦ ,Input 1,Voltage
8487020x | Input 2,Spec
8487020x | Input 3,
8487020x | Output 1,
8487020x | Output 2,
8487020x[Ui] rated insulation voltage | IEC60664-1,Supply,
8487020x[Ui] rated insulation voltage | IEC60664-1,Input 1,
8487020x[Ui] rated insulation voltage | IEC60664-1,Input 2,
8487020x[Ui] rated insulation voltage | IEC60664-1,Input 3,
8487020x[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Output 1,
8487020x[Ui] rated insulation voltage | IEC60664-1,Output 2,
8487020x[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
8487020x[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
8487020x[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
8487020x[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
8487020x[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
8487020x[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
8487020x[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
8487020x[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
8487020x[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
8487020x[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
8487020x[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
8487020x[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
8487020x[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
8487020x[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
8487020x[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
8487020x[Uimp] rated impulse withstand voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
8487020xdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
8487020xdielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
8487020xdielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
8487020xdielectric strength | IEC60255-27,Supply / Output 1,
8487020xdielectric strength | IEC60255-27,Supply / Output 2,
8487020xdielectric strength | IEC60255-27,Output 1 / Output 2,
8487020xdielectric strength | IEC60255-27,Input 1 / Output 1,
8487020xdielectric strength | IEC60255-27,Input 1 / Output 2,
8487020xdielectric strength | IEC60255-27,Input 2 / Output 1,
8487020xdielectric strength | IEC60255-27,Input 2 / Output 2,
8487020xdielectric strength | IEC60255-27,Input 3 / Output 1,
8487020xdielectric strength | IEC60255-27,Input 3 / Output 2,
8487020xdielectric strength | IEC60255-27,Input 1 / Input 2,
8487020xdielectric strength | IEC60255-27,Input 2 / Input 3,
8487020xdielectric strength | IEC60255-27,Input 1 / Input 3,
8487020xinsulation resistance | IEC60255-27,Supply / Input 1,
8487020xinsulation resistance | IEC60255-27,Supply / Input 2,
8487020xinsulation resistance | IEC60255-27,Supply / Input 3,
8487020xinsulation resistance | IEC60255-27,Supply / Output 1,
8487020xinsulation resistance | IEC60255-27,Supply / Output 2,
8487020xinsulation resistance | IEC60255-27,Output 1 / Output 2,
8487020xinsulation resistance | IEC60255-27,Input 1 / Output 1,
8487020xinsulation resistance | IEC60255-27,Input 1 / Output 2,
8487020xinsulation resistance | IEC60255-27,Input 2 / Output 1,
8487020xinsulation resistance | IEC60255-27,Input 2 / Output 2,
8487020xinsulation resistance | IEC60255-27,Input 3 / Output 1,
8487020xinsulation resistance | IEC60255-27,Input 3 / Output 2,
8487020xinsulation resistance | IEC60255-27,Input 1 / Input 2,
8487020xinsulation resistance | IEC60255-27,Input 2 / Input 3,
8487020xinsulation resistance | IEC60255-27,Input 1 / Input 3,
8487020x
8487020x[Us] rated supply voltage | 84870201: ~ 24 84870203: ~120 84870204: ~230
8487020xsupply voltage limits | Not specified
8487020xpolarity
8487020xsupply frequency | 50 / 60
8487020xsupply frequency | Not specified
8487020xpower consumption | 3VA
8487020ximmunity to microbreaks | Not specified
8487020xsupply terminal | A1-A2
8487020xon-load factor
8487020xrelease of input voltage
8487020x
8487020xmonitoring functions | 1 level - Fill operation,
8487020xmonitoring functions | 1 level - Empty operation,
8487020xmonitoring functions | 2 level - Fill operation,
8487020xmonitoring functions | 2 level - Empty operation,
8487020x
8487020x
8487020x
8487020x
8487020x
8487020x
8487020x
8487020x | Measurement mode,
8487020xinternal input resistance | Internal input resistance,
8487020xinput terminal | Input terminal,
8487020xMaximum probe supplied voltage | 24 ¦ ,Maximum probe supplied voltage,
8487020xMaximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
8487020xMaximum length of probes cable | Not specified ¦ ,Maximum length of probes cable,
8487020xinput frequency | 10 ¦ ,Maximum cable capacitance,
8487020xsetting accuracy of the switching threshold | +/- 30% at max sensitivity ¦ ,Setting accuracy,
8487020xrepeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
8487020xmeasurement method | Liquid level probe ¦ ,Measurement method,
8487020xswitching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation,
8487020xswitching threshold drift | Not specified ¦ ,Measurement error with temperature variation,
8487020xmaximum measuring cycle | Maximum measuring cycles,
8487020xmeasurement range | 1 level - Fill operation,
8487020xmeasurement range | 1 level - Empty operation,
8487020xmeasurement range | 2 level - Fill operation,
8487020xmeasurement range | 2 level - Empty operation,
8487020x
8487020x
8487020x
8487020x
8487020x
8487020x
8487020x
8487020xtripping threshold | 1 level - Fill operation,
8487020xtripping threshold | 1 level - Empty operation,
8487020xtripping threshold | 2 level - Fill operation,
8487020xtripping threshold | 2 level - Empty operation,
8487020x
8487020x
8487020x
8487020x
8487020x
8487020x
8487020x
8487020xhysteresis | 1 level - Fill operation,
8487020xhysteresis | 1 level - Empty operation,
8487020xhysteresis | 2 level - Fill operation,
8487020xhysteresis | 2 level - Empty operation,
8487020x
8487020x
8487020x
8487020x
8487020x
8487020x
8487020x
8487020x
8487020xoutput type | 1 x C/O relay contacts
8487020xoutput terminal | 11-12-14
8487020xoutput logic | Not specified ¦ ,R1 (11-12-14),
8487020xoutput logic | R2 (21-22-24),
8487020xcontacts material | Cadmium free
8487020xmechanical durability | Not specified ¦ IEC61810-1
8487020xelectrical durability | Not specified ¦ IEC60947-4-1,AC-1,
8487020xelectrical durability | IEC60947-4-1,DC-1,
8487020xelectrical durability | IEC60947-5-1,AC-15,
8487020xelectrical durability | IEC60947-5-1,DC-13,
8487020x[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
8487020x[Ie] rated operational current | IEC61810-1,Rated switching current,
8487020xmaximum switching capacity | Not specified ¦ ,Maximum switching voltage,
8487020xmaximum switching capacity | Not specified ¦ ,Maximum switching current,
8487020xmaximum switching capacity | Not specified ¦ ,Maximum switching capacity,
8487020xminimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching voltage,
8487020xminimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching current,
8487020xminimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching capacity,
8487020xmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
8487020xmaximum leakage current | - ¦ IEC62314,Only for solid state output,
8487020xthermal current | IEC60947-5-1
8487020xshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
8487020xshort circuit protection | IEC62314,Solid State Output by external fuse,
8487020x
8487020xtime delay type | - ¦ ,"OFF" delay,
8487020xtime delay type | - ¦ ,"ON" delay,
8487020xtime delay type | - ¦ ,Inhibition,
8487020xtime delay range | - ¦ ,"OFF" delay,
8487020xtime delay range | - ¦ ,"ON" delay,
8487020xtime delay range | - ¦ ,Inhibition,
8487020xresponse time | 300 high level; 500 low level ¦ ,on crossing the threshold,
8487020xresponse time
8487020xresponse time
8487020xresponse time
8487020xresponse time
8487020xpower on delay | Not specified
8487020xreset time | Not specified ¦ ,through Un power reset,
8487020xreset time | through front panel reset,
8487020xreset time | through input control reset,
8487020xsetting accuracy of time delay | Not specified
8487020xrepeat accuracy of time delay | Not specified
8487020xtime delay drift | Not specified
8487020xtime delay drift | Not specified
8487020x
8487020xstatus LED
8487020xlocal signalling | Power supply availability,
8487020xlocal signalling | Power supply not availability,
8487020xlocal signalling | Timing in-progress,
8487020xlocal signalling | Output is energized,
8487020xlocal signalling | Output is de-energized,
8487020xlocal signalling | Range Setting Changes,
8487020xlocal signalling
8487020xlocal signalling
8487020xlocal signalling
8487020xlocal signalling
8487020xlocal signalling
8487020xlocal signalling
8487020xlocal signalling
8487020xlocal signalling
8487020xlocal signalling
8487020x
8487020x
8487020x
8487020xdiagnostic button
8487020x
8487020x
8487020x
8487020xsafety reliability data | MTTF,
8487020xsafety reliability data | B10,
8487020x | MTTFd,
8487020x | B10d,
8487020x
RM22 (Catch Up)
RM22 (Catch Up)standards | EN60255-6, IEC60255-6
RM22 (Catch Up)product certifications | UL, CSA, GL, C-Tick, GOST
RM22 (Catch Up)marking | UL, CSA, GL, C-Tick, GOST, CE
RM22 (Catch Up)directives | No 73/23/EEC + 93/68/EEC
RM22 (Catch Up)directives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
RM22 (Catch Up)directives | 2002/95/EC
RM22 (Catch Up)
RM22 (Catch Up) | Not specified ¦ IEC60721-3-3,Climatic category,
RM22 (Catch Up) | Germanisher Lloyd,Environmental category,
RM22 (Catch Up)ambient air temperature for storage | -40…+70 ¦ ,Storage,
RM22 (Catch Up)ambient air temperature for operation | -20…+50 ¦ ,Operation,
RM22 (Catch Up)relative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM22 (Catch Up) | IEC60947-5-1,Cyclic Damp Heat Test,
RM22 (Catch Up)vibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM22 (Catch Up)shock resistance | 5 gn ¦ IEC60068-2-27
RM22 (Catch Up)bump resistance | IEC60068-2-29
RM22 (Catch Up)seismic resistance | IEC60068-3-3
RM22 (Catch Up)IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22 (Catch Up)IP degree of protection | IP30 ¦ IEC60529,Housing,
RM22 (Catch Up)IP degree of protection | IEC60529,Front Panel,
RM22 (Catch Up)
RM22 (Catch Up)width | 22.5 x ? x ? ¦ ,Width,
RM22 (Catch Up)height | Height,
RM22 (Catch Up)depth | Depth,
RM22 (Catch Up)net weight | ?
RM22 (Catch Up)mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22 (Catch Up)mounting support | - ¦ IEC/EN 60715,With socket,
RM22 (Catch Up)mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22 (Catch Up)Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22 (Catch Up)Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22 (Catch Up)connections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22 (Catch Up)connections - terminals | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22 (Catch Up)connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22 (Catch Up)connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22 (Catch Up)tightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM22 (Catch Up)cable stripping length | Not specified ¦ ,Cable stripping length,
RM22 (Catch Up)duty time | Not specified
RM22 (Catch Up)
RM22 (Catch Up)electromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard,
RM22 (Catch Up)electromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22 (Catch Up)electromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22 (Catch Up)electromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM22 (Catch Up)electromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM22 (Catch Up)electromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22 (Catch Up)electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM22 (Catch Up)electromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22 (Catch Up)electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM22 (Catch Up)electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM22 (Catch Up)electromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM22 (Catch Up)electromagnetic compatibility | · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22 (Catch Up)electromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM22 (Catch Up)electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22 (Catch Up)electromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22 (Catch Up)electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22 (Catch Up)electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22 (Catch Up)electromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22 (Catch Up)electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22 (Catch Up)
RM22 (Catch Up)pollution degree | 3 ¦ IEC60664-1
RM22 (Catch Up)overvoltage category | III ¦ IEC60664-1
RM22 (Catch Up)circuit group | Supply,Terminal
RM22 (Catch Up)circuit group | Input 1,
RM22 (Catch Up)circuit group | Input 2,
RM22 (Catch Up)circuit group | Input 3,
RM22 (Catch Up)circuit group | Output 1,
RM22 (Catch Up)circuit group | 600 ¦ ,Output 2,
RM22 (Catch Up) | 600 ¦ ,Supply,Rated
RM22 (Catch Up) | 600 ¦ ,Input 1,Voltage
RM22 (Catch Up) | Input 2,Spec
RM22 (Catch Up) | Input 3,
RM22 (Catch Up) | Output 1,
RM22 (Catch Up) | Output 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM22 (Catch Up)[Ui] rated insulation voltage | 4 ¦ IEC60664-1,Output 1,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM22 (Catch Up)[Ui] rated insulation voltage | 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM22 (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM22 (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM22 (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM22 (Catch Up)dielectric strength | IEC60255-27,Supply / Output 1,
RM22 (Catch Up)dielectric strength | IEC60255-27,Supply / Output 2,
RM22 (Catch Up)dielectric strength | IEC60255-27,Output 1 / Output 2,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 1 / Output 1,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 1 / Output 2,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 2 / Output 1,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 2 / Output 2,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 3 / Output 1,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 3 / Output 2,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 1 / Input 2,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 2 / Input 3,
RM22 (Catch Up)dielectric strength | IEC60255-27,Input 1 / Input 3,
RM22 (Catch Up)insulation resistance | IEC60255-27,Supply / Input 1,
RM22 (Catch Up)insulation resistance | IEC60255-27,Supply / Input 2,
RM22 (Catch Up)insulation resistance | IEC60255-27,Supply / Input 3,
RM22 (Catch Up)insulation resistance | IEC60255-27,Supply / Output 1,
RM22 (Catch Up)insulation resistance | IEC60255-27,Supply / Output 2,
RM22 (Catch Up)insulation resistance | IEC60255-27,Output 1 / Output 2,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 1 / Output 1,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 1 / Output 2,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 2 / Output 1,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 2 / Output 2,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 3 / Output 1,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 3 / Output 2,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 1 / Input 2,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 2 / Input 3,
RM22 (Catch Up)insulation resistance | IEC60255-27,Input 1 / Input 3,
RM22 (Catch Up)
RM22 (Catch Up)[Us] rated supply voltage | ~/-- 24…240
RM22 (Catch Up)supply voltage limits | ~/-- 20.4…264
RM22 (Catch Up)polarity
RM22 (Catch Up)supply frequency | 50 / 60
RM22 (Catch Up)supply frequency | 45…66
RM22 (Catch Up)power consumption | ~ 5VA, -- 1.5W
RM22 (Catch Up)immunity to microbreaks | 90 (AC), 100 (DC)
RM22 (Catch Up)supply terminal | A1-A2
RM22 (Catch Up)on-load factor
RM22 (Catch Up)release of input voltage
RM22 (Catch Up)
RM22 (Catch Up)monitoring functions | 1 level - Fill operation,
RM22 (Catch Up)monitoring functions | 1 level - Empty operation,
RM22 (Catch Up)monitoring functions | 2 level - Fill operation,
RM22 (Catch Up)monitoring functions | 2 level - Empty operation,
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up) | Measurement mode,
RM22 (Catch Up)internal input resistance | Internal input resistance,
RM22 (Catch Up)input terminal | Input terminal,
RM22 (Catch Up)Maximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage,
RM22 (Catch Up)Maximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
RM22 (Catch Up)Maximum length of probes cable | 100 ¦ ,Maximum length of probes cable,
RM22 (Catch Up)input frequency | Maximum cable capacitance,
RM22 (Catch Up)setting accuracy of the switching threshold | +/- 10% of full scale value, +/- 20% for HS range ¦ ,Setting accuracy,
RM22 (Catch Up)repeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM22 (Catch Up)measurement method | Liquid level probe ¦ ,Measurement method,
RM22 (Catch Up)switching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation,
RM22 (Catch Up)switching threshold drift | 0.5% / oC ¦ ,Measurement error with temperature variation,
RM22 (Catch Up)maximum measuring cycle | Maximum measuring cycles,
RM22 (Catch Up)measurement range | 1 level - Fill operation,
RM22 (Catch Up)measurement range | 1 level - Empty operation,
RM22 (Catch Up)measurement range | 2 level - Fill operation,
RM22 (Catch Up)measurement range | 2 level - Empty operation,
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)tripping threshold | 1 level - Fill operation,
RM22 (Catch Up)tripping threshold | 1 level - Empty operation,
RM22 (Catch Up)tripping threshold | 2 level - Fill operation,
RM22 (Catch Up)tripping threshold | 2 level - Empty operation,
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)hysteresis | 1 level - Fill operation,
RM22 (Catch Up)hysteresis | 1 level - Empty operation,
RM22 (Catch Up)hysteresis | 2 level - Fill operation,
RM22 (Catch Up)hysteresis | 2 level - Empty operation,
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)output type | 2 x C/O relay contacts
RM22 (Catch Up)output terminal | 11-12-14, 21-22-24
RM22 (Catch Up)output logic | Not specified ¦ ,R1 (11-12-14),
RM22 (Catch Up)output logic | R2 (21-22-24),
RM22 (Catch Up)contacts material | Cadmium free
RM22 (Catch Up)mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM22 (Catch Up)electrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1,
RM22 (Catch Up)electrical durability | IEC60947-4-1,DC-1,
RM22 (Catch Up)electrical durability | IEC60947-5-1,AC-15,
RM22 (Catch Up)electrical durability | IEC60947-5-1,DC-13,
RM22 (Catch Up)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM22 (Catch Up)[Ie] rated operational current | IEC61810-1,Rated switching current,
RM22 (Catch Up)maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM22 (Catch Up)maximum switching capacity | ~ 5 ¦ ,Maximum switching current,
RM22 (Catch Up)maximum switching capacity | 1250 ¦ ,Maximum switching capacity,
RM22 (Catch Up)minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
RM22 (Catch Up)minimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM22 (Catch Up)minimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM22 (Catch Up)maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22 (Catch Up)maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22 (Catch Up)thermal current | IEC60947-5-1
RM22 (Catch Up)short circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM22 (Catch Up)short circuit protection | IEC62314,Solid State Output by external fuse,
RM22 (Catch Up)
RM22 (Catch Up)time delay type | · ¦ ,"OFF" delay,
RM22 (Catch Up)time delay type | · ¦ ,"ON" delay,
RM22 (Catch Up)time delay type | - ¦ ,Inhibition,
RM22 (Catch Up)time delay range | Adjustable 0.1…5 ¦ ,"OFF" delay,
RM22 (Catch Up)time delay range | Adjustable 0.1…5 ¦ ,"ON" delay,
RM22 (Catch Up)time delay range | - ¦ ,Inhibition,
RM22 (Catch Up)response time | Not specified ¦ ,on crossing the threshold,
RM22 (Catch Up)response time
RM22 (Catch Up)response time
RM22 (Catch Up)response time
RM22 (Catch Up)response time
RM22 (Catch Up)power on delay | 0
RM22 (Catch Up)reset time | 0
RM22 (Catch Up)reset time | through front panel reset,
RM22 (Catch Up)reset time | through input control reset,
RM22 (Catch Up)setting accuracy of time delay | +/- 10% of full scales
RM22 (Catch Up)repeat accuracy of time delay | +/- 2%
RM22 (Catch Up)time delay drift | Not specified
RM22 (Catch Up)time delay drift | Not specified
RM22 (Catch Up)
RM22 (Catch Up)status LED
RM22 (Catch Up)local signalling | Power supply availability,
RM22 (Catch Up)local signalling | Power supply not availability,
RM22 (Catch Up)local signalling | Timing in-progress,
RM22 (Catch Up)local signalling | Output is energized,
RM22 (Catch Up)local signalling | Output is de-energized,
RM22 (Catch Up)local signalling | Range Setting Changes,
RM22 (Catch Up)local signalling
RM22 (Catch Up)local signalling
RM22 (Catch Up)local signalling
RM22 (Catch Up)local signalling
RM22 (Catch Up)local signalling
RM22 (Catch Up)local signalling
RM22 (Catch Up)local signalling
RM22 (Catch Up)local signalling
RM22 (Catch Up)local signalling
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)diagnostic button
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)
RM22 (Catch Up)safety reliability data | MTTF,
RM22 (Catch Up)safety reliability data | B10,
RM22 (Catch Up) | MTTFd,
RM22 (Catch Up) | B10d,
RM22 (Catch Up)
8487021x
8487021xstandards | Not specified
8487021xproduct certifications | cULus, CE, CSA
8487021xmarking | cULus, CE, CSA
8487021xdirectives | Not specified
8487021xdirectives | Not specified
8487021xdirectives | Not specified
8487021x
8487021x | Not specified ¦ IEC60721-3-3,Climatic category,
8487021x | Germanisher Lloyd,Environmental category,
8487021xambient air temperature for storage | -40…+70 ¦ ,Storage,
8487021xambient air temperature for operation | -20…+50 ¦ ,Operation,
8487021xrelative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
8487021x | IEC60947-5-1,Cyclic Damp Heat Test,
8487021xvibration resistance | Not specified ¦ IEC60068-2-6
8487021xshock resistance | Not specified ¦ IEC60068-2-27
8487021xbump resistance | IEC60068-2-29
8487021xseismic resistance | IEC60068-3-3
8487021xIP degree of protection | Not specified ¦ IEC60529,Terminal Block,
8487021xIP degree of protection | Not specified ¦ IEC60529,Housing,
8487021xIP degree of protection | IEC60529,Front Panel,
8487021x
8487021xwidth | 22.5 x 78.5 x 100 ¦ ,Width,
8487021xheight | Height,
8487021xdepth | Depth,
8487021xnet weight | 150
8487021xmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
8487021xmounting support | - ¦ IEC/EN 60715,With socket,
8487021xmounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
8487021xMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
8487021xMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
8487021xconnections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal),
8487021xconnections - terminals | Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
8487021xconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
8487021xconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
8487021xtightening torque | Not specified ¦ IEC60947-1,Tightening torque,
8487021xcable stripping length | Not specified ¦ ,Cable stripping length,
8487021xduty time | Not specified
8487021x
8487021xelectromagnetic compatibility | Not specified ¦ ,Generic immunity standard,
8487021xelectromagnetic compatibility | Not specified ¦ IEC61000-4-2,Electrostatic discharge,
8487021xelectromagnetic compatibility | Not specified ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
8487021xelectromagnetic compatibility | Not specified ¦ IEC61000-4-4,Fast transient / burst,
8487021xelectromagnetic compatibility | Not specified ¦ IEC61000-4-5,Surge,
8487021xelectromagnetic compatibility | Not specified ¦ IEC61000-4-6,Conducted RF disturbance,
8487021xelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
8487021xelectromagnetic compatibility | Not specified ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
8487021xelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
8487021xelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
8487021xelectromagnetic compatibility | Not specified ¦ IEC61000-4-13,Low frequency harmonics,
8487021xelectromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
8487021xelectromagnetic compatibility | Not specified ¦ ,Generic emission standard,
8487021xelectromagnetic compatibility | Not specified ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
8487021xelectromagnetic compatibility | Not specified ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
8487021xelectromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Radiated emission from enclosure port,
8487021xelectromagnetic compatibility | Not specified ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
8487021xelectromagnetic compatibility | Not specified ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
8487021xelectromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Conducted emission,
8487021x
8487021xpollution degree | Not specified ¦ IEC60664-1
8487021xovervoltage category | Not specified ¦ IEC60664-1
8487021xcircuit group | Supply,Terminal
8487021xcircuit group | Input 1,
8487021xcircuit group | Input 2,
8487021xcircuit group | Input 3,
8487021xcircuit group | Output 1,
8487021xcircuit group | Not specified ¦ ,Output 2,
8487021x | Not specified ¦ ,Supply,Rated
8487021x | Not specified ¦ ,Input 1,Voltage
8487021x | Input 2,Spec
8487021x | Input 3,
8487021x | Output 1,
8487021x | Output 2,
8487021x[Ui] rated insulation voltage | IEC60664-1,Supply,
8487021x[Ui] rated insulation voltage | IEC60664-1,Input 1,
8487021x[Ui] rated insulation voltage | IEC60664-1,Input 2,
8487021x[Ui] rated insulation voltage | IEC60664-1,Input 3,
8487021x[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Output 1,
8487021x[Ui] rated insulation voltage | IEC60664-1,Output 2,
8487021x[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
8487021x[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
8487021x[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
8487021x[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
8487021x[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
8487021x[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
8487021x[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
8487021x[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
8487021x[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
8487021x[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
8487021x[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
8487021x[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
8487021x[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
8487021x[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
8487021x[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
8487021x[Uimp] rated impulse withstand voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
8487021xdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
8487021xdielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
8487021xdielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
8487021xdielectric strength | IEC60255-27,Supply / Output 1,
8487021xdielectric strength | IEC60255-27,Supply / Output 2,
8487021xdielectric strength | IEC60255-27,Output 1 / Output 2,
8487021xdielectric strength | IEC60255-27,Input 1 / Output 1,
8487021xdielectric strength | IEC60255-27,Input 1 / Output 2,
8487021xdielectric strength | IEC60255-27,Input 2 / Output 1,
8487021xdielectric strength | IEC60255-27,Input 2 / Output 2,
8487021xdielectric strength | IEC60255-27,Input 3 / Output 1,
8487021xdielectric strength | IEC60255-27,Input 3 / Output 2,
8487021xdielectric strength | IEC60255-27,Input 1 / Input 2,
8487021xdielectric strength | IEC60255-27,Input 2 / Input 3,
8487021xdielectric strength | IEC60255-27,Input 1 / Input 3,
8487021xinsulation resistance | IEC60255-27,Supply / Input 1,
8487021xinsulation resistance | IEC60255-27,Supply / Input 2,
8487021xinsulation resistance | IEC60255-27,Supply / Input 3,
8487021xinsulation resistance | IEC60255-27,Supply / Output 1,
8487021xinsulation resistance | IEC60255-27,Supply / Output 2,
8487021xinsulation resistance | IEC60255-27,Output 1 / Output 2,
8487021xinsulation resistance | IEC60255-27,Input 1 / Output 1,
8487021xinsulation resistance | IEC60255-27,Input 1 / Output 2,
8487021xinsulation resistance | IEC60255-27,Input 2 / Output 1,
8487021xinsulation resistance | IEC60255-27,Input 2 / Output 2,
8487021xinsulation resistance | IEC60255-27,Input 3 / Output 1,
8487021xinsulation resistance | IEC60255-27,Input 3 / Output 2,
8487021xinsulation resistance | IEC60255-27,Input 1 / Input 2,
8487021xinsulation resistance | IEC60255-27,Input 2 / Input 3,
8487021xinsulation resistance | IEC60255-27,Input 1 / Input 3,
8487021x
8487021x[Us] rated supply voltage | 84870211: ~ 24 84870213: ~120 84870214: ~230
8487021xsupply voltage limits | Not specified
8487021xpolarity
8487021xsupply frequency | 50 / 60
8487021xsupply frequency | Not specified
8487021xpower consumption | 3VA
8487021ximmunity to microbreaks | Not specified
8487021xsupply terminal | A1-A2
8487021xon-load factor
8487021xrelease of input voltage
8487021x
8487021xmonitoring functions | 1 level - Fill operation,
8487021xmonitoring functions | 1 level - Empty operation,
8487021xmonitoring functions | 2 level - Fill operation,
8487021xmonitoring functions | 2 level - Empty operation,
8487021x
8487021x
8487021x
8487021x
8487021x
8487021x
8487021x
8487021x | Measurement mode,
8487021xinternal input resistance | Internal input resistance,
8487021xinput terminal | Input terminal,
8487021xMaximum probe supplied voltage | 24 ¦ ,Maximum probe supplied voltage,
8487021xMaximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
8487021xMaximum length of probes cable | Not specified ¦ ,Maximum length of probes cable,
8487021xinput frequency | 10 ¦ ,Maximum cable capacitance,
8487021xsetting accuracy of the switching threshold | +/- 30% at max sensitivity ¦ ,Setting accuracy,
8487021xrepeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
8487021xmeasurement method | Liquid level probe ¦ ,Measurement method,
8487021xswitching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation,
8487021xswitching threshold drift | Not specified ¦ ,Measurement error with temperature variation,
8487021xmaximum measuring cycle | Maximum measuring cycles,
8487021xmeasurement range | 1 level - Fill operation,
8487021xmeasurement range | 1 level - Empty operation,
8487021xmeasurement range | 2 level - Fill operation,
8487021xmeasurement range | 2 level - Empty operation,
8487021x
8487021x
8487021x
8487021x
8487021x
8487021x
8487021x
8487021xtripping threshold | 1 level - Fill operation,
8487021xtripping threshold | 1 level - Empty operation,
8487021xtripping threshold | 2 level - Fill operation,
8487021xtripping threshold | 2 level - Empty operation,
8487021x
8487021x
8487021x
8487021x
8487021x
8487021x
8487021x
8487021xhysteresis | 1 level - Fill operation,
8487021xhysteresis | 1 level - Empty operation,
8487021xhysteresis | 2 level - Fill operation,
8487021xhysteresis | 2 level - Empty operation,
8487021x
8487021x
8487021x
8487021x
8487021x
8487021x
8487021x
8487021x
8487021xoutput type | 1 x C/O relay contacts
8487021xoutput terminal | 11-12-14
8487021xoutput logic | Not specified ¦ ,R1 (11-12-14),
8487021xoutput logic | R2 (21-22-24),
8487021xcontacts material | Cadmium free
8487021xmechanical durability | Not specified ¦ IEC61810-1
8487021xelectrical durability | Not specified ¦ IEC60947-4-1,AC-1,
8487021xelectrical durability | IEC60947-4-1,DC-1,
8487021xelectrical durability | IEC60947-5-1,AC-15,
8487021xelectrical durability | IEC60947-5-1,DC-13,
8487021x[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
8487021x[Ie] rated operational current | IEC61810-1,Rated switching current,
8487021xmaximum switching capacity | Not specified ¦ ,Maximum switching voltage,
8487021xmaximum switching capacity | Not specified ¦ ,Maximum switching current,
8487021xmaximum switching capacity | Not specified ¦ ,Maximum switching capacity,
8487021xminimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching voltage,
8487021xminimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching current,
8487021xminimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching capacity,
8487021xmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
8487021xmaximum leakage current | - ¦ IEC62314,Only for solid state output,
8487021xthermal current | IEC60947-5-1
8487021xshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
8487021xshort circuit protection | IEC62314,Solid State Output by external fuse,
8487021x
8487021xtime delay type | · ¦ ,"OFF" delay,
8487021xtime delay type | · ¦ ,"ON" delay,
8487021xtime delay type | - ¦ ,Inhibition,
8487021xtime delay range | Adjustable 0.1…5 ¦ ,"OFF" delay,
8487021xtime delay range | Adjustable 0.1…5 ¦ ,"ON" delay,
8487021xtime delay range | - ¦ ,Inhibition,
8487021xresponse time | 300 high level; 500 low level ¦ ,on crossing the threshold,
8487021xresponse time
8487021xresponse time
8487021xresponse time
8487021xresponse time
8487021xpower on delay | Not specified
8487021xreset time | Not specified ¦ ,through Un power reset,
8487021xreset time | through front panel reset,
8487021xreset time | through input control reset,
8487021xsetting accuracy of time delay | Not specified
8487021xrepeat accuracy of time delay | Not specified
8487021xtime delay drift | Not specified
8487021xtime delay drift | Not specified
8487021x
8487021xstatus LED
8487021xlocal signalling | Power supply availability,
8487021xlocal signalling | Power supply not availability,
8487021xlocal signalling | Timing in-progress,
8487021xlocal signalling | Output is energized,
8487021xlocal signalling | Output is de-energized,
8487021xlocal signalling | Range Setting Changes,
8487021xlocal signalling
8487021xlocal signalling
8487021xlocal signalling
8487021xlocal signalling
8487021xlocal signalling
8487021xlocal signalling
8487021xlocal signalling
8487021xlocal signalling
8487021xlocal signalling
8487021x
8487021x
8487021x
8487021xdiagnostic button
8487021x
8487021x
8487021x
8487021xsafety reliability data | MTTF,
8487021xsafety reliability data | B10,
8487021x | MTTFd,
8487021x | B10d,
8487021x
RM35HZ21FM
RM35HZ21FMstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM35HZ21FMproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35HZ21FMmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35HZ21FMdirectives | 2014/35/EU
RM35HZ21FMdirectives | 2014/30/EU
RM35HZ21FMdirectives | 2011/65/EU
RM35HZ21FM
RM35HZ21FM | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM35HZ21FM | Class C ¦ Germanisher Lloyd,Environmental category,
RM35HZ21FMambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM35HZ21FMambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM35HZ21FMrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM35HZ21FM | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM35HZ21FMvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM35HZ21FMshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM35HZ21FMbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM35HZ21FMseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM35HZ21FMIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM35HZ21FMIP degree of protection | IP30 ¦ IEC60529,Housing,
RM35HZ21FMIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM35HZ21FM
RM35HZ21FMwidth | 35 ¦ ,Width,
RM35HZ21FMheight | 90 ¦ ,Height,
RM35HZ21FMdepth | 72 ¦ ,Depth,
RM35HZ21FMnet weight | 95
RM35HZ21FMmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM35HZ21FMmounting support | - ¦ IEC/EN 60715,With socket,
RM35HZ21FMmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35HZ21FMMinimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM35HZ21FMMinimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM35HZ21FMconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35HZ21FMconnections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35HZ21FMconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM35HZ21FMconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35HZ21FMtightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM35HZ21FMcable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM35HZ21FMduty time | 1
RM35HZ21FM
RM35HZ21FMelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM35HZ21FMelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM35HZ21FMelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM35HZ21FMelectromagnetic compatibility | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM35HZ21FMelectromagnetic compatibility | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge,
RM35HZ21FMelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM35HZ21FMelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM35HZ21FMelectromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35HZ21FMelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM35HZ21FMelectromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM35HZ21FMelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM35HZ21FMelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35HZ21FMelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM35HZ21FMelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35HZ21FMelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35HZ21FMelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM35HZ21FMelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35HZ21FMelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35HZ21FMelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35HZ21FM
RM35HZ21FMpollution degree | 3 ¦ IEC60664-1
RM35HZ21FMovervoltage category | 3 ¦ IEC60664-1
RM35HZ21FMcircuit group | A1, A2 ¦ ,Supply,Terminal
RM35HZ21FMcircuit group | - ¦ ,Input 1,
RM35HZ21FMcircuit group | - ¦ ,Input 2,
RM35HZ21FMcircuit group | - ¦ ,Input 3,
RM35HZ21FMcircuit group | 11,12,14 ¦ ,Output 1,
RM35HZ21FMcircuit group | 21,22,24 ¦ ,Output 2,
RM35HZ21FM | 120…277 AC/DC ¦ ,Supply,Rated
RM35HZ21FM | - ¦ ,Input 1,Voltage
RM35HZ21FM | - ¦ ,Input 2,Spec
RM35HZ21FM | - ¦ ,Input 3,
RM35HZ21FM | 250V ¦ ,Output 1,
RM35HZ21FM | 250V ¦ ,Output 2,
RM35HZ21FM[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply,
RM35HZ21FM[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM35HZ21FM[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM35HZ21FM[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM35HZ21FM[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM35HZ21FM[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM35HZ21FM[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35HZ21FM[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM35HZ21FM[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM35HZ21FM[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 1,
RM35HZ21FM[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 2,
RM35HZ21FM[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM35HZ21FM[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM35HZ21FM[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM35HZ21FM[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM35HZ21FM[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM35HZ21FM[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM35HZ21FM[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM35HZ21FM[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM35HZ21FM[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM35HZ21FM[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM35HZ21FM[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM35HZ21FM[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM35HZ21FM[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM35HZ21FM[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM35HZ21FM[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM35HZ21FMdielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM35HZ21FMdielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM35HZ21FMdielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM35HZ21FMdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM35HZ21FMdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM35HZ21FMdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM35HZ21FMdielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM35HZ21FMdielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM35HZ21FMdielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM35HZ21FMdielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM35HZ21FMdielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM35HZ21FMdielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM35HZ21FMdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM35HZ21FMdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM35HZ21FMdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM35HZ21FMinsulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM35HZ21FMinsulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM35HZ21FMinsulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM35HZ21FMinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM35HZ21FMinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM35HZ21FMinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM35HZ21FMinsulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM35HZ21FMinsulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM35HZ21FMinsulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM35HZ21FMinsulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM35HZ21FMinsulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM35HZ21FMinsulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM35HZ21FMinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM35HZ21FMinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM35HZ21FMinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM35HZ21FM
RM35HZ21FM[Us] rated supply voltage | ~ 120…277
RM35HZ21FMsupply voltage limits | ~ 102…308
RM35HZ21FMpolarity | -
RM35HZ21FMsupply frequency | 50 / 60
RM35HZ21FMsupply frequency | 45…66
RM35HZ21FMpower consumption | 6
RM35HZ21FMimmunity to microbreaks | 10
RM35HZ21FMsupply terminal | A1-A2
RM35HZ21FMon-load factor | 1
RM35HZ21FMrelease of input voltage | -
RM35HZ21FM
RM35HZ21FMmonitoring functions | - governed by time delay - status reflects to R1 - fault status will be memorized and only resetable through power cycle ¦ ,Over frequency @ 50Hz, With Memory,
RM35HZ21FMmonitoring functions | - governed by time delay - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis ¦ ,Over frequency @ 50Hz, Without Memory,
RM35HZ21FMmonitoring functions | - governed by time delay - status reflects to R1 - fault status will be memorized and only resetable through power cycle ¦ ,Over frequency @ 60Hz, With Memory,
RM35HZ21FMmonitoring functions | - governed by time delay - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis ¦ ,Over frequency @ 60Hz, Without Memory,
RM35HZ21FMmonitoring functions | - governed by time delay - status reflects to R2 - fault status will be memorized and only resetable through power cycle ¦ ,Under frequency @ 50Hz, With Memory,
RM35HZ21FMmonitoring functions | - governed by time delay - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis ¦ ,Under frequency @ 50Hz, Without Memory,
RM35HZ21FMmonitoring functions | - governed by time delay - status reflects to R2 - fault status will be memorized and only resetable through power cycle ¦ ,Under frequency @ 60Hz, With Memory,
RM35HZ21FMmonitoring functions | - governed by time delay - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis ¦ ,Under frequency @ 60Hz, Without Memory,
RM35HZ21FM
RM35HZ21FM
RM35HZ21FM
RM35HZ21FM | Resistive Voltage Step Down ¦ ,Measurement mode,
RM35HZ21FMinternal input resistance | - ¦ ,Internal input resistance,
RM35HZ21FMinput terminal | A1-A2 ¦ ,Input terminal,
RM35HZ21FMInput nominal frequency selection | 50, 60 ¦ ,Input nominal frequency selection,
RM35HZ21FMpermissible input overload | 70 ¦ ,permissible input overload,
RM35HZ21FMinput frequency | 50 / 60 ¦ ,Rated frequency,
RM35HZ21FMinput frequency | 40…70 ¦ ,Frequency operating range,
RM35HZ21FMsetting accuracy of the switching threshold | ± 10 % of the full scale value ¦ ,Setting accuracy,
RM35HZ21FMrepeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM35HZ21FMmeasurement method | - ¦ ,Measurement method,
RM35HZ21FMswitching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation,
RM35HZ21FMswitching threshold drift | < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM35HZ21FMmaximum measuring cycle | 200ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM35HZ21FMmeasurement range | 40...70 ¦ ,Over frequency @ 50Hz, With Memory,
RM35HZ21FMmeasurement range | same as above ¦ ,Over frequency @ 50Hz, Without Memory,
RM35HZ21FMmeasurement range | same as above ¦ ,Over frequency @ 60Hz, With Memory,
RM35HZ21FMmeasurement range | same as above ¦ ,Over frequency @ 60Hz, Without Memory,
RM35HZ21FMmeasurement range | same as above ¦ ,Under frequency @ 50Hz, With Memory,
RM35HZ21FMmeasurement range | same as above ¦ ,Under frequency @ 50Hz, Without Memory,
RM35HZ21FMmeasurement range | same as above ¦ ,Under frequency @ 60Hz, With Memory,
RM35HZ21FMmeasurement range | same as above ¦ ,Under frequency @ 60Hz, Without Memory,
RM35HZ21FM
RM35HZ21FM
RM35HZ21FM
RM35HZ21FMtripping threshold | Adjustable -1 Hz…5 Hz for x1 scale Adjustable -2 Hz…10 Hz for x2 scale ¦ ,Over frequency @ 50Hz, With Memory,
RM35HZ21FMtripping threshold | same as above ¦ ,Over frequency @ 50Hz, Without Memory,
RM35HZ21FMtripping threshold | same as above ¦ ,Over frequency @ 60Hz, With Memory,
RM35HZ21FMtripping threshold | same as above ¦ ,Over frequency @ 60Hz, Without Memory,
RM35HZ21FMtripping threshold | Adjustable -5 Hz…1 Hz for x1 scale Adjustable -10 Hz…2 Hz for x2 scale ¦ ,Under frequency @ 50Hz, With Memory,
RM35HZ21FMtripping threshold | same as above ¦ ,Under frequency @ 50Hz, Without Memory,
RM35HZ21FMtripping threshold | same as above ¦ ,Under frequency @ 60Hz, With Memory,
RM35HZ21FMtripping threshold | same as above ¦ ,Under frequency @ 60Hz, Without Memory,
RM35HZ21FM
RM35HZ21FM
RM35HZ21FM
RM35HZ21FMhysteresis | Fixed +/- 0.3Hz Internal design spec: Fixed +/- 0.2Hz ¦ ,Over frequency @ 50Hz, With Memory,
RM35HZ21FMhysteresis | same as above ¦ ,Over frequency @ 50Hz, Without Memory,
RM35HZ21FMhysteresis | same as above ¦ ,Over frequency @ 60Hz, With Memory,
RM35HZ21FMhysteresis | same as above ¦ ,Over frequency @ 60Hz, Without Memory,
RM35HZ21FMhysteresis | same as above ¦ ,Under frequency @ 50Hz, With Memory,
RM35HZ21FMhysteresis | same as above ¦ ,Under frequency @ 50Hz, Without Memory,
RM35HZ21FMhysteresis | same as above ¦ ,Under frequency @ 60Hz, With Memory,
RM35HZ21FMhysteresis | same as above ¦ ,Under frequency @ 60Hz, Without Memory,
RM35HZ21FM
RM35HZ21FM
RM35HZ21FM
RM35HZ21FM
RM35HZ21FMoutput type | 2 x C/O relay contacts
RM35HZ21FMoutput terminal | 15-16-18, 25-26-28
RM35HZ21FMoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM35HZ21FMoutput logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM35HZ21FMcontacts material | Cadmium free
RM35HZ21FMmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM35HZ21FMelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM35HZ21FMelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM35HZ21FMelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM35HZ21FMelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM35HZ21FM[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM35HZ21FM[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM35HZ21FMmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM35HZ21FMmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM35HZ21FMmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM35HZ21FMminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM35HZ21FMminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM35HZ21FMminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM35HZ21FMmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35HZ21FMmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35HZ21FMthermal current | 8A ¦ IEC60947-5-1
RM35HZ21FMshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM35HZ21FMshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM35HZ21FM
RM35HZ21FMtime delay type | Yes ¦ ,"OFF" delay,
RM35HZ21FMtime delay type | - ¦ ,"ON" delay,
RM35HZ21FMtime delay type | - ¦ ,Inhibition,
RM35HZ21FMtime delay range | Adjustable 0.1…10 ¦ ,"OFF" delay,
RM35HZ21FMtime delay range | - ¦ ,"ON" delay,
RM35HZ21FMtime delay range | - ¦ ,Inhibition,
RM35HZ21FMresponse time | TBD ¦ ,on crossing the threshold (all monitoring functions),
RM35HZ21FMresponse time | - ¦ ,on crossing the hysteresis (all monitoring functions),
RM35HZ21FMresponse time | - ¦ ,on crossing the threshold (specific monitoring functions 1),
RM35HZ21FMresponse time | - ¦ ,on crossing the threshold (specific monitoring functions 2),
RM35HZ21FMresponse time | - ¦ ,on crossing the threshold (specific monitoring functions 3),
RM35HZ21FMpower on delay | 0
RM35HZ21FMreset time | 0
RM35HZ21FMreset time | - ¦ ,through front panel reset,
RM35HZ21FMreset time | - ¦ ,through input control reset,
RM35HZ21FMsetting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM35HZ21FMrepeat accuracy of time delay | +/- 0.5%
RM35HZ21FMtime delay drift | -
RM35HZ21FMtime delay drift | -
RM35HZ21FM
RM35HZ21FMstatus LED | Un (Green) R1 (Amber) R2 (Amber)
RM35HZ21FMlocal signalling | Un - ON ¦ ,Power supply availability,
RM35HZ21FMlocal signalling | Un - OFF ¦ ,Power supply not availability,
RM35HZ21FMlocal signalling | Rx - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM35HZ21FMlocal signalling | Rx - ON ¦ ,Output is energized,
RM35HZ21FMlocal signalling | Rx - OFF ¦ ,Output is de-energized,
RM35HZ21FMlocal signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM35HZ21FMlocal signalling
RM35HZ21FMlocal signalling
RM35HZ21FMlocal signalling
RM35HZ21FMlocal signalling
RM35HZ21FMlocal signalling
RM35HZ21FMlocal signalling
RM35HZ21FMlocal signalling
RM35HZ21FMlocal signalling
RM35HZ21FMlocal signalling
RM35HZ21FM
RM35HZ21FM | -
RM35HZ21FM | -
RM35HZ21FMdiagnostic button | -
RM35HZ21FM | -
RM35HZ21FM | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM35HZ21FM
RM35HZ21FMsafety reliability data | TBD ¦ ,MTTF,
RM35HZ21FMsafety reliability data | TBD ¦ ,B10,
RM35HZ21FM | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM35HZ21FM | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM35HZ21FM
RM35TM250MW
RM35TM250MWstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM35TM250MWproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35TM250MWmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35TM250MWdirectives | 2014/35/EU
RM35TM250MWdirectives | 2014/30/EU
RM35TM250MWdirectives | 2011/65/EU
RM35TM250MW
RM35TM250MW | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM35TM250MW | Class C ¦ Germanisher Lloyd,Environmental category,
RM35TM250MWambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM35TM250MWambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM35TM250MWrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM35TM250MW | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM35TM250MWvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM35TM250MWshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM35TM250MWbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM35TM250MWseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM35TM250MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM35TM250MWIP degree of protection | IP30 ¦ IEC60529,Housing,
RM35TM250MWIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM35TM250MW
RM35TM250MWwidth | 35 ¦ ,Width,
RM35TM250MWheight | 90 ¦ ,Height,
RM35TM250MWdepth | 72 ¦ ,Depth,
RM35TM250MWnet weight | 95
RM35TM250MWmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM35TM250MWmounting support | - ¦ IEC/EN 60715,With socket,
RM35TM250MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35TM250MWMinimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM35TM250MWMinimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM35TM250MWconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35TM250MWconnections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35TM250MWconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM35TM250MWconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35TM250MWtightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM35TM250MWcable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM35TM250MWduty time | 1
RM35TM250MW
RM35TM250MWelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM35TM250MWelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM35TM250MWelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM35TM250MWelectromagnetic compatibility | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM35TM250MWelectromagnetic compatibility | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge,
RM35TM250MWelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM35TM250MWelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM35TM250MWelectromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35TM250MWelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM35TM250MWelectromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM35TM250MWelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM35TM250MWelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35TM250MWelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM35TM250MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35TM250MWelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35TM250MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM35TM250MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35TM250MWelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35TM250MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35TM250MW
RM35TM250MWpollution degree | 3 ¦ IEC60664-1
RM35TM250MWovervoltage category | 3 ¦ IEC60664-1
RM35TM250MWcircuit group | A1, A2 ¦ ,Supply,Terminal
RM35TM250MWcircuit group | T1, T2 ¦ ,Input 1,
RM35TM250MWcircuit group | Y1 ¦ ,Input 2,
RM35TM250MWcircuit group | L1, L2, L3 ¦ ,Input 3,
RM35TM250MWcircuit group | 11,12,14 ¦ ,Output 1,
RM35TM250MWcircuit group | 21,22,24 ¦ ,Output 2,
RM35TM250MW | 24…240 AC/DC ¦ ,Supply,Rated
RM35TM250MW | PTC probe ¦ ,Input 1,Voltage
RM35TM250MW | Push Button Switch ¦ ,Input 2,Spec
RM35TM250MW | 208..480 AC/DC ¦ ,Input 3,
RM35TM250MW | 250V ¦ ,Output 1,
RM35TM250MW | 250V ¦ ,Output 2,
RM35TM250MW[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply,
RM35TM250MW[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 1,
RM35TM250MW[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 2,
RM35TM250MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 3,
RM35TM250MW[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM35TM250MW[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM35TM250MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35TM250MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Input 2,Isolated
RM35TM250MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Input 3,Circuit
RM35TM250MW[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 1,
RM35TM250MW[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 2,
RM35TM250MW[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM35TM250MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 1 / Output 1,
RM35TM250MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 1 / Output 2,
RM35TM250MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 2 / Output 1,
RM35TM250MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 2 / Output 2,
RM35TM250MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 3 / Output 1,
RM35TM250MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 3 / Output 2,
RM35TM250MW[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM35TM250MW[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM35TM250MW[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM35TM250MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM35TM250MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM35TM250MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM35TM250MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3,
RM35TM250MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM35TM250MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM35TM250MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35TM250MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated
RM35TM250MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit
RM35TM250MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM35TM250MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM35TM250MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM35TM250MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM35TM250MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2,
RM35TM250MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1,
RM35TM250MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2,
RM35TM250MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1,
RM35TM250MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2,
RM35TM250MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM35TM250MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM35TM250MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM35TM250MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM35TM250MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2,
RM35TM250MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3,
RM35TM250MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM35TM250MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM35TM250MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM35TM250MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM35TM250MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2,
RM35TM250MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1,
RM35TM250MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2,
RM35TM250MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1,
RM35TM250MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2,
RM35TM250MWdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM35TM250MWdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM35TM250MWdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM35TM250MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM35TM250MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2,
RM35TM250MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3,
RM35TM250MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM35TM250MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM35TM250MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM35TM250MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM35TM250MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2,
RM35TM250MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1,
RM35TM250MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2,
RM35TM250MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1,
RM35TM250MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2,
RM35TM250MWinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM35TM250MWinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM35TM250MWinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM35TM250MW
RM35TM250MW[Us] rated supply voltage | ~/-- 24…240
RM35TM250MWsupply voltage limits | ~/-- 20.4…264
RM35TM250MWpolarity | No
RM35TM250MWsupply frequency | 50 / 60
RM35TM250MWsupply frequency | 45…66
RM35TM250MWpower consumption | 1 4 VA / 2 0.5 W
RM35TM250MWimmunity to microbreaks | 20 ms at 20.4 V
RM35TM250MWsupply terminal | A1-A2
RM35TM250MWon-load factor | 1
RM35TM250MWrelease of input voltage | -
RM35TM250MW
RM35TM250MWmonitoring functions | - governed by response time only - status reflects to R1 - fault status will be memorized and only resetable through power cycle, Test/Reset button or Y1-T1 volt-free input ¦ ,Motor temperature through PTC sensor, With Memory,
RM35TM250MWmonitoring functions | - governed by response time only - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis ¦ ,Motor temperature through PTC sensor, Without Memory,
RM35TM250MWmonitoring functions | - governed by response time only - status reflects to R1 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis ¦ ,Short circuit of PTC sensor,
RM35TM250MWmonitoring functions | - governed by response time only, - status reflects to R2 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis ¦ ,Phase lost ,
RM35TM250MWmonitoring functions | - governed by response time only, - status reflects to R2 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis ¦ ,Phase sequence,
RM35TM250MWmonitoring functions | - governed by response time only, - status reflects to R2 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis ¦ ,Voltage Regeneration,
RM35TM250MWmonitoring functions | - governed by response time only, - status reflects to R2 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis ¦ ,Extreme undervoltage (Phase loss),
RM35TM250MW
RM35TM250MW
RM35TM250MW
RM35TM250MW
RM35TM250MWinput terminal | T1-T2 ¦ ,Input terminal,Motor temperature
RM35TM250MWMaximum voltage of temperature control circuit | 3.6V when T1-T2 is open ¦ ,Maximum voltage of temperature control circuit,
RM35TM250MWTemperature sensing circuit short-circuit current | 7mA when T1-T2 is short-circuited ¦ ,Temperature sensing circuit short-circuit current,
RM35TM250MWMaximum resistance of temperature sensor at 20°C | 1500Ω ¦ ,Maximum resistance of temperature sensor at 20°C,
RM35TM250MW
RM35TM250MW
RM35TM250MWinput frequency | Resistive Voltage Step Down ¦ ,Measurement mode,3 Phase
RM35TM250MWsetting accuracy of the switching threshold | 602/line ¦ ,Internal input resistance,
RM35TM250MWrepeat accuracy of the switching threshold | L1-L2-L3 ¦ ,Input terminal,
RM35TM250MWmeasurement method | - ¦ ,Input nominal voltage selection,
RM35TM250MWswitching threshold drift | ~ 3 x 176…3 x 528 ¦ ,permissible input overload,
RM35TM250MWswitching threshold drift | 50 / 60 ¦ ,Rated frequency,
RM35TM250MWmaximum measuring cycle | 45…66 ¦ ,Frequency operating range,
RM35TM250MWmeasurement range | Mark A probe characteristics ¦ IEC60034-11,Motor temperature through PTC sensor,
RM35TM250MWmeasurement range | ~ 3 x 208…3 x 480 ¦ ,Short circuit of PTC sensor,
RM35TM250MWmeasurement range | same as above ¦ ,Phase lost ,
RM35TM250MWmeasurement range | same as above ¦ ,Phase sequence,
RM35TM250MWmeasurement range | same as above ¦ ,Voltage Regeneration,
RM35TM250MW
RM35TM250MW
RM35TM250MW
RM35TM250MW
RM35TM250MW
RM35TM250MW
RM35TM250MWtripping threshold | 3100 ± 10 % Internal design spec: TBD ¦ ,Motor temperature through PTC sensor,
RM35TM250MWtripping threshold | 0…15 ± 5 Internal design spec: TBD ¦ ,Short circuit of PTC sensor,
RM35TM250MWtripping threshold | 1 or more phase cut ¦ ,Phase lost ,
RM35TM250MWtripping threshold | Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence,
RM35TM250MWtripping threshold | 1 or more phase =< 30% * [(L21 + L31 + L32) / 3] Internal design spec: TBD ¦ ,Voltage Regeneration,
RM35TM250MWtripping threshold | Internal design spec: TBD ¦ ,Extreme undervoltage (Phase loss),
RM35TM250MW
RM35TM250MW
RM35TM250MW
RM35TM250MW
RM35TM250MW
RM35TM250MWhysteresis | 1650 ± 10 % Internal design spec: TBD ¦ ,Motor temperature through PTC sensor,
RM35TM250MWhysteresis | Internal design spec: TBD ¦ ,Short circuit of PTC sensor,
RM35TM250MWhysteresis | All phase cut recover ¦ ,Phase lost ,
RM35TM250MWhysteresis | Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence,
RM35TM250MWhysteresis | Internal design spec: TBD ¦ ,Voltage Regeneration,
RM35TM250MWhysteresis | Internal design spec: TBD ¦ ,Extreme undervoltage (Phase loss),
RM35TM250MW
RM35TM250MW
RM35TM250MW
RM35TM250MW
RM35TM250MW
RM35TM250MW
RM35TM250MWoutput type | 2 x C/O relay contacts
RM35TM250MWoutput terminal | 15-16-18, 25-26-28
RM35TM250MWoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM35TM250MWoutput logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM35TM250MWcontacts material | Cadmium free
RM35TM250MWmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM35TM250MWelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM35TM250MWelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM35TM250MWelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM35TM250MWelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM35TM250MW[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM35TM250MW[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM35TM250MWmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM35TM250MWmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM35TM250MWmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM35TM250MWminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM35TM250MWminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM35TM250MWminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM35TM250MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35TM250MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35TM250MWthermal current | 8A ¦ IEC60947-5-1
RM35TM250MWshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM35TM250MWshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM35TM250MW
RM35TM250MWtime delay type | - ¦ ,"OFF" delay,
RM35TM250MWtime delay type | - ¦ ,"ON" delay,
RM35TM250MWtime delay type | - ¦ ,Inhibition,
RM35TM250MWtime delay range | - ¦ ,"OFF" delay,
RM35TM250MWtime delay range | - ¦ ,"ON" delay,
RM35TM250MWtime delay range | - ¦ ,Inhibition,
RM35TM250MWresponse time | 300 ¦ ,on crossing the threshold (Motor Temperature),
RM35TM250MWresponse time | 300 ¦ ,on crossing the hysteresis (all 3 Phase functions),
RM35TM250MWresponse time
RM35TM250MWresponse time
RM35TM250MWresponse time
RM35TM250MWpower on delay | 500
RM35TM250MWreset time | 10 000 ¦ ,through Un power reset,
RM35TM250MWreset time | >= 50 (press to release) ¦ ,through front panel reset,
RM35TM250MWreset time | >= 50 (Y1 short to T1) ¦ ,through input control reset,
RM35TM250MWsetting accuracy of time delay | -
RM35TM250MWrepeat accuracy of time delay | -
RM35TM250MWtime delay drift | -
RM35TM250MWtime delay drift | -
RM35TM250MW
RM35TM250MWstatus LED | Un (Green) R1 (Amber) R2 (Amber)
RM35TM250MWlocal signalling | Un - ON ¦ ,Power supply availability,
RM35TM250MWlocal signalling | Un - OFF ¦ ,Power supply not availability,
RM35TM250MWlocal signalling | - ¦ ,Timing in-progress,
RM35TM250MWlocal signalling | Rx - ON ¦ ,Output is energized,
RM35TM250MWlocal signalling | Rx - OFF ¦ ,Output is de-energized,
RM35TM250MWlocal signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM35TM250MWlocal signalling
RM35TM250MWlocal signalling
RM35TM250MWlocal signalling
RM35TM250MWlocal signalling
RM35TM250MWlocal signalling
RM35TM250MWlocal signalling
RM35TM250MWlocal signalling
RM35TM250MWlocal signalling
RM35TM250MWlocal signalling
RM35TM250MW
RM35TM250MW | 1) When Set to "No Memory" 1a) When motor temperature is normal, - pressing the "Test/Reset" button simulates overheating, R1 is de-energized - R1 will remain energized as long as "Test/Reset" button remains pressed 1b) When motor temperature is abnormal, - pressing the "Test/Reset" button will not change any product status 2) When Set to "Memory" 2a) When motor temperature is normal, - pressing the "Test/Reset" button simulates overheating, R1 is de-energized - R1 will remain energized as long as "Test/Reset" button remains pressed 2b) When motor temperature is abnormal, - pressing the "Test/Reset" button will not change any product status 2c) When motor temperature is abnormal at first and recover to normal - pressing the "Test/Reset" button will reset the fault, R1 is energized
RM35TM250MW | 1) Same function as per Test / Reset button 2) Short Y1 to T1 is the same meaning as pressing "Test/Reset" button 3) Open Y1 to T1 is the same meaning as releasing "Test/Reset" button
RM35TM250MWdiagnostic button | -
RM35TM250MW | -
RM35TM250MW | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM35TM250MW
RM35TM250MWsafety reliability data | TBD ¦ ,MTTF,
RM35TM250MWsafety reliability data | TBD ¦ ,B10,
RM35TM250MW | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM35TM250MW | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM35TM250MW
RM35TM50MW
RM35TM50MWstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM35TM50MWproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35TM50MWmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35TM50MWdirectives | 2014/35/EU
RM35TM50MWdirectives | 2014/30/EU
RM35TM50MWdirectives | 2011/65/EU
RM35TM50MW
RM35TM50MW | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category,
RM35TM50MW | Class C ¦ Germanisher Lloyd,Environmental category,
RM35TM50MWambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM35TM50MWambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM35TM50MWrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM35TM50MW | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM35TM50MWvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM35TM50MWshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM35TM50MWbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM35TM50MWseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM35TM50MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM35TM50MWIP degree of protection | IP30 ¦ IEC60529,Housing,
RM35TM50MWIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM35TM50MW
RM35TM50MWwidth | 35 ¦ ,Width,
RM35TM50MWheight | 90 ¦ ,Height,
RM35TM50MWdepth | 72 ¦ ,Depth,
RM35TM50MWnet weight | 95
RM35TM50MWmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM35TM50MWmounting support | - ¦ IEC/EN 60715,With socket,
RM35TM50MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35TM50MWMinimum distance to adjacent devices | 1x product height ¦ ,Horizontal,
RM35TM50MWMinimum distance to adjacent devices | 1x product width ¦ ,Vertical,
RM35TM50MWconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35TM50MWconnections - terminals | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35TM50MWconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM35TM50MWconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35TM50MWtightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM35TM50MWcable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM35TM50MWduty time | 1
RM35TM50MW
RM35TM50MWelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM35TM50MWelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM35TM50MWelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM35TM50MWelectromagnetic compatibility | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM35TM50MWelectromagnetic compatibility | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge,
RM35TM50MWelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM35TM50MWelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM35TM50MWelectromagnetic compatibility | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35TM50MWelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM35TM50MWelectromagnetic compatibility | - ¦ IEC61000-4-29,DC voltage interruption,
RM35TM50MWelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM35TM50MWelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35TM50MWelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM35TM50MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35TM50MWelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35TM50MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM35TM50MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35TM50MWelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35TM50MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35TM50MW
RM35TM50MWpollution degree | 3 ¦ IEC60664-1
RM35TM50MWovervoltage category | 3 ¦ IEC60664-1
RM35TM50MWcircuit group | A1, A2 ¦ ,Supply,Terminal
RM35TM50MWcircuit group | T1, T2 ¦ ,Input 1,
RM35TM50MWcircuit group | - ¦ ,Input 2,
RM35TM50MWcircuit group | L1, L2, L3 ¦ ,Input 3,
RM35TM50MWcircuit group | 11,12,14 ¦ ,Output 1,
RM35TM50MWcircuit group | 21,22,24 ¦ ,Output 2,
RM35TM50MW | 24…240 AC/DC ¦ ,Supply,Rated
RM35TM50MW | PTC probe ¦ ,Input 1,Voltage
RM35TM50MW | Push Button Switch ¦ ,Input 2,Spec
RM35TM50MW | 208..480 AC/DC ¦ ,Input 3,
RM35TM50MW | 250V ¦ ,Output 1,
RM35TM50MW | 250V ¦ ,Output 2,
RM35TM50MW[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply,
RM35TM50MW[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 1,
RM35TM50MW[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM35TM50MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 3,
RM35TM50MW[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM35TM50MW[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM35TM50MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35TM50MW[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM35TM50MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Input 3,Circuit
RM35TM50MW[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 1,
RM35TM50MW[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 2,
RM35TM50MW[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM35TM50MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 1 / Output 1,
RM35TM50MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 1 / Output 2,
RM35TM50MW[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM35TM50MW[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM35TM50MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 3 / Output 1,
RM35TM50MW[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 3 / Output 2,
RM35TM50MW[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM35TM50MW[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM35TM50MW[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM35TM50MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM35TM50MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM35TM50MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM35TM50MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3,
RM35TM50MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM35TM50MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM35TM50MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35TM50MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM35TM50MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit
RM35TM50MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM35TM50MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM35TM50MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM35TM50MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM35TM50MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2,
RM35TM50MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM35TM50MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM35TM50MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1,
RM35TM50MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2,
RM35TM50MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM35TM50MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM35TM50MW[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM35TM50MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM35TM50MWdielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM35TM50MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3,
RM35TM50MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM35TM50MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM35TM50MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM35TM50MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM35TM50MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2,
RM35TM50MWdielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM35TM50MWdielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM35TM50MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1,
RM35TM50MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2,
RM35TM50MWdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM35TM50MWdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM35TM50MWdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM35TM50MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM35TM50MWinsulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM35TM50MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3,
RM35TM50MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM35TM50MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM35TM50MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM35TM50MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM35TM50MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2,
RM35TM50MWinsulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM35TM50MWinsulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM35TM50MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1,
RM35TM50MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2,
RM35TM50MWinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM35TM50MWinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM35TM50MWinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM35TM50MW
RM35TM50MW[Us] rated supply voltage | ~/-- 24…240
RM35TM50MWsupply voltage limits | ~/-- 20.4…264
RM35TM50MWpolarity | No
RM35TM50MWsupply frequency | 50 / 60
RM35TM50MWsupply frequency | 45…66
RM35TM50MWpower consumption | 1 4 VA / 2 0.5 W
RM35TM50MWimmunity to microbreaks | 20 ms at 20.4 V
RM35TM50MWsupply terminal | A1-A2
RM35TM50MWon-load factor | 1
RM35TM50MWrelease of input voltage | -
RM35TM50MW
RM35TM50MWmonitoring functions | - ¦ ,Motor temperature through PTC sensor, With Memory,
RM35TM50MWmonitoring functions | - governed by response time only - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis ¦ ,Motor temperature through PTC sensor, Without Memory,
RM35TM50MWmonitoring functions | - governed by response time only - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis ¦ ,Short circuit of PTC sensor,
RM35TM50MWmonitoring functions | - governed by response time only, - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis ¦ ,Phase lost ,
RM35TM50MWmonitoring functions | - governed by response time only, - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis ¦ ,Phase sequence,
RM35TM50MWmonitoring functions | - governed by response time only, - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis ¦ ,Voltage Regeneration,
RM35TM50MWmonitoring functions | - governed by response time only, - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis ¦ ,Extreme undervoltage (Phase loss),
RM35TM50MW
RM35TM50MW
RM35TM50MW
RM35TM50MW
RM35TM50MWinput terminal | T1-T2 ¦ ,Input terminal,Motor temperature
RM35TM50MWMaximum voltage of temperature control circuit | 3.6V when T1-T2 is open ¦ ,Maximum voltage of temperature control circuit,
RM35TM50MWTemperature sensing circuit short-circuit current | 7mA when T1-T2 is short-circuited ¦ ,Temperature sensing circuit short-circuit current,
RM35TM50MWMaximum resistance of temperature sensor at 20°C | 1500Ω ¦ ,Maximum resistance of temperature sensor at 20°C,
RM35TM50MW
RM35TM50MW
RM35TM50MWinput frequency | Resistive Voltage Step Down ¦ ,Measurement mode,3 Phase
RM35TM50MWsetting accuracy of the switching threshold | 602/line ¦ ,Internal input resistance,
RM35TM50MWrepeat accuracy of the switching threshold | L1-L2-L3 ¦ ,Input terminal,
RM35TM50MWmeasurement method | - ¦ ,Input nominal voltage selection,
RM35TM50MWswitching threshold drift | ~ 3 x 176…3 x 528 ¦ ,permissible input overload,
RM35TM50MWswitching threshold drift | 50 / 60 ¦ ,Rated frequency,
RM35TM50MWmaximum measuring cycle | 45…66 ¦ ,Frequency operating range,
RM35TM50MWmeasurement range | Mark A probe characteristics ¦ IEC60034-11,Motor temperature through PTC sensor,
RM35TM50MWmeasurement range | ~ 3 x 208…3 x 480 ¦ ,Short circuit of PTC sensor,
RM35TM50MWmeasurement range | same as above ¦ ,Phase lost ,
RM35TM50MWmeasurement range | same as above ¦ ,Phase sequence,
RM35TM50MWmeasurement range | same as above ¦ ,Voltage Regeneration,
RM35TM50MW
RM35TM50MW
RM35TM50MW
RM35TM50MW
RM35TM50MW
RM35TM50MW
RM35TM50MWtripping threshold | 3100 ± 10 % Internal design spec: TBD ¦ ,Motor temperature through PTC sensor,
RM35TM50MWtripping threshold | 0…15 ± 5 Internal design spec: TBD ¦ ,Short circuit of PTC sensor,
RM35TM50MWtripping threshold | 1 or more phase cut ¦ ,Phase lost ,
RM35TM50MWtripping threshold | Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence,
RM35TM50MWtripping threshold | 1 or more phase =< 30% * [(L21 + L31 + L32) / 3] Internal design spec: TBD ¦ ,Voltage Regeneration,
RM35TM50MWtripping threshold | Internal design spec: TBD ¦ ,Extreme undervoltage (Phase loss),
RM35TM50MW
RM35TM50MW
RM35TM50MW
RM35TM50MW
RM35TM50MW
RM35TM50MWhysteresis | 1650 ± 10 % Internal design spec: TBD ¦ ,Motor temperature through PTC sensor,
RM35TM50MWhysteresis | Internal design spec: TBD ¦ ,Short circuit of PTC sensor,
RM35TM50MWhysteresis | All phase cut recover ¦ ,Phase lost ,
RM35TM50MWhysteresis | Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence,
RM35TM50MWhysteresis | Internal design spec: TBD ¦ ,Voltage Regeneration,
RM35TM50MWhysteresis | Internal design spec: TBD ¦ ,Extreme undervoltage (Phase loss),
RM35TM50MW
RM35TM50MW
RM35TM50MW
RM35TM50MW
RM35TM50MW
RM35TM50MW
RM35TM50MWoutput type | 2 x C/O relay contacts
RM35TM50MWoutput terminal | 15-16-18, 25-26-28
RM35TM50MWoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM35TM50MWoutput logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM35TM50MWcontacts material | Cadmium free
RM35TM50MWmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM35TM50MWelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM35TM50MWelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM35TM50MWelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM35TM50MWelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM35TM50MW[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM35TM50MW[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM35TM50MWmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM35TM50MWmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM35TM50MWmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM35TM50MWminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM35TM50MWminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM35TM50MWminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM35TM50MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35TM50MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35TM50MWthermal current | 8A ¦ IEC60947-5-1
RM35TM50MWshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM35TM50MWshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM35TM50MW
RM35TM50MWtime delay type | - ¦ ,"OFF" delay,
RM35TM50MWtime delay type | - ¦ ,"ON" delay,
RM35TM50MWtime delay type | - ¦ ,Inhibition,
RM35TM50MWtime delay range | - ¦ ,"OFF" delay,
RM35TM50MWtime delay range | - ¦ ,"ON" delay,
RM35TM50MWtime delay range | - ¦ ,Inhibition,
RM35TM50MWresponse time | 300 ¦ ,on crossing the threshold (Motor Temperature),
RM35TM50MWresponse time | 300 ¦ ,on crossing the hysteresis (all 3 Phase functions),
RM35TM50MWresponse time
RM35TM50MWresponse time
RM35TM50MWresponse time
RM35TM50MWpower on delay | 500
RM35TM50MWreset time | 10 000 ¦ ,through Un power reset,
RM35TM50MWreset time | - ¦ ,through front panel reset,
RM35TM50MWreset time | - ¦ ,through input control reset,
RM35TM50MWsetting accuracy of time delay | -
RM35TM50MWrepeat accuracy of time delay | -
RM35TM50MWtime delay drift | -
RM35TM50MWtime delay drift | -
RM35TM50MW
RM35TM50MWstatus LED | Un (Green) R1 (Amber) R2 (Amber)
RM35TM50MWlocal signalling | Un - ON ¦ ,Power supply availability,
RM35TM50MWlocal signalling | Un - OFF ¦ ,Power supply not availability,
RM35TM50MWlocal signalling | - ¦ ,Timing in-progress,
RM35TM50MWlocal signalling | Rx - ON ¦ ,Output is energized,
RM35TM50MWlocal signalling | Rx - OFF ¦ ,Output is de-energized,
RM35TM50MWlocal signalling | - ¦ ,Range Setting Changes,
RM35TM50MWlocal signalling
RM35TM50MWlocal signalling
RM35TM50MWlocal signalling
RM35TM50MWlocal signalling
RM35TM50MWlocal signalling
RM35TM50MWlocal signalling
RM35TM50MWlocal signalling
RM35TM50MWlocal signalling
RM35TM50MWlocal signalling
RM35TM50MW
RM35TM50MW | -
RM35TM50MW | -
RM35TM50MWdiagnostic button | -
RM35TM50MW | -
RM35TM50MW | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM35TM50MW
RM35TM50MWsafety reliability data | TBD ¦ ,MTTF,
RM35TM50MWsafety reliability data | TBD ¦ ,B10,
RM35TM50MW | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM35TM50MW | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM35TM50MW
RM22UA21MR
RM22UA21MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22UA21MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA21MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA21MRdirectives | 2014/35/EU
RM22UA21MRdirectives | 2014/30/EU
RM22UA21MRdirectives | 2011/65/EU
RM22UA21MR
RM22UA21MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category,
RM22UA21MR | Class C ¦ Germanisher Lloyd,Environmental category,
RM22UA21MRambient air temperature for storage | -40oC..+80oC ¦ ,Storage,
RM22UA21MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22UA21MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22UA21MR | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22UA21MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22UA21MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22UA21MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22UA21MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22UA21MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22UA21MRIP degree of protection | IP40 ¦ IEC60529,Housing,
RM22UA21MRIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22UA21MR
RM22UA21MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22UA21MRheight | Height,
RM22UA21MRdepth | Depth,
RM22UA21MRnet weight | 110
RM22UA21MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22UA21MRmounting support | - ¦ IEC/EN 60715,With socket,
RM22UA21MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UA21MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22UA21MRMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22UA21MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22UA21MRconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22UA21MRconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22UA21MRconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UA21MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22UA21MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22UA21MRduty time | 1
RM22UA21MR
RM22UA21MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22UA21MRelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22UA21MRelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22UA21MRelectromagnetic compatibility | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22UA21MRelectromagnetic compatibility | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22UA21MRelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22UA21MRelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22UA21MRelectromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22UA21MRelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22UA21MRelectromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
RM22UA21MRelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22UA21MRelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22UA21MRelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22UA21MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22UA21MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22UA21MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22UA21MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22UA21MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22UA21MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UA21MR
RM22UA21MRpollution degree | 3 ¦ IEC60664-1
RM22UA21MRovervoltage category | 3 ¦ IEC60664-1
RM22UA21MRcircuit group | A1, A2 ¦ ,Supply,Terminal
RM22UA21MRcircuit group | E1, M ¦ ,Input 1,
RM22UA21MRcircuit group | E2, M ¦ ,Input 2,
RM22UA21MRcircuit group | E3, M ¦ ,Input 3,
RM22UA21MRcircuit group | 11,12,14 ¦ ,Output 1,
RM22UA21MRcircuit group | 21,22,24 ¦ ,Output 2,
RM22UA21MR | 24…240 AC/DC ¦ ,Supply,Rated
RM22UA21MR | 0.05..0.5 AC/DC [full: 0.05..0.5 AC/DC] ¦ ,Input 1,Voltage
RM22UA21MR | 0.3..3 AC/DC [full: 0.3..3 AC/DC] ¦ ,Input 2,Spec
RM22UA21MR | 0.5..5 AC/DC [full: 0.5..5 AC/DC] ¦ ,Input 3,
RM22UA21MR | 250V ¦ ,Output 1,
RM22UA21MR | 250V ¦ ,Output 2,
RM22UA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply,
RM22UA21MR[Ui] rated insulation voltage | 12.5 ¦ IEC60664-1,Input 1,
RM22UA21MR[Ui] rated insulation voltage | 12.5 ¦ IEC60664-1,Input 2,
RM22UA21MR[Ui] rated insulation voltage | 12.5 ¦ IEC60664-1,Input 3,
RM22UA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22UA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22UA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22UA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 2,Isolated
RM22UA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 3,Circuit
RM22UA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 1,
RM22UA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 2,
RM22UA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22UA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 1,
RM22UA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 2,
RM22UA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 1,
RM22UA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 2,
RM22UA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 3 / Output 1,
RM22UA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 3 / Output 2,
RM22UA21MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22UA21MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22UA21MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22UA21MR[Uimp] rated impulse withstand voltage | 0.8kV, OVC3 ¦ IEC60664-1,Input 1,
RM22UA21MR[Uimp] rated impulse withstand voltage | 0.8kV, OVC3 ¦ IEC60664-1,Input 2,
RM22UA21MR[Uimp] rated impulse withstand voltage | 0.8kV, OVC3 ¦ IEC60664-1,Input 3,
RM22UA21MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22UA21MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22UA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22UA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated
RM22UA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit
RM22UA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22UA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22UA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22UA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM22UA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2,
RM22UA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1,
RM22UA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2,
RM22UA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1,
RM22UA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2,
RM22UA21MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22UA21MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22UA21MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM22UA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2,
RM22UA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3,
RM22UA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22UA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22UA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22UA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM22UA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2,
RM22UA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1,
RM22UA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2,
RM22UA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1,
RM22UA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2,
RM22UA21MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22UA21MRdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22UA21MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM22UA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2,
RM22UA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3,
RM22UA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22UA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22UA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22UA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM22UA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2,
RM22UA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1,
RM22UA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2,
RM22UA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1,
RM22UA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2,
RM22UA21MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22UA21MRinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22UA21MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA21MR
RM22UA21MR[Us] rated supply voltage | ~/-- 24…240
RM22UA21MRsupply voltage limits | ~/-- 20.4…264
RM22UA21MRpolarity
RM22UA21MRsupply frequency | 50 / 60
RM22UA21MRsupply frequency | 45…66
RM22UA21MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM22UA21MRimmunity to microbreaks | 10
RM22UA21MRsupply terminal | A1-A2
RM22UA21MRon-load factor | 1
RM22UA21MRrelease of input voltage | -
RM22UA21MR
RM22UA21MR | - ¦ ,Over / undervoltage (windows mode),
RM22UA21MR | Without memory ¦ ,Over voltage,
RM22UA21MR | - ¦ ,Undervoltage ,
RM22UA21MR | ~/-- 0.05…5
RM22UA21MR | 5 ¦ ,E1-M / B1-C,
RM22UA21MR | 30 ¦ ,E2-M / B2-C,
RM22UA21MR | 50 ¦ ,E3-M / B3-C,
RM22UA21MR | - ¦ ,A1+ / A2-,
RM22UA21MR | - ¦ ,Built in current transformer,
RM22UA21MR | ~/-- 0.05…0.5 ¦ ,E1-M / B1-C,
RM22UA21MR | ~/-- 0.3…3 ¦ ,E2-M / B2-C,
RM22UA21MR | ~/-- 0.5…5 ¦ ,E3-M / B3-C,
RM22UA21MR | - ¦ ,A1+ / A2-,
RM22UA21MR | - ¦ ,Built in current transformer,
RM22UA21MR | Adjustable 10%...100% of 0.5V ¦ ,E1-M / B1-C,
RM22UA21MR | Adjustable 10%...100% of 3V ¦ ,E2-M / B2-C,
RM22UA21MR | Adjustable 10%...100% of 5V ¦ ,E3-M / B3-C,
RM22UA21MR | - ¦ ,A1+ / A2-,
RM22UA21MR | - ¦ ,Built in current transformer,
RM22UA21MR | Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C,
RM22UA21MR | Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C,
RM22UA21MR | Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C,
RM22UA21MR | - ¦ ,A1+ / A2-,
RM22UA21MR | - ¦ ,Built in current transformer,
RM22UA21MR | Resistive Voltage Step Down
RM22UA21MR | E1-M, E2-M, E3-M
RM22UA21MR | 50 / 60
RM22UA21MR | 36…77
RM22UA21MR | +/- 10% of full scale value
RM22UA21MR | +/- 0.5%
RM22UA21MR | < 1% over whole range
RM22UA21MR | 0.05% / oC
RM22UA21MR | 30 100
RM22UA21MR | True RMS
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MR
RM22UA21MRoutput type | 2 x C/O relay contacts
RM22UA21MRoutput terminal | 11-12-14, 21-22-24
RM22UA21MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22UA21MRoutput logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22UA21MRcontacts material | Cadmium free
RM22UA21MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22UA21MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22UA21MRelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22UA21MRelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22UA21MRelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22UA21MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22UA21MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22UA21MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22UA21MRmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM22UA21MRmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM22UA21MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22UA21MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22UA21MRminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UA21MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UA21MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UA21MRthermal current | 8A ¦ IEC60947-5-1
RM22UA21MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22UA21MRshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22UA21MR
RM22UA21MRtime delay type | - ¦ ,"OFF" delay,
RM22UA21MRtime delay type | - ¦ ,"ON" delay,
RM22UA21MRtime delay type | - ¦ ,Inhibition,
RM22UA21MRtime delay range | - ¦ ,"OFF" delay,
RM22UA21MRtime delay range | - ¦ ,"ON" delay,
RM22UA21MRtime delay range | - ¦ ,Inhibition,
RM22UA21MRresponse time | Not specified =< 300ms ¦ ,on crossing the threshold,
RM22UA21MRresponse time
RM22UA21MRresponse time
RM22UA21MRresponse time
RM22UA21MRresponse time
RM22UA21MRpower on delay | 0
RM22UA21MRreset time | 0
RM22UA21MRreset time | through front panel reset,
RM22UA21MRreset time | through input control reset,
RM22UA21MRsetting accuracy of time delay | +/- 10% of full scales
RM22UA21MRrepeat accuracy of time delay | +/- 2%
RM22UA21MRtime delay drift | < 1
RM22UA21MRtime delay drift | < 0.05
RM22UA21MR
RM22UA21MRstatus LED | Dial pointer (Green) R (Amber)
RM22UA21MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22UA21MRlocal signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22UA21MRlocal signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22UA21MRlocal signalling | R - ON ¦ ,Output is energized,
RM22UA21MRlocal signalling | R - OFF ¦ ,Output is de-energized,
RM22UA21MRlocal signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22UA21MRlocal signalling
RM22UA21MRlocal signalling
RM22UA21MRlocal signalling
RM22UA21MRlocal signalling
RM22UA21MRlocal signalling
RM22UA21MRlocal signalling
RM22UA21MRlocal signalling
RM22UA21MRlocal signalling
RM22UA21MRlocal signalling
RM22UA21MR
RM22UA21MR | Yes
RM22UA21MR | 1) Will always illuminated when power is supplied to the product
RM22UA21MRdiagnostic button | Output will be de-energized when activated
RM22UA21MR | -
RM22UA21MR | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22UA21MR
RM22UA21MRsafety reliability data | 2,700,000 hours ¦ ,MTTF,
RM22UA21MRsafety reliability data | 290,000 hours ¦ ,B10,
RM22UA21MR | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22UA21MR | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22UA21MR
RM22UA22MR
RM22UA22MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22UA22MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA22MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA22MRdirectives | 2014/35/EU
RM22UA22MRdirectives | 2014/30/EU
RM22UA22MRdirectives | 2011/65/EU
RM22UA22MR
RM22UA22MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category,
RM22UA22MR | Class C ¦ Germanisher Lloyd,Environmental category,
RM22UA22MRambient air temperature for storage | -40oC..+80oC ¦ ,Storage,
RM22UA22MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22UA22MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22UA22MR | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22UA22MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22UA22MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22UA22MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22UA22MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22UA22MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22UA22MRIP degree of protection | IP40 ¦ IEC60529,Housing,
RM22UA22MRIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22UA22MR
RM22UA22MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22UA22MRheight | Height,
RM22UA22MRdepth | Depth,
RM22UA22MRnet weight | 110
RM22UA22MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22UA22MRmounting support | - ¦ IEC/EN 60715,With socket,
RM22UA22MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UA22MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22UA22MRMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22UA22MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22UA22MRconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22UA22MRconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22UA22MRconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UA22MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22UA22MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22UA22MRduty time | 1
RM22UA22MR
RM22UA22MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22UA22MRelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22UA22MRelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22UA22MRelectromagnetic compatibility | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22UA22MRelectromagnetic compatibility | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22UA22MRelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22UA22MRelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22UA22MRelectromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22UA22MRelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22UA22MRelectromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
RM22UA22MRelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22UA22MRelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22UA22MRelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22UA22MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22UA22MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22UA22MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22UA22MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22UA22MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22UA22MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UA22MR
RM22UA22MRpollution degree | 3 ¦ IEC60664-1
RM22UA22MRovervoltage category | 3 ¦ IEC60664-1
RM22UA22MRcircuit group | A1, A2 ¦ ,Supply,Terminal
RM22UA22MRcircuit group | E1, M ¦ ,Input 1,
RM22UA22MRcircuit group | E2, M ¦ ,Input 2,
RM22UA22MRcircuit group | E3, M ¦ ,Input 3,
RM22UA22MRcircuit group | 11,12,14 ¦ ,Output 1,
RM22UA22MRcircuit group | 21,22,24 ¦ ,Output 2,
RM22UA22MR | 24…240 AC/DC ¦ ,Supply,Rated
RM22UA22MR | 1..10 AC/DC [full: 1..10 AC/DC] ¦ ,Input 1,Voltage
RM22UA22MR | 5..50 AC/DC [full: 5..50 AC/DC] ¦ ,Input 2,Spec
RM22UA22MR | 10..100 AC/DC [full: 10..100 AC/DC] ¦ ,Input 3,
RM22UA22MR | 250V ¦ ,Output 1,
RM22UA22MR | 250V ¦ ,Output 2,
RM22UA22MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply,
RM22UA22MR[Ui] rated insulation voltage | 12.5 ¦ IEC60664-1,Input 1,
RM22UA22MR[Ui] rated insulation voltage | 50 ¦ IEC60664-1,Input 2,
RM22UA22MR[Ui] rated insulation voltage | 100 ¦ IEC60664-1,Input 3,
RM22UA22MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22UA22MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22UA22MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22UA22MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 2,Isolated
RM22UA22MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 3,Circuit
RM22UA22MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 1,
RM22UA22MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 2,
RM22UA22MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22UA22MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 1,
RM22UA22MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 2,
RM22UA22MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 1,
RM22UA22MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 2,
RM22UA22MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 3 / Output 1,
RM22UA22MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 3 / Output 2,
RM22UA22MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22UA22MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22UA22MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA22MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22UA22MR[Uimp] rated impulse withstand voltage | 0.8kV, OVC3 ¦ IEC60664-1,Input 1,
RM22UA22MR[Uimp] rated impulse withstand voltage | 0.8kV, OVC3 ¦ IEC60664-1,Input 2,
RM22UA22MR[Uimp] rated impulse withstand voltage | 1.5kV, OVC3 ¦ IEC60664-1,Input 3,
RM22UA22MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22UA22MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22UA22MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22UA22MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated
RM22UA22MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit
RM22UA22MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22UA22MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22UA22MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22UA22MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM22UA22MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2,
RM22UA22MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1,
RM22UA22MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2,
RM22UA22MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1,
RM22UA22MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2,
RM22UA22MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22UA22MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22UA22MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA22MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM22UA22MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2,
RM22UA22MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3,
RM22UA22MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22UA22MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22UA22MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22UA22MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM22UA22MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2,
RM22UA22MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1,
RM22UA22MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2,
RM22UA22MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1,
RM22UA22MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2,
RM22UA22MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22UA22MRdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22UA22MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA22MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM22UA22MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2,
RM22UA22MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3,
RM22UA22MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22UA22MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22UA22MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22UA22MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM22UA22MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2,
RM22UA22MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1,
RM22UA22MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2,
RM22UA22MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1,
RM22UA22MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2,
RM22UA22MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22UA22MRinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22UA22MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA22MR
RM22UA22MR[Us] rated supply voltage | ~/-- 24…240
RM22UA22MRsupply voltage limits | ~/-- 20.4…264
RM22UA22MRpolarity
RM22UA22MRsupply frequency | 50 / 60
RM22UA22MRsupply frequency | 45…66
RM22UA22MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM22UA22MRimmunity to microbreaks | 10
RM22UA22MRsupply terminal | A1-A2
RM22UA22MRon-load factor | 1
RM22UA22MRrelease of input voltage | -
RM22UA22MR
RM22UA22MR | - ¦ ,Over / undervoltage (windows mode),
RM22UA22MR | Without memory ¦ ,Over voltage,
RM22UA22MR | - ¦ ,Undervoltage ,
RM22UA22MR | ~/-- 1…100
RM22UA22MR | 22 ¦ ,E1-M / B1-C,
RM22UA22MR | 110 ¦ ,E2-M / B2-C,
RM22UA22MR | 220 ¦ ,E3-M / B3-C,
RM22UA22MR | - ¦ ,A1+ / A2-,
RM22UA22MR | - ¦ ,Built in current transformer,
RM22UA22MR | ~/-- 1…10 ¦ ,E1-M / B1-C,
RM22UA22MR | ~/-- 5…50 ¦ ,E2-M / B2-C,
RM22UA22MR | ~/-- 10…100 ¦ ,E3-M / B3-C,
RM22UA22MR | - ¦ ,A1+ / A2-,
RM22UA22MR | - ¦ ,Built in current transformer,
RM22UA22MR | Adjustable 10%...100% of 10V ¦ ,E1-M / B1-C,
RM22UA22MR | Adjustable 10%...100% of 50V ¦ ,E2-M / B2-C,
RM22UA22MR | Adjustable 10%...100% of 100V ¦ ,E3-M / B3-C,
RM22UA22MR | - ¦ ,A1+ / A2-,
RM22UA22MR | - ¦ ,Built in current transformer,
RM22UA22MR | Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C,
RM22UA22MR | Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C,
RM22UA22MR | Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C,
RM22UA22MR | - ¦ ,A1+ / A2-,
RM22UA22MR | - ¦ ,Built in current transformer,
RM22UA22MR | Resistive Voltage Step Down
RM22UA22MR | E1-M, E2-M, E3-M
RM22UA22MR | 50 / 60
RM22UA22MR | 36…77
RM22UA22MR | +/- 10% of full scale value
RM22UA22MR | +/- 0.5%
RM22UA22MR | < 1% over whole range
RM22UA22MR | 0.05% / oC
RM22UA22MR | 30 100
RM22UA22MR | True RMS
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MR
RM22UA22MRoutput type | 2 x C/O relay contacts
RM22UA22MRoutput terminal | 11-12-14, 21-22-24
RM22UA22MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22UA22MRoutput logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22UA22MRcontacts material | Cadmium free
RM22UA22MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22UA22MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22UA22MRelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22UA22MRelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22UA22MRelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22UA22MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22UA22MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22UA22MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22UA22MRmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM22UA22MRmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM22UA22MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22UA22MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22UA22MRminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UA22MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UA22MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UA22MRthermal current | 8A ¦ IEC60947-5-1
RM22UA22MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22UA22MRshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22UA22MR
RM22UA22MRtime delay type | - ¦ ,"OFF" delay,
RM22UA22MRtime delay type | - ¦ ,"ON" delay,
RM22UA22MRtime delay type | - ¦ ,Inhibition,
RM22UA22MRtime delay range | - ¦ ,"OFF" delay,
RM22UA22MRtime delay range | - ¦ ,"ON" delay,
RM22UA22MRtime delay range | - ¦ ,Inhibition,
RM22UA22MRresponse time | Not specified =< 300ms ¦ ,on crossing the threshold,
RM22UA22MRresponse time
RM22UA22MRresponse time
RM22UA22MRresponse time
RM22UA22MRresponse time
RM22UA22MRpower on delay | 0
RM22UA22MRreset time | 0
RM22UA22MRreset time | through front panel reset,
RM22UA22MRreset time | through input control reset,
RM22UA22MRsetting accuracy of time delay | +/- 10% of full scales
RM22UA22MRrepeat accuracy of time delay | +/- 2%
RM22UA22MRtime delay drift | < 1
RM22UA22MRtime delay drift | < 0.05
RM22UA22MR
RM22UA22MRstatus LED | Dial pointer (Green) R (Amber)
RM22UA22MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22UA22MRlocal signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22UA22MRlocal signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22UA22MRlocal signalling | R - ON ¦ ,Output is energized,
RM22UA22MRlocal signalling | R - OFF ¦ ,Output is de-energized,
RM22UA22MRlocal signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22UA22MRlocal signalling
RM22UA22MRlocal signalling
RM22UA22MRlocal signalling
RM22UA22MRlocal signalling
RM22UA22MRlocal signalling
RM22UA22MRlocal signalling
RM22UA22MRlocal signalling
RM22UA22MRlocal signalling
RM22UA22MRlocal signalling
RM22UA22MR
RM22UA22MR | Yes
RM22UA22MR | 1) Will always illuminated when power is supplied to the product
RM22UA22MRdiagnostic button | Output will be de-energized when activated
RM22UA22MR | -
RM22UA22MR | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22UA22MR
RM22UA22MRsafety reliability data | 2,700,000 hours ¦ ,MTTF,
RM22UA22MRsafety reliability data | 290,000 hours ¦ ,B10,
RM22UA22MR | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22UA22MR | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22UA22MR
RM22UA23MR
RM22UA23MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22UA23MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA23MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA23MRdirectives | 2014/35/EU
RM22UA23MRdirectives | 2014/30/EU
RM22UA23MRdirectives | 2011/65/EU
RM22UA23MR
RM22UA23MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category,
RM22UA23MR | Class C ¦ Germanisher Lloyd,Environmental category,
RM22UA23MRambient air temperature for storage | -40oC..+80oC ¦ ,Storage,
RM22UA23MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22UA23MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22UA23MR | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22UA23MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22UA23MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22UA23MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22UA23MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22UA23MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22UA23MRIP degree of protection | IP40 ¦ IEC60529,Housing,
RM22UA23MRIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22UA23MR
RM22UA23MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22UA23MRheight | Height,
RM22UA23MRdepth | Depth,
RM22UA23MRnet weight | 110
RM22UA23MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22UA23MRmounting support | - ¦ IEC/EN 60715,With socket,
RM22UA23MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UA23MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22UA23MRMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22UA23MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22UA23MRconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22UA23MRconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22UA23MRconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UA23MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22UA23MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22UA23MRduty time | 1
RM22UA23MR
RM22UA23MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22UA23MRelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22UA23MRelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22UA23MRelectromagnetic compatibility | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22UA23MRelectromagnetic compatibility | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22UA23MRelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22UA23MRelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22UA23MRelectromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22UA23MRelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22UA23MRelectromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
RM22UA23MRelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22UA23MRelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22UA23MRelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22UA23MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22UA23MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22UA23MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22UA23MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22UA23MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22UA23MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UA23MR
RM22UA23MRpollution degree | 3 ¦ IEC60664-1
RM22UA23MRovervoltage category | 3 ¦ IEC60664-1
RM22UA23MRcircuit group | A1, A2 ¦ ,Supply,Terminal
RM22UA23MRcircuit group | E1, M ¦ ,Input 1,
RM22UA23MRcircuit group | E2, M ¦ ,Input 2,
RM22UA23MRcircuit group | E3, M ¦ ,Input 3,
RM22UA23MRcircuit group | 11,12,14 ¦ ,Output 1,
RM22UA23MRcircuit group | 21,22,24 ¦ ,Output 2,
RM22UA23MR | 24…240 AC/DC ¦ ,Supply,Rated
RM22UA23MR | 18..125 AC/DC [full: 15..150 AC/DC] ¦ ,Input 1,Voltage
RM22UA23MR | 37..250 AC/DC [full: 30..300 AC/DC] ¦ ,Input 2,Spec
RM22UA23MR | 75..440 AC/DC [full: 50..500 AC/DC] ¦ ,Input 3,
RM22UA23MR | 250V ¦ ,Output 1,
RM22UA23MR | 250V ¦ ,Output 2,
RM22UA23MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply,
RM22UA23MR[Ui] rated insulation voltage | 125V ¦ IEC60664-1,Input 1,
RM22UA23MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2,
RM22UA23MR[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 3,
RM22UA23MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22UA23MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22UA23MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22UA23MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 2,Isolated
RM22UA23MR[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Input 3,Circuit
RM22UA23MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 1,
RM22UA23MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 2,
RM22UA23MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22UA23MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 1,
RM22UA23MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 2,
RM22UA23MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 1,
RM22UA23MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 2,
RM22UA23MR[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 3 / Output 1,
RM22UA23MR[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 3 / Output 2,
RM22UA23MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22UA23MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22UA23MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA23MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22UA23MR[Uimp] rated impulse withstand voltage | 2.5kV, OVC3 ¦ IEC60664-1,Input 1,
RM22UA23MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2,
RM22UA23MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3,
RM22UA23MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22UA23MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22UA23MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22UA23MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated
RM22UA23MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit
RM22UA23MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22UA23MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22UA23MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22UA23MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM22UA23MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2,
RM22UA23MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1,
RM22UA23MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2,
RM22UA23MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1,
RM22UA23MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2,
RM22UA23MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22UA23MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22UA23MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA23MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM22UA23MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2,
RM22UA23MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3,
RM22UA23MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22UA23MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22UA23MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22UA23MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM22UA23MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2,
RM22UA23MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1,
RM22UA23MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2,
RM22UA23MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1,
RM22UA23MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2,
RM22UA23MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22UA23MRdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22UA23MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA23MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM22UA23MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2,
RM22UA23MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3,
RM22UA23MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22UA23MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22UA23MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22UA23MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM22UA23MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2,
RM22UA23MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1,
RM22UA23MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2,
RM22UA23MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1,
RM22UA23MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2,
RM22UA23MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22UA23MRinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22UA23MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA23MR
RM22UA23MR[Us] rated supply voltage | ~/-- 24…240
RM22UA23MRsupply voltage limits | ~/-- 20.4…264
RM22UA23MRpolarity
RM22UA23MRsupply frequency | 50 / 60
RM22UA23MRsupply frequency | 45…66
RM22UA23MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM22UA23MRimmunity to microbreaks | 10
RM22UA23MRsupply terminal | A1-A2
RM22UA23MRon-load factor | 1
RM22UA23MRrelease of input voltage | -
RM22UA23MR
RM22UA23MR | - ¦ ,Over / undervoltage (windows mode),
RM22UA23MR | Without memory ¦ ,Over voltage,
RM22UA23MR | - ¦ ,Undervoltage ,
RM22UA23MR | ~/-- 15…500
RM22UA23MR | 150 ¦ ,E1-M / B1-C,
RM22UA23MR | 300 ¦ ,E2-M / B2-C,
RM22UA23MR | 500 ¦ ,E3-M / B3-C,
RM22UA23MR | - ¦ ,A1+ / A2-,
RM22UA23MR | - ¦ ,Built in current transformer,
RM22UA23MR | ~/-- 15…150 ¦ ,E1-M / B1-C,
RM22UA23MR | ~/-- 30…300 ¦ ,E2-M / B2-C,
RM22UA23MR | ~/-- 50…500 ¦ ,E3-M / B3-C,
RM22UA23MR | - ¦ ,A1+ / A2-,
RM22UA23MR | - ¦ ,Built in current transformer,
RM22UA23MR | Adjustable 10%...100% of 150V ¦ ,E1-M / B1-C,
RM22UA23MR | Adjustable 10%...100% of 300V ¦ ,E2-M / B2-C,
RM22UA23MR | Adjustable 10%...100% of 500V ¦ ,E3-M / B3-C,
RM22UA23MR | - ¦ ,A1+ / A2-,
RM22UA23MR | - ¦ ,Built in current transformer,
RM22UA23MR | Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C,
RM22UA23MR | Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C,
RM22UA23MR | Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C,
RM22UA23MR | - ¦ ,A1+ / A2-,
RM22UA23MR | - ¦ ,Built in current transformer,
RM22UA23MR | Resistive Voltage Step Down
RM22UA23MR | E1-M, E2-M, E3-M
RM22UA23MR | 50 / 60
RM22UA23MR | 36…77
RM22UA23MR | +/- 10% of full scale value
RM22UA23MR | +/- 0.5%
RM22UA23MR | < 1% over whole range
RM22UA23MR | 0.05% / oC
RM22UA23MR | 30 100
RM22UA23MR | True RMS
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MR
RM22UA23MRoutput type | 2 x C/O relay contacts
RM22UA23MRoutput terminal | 11-12-14, 21-22-24
RM22UA23MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22UA23MRoutput logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22UA23MRcontacts material | Cadmium free
RM22UA23MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22UA23MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22UA23MRelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22UA23MRelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22UA23MRelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22UA23MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22UA23MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22UA23MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22UA23MRmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM22UA23MRmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM22UA23MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22UA23MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22UA23MRminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UA23MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UA23MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UA23MRthermal current | 8A ¦ IEC60947-5-1
RM22UA23MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22UA23MRshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22UA23MR
RM22UA23MRtime delay type | - ¦ ,"OFF" delay,
RM22UA23MRtime delay type | - ¦ ,"ON" delay,
RM22UA23MRtime delay type | - ¦ ,Inhibition,
RM22UA23MRtime delay range | - ¦ ,"OFF" delay,
RM22UA23MRtime delay range | - ¦ ,"ON" delay,
RM22UA23MRtime delay range | - ¦ ,Inhibition,
RM22UA23MRresponse time | Not specified =< 300ms ¦ ,on crossing the threshold,
RM22UA23MRresponse time
RM22UA23MRresponse time
RM22UA23MRresponse time
RM22UA23MRresponse time
RM22UA23MRpower on delay | 0
RM22UA23MRreset time | 0
RM22UA23MRreset time | through front panel reset,
RM22UA23MRreset time | through input control reset,
RM22UA23MRsetting accuracy of time delay | +/- 10% of full scales
RM22UA23MRrepeat accuracy of time delay | +/- 2%
RM22UA23MRtime delay drift | < 1
RM22UA23MRtime delay drift | < 0.05
RM22UA23MR
RM22UA23MRstatus LED | Dial pointer (Green) R (Amber)
RM22UA23MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22UA23MRlocal signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22UA23MRlocal signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22UA23MRlocal signalling | R - ON ¦ ,Output is energized,
RM22UA23MRlocal signalling | R - OFF ¦ ,Output is de-energized,
RM22UA23MRlocal signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22UA23MRlocal signalling
RM22UA23MRlocal signalling
RM22UA23MRlocal signalling
RM22UA23MRlocal signalling
RM22UA23MRlocal signalling
RM22UA23MRlocal signalling
RM22UA23MRlocal signalling
RM22UA23MRlocal signalling
RM22UA23MRlocal signalling
RM22UA23MR
RM22UA23MR | Yes
RM22UA23MR | 1) Will always illuminated when power is supplied to the product
RM22UA23MRdiagnostic button | Output will be de-energized when activated
RM22UA23MR | -
RM22UA23MR | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22UA23MR
RM22UA23MRsafety reliability data | 2,700,000 hours ¦ ,MTTF,
RM22UA23MRsafety reliability data | 290,000 hours ¦ ,B10,
RM22UA23MR | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22UA23MR | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22UA23MR
RM22UA31MR
RM22UA31MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22UA31MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA31MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA31MRdirectives | 2014/35/EU
RM22UA31MRdirectives | 2014/30/EU
RM22UA31MRdirectives | 2011/65/EU
RM22UA31MR
RM22UA31MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category,
RM22UA31MR | Class C ¦ Germanisher Lloyd,Environmental category,
RM22UA31MRambient air temperature for storage | -40oC..+80oC ¦ ,Storage,
RM22UA31MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22UA31MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22UA31MR | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22UA31MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22UA31MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22UA31MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22UA31MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22UA31MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22UA31MRIP degree of protection | IP40 ¦ IEC60529,Housing,
RM22UA31MRIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22UA31MR
RM22UA31MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22UA31MRheight | Height,
RM22UA31MRdepth | Depth,
RM22UA31MRnet weight | 110
RM22UA31MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22UA31MRmounting support | - ¦ IEC/EN 60715,With socket,
RM22UA31MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UA31MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22UA31MRMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22UA31MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22UA31MRconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22UA31MRconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22UA31MRconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UA31MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22UA31MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22UA31MRduty time | 1
RM22UA31MR
RM22UA31MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22UA31MRelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22UA31MRelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22UA31MRelectromagnetic compatibility | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22UA31MRelectromagnetic compatibility | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22UA31MRelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22UA31MRelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22UA31MRelectromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22UA31MRelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22UA31MRelectromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
RM22UA31MRelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22UA31MRelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22UA31MRelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22UA31MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22UA31MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22UA31MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22UA31MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22UA31MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22UA31MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UA31MR
RM22UA31MRpollution degree | 3 ¦ IEC60664-1
RM22UA31MRovervoltage category | 3 ¦ IEC60664-1
RM22UA31MRcircuit group | A1, A2 ¦ ,Supply,Terminal
RM22UA31MRcircuit group | E1, M ¦ ,Input 1,
RM22UA31MRcircuit group | E2, M ¦ ,Input 2,
RM22UA31MRcircuit group | E3, M ¦ ,Input 3,
RM22UA31MRcircuit group | 11,12,14 ¦ ,Output 1,
RM22UA31MRcircuit group | 21,22,24 ¦ ,Output 2,
RM22UA31MR | 24…240 AC/DC ¦ ,Supply,Rated
RM22UA31MR | 0.05..0.5 AC/DC [full: 0.05..0.5 AC/DC] ¦ ,Input 1,Voltage
RM22UA31MR | 0.3..3 AC/DC [full: 0.3..3 AC/DC] ¦ ,Input 2,Spec
RM22UA31MR | 0.5..5 AC/DC [full: 0.5..5 AC/DC] ¦ ,Input 3,
RM22UA31MR | 250V ¦ ,Output 1,
RM22UA31MR | 250V ¦ ,Output 2,
RM22UA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply,
RM22UA31MR[Ui] rated insulation voltage | 12.5 ¦ IEC60664-1,Input 1,
RM22UA31MR[Ui] rated insulation voltage | 12.5 ¦ IEC60664-1,Input 2,
RM22UA31MR[Ui] rated insulation voltage | 12.5 ¦ IEC60664-1,Input 3,
RM22UA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22UA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22UA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22UA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 2,Isolated
RM22UA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 3,Circuit
RM22UA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 1,
RM22UA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 2,
RM22UA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22UA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 1,
RM22UA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 2,
RM22UA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 1,
RM22UA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 2,
RM22UA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 3 / Output 1,
RM22UA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 3 / Output 2,
RM22UA31MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22UA31MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22UA31MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22UA31MR[Uimp] rated impulse withstand voltage | 0.8kV, OVC3 ¦ IEC60664-1,Input 1,
RM22UA31MR[Uimp] rated impulse withstand voltage | 0.8kV, OVC3 ¦ IEC60664-1,Input 2,
RM22UA31MR[Uimp] rated impulse withstand voltage | 0.8kV, OVC3 ¦ IEC60664-1,Input 3,
RM22UA31MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22UA31MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22UA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22UA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated
RM22UA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit
RM22UA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22UA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22UA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22UA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM22UA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2,
RM22UA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1,
RM22UA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2,
RM22UA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1,
RM22UA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2,
RM22UA31MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22UA31MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22UA31MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM22UA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2,
RM22UA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3,
RM22UA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22UA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22UA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22UA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM22UA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2,
RM22UA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1,
RM22UA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2,
RM22UA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1,
RM22UA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2,
RM22UA31MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22UA31MRdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22UA31MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM22UA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2,
RM22UA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3,
RM22UA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22UA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22UA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22UA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM22UA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2,
RM22UA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1,
RM22UA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2,
RM22UA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1,
RM22UA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2,
RM22UA31MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22UA31MRinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22UA31MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA31MR
RM22UA31MR[Us] rated supply voltage | ~/-- 24…240
RM22UA31MRsupply voltage limits | ~/-- 20.4…264
RM22UA31MRpolarity
RM22UA31MRsupply frequency | 50 / 60
RM22UA31MRsupply frequency | 45…66
RM22UA31MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM22UA31MRimmunity to microbreaks | 10
RM22UA31MRsupply terminal | A1-A2
RM22UA31MRon-load factor | 1
RM22UA31MRrelease of input voltage | -
RM22UA31MR
RM22UA31MR | Selectable with memory / without memory ¦ ,Over / undervoltage (windows mode),
RM22UA31MR | Selectable with memory / without memory ¦ ,Over voltage,
RM22UA31MR | Selectable with memory / without memory ¦ ,Undervoltage ,
RM22UA31MR | ~/-- 0.05…5
RM22UA31MR | 5 ¦ ,E1-M / B1-C,
RM22UA31MR | 30 ¦ ,E2-M / B2-C,
RM22UA31MR | 50 ¦ ,E3-M / B3-C,
RM22UA31MR | - ¦ ,A1+ / A2-,
RM22UA31MR | - ¦ ,Built in current transformer,
RM22UA31MR | ~/-- 0.05…0.5 ¦ ,E1-M / B1-C,
RM22UA31MR | ~/-- 0.3…3 ¦ ,E2-M / B2-C,
RM22UA31MR | ~/-- 0.5…5 ¦ ,E3-M / B3-C,
RM22UA31MR | - ¦ ,A1+ / A2-,
RM22UA31MR | - ¦ ,Built in current transformer,
RM22UA31MR | Adjustable 10%...100% of 0.5V ¦ ,E1-M / B1-C,
RM22UA31MR | Adjustable 10%...100% of 3V ¦ ,E2-M / B2-C,
RM22UA31MR | Adjustable 10%...100% of 5V ¦ ,E3-M / B3-C,
RM22UA31MR | - ¦ ,A1+ / A2-,
RM22UA31MR | - ¦ ,Built in current transformer,
RM22UA31MR | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E1-M / B1-C,
RM22UA31MR | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E2-M / B2-C,
RM22UA31MR | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E3-M / B3-C,
RM22UA31MR | - ¦ ,A1+ / A2-,
RM22UA31MR | - ¦ ,Built in current transformer,
RM22UA31MR | Resistive Voltage Step Down
RM22UA31MR | E1-M, E2-M, E3-M
RM22UA31MR | 50 / 60
RM22UA31MR | 36…77
RM22UA31MR | +/- 10% of full scale value
RM22UA31MR | +/- 0.5%
RM22UA31MR | < 1% over whole range
RM22UA31MR | 0.05% / oC
RM22UA31MR | 30 100
RM22UA31MR | True RMS
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MR
RM22UA31MRoutput type | 2 x C/O relay contacts
RM22UA31MRoutput terminal | 11-12-14, 21-22-24
RM22UA31MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22UA31MRoutput logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22UA31MRcontacts material | Cadmium free
RM22UA31MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22UA31MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22UA31MRelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22UA31MRelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22UA31MRelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22UA31MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22UA31MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22UA31MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22UA31MRmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM22UA31MRmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM22UA31MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22UA31MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22UA31MRminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UA31MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UA31MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UA31MRthermal current | 8A ¦ IEC60947-5-1
RM22UA31MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22UA31MRshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22UA31MR
RM22UA31MRtime delay type | Yes ¦ ,"OFF" delay,
RM22UA31MRtime delay type | - ¦ ,"ON" delay,
RM22UA31MRtime delay type | - ¦ ,Inhibition,
RM22UA31MRtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay,
RM22UA31MRtime delay range | - ¦ ,"ON" delay,
RM22UA31MRtime delay range | - ¦ ,Inhibition,
RM22UA31MRresponse time | Not specified =< 300ms ¦ ,on crossing the threshold,
RM22UA31MRresponse time
RM22UA31MRresponse time
RM22UA31MRresponse time
RM22UA31MRresponse time
RM22UA31MRpower on delay | 0
RM22UA31MRreset time | 0
RM22UA31MRreset time | through front panel reset,
RM22UA31MRreset time | through input control reset,
RM22UA31MRsetting accuracy of time delay | +/- 10% of full scales
RM22UA31MRrepeat accuracy of time delay | +/- 2%
RM22UA31MRtime delay drift | < 1
RM22UA31MRtime delay drift | < 0.05
RM22UA31MR
RM22UA31MRstatus LED | Dial pointer (Green) R (Amber)
RM22UA31MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22UA31MRlocal signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22UA31MRlocal signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22UA31MRlocal signalling | R - ON ¦ ,Output is energized,
RM22UA31MRlocal signalling | R - OFF ¦ ,Output is de-energized,
RM22UA31MRlocal signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22UA31MRlocal signalling
RM22UA31MRlocal signalling
RM22UA31MRlocal signalling
RM22UA31MRlocal signalling
RM22UA31MRlocal signalling
RM22UA31MRlocal signalling
RM22UA31MRlocal signalling
RM22UA31MRlocal signalling
RM22UA31MRlocal signalling
RM22UA31MR
RM22UA31MR | Yes
RM22UA31MR | 1) Will always illuminated when power is supplied to the product
RM22UA31MRdiagnostic button | Output will be de-energized when activated
RM22UA31MR | -
RM22UA31MR | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22UA31MR
RM22UA31MRsafety reliability data | 2,700,000 hours ¦ ,MTTF,
RM22UA31MRsafety reliability data | 290,000 hours ¦ ,B10,
RM22UA31MR | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22UA31MR | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22UA31MR
RM22UA32MR
RM22UA32MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22UA32MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA32MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA32MRdirectives | 2014/35/EU
RM22UA32MRdirectives | 2014/30/EU
RM22UA32MRdirectives | 2011/65/EU
RM22UA32MR
RM22UA32MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category,
RM22UA32MR | Class C ¦ Germanisher Lloyd,Environmental category,
RM22UA32MRambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22UA32MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22UA32MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22UA32MR | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22UA32MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22UA32MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22UA32MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22UA32MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22UA32MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22UA32MRIP degree of protection | IP40 ¦ IEC60529,Housing,
RM22UA32MRIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22UA32MR
RM22UA32MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22UA32MRheight | Height,
RM22UA32MRdepth | Depth,
RM22UA32MRnet weight | 110
RM22UA32MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22UA32MRmounting support | - ¦ IEC/EN 60715,With socket,
RM22UA32MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UA32MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22UA32MRMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22UA32MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22UA32MRconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22UA32MRconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22UA32MRconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UA32MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22UA32MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22UA32MRduty time | 1
RM22UA32MR
RM22UA32MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22UA32MRelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22UA32MRelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22UA32MRelectromagnetic compatibility | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22UA32MRelectromagnetic compatibility | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22UA32MRelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22UA32MRelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22UA32MRelectromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22UA32MRelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22UA32MRelectromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
RM22UA32MRelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22UA32MRelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22UA32MRelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22UA32MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22UA32MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22UA32MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22UA32MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22UA32MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22UA32MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UA32MR
RM22UA32MRpollution degree | 3 ¦ IEC60664-1
RM22UA32MRovervoltage category | 3 ¦ IEC60664-1
RM22UA32MRcircuit group | A1, A2 ¦ ,Supply,Terminal
RM22UA32MRcircuit group | E1, M ¦ ,Input 1,
RM22UA32MRcircuit group | E2, M ¦ ,Input 2,
RM22UA32MRcircuit group | E3, M ¦ ,Input 3,
RM22UA32MRcircuit group | 11,12,14 ¦ ,Output 1,
RM22UA32MRcircuit group | 21,22,24 ¦ ,Output 2,
RM22UA32MR | 24…240 AC/DC ¦ ,Supply,Rated
RM22UA32MR | 1..10 AC/DC [full: 1..10 AC/DC] ¦ ,Input 1,Voltage
RM22UA32MR | 5..50 AC/DC [full: 5..50 AC/DC] ¦ ,Input 2,Spec
RM22UA32MR | 10..100 AC/DC [full: 10..100 AC/DC] ¦ ,Input 3,
RM22UA32MR | 250V ¦ ,Output 1,
RM22UA32MR | 250V ¦ ,Output 2,
RM22UA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply,
RM22UA32MR[Ui] rated insulation voltage | 12.5 ¦ IEC60664-1,Input 1,
RM22UA32MR[Ui] rated insulation voltage | 50 ¦ IEC60664-1,Input 2,
RM22UA32MR[Ui] rated insulation voltage | 100 ¦ IEC60664-1,Input 3,
RM22UA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22UA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22UA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22UA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 2,Isolated
RM22UA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 3,Circuit
RM22UA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 1,
RM22UA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 2,
RM22UA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22UA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 1,
RM22UA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 2,
RM22UA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 1,
RM22UA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 2,
RM22UA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 3 / Output 1,
RM22UA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 3 / Output 2,
RM22UA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22UA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22UA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22UA32MR[Uimp] rated impulse withstand voltage | 0.8kV, OVC3 ¦ IEC60664-1,Input 1,
RM22UA32MR[Uimp] rated impulse withstand voltage | 0.8kV, OVC3 ¦ IEC60664-1,Input 2,
RM22UA32MR[Uimp] rated impulse withstand voltage | 1.5kV, OVC3 ¦ IEC60664-1,Input 3,
RM22UA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22UA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22UA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22UA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated
RM22UA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit
RM22UA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22UA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22UA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22UA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM22UA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2,
RM22UA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1,
RM22UA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2,
RM22UA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1,
RM22UA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2,
RM22UA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22UA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22UA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM22UA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2,
RM22UA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3,
RM22UA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22UA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22UA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22UA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM22UA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2,
RM22UA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1,
RM22UA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2,
RM22UA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1,
RM22UA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2,
RM22UA32MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22UA32MRdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22UA32MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM22UA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2,
RM22UA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3,
RM22UA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22UA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22UA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22UA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM22UA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2,
RM22UA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1,
RM22UA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2,
RM22UA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1,
RM22UA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2,
RM22UA32MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22UA32MRinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22UA32MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA32MR
RM22UA32MR[Us] rated supply voltage | ~/-- 24…240
RM22UA32MRsupply voltage limits | ~/-- 20.4…264
RM22UA32MRpolarity
RM22UA32MRsupply frequency | 50 / 60
RM22UA32MRsupply frequency | 45…66
RM22UA32MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM22UA32MRimmunity to microbreaks | 10
RM22UA32MRsupply terminal | A1-A2
RM22UA32MRon-load factor | 1
RM22UA32MRrelease of input voltage | -
RM22UA32MR
RM22UA32MR | Selectable with memory / without memory ¦ ,Over / undervoltage (windows mode),
RM22UA32MR | Selectable with memory / without memory ¦ ,Over voltage,
RM22UA32MR | Selectable with memory / without memory ¦ ,Undervoltage ,
RM22UA32MR | ~/-- 1…100
RM22UA32MR | 22 ¦ ,E1-M / B1-C,
RM22UA32MR | 110 ¦ ,E2-M / B2-C,
RM22UA32MR | 220 ¦ ,E3-M / B3-C,
RM22UA32MR | - ¦ ,A1+ / A2-,
RM22UA32MR | - ¦ ,Built in current transformer,
RM22UA32MR | ~/-- 1…10 ¦ ,E1-M / B1-C,
RM22UA32MR | ~/-- 5…50 ¦ ,E2-M / B2-C,
RM22UA32MR | ~/-- 10…100 ¦ ,E3-M / B3-C,
RM22UA32MR | - ¦ ,A1+ / A2-,
RM22UA32MR | - ¦ ,Built in current transformer,
RM22UA32MR | Adjustable 10%...100% of 10V ¦ ,E1-M / B1-C,
RM22UA32MR | Adjustable 10%...100% of 50V ¦ ,E2-M / B2-C,
RM22UA32MR | Adjustable 10%...100% of 100V ¦ ,E3-M / B3-C,
RM22UA32MR | - ¦ ,A1+ / A2-,
RM22UA32MR | - ¦ ,Built in current transformer,
RM22UA32MR | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E1-M / B1-C,
RM22UA32MR | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E2-M / B2-C,
RM22UA32MR | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E3-M / B3-C,
RM22UA32MR | - ¦ ,A1+ / A2-,
RM22UA32MR | - ¦ ,Built in current transformer,
RM22UA32MR | Resistive Voltage Step Down
RM22UA32MR | E1-M, E2-M, E3-M
RM22UA32MR | 50 / 60
RM22UA32MR | 36…77
RM22UA32MR | +/- 10% of full scale value
RM22UA32MR | +/- 0.5%
RM22UA32MR | < 1% over whole range
RM22UA32MR | 0.05% / oC
RM22UA32MR | 30 100
RM22UA32MR | True RMS
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MR
RM22UA32MRoutput type | 2 x C/O relay contacts
RM22UA32MRoutput terminal | 11-12-14, 21-22-24
RM22UA32MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22UA32MRoutput logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22UA32MRcontacts material | Cadmium free
RM22UA32MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22UA32MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22UA32MRelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22UA32MRelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22UA32MRelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22UA32MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22UA32MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22UA32MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22UA32MRmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM22UA32MRmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM22UA32MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22UA32MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22UA32MRminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UA32MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UA32MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UA32MRthermal current | 8A ¦ IEC60947-5-1
RM22UA32MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22UA32MRshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22UA32MR
RM22UA32MRtime delay type | Yes ¦ ,"OFF" delay,
RM22UA32MRtime delay type | - ¦ ,"ON" delay,
RM22UA32MRtime delay type | - ¦ ,Inhibition,
RM22UA32MRtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay,
RM22UA32MRtime delay range | - ¦ ,"ON" delay,
RM22UA32MRtime delay range | - ¦ ,Inhibition,
RM22UA32MRresponse time | Not specified =< 300ms ¦ ,on crossing the threshold,
RM22UA32MRresponse time
RM22UA32MRresponse time
RM22UA32MRresponse time
RM22UA32MRresponse time
RM22UA32MRpower on delay | 0
RM22UA32MRreset time | 0
RM22UA32MRreset time | through front panel reset,
RM22UA32MRreset time | through input control reset,
RM22UA32MRsetting accuracy of time delay | +/- 10% of full scales
RM22UA32MRrepeat accuracy of time delay | +/- 2%
RM22UA32MRtime delay drift | < 1
RM22UA32MRtime delay drift | < 0.05
RM22UA32MR
RM22UA32MRstatus LED | Dial pointer (Green) R (Amber)
RM22UA32MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22UA32MRlocal signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22UA32MRlocal signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22UA32MRlocal signalling | R - ON ¦ ,Output is energized,
RM22UA32MRlocal signalling | R - OFF ¦ ,Output is de-energized,
RM22UA32MRlocal signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22UA32MRlocal signalling
RM22UA32MRlocal signalling
RM22UA32MRlocal signalling
RM22UA32MRlocal signalling
RM22UA32MRlocal signalling
RM22UA32MRlocal signalling
RM22UA32MRlocal signalling
RM22UA32MRlocal signalling
RM22UA32MRlocal signalling
RM22UA32MR
RM22UA32MR | Yes
RM22UA32MR | 1) Will always illuminated when power is supplied to the product
RM22UA32MRdiagnostic button | Output will be de-energized when activated
RM22UA32MR | -
RM22UA32MR | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22UA32MR
RM22UA32MRsafety reliability data | 2,700,000 hours ¦ ,MTTF,
RM22UA32MRsafety reliability data | 290,000 hours ¦ ,B10,
RM22UA32MR | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22UA32MR | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22UA32MR
RM22UA33MR
RM22UA33MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22UA33MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA33MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA33MRdirectives | 2014/35/EU
RM22UA33MRdirectives | 2014/30/EU
RM22UA33MRdirectives | 2011/65/EU
RM22UA33MR
RM22UA33MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category,
RM22UA33MR | Class C ¦ Germanisher Lloyd,Environmental category,
RM22UA33MRambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22UA33MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22UA33MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22UA33MR | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22UA33MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22UA33MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22UA33MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22UA33MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22UA33MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22UA33MRIP degree of protection | IP40 ¦ IEC60529,Housing,
RM22UA33MRIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22UA33MR
RM22UA33MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22UA33MRheight | Height,
RM22UA33MRdepth | Depth,
RM22UA33MRnet weight | 110
RM22UA33MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22UA33MRmounting support | - ¦ IEC/EN 60715,With socket,
RM22UA33MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UA33MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22UA33MRMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22UA33MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22UA33MRconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22UA33MRconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22UA33MRconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UA33MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22UA33MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22UA33MRduty time | 1
RM22UA33MR
RM22UA33MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22UA33MRelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22UA33MRelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22UA33MRelectromagnetic compatibility | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22UA33MRelectromagnetic compatibility | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22UA33MRelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22UA33MRelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22UA33MRelectromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22UA33MRelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22UA33MRelectromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
RM22UA33MRelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22UA33MRelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22UA33MRelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22UA33MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22UA33MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22UA33MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22UA33MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22UA33MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22UA33MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UA33MR
RM22UA33MRpollution degree | 3 ¦ IEC60664-1
RM22UA33MRovervoltage category | 3 ¦ IEC60664-1
RM22UA33MRcircuit group | A1, A2 ¦ ,Supply,Terminal
RM22UA33MRcircuit group | E1, M ¦ ,Input 1,
RM22UA33MRcircuit group | E2, M ¦ ,Input 2,
RM22UA33MRcircuit group | E3, M ¦ ,Input 3,
RM22UA33MRcircuit group | 11,12,14 ¦ ,Output 1,
RM22UA33MRcircuit group | 21,22,24 ¦ ,Output 2,
RM22UA33MR | 24…240 AC/DC ¦ ,Supply,Rated
RM22UA33MR | 18..125 AC/DC [full: 15..150 AC/DC] ¦ ,Input 1,Voltage
RM22UA33MR | 37..250 AC/DC [full: 30..300 AC/DC] ¦ ,Input 2,Spec
RM22UA33MR | 75..440 AC/DC [full: 50..500 AC/DC] ¦ ,Input 3,
RM22UA33MR | 250V ¦ ,Output 1,
RM22UA33MR | 250V ¦ ,Output 2,
RM22UA33MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply,
RM22UA33MR[Ui] rated insulation voltage | 125V ¦ IEC60664-1,Input 1,
RM22UA33MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2,
RM22UA33MR[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 3,
RM22UA33MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22UA33MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22UA33MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22UA33MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 2,Isolated
RM22UA33MR[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Input 3,Circuit
RM22UA33MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 1,
RM22UA33MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 2,
RM22UA33MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22UA33MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 1,
RM22UA33MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 2,
RM22UA33MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 1,
RM22UA33MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 2,
RM22UA33MR[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 3 / Output 1,
RM22UA33MR[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 3 / Output 2,
RM22UA33MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22UA33MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22UA33MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA33MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22UA33MR[Uimp] rated impulse withstand voltage | 2.5kV, OVC3 ¦ IEC60664-1,Input 1,
RM22UA33MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2,
RM22UA33MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3,
RM22UA33MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22UA33MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22UA33MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22UA33MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated
RM22UA33MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit
RM22UA33MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22UA33MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22UA33MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22UA33MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM22UA33MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2,
RM22UA33MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1,
RM22UA33MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2,
RM22UA33MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1,
RM22UA33MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2,
RM22UA33MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22UA33MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22UA33MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA33MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM22UA33MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2,
RM22UA33MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3,
RM22UA33MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22UA33MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22UA33MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22UA33MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM22UA33MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2,
RM22UA33MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1,
RM22UA33MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2,
RM22UA33MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1,
RM22UA33MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2,
RM22UA33MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22UA33MRdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22UA33MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA33MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM22UA33MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2,
RM22UA33MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3,
RM22UA33MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22UA33MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22UA33MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22UA33MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM22UA33MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2,
RM22UA33MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1,
RM22UA33MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2,
RM22UA33MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1,
RM22UA33MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2,
RM22UA33MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22UA33MRinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22UA33MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA33MR
RM22UA33MR[Us] rated supply voltage | ~/-- 24…240
RM22UA33MRsupply voltage limits | ~/-- 20.4…264
RM22UA33MRpolarity
RM22UA33MRsupply frequency | 50 / 60
RM22UA33MRsupply frequency | 45…66
RM22UA33MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM22UA33MRimmunity to microbreaks | 10
RM22UA33MRsupply terminal | A1-A2
RM22UA33MRon-load factor | 1
RM22UA33MRrelease of input voltage | -
RM22UA33MR
RM22UA33MR | Selectable with memory / without memory ¦ ,Over / undervoltage (windows mode),
RM22UA33MR | Selectable with memory / without memory ¦ ,Over voltage,
RM22UA33MR | Selectable with memory / without memory ¦ ,Undervoltage ,
RM22UA33MR | ~/-- 15…500
RM22UA33MR | 150 ¦ ,E1-M / B1-C,
RM22UA33MR | 300 ¦ ,E2-M / B2-C,
RM22UA33MR | 500 ¦ ,E3-M / B3-C,
RM22UA33MR | - ¦ ,A1+ / A2-,
RM22UA33MR | - ¦ ,Built in current transformer,
RM22UA33MR | ~/-- 15…150 ¦ ,E1-M / B1-C,
RM22UA33MR | ~/-- 30…300 ¦ ,E2-M / B2-C,
RM22UA33MR | ~/-- 50…500 ¦ ,E3-M / B3-C,
RM22UA33MR | - ¦ ,A1+ / A2-,
RM22UA33MR | - ¦ ,Built in current transformer,
RM22UA33MR | Adjustable 10%...100% of 150V ¦ ,E1-M / B1-C,
RM22UA33MR | Adjustable 10%...100% of 300V ¦ ,E2-M / B2-C,
RM22UA33MR | Adjustable 10%...100% of 500V ¦ ,E3-M / B3-C,
RM22UA33MR | - ¦ ,A1+ / A2-,
RM22UA33MR | - ¦ ,Built in current transformer,
RM22UA33MR | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E1-M / B1-C,
RM22UA33MR | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E2-M / B2-C,
RM22UA33MR | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E3-M / B3-C,
RM22UA33MR | - ¦ ,A1+ / A2-,
RM22UA33MR | - ¦ ,Built in current transformer,
RM22UA33MR | Resistive Voltage Step Down
RM22UA33MR | E1-M, E2-M, E3-M
RM22UA33MR | 50 / 60
RM22UA33MR | 36…77
RM22UA33MR | +/- 10% of full scale value
RM22UA33MR | +/- 0.5%
RM22UA33MR | < 1% over whole range
RM22UA33MR | 0.05% / oC
RM22UA33MR | 30 100
RM22UA33MR | True RMS
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MR
RM22UA33MRoutput type | 2 x C/O relay contacts
RM22UA33MRoutput terminal | 11-12-14, 21-22-24
RM22UA33MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22UA33MRoutput logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22UA33MRcontacts material | Cadmium free
RM22UA33MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22UA33MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22UA33MRelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22UA33MRelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22UA33MRelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22UA33MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22UA33MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22UA33MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22UA33MRmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM22UA33MRmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM22UA33MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22UA33MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22UA33MRminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UA33MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UA33MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UA33MRthermal current | 8A ¦ IEC60947-5-1
RM22UA33MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22UA33MRshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22UA33MR
RM22UA33MRtime delay type | Yes ¦ ,"OFF" delay,
RM22UA33MRtime delay type | - ¦ ,"ON" delay,
RM22UA33MRtime delay type | - ¦ ,Inhibition,
RM22UA33MRtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay,
RM22UA33MRtime delay range | - ¦ ,"ON" delay,
RM22UA33MRtime delay range | - ¦ ,Inhibition,
RM22UA33MRresponse time | Not specified =< 300ms ¦ ,on crossing the threshold,
RM22UA33MRresponse time
RM22UA33MRresponse time
RM22UA33MRresponse time
RM22UA33MRresponse time
RM22UA33MRpower on delay | 0
RM22UA33MRreset time | 0
RM22UA33MRreset time | through front panel reset,
RM22UA33MRreset time | through input control reset,
RM22UA33MRsetting accuracy of time delay | +/- 10% of full scales
RM22UA33MRrepeat accuracy of time delay | +/- 2%
RM22UA33MRtime delay drift | < 1
RM22UA33MRtime delay drift | < 0.05
RM22UA33MR
RM22UA33MRstatus LED | Dial pointer (Green) R (Amber)
RM22UA33MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22UA33MRlocal signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22UA33MRlocal signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22UA33MRlocal signalling | R - ON ¦ ,Output is energized,
RM22UA33MRlocal signalling | R - OFF ¦ ,Output is de-energized,
RM22UA33MRlocal signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22UA33MRlocal signalling
RM22UA33MRlocal signalling
RM22UA33MRlocal signalling
RM22UA33MRlocal signalling
RM22UA33MRlocal signalling
RM22UA33MRlocal signalling
RM22UA33MRlocal signalling
RM22UA33MRlocal signalling
RM22UA33MRlocal signalling
RM22UA33MR
RM22UA33MR | Yes
RM22UA33MR | 1) Will always illuminated when power is supplied to the product
RM22UA33MRdiagnostic button | Output will be de-energized when activated
RM22UA33MR | -
RM22UA33MR | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22UA33MR
RM22UA33MRsafety reliability data | 2,700,000 hours ¦ ,MTTF,
RM22UA33MRsafety reliability data | 290,000 hours ¦ ,B10,
RM22UA33MR | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22UA33MR | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22UA33MR
RM22UA33MT
RM22UA33MTstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22UA33MTproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA33MTmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA33MTdirectives | 2014/35/EU
RM22UA33MTdirectives | 2014/30/EU
RM22UA33MTdirectives | 2011/65/EU
RM22UA33MT
RM22UA33MT | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category,
RM22UA33MT | Class C ¦ Germanisher Lloyd,Environmental category,
RM22UA33MTambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22UA33MTambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22UA33MTrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22UA33MT | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22UA33MTvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22UA33MTshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22UA33MTbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22UA33MTseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22UA33MTIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22UA33MTIP degree of protection | IP40 ¦ IEC60529,Housing,
RM22UA33MTIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22UA33MT
RM22UA33MTwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22UA33MTheight | Height,
RM22UA33MTdepth | Depth,
RM22UA33MTnet weight | 110
RM22UA33MTmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22UA33MTmounting support | - ¦ IEC/EN 60715,With socket,
RM22UA33MTmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UA33MTMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22UA33MTMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22UA33MTconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22UA33MTconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22UA33MTconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22UA33MTconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UA33MTtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22UA33MTcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22UA33MTduty time | 1
RM22UA33MT
RM22UA33MTelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22UA33MTelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22UA33MTelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22UA33MTelectromagnetic compatibility | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22UA33MTelectromagnetic compatibility | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22UA33MTelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22UA33MTelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22UA33MTelectromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22UA33MTelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22UA33MTelectromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
RM22UA33MTelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22UA33MTelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22UA33MTelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 (Except Radiared RF IEC 61000-6-4 only) ¦ ,Generic emission standard,
RM22UA33MTelectromagnetic compatibility | Class A ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22UA33MTelectromagnetic compatibility | Class A, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22UA33MTelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22UA33MTelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22UA33MTelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22UA33MTelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UA33MT
RM22UA33MTpollution degree | 3 ¦ IEC60664-1
RM22UA33MTovervoltage category | 3 ¦ IEC60664-1
RM22UA33MTcircuit group | A1, A2 ¦ ,Supply,Terminal
RM22UA33MTcircuit group | E1, M ¦ ,Input 1,
RM22UA33MTcircuit group | E2, M ¦ ,Input 2,
RM22UA33MTcircuit group | E3, M ¦ ,Input 3,
RM22UA33MTcircuit group | 11,12,14 ¦ ,Output 1,
RM22UA33MTcircuit group | 21,22,24 ¦ ,Output 2,
RM22UA33MT | 380…415 AC ¦ ,Supply,Rated
RM22UA33MT | 18..125 AC/DC [full: 15..150 AC/DC] ¦ ,Input 1,Voltage
RM22UA33MT | 37..250 AC/DC [full: 30..300 AC/DC] ¦ ,Input 2,Spec
RM22UA33MT | 75..440 AC/DC [full: 50..500 AC/DC] ¦ ,Input 3,
RM22UA33MT | 250V ¦ ,Output 1,
RM22UA33MT | 250V ¦ ,Output 2,
RM22UA33MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply,
RM22UA33MT[Ui] rated insulation voltage | 125V ¦ IEC60664-1,Input 1,
RM22UA33MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2,
RM22UA33MT[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 3,
RM22UA33MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22UA33MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22UA33MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22UA33MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply / Input 2,Isolated
RM22UA33MT[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply / Input 3,Circuit
RM22UA33MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply / Output 1,
RM22UA33MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply / Output 2,
RM22UA33MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22UA33MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 1,
RM22UA33MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 2,
RM22UA33MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 1,
RM22UA33MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 2,
RM22UA33MT[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 3 / Output 1,
RM22UA33MT[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Input 3 / Output 2,
RM22UA33MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22UA33MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22UA33MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA33MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22UA33MT[Uimp] rated impulse withstand voltage | 2.5kV, OVC3 ¦ IEC60664-1,Input 1,
RM22UA33MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2,
RM22UA33MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3,
RM22UA33MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22UA33MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22UA33MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22UA33MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated
RM22UA33MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit
RM22UA33MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22UA33MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22UA33MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22UA33MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM22UA33MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2,
RM22UA33MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1,
RM22UA33MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2,
RM22UA33MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1,
RM22UA33MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2,
RM22UA33MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22UA33MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22UA33MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA33MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM22UA33MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2,
RM22UA33MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3,
RM22UA33MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22UA33MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22UA33MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22UA33MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM22UA33MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2,
RM22UA33MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1,
RM22UA33MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2,
RM22UA33MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1,
RM22UA33MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2,
RM22UA33MTdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22UA33MTdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22UA33MTdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA33MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM22UA33MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2,
RM22UA33MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3,
RM22UA33MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22UA33MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22UA33MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22UA33MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM22UA33MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2,
RM22UA33MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1,
RM22UA33MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2,
RM22UA33MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1,
RM22UA33MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2,
RM22UA33MTinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22UA33MTinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22UA33MTinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA33MT
RM22UA33MT[Us] rated supply voltage | ~380…415
RM22UA33MTsupply voltage limits | ~323…456.5
RM22UA33MTpolarity
RM22UA33MTsupply frequency | 50 / 60
RM22UA33MTsupply frequency | 45…66
RM22UA33MTpower consumption | ~ 10VA ~ 8VA
RM22UA33MTimmunity to microbreaks | 10
RM22UA33MTsupply terminal | A1-A2
RM22UA33MTon-load factor | 1
RM22UA33MTrelease of input voltage | -
RM22UA33MT
RM22UA33MT | Selectable with memory / without memory ¦ ,Over / undervoltage (windows mode),
RM22UA33MT | Selectable with memory / without memory ¦ ,Over voltage,
RM22UA33MT | Selectable with memory / without memory ¦ ,Undervoltage ,
RM22UA33MT | ~/-- 15…500
RM22UA33MT | 150 ¦ ,E1-M / B1-C,
RM22UA33MT | 300 ¦ ,E2-M / B2-C,
RM22UA33MT | 500 ¦ ,E3-M / B3-C,
RM22UA33MT | - ¦ ,A1+ / A2-,
RM22UA33MT | - ¦ ,Built in current transformer,
RM22UA33MT | ~/-- 15…150 ¦ ,E1-M / B1-C,
RM22UA33MT | ~/-- 30…300 ¦ ,E2-M / B2-C,
RM22UA33MT | ~/-- 50…500 ¦ ,E3-M / B3-C,
RM22UA33MT | - ¦ ,A1+ / A2-,
RM22UA33MT | - ¦ ,Built in current transformer,
RM22UA33MT | Adjustable 10%...100% of 150V ¦ ,E1-M / B1-C,
RM22UA33MT | Adjustable 10%...100% of 300V ¦ ,E2-M / B2-C,
RM22UA33MT | Adjustable 10%...100% of 500V ¦ ,E3-M / B3-C,
RM22UA33MT | - ¦ ,A1+ / A2-,
RM22UA33MT | - ¦ ,Built in current transformer,
RM22UA33MT | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E1-M / B1-C,
RM22UA33MT | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E2-M / B2-C,
RM22UA33MT | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E3-M / B3-C,
RM22UA33MT | - ¦ ,A1+ / A2-,
RM22UA33MT | - ¦ ,Built in current transformer,
RM22UA33MT | Resistive Voltage Step Down
RM22UA33MT | E1-M, E2-M, E3-M
RM22UA33MT | 50 / 60
RM22UA33MT | 36…77
RM22UA33MT | +/- 10% of full scale value
RM22UA33MT | +/- 0.5%
RM22UA33MT | < 1% over whole range
RM22UA33MT | 0.05% / oC
RM22UA33MT | 30 100
RM22UA33MT | True RMS
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MT
RM22UA33MToutput type | 2 x C/O relay contacts
RM22UA33MToutput terminal | 11-12-14, 21-22-24
RM22UA33MToutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22UA33MToutput logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22UA33MTcontacts material | Cadmium free
RM22UA33MTmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22UA33MTelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22UA33MTelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22UA33MTelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22UA33MTelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22UA33MT[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22UA33MT[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22UA33MTmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22UA33MTmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM22UA33MTmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM22UA33MTminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22UA33MTminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22UA33MTminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UA33MTmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UA33MTmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UA33MTthermal current | 8A ¦ IEC60947-5-1
RM22UA33MTshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22UA33MTshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22UA33MT
RM22UA33MTtime delay type | Yes ¦ ,"OFF" delay,
RM22UA33MTtime delay type | - ¦ ,"ON" delay,
RM22UA33MTtime delay type | - ¦ ,Inhibition,
RM22UA33MTtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay,
RM22UA33MTtime delay range | - ¦ ,"ON" delay,
RM22UA33MTtime delay range | - ¦ ,Inhibition,
RM22UA33MTresponse time | Not specified =< 300ms ¦ ,on crossing the threshold,
RM22UA33MTresponse time
RM22UA33MTresponse time
RM22UA33MTresponse time
RM22UA33MTresponse time
RM22UA33MTpower on delay | 0
RM22UA33MTreset time | 0
RM22UA33MTreset time | through front panel reset,
RM22UA33MTreset time | through input control reset,
RM22UA33MTsetting accuracy of time delay | +/- 10% of full scales
RM22UA33MTrepeat accuracy of time delay | +/- 2%
RM22UA33MTtime delay drift | < 1
RM22UA33MTtime delay drift | < 0.05
RM22UA33MT
RM22UA33MTstatus LED | Dial pointer (Green) R (Amber)
RM22UA33MTlocal signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22UA33MTlocal signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22UA33MTlocal signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22UA33MTlocal signalling | R - ON ¦ ,Output is energized,
RM22UA33MTlocal signalling | R - OFF ¦ ,Output is de-energized,
RM22UA33MTlocal signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22UA33MTlocal signalling
RM22UA33MTlocal signalling
RM22UA33MTlocal signalling
RM22UA33MTlocal signalling
RM22UA33MTlocal signalling
RM22UA33MTlocal signalling
RM22UA33MTlocal signalling
RM22UA33MTlocal signalling
RM22UA33MTlocal signalling
RM22UA33MT
RM22UA33MT | Yes
RM22UA33MT | 1) Will always illuminated when power is supplied to the product
RM22UA33MTdiagnostic button | Output will be de-energized when activated
RM22UA33MT | -
RM22UA33MT | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22UA33MT
RM22UA33MTsafety reliability data | 2,700,000 hours ¦ ,MTTF,
RM22UA33MTsafety reliability data | 290,000 hours ¦ ,B10,
RM22UA33MT | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22UA33MT | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22UA33MT
RM22UB34
RM22UB34standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22UB34product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UB34marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UB34directives | 2014/35/EU
RM22UB34directives | 2014/30/EU
RM22UB34directives | 2011/65/EU
RM22UB34
RM22UB34 | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category,
RM22UB34 | Class C ¦ Germanisher Lloyd,Environmental category,
RM22UB34ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22UB34ambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22UB34relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22UB34 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22UB34vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22UB34shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22UB34bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22UB34seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22UB34IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22UB34IP degree of protection | IP40 ¦ IEC60529,Housing,
RM22UB34IP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22UB34
RM22UB34width | 22.5 x 90 x 73 ¦ ,Width,
RM22UB34height | Height,
RM22UB34depth | Depth,
RM22UB34net weight | 90
RM22UB34mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22UB34mounting support | - ¦ IEC/EN 60715,With socket,
RM22UB34mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UB34Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22UB34Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22UB34connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22UB34connections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22UB34connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22UB34connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UB34tightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22UB34cable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22UB34duty time | 1
RM22UB34
RM22UB34electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22UB34electromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22UB34electromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22UB34electromagnetic compatibility | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22UB34electromagnetic compatibility | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22UB34electromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22UB34electromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22UB34electromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22UB34electromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22UB34electromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
RM22UB34electromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22UB34electromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22UB34electromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22UB34electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22UB34electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22UB34electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22UB34electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22UB34electromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22UB34electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UB34
RM22UB34pollution degree | 3 ¦ IEC60664-1
RM22UB34overvoltage category | 3 ¦ IEC60664-1
RM22UB34circuit group | A1, A2 ¦ ,Supply,Terminal
RM22UB34circuit group | - ¦ ,Input 1,
RM22UB34circuit group | - ¦ ,Input 2,
RM22UB34circuit group | - ¦ ,Input 3,
RM22UB34circuit group | 11,12,14 ¦ ,Output 1,
RM22UB34circuit group | 21,22,24 ¦ ,Output 2,
RM22UB34 | 110…240 AC/DC ¦ ,Supply,Rated
RM22UB34 | - ¦ ,Input 1,Voltage
RM22UB34 | - ¦ ,Input 2,Spec
RM22UB34 | - ¦ ,Input 3,
RM22UB34 | 250V ¦ ,Output 1,
RM22UB34 | 250V ¦ ,Output 2,
RM22UB34[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply,
RM22UB34[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1,
RM22UB34[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2,
RM22UB34[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3,
RM22UB34[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22UB34[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22UB34[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22UB34[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22UB34[Ui] rated insulation voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22UB34[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 1,
RM22UB34[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 2,
RM22UB34[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22UB34[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM22UB34[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22UB34[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22UB34[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22UB34[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22UB34[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22UB34[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22UB34[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22UB34[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22UB34[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 2,Isolated
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Supply / Input 3,Circuit
RM22UB34[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22UB34[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22UB34[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 1,
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Output 2,
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 1,
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Output 2,
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 1,
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3 / Output 2,
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22UB34[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22UB34dielectric strength | - ¦ IEC60255-27,Supply / Input 1,
RM22UB34dielectric strength | - ¦ IEC60255-27,Supply / Input 2,
RM22UB34dielectric strength | - ¦ IEC60255-27,Supply / Input 3,
RM22UB34dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22UB34dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22UB34dielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22UB34dielectric strength | - ¦ IEC60255-27,Input 1 / Output 1,
RM22UB34dielectric strength | - ¦ IEC60255-27,Input 1 / Output 2,
RM22UB34dielectric strength | - ¦ IEC60255-27,Input 2 / Output 1,
RM22UB34dielectric strength | - ¦ IEC60255-27,Input 2 / Output 2,
RM22UB34dielectric strength | - ¦ IEC60255-27,Input 3 / Output 1,
RM22UB34dielectric strength | - ¦ IEC60255-27,Input 3 / Output 2,
RM22UB34dielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22UB34dielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22UB34dielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22UB34insulation resistance | - ¦ IEC60255-27,Supply / Input 1,
RM22UB34insulation resistance | - ¦ IEC60255-27,Supply / Input 2,
RM22UB34insulation resistance | - ¦ IEC60255-27,Supply / Input 3,
RM22UB34insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22UB34insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22UB34insulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22UB34insulation resistance | - ¦ IEC60255-27,Input 1 / Output 1,
RM22UB34insulation resistance | - ¦ IEC60255-27,Input 1 / Output 2,
RM22UB34insulation resistance | - ¦ IEC60255-27,Input 2 / Output 1,
RM22UB34insulation resistance | - ¦ IEC60255-27,Input 2 / Output 2,
RM22UB34insulation resistance | - ¦ IEC60255-27,Input 3 / Output 1,
RM22UB34insulation resistance | - ¦ IEC60255-27,Input 3 / Output 2,
RM22UB34insulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22UB34insulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22UB34insulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22UB34
RM22UB34[Us] rated supply voltage | ~/--110…240
RM22UB34supply voltage limits | ~60…280 (F0) ~80…300 (F1)
RM22UB34polarity
RM22UB34supply frequency | 50 / 60
RM22UB34supply frequency | 45…66
RM22UB34power consumption | ~ 3.5VA, -- 1.5W ~ 5VA, -- 2W
RM22UB34immunity to microbreaks | 20
RM22UB34supply terminal | A1+ - A2-
RM22UB34on-load factor | 1
RM22UB34release of input voltage | -
RM22UB34
RM22UB34 | Selectable threshold ¦ ,Over / undervoltage (windows mode),
RM22UB34 | - ¦ ,Over voltage,
RM22UB34 | - ¦ ,Undervoltage ,
RM22UB34 | ~60…280 (F0) ~60…300 (F1) ~/--80…300 (F1)
RM22UB34 | - ¦ ,E1-M / B1-C,
RM22UB34 | - ¦ ,E2-M / B2-C,
RM22UB34 | - ¦ ,E3-M / B3-C,
RM22UB34 | Not specified ¦ ,A1+ / A2-,
RM22UB34 | - ¦ ,Built in current transformer,
RM22UB34 | - ¦ ,E1-M / B1-C,
RM22UB34 | - ¦ ,E2-M / B2-C,
RM22UB34 | - ¦ ,E3-M / B3-C,
RM22UB34 | - ¦ ,A1+ / A2-,
RM22UB34 | - ¦ ,Built in current transformer,
RM22UB34 | - ¦ ,E1-M / B1-C,
RM22UB34 | - ¦ ,E2-M / B2-C,
RM22UB34 | - ¦ ,E3-M / B3-C,
RM22UB34 | Adjustable <U : 80…300 Adjustable >U : 80…300 ¦ ,A1+ / A2-,
RM22UB34 | - ¦ ,Built in current transformer,
RM22UB34 | - ¦ ,E1-M / B1-C,
RM22UB34 | - ¦ ,E2-M / B2-C,
RM22UB34 | - ¦ ,E3-M / B3-C,
RM22UB34 | Fixed 3% of threshold setting ¦ ,A1+ / A2-,
RM22UB34 | - ¦ ,Built in current transformer,
RM22UB34 | Resistive Voltage Step Down
RM22UB34 | A1+ / A2-
RM22UB34 | 50 / 60
RM22UB34 | 45…66
RM22UB34 | +/- 10% of full scale value
RM22UB34 | +/- 0.5%
RM22UB34 | < 1% over whole range
RM22UB34 | 0.2% / oC
RM22UB34 | 250
RM22UB34 | True RMS
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34
RM22UB34output type | 2 x C/O relay contacts
RM22UB34output terminal | 11-12-14, 21-22-24
RM22UB34output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22UB34output logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22UB34contacts material | Cadmium free
RM22UB34mechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22UB34electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22UB34electrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22UB34electrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22UB34electrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22UB34[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22UB34[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22UB34maximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22UB34maximum switching capacity | 8A ¦ ,Maximum switching current,
RM22UB34maximum switching capacity | - ¦ ,Maximum switching capacity,
RM22UB34minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22UB34minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22UB34minimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UB34maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UB34maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UB34thermal current | 8A ¦ IEC60947-5-1
RM22UB34short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22UB34short circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22UB34
RM22UB34time delay type | Yes ¦ ,"OFF" delay,
RM22UB34time delay type | Yes ¦ ,"ON" delay,
RM22UB34time delay type | - ¦ ,Inhibition,
RM22UB34time delay range | Adjustable 0.1…30 ¦ ,"OFF" delay,
RM22UB34time delay range | Adjustable 0.1…30 ¦ ,"ON" delay,
RM22UB34time delay range | - ¦ ,Inhibition,
RM22UB34response time | Not specified =< 300ms ¦ ,on crossing the threshold,
RM22UB34response time
RM22UB34response time
RM22UB34response time
RM22UB34response time
RM22UB34power on delay | 0
RM22UB34reset time | 0
RM22UB34reset time | through front panel reset,
RM22UB34reset time | through input control reset,
RM22UB34setting accuracy of time delay | +/- 10% of full scales
RM22UB34repeat accuracy of time delay | +/- 2%
RM22UB34time delay drift | < 1
RM22UB34time delay drift | < 0.05
RM22UB34
RM22UB34status LED | Dial pointer (Green) R (Amber)
RM22UB34local signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22UB34local signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22UB34local signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22UB34local signalling | R - ON ¦ ,Output is energized,
RM22UB34local signalling | R - OFF ¦ ,Output is de-energized,
RM22UB34local signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22UB34local signalling
RM22UB34local signalling
RM22UB34local signalling
RM22UB34local signalling
RM22UB34local signalling
RM22UB34local signalling
RM22UB34local signalling
RM22UB34local signalling
RM22UB34local signalling
RM22UB34
RM22UB34 | Yes
RM22UB34 | 1) Will always illuminated when power is supplied to the product
RM22UB34diagnostic button | Output will be de-energized when activated
RM22UB34 | -
RM22UB34 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22UB34
RM22UB34safety reliability data | 3,800,000 hours ¦ ,MTTF,
RM22UB34safety reliability data | 400,000 hours ¦ ,B10,
RM22UB34 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22UB34 | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22UB34
col17
col17standards
col17product certifications
col17marking
col17directives
col17directives
col17directives
col17
col17 | IEC60721-3-3,Climatic category,
col17 | Germanisher Lloyd,Environmental category,
col17ambient air temperature for storage | Storage,
col17ambient air temperature for operation | Operation,
col17relative humidity | IEC60068-2-30,Damp heat,
col17 | IEC60947-5-1,Cyclic Damp Heat Test,
col17vibration resistance | IEC60068-2-6
col17shock resistance | IEC60068-2-27
col17bump resistance | IEC60068-2-29
col17seismic resistance | IEC60068-3-3
col17IP degree of protection | IEC60529,Terminal Block,
col17IP degree of protection | IEC60529,Housing,
col17IP degree of protection | IEC60529,Front Panel,
col17
col17width | Width,
col17height | Height,
col17depth | Depth,
col17net weight
col17mounting support | IEC/EN 60715,Without socket,
col17mounting support | IEC/EN 60715,With socket,
col17mounting position | In relation to normal vertical mounting plane,
col17Minimum distance to adjacent devices | Horizontal,
col17Minimum distance to adjacent devices | Vertical,
col17connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
col17connections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
col17connections - terminals | IEC60947-1,Solid cable (spring terminal),
col17connections - terminals | IEC60947-1,Flexible cable (spring terminal),
col17tightening torque | IEC60947-1,Tightening torque,
col17cable stripping length | Cable stripping length,
col17duty time
col17
col17electromagnetic compatibility | Generic immunity standard,
col17electromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
col17electromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
col17electromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
col17electromagnetic compatibility | IEC61000-4-5,Surge,
col17electromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
col17electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
col17electromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
col17electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
col17electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
col17electromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
col17electromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
col17electromagnetic compatibility | Generic emission standard,
col17electromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
col17electromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
col17electromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
col17electromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
col17electromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
col17electromagnetic compatibility | Germanisher Lloyd,Conducted emission,
col17
col17pollution degree | IEC60664-1
col17overvoltage category | IEC60664-1
col17circuit group | Supply,Terminal
col17circuit group | Input 1,
col17circuit group | Input 2,
col17circuit group | Input 3,
col17circuit group | Output 1,
col17circuit group | Output 2,
col17 | Supply,Rated
col17 | Input 1,Voltage
col17 | Input 2,Spec
col17 | Input 3,
col17 | Output 1,
col17 | Output 2,
col17[Ui] rated insulation voltage | IEC60664-1,Supply,
col17[Ui] rated insulation voltage | IEC60664-1,Input 1,
col17[Ui] rated insulation voltage | IEC60664-1,Input 2,
col17[Ui] rated insulation voltage | IEC60664-1,Input 3,
col17[Ui] rated insulation voltage | IEC60664-1,Output 1,
col17[Ui] rated insulation voltage | IEC60664-1,Output 2,
col17[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
col17[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
col17[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
col17[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
col17[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
col17[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
col17[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
col17[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
col17[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
col17[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
col17[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
col17[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
col17[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
col17[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
col17[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
col17dielectric strength | IEC60255-27,Supply / Input 1,
col17dielectric strength | IEC60255-27,Supply / Input 2,
col17dielectric strength | IEC60255-27,Supply / Input 3,
col17dielectric strength | IEC60255-27,Supply / Output 1,
col17dielectric strength | IEC60255-27,Supply / Output 2,
col17dielectric strength | IEC60255-27,Output 1 / Output 2,
col17dielectric strength | IEC60255-27,Input 1 / Output 1,
col17dielectric strength | IEC60255-27,Input 1 / Output 2,
col17dielectric strength | IEC60255-27,Input 2 / Output 1,
col17dielectric strength | IEC60255-27,Input 2 / Output 2,
col17dielectric strength | IEC60255-27,Input 3 / Output 1,
col17dielectric strength | IEC60255-27,Input 3 / Output 2,
col17dielectric strength | IEC60255-27,Input 1 / Input 2,
col17dielectric strength | IEC60255-27,Input 2 / Input 3,
col17dielectric strength | IEC60255-27,Input 1 / Input 3,
col17insulation resistance | IEC60255-27,Supply / Input 1,
col17insulation resistance | IEC60255-27,Supply / Input 2,
col17insulation resistance | IEC60255-27,Supply / Input 3,
col17insulation resistance | IEC60255-27,Supply / Output 1,
col17insulation resistance | IEC60255-27,Supply / Output 2,
col17insulation resistance | IEC60255-27,Output 1 / Output 2,
col17insulation resistance | IEC60255-27,Input 1 / Output 1,
col17insulation resistance | IEC60255-27,Input 1 / Output 2,
col17insulation resistance | IEC60255-27,Input 2 / Output 1,
col17insulation resistance | IEC60255-27,Input 2 / Output 2,
col17insulation resistance | IEC60255-27,Input 3 / Output 1,
col17insulation resistance | IEC60255-27,Input 3 / Output 2,
col17insulation resistance | IEC60255-27,Input 1 / Input 2,
col17insulation resistance | IEC60255-27,Input 2 / Input 3,
col17insulation resistance | IEC60255-27,Input 1 / Input 3,
col17
col17[Us] rated supply voltage
col17supply voltage limits
col17polarity
col17supply frequency
col17supply frequency
col17power consumption
col17immunity to microbreaks
col17supply terminal
col17on-load factor
col17release of input voltage
col17
col17 | Over / undervoltage (windows mode),
col17 | Over voltage,
col17 | Undervoltage ,
col17
col17 | E1-M / B1-C,
col17 | E2-M / B2-C,
col17 | E3-M / B3-C,
col17 | A1+ / A2-,
col17 | Built in current transformer,
col17 | E1-M / B1-C,
col17 | E2-M / B2-C,
col17 | E3-M / B3-C,
col17 | A1+ / A2-,
col17 | Built in current transformer,
col17 | E1-M / B1-C,
col17 | E2-M / B2-C,
col17 | E3-M / B3-C,
col17 | A1+ / A2-,
col17 | Built in current transformer,
col17 | E1-M / B1-C,
col17 | E2-M / B2-C,
col17 | E3-M / B3-C,
col17 | A1+ / A2-,
col17 | Built in current transformer,
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17
col17output type
col17output terminal
col17output logic | R1 (11-12-14),
col17output logic | R2 (21-22-24),
col17contacts material
col17mechanical durability | IEC61810-1
col17electrical durability | IEC60947-4-1,AC-1,
col17electrical durability | IEC60947-4-1,DC-1,
col17electrical durability | IEC60947-5-1,AC-15,
col17electrical durability | IEC60947-5-1,DC-13,
col17[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col17[Ie] rated operational current | IEC61810-1,Rated switching current,
col17maximum switching capacity | Maximum switching voltage,
col17maximum switching capacity | Maximum switching current,
col17maximum switching capacity | Maximum switching capacity,
col17minimum switching capacity | IEC60947-5-4,Minimum switching voltage,
col17minimum switching capacity | IEC60947-5-4,Minimum switching current,
col17minimum switching capacity | IEC60947-5-4,Minimum switching capacity,
col17maximum voltage drop | IEC62314,Only for solid state output,
col17maximum leakage current | IEC62314,Only for solid state output,
col17thermal current | IEC60947-5-1
col17short circuit protection | IEC60947-5-1,Relay Output by external fuse,
col17short circuit protection | IEC62314,Solid State Output by external fuse,
col17
col17time delay type | "OFF" delay,
col17time delay type | "ON" delay,
col17time delay type | Inhibition,
col17time delay range | "OFF" delay,
col17time delay range | "ON" delay,
col17time delay range | Inhibition,
col17response time | on crossing the threshold,
col17response time
col17response time
col17response time
col17response time
col17power on delay
col17reset time | through Un power reset,
col17reset time | through front panel reset,
col17reset time | through input control reset,
col17setting accuracy of time delay
col17repeat accuracy of time delay
col17time delay drift
col17time delay drift
col17
col17status LED
col17local signalling | Power supply availability,
col17local signalling | Power supply not availability,
col17local signalling | Timing in-progress,
col17local signalling | Output is energized,
col17local signalling | Output is de-energized,
col17local signalling | Range Setting Changes,
col17local signalling
col17local signalling
col17local signalling
col17local signalling
col17local signalling
col17local signalling
col17local signalling
col17local signalling
col17local signalling
col17
col17
col17
col17diagnostic button
col17
col17
col17
col17safety reliability data | MTTF,
col17safety reliability data | B10,
col17 | MTTFd,
col17 | B10d,
col17
col18
col18standards
col18product certifications
col18marking
col18directives
col18directives
col18directives
col18
col18 | IEC60721-3-3,Climatic category,
col18 | Germanisher Lloyd,Environmental category,
col18ambient air temperature for storage | Storage,
col18ambient air temperature for operation | Operation,
col18relative humidity | IEC60068-2-30,Damp heat,
col18 | IEC60947-5-1,Cyclic Damp Heat Test,
col18vibration resistance | IEC60068-2-6
col18shock resistance | IEC60068-2-27
col18bump resistance | IEC60068-2-29
col18seismic resistance | IEC60068-3-3
col18IP degree of protection | IEC60529,Terminal Block,
col18IP degree of protection | IEC60529,Housing,
col18IP degree of protection | IEC60529,Front Panel,
col18
col18width | Width,
col18height | Height,
col18depth | Depth,
col18net weight
col18mounting support | IEC/EN 60715,Without socket,
col18mounting support | IEC/EN 60715,With socket,
col18mounting position | In relation to normal vertical mounting plane,
col18Minimum distance to adjacent devices | Horizontal,
col18Minimum distance to adjacent devices | Vertical,
col18connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
col18connections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
col18connections - terminals | IEC60947-1,Solid cable (spring terminal),
col18connections - terminals | IEC60947-1,Flexible cable (spring terminal),
col18tightening torque | IEC60947-1,Tightening torque,
col18cable stripping length | Cable stripping length,
col18duty time
col18
col18electromagnetic compatibility | Generic immunity standard,
col18electromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
col18electromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
col18electromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
col18electromagnetic compatibility | IEC61000-4-5,Surge,
col18electromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
col18electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
col18electromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
col18electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
col18electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
col18electromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
col18electromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
col18electromagnetic compatibility | Generic emission standard,
col18electromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
col18electromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
col18electromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
col18electromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
col18electromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
col18electromagnetic compatibility | Germanisher Lloyd,Conducted emission,
col18
col18pollution degree | IEC60664-1
col18overvoltage category | IEC60664-1
col18circuit group | Supply,Terminal
col18circuit group | Input 1,
col18circuit group | Input 2,
col18circuit group | Input 3,
col18circuit group | Output 1,
col18circuit group | Output 2,
col18 | Supply,Rated
col18 | Input 1,Voltage
col18 | Input 2,Spec
col18 | Input 3,
col18 | Output 1,
col18 | Output 2,
col18[Ui] rated insulation voltage | IEC60664-1,Supply,
col18[Ui] rated insulation voltage | IEC60664-1,Input 1,
col18[Ui] rated insulation voltage | IEC60664-1,Input 2,
col18[Ui] rated insulation voltage | IEC60664-1,Input 3,
col18[Ui] rated insulation voltage | IEC60664-1,Output 1,
col18[Ui] rated insulation voltage | IEC60664-1,Output 2,
col18[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
col18[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
col18[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
col18[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
col18[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
col18[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
col18[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
col18[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
col18[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
col18[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
col18[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
col18[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
col18[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
col18[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
col18[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
col18dielectric strength | IEC60255-27,Supply / Input 1,
col18dielectric strength | IEC60255-27,Supply / Input 2,
col18dielectric strength | IEC60255-27,Supply / Input 3,
col18dielectric strength | IEC60255-27,Supply / Output 1,
col18dielectric strength | IEC60255-27,Supply / Output 2,
col18dielectric strength | IEC60255-27,Output 1 / Output 2,
col18dielectric strength | IEC60255-27,Input 1 / Output 1,
col18dielectric strength | IEC60255-27,Input 1 / Output 2,
col18dielectric strength | IEC60255-27,Input 2 / Output 1,
col18dielectric strength | IEC60255-27,Input 2 / Output 2,
col18dielectric strength | IEC60255-27,Input 3 / Output 1,
col18dielectric strength | IEC60255-27,Input 3 / Output 2,
col18dielectric strength | IEC60255-27,Input 1 / Input 2,
col18dielectric strength | IEC60255-27,Input 2 / Input 3,
col18dielectric strength | IEC60255-27,Input 1 / Input 3,
col18insulation resistance | IEC60255-27,Supply / Input 1,
col18insulation resistance | IEC60255-27,Supply / Input 2,
col18insulation resistance | IEC60255-27,Supply / Input 3,
col18insulation resistance | IEC60255-27,Supply / Output 1,
col18insulation resistance | IEC60255-27,Supply / Output 2,
col18insulation resistance | IEC60255-27,Output 1 / Output 2,
col18insulation resistance | IEC60255-27,Input 1 / Output 1,
col18insulation resistance | IEC60255-27,Input 1 / Output 2,
col18insulation resistance | IEC60255-27,Input 2 / Output 1,
col18insulation resistance | IEC60255-27,Input 2 / Output 2,
col18insulation resistance | IEC60255-27,Input 3 / Output 1,
col18insulation resistance | IEC60255-27,Input 3 / Output 2,
col18insulation resistance | IEC60255-27,Input 1 / Input 2,
col18insulation resistance | IEC60255-27,Input 2 / Input 3,
col18insulation resistance | IEC60255-27,Input 1 / Input 3,
col18
col18[Us] rated supply voltage
col18supply voltage limits
col18polarity
col18supply frequency
col18supply frequency
col18power consumption
col18immunity to microbreaks
col18supply terminal
col18on-load factor
col18release of input voltage
col18
col18 | Over / undervoltage (windows mode),
col18 | Over voltage,
col18 | Undervoltage ,
col18
col18 | E1-M / B1-C,
col18 | E2-M / B2-C,
col18 | E3-M / B3-C,
col18 | A1+ / A2-,
col18 | Built in current transformer,
col18 | E1-M / B1-C,
col18 | E2-M / B2-C,
col18 | E3-M / B3-C,
col18 | A1+ / A2-,
col18 | Built in current transformer,
col18 | E1-M / B1-C,
col18 | E2-M / B2-C,
col18 | E3-M / B3-C,
col18 | A1+ / A2-,
col18 | Built in current transformer,
col18 | E1-M / B1-C,
col18 | E2-M / B2-C,
col18 | E3-M / B3-C,
col18 | A1+ / A2-,
col18 | Built in current transformer,
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18
col18output type
col18output terminal
col18output logic | R1 (11-12-14),
col18output logic | R2 (21-22-24),
col18contacts material
col18mechanical durability | IEC61810-1
col18electrical durability | IEC60947-4-1,AC-1,
col18electrical durability | IEC60947-4-1,DC-1,
col18electrical durability | IEC60947-5-1,AC-15,
col18electrical durability | IEC60947-5-1,DC-13,
col18[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col18[Ie] rated operational current | IEC61810-1,Rated switching current,
col18maximum switching capacity | Maximum switching voltage,
col18maximum switching capacity | Maximum switching current,
col18maximum switching capacity | Maximum switching capacity,
col18minimum switching capacity | IEC60947-5-4,Minimum switching voltage,
col18minimum switching capacity | IEC60947-5-4,Minimum switching current,
col18minimum switching capacity | IEC60947-5-4,Minimum switching capacity,
col18maximum voltage drop | IEC62314,Only for solid state output,
col18maximum leakage current | IEC62314,Only for solid state output,
col18thermal current | IEC60947-5-1
col18short circuit protection | IEC60947-5-1,Relay Output by external fuse,
col18short circuit protection | IEC62314,Solid State Output by external fuse,
col18
col18time delay type | "OFF" delay,
col18time delay type | "ON" delay,
col18time delay type | Inhibition,
col18time delay range | "OFF" delay,
col18time delay range | "ON" delay,
col18time delay range | Inhibition,
col18response time | on crossing the threshold,
col18response time
col18response time
col18response time
col18response time
col18power on delay
col18reset time | through Un power reset,
col18reset time | through front panel reset,
col18reset time | through input control reset,
col18setting accuracy of time delay
col18repeat accuracy of time delay
col18time delay drift
col18time delay drift
col18
col18status LED
col18local signalling | Power supply availability,
col18local signalling | Power supply not availability,
col18local signalling | Timing in-progress,
col18local signalling | Output is energized,
col18local signalling | Output is de-energized,
col18local signalling | Range Setting Changes,
col18local signalling
col18local signalling
col18local signalling
col18local signalling
col18local signalling
col18local signalling
col18local signalling
col18local signalling
col18local signalling
col18
col18
col18
col18diagnostic button
col18
col18
col18
col18safety reliability data | MTTF,
col18safety reliability data | B10,
col18 | MTTFd,
col18 | B10d,
col18
col19
col19standards
col19product certifications
col19marking
col19directives
col19directives
col19directives
col19
col19 | IEC60721-3-3,Climatic category,
col19 | Germanisher Lloyd,Environmental category,
col19ambient air temperature for storage | Storage,
col19ambient air temperature for operation | Operation,
col19relative humidity | IEC60068-2-30,Damp heat,
col19 | IEC60947-5-1,Cyclic Damp Heat Test,
col19vibration resistance | IEC60068-2-6
col19shock resistance | IEC60068-2-27
col19bump resistance | IEC60068-2-29
col19seismic resistance | IEC60068-3-3
col19IP degree of protection | IEC60529,Terminal Block,
col19IP degree of protection | IEC60529,Housing,
col19IP degree of protection | IEC60529,Front Panel,
col19
col19width | Width,
col19height | Height,
col19depth | Depth,
col19net weight
col19mounting support | IEC/EN 60715,Without socket,
col19mounting support | IEC/EN 60715,With socket,
col19mounting position | In relation to normal vertical mounting plane,
col19Minimum distance to adjacent devices | Horizontal,
col19Minimum distance to adjacent devices | Vertical,
col19connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
col19connections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
col19connections - terminals | IEC60947-1,Solid cable (spring terminal),
col19connections - terminals | IEC60947-1,Flexible cable (spring terminal),
col19tightening torque | IEC60947-1,Tightening torque,
col19cable stripping length | Cable stripping length,
col19duty time
col19
col19electromagnetic compatibility | Generic immunity standard,
col19electromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
col19electromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
col19electromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
col19electromagnetic compatibility | IEC61000-4-5,Surge,
col19electromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
col19electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
col19electromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
col19electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
col19electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
col19electromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
col19electromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
col19electromagnetic compatibility | Generic emission standard,
col19electromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
col19electromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
col19electromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
col19electromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
col19electromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
col19electromagnetic compatibility | Germanisher Lloyd,Conducted emission,
col19
col19pollution degree | IEC60664-1
col19overvoltage category | IEC60664-1
col19circuit group | Supply,Terminal
col19circuit group | Input 1,
col19circuit group | Input 2,
col19circuit group | Input 3,
col19circuit group | Output 1,
col19circuit group | Output 2,
col19 | Supply,Rated
col19 | Input 1,Voltage
col19 | Input 2,Spec
col19 | Input 3,
col19 | Output 1,
col19 | Output 2,
col19[Ui] rated insulation voltage | IEC60664-1,Supply,
col19[Ui] rated insulation voltage | IEC60664-1,Input 1,
col19[Ui] rated insulation voltage | IEC60664-1,Input 2,
col19[Ui] rated insulation voltage | IEC60664-1,Input 3,
col19[Ui] rated insulation voltage | IEC60664-1,Output 1,
col19[Ui] rated insulation voltage | IEC60664-1,Output 2,
col19[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
col19[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
col19[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
col19[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
col19[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
col19[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
col19[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
col19[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
col19[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
col19[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
col19[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
col19[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
col19[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
col19[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
col19[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
col19dielectric strength | IEC60255-27,Supply / Input 1,
col19dielectric strength | IEC60255-27,Supply / Input 2,
col19dielectric strength | IEC60255-27,Supply / Input 3,
col19dielectric strength | IEC60255-27,Supply / Output 1,
col19dielectric strength | IEC60255-27,Supply / Output 2,
col19dielectric strength | IEC60255-27,Output 1 / Output 2,
col19dielectric strength | IEC60255-27,Input 1 / Output 1,
col19dielectric strength | IEC60255-27,Input 1 / Output 2,
col19dielectric strength | IEC60255-27,Input 2 / Output 1,
col19dielectric strength | IEC60255-27,Input 2 / Output 2,
col19dielectric strength | IEC60255-27,Input 3 / Output 1,
col19dielectric strength | IEC60255-27,Input 3 / Output 2,
col19dielectric strength | IEC60255-27,Input 1 / Input 2,
col19dielectric strength | IEC60255-27,Input 2 / Input 3,
col19dielectric strength | IEC60255-27,Input 1 / Input 3,
col19insulation resistance | IEC60255-27,Supply / Input 1,
col19insulation resistance | IEC60255-27,Supply / Input 2,
col19insulation resistance | IEC60255-27,Supply / Input 3,
col19insulation resistance | IEC60255-27,Supply / Output 1,
col19insulation resistance | IEC60255-27,Supply / Output 2,
col19insulation resistance | IEC60255-27,Output 1 / Output 2,
col19insulation resistance | IEC60255-27,Input 1 / Output 1,
col19insulation resistance | IEC60255-27,Input 1 / Output 2,
col19insulation resistance | IEC60255-27,Input 2 / Output 1,
col19insulation resistance | IEC60255-27,Input 2 / Output 2,
col19insulation resistance | IEC60255-27,Input 3 / Output 1,
col19insulation resistance | IEC60255-27,Input 3 / Output 2,
col19insulation resistance | IEC60255-27,Input 1 / Input 2,
col19insulation resistance | IEC60255-27,Input 2 / Input 3,
col19insulation resistance | IEC60255-27,Input 1 / Input 3,
col19
col19[Us] rated supply voltage
col19supply voltage limits
col19polarity
col19supply frequency
col19supply frequency
col19power consumption
col19immunity to microbreaks
col19supply terminal
col19on-load factor
col19release of input voltage
col19
col19 | Over / undervoltage (windows mode),
col19 | Over voltage,
col19 | Undervoltage ,
col19
col19 | E1-M / B1-C,
col19 | E2-M / B2-C,
col19 | E3-M / B3-C,
col19 | A1+ / A2-,
col19 | Built in current transformer,
col19 | E1-M / B1-C,
col19 | E2-M / B2-C,
col19 | E3-M / B3-C,
col19 | A1+ / A2-,
col19 | Built in current transformer,
col19 | E1-M / B1-C,
col19 | E2-M / B2-C,
col19 | E3-M / B3-C,
col19 | A1+ / A2-,
col19 | Built in current transformer,
col19 | E1-M / B1-C,
col19 | E2-M / B2-C,
col19 | E3-M / B3-C,
col19 | A1+ / A2-,
col19 | Built in current transformer,
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19
col19output type
col19output terminal
col19output logic | R1 (11-12-14),
col19output logic | R2 (21-22-24),
col19contacts material
col19mechanical durability | IEC61810-1
col19electrical durability | IEC60947-4-1,AC-1,
col19electrical durability | IEC60947-4-1,DC-1,
col19electrical durability | IEC60947-5-1,AC-15,
col19electrical durability | IEC60947-5-1,DC-13,
col19[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col19[Ie] rated operational current | IEC61810-1,Rated switching current,
col19maximum switching capacity | Maximum switching voltage,
col19maximum switching capacity | Maximum switching current,
col19maximum switching capacity | Maximum switching capacity,
col19minimum switching capacity | IEC60947-5-4,Minimum switching voltage,
col19minimum switching capacity | IEC60947-5-4,Minimum switching current,
col19minimum switching capacity | IEC60947-5-4,Minimum switching capacity,
col19maximum voltage drop | IEC62314,Only for solid state output,
col19maximum leakage current | IEC62314,Only for solid state output,
col19thermal current | IEC60947-5-1
col19short circuit protection | IEC60947-5-1,Relay Output by external fuse,
col19short circuit protection | IEC62314,Solid State Output by external fuse,
col19
col19time delay type | "OFF" delay,
col19time delay type | "ON" delay,
col19time delay type | Inhibition,
col19time delay range | "OFF" delay,
col19time delay range | "ON" delay,
col19time delay range | Inhibition,
col19response time | on crossing the threshold,
col19response time
col19response time
col19response time
col19response time
col19power on delay
col19reset time | through Un power reset,
col19reset time | through front panel reset,
col19reset time | through input control reset,
col19setting accuracy of time delay
col19repeat accuracy of time delay
col19time delay drift
col19time delay drift
col19
col19status LED
col19local signalling | Power supply availability,
col19local signalling | Power supply not availability,
col19local signalling | Timing in-progress,
col19local signalling | Output is energized,
col19local signalling | Output is de-energized,
col19local signalling | Range Setting Changes,
col19local signalling
col19local signalling
col19local signalling
col19local signalling
col19local signalling
col19local signalling
col19local signalling
col19local signalling
col19local signalling
col19
col19
col19
col19diagnostic button
col19
col19
col19
col19safety reliability data | MTTF,
col19safety reliability data | B10,
col19 | MTTFd,
col19 | B10d,
col19
Competitor Spec Reference
Competitor Spec Referencestandards
Competitor Spec Referenceproduct certifications
Competitor Spec Referencemarking
Competitor Spec Referencedirectives
Competitor Spec Referencedirectives
Competitor Spec Referencedirectives
Competitor Spec Reference
Competitor Spec Reference | IEC60721-3-3,Climatic category,
Competitor Spec Reference | Germanisher Lloyd,Environmental category,
Competitor Spec Referenceambient air temperature for storage | Storage,
Competitor Spec Referenceambient air temperature for operation | Operation,
Competitor Spec Referencerelative humidity | IEC60068-2-30,Damp heat,
Competitor Spec Reference | IEC60947-5-1,Cyclic Damp Heat Test,
Competitor Spec Referencevibration resistance | IEC60068-2-6
Competitor Spec Referenceshock resistance | IEC60068-2-27
Competitor Spec Referencebump resistance | IEC60068-2-29
Competitor Spec Referenceseismic resistance | IEC60068-3-3
Competitor Spec ReferenceIP degree of protection | IEC60529,Terminal Block,
Competitor Spec ReferenceIP degree of protection | IEC60529,Housing,
Competitor Spec ReferenceIP degree of protection | IEC60529,Front Panel,
Competitor Spec Reference
Competitor Spec Referencewidth | Width,
Competitor Spec Referenceheight | Height,
Competitor Spec Referencedepth | Depth,
Competitor Spec Referencenet weight
Competitor Spec Referencemounting support | IEC/EN 60715,Without socket,
Competitor Spec Referencemounting support | IEC/EN 60715,With socket,
Competitor Spec Referencemounting position | In relation to normal vertical mounting plane,
Competitor Spec ReferenceMinimum distance to adjacent devices | Horizontal,
Competitor Spec ReferenceMinimum distance to adjacent devices | Vertical,
Competitor Spec Referenceconnections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
Competitor Spec Referenceconnections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
Competitor Spec Referenceconnections - terminals | IEC60947-1,Solid cable (spring terminal),
Competitor Spec Referenceconnections - terminals | IEC60947-1,Flexible cable (spring terminal),
Competitor Spec Referencetightening torque | IEC60947-1,Tightening torque,
Competitor Spec Referencecable stripping length | Cable stripping length,
Competitor Spec Referenceduty time
Competitor Spec Reference
Competitor Spec Referenceelectromagnetic compatibility | Generic immunity standard,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-5,Surge,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
Competitor Spec Referenceelectromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
Competitor Spec Referenceelectromagnetic compatibility | Generic emission standard,
Competitor Spec Referenceelectromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
Competitor Spec Referenceelectromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
Competitor Spec Referenceelectromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
Competitor Spec Referenceelectromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
Competitor Spec Referenceelectromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
Competitor Spec Referenceelectromagnetic compatibility | Germanisher Lloyd,Conducted emission,
Competitor Spec Reference
Competitor Spec Referencepollution degree | IEC60664-1
Competitor Spec Referenceovervoltage category | IEC60664-1
Competitor Spec Referencecircuit group | Supply,Terminal
Competitor Spec Referencecircuit group | Input 1,
Competitor Spec Referencecircuit group | Input 2,
Competitor Spec Referencecircuit group | Input 3,
Competitor Spec Referencecircuit group | Output 1,
Competitor Spec Referencecircuit group | Output 2,
Competitor Spec Reference | Supply,Rated
Competitor Spec Reference | Input 1,Voltage
Competitor Spec Reference | Input 2,Spec
Competitor Spec Reference | Input 3,
Competitor Spec Reference | Output 1,
Competitor Spec Reference | Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 3,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Input 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Input 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Input 3,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Output 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Output 1 / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 1 / Output 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 1 / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 2 / Output 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 2 / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 3 / Output 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 3 / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 1 / Input 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 2 / Input 3,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 1 / Input 3,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Input 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Input 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Input 3,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Output 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Output 1 / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 1 / Output 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 1 / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 2 / Output 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 2 / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 3 / Output 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 3 / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 1 / Input 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 2 / Input 3,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 1 / Input 3,
Competitor Spec Reference
Competitor Spec Reference[Us] rated supply voltage
Competitor Spec Referencesupply voltage limits
Competitor Spec Referencepolarity
Competitor Spec Referencesupply frequency
Competitor Spec Referencesupply frequency
Competitor Spec Referencepower consumption
Competitor Spec Referenceimmunity to microbreaks
Competitor Spec Referencesupply terminal
Competitor Spec Referenceon-load factor
Competitor Spec Referencerelease of input voltage
Competitor Spec Reference
Competitor Spec Reference | Over / undervoltage (windows mode),
Competitor Spec Reference | Over voltage,
Competitor Spec Reference | Undervoltage ,
Competitor Spec Reference
Competitor Spec Reference | E1-M / B1-C,
Competitor Spec Reference | E2-M / B2-C,
Competitor Spec Reference | E3-M / B3-C,
Competitor Spec Reference | A1+ / A2-,
Competitor Spec Reference | Built in current transformer,
Competitor Spec Reference | E1-M / B1-C,
Competitor Spec Reference | E2-M / B2-C,
Competitor Spec Reference | E3-M / B3-C,
Competitor Spec Reference | A1+ / A2-,
Competitor Spec Reference | Built in current transformer,
Competitor Spec Reference | E1-M / B1-C,
Competitor Spec Reference | E2-M / B2-C,
Competitor Spec Reference | E3-M / B3-C,
Competitor Spec Reference | A1+ / A2-,
Competitor Spec Reference | Built in current transformer,
Competitor Spec Reference | E1-M / B1-C,
Competitor Spec Reference | E2-M / B2-C,
Competitor Spec Reference | E3-M / B3-C,
Competitor Spec Reference | A1+ / A2-,
Competitor Spec Reference | Built in current transformer,
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Referenceoutput type
Competitor Spec Referenceoutput terminal
Competitor Spec Referenceoutput logic | R1 (11-12-14),
Competitor Spec Referenceoutput logic | R2 (21-22-24),
Competitor Spec Referencecontacts material
Competitor Spec Referencemechanical durability | IEC61810-1
Competitor Spec Referenceelectrical durability | IEC60947-4-1,AC-1,
Competitor Spec Referenceelectrical durability | IEC60947-4-1,DC-1,
Competitor Spec Referenceelectrical durability | IEC60947-5-1,AC-15,
Competitor Spec Referenceelectrical durability | IEC60947-5-1,DC-13,
Competitor Spec Reference[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
Competitor Spec Reference[Ie] rated operational current | IEC61810-1,Rated switching current,
Competitor Spec Referencemaximum switching capacity | Maximum switching voltage,
Competitor Spec Referencemaximum switching capacity | Maximum switching current,
Competitor Spec Referencemaximum switching capacity | Maximum switching capacity,
Competitor Spec Referenceminimum switching capacity | IEC60947-5-4,Minimum switching voltage,
Competitor Spec Referenceminimum switching capacity | IEC60947-5-4,Minimum switching current,
Competitor Spec Referenceminimum switching capacity | IEC60947-5-4,Minimum switching capacity,
Competitor Spec Referencemaximum voltage drop | IEC62314,Only for solid state output,
Competitor Spec Referencemaximum leakage current | IEC62314,Only for solid state output,
Competitor Spec Referencethermal current | IEC60947-5-1
Competitor Spec Referenceshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
Competitor Spec Referenceshort circuit protection | IEC62314,Solid State Output by external fuse,
Competitor Spec Reference
Competitor Spec Referencetime delay type | "OFF" delay,
Competitor Spec Referencetime delay type | "ON" delay,
Competitor Spec Referencetime delay type | Inhibition,
Competitor Spec Referencetime delay range | "OFF" delay,
Competitor Spec Referencetime delay range | "ON" delay,
Competitor Spec Referencetime delay range | Inhibition,
Competitor Spec Referenceresponse time | on crossing the threshold,
Competitor Spec Referenceresponse time
Competitor Spec Referenceresponse time
Competitor Spec Referenceresponse time
Competitor Spec Referenceresponse time
Competitor Spec Referencepower on delay
Competitor Spec Referencereset time | through Un power reset,
Competitor Spec Referencereset time | through front panel reset,
Competitor Spec Referencereset time | through input control reset,
Competitor Spec Referencesetting accuracy of time delay
Competitor Spec Referencerepeat accuracy of time delay
Competitor Spec Referencetime delay drift
Competitor Spec Referencetime delay drift
Competitor Spec Reference
Competitor Spec Referencestatus LED
Competitor Spec Referencelocal signalling | Power supply availability,
Competitor Spec Referencelocal signalling | Power supply not availability,
Competitor Spec Referencelocal signalling | Timing in-progress,
Competitor Spec Referencelocal signalling | Output is energized,
Competitor Spec Referencelocal signalling | Output is de-energized,
Competitor Spec Referencelocal signalling | Range Setting Changes,
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Referencediagnostic button
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Referencesafety reliability data | MTTF,
Competitor Spec Referencesafety reliability data | B10,
Competitor Spec Reference | MTTFd,
Competitor Spec Reference | B10d,
Competitor Spec Reference
RM35UA11MW
RM35UA11MWstandards | EN60255-6, IEC60255-6
RM35UA11MWproduct certifications | UL, CSA, GL, C-Tick, GOST
RM35UA11MWmarking | UL, CSA, GL, C-Tick, GOST, CE
RM35UA11MWdirectives | No 73/23/EEC + 93/68/EEC
RM35UA11MWdirectives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
RM35UA11MWdirectives | 2002/95/EC
RM35UA11MW
RM35UA11MW | Not specified ¦ IEC60721-3-3,Climatic category,
RM35UA11MW | Germanisher Lloyd,Environmental category,
RM35UA11MWambient air temperature for storage | -40…+70 ¦ ,Storage,
RM35UA11MWambient air temperature for operation | -20…+50 ¦ ,Operation,
RM35UA11MWrelative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM35UA11MW | IEC60947-5-1,Cyclic Damp Heat Test,
RM35UA11MWvibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM35UA11MWshock resistance | 5 gn ¦ IEC60068-2-27
RM35UA11MWbump resistance | IEC60068-2-29
RM35UA11MWseismic resistance | IEC60068-3-3
RM35UA11MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM35UA11MWIP degree of protection | IP30 ¦ IEC60529,Housing,
RM35UA11MWIP degree of protection | IEC60529,Front Panel,
RM35UA11MW
RM35UA11MWwidth | 35 x 90 x 72 ¦ ,Width,
RM35UA11MWheight | Height,
RM35UA11MWdepth | Depth,
RM35UA11MWnet weight | 130
RM35UA11MWmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM35UA11MWmounting support | - ¦ IEC/EN 60715,With socket,
RM35UA11MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35UA11MWMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM35UA11MWMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM35UA11MWconnections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35UA11MWconnections - terminals | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35UA11MWconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM35UA11MWconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35UA11MWtightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM35UA11MWcable stripping length | Not specified ¦ ,Cable stripping length,
RM35UA11MWduty time | Not specified
RM35UA11MW
RM35UA11MWelectromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard,
RM35UA11MWelectromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM35UA11MWelectromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM35UA11MWelectromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM35UA11MWelectromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM35UA11MWelectromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM35UA11MWelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM35UA11MWelectromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35UA11MWelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM35UA11MWelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM35UA11MWelectromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM35UA11MWelectromagnetic compatibility | · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35UA11MWelectromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM35UA11MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35UA11MWelectromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35UA11MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM35UA11MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35UA11MWelectromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35UA11MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35UA11MW
RM35UA11MWpollution degree | 3 ¦ IEC60664-1
RM35UA11MWovervoltage category | III ¦ IEC60664-1
RM35UA11MWcircuit group | Supply,Terminal
RM35UA11MWcircuit group | Input 1,
RM35UA11MWcircuit group | Input 2,
RM35UA11MWcircuit group | Input 3,
RM35UA11MWcircuit group | Output 1,
RM35UA11MWcircuit group | 600 ¦ ,Output 2,
RM35UA11MW | 600 ¦ ,Supply,Rated
RM35UA11MW | 600 ¦ ,Input 1,Voltage
RM35UA11MW | Input 2,Spec
RM35UA11MW | Input 3,
RM35UA11MW | Output 1,
RM35UA11MW | Output 2,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Supply,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM35UA11MW[Ui] rated insulation voltage | 4 ¦ IEC60664-1,Output 1,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM35UA11MW[Ui] rated insulation voltage | 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM35UA11MW[Uimp] rated impulse withstand voltage | > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM35UA11MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM35UA11MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM35UA11MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM35UA11MWdielectric strength | IEC60255-27,Supply / Output 1,
RM35UA11MWdielectric strength | IEC60255-27,Supply / Output 2,
RM35UA11MWdielectric strength | IEC60255-27,Output 1 / Output 2,
RM35UA11MWdielectric strength | IEC60255-27,Input 1 / Output 1,
RM35UA11MWdielectric strength | IEC60255-27,Input 1 / Output 2,
RM35UA11MWdielectric strength | IEC60255-27,Input 2 / Output 1,
RM35UA11MWdielectric strength | IEC60255-27,Input 2 / Output 2,
RM35UA11MWdielectric strength | IEC60255-27,Input 3 / Output 1,
RM35UA11MWdielectric strength | IEC60255-27,Input 3 / Output 2,
RM35UA11MWdielectric strength | IEC60255-27,Input 1 / Input 2,
RM35UA11MWdielectric strength | IEC60255-27,Input 2 / Input 3,
RM35UA11MWdielectric strength | IEC60255-27,Input 1 / Input 3,
RM35UA11MWinsulation resistance | IEC60255-27,Supply / Input 1,
RM35UA11MWinsulation resistance | IEC60255-27,Supply / Input 2,
RM35UA11MWinsulation resistance | IEC60255-27,Supply / Input 3,
RM35UA11MWinsulation resistance | IEC60255-27,Supply / Output 1,
RM35UA11MWinsulation resistance | IEC60255-27,Supply / Output 2,
RM35UA11MWinsulation resistance | IEC60255-27,Output 1 / Output 2,
RM35UA11MWinsulation resistance | IEC60255-27,Input 1 / Output 1,
RM35UA11MWinsulation resistance | IEC60255-27,Input 1 / Output 2,
RM35UA11MWinsulation resistance | IEC60255-27,Input 2 / Output 1,
RM35UA11MWinsulation resistance | IEC60255-27,Input 2 / Output 2,
RM35UA11MWinsulation resistance | IEC60255-27,Input 3 / Output 1,
RM35UA11MWinsulation resistance | IEC60255-27,Input 3 / Output 2,
RM35UA11MWinsulation resistance | IEC60255-27,Input 1 / Input 2,
RM35UA11MWinsulation resistance | IEC60255-27,Input 2 / Input 3,
RM35UA11MWinsulation resistance | IEC60255-27,Input 1 / Input 3,
RM35UA11MW
RM35UA11MW[Us] rated supply voltage | ~/-- 24…240
RM35UA11MWsupply voltage limits | ~/-- 20.4…264
RM35UA11MWpolarity
RM35UA11MWsupply frequency | 50 / 60
RM35UA11MWsupply frequency | 45…66
RM35UA11MWpower consumption | ~ 3.5VA, -- 0.6W
RM35UA11MWimmunity to microbreaks | 10
RM35UA11MWsupply terminal | A1-A2
RM35UA11MWon-load factor
RM35UA11MWrelease of input voltage
RM35UA11MW
RM35UA11MW | - ¦ ,Over / undervoltage (windows mode),
RM35UA11MW | Selectable with memory / without memory ¦ ,Over voltage,
RM35UA11MW | Selectable with memory / without memory ¦ ,Undervoltage ,
RM35UA11MW | ~/-- 0.05…5
RM35UA11MW | 5 ¦ ,E1-M / B1-C,
RM35UA11MW | 30 ¦ ,E2-M / B2-C,
RM35UA11MW | 50 ¦ ,E3-M / B3-C,
RM35UA11MW | A1+ / A2-,
RM35UA11MW | - ¦ ,Built in current transformer,
RM35UA11MW | ~/-- 0.05…0.5 ¦ ,E1-M / B1-C,
RM35UA11MW | ~/-- 0.3…3 ¦ ,E2-M / B2-C,
RM35UA11MW | ~/-- 0.5…5 ¦ ,E3-M / B3-C,
RM35UA11MW | A1+ / A2-,
RM35UA11MW | - ¦ ,Built in current transformer,
RM35UA11MW | Adjustable 10%...100% of 0.5V ¦ ,E1-M / B1-C,
RM35UA11MW | Adjustable 10%...100% of 3V ¦ ,E2-M / B2-C,
RM35UA11MW | Adjustable 10%...100% of 5V ¦ ,E3-M / B3-C,
RM35UA11MW | A1+ / A2-,
RM35UA11MW | - ¦ ,Built in current transformer,
RM35UA11MW | Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C,
RM35UA11MW | Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C,
RM35UA11MW | Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C,
RM35UA11MW | A1+ / A2-,
RM35UA11MW | - ¦ ,Built in current transformer,
RM35UA11MW | Resistive Voltage Step Down
RM35UA11MW | E1-M, E2-M, E3-M
RM35UA11MW | 50 / 60
RM35UA11MW | 36…77
RM35UA11MW | +/- 10% of full scale value
RM35UA11MW | +/- 0.5%
RM35UA11MW | < 1% over whole range
RM35UA11MW | 0.05% / oC
RM35UA11MW | 30
RM35UA11MW | True RMS
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MWoutput type | 2 x C/O relay contacts
RM35UA11MWoutput terminal | 11-12-14, 21-22-24
RM35UA11MWoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM35UA11MWoutput logic | R2 (21-22-24),
RM35UA11MWcontacts material | Cadmium-free
RM35UA11MWmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM35UA11MWelectrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1,
RM35UA11MWelectrical durability | IEC60947-4-1,DC-1,
RM35UA11MWelectrical durability | IEC60947-5-1,AC-15,
RM35UA11MWelectrical durability | IEC60947-5-1,DC-13,
RM35UA11MW[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM35UA11MW[Ie] rated operational current | IEC61810-1,Rated switching current,
RM35UA11MWmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM35UA11MWmaximum switching capacity | 5 ¦ ,Maximum switching current,
RM35UA11MWmaximum switching capacity | 1250 ¦ ,Maximum switching capacity,
RM35UA11MWminimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
RM35UA11MWminimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM35UA11MWminimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM35UA11MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35UA11MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35UA11MWthermal current | IEC60947-5-1
RM35UA11MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM35UA11MWshort circuit protection | IEC62314,Solid State Output by external fuse,
RM35UA11MW
RM35UA11MWtime delay type | · ¦ ,"OFF" delay,
RM35UA11MWtime delay type | - ¦ ,"ON" delay,
RM35UA11MWtime delay type | - ¦ ,Inhibition,
RM35UA11MWtime delay range | Adjustable 0.3…30 ¦ ,"OFF" delay,
RM35UA11MWtime delay range | - ¦ ,"ON" delay,
RM35UA11MWtime delay range | - ¦ ,Inhibition,
RM35UA11MWresponse time | Not specified ¦ ,on crossing the threshold,
RM35UA11MWresponse time
RM35UA11MWresponse time
RM35UA11MWresponse time
RM35UA11MWresponse time
RM35UA11MWpower on delay | 0
RM35UA11MWreset time | 0
RM35UA11MWreset time | through front panel reset,
RM35UA11MWreset time | through input control reset,
RM35UA11MWsetting accuracy of time delay | +/- 10% of full scales
RM35UA11MWrepeat accuracy of time delay | +/- 2%
RM35UA11MWtime delay drift | Not specified
RM35UA11MWtime delay drift | Not specified
RM35UA11MW
RM35UA11MWstatus LED
RM35UA11MWlocal signalling | Power supply availability,
RM35UA11MWlocal signalling | Power supply not availability,
RM35UA11MWlocal signalling | Timing in-progress,
RM35UA11MWlocal signalling | Output is energized,
RM35UA11MWlocal signalling | Output is de-energized,
RM35UA11MWlocal signalling | Range Setting Changes,
RM35UA11MWlocal signalling
RM35UA11MWlocal signalling
RM35UA11MWlocal signalling
RM35UA11MWlocal signalling
RM35UA11MWlocal signalling
RM35UA11MWlocal signalling
RM35UA11MWlocal signalling
RM35UA11MWlocal signalling
RM35UA11MWlocal signalling
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MWdiagnostic button
RM35UA11MW
RM35UA11MW
RM35UA11MW
RM35UA11MWsafety reliability data | MTTF,
RM35UA11MWsafety reliability data | B10,
RM35UA11MW | MTTFd,
RM35UA11MW | B10d,
RM35UA11MW
RM35UA12MW
RM35UA12MWstandards | EN60255-6, IEC60255-6
RM35UA12MWproduct certifications | UL, CSA, GL, C-Tick, GOST
RM35UA12MWmarking | UL, CSA, GL, C-Tick, GOST, CE
RM35UA12MWdirectives | No 73/23/EEC + 93/68/EEC
RM35UA12MWdirectives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
RM35UA12MWdirectives | 2002/95/EC
RM35UA12MW
RM35UA12MW | Not specified ¦ IEC60721-3-3,Climatic category,
RM35UA12MW | Germanisher Lloyd,Environmental category,
RM35UA12MWambient air temperature for storage | -40…+70 ¦ ,Storage,
RM35UA12MWambient air temperature for operation | -20…+50 ¦ ,Operation,
RM35UA12MWrelative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM35UA12MW | IEC60947-5-1,Cyclic Damp Heat Test,
RM35UA12MWvibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM35UA12MWshock resistance | 5 gn ¦ IEC60068-2-27
RM35UA12MWbump resistance | IEC60068-2-29
RM35UA12MWseismic resistance | IEC60068-3-3
RM35UA12MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM35UA12MWIP degree of protection | IP30 ¦ IEC60529,Housing,
RM35UA12MWIP degree of protection | IEC60529,Front Panel,
RM35UA12MW
RM35UA12MWwidth | 35 x 90 x 72 ¦ ,Width,
RM35UA12MWheight | Height,
RM35UA12MWdepth | Depth,
RM35UA12MWnet weight | 130
RM35UA12MWmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM35UA12MWmounting support | - ¦ IEC/EN 60715,With socket,
RM35UA12MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35UA12MWMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM35UA12MWMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM35UA12MWconnections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35UA12MWconnections - terminals | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35UA12MWconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM35UA12MWconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35UA12MWtightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM35UA12MWcable stripping length | Not specified ¦ ,Cable stripping length,
RM35UA12MWduty time | Not specified
RM35UA12MW
RM35UA12MWelectromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard,
RM35UA12MWelectromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM35UA12MWelectromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM35UA12MWelectromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM35UA12MWelectromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM35UA12MWelectromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM35UA12MWelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM35UA12MWelectromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35UA12MWelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM35UA12MWelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM35UA12MWelectromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM35UA12MWelectromagnetic compatibility | · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35UA12MWelectromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM35UA12MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35UA12MWelectromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35UA12MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM35UA12MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35UA12MWelectromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35UA12MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35UA12MW
RM35UA12MWpollution degree | 3 ¦ IEC60664-1
RM35UA12MWovervoltage category | III ¦ IEC60664-1
RM35UA12MWcircuit group | Supply,Terminal
RM35UA12MWcircuit group | Input 1,
RM35UA12MWcircuit group | Input 2,
RM35UA12MWcircuit group | Input 3,
RM35UA12MWcircuit group | Output 1,
RM35UA12MWcircuit group | 600 ¦ ,Output 2,
RM35UA12MW | 600 ¦ ,Supply,Rated
RM35UA12MW | 600 ¦ ,Input 1,Voltage
RM35UA12MW | Input 2,Spec
RM35UA12MW | Input 3,
RM35UA12MW | Output 1,
RM35UA12MW | Output 2,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Supply,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM35UA12MW[Ui] rated insulation voltage | 4 ¦ IEC60664-1,Output 1,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM35UA12MW[Ui] rated insulation voltage | 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM35UA12MW[Uimp] rated impulse withstand voltage | > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM35UA12MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM35UA12MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM35UA12MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM35UA12MWdielectric strength | IEC60255-27,Supply / Output 1,
RM35UA12MWdielectric strength | IEC60255-27,Supply / Output 2,
RM35UA12MWdielectric strength | IEC60255-27,Output 1 / Output 2,
RM35UA12MWdielectric strength | IEC60255-27,Input 1 / Output 1,
RM35UA12MWdielectric strength | IEC60255-27,Input 1 / Output 2,
RM35UA12MWdielectric strength | IEC60255-27,Input 2 / Output 1,
RM35UA12MWdielectric strength | IEC60255-27,Input 2 / Output 2,
RM35UA12MWdielectric strength | IEC60255-27,Input 3 / Output 1,
RM35UA12MWdielectric strength | IEC60255-27,Input 3 / Output 2,
RM35UA12MWdielectric strength | IEC60255-27,Input 1 / Input 2,
RM35UA12MWdielectric strength | IEC60255-27,Input 2 / Input 3,
RM35UA12MWdielectric strength | IEC60255-27,Input 1 / Input 3,
RM35UA12MWinsulation resistance | IEC60255-27,Supply / Input 1,
RM35UA12MWinsulation resistance | IEC60255-27,Supply / Input 2,
RM35UA12MWinsulation resistance | IEC60255-27,Supply / Input 3,
RM35UA12MWinsulation resistance | IEC60255-27,Supply / Output 1,
RM35UA12MWinsulation resistance | IEC60255-27,Supply / Output 2,
RM35UA12MWinsulation resistance | IEC60255-27,Output 1 / Output 2,
RM35UA12MWinsulation resistance | IEC60255-27,Input 1 / Output 1,
RM35UA12MWinsulation resistance | IEC60255-27,Input 1 / Output 2,
RM35UA12MWinsulation resistance | IEC60255-27,Input 2 / Output 1,
RM35UA12MWinsulation resistance | IEC60255-27,Input 2 / Output 2,
RM35UA12MWinsulation resistance | IEC60255-27,Input 3 / Output 1,
RM35UA12MWinsulation resistance | IEC60255-27,Input 3 / Output 2,
RM35UA12MWinsulation resistance | IEC60255-27,Input 1 / Input 2,
RM35UA12MWinsulation resistance | IEC60255-27,Input 2 / Input 3,
RM35UA12MWinsulation resistance | IEC60255-27,Input 1 / Input 3,
RM35UA12MW
RM35UA12MW[Us] rated supply voltage | ~/-- 24…240
RM35UA12MWsupply voltage limits | ~/-- 20.4…264
RM35UA12MWpolarity
RM35UA12MWsupply frequency | 50 / 60
RM35UA12MWsupply frequency | 45…66
RM35UA12MWpower consumption | ~ 3.5VA, -- 0.6W
RM35UA12MWimmunity to microbreaks | 10
RM35UA12MWsupply terminal | A1-A2
RM35UA12MWon-load factor
RM35UA12MWrelease of input voltage
RM35UA12MW
RM35UA12MW | - ¦ ,Over / undervoltage (windows mode),
RM35UA12MW | Selectable with memory / without memory ¦ ,Over voltage,
RM35UA12MW | Selectable with memory / without memory ¦ ,Undervoltage ,
RM35UA12MW | ~/-- 1…100
RM35UA12MW | 22 ¦ ,E1-M / B1-C,
RM35UA12MW | 110 ¦ ,E2-M / B2-C,
RM35UA12MW | 220 ¦ ,E3-M / B3-C,
RM35UA12MW | A1+ / A2-,
RM35UA12MW | - ¦ ,Built in current transformer,
RM35UA12MW | ~/-- 1…10 ¦ ,E1-M / B1-C,
RM35UA12MW | ~/-- 5…50 ¦ ,E2-M / B2-C,
RM35UA12MW | ~/-- 10…100 ¦ ,E3-M / B3-C,
RM35UA12MW | A1+ / A2-,
RM35UA12MW | - ¦ ,Built in current transformer,
RM35UA12MW | Adjustable 10%...100% of 0.5V ¦ ,E1-M / B1-C,
RM35UA12MW | Adjustable 10%...100% of 3V ¦ ,E2-M / B2-C,
RM35UA12MW | Adjustable 10%...100% of 5V ¦ ,E3-M / B3-C,
RM35UA12MW | A1+ / A2-,
RM35UA12MW | - ¦ ,Built in current transformer,
RM35UA12MW | Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C,
RM35UA12MW | Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C,
RM35UA12MW | Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C,
RM35UA12MW | A1+ / A2-,
RM35UA12MW | - ¦ ,Built in current transformer,
RM35UA12MW | Resistive Voltage Step Down
RM35UA12MW | E1-M, E2-M, E3-M
RM35UA12MW | 50 / 60
RM35UA12MW | 36…77
RM35UA12MW | +/- 10% of full scale value
RM35UA12MW | +/- 0.5%
RM35UA12MW | < 1% over whole range
RM35UA12MW | 0.05% / oC
RM35UA12MW | 30
RM35UA12MW | True RMS
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MWoutput type | 2 x C/O relay contacts
RM35UA12MWoutput terminal | 11-12-14, 21-22-24
RM35UA12MWoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM35UA12MWoutput logic | R2 (21-22-24),
RM35UA12MWcontacts material | Cadmium-free
RM35UA12MWmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM35UA12MWelectrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1,
RM35UA12MWelectrical durability | IEC60947-4-1,DC-1,
RM35UA12MWelectrical durability | IEC60947-5-1,AC-15,
RM35UA12MWelectrical durability | IEC60947-5-1,DC-13,
RM35UA12MW[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM35UA12MW[Ie] rated operational current | IEC61810-1,Rated switching current,
RM35UA12MWmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM35UA12MWmaximum switching capacity | 5 ¦ ,Maximum switching current,
RM35UA12MWmaximum switching capacity | 1250 ¦ ,Maximum switching capacity,
RM35UA12MWminimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
RM35UA12MWminimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM35UA12MWminimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM35UA12MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35UA12MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35UA12MWthermal current | IEC60947-5-1
RM35UA12MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM35UA12MWshort circuit protection | IEC62314,Solid State Output by external fuse,
RM35UA12MW
RM35UA12MWtime delay type | · ¦ ,"OFF" delay,
RM35UA12MWtime delay type | - ¦ ,"ON" delay,
RM35UA12MWtime delay type | - ¦ ,Inhibition,
RM35UA12MWtime delay range | Adjustable 0.3…30 ¦ ,"OFF" delay,
RM35UA12MWtime delay range | - ¦ ,"ON" delay,
RM35UA12MWtime delay range | - ¦ ,Inhibition,
RM35UA12MWresponse time | Not specified ¦ ,on crossing the threshold,
RM35UA12MWresponse time
RM35UA12MWresponse time
RM35UA12MWresponse time
RM35UA12MWresponse time
RM35UA12MWpower on delay | 0
RM35UA12MWreset time | 0
RM35UA12MWreset time | through front panel reset,
RM35UA12MWreset time | through input control reset,
RM35UA12MWsetting accuracy of time delay | +/- 10% of full scales
RM35UA12MWrepeat accuracy of time delay | +/- 2%
RM35UA12MWtime delay drift | Not specified
RM35UA12MWtime delay drift | Not specified
RM35UA12MW
RM35UA12MWstatus LED
RM35UA12MWlocal signalling | Power supply availability,
RM35UA12MWlocal signalling | Power supply not availability,
RM35UA12MWlocal signalling | Timing in-progress,
RM35UA12MWlocal signalling | Output is energized,
RM35UA12MWlocal signalling | Output is de-energized,
RM35UA12MWlocal signalling | Range Setting Changes,
RM35UA12MWlocal signalling
RM35UA12MWlocal signalling
RM35UA12MWlocal signalling
RM35UA12MWlocal signalling
RM35UA12MWlocal signalling
RM35UA12MWlocal signalling
RM35UA12MWlocal signalling
RM35UA12MWlocal signalling
RM35UA12MWlocal signalling
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MWdiagnostic button
RM35UA12MW
RM35UA12MW
RM35UA12MW
RM35UA12MWsafety reliability data | MTTF,
RM35UA12MWsafety reliability data | B10,
RM35UA12MW | MTTFd,
RM35UA12MW | B10d,
RM35UA12MW
RM35UA13MW
RM35UA13MWstandards | EN60255-6, IEC60255-6
RM35UA13MWproduct certifications | UL, CSA, GL, C-Tick, GOST
RM35UA13MWmarking | UL, CSA, GL, C-Tick, GOST, CE
RM35UA13MWdirectives | No 73/23/EEC + 93/68/EEC
RM35UA13MWdirectives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
RM35UA13MWdirectives | 2002/95/EC
RM35UA13MW
RM35UA13MW | Not specified ¦ IEC60721-3-3,Climatic category,
RM35UA13MW | Germanisher Lloyd,Environmental category,
RM35UA13MWambient air temperature for storage | -40…+70 ¦ ,Storage,
RM35UA13MWambient air temperature for operation | -20…+50 ¦ ,Operation,
RM35UA13MWrelative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM35UA13MW | IEC60947-5-1,Cyclic Damp Heat Test,
RM35UA13MWvibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM35UA13MWshock resistance | 5 gn ¦ IEC60068-2-27
RM35UA13MWbump resistance | IEC60068-2-29
RM35UA13MWseismic resistance | IEC60068-3-3
RM35UA13MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM35UA13MWIP degree of protection | IP30 ¦ IEC60529,Housing,
RM35UA13MWIP degree of protection | IEC60529,Front Panel,
RM35UA13MW
RM35UA13MWwidth | 35 x 90 x 72 ¦ ,Width,
RM35UA13MWheight | Height,
RM35UA13MWdepth | Depth,
RM35UA13MWnet weight | 130
RM35UA13MWmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM35UA13MWmounting support | - ¦ IEC/EN 60715,With socket,
RM35UA13MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35UA13MWMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM35UA13MWMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM35UA13MWconnections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35UA13MWconnections - terminals | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35UA13MWconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM35UA13MWconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35UA13MWtightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM35UA13MWcable stripping length | Not specified ¦ ,Cable stripping length,
RM35UA13MWduty time | Not specified
RM35UA13MW
RM35UA13MWelectromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard,
RM35UA13MWelectromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM35UA13MWelectromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM35UA13MWelectromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM35UA13MWelectromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM35UA13MWelectromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM35UA13MWelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM35UA13MWelectromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35UA13MWelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM35UA13MWelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM35UA13MWelectromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM35UA13MWelectromagnetic compatibility | · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35UA13MWelectromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM35UA13MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35UA13MWelectromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35UA13MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM35UA13MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35UA13MWelectromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35UA13MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35UA13MW
RM35UA13MWpollution degree | 3 ¦ IEC60664-1
RM35UA13MWovervoltage category | III ¦ IEC60664-1
RM35UA13MWcircuit group | Supply,Terminal
RM35UA13MWcircuit group | Input 1,
RM35UA13MWcircuit group | Input 2,
RM35UA13MWcircuit group | Input 3,
RM35UA13MWcircuit group | Output 1,
RM35UA13MWcircuit group | 600 ¦ ,Output 2,
RM35UA13MW | 600 ¦ ,Supply,Rated
RM35UA13MW | 600 ¦ ,Input 1,Voltage
RM35UA13MW | Input 2,Spec
RM35UA13MW | Input 3,
RM35UA13MW | Output 1,
RM35UA13MW | Output 2,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Supply,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM35UA13MW[Ui] rated insulation voltage | 4 ¦ IEC60664-1,Output 1,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM35UA13MW[Ui] rated insulation voltage | 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM35UA13MW[Uimp] rated impulse withstand voltage | > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM35UA13MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM35UA13MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM35UA13MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM35UA13MWdielectric strength | IEC60255-27,Supply / Output 1,
RM35UA13MWdielectric strength | IEC60255-27,Supply / Output 2,
RM35UA13MWdielectric strength | IEC60255-27,Output 1 / Output 2,
RM35UA13MWdielectric strength | IEC60255-27,Input 1 / Output 1,
RM35UA13MWdielectric strength | IEC60255-27,Input 1 / Output 2,
RM35UA13MWdielectric strength | IEC60255-27,Input 2 / Output 1,
RM35UA13MWdielectric strength | IEC60255-27,Input 2 / Output 2,
RM35UA13MWdielectric strength | IEC60255-27,Input 3 / Output 1,
RM35UA13MWdielectric strength | IEC60255-27,Input 3 / Output 2,
RM35UA13MWdielectric strength | IEC60255-27,Input 1 / Input 2,
RM35UA13MWdielectric strength | IEC60255-27,Input 2 / Input 3,
RM35UA13MWdielectric strength | IEC60255-27,Input 1 / Input 3,
RM35UA13MWinsulation resistance | IEC60255-27,Supply / Input 1,
RM35UA13MWinsulation resistance | IEC60255-27,Supply / Input 2,
RM35UA13MWinsulation resistance | IEC60255-27,Supply / Input 3,
RM35UA13MWinsulation resistance | IEC60255-27,Supply / Output 1,
RM35UA13MWinsulation resistance | IEC60255-27,Supply / Output 2,
RM35UA13MWinsulation resistance | IEC60255-27,Output 1 / Output 2,
RM35UA13MWinsulation resistance | IEC60255-27,Input 1 / Output 1,
RM35UA13MWinsulation resistance | IEC60255-27,Input 1 / Output 2,
RM35UA13MWinsulation resistance | IEC60255-27,Input 2 / Output 1,
RM35UA13MWinsulation resistance | IEC60255-27,Input 2 / Output 2,
RM35UA13MWinsulation resistance | IEC60255-27,Input 3 / Output 1,
RM35UA13MWinsulation resistance | IEC60255-27,Input 3 / Output 2,
RM35UA13MWinsulation resistance | IEC60255-27,Input 1 / Input 2,
RM35UA13MWinsulation resistance | IEC60255-27,Input 2 / Input 3,
RM35UA13MWinsulation resistance | IEC60255-27,Input 1 / Input 3,
RM35UA13MW
RM35UA13MW[Us] rated supply voltage | ~/-- 24…240
RM35UA13MWsupply voltage limits | 0.85…1.1 Un (~/-- 20.4…264)
RM35UA13MWpolarity
RM35UA13MWsupply frequency | 50 / 60
RM35UA13MWsupply frequency | 45…66
RM35UA13MWpower consumption | ~ 3.5VA, -- 0.6W
RM35UA13MWimmunity to microbreaks | 10
RM35UA13MWsupply terminal | A1-A2
RM35UA13MWon-load factor
RM35UA13MWrelease of input voltage
RM35UA13MW
RM35UA13MW | - ¦ ,Over / undervoltage (windows mode),
RM35UA13MW | Selectable with memory / without memory ¦ ,Over voltage,
RM35UA13MW | Selectable with memory / without memory ¦ ,Undervoltage ,
RM35UA13MW | ~/-- 15…600
RM35UA13MW | 150 ¦ ,E1-M / B1-C,
RM35UA13MW | 300 ¦ ,E2-M / B2-C,
RM35UA13MW | 600 ¦ ,E3-M / B3-C,
RM35UA13MW | A1+ / A2-,
RM35UA13MW | - ¦ ,Built in current transformer,
RM35UA13MW | ~/-- 15…150 ¦ ,E1-M / B1-C,
RM35UA13MW | ~/-- 30…300 ¦ ,E2-M / B2-C,
RM35UA13MW | ~/-- 60…600 ¦ ,E3-M / B3-C,
RM35UA13MW | A1+ / A2-,
RM35UA13MW | - ¦ ,Built in current transformer,
RM35UA13MW | Adjustable 10%...100% ¦ ,E1-M / B1-C,
RM35UA13MW | Adjustable 10%...100% ¦ ,E2-M / B2-C,
RM35UA13MW | Adjustable 10%...100% ¦ ,E3-M / B3-C,
RM35UA13MW | A1+ / A2-,
RM35UA13MW | - ¦ ,Built in current transformer,
RM35UA13MW | Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C,
RM35UA13MW | Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C,
RM35UA13MW | Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C,
RM35UA13MW | A1+ / A2-,
RM35UA13MW | - ¦ ,Built in current transformer,
RM35UA13MW | Resistive Voltage Step Down
RM35UA13MW | E1-M, E2-M, E3-M
RM35UA13MW | 50 / 60
RM35UA13MW | 36…77
RM35UA13MW | +/- 10% of full scale value
RM35UA13MW | +/- 0.5%
RM35UA13MW | < 1% over whole range
RM35UA13MW | 0.05% / oC
RM35UA13MW | 30
RM35UA13MW | True RMS
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MWoutput type | 2 x C/O relay contacts
RM35UA13MWoutput terminal | 11-12-14, 21-22-24
RM35UA13MWoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM35UA13MWoutput logic | R2 (21-22-24),
RM35UA13MWcontacts material | Cadmium-free
RM35UA13MWmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM35UA13MWelectrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1,
RM35UA13MWelectrical durability | IEC60947-4-1,DC-1,
RM35UA13MWelectrical durability | IEC60947-5-1,AC-15,
RM35UA13MWelectrical durability | IEC60947-5-1,DC-13,
RM35UA13MW[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM35UA13MW[Ie] rated operational current | IEC61810-1,Rated switching current,
RM35UA13MWmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM35UA13MWmaximum switching capacity | 5 ¦ ,Maximum switching current,
RM35UA13MWmaximum switching capacity | 1250 ¦ ,Maximum switching capacity,
RM35UA13MWminimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
RM35UA13MWminimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM35UA13MWminimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM35UA13MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35UA13MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35UA13MWthermal current | IEC60947-5-1
RM35UA13MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM35UA13MWshort circuit protection | IEC62314,Solid State Output by external fuse,
RM35UA13MW
RM35UA13MWtime delay type | · ¦ ,"OFF" delay,
RM35UA13MWtime delay type | - ¦ ,"ON" delay,
RM35UA13MWtime delay type | - ¦ ,Inhibition,
RM35UA13MWtime delay range | Adjustable 0.3…30 ¦ ,"OFF" delay,
RM35UA13MWtime delay range | - ¦ ,"ON" delay,
RM35UA13MWtime delay range | - ¦ ,Inhibition,
RM35UA13MWresponse time | Not specified ¦ ,on crossing the threshold,
RM35UA13MWresponse time
RM35UA13MWresponse time
RM35UA13MWresponse time
RM35UA13MWresponse time
RM35UA13MWpower on delay | 0
RM35UA13MWreset time | 0
RM35UA13MWreset time | through front panel reset,
RM35UA13MWreset time | through input control reset,
RM35UA13MWsetting accuracy of time delay | +/- 10% of full scales
RM35UA13MWrepeat accuracy of time delay | +/- 2%
RM35UA13MWtime delay drift | Not specified
RM35UA13MWtime delay drift | Not specified
RM35UA13MW
RM35UA13MWstatus LED
RM35UA13MWlocal signalling | Power supply availability,
RM35UA13MWlocal signalling | Power supply not availability,
RM35UA13MWlocal signalling | Timing in-progress,
RM35UA13MWlocal signalling | Output is energized,
RM35UA13MWlocal signalling | Output is de-energized,
RM35UA13MWlocal signalling | Range Setting Changes,
RM35UA13MWlocal signalling
RM35UA13MWlocal signalling
RM35UA13MWlocal signalling
RM35UA13MWlocal signalling
RM35UA13MWlocal signalling
RM35UA13MWlocal signalling
RM35UA13MWlocal signalling
RM35UA13MWlocal signalling
RM35UA13MWlocal signalling
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MWdiagnostic button
RM35UA13MW
RM35UA13MW
RM35UA13MW
RM35UA13MWsafety reliability data | MTTF,
RM35UA13MWsafety reliability data | B10,
RM35UA13MW | MTTFd,
RM35UA13MW | B10d,
RM35UA13MW
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)standards | EN60255-6, IEC60255-6
RM22UA3 (Catch Up)product certifications | UL, CSA, GL, C-Tick, GOST
RM22UA3 (Catch Up)marking | UL, CSA, GL, C-Tick, GOST, CE
RM22UA3 (Catch Up)directives | No 73/23/EEC + 93/68/EEC
RM22UA3 (Catch Up)directives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
RM22UA3 (Catch Up)directives | 2002/95/EC
RM22UA3 (Catch Up)
RM22UA3 (Catch Up) | Not specified ¦ IEC60721-3-3,Climatic category,
RM22UA3 (Catch Up) | Germanisher Lloyd,Environmental category,
RM22UA3 (Catch Up)ambient air temperature for storage | -40…+70 ¦ ,Storage,
RM22UA3 (Catch Up)ambient air temperature for operation | -20…+50 ¦ ,Operation,
RM22UA3 (Catch Up)relative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM22UA3 (Catch Up) | IEC60947-5-1,Cyclic Damp Heat Test,
RM22UA3 (Catch Up)vibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM22UA3 (Catch Up)shock resistance | 5 gn ¦ IEC60068-2-27
RM22UA3 (Catch Up)bump resistance | IEC60068-2-29
RM22UA3 (Catch Up)seismic resistance | IEC60068-3-3
RM22UA3 (Catch Up)IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22UA3 (Catch Up)IP degree of protection | IP30 ¦ IEC60529,Housing,
RM22UA3 (Catch Up)IP degree of protection | IEC60529,Front Panel,
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)width | 22.5 x ? x ? ¦ ,Width,
RM22UA3 (Catch Up)height | Height,
RM22UA3 (Catch Up)depth | Depth,
RM22UA3 (Catch Up)net weight | ?
RM22UA3 (Catch Up)mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22UA3 (Catch Up)mounting support | - ¦ IEC/EN 60715,With socket,
RM22UA3 (Catch Up)mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UA3 (Catch Up)Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22UA3 (Catch Up)Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22UA3 (Catch Up)connections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22UA3 (Catch Up)connections - terminals | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22UA3 (Catch Up)connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22UA3 (Catch Up)connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UA3 (Catch Up)tightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM22UA3 (Catch Up)cable stripping length | Not specified ¦ ,Cable stripping length,
RM22UA3 (Catch Up)duty time | Not specified
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)electromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard,
RM22UA3 (Catch Up)electromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22UA3 (Catch Up)electromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22UA3 (Catch Up)electromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM22UA3 (Catch Up)electromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM22UA3 (Catch Up)electromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22UA3 (Catch Up)electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM22UA3 (Catch Up)electromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22UA3 (Catch Up)electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM22UA3 (Catch Up)electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM22UA3 (Catch Up)electromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM22UA3 (Catch Up)electromagnetic compatibility | · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22UA3 (Catch Up)electromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM22UA3 (Catch Up)electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22UA3 (Catch Up)electromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22UA3 (Catch Up)electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22UA3 (Catch Up)electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22UA3 (Catch Up)electromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22UA3 (Catch Up)electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)pollution degree | 3 ¦ IEC60664-1
RM22UA3 (Catch Up)overvoltage category | III ¦ IEC60664-1
RM22UA3 (Catch Up)circuit group | Supply,Terminal
RM22UA3 (Catch Up)circuit group | Input 1,
RM22UA3 (Catch Up)circuit group | Input 2,
RM22UA3 (Catch Up)circuit group | Input 3,
RM22UA3 (Catch Up)circuit group | Output 1,
RM22UA3 (Catch Up)circuit group | 600 ¦ ,Output 2,
RM22UA3 (Catch Up) | 600 ¦ ,Supply,Rated
RM22UA3 (Catch Up) | 600 ¦ ,Input 1,Voltage
RM22UA3 (Catch Up) | Input 2,Spec
RM22UA3 (Catch Up) | Input 3,
RM22UA3 (Catch Up) | Output 1,
RM22UA3 (Catch Up) | Output 2,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | 4 ¦ IEC60664-1,Output 1,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM22UA3 (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM22UA3 (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM22UA3 (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM22UA3 (Catch Up)dielectric strength | IEC60255-27,Supply / Output 1,
RM22UA3 (Catch Up)dielectric strength | IEC60255-27,Supply / Output 2,
RM22UA3 (Catch Up)dielectric strength | IEC60255-27,Output 1 / Output 2,
RM22UA3 (Catch Up)dielectric strength | IEC60255-27,Input 1 / Output 1,
RM22UA3 (Catch Up)dielectric strength | IEC60255-27,Input 1 / Output 2,
RM22UA3 (Catch Up)dielectric strength | IEC60255-27,Input 2 / Output 1,
RM22UA3 (Catch Up)dielectric strength | IEC60255-27,Input 2 / Output 2,
RM22UA3 (Catch Up)dielectric strength | IEC60255-27,Input 3 / Output 1,
RM22UA3 (Catch Up)dielectric strength | IEC60255-27,Input 3 / Output 2,
RM22UA3 (Catch Up)dielectric strength | IEC60255-27,Input 1 / Input 2,
RM22UA3 (Catch Up)dielectric strength | IEC60255-27,Input 2 / Input 3,
RM22UA3 (Catch Up)dielectric strength | IEC60255-27,Input 1 / Input 3,
RM22UA3 (Catch Up)insulation resistance | IEC60255-27,Supply / Input 1,
RM22UA3 (Catch Up)insulation resistance | IEC60255-27,Supply / Input 2,
RM22UA3 (Catch Up)insulation resistance | IEC60255-27,Supply / Input 3,
RM22UA3 (Catch Up)insulation resistance | IEC60255-27,Supply / Output 1,
RM22UA3 (Catch Up)insulation resistance | IEC60255-27,Supply / Output 2,
RM22UA3 (Catch Up)insulation resistance | IEC60255-27,Output 1 / Output 2,
RM22UA3 (Catch Up)insulation resistance | IEC60255-27,Input 1 / Output 1,
RM22UA3 (Catch Up)insulation resistance | IEC60255-27,Input 1 / Output 2,
RM22UA3 (Catch Up)insulation resistance | IEC60255-27,Input 2 / Output 1,
RM22UA3 (Catch Up)insulation resistance | IEC60255-27,Input 2 / Output 2,
RM22UA3 (Catch Up)insulation resistance | IEC60255-27,Input 3 / Output 1,
RM22UA3 (Catch Up)insulation resistance | IEC60255-27,Input 3 / Output 2,
RM22UA3 (Catch Up)insulation resistance | IEC60255-27,Input 1 / Input 2,
RM22UA3 (Catch Up)insulation resistance | IEC60255-27,Input 2 / Input 3,
RM22UA3 (Catch Up)insulation resistance | IEC60255-27,Input 1 / Input 3,
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)[Us] rated supply voltage | ~/-- 24…240
RM22UA3 (Catch Up)supply voltage limits | ~/-- 20.4…264
RM22UA3 (Catch Up)polarity
RM22UA3 (Catch Up)supply frequency | 50 / 60
RM22UA3 (Catch Up)supply frequency | 45…66
RM22UA3 (Catch Up)power consumption | ~ 3.5VA, -- 0.6W
RM22UA3 (Catch Up)immunity to microbreaks | 10
RM22UA3 (Catch Up)supply terminal | A1-A2
RM22UA3 (Catch Up)on-load factor
RM22UA3 (Catch Up)release of input voltage
RM22UA3 (Catch Up)
RM22UA3 (Catch Up) | - ¦ ,Over / undervoltage (windows mode),
RM22UA3 (Catch Up) | Selectable with memory / without memory ¦ ,Over voltage,
RM22UA3 (Catch Up) | Selectable with memory / without memory ¦ ,Undervoltage ,
RM22UA3 (Catch Up) | ~/-- 0.05…5
RM22UA3 (Catch Up) | RM22UA31MW: 5 RM22UA32MW: 22 RM22UA33MW: 150 ¦ ,E1-M / B1-C,
RM22UA3 (Catch Up) | RM22UA31MW: 30 RM22UA32MW: 110 RM22UA33MW: 300 ¦ ,E2-M / B2-C,
RM22UA3 (Catch Up) | RM22UA31MW: 50 RM22UA32MW: 220 RM22UA33MW: 600 ¦ ,E3-M / B3-C,
RM22UA3 (Catch Up) | A1+ / A2-,
RM22UA3 (Catch Up) | - ¦ ,Built in current transformer,
RM22UA3 (Catch Up) | RM22UA31MW: ~/-- 0.05…0.5 RM22UA32MW: ~/-- 1…10 RM22UA33MW: ~/-- 15…150 ¦ ,E1-M / B1-C,
RM22UA3 (Catch Up) | RM22UA31MW: ~/-- 0.5…3 RM22UA32MW: ~/-- 5…50 RM22UA33MW: ~/-- 30…300 ¦ ,E2-M / B2-C,
RM22UA3 (Catch Up) | RM22UA31MW: ~/-- 0.5…5 RM22UA32MW: ~/-- 10…100 RM22UA33MW: ~/-- 60…600 ¦ ,E3-M / B3-C,
RM22UA3 (Catch Up) | A1+ / A2-,
RM22UA3 (Catch Up) | - ¦ ,Built in current transformer,
RM22UA3 (Catch Up) | Adjustable 10%...100% of full range ¦ ,E1-M / B1-C,
RM22UA3 (Catch Up) | Adjustable 10%...100% of full range ¦ ,E2-M / B2-C,
RM22UA3 (Catch Up) | Adjustable 10%...100% of full range ¦ ,E3-M / B3-C,
RM22UA3 (Catch Up) | A1+ / A2-,
RM22UA3 (Catch Up) | - ¦ ,Built in current transformer,
RM22UA3 (Catch Up) | Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C,
RM22UA3 (Catch Up) | Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C,
RM22UA3 (Catch Up) | Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C,
RM22UA3 (Catch Up) | A1+ / A2-,
RM22UA3 (Catch Up) | - ¦ ,Built in current transformer,
RM22UA3 (Catch Up) | Resistive Voltage Step Down
RM22UA3 (Catch Up) | E1-M, E2-M, E3-M
RM22UA3 (Catch Up) | 50 / 60
RM22UA3 (Catch Up) | 36…77
RM22UA3 (Catch Up) | +/- 10% of full scale value
RM22UA3 (Catch Up) | +/- 0.5%
RM22UA3 (Catch Up) | < 1% over whole range
RM22UA3 (Catch Up) | 0.05% / oC
RM22UA3 (Catch Up) | 30
RM22UA3 (Catch Up) | True RMS
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)output type | 2 x C/O relay contacts
RM22UA3 (Catch Up)output terminal | 11-12-14, 21-22-24
RM22UA3 (Catch Up)output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22UA3 (Catch Up)output logic | R2 (21-22-24),
RM22UA3 (Catch Up)contacts material | Cadmium-free
RM22UA3 (Catch Up)mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM22UA3 (Catch Up)electrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1,
RM22UA3 (Catch Up)electrical durability | IEC60947-4-1,DC-1,
RM22UA3 (Catch Up)electrical durability | IEC60947-5-1,AC-15,
RM22UA3 (Catch Up)electrical durability | IEC60947-5-1,DC-13,
RM22UA3 (Catch Up)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM22UA3 (Catch Up)[Ie] rated operational current | IEC61810-1,Rated switching current,
RM22UA3 (Catch Up)maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM22UA3 (Catch Up)maximum switching capacity | ~ 8 ¦ ,Maximum switching current,
RM22UA3 (Catch Up)maximum switching capacity | 2000 ¦ ,Maximum switching capacity,
RM22UA3 (Catch Up)minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
RM22UA3 (Catch Up)minimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM22UA3 (Catch Up)minimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UA3 (Catch Up)maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UA3 (Catch Up)maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UA3 (Catch Up)thermal current | IEC60947-5-1
RM22UA3 (Catch Up)short circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM22UA3 (Catch Up)short circuit protection | IEC62314,Solid State Output by external fuse,
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)time delay type | · ¦ ,"OFF" delay,
RM22UA3 (Catch Up)time delay type | - ¦ ,"ON" delay,
RM22UA3 (Catch Up)time delay type | - ¦ ,Inhibition,
RM22UA3 (Catch Up)time delay range | Adjustable 0.3…30 ¦ ,"OFF" delay,
RM22UA3 (Catch Up)time delay range | - ¦ ,"ON" delay,
RM22UA3 (Catch Up)time delay range | - ¦ ,Inhibition,
RM22UA3 (Catch Up)response time | Not specified ¦ ,on crossing the threshold,
RM22UA3 (Catch Up)response time
RM22UA3 (Catch Up)response time
RM22UA3 (Catch Up)response time
RM22UA3 (Catch Up)response time
RM22UA3 (Catch Up)power on delay | 0
RM22UA3 (Catch Up)reset time | 0
RM22UA3 (Catch Up)reset time | through front panel reset,
RM22UA3 (Catch Up)reset time | through input control reset,
RM22UA3 (Catch Up)setting accuracy of time delay | +/- 10% of full scales
RM22UA3 (Catch Up)repeat accuracy of time delay | +/- 2%
RM22UA3 (Catch Up)time delay drift | Not specified
RM22UA3 (Catch Up)time delay drift | Not specified
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)status LED
RM22UA3 (Catch Up)local signalling | Power supply availability,
RM22UA3 (Catch Up)local signalling | Power supply not availability,
RM22UA3 (Catch Up)local signalling | Timing in-progress,
RM22UA3 (Catch Up)local signalling | Output is energized,
RM22UA3 (Catch Up)local signalling | Output is de-energized,
RM22UA3 (Catch Up)local signalling | Range Setting Changes,
RM22UA3 (Catch Up)local signalling
RM22UA3 (Catch Up)local signalling
RM22UA3 (Catch Up)local signalling
RM22UA3 (Catch Up)local signalling
RM22UA3 (Catch Up)local signalling
RM22UA3 (Catch Up)local signalling
RM22UA3 (Catch Up)local signalling
RM22UA3 (Catch Up)local signalling
RM22UA3 (Catch Up)local signalling
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)diagnostic button
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)
RM22UA3 (Catch Up)safety reliability data | MTTF,
RM22UA3 (Catch Up)safety reliability data | B10,
RM22UA3 (Catch Up) | MTTFd,
RM22UA3 (Catch Up) | B10d,
RM22UA3 (Catch Up)
RM4UA3
RM4UA3standards | EN60255-6, IEC60255-6
RM4UA3product certifications | UL, CSA, GL, C-Tick, GOST
RM4UA3marking | UL, CSA, GL, C-Tick, GOST, CE
RM4UA3directives | No 73/23/EEC + 93/68/EEC
RM4UA3directives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
RM4UA3directives | 2002/95/EC
RM4UA3
RM4UA3 | Not specified ¦ IEC60721-3-3,Climatic category,
RM4UA3 | Germanisher Lloyd,Environmental category,
RM4UA3ambient air temperature for storage | Not specified ¦ ,Storage,
RM4UA3ambient air temperature for operation | Not specified ¦ ,Operation,
RM4UA3relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
RM4UA3 | IEC60947-5-1,Cyclic Damp Heat Test,
RM4UA3vibration resistance | Not specified ¦ IEC60068-2-6
RM4UA3shock resistance | Not specified ¦ IEC60068-2-27
RM4UA3bump resistance | IEC60068-2-29
RM4UA3seismic resistance | IEC60068-3-3
RM4UA3IP degree of protection | Not specified ¦ IEC60529,Terminal Block,
RM4UA3IP degree of protection | Not specified ¦ IEC60529,Housing,
RM4UA3IP degree of protection | IEC60529,Front Panel,
RM4UA3
RM4UA3width | 22.5 x 78 x 80 ¦ ,Width,
RM4UA3height | Height,
RM4UA3depth | Depth,
RM4UA3net weight | 168
RM4UA3mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM4UA3mounting support | - ¦ IEC/EN 60715,With socket,
RM4UA3mounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
RM4UA3Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM4UA3Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM4UA3connections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM4UA3connections - terminals | Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM4UA3connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM4UA3connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4UA3tightening torque | Not specified ¦ IEC60947-1,Tightening torque,
RM4UA3cable stripping length | Not specified ¦ ,Cable stripping length,
RM4UA3duty time | Not specified
RM4UA3
RM4UA3electromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard,
RM4UA3electromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM4UA3electromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM4UA3electromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM4UA3electromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM4UA3electromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM4UA3electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM4UA3electromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM4UA3electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM4UA3electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM4UA3electromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM4UA3electromagnetic compatibility | ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM4UA3electromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM4UA3electromagnetic compatibility | Class B Group1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM4UA3electromagnetic compatibility | Class B Group1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM4UA3electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM4UA3electromagnetic compatibility | Class B Group1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM4UA3electromagnetic compatibility | Class B Group1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM4UA3electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4UA3
RM4UA3pollution degree | Not specified ¦ IEC60664-1
RM4UA3overvoltage category | Not specified ¦ IEC60664-1
RM4UA3circuit group | Supply,Terminal
RM4UA3circuit group | Input 1,
RM4UA3circuit group | Input 2,
RM4UA3circuit group | Input 3,
RM4UA3circuit group | Output 1,
RM4UA3circuit group | Not specified ¦ ,Output 2,
RM4UA3 | Not specified ¦ ,Supply,Rated
RM4UA3 | Not specified ¦ ,Input 1,Voltage
RM4UA3 | Input 2,Spec
RM4UA3 | Input 3,
RM4UA3 | Output 1,
RM4UA3 | Output 2,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Supply,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM4UA3[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Output 1,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM4UA3[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM4UA3[Uimp] rated impulse withstand voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM4UA3dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM4UA3dielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM4UA3dielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM4UA3dielectric strength | IEC60255-27,Supply / Output 1,
RM4UA3dielectric strength | IEC60255-27,Supply / Output 2,
RM4UA3dielectric strength | IEC60255-27,Output 1 / Output 2,
RM4UA3dielectric strength | IEC60255-27,Input 1 / Output 1,
RM4UA3dielectric strength | IEC60255-27,Input 1 / Output 2,
RM4UA3dielectric strength | IEC60255-27,Input 2 / Output 1,
RM4UA3dielectric strength | IEC60255-27,Input 2 / Output 2,
RM4UA3dielectric strength | IEC60255-27,Input 3 / Output 1,
RM4UA3dielectric strength | IEC60255-27,Input 3 / Output 2,
RM4UA3dielectric strength | IEC60255-27,Input 1 / Input 2,
RM4UA3dielectric strength | IEC60255-27,Input 2 / Input 3,
RM4UA3dielectric strength | IEC60255-27,Input 1 / Input 3,
RM4UA3insulation resistance | IEC60255-27,Supply / Input 1,
RM4UA3insulation resistance | IEC60255-27,Supply / Input 2,
RM4UA3insulation resistance | IEC60255-27,Supply / Input 3,
RM4UA3insulation resistance | IEC60255-27,Supply / Output 1,
RM4UA3insulation resistance | IEC60255-27,Supply / Output 2,
RM4UA3insulation resistance | IEC60255-27,Output 1 / Output 2,
RM4UA3insulation resistance | IEC60255-27,Input 1 / Output 1,
RM4UA3insulation resistance | IEC60255-27,Input 1 / Output 2,
RM4UA3insulation resistance | IEC60255-27,Input 2 / Output 1,
RM4UA3insulation resistance | IEC60255-27,Input 2 / Output 2,
RM4UA3insulation resistance | IEC60255-27,Input 3 / Output 1,
RM4UA3insulation resistance | IEC60255-27,Input 3 / Output 2,
RM4UA3insulation resistance | IEC60255-27,Input 1 / Input 2,
RM4UA3insulation resistance | IEC60255-27,Input 2 / Input 3,
RM4UA3insulation resistance | IEC60255-27,Input 1 / Input 3,
RM4UA3
RM4UA3[Us] rated supply voltage | RM4UA3xMW: ~/-- 24…240 RM4UA3xF: ~110…130 RM4UA3xM: ~220…240 RM4UA3xQ: ~380…415
RM4UA3supply voltage limits | 0.85…1.1 Un
RM4UA3polarity
RM4UA3supply frequency | 50 / 60
RM4UA3supply frequency | Not specified
RM4UA3power consumption | RM4UA3xMW: ~ 3.3VA, -- 1.2W RM4UA3xF: ~ 3.3VA RM4UA3xM: ~ 3.4VA RM4UA3xQ: ~ 3VA
RM4UA3immunity to microbreaks | Not specified
RM4UA3supply terminal | A1-A2
RM4UA3on-load factor
RM4UA3release of input voltage
RM4UA3
RM4UA3 | - ¦ ,Over / undervoltage (windows mode),
RM4UA3 | Without memory ¦ ,Over voltage,
RM4UA3 | Without memory ¦ ,Undervoltage ,
RM4UA3 | RM4UA31xx: ~/-- 0.05…5 RM4UA32xx: ~/-- 1…100 RM4UA33xx: ~/-- 30…500
RM4UA3 | RM4UA31xx: 6.6 RM4UA32xx: ~/-- 23 ¦ ,E1-M / B1-C,
RM4UA3 | RM4UA31xx: 43 RM4UA32xx: ~/-- 112 RM4UA33xx: ~/-- 668 ¦ ,E2-M / B2-C,
RM4UA3 | RM4UA31xx: 71 RM4UA32xx: ~/-- 225 RM4UA33xx: ~/-- 1111 ¦ ,E3-M / B3-C,
RM4UA3 | A1+ / A2-,
RM4UA3 | - ¦ ,Built in current transformer,
RM4UA3 | RM4UA31xx: ~/-- 0.05…0.5 RM4UA32xx: ~/-- 1…10 ¦ ,E1-M / B1-C,
RM4UA3 | RM4UA31xx: ~/-- 0.3…3 RM4UA32xx: ~/-- 5…50 RM4UA33xx: ~/-- 30…300 ¦ ,E2-M / B2-C,
RM4UA3 | RM4UA31xx: ~/-- 0.5…5 RM4UA32xx: ~/-- 10…100 RM4UA33xx: ~/-- 50…500 ¦ ,E3-M / B3-C,
RM4UA3 | A1+ / A2-,
RM4UA3 | - ¦ ,Built in current transformer,
RM4UA3 | - ¦ ,E1-M / B1-C,
RM4UA3 | Adjustable 10%...100% ¦ ,E2-M / B2-C,
RM4UA3 | Adjustable 10%...100% ¦ ,E3-M / B3-C,
RM4UA3 | A1+ / A2-,
RM4UA3 | - ¦ ,Built in current transformer,
RM4UA3 | Adjustable 5%...30% of threshold setting ¦ ,E1-M / B1-C,
RM4UA3 | Adjustable 5%...30% of threshold setting ¦ ,E2-M / B2-C,
RM4UA3 | Adjustable 5%...30% of threshold setting ¦ ,E3-M / B3-C,
RM4UA3 | A1+ / A2-,
RM4UA3 | - ¦ ,Built in current transformer,
RM4UA3 | Resistive Voltage Step Down
RM4UA3 | B1-C, B2-C, B3-C
RM4UA3 | 50 / 60
RM4UA3 | Not specified
RM4UA3 | +/- 5% of full scale value
RM4UA3 | Not specified
RM4UA3 | < 0.5% over whole range
RM4UA3 | 0.06% / oC
RM4UA3 | 80
RM4UA3 | Voltage Peak Detection
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3
RM4UA3output type | 2 x C/O relay contacts
RM4UA3output terminal | 15-16-18, 25-26-28
RM4UA3output logic | Energized on fault ¦ ,R1 (11-12-14),
RM4UA3output logic | R2 (21-22-24),
RM4UA3contacts material | Not specified
RM4UA3mechanical durability | Not specified ¦ IEC61810-1
RM4UA3electrical durability | Not specified ¦ IEC60947-4-1,AC-1,
RM4UA3electrical durability | IEC60947-4-1,DC-1,
RM4UA3electrical durability | IEC60947-5-1,AC-15,
RM4UA3electrical durability | IEC60947-5-1,DC-13,
RM4UA3[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4UA3[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4UA3maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM4UA3maximum switching capacity | 8 ¦ ,Maximum switching current,
RM4UA3maximum switching capacity | 2000VA ¦ ,Maximum switching capacity,
RM4UA3minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching voltage,
RM4UA3minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching current,
RM4UA3minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching capacity,
RM4UA3maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM4UA3maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM4UA3thermal current | IEC60947-5-1
RM4UA3short circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM4UA3short circuit protection | IEC62314,Solid State Output by external fuse,
RM4UA3
RM4UA3time delay type | · ¦ ,"OFF" delay,
RM4UA3time delay type | - ¦ ,"ON" delay,
RM4UA3time delay type | - ¦ ,Inhibition,
RM4UA3time delay range | Adjustable (0.5…1),(0.15…3),(0.5…10),(1.5…30) ¦ ,"OFF" delay,
RM4UA3time delay range | - ¦ ,"ON" delay,
RM4UA3time delay range | - ¦ ,Inhibition,
RM4UA3response time | Not specified ¦ ,on crossing the threshold,
RM4UA3response time
RM4UA3response time
RM4UA3response time
RM4UA3response time
RM4UA3power on delay | Not specified
RM4UA3reset time | Not specified ¦ ,through Un power reset,
RM4UA3reset time | through front panel reset,
RM4UA3reset time | through input control reset,
RM4UA3setting accuracy of time delay | +/- 10% of full scales
RM4UA3repeat accuracy of time delay | Not specified
RM4UA3time delay drift | < 0.5% over whole range
RM4UA3time delay drift | 0.07% / oC
RM4UA3
RM4UA3status LED
RM4UA3local signalling | Power supply availability,
RM4UA3local signalling | Power supply not availability,
RM4UA3local signalling | Timing in-progress,
RM4UA3local signalling | Output is energized,
RM4UA3local signalling | Output is de-energized,
RM4UA3local signalling | Range Setting Changes,
RM4UA3local signalling
RM4UA3local signalling
RM4UA3local signalling
RM4UA3local signalling
RM4UA3local signalling
RM4UA3local signalling
RM4UA3local signalling
RM4UA3local signalling
RM4UA3local signalling
RM4UA3
RM4UA3
RM4UA3
RM4UA3diagnostic button
RM4UA3
RM4UA3
RM4UA3
RM4UA3safety reliability data | MTTF,
RM4UA3safety reliability data | B10,
RM4UA3 | MTTFd,
RM4UA3 | B10d,
RM4UA3
RM4UA0
RM4UA0standards | EN60255-6, IEC60255-6
RM4UA0product certifications | UL, CSA, GL, C-Tick, GOST
RM4UA0marking | UL, CSA, GL, C-Tick, GOST, CE
RM4UA0directives | No 73/23/EEC + 93/68/EEC
RM4UA0directives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
RM4UA0directives | 2002/95/EC
RM4UA0
RM4UA0 | Not specified ¦ IEC60721-3-3,Climatic category,
RM4UA0 | Germanisher Lloyd,Environmental category,
RM4UA0ambient air temperature for storage | Not specified ¦ ,Storage,
RM4UA0ambient air temperature for operation | Not specified ¦ ,Operation,
RM4UA0relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
RM4UA0 | IEC60947-5-1,Cyclic Damp Heat Test,
RM4UA0vibration resistance | Not specified ¦ IEC60068-2-6
RM4UA0shock resistance | Not specified ¦ IEC60068-2-27
RM4UA0bump resistance | IEC60068-2-29
RM4UA0seismic resistance | IEC60068-3-3
RM4UA0IP degree of protection | Not specified ¦ IEC60529,Terminal Block,
RM4UA0IP degree of protection | Not specified ¦ IEC60529,Housing,
RM4UA0IP degree of protection | IEC60529,Front Panel,
RM4UA0
RM4UA0width | 22.5 x 78 x 80 ¦ ,Width,
RM4UA0height | Height,
RM4UA0depth | Depth,
RM4UA0net weight | 168
RM4UA0mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM4UA0mounting support | - ¦ IEC/EN 60715,With socket,
RM4UA0mounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
RM4UA0Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM4UA0Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM4UA0connections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM4UA0connections - terminals | Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM4UA0connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM4UA0connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4UA0tightening torque | Not specified ¦ IEC60947-1,Tightening torque,
RM4UA0cable stripping length | Not specified ¦ ,Cable stripping length,
RM4UA0duty time | Not specified
RM4UA0
RM4UA0electromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard,
RM4UA0electromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM4UA0electromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM4UA0electromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM4UA0electromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM4UA0electromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM4UA0electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM4UA0electromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM4UA0electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM4UA0electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM4UA0electromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM4UA0electromagnetic compatibility | ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM4UA0electromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM4UA0electromagnetic compatibility | Class B Group1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM4UA0electromagnetic compatibility | Class B Group1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM4UA0electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM4UA0electromagnetic compatibility | Class B Group1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM4UA0electromagnetic compatibility | Class B Group1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM4UA0electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4UA0
RM4UA0pollution degree | Not specified ¦ IEC60664-1
RM4UA0overvoltage category | Not specified ¦ IEC60664-1
RM4UA0circuit group | Supply,Terminal
RM4UA0circuit group | Input 1,
RM4UA0circuit group | Input 2,
RM4UA0circuit group | Input 3,
RM4UA0circuit group | Output 1,
RM4UA0circuit group | Not specified ¦ ,Output 2,
RM4UA0 | Not specified ¦ ,Supply,Rated
RM4UA0 | Not specified ¦ ,Input 1,Voltage
RM4UA0 | Input 2,Spec
RM4UA0 | Input 3,
RM4UA0 | Output 1,
RM4UA0 | Output 2,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Supply,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM4UA0[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Output 1,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM4UA0[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM4UA0[Uimp] rated impulse withstand voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM4UA0dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM4UA0dielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM4UA0dielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM4UA0dielectric strength | IEC60255-27,Supply / Output 1,
RM4UA0dielectric strength | IEC60255-27,Supply / Output 2,
RM4UA0dielectric strength | IEC60255-27,Output 1 / Output 2,
RM4UA0dielectric strength | IEC60255-27,Input 1 / Output 1,
RM4UA0dielectric strength | IEC60255-27,Input 1 / Output 2,
RM4UA0dielectric strength | IEC60255-27,Input 2 / Output 1,
RM4UA0dielectric strength | IEC60255-27,Input 2 / Output 2,
RM4UA0dielectric strength | IEC60255-27,Input 3 / Output 1,
RM4UA0dielectric strength | IEC60255-27,Input 3 / Output 2,
RM4UA0dielectric strength | IEC60255-27,Input 1 / Input 2,
RM4UA0dielectric strength | IEC60255-27,Input 2 / Input 3,
RM4UA0dielectric strength | IEC60255-27,Input 1 / Input 3,
RM4UA0insulation resistance | IEC60255-27,Supply / Input 1,
RM4UA0insulation resistance | IEC60255-27,Supply / Input 2,
RM4UA0insulation resistance | IEC60255-27,Supply / Input 3,
RM4UA0insulation resistance | IEC60255-27,Supply / Output 1,
RM4UA0insulation resistance | IEC60255-27,Supply / Output 2,
RM4UA0insulation resistance | IEC60255-27,Output 1 / Output 2,
RM4UA0insulation resistance | IEC60255-27,Input 1 / Output 1,
RM4UA0insulation resistance | IEC60255-27,Input 1 / Output 2,
RM4UA0insulation resistance | IEC60255-27,Input 2 / Output 1,
RM4UA0insulation resistance | IEC60255-27,Input 2 / Output 2,
RM4UA0insulation resistance | IEC60255-27,Input 3 / Output 1,
RM4UA0insulation resistance | IEC60255-27,Input 3 / Output 2,
RM4UA0insulation resistance | IEC60255-27,Input 1 / Input 2,
RM4UA0insulation resistance | IEC60255-27,Input 2 / Input 3,
RM4UA0insulation resistance | IEC60255-27,Input 1 / Input 3,
RM4UA0
RM4UA0[Us] rated supply voltage | RM4UA0xB: ~24 RM4UA0xF: ~110…130 RM4UA0xM: ~220…240
RM4UA0supply voltage limits | 0.85…1.1 Un
RM4UA0polarity
RM4UA0supply frequency | 50 / 60
RM4UA0supply frequency | Not specified
RM4UA0power consumption | RM4UA0xB: ~ 2VA RM4UA0xF: ~ 3.3VA RM4UA0xM: ~ 3.5VA
RM4UA0immunity to microbreaks | Not specified
RM4UA0supply terminal | A1-A2
RM4UA0on-load factor
RM4UA0release of input voltage
RM4UA0
RM4UA0 | - ¦ ,Over / undervoltage (windows mode),
RM4UA0 | Without memory ¦ ,Over voltage,
RM4UA0 | - ¦ ,Undervoltage ,
RM4UA0 | RM4UA01xx: ~/-- 0.05…5 RM4UA02xx: ~/-- 1…100 RM4UA03xx: ~/-- 30…500
RM4UA0 | RM4UA31xx: 6.6 RM4UA32xx: ~/-- 23 ¦ ,E1-M / B1-C,
RM4UA0 | RM4UA01xx: 43 RM4UA02xx: ~/-- 112 RM4UA03xx: ~/-- 668 ¦ ,E2-M / B2-C,
RM4UA0 | RM4UA01xx: 71 RM4UA02xx: ~/-- 225 RM4UA03xx: ~/-- 1111 ¦ ,E3-M / B3-C,
RM4UA0 | A1+ / A2-,
RM4UA0 | - ¦ ,Built in current transformer,
RM4UA0 | RM4UA01xx: ~/-- 0.05…0.5 RM4UA02xx: ~/-- 1…10 ¦ ,E1-M / B1-C,
RM4UA0 | RM4UA01xx: ~/-- 0.3…3 RM4UA02xx: ~/-- 5…50 RM4UA03xx: ~/-- 30…300 ¦ ,E2-M / B2-C,
RM4UA0 | RM4UA01xx: ~/-- 0.5…5 RM4UA02xx: ~/-- 10…100 RM4UA03xx: ~/-- 50…500 ¦ ,E3-M / B3-C,
RM4UA0 | A1+ / A2-,
RM4UA0 | - ¦ ,Built in current transformer,
RM4UA0 | - ¦ ,E1-M / B1-C,
RM4UA0 | Adjustable 10%...100% ¦ ,E2-M / B2-C,
RM4UA0 | Adjustable 10%...100% ¦ ,E3-M / B3-C,
RM4UA0 | A1+ / A2-,
RM4UA0 | - ¦ ,Built in current transformer,
RM4UA0 | Adjustable 5%...30% of threshold setting ¦ ,E1-M / B1-C,
RM4UA0 | Adjustable 5%...30% of threshold setting ¦ ,E2-M / B2-C,
RM4UA0 | Adjustable 5%...30% of threshold setting ¦ ,E3-M / B3-C,
RM4UA0 | A1+ / A2-,
RM4UA0 | - ¦ ,Built in current transformer,
RM4UA0 | Resistive Voltage Step Down
RM4UA0 | B1-C, B2-C, B3-C
RM4UA0 | 50 / 60
RM4UA0 | Not specified
RM4UA0 | +/- 5% of full scale value
RM4UA0 | Not specified
RM4UA0 | < 0.5% over whole range
RM4UA0 | 0.06% / oC
RM4UA0 | 80
RM4UA0 | Voltage Peak Detection
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0
RM4UA0output type | 1 x C/O relay contacts
RM4UA0output terminal | 15-16-18
RM4UA0output logic | Energized on fault ¦ ,R1 (11-12-14),
RM4UA0output logic | R2 (21-22-24),
RM4UA0contacts material | Not specified
RM4UA0mechanical durability | Not specified ¦ IEC61810-1
RM4UA0electrical durability | Not specified ¦ IEC60947-4-1,AC-1,
RM4UA0electrical durability | IEC60947-4-1,DC-1,
RM4UA0electrical durability | IEC60947-5-1,AC-15,
RM4UA0electrical durability | IEC60947-5-1,DC-13,
RM4UA0[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4UA0[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4UA0maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM4UA0maximum switching capacity | 8 ¦ ,Maximum switching current,
RM4UA0maximum switching capacity | 2000VA ¦ ,Maximum switching capacity,
RM4UA0minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching voltage,
RM4UA0minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching current,
RM4UA0minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching capacity,
RM4UA0maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM4UA0maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM4UA0thermal current | IEC60947-5-1
RM4UA0short circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM4UA0short circuit protection | IEC62314,Solid State Output by external fuse,
RM4UA0
RM4UA0time delay type | - ¦ ,"OFF" delay,
RM4UA0time delay type | - ¦ ,"ON" delay,
RM4UA0time delay type | - ¦ ,Inhibition,
RM4UA0time delay range | - ¦ ,"OFF" delay,
RM4UA0time delay range | - ¦ ,"ON" delay,
RM4UA0time delay range | - ¦ ,Inhibition,
RM4UA0response time | Not specified ¦ ,on crossing the threshold,
RM4UA0response time
RM4UA0response time
RM4UA0response time
RM4UA0response time
RM4UA0power on delay | Not specified
RM4UA0reset time | Not specified ¦ ,through Un power reset,
RM4UA0reset time | through front panel reset,
RM4UA0reset time | through input control reset,
RM4UA0setting accuracy of time delay | -
RM4UA0repeat accuracy of time delay | Not specified
RM4UA0time delay drift | -
RM4UA0time delay drift | -
RM4UA0
RM4UA0status LED
RM4UA0local signalling | Power supply availability,
RM4UA0local signalling | Power supply not availability,
RM4UA0local signalling | Timing in-progress,
RM4UA0local signalling | Output is energized,
RM4UA0local signalling | Output is de-energized,
RM4UA0local signalling | Range Setting Changes,
RM4UA0local signalling
RM4UA0local signalling
RM4UA0local signalling
RM4UA0local signalling
RM4UA0local signalling
RM4UA0local signalling
RM4UA0local signalling
RM4UA0local signalling
RM4UA0local signalling
RM4UA0
RM4UA0
RM4UA0
RM4UA0diagnostic button
RM4UA0
RM4UA0
RM4UA0
RM4UA0safety reliability data | MTTF,
RM4UA0safety reliability data | B10,
RM4UA0 | MTTFd,
RM4UA0 | B10d,
RM4UA0
RM22JA21MR
RM22JA21MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22JA21MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22JA21MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22JA21MRdirectives | 2014/35/EU
RM22JA21MRdirectives | 2014/30/EU
RM22JA21MRdirectives | 2011/65/EU
RM22JA21MR
RM22JA21MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category,
RM22JA21MR | Class C ¦ Germanisher Lloyd,Environmental category,
RM22JA21MRambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22JA21MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22JA21MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22JA21MR | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22JA21MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22JA21MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22JA21MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22JA21MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22JA21MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22JA21MRIP degree of protection | IP40 ¦ IEC60529,Housing,
RM22JA21MRIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22JA21MR
RM22JA21MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22JA21MRheight | Height,
RM22JA21MRdepth | Depth,
RM22JA21MRnet weight | 110
RM22JA21MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22JA21MRmounting support | - ¦ IEC/EN 60715,With socket,
RM22JA21MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22JA21MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22JA21MRMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22JA21MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22JA21MRconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22JA21MRconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22JA21MRconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22JA21MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22JA21MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22JA21MRduty time | 1
RM22JA21MR
RM22JA21MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22JA21MRelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22JA21MRelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22JA21MRelectromagnetic compatibility | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22JA21MRelectromagnetic compatibility | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22JA21MRelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22JA21MRelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22JA21MRelectromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22JA21MRelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22JA21MRelectromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
RM22JA21MRelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22JA21MRelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22JA21MRelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22JA21MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22JA21MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22JA21MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22JA21MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22JA21MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22JA21MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22JA21MR
RM22JA21MRpollution degree | 3 ¦ IEC60664-1
RM22JA21MRovervoltage category | 3 ¦ IEC60664-1
RM22JA21MRcircuit group | A1, A2 ¦ ,Supply,Terminal
RM22JA21MRcircuit group | E1, M ¦ ,Input 1,
RM22JA21MRcircuit group | E2, M ¦ ,Input 2,
RM22JA21MRcircuit group | E3, M ¦ ,Input 3,
RM22JA21MRcircuit group | 11,12,14 ¦ ,Output 1,
RM22JA21MRcircuit group | 21,22,24 ¦ ,Output 2,
RM22JA21MR | 24…240 AC/DC ¦ ,Supply,Rated
RM22JA21MR | 4..40mA AC/DC [full: 4..40mA AC/DC ] ¦ ,Input 1,Voltage
RM22JA21MR | 20..200mA AC/DC [full: 20..200mA AC/DC] ¦ ,Input 2,Spec
RM22JA21MR | 100..1000mA AC/DC [full: 100..1000mA AC/DC] ¦ ,Input 3,
RM22JA21MR | 250V ¦ ,Output 1,
RM22JA21MR | 250V ¦ ,Output 2,
RM22JA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply,
RM22JA21MR[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 1,
RM22JA21MR[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 2,
RM22JA21MR[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 3,
RM22JA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22JA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22JA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22JA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 2,Isolated
RM22JA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 3,Circuit
RM22JA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 1,
RM22JA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 2,
RM22JA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22JA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 1,
RM22JA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 2,
RM22JA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 1,
RM22JA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 2,
RM22JA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 3 / Output 1,
RM22JA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 3 / Output 2,
RM22JA21MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22JA21MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22JA21MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22JA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22JA21MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM22JA21MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM22JA21MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM22JA21MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22JA21MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22JA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22JA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated
RM22JA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit
RM22JA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22JA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22JA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22JA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM22JA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2,
RM22JA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1,
RM22JA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2,
RM22JA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1,
RM22JA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2,
RM22JA21MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22JA21MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22JA21MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22JA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM22JA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2,
RM22JA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3,
RM22JA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22JA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22JA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22JA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM22JA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2,
RM22JA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1,
RM22JA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2,
RM22JA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1,
RM22JA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2,
RM22JA21MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22JA21MRdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22JA21MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22JA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM22JA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2,
RM22JA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3,
RM22JA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22JA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22JA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22JA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM22JA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2,
RM22JA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1,
RM22JA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2,
RM22JA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1,
RM22JA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2,
RM22JA21MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22JA21MRinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22JA21MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22JA21MR
RM22JA21MR[Us] rated supply voltage | ~/-- 24…240
RM22JA21MRsupply voltage limits | ~/-- 20.4…264
RM22JA21MRpolarity
RM22JA21MRsupply frequency | 50 / 60
RM22JA21MRsupply frequency | 45…66
RM22JA21MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM22JA21MRimmunity to microbreaks | 50
RM22JA21MRsupply terminal | A1-A2
RM22JA21MRon-load factor | 1
RM22JA21MRrelease of input voltage | -
RM22JA21MR
RM22JA21MR | - ¦ ,Over / undercurrent (windows mode),
RM22JA21MR | Selectable with memory / without memory ¦ ,Over current,
RM22JA21MR | - ¦ ,Under current,
RM22JA21MR | ~/-- 4…1000
RM22JA21MR | 2.5 ¦ ,E1-M / B1-C,
RM22JA21MR | 0.5 ¦ ,E2-M / B2-C,
RM22JA21MR | 0.1 ¦ ,E3-M / B3-C,
RM22JA21MR | - ¦ ,A1+ / A2-,
RM22JA21MR | - ¦ ,Built in current transformer,
RM22JA21MR | ~/-- 4…40 ¦ ,E1-M / B1-C,
RM22JA21MR | ~/-- 20…200 ¦ ,E2-M / B2-C,
RM22JA21MR | ~/-- 100…1000 ¦ ,E3-M / B3-C,
RM22JA21MR | - ¦ ,A1+ / A2-,
RM22JA21MR | - ¦ ,Built in current transformer,
RM22JA21MR | Adjustable 10%...100% of 40 ¦ ,E1-M / B1-C,
RM22JA21MR | Adjustable 10%...100% of 200 ¦ ,E2-M / B2-C,
RM22JA21MR | Adjustable 10%...100% of 1000 ¦ ,E3-M / B3-C,
RM22JA21MR | - ¦ ,A1+ / A2-,
RM22JA21MR | - ¦ ,Built in current transformer,
RM22JA21MR | Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C,
RM22JA21MR | Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C,
RM22JA21MR | Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C,
RM22JA21MR | - ¦ ,A1+ / A2-,
RM22JA21MR | - ¦ ,Built in current transformer,
RM22JA21MR | Shunt resistor
RM22JA21MR | E1-M, E2-M, E3-M
RM22JA21MR | 50 / 60
RM22JA21MR | 36…77
RM22JA21MR | +/- 10% of full scale value
RM22JA21MR | +/- 0.5%
RM22JA21MR | < 1% over whole range
RM22JA21MR | 0.05% / oC
RM22JA21MR | 30 100
RM22JA21MR | True RMS
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MR
RM22JA21MRoutput type | 2 x C/O relay contacts
RM22JA21MRoutput terminal | 11-12-14, 21-22-24
RM22JA21MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22JA21MRoutput logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22JA21MRcontacts material | Cadmium free
RM22JA21MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22JA21MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22JA21MRelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22JA21MRelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22JA21MRelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22JA21MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22JA21MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22JA21MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22JA21MRmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM22JA21MRmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM22JA21MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22JA21MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22JA21MRminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22JA21MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22JA21MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22JA21MRthermal current | 8A ¦ IEC60947-5-1
RM22JA21MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22JA21MRshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22JA21MR
RM22JA21MRtime delay type | Yes ¦ ,"OFF" delay,
RM22JA21MRtime delay type | - ¦ ,"ON" delay,
RM22JA21MRtime delay type | - ¦ ,Inhibition,
RM22JA21MRtime delay range | - ¦ ,"OFF" delay,
RM22JA21MRtime delay range | - ¦ ,"ON" delay,
RM22JA21MRtime delay range | - ¦ ,Inhibition,
RM22JA21MRresponse time | Not specified =< 500ms ¦ ,on crossing the threshold,
RM22JA21MRresponse time
RM22JA21MRresponse time
RM22JA21MRresponse time
RM22JA21MRresponse time
RM22JA21MRpower on delay | 0
RM22JA21MRreset time | 0
RM22JA21MRreset time | through front panel reset,
RM22JA21MRreset time | through input control reset,
RM22JA21MRsetting accuracy of time delay | +/- 10% of full scales
RM22JA21MRrepeat accuracy of time delay | +/- 2%
RM22JA21MRtime delay drift | < 1
RM22JA21MRtime delay drift | < 0.05
RM22JA21MR
RM22JA21MRstatus LED | Dial pointer (Green) R (Amber)
RM22JA21MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22JA21MRlocal signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22JA21MRlocal signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22JA21MRlocal signalling | R - ON ¦ ,Output is energized,
RM22JA21MRlocal signalling | R - OFF ¦ ,Output is de-energized,
RM22JA21MRlocal signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22JA21MRlocal signalling
RM22JA21MRlocal signalling
RM22JA21MRlocal signalling
RM22JA21MRlocal signalling
RM22JA21MRlocal signalling
RM22JA21MRlocal signalling
RM22JA21MRlocal signalling
RM22JA21MRlocal signalling
RM22JA21MRlocal signalling
RM22JA21MR
RM22JA21MR | Yes
RM22JA21MR | 1) Will always illuminated when power is supplied to the product
RM22JA21MRdiagnostic button | Output will be de-energized when activated
RM22JA21MR | -
RM22JA21MR | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22JA21MR
RM22JA21MRsafety reliability data | 2,600,000 hours ¦ ,MTTF,
RM22JA21MRsafety reliability data | 270,000 hours ¦ ,B10,
RM22JA21MR | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22JA21MR | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22JA21MR
RM22JA31MR
RM22JA31MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22JA31MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22JA31MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22JA31MRdirectives | 2014/35/EU
RM22JA31MRdirectives | 2014/30/EU
RM22JA31MRdirectives | 2011/65/EU
RM22JA31MR
RM22JA31MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category,
RM22JA31MR | Class C ¦ Germanisher Lloyd,Environmental category,
RM22JA31MRambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22JA31MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22JA31MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22JA31MR | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM22JA31MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22JA31MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22JA31MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22JA31MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22JA31MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22JA31MRIP degree of protection | IP40 ¦ IEC60529,Housing,
RM22JA31MRIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22JA31MR
RM22JA31MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22JA31MRheight | Height,
RM22JA31MRdepth | Depth,
RM22JA31MRnet weight | 110
RM22JA31MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22JA31MRmounting support | - ¦ IEC/EN 60715,With socket,
RM22JA31MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22JA31MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22JA31MRMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22JA31MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22JA31MRconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22JA31MRconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22JA31MRconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22JA31MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22JA31MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22JA31MRduty time | 1
RM22JA31MR
RM22JA31MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM22JA31MRelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22JA31MRelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22JA31MRelectromagnetic compatibility | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM22JA31MRelectromagnetic compatibility | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM22JA31MRelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22JA31MRelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM22JA31MRelectromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22JA31MRelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM22JA31MRelectromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
RM22JA31MRelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM22JA31MRelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22JA31MRelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM22JA31MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22JA31MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22JA31MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22JA31MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22JA31MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22JA31MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22JA31MR
RM22JA31MRpollution degree | 3 ¦ IEC60664-1
RM22JA31MRovervoltage category | 3 ¦ IEC60664-1
RM22JA31MRcircuit group | A1, A2 ¦ ,Supply,Terminal
RM22JA31MRcircuit group | E1, M ¦ ,Input 1,
RM22JA31MRcircuit group | E2, M ¦ ,Input 2,
RM22JA31MRcircuit group | E3, M ¦ ,Input 3,
RM22JA31MRcircuit group | 11,12,14 ¦ ,Output 1,
RM22JA31MRcircuit group | 21,22,24 ¦ ,Output 2,
RM22JA31MR | 24…240 AC/DC ¦ ,Supply,Rated
RM22JA31MR | 4..40mA AC/DC [full: 4..40mA AC/DC ] ¦ ,Input 1,Voltage
RM22JA31MR | 20..200mA AC/DC [full: 20..200mA AC/DC] ¦ ,Input 2,Spec
RM22JA31MR | 100..1000mA AC/DC [full: 100..1000mA AC/DC] ¦ ,Input 3,
RM22JA31MR | 250V ¦ ,Output 1,
RM22JA31MR | 250V ¦ ,Output 2,
RM22JA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply,
RM22JA31MR[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 1,
RM22JA31MR[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 2,
RM22JA31MR[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 3,
RM22JA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM22JA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM22JA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22JA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 2,Isolated
RM22JA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 3,Circuit
RM22JA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 1,
RM22JA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 2,
RM22JA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM22JA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 1,
RM22JA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 2,
RM22JA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 1,
RM22JA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 2,
RM22JA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 3 / Output 1,
RM22JA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 3 / Output 2,
RM22JA31MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22JA31MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22JA31MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22JA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM22JA31MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM22JA31MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM22JA31MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM22JA31MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM22JA31MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM22JA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM22JA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated
RM22JA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit
RM22JA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM22JA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM22JA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM22JA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM22JA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2,
RM22JA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1,
RM22JA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2,
RM22JA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1,
RM22JA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2,
RM22JA31MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM22JA31MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM22JA31MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM22JA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM22JA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2,
RM22JA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3,
RM22JA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM22JA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM22JA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM22JA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM22JA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2,
RM22JA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1,
RM22JA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2,
RM22JA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1,
RM22JA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2,
RM22JA31MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM22JA31MRdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM22JA31MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM22JA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM22JA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2,
RM22JA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3,
RM22JA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM22JA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM22JA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM22JA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM22JA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2,
RM22JA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1,
RM22JA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2,
RM22JA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1,
RM22JA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2,
RM22JA31MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM22JA31MRinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM22JA31MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM22JA31MR
RM22JA31MR[Us] rated supply voltage | ~/-- 24…240
RM22JA31MRsupply voltage limits | ~/-- 20.4…264
RM22JA31MRpolarity
RM22JA31MRsupply frequency | 50 / 60
RM22JA31MRsupply frequency | 45…66
RM22JA31MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM22JA31MRimmunity to microbreaks | 50
RM22JA31MRsupply terminal | A1-A2
RM22JA31MRon-load factor | 1
RM22JA31MRrelease of input voltage | -
RM22JA31MR
RM22JA31MR | Selectable with memory / without memory ¦ ,Over / undercurrent (windows mode),
RM22JA31MR | Selectable with memory / without memory ¦ ,Over current,
RM22JA31MR | Selectable with memory / without memory ¦ ,Under current,
RM22JA31MR | ~/-- 4…1000
RM22JA31MR | 2.5 ¦ ,E1-M / B1-C,
RM22JA31MR | 0.5 ¦ ,E2-M / B2-C,
RM22JA31MR | 0.1 ¦ ,E3-M / B3-C,
RM22JA31MR | - ¦ ,A1+ / A2-,
RM22JA31MR | - ¦ ,Built in current transformer,
RM22JA31MR | ~/-- 4…40 ¦ ,E1-M / B1-C,
RM22JA31MR | ~/-- 20…200 ¦ ,E2-M / B2-C,
RM22JA31MR | ~/-- 100…1000 ¦ ,E3-M / B3-C,
RM22JA31MR | - ¦ ,A1+ / A2-,
RM22JA31MR | - ¦ ,Built in current transformer,
RM22JA31MR | Adjustable 10%...100% of 40 ¦ ,E1-M / B1-C,
RM22JA31MR | Adjustable 10%...100% of 200 ¦ ,E2-M / B2-C,
RM22JA31MR | Adjustable 10%...100% of 1000 ¦ ,E3-M / B3-C,
RM22JA31MR | - ¦ ,A1+ / A2-,
RM22JA31MR | - ¦ ,Built in current transformer,
RM22JA31MR | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E1-M / B1-C,
RM22JA31MR | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E2-M / B2-C,
RM22JA31MR | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E3-M / B3-C,
RM22JA31MR | - ¦ ,A1+ / A2-,
RM22JA31MR | - ¦ ,Built in current transformer,
RM22JA31MR | Shunt resistor
RM22JA31MR | E1-M, E2-M, E3-M
RM22JA31MR | 50 / 60
RM22JA31MR | 36…77
RM22JA31MR | +/- 10% of full scale value
RM22JA31MR | +/- 0.5%
RM22JA31MR | < 1% over whole range
RM22JA31MR | 0.05% / oC
RM22JA31MR | 30 100
RM22JA31MR | True RMS
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MR
RM22JA31MRoutput type | 2 x C/O relay contacts
RM22JA31MRoutput terminal | 11-12-14, 21-22-24
RM22JA31MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22JA31MRoutput logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM22JA31MRcontacts material | Cadmium free
RM22JA31MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22JA31MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM22JA31MRelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM22JA31MRelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM22JA31MRelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22JA31MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22JA31MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22JA31MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM22JA31MRmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM22JA31MRmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM22JA31MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM22JA31MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM22JA31MRminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22JA31MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22JA31MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22JA31MRthermal current | 8A ¦ IEC60947-5-1
RM22JA31MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM22JA31MRshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM22JA31MR
RM22JA31MRtime delay type | Yes ¦ ,"OFF" delay,
RM22JA31MRtime delay type | - ¦ ,"ON" delay,
RM22JA31MRtime delay type | - ¦ ,Inhibition,
RM22JA31MRtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay,
RM22JA31MRtime delay range | - ¦ ,"ON" delay,
RM22JA31MRtime delay range | - ¦ ,Inhibition,
RM22JA31MRresponse time | Not specified =< 500ms ¦ ,on crossing the threshold,
RM22JA31MRresponse time
RM22JA31MRresponse time
RM22JA31MRresponse time
RM22JA31MRresponse time
RM22JA31MRpower on delay | 0
RM22JA31MRreset time | 0
RM22JA31MRreset time | through front panel reset,
RM22JA31MRreset time | through input control reset,
RM22JA31MRsetting accuracy of time delay | +/- 10% of full scales
RM22JA31MRrepeat accuracy of time delay | +/- 2%
RM22JA31MRtime delay drift | < 1
RM22JA31MRtime delay drift | < 0.05
RM22JA31MR
RM22JA31MRstatus LED | Dial pointer (Green) R (Amber)
RM22JA31MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability,
RM22JA31MRlocal signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM22JA31MRlocal signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM22JA31MRlocal signalling | R - ON ¦ ,Output is energized,
RM22JA31MRlocal signalling | R - OFF ¦ ,Output is de-energized,
RM22JA31MRlocal signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22JA31MRlocal signalling
RM22JA31MRlocal signalling
RM22JA31MRlocal signalling
RM22JA31MRlocal signalling
RM22JA31MRlocal signalling
RM22JA31MRlocal signalling
RM22JA31MRlocal signalling
RM22JA31MRlocal signalling
RM22JA31MRlocal signalling
RM22JA31MR
RM22JA31MR | Yes
RM22JA31MR | 1) Will always illuminated when power is supplied to the product
RM22JA31MRdiagnostic button | Output will be de-energized when activated
RM22JA31MR | -
RM22JA31MR | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM22JA31MR
RM22JA31MRsafety reliability data | 2,600,000 hours ¦ ,MTTF,
RM22JA31MRsafety reliability data | 270,000 hours ¦ ,B10,
RM22JA31MR | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM22JA31MR | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22JA31MR
RM35JA32MR
RM35JA32MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM35JA32MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35JA32MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35JA32MRdirectives | 2014/35/EU
RM35JA32MRdirectives | 2014/30/EU
RM35JA32MRdirectives | 2011/65/EU
RM35JA32MR
RM35JA32MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category,
RM35JA32MR | Class C ¦ Germanisher Lloyd,Environmental category,
RM35JA32MRambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM35JA32MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM35JA32MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM35JA32MR | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM35JA32MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM35JA32MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM35JA32MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM35JA32MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM35JA32MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM35JA32MRIP degree of protection | IP30 ¦ IEC60529,Housing,
RM35JA32MRIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM35JA32MR
RM35JA32MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM35JA32MRheight | Height,
RM35JA32MRdepth | Depth,
RM35JA32MRnet weight | 120
RM35JA32MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM35JA32MRmounting support | - ¦ IEC/EN 60715,With socket,
RM35JA32MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35JA32MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM35JA32MRMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM35JA32MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35JA32MRconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35JA32MRconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM35JA32MRconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35JA32MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM35JA32MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM35JA32MRduty time | 1
RM35JA32MR
RM35JA32MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM35JA32MRelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM35JA32MRelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM35JA32MRelectromagnetic compatibility | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM35JA32MRelectromagnetic compatibility | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM35JA32MRelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM35JA32MRelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM35JA32MRelectromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35JA32MRelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM35JA32MRelectromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
RM35JA32MRelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM35JA32MRelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35JA32MRelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM35JA32MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35JA32MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35JA32MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM35JA32MRelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35JA32MRelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35JA32MRelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35JA32MR
RM35JA32MRpollution degree | 3 ¦ IEC60664-1
RM35JA32MRovervoltage category | 3 ¦ IEC60664-1
RM35JA32MRcircuit group | A1, A2 ¦ ,Supply,Terminal
RM35JA32MRcircuit group | E1, M ¦ ,Input 1,
RM35JA32MRcircuit group | E2, M ¦ ,Input 2,
RM35JA32MRcircuit group | E3, M ¦ ,Input 3,
RM35JA32MRcircuit group | 11,12,14 ¦ ,Output 1,
RM35JA32MRcircuit group | 21,22,24 ¦ ,Output 2,
RM35JA32MR | 24…240 AC/DC ¦ ,Supply,Rated
RM35JA32MR | 0.15..1.5A AC/DC [full: 0.18..1.2A AC/DC] ¦ ,Input 1,Voltage
RM35JA32MR | 0.5..5A AC/DC [full: 6..4A AC/DC] ¦ ,Input 2,Spec
RM35JA32MR | 1.8..12A AC/DC [full: 1.5..15A AC/DC] ¦ ,Input 3,
RM35JA32MR | 250V ¦ ,Output 1,
RM35JA32MR | 250V ¦ ,Output 2,
RM35JA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply,
RM35JA32MR[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 1,
RM35JA32MR[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 2,
RM35JA32MR[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 3,
RM35JA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM35JA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM35JA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35JA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 2,Isolated
RM35JA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 3,Circuit
RM35JA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 1,
RM35JA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Output 2,
RM35JA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM35JA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 1,
RM35JA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 2,
RM35JA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 1,
RM35JA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 2,
RM35JA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 3 / Output 1,
RM35JA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 3 / Output 2,
RM35JA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM35JA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM35JA32MR[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM35JA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM35JA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM35JA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM35JA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM35JA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM35JA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM35JA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35JA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated
RM35JA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit
RM35JA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM35JA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM35JA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM35JA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM35JA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2,
RM35JA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1,
RM35JA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2,
RM35JA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1,
RM35JA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2,
RM35JA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM35JA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM35JA32MR[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM35JA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM35JA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2,
RM35JA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3,
RM35JA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM35JA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM35JA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM35JA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM35JA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2,
RM35JA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1,
RM35JA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2,
RM35JA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1,
RM35JA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2,
RM35JA32MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM35JA32MRdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM35JA32MRdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM35JA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM35JA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2,
RM35JA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3,
RM35JA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM35JA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM35JA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM35JA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM35JA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2,
RM35JA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1,
RM35JA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2,
RM35JA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1,
RM35JA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2,
RM35JA32MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM35JA32MRinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM35JA32MRinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM35JA32MR
RM35JA32MR[Us] rated supply voltage | ~/-- 24…240
RM35JA32MRsupply voltage limits | ~/-- 20.4…264
RM35JA32MRpolarity
RM35JA32MRsupply frequency | 50 / 60
RM35JA32MRsupply frequency | 45…66
RM35JA32MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM35JA32MRimmunity to microbreaks | 50
RM35JA32MRsupply terminal | A1-A2
RM35JA32MRon-load factor | 1
RM35JA32MRrelease of input voltage | -
RM35JA32MR
RM35JA32MR | Selectable with memory / without memory ¦ ,Over / undercurrent (windows mode),
RM35JA32MR | Selectable with memory / without memory ¦ ,Over current,
RM35JA32MR | Selectable with memory / without memory ¦ ,Under current,
RM35JA32MR | ~/-- 150…15000
RM35JA32MR | 0.05 ¦ ,E1-M / B1-C,
RM35JA32MR | 0.015 ¦ ,E2-M / B2-C,
RM35JA32MR | 0.005 ¦ ,E3-M / B3-C,
RM35JA32MR | - ¦ ,A1+ / A2-,
RM35JA32MR | Built in current transformer,
RM35JA32MR | ~/-- 150…1500 ¦ ,E1-M / B1-C,
RM35JA32MR | ~/-- 500…5000 ¦ ,E2-M / B2-C,
RM35JA32MR | ~/-- 1500…15000 ¦ ,E3-M / B3-C,
RM35JA32MR | - ¦ ,A1+ / A2-,
RM35JA32MR | - ¦ ,Built in current transformer,
RM35JA32MR | Adjustable 10%...100% of 1500 ¦ ,E1-M / B1-C,
RM35JA32MR | Adjustable 10%...100% of 5000 ¦ ,E2-M / B2-C,
RM35JA32MR | Adjustable 10%...100% of 15000 ¦ ,E3-M / B3-C,
RM35JA32MR | - ¦ ,A1+ / A2-,
RM35JA32MR | - ¦ ,Built in current transformer,
RM35JA32MR | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E1-M / B1-C,
RM35JA32MR | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E2-M / B2-C,
RM35JA32MR | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E3-M / B3-C,
RM35JA32MR | - ¦ ,A1+ / A2-,
RM35JA32MR | - ¦ ,Built in current transformer,
RM35JA32MR | Shunt resistor
RM35JA32MR | E1-M, E2-M, E3-M
RM35JA32MR | 50 / 60
RM35JA32MR | 36…77
RM35JA32MR | +/- 10% of full scale value
RM35JA32MR | +/- 0.5%
RM35JA32MR | < 1% over whole range
RM35JA32MR | 0.05% / oC
RM35JA32MR | 30 100
RM35JA32MR | True RMS
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MR
RM35JA32MRoutput type | 2 x C/O relay contacts
RM35JA32MRoutput terminal | 11-12-14, 21-22-24
RM35JA32MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM35JA32MRoutput logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM35JA32MRcontacts material | Cadmium free
RM35JA32MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM35JA32MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM35JA32MRelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM35JA32MRelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM35JA32MRelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM35JA32MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM35JA32MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM35JA32MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM35JA32MRmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM35JA32MRmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM35JA32MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM35JA32MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM35JA32MRminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM35JA32MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35JA32MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35JA32MRthermal current | 8A ¦ IEC60947-5-1
RM35JA32MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM35JA32MRshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM35JA32MR
RM35JA32MRtime delay type | Yes ¦ ,"OFF" delay,
RM35JA32MRtime delay type | - ¦ ,"ON" delay,
RM35JA32MRtime delay type | - ¦ ,Inhibition,
RM35JA32MRtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay,
RM35JA32MRtime delay range | - ¦ ,"ON" delay,
RM35JA32MRtime delay range | - ¦ ,Inhibition,
RM35JA32MRresponse time | Not specified =< 500ms ¦ ,on crossing the threshold,
RM35JA32MRresponse time
RM35JA32MRresponse time
RM35JA32MRresponse time
RM35JA32MRresponse time
RM35JA32MRpower on delay | 0
RM35JA32MRreset time | 0
RM35JA32MRreset time | through front panel reset,
RM35JA32MRreset time | through input control reset,
RM35JA32MRsetting accuracy of time delay | +/- 10% of full scales
RM35JA32MRrepeat accuracy of time delay | +/- 2%
RM35JA32MRtime delay drift | < 1
RM35JA32MRtime delay drift | < 0.05
RM35JA32MR
RM35JA32MRstatus LED | Dial pointer (Green) R (Amber)
RM35JA32MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability,
RM35JA32MRlocal signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM35JA32MRlocal signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM35JA32MRlocal signalling | R - ON ¦ ,Output is energized,
RM35JA32MRlocal signalling | R - OFF ¦ ,Output is de-energized,
RM35JA32MRlocal signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM35JA32MRlocal signalling
RM35JA32MRlocal signalling
RM35JA32MRlocal signalling
RM35JA32MRlocal signalling
RM35JA32MRlocal signalling
RM35JA32MRlocal signalling
RM35JA32MRlocal signalling
RM35JA32MRlocal signalling
RM35JA32MRlocal signalling
RM35JA32MR
RM35JA32MR | Yes
RM35JA32MR | 1) Will always illuminated when power is supplied to the product
RM35JA32MRdiagnostic button | Output will be de-energized when activated
RM35JA32MR | -
RM35JA32MR | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM35JA32MR
RM35JA32MRsafety reliability data | 2,600,000 hours ¦ ,MTTF,
RM35JA32MRsafety reliability data | 270,000 hours ¦ ,B10,
RM35JA32MR | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM35JA32MR | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM35JA32MR
RM35JA32MT
RM35JA32MTstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM35JA32MTproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35JA32MTmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35JA32MTdirectives | 2014/35/EU
RM35JA32MTdirectives | 2014/30/EU
RM35JA32MTdirectives | 2011/65/EU
RM35JA32MT
RM35JA32MT | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category,
RM35JA32MT | Class C ¦ Germanisher Lloyd,Environmental category,
RM35JA32MTambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM35JA32MTambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM35JA32MTrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM35JA32MT | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test,
RM35JA32MTvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM35JA32MTshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM35JA32MTbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM35JA32MTseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM35JA32MTIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM35JA32MTIP degree of protection | IP30 ¦ IEC60529,Housing,
RM35JA32MTIP degree of protection | IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM35JA32MT
RM35JA32MTwidth | 22.5 x 90 x 73 ¦ ,Width,
RM35JA32MTheight | Height,
RM35JA32MTdepth | Depth,
RM35JA32MTnet weight | 120
RM35JA32MTmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket,
RM35JA32MTmounting support | - ¦ IEC/EN 60715,With socket,
RM35JA32MTmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35JA32MTMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM35JA32MTMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM35JA32MTconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35JA32MTconnections - terminals | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35JA32MTconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM35JA32MTconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35JA32MTtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM35JA32MTcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM35JA32MTduty time | 1
RM35JA32MT
RM35JA32MTelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard,
RM35JA32MTelectromagnetic compatibility | Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM35JA32MTelectromagnetic compatibility | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM35JA32MTelectromagnetic compatibility | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst,
RM35JA32MTelectromagnetic compatibility | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge,
RM35JA32MTelectromagnetic compatibility | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance,
RM35JA32MTelectromagnetic compatibility | Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field,
RM35JA32MTelectromagnetic compatibility | - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35JA32MTelectromagnetic compatibility | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave,
RM35JA32MTelectromagnetic compatibility | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption,
RM35JA32MTelectromagnetic compatibility | - ¦ IEC61000-4-13,Low frequency harmonics,
RM35JA32MTelectromagnetic compatibility | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35JA32MTelectromagnetic compatibility | IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard,
RM35JA32MTelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35JA32MTelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35JA32MTelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM35JA32MTelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35JA32MTelectromagnetic compatibility | Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35JA32MTelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35JA32MT
RM35JA32MTpollution degree | 3 ¦ IEC60664-1
RM35JA32MTovervoltage category | 3 ¦ IEC60664-1
RM35JA32MTcircuit group | A1, A2 ¦ ,Supply,Terminal
RM35JA32MTcircuit group | E1, M ¦ ,Input 1,
RM35JA32MTcircuit group | E2, M ¦ ,Input 2,
RM35JA32MTcircuit group | E3, M ¦ ,Input 3,
RM35JA32MTcircuit group | 11,12,14 ¦ ,Output 1,
RM35JA32MTcircuit group | 21,22,24 ¦ ,Output 2,
RM35JA32MT | 380…415 AC ¦ ,Supply,Rated
RM35JA32MT | 0.15..1.5A AC/DC [full: 0.18..1.2A AC/DC] ¦ ,Input 1,Voltage
RM35JA32MT | 0.5..5A AC/DC [full: 6..4A AC/DC] ¦ ,Input 2,Spec
RM35JA32MT | 1.8..12A AC/DC [full: 1.5..15A AC/DC] ¦ ,Input 3,
RM35JA32MT | 250V ¦ ,Output 1,
RM35JA32MT | 250V ¦ ,Output 2,
RM35JA32MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply,
RM35JA32MT[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 1,
RM35JA32MT[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 2,
RM35JA32MT[Ui] rated insulation voltage | 10V ¦ IEC60664-1,Input 3,
RM35JA32MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1,
RM35JA32MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 2,
RM35JA32MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35JA32MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply / Input 2,Isolated
RM35JA32MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply / Input 3,Circuit
RM35JA32MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply / Output 1,
RM35JA32MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply / Output 2,
RM35JA32MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Output 1 / Output 2,
RM35JA32MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 1,
RM35JA32MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 1 / Output 2,
RM35JA32MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 1,
RM35JA32MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 2 / Output 2,
RM35JA32MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 3 / Output 1,
RM35JA32MT[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Input 3 / Output 2,
RM35JA32MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM35JA32MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM35JA32MT[Ui] rated insulation voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM35JA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply,
RM35JA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1,
RM35JA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2,
RM35JA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 3,
RM35JA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 1,
RM35JA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Output 2,
RM35JA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic
RM35JA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated
RM35JA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit
RM35JA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1,
RM35JA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2,
RM35JA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2,
RM35JA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1,
RM35JA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2,
RM35JA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1,
RM35JA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2,
RM35JA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1,
RM35JA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2,
RM35JA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 2,
RM35JA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 2 / Input 3,
RM35JA32MT[Uimp] rated impulse withstand voltage | - ¦ IEC60664-1,Input 1 / Input 3,
RM35JA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1,
RM35JA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2,
RM35JA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3,
RM35JA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1,
RM35JA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2,
RM35JA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2,
RM35JA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1,
RM35JA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2,
RM35JA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1,
RM35JA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2,
RM35JA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1,
RM35JA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2,
RM35JA32MTdielectric strength | - ¦ IEC60255-27,Input 1 / Input 2,
RM35JA32MTdielectric strength | - ¦ IEC60255-27,Input 2 / Input 3,
RM35JA32MTdielectric strength | - ¦ IEC60255-27,Input 1 / Input 3,
RM35JA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1,
RM35JA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2,
RM35JA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3,
RM35JA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1,
RM35JA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2,
RM35JA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2,
RM35JA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1,
RM35JA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2,
RM35JA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1,
RM35JA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2,
RM35JA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1,
RM35JA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2,
RM35JA32MTinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 2,
RM35JA32MTinsulation resistance | - ¦ IEC60255-27,Input 2 / Input 3,
RM35JA32MTinsulation resistance | - ¦ IEC60255-27,Input 1 / Input 3,
RM35JA32MT
RM35JA32MT[Us] rated supply voltage | ~380…415
RM35JA32MTsupply voltage limits | ~323…456.5
RM35JA32MTpolarity
RM35JA32MTsupply frequency | 50 / 60
RM35JA32MTsupply frequency | 45…66
RM35JA32MTpower consumption | ~ 10VA ~ 8VA
RM35JA32MTimmunity to microbreaks | 50
RM35JA32MTsupply terminal | A1-A2
RM35JA32MTon-load factor | 1
RM35JA32MTrelease of input voltage | -
RM35JA32MT
RM35JA32MT | Selectable with memory / without memory ¦ ,Over / undercurrent (windows mode),
RM35JA32MT | Selectable with memory / without memory ¦ ,Over current,
RM35JA32MT | Selectable with memory / without memory ¦ ,Under current,
RM35JA32MT | ~/-- 150…15000
RM35JA32MT | 0.05 ¦ ,E1-M / B1-C,
RM35JA32MT | 0.015 ¦ ,E2-M / B2-C,
RM35JA32MT | 0.005 ¦ ,E3-M / B3-C,
RM35JA32MT | - ¦ ,A1+ / A2-,
RM35JA32MT | - ¦ ,Built in current transformer,
RM35JA32MT | ~/-- 150…1500 ¦ ,E1-M / B1-C,
RM35JA32MT | ~/-- 500…5000 ¦ ,E2-M / B2-C,
RM35JA32MT | ~/-- 1500…15000 ¦ ,E3-M / B3-C,
RM35JA32MT | - ¦ ,A1+ / A2-,
RM35JA32MT | - ¦ ,Built in current transformer,
RM35JA32MT | Adjustable 10%...100% of 1500 ¦ ,E1-M / B1-C,
RM35JA32MT | Adjustable 10%...100% of 5000 ¦ ,E2-M / B2-C,
RM35JA32MT | Adjustable 10%...100% of 15000 ¦ ,E3-M / B3-C,
RM35JA32MT | - ¦ ,A1+ / A2-,
RM35JA32MT | - ¦ ,Built in current transformer,
RM35JA32MT | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E1-M / B1-C,
RM35JA32MT | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E2-M / B2-C,
RM35JA32MT | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E3-M / B3-C,
RM35JA32MT | - ¦ ,A1+ / A2-,
RM35JA32MT | - ¦ ,Built in current transformer,
RM35JA32MT | Shunt resistor
RM35JA32MT | E1-M, E2-M, E3-M
RM35JA32MT | 50 / 60
RM35JA32MT | 36…77
RM35JA32MT | +/- 10% of full scale value (For 1.5A and 5A) +/- 20% of full scale value (For 15A)
RM35JA32MT | +/- 0.5%
RM35JA32MT | < 1% over whole range
RM35JA32MT | 0.05% / oC
RM35JA32MT | 30 100
RM35JA32MT | True RMS
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MT
RM35JA32MToutput type | 2 x C/O relay contacts
RM35JA32MToutput terminal | 11-12-14, 21-22-24
RM35JA32MToutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM35JA32MToutput logic | Energized on fault-free ¦ ,R2 (21-22-24),
RM35JA32MTcontacts material | Cadmium free
RM35JA32MTmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM35JA32MTelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1,
RM35JA32MTelectrical durability | NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1,
RM35JA32MTelectrical durability | NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15,
RM35JA32MTelectrical durability | NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM35JA32MT[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM35JA32MT[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM35JA32MTmaximum switching capacity | 250V ¦ ,Maximum switching voltage,
RM35JA32MTmaximum switching capacity | 8A ¦ ,Maximum switching current,
RM35JA32MTmaximum switching capacity | - ¦ ,Maximum switching capacity,
RM35JA32MTminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage,
RM35JA32MTminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching current,
RM35JA32MTminimum switching capacity | NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM35JA32MTmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35JA32MTmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35JA32MTthermal current | 8A ¦ IEC60947-5-1
RM35JA32MTshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse,
RM35JA32MTshort circuit protection | - ¦ IEC62314,Solid State Output by external fuse,
RM35JA32MT
RM35JA32MTtime delay type | Yes ¦ ,"OFF" delay,
RM35JA32MTtime delay type | - ¦ ,"ON" delay,
RM35JA32MTtime delay type | - ¦ ,Inhibition,
RM35JA32MTtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay,
RM35JA32MTtime delay range | - ¦ ,"ON" delay,
RM35JA32MTtime delay range | - ¦ ,Inhibition,
RM35JA32MTresponse time | Not specified =< 500ms ¦ ,on crossing the threshold,
RM35JA32MTresponse time
RM35JA32MTresponse time
RM35JA32MTresponse time
RM35JA32MTresponse time
RM35JA32MTpower on delay | 0
RM35JA32MTreset time | 0
RM35JA32MTreset time | through front panel reset,
RM35JA32MTreset time | through input control reset,
RM35JA32MTsetting accuracy of time delay | +/- 10% of full scales
RM35JA32MTrepeat accuracy of time delay | +/- 2%
RM35JA32MTtime delay drift | < 1
RM35JA32MTtime delay drift | < 0.05
RM35JA32MT
RM35JA32MTstatus LED | Dial pointer (Green) R (Amber)
RM35JA32MTlocal signalling | Dial pointer - ON ¦ ,Power supply availability,
RM35JA32MTlocal signalling | Dial pointer - OFF ¦ ,Power supply not availability,
RM35JA32MTlocal signalling | R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress,
RM35JA32MTlocal signalling | R - ON ¦ ,Output is energized,
RM35JA32MTlocal signalling | R - OFF ¦ ,Output is de-energized,
RM35JA32MTlocal signalling | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM35JA32MTlocal signalling
RM35JA32MTlocal signalling
RM35JA32MTlocal signalling
RM35JA32MTlocal signalling
RM35JA32MTlocal signalling
RM35JA32MTlocal signalling
RM35JA32MTlocal signalling
RM35JA32MTlocal signalling
RM35JA32MTlocal signalling
RM35JA32MT
RM35JA32MT | Yes
RM35JA32MT | 1) Will always illuminated when power is supplied to the product
RM35JA32MTdiagnostic button | Output will be de-energized when activated
RM35JA32MT | -
RM35JA32MT | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
RM35JA32MT
RM35JA32MTsafety reliability data | 2,600,000 hours ¦ ,MTTF,
RM35JA32MTsafety reliability data | 270,000 hours ¦ ,B10,
RM35JA32MT | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd,
RM35JA32MT | Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM35JA32MT
col13
col13standards
col13product certifications
col13marking
col13directives
col13directives
col13directives
col13
col13 | IEC60721-3-3,Climatic category,
col13 | Germanisher Lloyd,Environmental category,
col13ambient air temperature for storage | Storage,
col13ambient air temperature for operation | Operation,
col13relative humidity | IEC60068-2-30,Damp heat,
col13 | IEC60947-5-1,Cyclic Damp Heat Test,
col13vibration resistance | IEC60068-2-6
col13shock resistance | IEC60068-2-27
col13bump resistance | IEC60068-2-29
col13seismic resistance | IEC60068-3-3
col13IP degree of protection | IEC60529,Terminal Block,
col13IP degree of protection | IEC60529,Housing,
col13IP degree of protection | IEC60529,Front Panel,
col13
col13width | Width,
col13height | Height,
col13depth | Depth,
col13net weight
col13mounting support | IEC/EN 60715,Without socket,
col13mounting support | IEC/EN 60715,With socket,
col13mounting position | In relation to normal vertical mounting plane,
col13Minimum distance to adjacent devices | Horizontal,
col13Minimum distance to adjacent devices | Vertical,
col13connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
col13connections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
col13connections - terminals | IEC60947-1,Solid cable (spring terminal),
col13connections - terminals | IEC60947-1,Flexible cable (spring terminal),
col13tightening torque | IEC60947-1,Tightening torque,
col13cable stripping length | Cable stripping length,
col13duty time
col13
col13electromagnetic compatibility | Generic immunity standard,
col13electromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
col13electromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
col13electromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
col13electromagnetic compatibility | IEC61000-4-5,Surge,
col13electromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
col13electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
col13electromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
col13electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
col13electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
col13electromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
col13electromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
col13electromagnetic compatibility | Generic emission standard,
col13electromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
col13electromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
col13electromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
col13electromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
col13electromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
col13electromagnetic compatibility | Germanisher Lloyd,Conducted emission,
col13
col13pollution degree | IEC60664-1
col13overvoltage category | IEC60664-1
col13circuit group | Supply,Terminal
col13circuit group | Input 1,
col13circuit group | Input 2,
col13circuit group | Input 3,
col13circuit group | Output 1,
col13circuit group | Output 2,
col13 | Supply,Rated
col13 | Input 1,Voltage
col13 | Input 2,Spec
col13 | Input 3,
col13 | Output 1,
col13 | Output 2,
col13[Ui] rated insulation voltage | IEC60664-1,Supply,
col13[Ui] rated insulation voltage | IEC60664-1,Input 1,
col13[Ui] rated insulation voltage | IEC60664-1,Input 2,
col13[Ui] rated insulation voltage | IEC60664-1,Input 3,
col13[Ui] rated insulation voltage | IEC60664-1,Output 1,
col13[Ui] rated insulation voltage | IEC60664-1,Output 2,
col13[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
col13[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
col13[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
col13[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
col13[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
col13[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
col13[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
col13[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
col13[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
col13[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
col13[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
col13[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
col13[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
col13[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
col13[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
col13dielectric strength | IEC60255-27,Supply / Input 1,
col13dielectric strength | IEC60255-27,Supply / Input 2,
col13dielectric strength | IEC60255-27,Supply / Input 3,
col13dielectric strength | IEC60255-27,Supply / Output 1,
col13dielectric strength | IEC60255-27,Supply / Output 2,
col13dielectric strength | IEC60255-27,Output 1 / Output 2,
col13dielectric strength | IEC60255-27,Input 1 / Output 1,
col13dielectric strength | IEC60255-27,Input 1 / Output 2,
col13dielectric strength | IEC60255-27,Input 2 / Output 1,
col13dielectric strength | IEC60255-27,Input 2 / Output 2,
col13dielectric strength | IEC60255-27,Input 3 / Output 1,
col13dielectric strength | IEC60255-27,Input 3 / Output 2,
col13dielectric strength | IEC60255-27,Input 1 / Input 2,
col13dielectric strength | IEC60255-27,Input 2 / Input 3,
col13dielectric strength | IEC60255-27,Input 1 / Input 3,
col13insulation resistance | IEC60255-27,Supply / Input 1,
col13insulation resistance | IEC60255-27,Supply / Input 2,
col13insulation resistance | IEC60255-27,Supply / Input 3,
col13insulation resistance | IEC60255-27,Supply / Output 1,
col13insulation resistance | IEC60255-27,Supply / Output 2,
col13insulation resistance | IEC60255-27,Output 1 / Output 2,
col13insulation resistance | IEC60255-27,Input 1 / Output 1,
col13insulation resistance | IEC60255-27,Input 1 / Output 2,
col13insulation resistance | IEC60255-27,Input 2 / Output 1,
col13insulation resistance | IEC60255-27,Input 2 / Output 2,
col13insulation resistance | IEC60255-27,Input 3 / Output 1,
col13insulation resistance | IEC60255-27,Input 3 / Output 2,
col13insulation resistance | IEC60255-27,Input 1 / Input 2,
col13insulation resistance | IEC60255-27,Input 2 / Input 3,
col13insulation resistance | IEC60255-27,Input 1 / Input 3,
col13
col13[Us] rated supply voltage
col13supply voltage limits
col13polarity
col13supply frequency
col13supply frequency
col13power consumption
col13immunity to microbreaks
col13supply terminal
col13on-load factor
col13release of input voltage
col13
col13 | Over / undercurrent (windows mode),
col13 | Over current,
col13 | Under current,
col13
col13 | E1-M / B1-C,
col13 | E2-M / B2-C,
col13 | E3-M / B3-C,
col13 | A1+ / A2-,
col13 | Built in current transformer,
col13 | E1-M / B1-C,
col13 | E2-M / B2-C,
col13 | E3-M / B3-C,
col13 | A1+ / A2-,
col13 | Built in current transformer,
col13 | E1-M / B1-C,
col13 | E2-M / B2-C,
col13 | E3-M / B3-C,
col13 | A1+ / A2-,
col13 | Built in current transformer,
col13 | E1-M / B1-C,
col13 | E2-M / B2-C,
col13 | E3-M / B3-C,
col13 | A1+ / A2-,
col13 | Built in current transformer,
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13
col13output type
col13output terminal
col13output logic | R1 (11-12-14),
col13output logic | R2 (21-22-24),
col13contacts material
col13mechanical durability | IEC61810-1
col13electrical durability | IEC60947-4-1,AC-1,
col13electrical durability | IEC60947-4-1,DC-1,
col13electrical durability | IEC60947-5-1,AC-15,
col13electrical durability | IEC60947-5-1,DC-13,
col13[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col13[Ie] rated operational current | IEC61810-1,Rated switching current,
col13maximum switching capacity | Maximum switching voltage,
col13maximum switching capacity | Maximum switching current,
col13maximum switching capacity | Maximum switching capacity,
col13minimum switching capacity | IEC60947-5-4,Minimum switching voltage,
col13minimum switching capacity | IEC60947-5-4,Minimum switching current,
col13minimum switching capacity | IEC60947-5-4,Minimum switching capacity,
col13maximum voltage drop | IEC62314,Only for solid state output,
col13maximum leakage current | IEC62314,Only for solid state output,
col13thermal current | IEC60947-5-1
col13short circuit protection | IEC60947-5-1,Relay Output by external fuse,
col13short circuit protection | IEC62314,Solid State Output by external fuse,
col13
col13time delay type | "OFF" delay,
col13time delay type | "ON" delay,
col13time delay type | Inhibition,
col13time delay range | "OFF" delay,
col13time delay range | "ON" delay,
col13time delay range | Inhibition,
col13response time | on crossing the threshold,
col13response time
col13response time
col13response time
col13response time
col13power on delay
col13reset time | through Un power reset,
col13reset time | through front panel reset,
col13reset time | through input control reset,
col13setting accuracy of time delay
col13repeat accuracy of time delay
col13time delay drift
col13time delay drift
col13
col13status LED
col13local signalling | Power supply availability,
col13local signalling | Power supply not availability,
col13local signalling | Timing in-progress,
col13local signalling | Output is energized,
col13local signalling | Output is de-energized,
col13local signalling | Range Setting Changes,
col13local signalling
col13local signalling
col13local signalling
col13local signalling
col13local signalling
col13local signalling
col13local signalling
col13local signalling
col13local signalling
col13
col13
col13
col13diagnostic button
col13
col13
col13
col13safety reliability data | MTTF,
col13safety reliability data | B10,
col13 | MTTFd,
col13 | B10d,
col13
col14
col14standards
col14product certifications
col14marking
col14directives
col14directives
col14directives
col14
col14 | IEC60721-3-3,Climatic category,
col14 | Germanisher Lloyd,Environmental category,
col14ambient air temperature for storage | Storage,
col14ambient air temperature for operation | Operation,
col14relative humidity | IEC60068-2-30,Damp heat,
col14 | IEC60947-5-1,Cyclic Damp Heat Test,
col14vibration resistance | IEC60068-2-6
col14shock resistance | IEC60068-2-27
col14bump resistance | IEC60068-2-29
col14seismic resistance | IEC60068-3-3
col14IP degree of protection | IEC60529,Terminal Block,
col14IP degree of protection | IEC60529,Housing,
col14IP degree of protection | IEC60529,Front Panel,
col14
col14width | Width,
col14height | Height,
col14depth | Depth,
col14net weight
col14mounting support | IEC/EN 60715,Without socket,
col14mounting support | IEC/EN 60715,With socket,
col14mounting position | In relation to normal vertical mounting plane,
col14Minimum distance to adjacent devices | Horizontal,
col14Minimum distance to adjacent devices | Vertical,
col14connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
col14connections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
col14connections - terminals | IEC60947-1,Solid cable (spring terminal),
col14connections - terminals | IEC60947-1,Flexible cable (spring terminal),
col14tightening torque | IEC60947-1,Tightening torque,
col14cable stripping length | Cable stripping length,
col14duty time
col14
col14electromagnetic compatibility | Generic immunity standard,
col14electromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
col14electromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
col14electromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
col14electromagnetic compatibility | IEC61000-4-5,Surge,
col14electromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
col14electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
col14electromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
col14electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
col14electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
col14electromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
col14electromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
col14electromagnetic compatibility | Generic emission standard,
col14electromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
col14electromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
col14electromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
col14electromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
col14electromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
col14electromagnetic compatibility | Germanisher Lloyd,Conducted emission,
col14
col14pollution degree | IEC60664-1
col14overvoltage category | IEC60664-1
col14circuit group | Supply,Terminal
col14circuit group | Input 1,
col14circuit group | Input 2,
col14circuit group | Input 3,
col14circuit group | Output 1,
col14circuit group | Output 2,
col14 | Supply,Rated
col14 | Input 1,Voltage
col14 | Input 2,Spec
col14 | Input 3,
col14 | Output 1,
col14 | Output 2,
col14[Ui] rated insulation voltage | IEC60664-1,Supply,
col14[Ui] rated insulation voltage | IEC60664-1,Input 1,
col14[Ui] rated insulation voltage | IEC60664-1,Input 2,
col14[Ui] rated insulation voltage | IEC60664-1,Input 3,
col14[Ui] rated insulation voltage | IEC60664-1,Output 1,
col14[Ui] rated insulation voltage | IEC60664-1,Output 2,
col14[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
col14[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
col14[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
col14[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
col14[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
col14[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
col14[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
col14[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
col14[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
col14[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
col14[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
col14[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
col14[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
col14[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
col14[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
col14dielectric strength | IEC60255-27,Supply / Input 1,
col14dielectric strength | IEC60255-27,Supply / Input 2,
col14dielectric strength | IEC60255-27,Supply / Input 3,
col14dielectric strength | IEC60255-27,Supply / Output 1,
col14dielectric strength | IEC60255-27,Supply / Output 2,
col14dielectric strength | IEC60255-27,Output 1 / Output 2,
col14dielectric strength | IEC60255-27,Input 1 / Output 1,
col14dielectric strength | IEC60255-27,Input 1 / Output 2,
col14dielectric strength | IEC60255-27,Input 2 / Output 1,
col14dielectric strength | IEC60255-27,Input 2 / Output 2,
col14dielectric strength | IEC60255-27,Input 3 / Output 1,
col14dielectric strength | IEC60255-27,Input 3 / Output 2,
col14dielectric strength | IEC60255-27,Input 1 / Input 2,
col14dielectric strength | IEC60255-27,Input 2 / Input 3,
col14dielectric strength | IEC60255-27,Input 1 / Input 3,
col14insulation resistance | IEC60255-27,Supply / Input 1,
col14insulation resistance | IEC60255-27,Supply / Input 2,
col14insulation resistance | IEC60255-27,Supply / Input 3,
col14insulation resistance | IEC60255-27,Supply / Output 1,
col14insulation resistance | IEC60255-27,Supply / Output 2,
col14insulation resistance | IEC60255-27,Output 1 / Output 2,
col14insulation resistance | IEC60255-27,Input 1 / Output 1,
col14insulation resistance | IEC60255-27,Input 1 / Output 2,
col14insulation resistance | IEC60255-27,Input 2 / Output 1,
col14insulation resistance | IEC60255-27,Input 2 / Output 2,
col14insulation resistance | IEC60255-27,Input 3 / Output 1,
col14insulation resistance | IEC60255-27,Input 3 / Output 2,
col14insulation resistance | IEC60255-27,Input 1 / Input 2,
col14insulation resistance | IEC60255-27,Input 2 / Input 3,
col14insulation resistance | IEC60255-27,Input 1 / Input 3,
col14
col14[Us] rated supply voltage
col14supply voltage limits
col14polarity
col14supply frequency
col14supply frequency
col14power consumption
col14immunity to microbreaks
col14supply terminal
col14on-load factor
col14release of input voltage
col14
col14 | Over / undercurrent (windows mode),
col14 | Over current,
col14 | Under current,
col14
col14 | E1-M / B1-C,
col14 | E2-M / B2-C,
col14 | E3-M / B3-C,
col14 | A1+ / A2-,
col14 | Built in current transformer,
col14 | E1-M / B1-C,
col14 | E2-M / B2-C,
col14 | E3-M / B3-C,
col14 | A1+ / A2-,
col14 | Built in current transformer,
col14 | E1-M / B1-C,
col14 | E2-M / B2-C,
col14 | E3-M / B3-C,
col14 | A1+ / A2-,
col14 | Built in current transformer,
col14 | E1-M / B1-C,
col14 | E2-M / B2-C,
col14 | E3-M / B3-C,
col14 | A1+ / A2-,
col14 | Built in current transformer,
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14
col14output type
col14output terminal
col14output logic | R1 (11-12-14),
col14output logic | R2 (21-22-24),
col14contacts material
col14mechanical durability | IEC61810-1
col14electrical durability | IEC60947-4-1,AC-1,
col14electrical durability | IEC60947-4-1,DC-1,
col14electrical durability | IEC60947-5-1,AC-15,
col14electrical durability | IEC60947-5-1,DC-13,
col14[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col14[Ie] rated operational current | IEC61810-1,Rated switching current,
col14maximum switching capacity | Maximum switching voltage,
col14maximum switching capacity | Maximum switching current,
col14maximum switching capacity | Maximum switching capacity,
col14minimum switching capacity | IEC60947-5-4,Minimum switching voltage,
col14minimum switching capacity | IEC60947-5-4,Minimum switching current,
col14minimum switching capacity | IEC60947-5-4,Minimum switching capacity,
col14maximum voltage drop | IEC62314,Only for solid state output,
col14maximum leakage current | IEC62314,Only for solid state output,
col14thermal current | IEC60947-5-1
col14short circuit protection | IEC60947-5-1,Relay Output by external fuse,
col14short circuit protection | IEC62314,Solid State Output by external fuse,
col14
col14time delay type | "OFF" delay,
col14time delay type | "ON" delay,
col14time delay type | Inhibition,
col14time delay range | "OFF" delay,
col14time delay range | "ON" delay,
col14time delay range | Inhibition,
col14response time | on crossing the threshold,
col14response time
col14response time
col14response time
col14response time
col14power on delay
col14reset time | through Un power reset,
col14reset time | through front panel reset,
col14reset time | through input control reset,
col14setting accuracy of time delay
col14repeat accuracy of time delay
col14time delay drift
col14time delay drift
col14
col14status LED
col14local signalling | Power supply availability,
col14local signalling | Power supply not availability,
col14local signalling | Timing in-progress,
col14local signalling | Output is energized,
col14local signalling | Output is de-energized,
col14local signalling | Range Setting Changes,
col14local signalling
col14local signalling
col14local signalling
col14local signalling
col14local signalling
col14local signalling
col14local signalling
col14local signalling
col14local signalling
col14
col14
col14
col14diagnostic button
col14
col14
col14
col14safety reliability data | MTTF,
col14safety reliability data | B10,
col14 | MTTFd,
col14 | B10d,
col14
col15
col15standards
col15product certifications
col15marking
col15directives
col15directives
col15directives
col15
col15 | IEC60721-3-3,Climatic category,
col15 | Germanisher Lloyd,Environmental category,
col15ambient air temperature for storage | Storage,
col15ambient air temperature for operation | Operation,
col15relative humidity | IEC60068-2-30,Damp heat,
col15 | IEC60947-5-1,Cyclic Damp Heat Test,
col15vibration resistance | IEC60068-2-6
col15shock resistance | IEC60068-2-27
col15bump resistance | IEC60068-2-29
col15seismic resistance | IEC60068-3-3
col15IP degree of protection | IEC60529,Terminal Block,
col15IP degree of protection | IEC60529,Housing,
col15IP degree of protection | IEC60529,Front Panel,
col15
col15width | Width,
col15height | Height,
col15depth | Depth,
col15net weight
col15mounting support | IEC/EN 60715,Without socket,
col15mounting support | IEC/EN 60715,With socket,
col15mounting position | In relation to normal vertical mounting plane,
col15Minimum distance to adjacent devices | Horizontal,
col15Minimum distance to adjacent devices | Vertical,
col15connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
col15connections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
col15connections - terminals | IEC60947-1,Solid cable (spring terminal),
col15connections - terminals | IEC60947-1,Flexible cable (spring terminal),
col15tightening torque | IEC60947-1,Tightening torque,
col15cable stripping length | Cable stripping length,
col15duty time
col15
col15electromagnetic compatibility | Generic immunity standard,
col15electromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
col15electromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
col15electromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
col15electromagnetic compatibility | IEC61000-4-5,Surge,
col15electromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
col15electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
col15electromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
col15electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
col15electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
col15electromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
col15electromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
col15electromagnetic compatibility | Generic emission standard,
col15electromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
col15electromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
col15electromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
col15electromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
col15electromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
col15electromagnetic compatibility | Germanisher Lloyd,Conducted emission,
col15
col15pollution degree | IEC60664-1
col15overvoltage category | IEC60664-1
col15circuit group | Supply,Terminal
col15circuit group | Input 1,
col15circuit group | Input 2,
col15circuit group | Input 3,
col15circuit group | Output 1,
col15circuit group | Output 2,
col15 | Supply,Rated
col15 | Input 1,Voltage
col15 | Input 2,Spec
col15 | Input 3,
col15 | Output 1,
col15 | Output 2,
col15[Ui] rated insulation voltage | IEC60664-1,Supply,
col15[Ui] rated insulation voltage | IEC60664-1,Input 1,
col15[Ui] rated insulation voltage | IEC60664-1,Input 2,
col15[Ui] rated insulation voltage | IEC60664-1,Input 3,
col15[Ui] rated insulation voltage | IEC60664-1,Output 1,
col15[Ui] rated insulation voltage | IEC60664-1,Output 2,
col15[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
col15[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
col15[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
col15[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
col15[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
col15[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
col15[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
col15[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
col15[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
col15[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
col15[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
col15[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
col15[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
col15[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
col15[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
col15dielectric strength | IEC60255-27,Supply / Input 1,
col15dielectric strength | IEC60255-27,Supply / Input 2,
col15dielectric strength | IEC60255-27,Supply / Input 3,
col15dielectric strength | IEC60255-27,Supply / Output 1,
col15dielectric strength | IEC60255-27,Supply / Output 2,
col15dielectric strength | IEC60255-27,Output 1 / Output 2,
col15dielectric strength | IEC60255-27,Input 1 / Output 1,
col15dielectric strength | IEC60255-27,Input 1 / Output 2,
col15dielectric strength | IEC60255-27,Input 2 / Output 1,
col15dielectric strength | IEC60255-27,Input 2 / Output 2,
col15dielectric strength | IEC60255-27,Input 3 / Output 1,
col15dielectric strength | IEC60255-27,Input 3 / Output 2,
col15dielectric strength | IEC60255-27,Input 1 / Input 2,
col15dielectric strength | IEC60255-27,Input 2 / Input 3,
col15dielectric strength | IEC60255-27,Input 1 / Input 3,
col15insulation resistance | IEC60255-27,Supply / Input 1,
col15insulation resistance | IEC60255-27,Supply / Input 2,
col15insulation resistance | IEC60255-27,Supply / Input 3,
col15insulation resistance | IEC60255-27,Supply / Output 1,
col15insulation resistance | IEC60255-27,Supply / Output 2,
col15insulation resistance | IEC60255-27,Output 1 / Output 2,
col15insulation resistance | IEC60255-27,Input 1 / Output 1,
col15insulation resistance | IEC60255-27,Input 1 / Output 2,
col15insulation resistance | IEC60255-27,Input 2 / Output 1,
col15insulation resistance | IEC60255-27,Input 2 / Output 2,
col15insulation resistance | IEC60255-27,Input 3 / Output 1,
col15insulation resistance | IEC60255-27,Input 3 / Output 2,
col15insulation resistance | IEC60255-27,Input 1 / Input 2,
col15insulation resistance | IEC60255-27,Input 2 / Input 3,
col15insulation resistance | IEC60255-27,Input 1 / Input 3,
col15
col15[Us] rated supply voltage
col15supply voltage limits
col15polarity
col15supply frequency
col15supply frequency
col15power consumption
col15immunity to microbreaks
col15supply terminal
col15on-load factor
col15release of input voltage
col15
col15 | Over / undercurrent (windows mode),
col15 | Over current,
col15 | Under current,
col15
col15 | E1-M / B1-C,
col15 | E2-M / B2-C,
col15 | E3-M / B3-C,
col15 | A1+ / A2-,
col15 | Built in current transformer,
col15 | E1-M / B1-C,
col15 | E2-M / B2-C,
col15 | E3-M / B3-C,
col15 | A1+ / A2-,
col15 | Built in current transformer,
col15 | E1-M / B1-C,
col15 | E2-M / B2-C,
col15 | E3-M / B3-C,
col15 | A1+ / A2-,
col15 | Built in current transformer,
col15 | E1-M / B1-C,
col15 | E2-M / B2-C,
col15 | E3-M / B3-C,
col15 | A1+ / A2-,
col15 | Built in current transformer,
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15
col15output type
col15output terminal
col15output logic | R1 (11-12-14),
col15output logic | R2 (21-22-24),
col15contacts material
col15mechanical durability | IEC61810-1
col15electrical durability | IEC60947-4-1,AC-1,
col15electrical durability | IEC60947-4-1,DC-1,
col15electrical durability | IEC60947-5-1,AC-15,
col15electrical durability | IEC60947-5-1,DC-13,
col15[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col15[Ie] rated operational current | IEC61810-1,Rated switching current,
col15maximum switching capacity | Maximum switching voltage,
col15maximum switching capacity | Maximum switching current,
col15maximum switching capacity | Maximum switching capacity,
col15minimum switching capacity | IEC60947-5-4,Minimum switching voltage,
col15minimum switching capacity | IEC60947-5-4,Minimum switching current,
col15minimum switching capacity | IEC60947-5-4,Minimum switching capacity,
col15maximum voltage drop | IEC62314,Only for solid state output,
col15maximum leakage current | IEC62314,Only for solid state output,
col15thermal current | IEC60947-5-1
col15short circuit protection | IEC60947-5-1,Relay Output by external fuse,
col15short circuit protection | IEC62314,Solid State Output by external fuse,
col15
col15time delay type | "OFF" delay,
col15time delay type | "ON" delay,
col15time delay type | Inhibition,
col15time delay range | "OFF" delay,
col15time delay range | "ON" delay,
col15time delay range | Inhibition,
col15response time | on crossing the threshold,
col15response time
col15response time
col15response time
col15response time
col15power on delay
col15reset time | through Un power reset,
col15reset time | through front panel reset,
col15reset time | through input control reset,
col15setting accuracy of time delay
col15repeat accuracy of time delay
col15time delay drift
col15time delay drift
col15
col15status LED
col15local signalling | Power supply availability,
col15local signalling | Power supply not availability,
col15local signalling | Timing in-progress,
col15local signalling | Output is energized,
col15local signalling | Output is de-energized,
col15local signalling | Range Setting Changes,
col15local signalling
col15local signalling
col15local signalling
col15local signalling
col15local signalling
col15local signalling
col15local signalling
col15local signalling
col15local signalling
col15
col15
col15
col15diagnostic button
col15
col15
col15
col15safety reliability data | MTTF,
col15safety reliability data | B10,
col15 | MTTFd,
col15 | B10d,
col15
col16
col16standards
col16product certifications
col16marking
col16directives
col16directives
col16directives
col16
col16 | IEC60721-3-3,Climatic category,
col16 | Germanisher Lloyd,Environmental category,
col16ambient air temperature for storage | Storage,
col16ambient air temperature for operation | Operation,
col16relative humidity | IEC60068-2-30,Damp heat,
col16 | IEC60947-5-1,Cyclic Damp Heat Test,
col16vibration resistance | IEC60068-2-6
col16shock resistance | IEC60068-2-27
col16bump resistance | IEC60068-2-29
col16seismic resistance | IEC60068-3-3
col16IP degree of protection | IEC60529,Terminal Block,
col16IP degree of protection | IEC60529,Housing,
col16IP degree of protection | IEC60529,Front Panel,
col16
col16width | Width,
col16height | Height,
col16depth | Depth,
col16net weight
col16mounting support | IEC/EN 60715,Without socket,
col16mounting support | IEC/EN 60715,With socket,
col16mounting position | In relation to normal vertical mounting plane,
col16Minimum distance to adjacent devices | Horizontal,
col16Minimum distance to adjacent devices | Vertical,
col16connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
col16connections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
col16connections - terminals | IEC60947-1,Solid cable (spring terminal),
col16connections - terminals | IEC60947-1,Flexible cable (spring terminal),
col16tightening torque | IEC60947-1,Tightening torque,
col16cable stripping length | Cable stripping length,
col16duty time
col16
col16electromagnetic compatibility | Generic immunity standard,
col16electromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
col16electromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
col16electromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
col16electromagnetic compatibility | IEC61000-4-5,Surge,
col16electromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
col16electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
col16electromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
col16electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
col16electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
col16electromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
col16electromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
col16electromagnetic compatibility | Generic emission standard,
col16electromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
col16electromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
col16electromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
col16electromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
col16electromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
col16electromagnetic compatibility | Germanisher Lloyd,Conducted emission,
col16
col16pollution degree | IEC60664-1
col16overvoltage category | IEC60664-1
col16circuit group | Supply,Terminal
col16circuit group | Input 1,
col16circuit group | Input 2,
col16circuit group | Input 3,
col16circuit group | Output 1,
col16circuit group | Output 2,
col16 | Supply,Rated
col16 | Input 1,Voltage
col16 | Input 2,Spec
col16 | Input 3,
col16 | Output 1,
col16 | Output 2,
col16[Ui] rated insulation voltage | IEC60664-1,Supply,
col16[Ui] rated insulation voltage | IEC60664-1,Input 1,
col16[Ui] rated insulation voltage | IEC60664-1,Input 2,
col16[Ui] rated insulation voltage | IEC60664-1,Input 3,
col16[Ui] rated insulation voltage | IEC60664-1,Output 1,
col16[Ui] rated insulation voltage | IEC60664-1,Output 2,
col16[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
col16[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
col16[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
col16[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
col16[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
col16[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
col16[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
col16[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
col16[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
col16[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
col16[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
col16[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
col16[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
col16[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
col16[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
col16dielectric strength | IEC60255-27,Supply / Input 1,
col16dielectric strength | IEC60255-27,Supply / Input 2,
col16dielectric strength | IEC60255-27,Supply / Input 3,
col16dielectric strength | IEC60255-27,Supply / Output 1,
col16dielectric strength | IEC60255-27,Supply / Output 2,
col16dielectric strength | IEC60255-27,Output 1 / Output 2,
col16dielectric strength | IEC60255-27,Input 1 / Output 1,
col16dielectric strength | IEC60255-27,Input 1 / Output 2,
col16dielectric strength | IEC60255-27,Input 2 / Output 1,
col16dielectric strength | IEC60255-27,Input 2 / Output 2,
col16dielectric strength | IEC60255-27,Input 3 / Output 1,
col16dielectric strength | IEC60255-27,Input 3 / Output 2,
col16dielectric strength | IEC60255-27,Input 1 / Input 2,
col16dielectric strength | IEC60255-27,Input 2 / Input 3,
col16dielectric strength | IEC60255-27,Input 1 / Input 3,
col16insulation resistance | IEC60255-27,Supply / Input 1,
col16insulation resistance | IEC60255-27,Supply / Input 2,
col16insulation resistance | IEC60255-27,Supply / Input 3,
col16insulation resistance | IEC60255-27,Supply / Output 1,
col16insulation resistance | IEC60255-27,Supply / Output 2,
col16insulation resistance | IEC60255-27,Output 1 / Output 2,
col16insulation resistance | IEC60255-27,Input 1 / Output 1,
col16insulation resistance | IEC60255-27,Input 1 / Output 2,
col16insulation resistance | IEC60255-27,Input 2 / Output 1,
col16insulation resistance | IEC60255-27,Input 2 / Output 2,
col16insulation resistance | IEC60255-27,Input 3 / Output 1,
col16insulation resistance | IEC60255-27,Input 3 / Output 2,
col16insulation resistance | IEC60255-27,Input 1 / Input 2,
col16insulation resistance | IEC60255-27,Input 2 / Input 3,
col16insulation resistance | IEC60255-27,Input 1 / Input 3,
col16
col16[Us] rated supply voltage
col16supply voltage limits
col16polarity
col16supply frequency
col16supply frequency
col16power consumption
col16immunity to microbreaks
col16supply terminal
col16on-load factor
col16release of input voltage
col16
col16 | Over / undercurrent (windows mode),
col16 | Over current,
col16 | Under current,
col16
col16 | E1-M / B1-C,
col16 | E2-M / B2-C,
col16 | E3-M / B3-C,
col16 | A1+ / A2-,
col16 | Built in current transformer,
col16 | E1-M / B1-C,
col16 | E2-M / B2-C,
col16 | E3-M / B3-C,
col16 | A1+ / A2-,
col16 | Built in current transformer,
col16 | E1-M / B1-C,
col16 | E2-M / B2-C,
col16 | E3-M / B3-C,
col16 | A1+ / A2-,
col16 | Built in current transformer,
col16 | E1-M / B1-C,
col16 | E2-M / B2-C,
col16 | E3-M / B3-C,
col16 | A1+ / A2-,
col16 | Built in current transformer,
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16
col16output type
col16output terminal
col16output logic | R1 (11-12-14),
col16output logic | R2 (21-22-24),
col16contacts material
col16mechanical durability | IEC61810-1
col16electrical durability | IEC60947-4-1,AC-1,
col16electrical durability | IEC60947-4-1,DC-1,
col16electrical durability | IEC60947-5-1,AC-15,
col16electrical durability | IEC60947-5-1,DC-13,
col16[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col16[Ie] rated operational current | IEC61810-1,Rated switching current,
col16maximum switching capacity | Maximum switching voltage,
col16maximum switching capacity | Maximum switching current,
col16maximum switching capacity | Maximum switching capacity,
col16minimum switching capacity | IEC60947-5-4,Minimum switching voltage,
col16minimum switching capacity | IEC60947-5-4,Minimum switching current,
col16minimum switching capacity | IEC60947-5-4,Minimum switching capacity,
col16maximum voltage drop | IEC62314,Only for solid state output,
col16maximum leakage current | IEC62314,Only for solid state output,
col16thermal current | IEC60947-5-1
col16short circuit protection | IEC60947-5-1,Relay Output by external fuse,
col16short circuit protection | IEC62314,Solid State Output by external fuse,
col16
col16time delay type | "OFF" delay,
col16time delay type | "ON" delay,
col16time delay type | Inhibition,
col16time delay range | "OFF" delay,
col16time delay range | "ON" delay,
col16time delay range | Inhibition,
col16response time | on crossing the threshold,
col16response time
col16response time
col16response time
col16response time
col16power on delay
col16reset time | through Un power reset,
col16reset time | through front panel reset,
col16reset time | through input control reset,
col16setting accuracy of time delay
col16repeat accuracy of time delay
col16time delay drift
col16time delay drift
col16
col16status LED
col16local signalling | Power supply availability,
col16local signalling | Power supply not availability,
col16local signalling | Timing in-progress,
col16local signalling | Output is energized,
col16local signalling | Output is de-energized,
col16local signalling | Range Setting Changes,
col16local signalling
col16local signalling
col16local signalling
col16local signalling
col16local signalling
col16local signalling
col16local signalling
col16local signalling
col16local signalling
col16
col16
col16
col16diagnostic button
col16
col16
col16
col16safety reliability data | MTTF,
col16safety reliability data | B10,
col16 | MTTFd,
col16 | B10d,
col16
Competitor Spec Reference
Competitor Spec Referencestandards
Competitor Spec Referenceproduct certifications
Competitor Spec Referencemarking
Competitor Spec Referencedirectives
Competitor Spec Referencedirectives
Competitor Spec Referencedirectives
Competitor Spec Reference
Competitor Spec Reference | IEC60721-3-3,Climatic category,
Competitor Spec Reference | Germanisher Lloyd,Environmental category,
Competitor Spec Referenceambient air temperature for storage | Storage,
Competitor Spec Referenceambient air temperature for operation | Operation,
Competitor Spec Referencerelative humidity | IEC60068-2-30,Damp heat,
Competitor Spec Reference | IEC60947-5-1,Cyclic Damp Heat Test,
Competitor Spec Referencevibration resistance | IEC60068-2-6
Competitor Spec Referenceshock resistance | IEC60068-2-27
Competitor Spec Referencebump resistance | IEC60068-2-29
Competitor Spec Referenceseismic resistance | IEC60068-3-3
Competitor Spec ReferenceIP degree of protection | IEC60529,Terminal Block,
Competitor Spec ReferenceIP degree of protection | IEC60529,Housing,
Competitor Spec ReferenceIP degree of protection | IEC60529,Front Panel,
Competitor Spec Reference
Competitor Spec Referencewidth | Width,
Competitor Spec Referenceheight | Height,
Competitor Spec Referencedepth | Depth,
Competitor Spec Referencenet weight
Competitor Spec Referencemounting support | IEC/EN 60715,Without socket,
Competitor Spec Referencemounting support | IEC/EN 60715,With socket,
Competitor Spec Referencemounting position | In relation to normal vertical mounting plane,
Competitor Spec ReferenceMinimum distance to adjacent devices | Horizontal,
Competitor Spec ReferenceMinimum distance to adjacent devices | Vertical,
Competitor Spec Referenceconnections - terminals | IEC60947-1,Solid cable without cable end (screw terminal),
Competitor Spec Referenceconnections - terminals | IEC60947-1,Flexible cable with cable end (screw terminal),
Competitor Spec Referenceconnections - terminals | IEC60947-1,Solid cable (spring terminal),
Competitor Spec Referenceconnections - terminals | IEC60947-1,Flexible cable (spring terminal),
Competitor Spec Referencetightening torque | IEC60947-1,Tightening torque,
Competitor Spec Referencecable stripping length | Cable stripping length,
Competitor Spec Referenceduty time
Competitor Spec Reference
Competitor Spec Referenceelectromagnetic compatibility | Generic immunity standard,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-2,Electrostatic discharge,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-3,Radiated RF & electromagnetic field,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-4,Fast transient / burst,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-5,Surge,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-6,Conducted RF disturbance,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-11,Voltage dips, short interruption & variations on power line,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
Competitor Spec Referenceelectromagnetic compatibility | IEC61000-4-13,Low frequency harmonics,
Competitor Spec Referenceelectromagnetic compatibility | Germanisher Lloyd,Conducted low frequency interference (harmonics),
Competitor Spec Referenceelectromagnetic compatibility | Generic emission standard,
Competitor Spec Referenceelectromagnetic compatibility | EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
Competitor Spec Referenceelectromagnetic compatibility | EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
Competitor Spec Referenceelectromagnetic compatibility | Germanisher Lloyd,Radiated emission from enclosure port,
Competitor Spec Referenceelectromagnetic compatibility | EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
Competitor Spec Referenceelectromagnetic compatibility | EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
Competitor Spec Referenceelectromagnetic compatibility | Germanisher Lloyd,Conducted emission,
Competitor Spec Reference
Competitor Spec Referencepollution degree | IEC60664-1
Competitor Spec Referenceovervoltage category | IEC60664-1
Competitor Spec Referencecircuit group | Supply,Terminal
Competitor Spec Referencecircuit group | Input 1,
Competitor Spec Referencecircuit group | Input 2,
Competitor Spec Referencecircuit group | Input 3,
Competitor Spec Referencecircuit group | Output 1,
Competitor Spec Referencecircuit group | Output 2,
Competitor Spec Reference | Supply,Rated
Competitor Spec Reference | Input 1,Voltage
Competitor Spec Reference | Input 2,Spec
Competitor Spec Reference | Input 3,
Competitor Spec Reference | Output 1,
Competitor Spec Reference | Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 3,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Input 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Input 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Input 3,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Output 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Output 1 / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 1 / Output 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 1 / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 2 / Output 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 2 / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 3 / Output 1,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 3 / Output 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 1 / Input 2,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 2 / Input 3,
Competitor Spec Referencedielectric strength | IEC60255-27,Input 1 / Input 3,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Input 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Input 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Input 3,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Output 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Output 1 / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 1 / Output 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 1 / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 2 / Output 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 2 / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 3 / Output 1,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 3 / Output 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 1 / Input 2,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 2 / Input 3,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Input 1 / Input 3,
Competitor Spec Reference
Competitor Spec Reference[Us] rated supply voltage
Competitor Spec Referencesupply voltage limits
Competitor Spec Referencepolarity
Competitor Spec Referencesupply frequency
Competitor Spec Referencesupply frequency
Competitor Spec Referencepower consumption
Competitor Spec Referenceimmunity to microbreaks
Competitor Spec Referencesupply terminal
Competitor Spec Referenceon-load factor
Competitor Spec Referencerelease of input voltage
Competitor Spec Reference
Competitor Spec Reference | Over / undercurrent (windows mode),
Competitor Spec Reference | Over current,
Competitor Spec Reference | Under current,
Competitor Spec Reference
Competitor Spec Reference | E1-M / B1-C,
Competitor Spec Reference | E2-M / B2-C,
Competitor Spec Reference | E3-M / B3-C,
Competitor Spec Reference | A1+ / A2-,
Competitor Spec Reference | Built in current transformer,
Competitor Spec Reference | E1-M / B1-C,
Competitor Spec Reference | E2-M / B2-C,
Competitor Spec Reference | E3-M / B3-C,
Competitor Spec Reference | A1+ / A2-,
Competitor Spec Reference | Built in current transformer,
Competitor Spec Reference | E1-M / B1-C,
Competitor Spec Reference | E2-M / B2-C,
Competitor Spec Reference | E3-M / B3-C,
Competitor Spec Reference | A1+ / A2-,
Competitor Spec Reference | Built in current transformer,
Competitor Spec Reference | E1-M / B1-C,
Competitor Spec Reference | E2-M / B2-C,
Competitor Spec Reference | E3-M / B3-C,
Competitor Spec Reference | A1+ / A2-,
Competitor Spec Reference | Built in current transformer,
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Referenceoutput type
Competitor Spec Referenceoutput terminal
Competitor Spec Referenceoutput logic | R1 (11-12-14),
Competitor Spec Referenceoutput logic | R2 (21-22-24),
Competitor Spec Referencecontacts material
Competitor Spec Referencemechanical durability | IEC61810-1
Competitor Spec Referenceelectrical durability | IEC60947-4-1,AC-1,
Competitor Spec Referenceelectrical durability | IEC60947-4-1,DC-1,
Competitor Spec Referenceelectrical durability | IEC60947-5-1,AC-15,
Competitor Spec Referenceelectrical durability | IEC60947-5-1,DC-13,
Competitor Spec Reference[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
Competitor Spec Reference[Ie] rated operational current | IEC61810-1,Rated switching current,
Competitor Spec Referencemaximum switching capacity | Maximum switching voltage,
Competitor Spec Referencemaximum switching capacity | Maximum switching current,
Competitor Spec Referencemaximum switching capacity | Maximum switching capacity,
Competitor Spec Referenceminimum switching capacity | IEC60947-5-4,Minimum switching voltage,
Competitor Spec Referenceminimum switching capacity | IEC60947-5-4,Minimum switching current,
Competitor Spec Referenceminimum switching capacity | IEC60947-5-4,Minimum switching capacity,
Competitor Spec Referencemaximum voltage drop | IEC62314,Only for solid state output,
Competitor Spec Referencemaximum leakage current | IEC62314,Only for solid state output,
Competitor Spec Referencethermal current | IEC60947-5-1
Competitor Spec Referenceshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
Competitor Spec Referenceshort circuit protection | IEC62314,Solid State Output by external fuse,
Competitor Spec Reference
Competitor Spec Referencetime delay type | "OFF" delay,
Competitor Spec Referencetime delay type | "ON" delay,
Competitor Spec Referencetime delay type | Inhibition,
Competitor Spec Referencetime delay range | "OFF" delay,
Competitor Spec Referencetime delay range | "ON" delay,
Competitor Spec Referencetime delay range | Inhibition,
Competitor Spec Referenceresponse time | on crossing the threshold,
Competitor Spec Referenceresponse time
Competitor Spec Referenceresponse time
Competitor Spec Referenceresponse time
Competitor Spec Referenceresponse time
Competitor Spec Referencepower on delay
Competitor Spec Referencereset time | through Un power reset,
Competitor Spec Referencereset time | through front panel reset,
Competitor Spec Referencereset time | through input control reset,
Competitor Spec Referencesetting accuracy of time delay
Competitor Spec Referencerepeat accuracy of time delay
Competitor Spec Referencetime delay drift
Competitor Spec Referencetime delay drift
Competitor Spec Reference
Competitor Spec Referencestatus LED
Competitor Spec Referencelocal signalling | Power supply availability,
Competitor Spec Referencelocal signalling | Power supply not availability,
Competitor Spec Referencelocal signalling | Timing in-progress,
Competitor Spec Referencelocal signalling | Output is energized,
Competitor Spec Referencelocal signalling | Output is de-energized,
Competitor Spec Referencelocal signalling | Range Setting Changes,
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Referencelocal signalling
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Referencediagnostic button
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Reference
Competitor Spec Referencesafety reliability data | MTTF,
Competitor Spec Referencesafety reliability data | B10,
Competitor Spec Reference | MTTFd,
Competitor Spec Reference | B10d,
Competitor Spec Reference
RM35JA31MW
RM35JA31MWstandards | EN60255-6, IEC60255-6
RM35JA31MWproduct certifications | UL, CSA, GL, C-Tick, GOST
RM35JA31MWmarking | UL, CSA, GL, C-Tick, GOST, CE
RM35JA31MWdirectives | No 73/23/EEC + 93/68/EEC
RM35JA31MWdirectives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
RM35JA31MWdirectives | 2002/95/EC
RM35JA31MW
RM35JA31MW | Not specified ¦ IEC60721-3-3,Climatic category,
RM35JA31MW | Germanisher Lloyd,Environmental category,
RM35JA31MWambient air temperature for storage | -40…+70 ¦ ,Storage,
RM35JA31MWambient air temperature for operation | -20…+50 ¦ ,Operation,
RM35JA31MWrelative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM35JA31MW | IEC60947-5-1,Cyclic Damp Heat Test,
RM35JA31MWvibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM35JA31MWshock resistance | 5 gn ¦ IEC60068-2-27
RM35JA31MWbump resistance | IEC60068-2-29
RM35JA31MWseismic resistance | IEC60068-3-3
RM35JA31MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM35JA31MWIP degree of protection | IP30 ¦ IEC60529,Housing,
RM35JA31MWIP degree of protection | IEC60529,Front Panel,
RM35JA31MW
RM35JA31MWwidth | 35 x 90 x 72 ¦ ,Width,
RM35JA31MWheight | Height,
RM35JA31MWdepth | Depth,
RM35JA31MWnet weight | 130
RM35JA31MWmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM35JA31MWmounting support | - ¦ IEC/EN 60715,With socket,
RM35JA31MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35JA31MWMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM35JA31MWMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM35JA31MWconnections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35JA31MWconnections - terminals | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35JA31MWconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM35JA31MWconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35JA31MWtightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM35JA31MWcable stripping length | Not specified ¦ ,Cable stripping length,
RM35JA31MWduty time | Not specified
RM35JA31MW
RM35JA31MWelectromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard,
RM35JA31MWelectromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM35JA31MWelectromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM35JA31MWelectromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM35JA31MWelectromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM35JA31MWelectromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM35JA31MWelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM35JA31MWelectromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35JA31MWelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM35JA31MWelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM35JA31MWelectromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM35JA31MWelectromagnetic compatibility | · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35JA31MWelectromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM35JA31MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35JA31MWelectromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35JA31MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM35JA31MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35JA31MWelectromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35JA31MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35JA31MW
RM35JA31MWpollution degree | 3 ¦ IEC60664-1
RM35JA31MWovervoltage category | III ¦ IEC60664-1
RM35JA31MWcircuit group | Supply,Terminal
RM35JA31MWcircuit group | Input 1,
RM35JA31MWcircuit group | Input 2,
RM35JA31MWcircuit group | Input 3,
RM35JA31MWcircuit group | Output 1,
RM35JA31MWcircuit group | 600 ¦ ,Output 2,
RM35JA31MW | 600 ¦ ,Supply,Rated
RM35JA31MW | 600 ¦ ,Input 1,Voltage
RM35JA31MW | Input 2,Spec
RM35JA31MW | Input 3,
RM35JA31MW | Output 1,
RM35JA31MW | Output 2,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Supply,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM35JA31MW[Ui] rated insulation voltage | 4 ¦ IEC60664-1,Output 1,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM35JA31MW[Ui] rated insulation voltage | 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM35JA31MW[Uimp] rated impulse withstand voltage | > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM35JA31MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM35JA31MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM35JA31MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM35JA31MWdielectric strength | IEC60255-27,Supply / Output 1,
RM35JA31MWdielectric strength | IEC60255-27,Supply / Output 2,
RM35JA31MWdielectric strength | IEC60255-27,Output 1 / Output 2,
RM35JA31MWdielectric strength | IEC60255-27,Input 1 / Output 1,
RM35JA31MWdielectric strength | IEC60255-27,Input 1 / Output 2,
RM35JA31MWdielectric strength | IEC60255-27,Input 2 / Output 1,
RM35JA31MWdielectric strength | IEC60255-27,Input 2 / Output 2,
RM35JA31MWdielectric strength | IEC60255-27,Input 3 / Output 1,
RM35JA31MWdielectric strength | IEC60255-27,Input 3 / Output 2,
RM35JA31MWdielectric strength | IEC60255-27,Input 1 / Input 2,
RM35JA31MWdielectric strength | IEC60255-27,Input 2 / Input 3,
RM35JA31MWdielectric strength | IEC60255-27,Input 1 / Input 3,
RM35JA31MWinsulation resistance | IEC60255-27,Supply / Input 1,
RM35JA31MWinsulation resistance | IEC60255-27,Supply / Input 2,
RM35JA31MWinsulation resistance | IEC60255-27,Supply / Input 3,
RM35JA31MWinsulation resistance | IEC60255-27,Supply / Output 1,
RM35JA31MWinsulation resistance | IEC60255-27,Supply / Output 2,
RM35JA31MWinsulation resistance | IEC60255-27,Output 1 / Output 2,
RM35JA31MWinsulation resistance | IEC60255-27,Input 1 / Output 1,
RM35JA31MWinsulation resistance | IEC60255-27,Input 1 / Output 2,
RM35JA31MWinsulation resistance | IEC60255-27,Input 2 / Output 1,
RM35JA31MWinsulation resistance | IEC60255-27,Input 2 / Output 2,
RM35JA31MWinsulation resistance | IEC60255-27,Input 3 / Output 1,
RM35JA31MWinsulation resistance | IEC60255-27,Input 3 / Output 2,
RM35JA31MWinsulation resistance | IEC60255-27,Input 1 / Input 2,
RM35JA31MWinsulation resistance | IEC60255-27,Input 2 / Input 3,
RM35JA31MWinsulation resistance | IEC60255-27,Input 1 / Input 3,
RM35JA31MW
RM35JA31MW[Us] rated supply voltage | ~/-- 24…240
RM35JA31MWsupply voltage limits | ~/-- 20.4…264
RM35JA31MWpolarity
RM35JA31MWsupply frequency | 50 / 60
RM35JA31MWsupply frequency | 45…66
RM35JA31MWpower consumption | ~ 3.5VA, -- 0.6W
RM35JA31MWimmunity to microbreaks | 50
RM35JA31MWsupply terminal | A1-A2
RM35JA31MWon-load factor
RM35JA31MWrelease of input voltage
RM35JA31MW
RM35JA31MW | - ¦ ,Over / undercurrent (windows mode),
RM35JA31MW | Selectable with memory / without memory ¦ ,Over current,
RM35JA31MW | Selectable with memory / without memory ¦ ,Under current,
RM35JA31MW | ~/-- 2…500
RM35JA31MW | 5 ¦ ,E1-M / B1-C,
RM35JA31MW | 1 ¦ ,E2-M / B2-C,
RM35JA31MW | 0.2 ¦ ,E3-M / B3-C,
RM35JA31MW | A1+ / A2-,
RM35JA31MW | - ¦ ,Built in current transformer,
RM35JA31MW | ~/-- 2…20 ¦ ,E1-M / B1-C,
RM35JA31MW | ~/-- 10…100 ¦ ,E2-M / B2-C,
RM35JA31MW | ~/-- 50…500 ¦ ,E3-M / B3-C,
RM35JA31MW | A1+ / A2-,
RM35JA31MW | - ¦ ,Built in current transformer,
RM35JA31MW | Adjustable 10%...100% of 20 ¦ ,E1-M / B1-C,
RM35JA31MW | Adjustable 10%...100% of 100 ¦ ,E2-M / B2-C,
RM35JA31MW | Adjustable 10%...100% of 500 ¦ ,E3-M / B3-C,
RM35JA31MW | A1+ / A2-,
RM35JA31MW | - ¦ ,Built in current transformer,
RM35JA31MW | Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C,
RM35JA31MW | Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C,
RM35JA31MW | Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C,
RM35JA31MW | A1+ / A2-,
RM35JA31MW | - ¦ ,Built in current transformer,
RM35JA31MW | Shunt resistor
RM35JA31MW | E1-M, E2-M, E3-M
RM35JA31MW | 50 / 60
RM35JA31MW | 36…77
RM35JA31MW | +/- 10% of full scale value
RM35JA31MW | +/- 0.5%
RM35JA31MW | < 1% over whole range
RM35JA31MW | 0.05% / oC
RM35JA31MW | 30
RM35JA31MW | True RMS
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MWoutput type | 2 x C/O relay contacts
RM35JA31MWoutput terminal | 11-12-14, 21-22-24
RM35JA31MWoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM35JA31MWoutput logic | R2 (21-22-24),
RM35JA31MWcontacts material | Cadmium free
RM35JA31MWmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM35JA31MWelectrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1,
RM35JA31MWelectrical durability | IEC60947-4-1,DC-1,
RM35JA31MWelectrical durability | IEC60947-5-1,AC-15,
RM35JA31MWelectrical durability | IEC60947-5-1,DC-13,
RM35JA31MW[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM35JA31MW[Ie] rated operational current | IEC61810-1,Rated switching current,
RM35JA31MWmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM35JA31MWmaximum switching capacity | 5 ¦ ,Maximum switching current,
RM35JA31MWmaximum switching capacity | 1250 ¦ ,Maximum switching capacity,
RM35JA31MWminimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
RM35JA31MWminimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM35JA31MWminimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM35JA31MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35JA31MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35JA31MWthermal current | IEC60947-5-1
RM35JA31MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM35JA31MWshort circuit protection | IEC62314,Solid State Output by external fuse,
RM35JA31MW
RM35JA31MWtime delay type | · ¦ ,"OFF" delay,
RM35JA31MWtime delay type | - ¦ ,"ON" delay,
RM35JA31MWtime delay type | · ¦ ,Inhibition,
RM35JA31MWtime delay range | Adjustable 0.3…30 ¦ ,"OFF" delay,
RM35JA31MWtime delay range | - ¦ ,"ON" delay,
RM35JA31MWtime delay range | Adjustable 1…20 ¦ ,Inhibition,
RM35JA31MWresponse time | Not specified ¦ ,on crossing the threshold,
RM35JA31MWresponse time
RM35JA31MWresponse time
RM35JA31MWresponse time
RM35JA31MWresponse time
RM35JA31MWpower on delay | 0
RM35JA31MWreset time | 0
RM35JA31MWreset time | through front panel reset,
RM35JA31MWreset time | through input control reset,
RM35JA31MWsetting accuracy of time delay | +/- 10% of full scales
RM35JA31MWrepeat accuracy of time delay | +/- 2%
RM35JA31MWtime delay drift | Not specified
RM35JA31MWtime delay drift | Not specified
RM35JA31MW
RM35JA31MWstatus LED
RM35JA31MWlocal signalling | Power supply availability,
RM35JA31MWlocal signalling | Power supply not availability,
RM35JA31MWlocal signalling | Timing in-progress,
RM35JA31MWlocal signalling | Output is energized,
RM35JA31MWlocal signalling | Output is de-energized,
RM35JA31MWlocal signalling | Range Setting Changes,
RM35JA31MWlocal signalling
RM35JA31MWlocal signalling
RM35JA31MWlocal signalling
RM35JA31MWlocal signalling
RM35JA31MWlocal signalling
RM35JA31MWlocal signalling
RM35JA31MWlocal signalling
RM35JA31MWlocal signalling
RM35JA31MWlocal signalling
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MWdiagnostic button
RM35JA31MW
RM35JA31MW
RM35JA31MW
RM35JA31MWsafety reliability data | MTTF,
RM35JA31MWsafety reliability data | B10,
RM35JA31MW | MTTFd,
RM35JA31MW | B10d,
RM35JA31MW
RM35JA32MW
RM35JA32MWstandards | EN60255-6, IEC60255-6
RM35JA32MWproduct certifications | UL, CSA, GL, C-Tick, GOST, CCC
RM35JA32MWmarking | UL, CSA, GL, C-Tick, GOST, CE, CCC
RM35JA32MWdirectives | No 73/23/EEC + 93/68/EEC
RM35JA32MWdirectives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
RM35JA32MWdirectives | 2002/95/EC
RM35JA32MW
RM35JA32MW | Not specified ¦ IEC60721-3-3,Climatic category,
RM35JA32MW | Germanisher Lloyd,Environmental category,
RM35JA32MWambient air temperature for storage | -40…+70 ¦ ,Storage,
RM35JA32MWambient air temperature for operation | -20…+50 ¦ ,Operation,
RM35JA32MWrelative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM35JA32MW | IEC60947-5-1,Cyclic Damp Heat Test,
RM35JA32MWvibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM35JA32MWshock resistance | 5 gn ¦ IEC60068-2-27
RM35JA32MWbump resistance | IEC60068-2-29
RM35JA32MWseismic resistance | IEC60068-3-3
RM35JA32MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM35JA32MWIP degree of protection | IP30 ¦ IEC60529,Housing,
RM35JA32MWIP degree of protection | IEC60529,Front Panel,
RM35JA32MW
RM35JA32MWwidth | 35 x 90 x 72 ¦ ,Width,
RM35JA32MWheight | Height,
RM35JA32MWdepth | Depth,
RM35JA32MWnet weight | 130
RM35JA32MWmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM35JA32MWmounting support | - ¦ IEC/EN 60715,With socket,
RM35JA32MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35JA32MWMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM35JA32MWMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM35JA32MWconnections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM35JA32MWconnections - terminals | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM35JA32MWconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM35JA32MWconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35JA32MWtightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM35JA32MWcable stripping length | Not specified ¦ ,Cable stripping length,
RM35JA32MWduty time | Not specified
RM35JA32MW
RM35JA32MWelectromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard,
RM35JA32MWelectromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM35JA32MWelectromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM35JA32MWelectromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM35JA32MWelectromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM35JA32MWelectromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM35JA32MWelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM35JA32MWelectromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM35JA32MWelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM35JA32MWelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM35JA32MWelectromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM35JA32MWelectromagnetic compatibility | · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM35JA32MWelectromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM35JA32MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM35JA32MWelectromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM35JA32MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM35JA32MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM35JA32MWelectromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM35JA32MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35JA32MW
RM35JA32MWpollution degree | 3 ¦ IEC60664-1
RM35JA32MWovervoltage category | III ¦ IEC60664-1
RM35JA32MWcircuit group | Supply,Terminal
RM35JA32MWcircuit group | Input 1,
RM35JA32MWcircuit group | Input 2,
RM35JA32MWcircuit group | Input 3,
RM35JA32MWcircuit group | Output 1,
RM35JA32MWcircuit group | 600 ¦ ,Output 2,
RM35JA32MW | 600 ¦ ,Supply,Rated
RM35JA32MW | 600 ¦ ,Input 1,Voltage
RM35JA32MW | Input 2,Spec
RM35JA32MW | Input 3,
RM35JA32MW | Output 1,
RM35JA32MW | Output 2,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Supply,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM35JA32MW[Ui] rated insulation voltage | 4 ¦ IEC60664-1,Output 1,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM35JA32MW[Ui] rated insulation voltage | 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM35JA32MW[Uimp] rated impulse withstand voltage | > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM35JA32MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM35JA32MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM35JA32MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM35JA32MWdielectric strength | IEC60255-27,Supply / Output 1,
RM35JA32MWdielectric strength | IEC60255-27,Supply / Output 2,
RM35JA32MWdielectric strength | IEC60255-27,Output 1 / Output 2,
RM35JA32MWdielectric strength | IEC60255-27,Input 1 / Output 1,
RM35JA32MWdielectric strength | IEC60255-27,Input 1 / Output 2,
RM35JA32MWdielectric strength | IEC60255-27,Input 2 / Output 1,
RM35JA32MWdielectric strength | IEC60255-27,Input 2 / Output 2,
RM35JA32MWdielectric strength | IEC60255-27,Input 3 / Output 1,
RM35JA32MWdielectric strength | IEC60255-27,Input 3 / Output 2,
RM35JA32MWdielectric strength | IEC60255-27,Input 1 / Input 2,
RM35JA32MWdielectric strength | IEC60255-27,Input 2 / Input 3,
RM35JA32MWdielectric strength | IEC60255-27,Input 1 / Input 3,
RM35JA32MWinsulation resistance | IEC60255-27,Supply / Input 1,
RM35JA32MWinsulation resistance | IEC60255-27,Supply / Input 2,
RM35JA32MWinsulation resistance | IEC60255-27,Supply / Input 3,
RM35JA32MWinsulation resistance | IEC60255-27,Supply / Output 1,
RM35JA32MWinsulation resistance | IEC60255-27,Supply / Output 2,
RM35JA32MWinsulation resistance | IEC60255-27,Output 1 / Output 2,
RM35JA32MWinsulation resistance | IEC60255-27,Input 1 / Output 1,
RM35JA32MWinsulation resistance | IEC60255-27,Input 1 / Output 2,
RM35JA32MWinsulation resistance | IEC60255-27,Input 2 / Output 1,
RM35JA32MWinsulation resistance | IEC60255-27,Input 2 / Output 2,
RM35JA32MWinsulation resistance | IEC60255-27,Input 3 / Output 1,
RM35JA32MWinsulation resistance | IEC60255-27,Input 3 / Output 2,
RM35JA32MWinsulation resistance | IEC60255-27,Input 1 / Input 2,
RM35JA32MWinsulation resistance | IEC60255-27,Input 2 / Input 3,
RM35JA32MWinsulation resistance | IEC60255-27,Input 1 / Input 3,
RM35JA32MW
RM35JA32MW[Us] rated supply voltage | ~/-- 24…240
RM35JA32MWsupply voltage limits | ~/-- 20.4…264
RM35JA32MWpolarity
RM35JA32MWsupply frequency | 50 / 60
RM35JA32MWsupply frequency | 45…66
RM35JA32MWpower consumption | ~ 3.5VA, -- 0.6W
RM35JA32MWimmunity to microbreaks | 10
RM35JA32MWsupply terminal | A1-A2
RM35JA32MWon-load factor
RM35JA32MWrelease of input voltage
RM35JA32MW
RM35JA32MW | - ¦ ,Over / undercurrent (windows mode),
RM35JA32MW | Selectable with memory / without memory ¦ ,Over current,
RM35JA32MW | Selectable with memory / without memory ¦ ,Under current,
RM35JA32MW | ~/-- 150…15000
RM35JA32MW | 0.05 ¦ ,E1-M / B1-C,
RM35JA32MW | 0.015 ¦ ,E2-M / B2-C,
RM35JA32MW | 0.005 ¦ ,E3-M / B3-C,
RM35JA32MW | A1+ / A2-,
RM35JA32MW | - ¦ ,Built in current transformer,
RM35JA32MW | ~/-- 150…1500 ¦ ,E1-M / B1-C,
RM35JA32MW | ~/-- 500…5000 ¦ ,E2-M / B2-C,
RM35JA32MW | ~/-- 1500…15000 ¦ ,E3-M / B3-C,
RM35JA32MW | A1+ / A2-,
RM35JA32MW | - ¦ ,Built in current transformer,
RM35JA32MW | Adjustable 10%...100% of 1500 ¦ ,E1-M / B1-C,
RM35JA32MW | Adjustable 10%...100% of 5000 ¦ ,E2-M / B2-C,
RM35JA32MW | Adjustable 10%...100% of 15000 ¦ ,E3-M / B3-C,
RM35JA32MW | A1+ / A2-,
RM35JA32MW | - ¦ ,Built in current transformer,
RM35JA32MW | Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C,
RM35JA32MW | Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C,
RM35JA32MW | Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C,
RM35JA32MW | A1+ / A2-,
RM35JA32MW | - ¦ ,Built in current transformer,
RM35JA32MW | Shunt resistor
RM35JA32MW | E1-M, E2-M, E3-M
RM35JA32MW | 50 / 60
RM35JA32MW | 36…77
RM35JA32MW | +/- 10% of full scale value
RM35JA32MW | +/- 0.5%
RM35JA32MW | < 1% over whole range
RM35JA32MW | 0.05% / oC
RM35JA32MW | 30
RM35JA32MW | True RMS
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MWoutput type | 2 x C/O relay contacts
RM35JA32MWoutput terminal | 11-12-14, 21-22-24
RM35JA32MWoutput logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM35JA32MWoutput logic | R2 (21-22-24),
RM35JA32MWcontacts material | Cadmium free
RM35JA32MWmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM35JA32MWelectrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1,
RM35JA32MWelectrical durability | IEC60947-4-1,DC-1,
RM35JA32MWelectrical durability | IEC60947-5-1,AC-15,
RM35JA32MWelectrical durability | IEC60947-5-1,DC-13,
RM35JA32MW[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM35JA32MW[Ie] rated operational current | IEC61810-1,Rated switching current,
RM35JA32MWmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM35JA32MWmaximum switching capacity | ~ 5 ¦ ,Maximum switching current,
RM35JA32MWmaximum switching capacity | 1250 ¦ ,Maximum switching capacity,
RM35JA32MWminimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
RM35JA32MWminimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM35JA32MWminimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM35JA32MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35JA32MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35JA32MWthermal current | IEC60947-5-1
RM35JA32MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM35JA32MWshort circuit protection | IEC62314,Solid State Output by external fuse,
RM35JA32MW
RM35JA32MWtime delay type | · ¦ ,"OFF" delay,
RM35JA32MWtime delay type | - ¦ ,"ON" delay,
RM35JA32MWtime delay type | · ¦ ,Inhibition,
RM35JA32MWtime delay range | Adjustable 0.3…30 ¦ ,"OFF" delay,
RM35JA32MWtime delay range | - ¦ ,"ON" delay,
RM35JA32MWtime delay range | Adjustable 1…20 ¦ ,Inhibition,
RM35JA32MWresponse time | Not specified ¦ ,on crossing the threshold,
RM35JA32MWresponse time
RM35JA32MWresponse time
RM35JA32MWresponse time
RM35JA32MWresponse time
RM35JA32MWpower on delay | 0
RM35JA32MWreset time | 0
RM35JA32MWreset time | through front panel reset,
RM35JA32MWreset time | through input control reset,
RM35JA32MWsetting accuracy of time delay | +/- 10% of full scales
RM35JA32MWrepeat accuracy of time delay | +/- 2%
RM35JA32MWtime delay drift | Not specified
RM35JA32MWtime delay drift | Not specified
RM35JA32MW
RM35JA32MWstatus LED
RM35JA32MWlocal signalling | Power supply availability,
RM35JA32MWlocal signalling | Power supply not availability,
RM35JA32MWlocal signalling | Timing in-progress,
RM35JA32MWlocal signalling | Output is energized,
RM35JA32MWlocal signalling | Output is de-energized,
RM35JA32MWlocal signalling | Range Setting Changes,
RM35JA32MWlocal signalling
RM35JA32MWlocal signalling
RM35JA32MWlocal signalling
RM35JA32MWlocal signalling
RM35JA32MWlocal signalling
RM35JA32MWlocal signalling
RM35JA32MWlocal signalling
RM35JA32MWlocal signalling
RM35JA32MWlocal signalling
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MWdiagnostic button
RM35JA32MW
RM35JA32MW
RM35JA32MW
RM35JA32MWsafety reliability data | MTTF,
RM35JA32MWsafety reliability data | B10,
RM35JA32MW | MTTFd,
RM35JA32MW | B10d,
RM35JA32MW
RM4JA3
RM4JA3standards | EN60255-6, IEC60255-6
RM4JA3product certifications | UL, CSA, GL, C-Tick, GOST, CCC
RM4JA3marking | UL, CSA, GL, C-Tick, GOST, CE, CCC
RM4JA3directives
RM4JA3directives
RM4JA3directives
RM4JA3
RM4JA3 | Not specified ¦ IEC60721-3-3,Climatic category,
RM4JA3 | Germanisher Lloyd,Environmental category,
RM4JA3ambient air temperature for storage | Not specified ¦ ,Storage,
RM4JA3ambient air temperature for operation | Not specified ¦ ,Operation,
RM4JA3relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
RM4JA3 | IEC60947-5-1,Cyclic Damp Heat Test,
RM4JA3vibration resistance | Not specified ¦ IEC60068-2-6
RM4JA3shock resistance | Not specified ¦ IEC60068-2-27
RM4JA3bump resistance | IEC60068-2-29
RM4JA3seismic resistance | IEC60068-3-3
RM4JA3IP degree of protection | Not specified ¦ IEC60529,Terminal Block,
RM4JA3IP degree of protection | Not specified ¦ IEC60529,Housing,
RM4JA3IP degree of protection | IEC60529,Front Panel,
RM4JA3
RM4JA3width | RM4JA31xx: 22.5 x 78 x 80 RM4JA32xx: 45 x 78 x 80 ¦ ,Width,
RM4JA3height | Height,
RM4JA3depth | Depth,
RM4JA3net weight | Not specified
RM4JA3mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM4JA3mounting support | - ¦ IEC/EN 60715,With socket,
RM4JA3mounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
RM4JA3Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM4JA3Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM4JA3connections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM4JA3connections - terminals | Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM4JA3connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM4JA3connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4JA3tightening torque | Not specified ¦ IEC60947-1,Tightening torque,
RM4JA3cable stripping length | Not specified ¦ ,Cable stripping length,
RM4JA3duty time | Not specified
RM4JA3
RM4JA3electromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard,
RM4JA3electromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM4JA3electromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM4JA3electromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM4JA3electromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM4JA3electromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM4JA3electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM4JA3electromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM4JA3electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM4JA3electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM4JA3electromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM4JA3electromagnetic compatibility | ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM4JA3electromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM4JA3electromagnetic compatibility | Class B Group1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM4JA3electromagnetic compatibility | Class B Group1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM4JA3electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM4JA3electromagnetic compatibility | Class B Group1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM4JA3electromagnetic compatibility | Class B Group1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM4JA3electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4JA3
RM4JA3pollution degree | Not specified ¦ IEC60664-1
RM4JA3overvoltage category | Not specified ¦ IEC60664-1
RM4JA3circuit group | Supply,Terminal
RM4JA3circuit group | Input 1,
RM4JA3circuit group | Input 2,
RM4JA3circuit group | Input 3,
RM4JA3circuit group | Output 1,
RM4JA3circuit group | Not specified ¦ ,Output 2,
RM4JA3 | Not specified ¦ ,Supply,Rated
RM4JA3 | Not specified ¦ ,Input 1,Voltage
RM4JA3 | Input 2,Spec
RM4JA3 | Input 3,
RM4JA3 | Output 1,
RM4JA3 | Output 2,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Supply,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM4JA3[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Output 1,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM4JA3[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM4JA3[Uimp] rated impulse withstand voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM4JA3dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM4JA3dielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM4JA3dielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM4JA3dielectric strength | IEC60255-27,Supply / Output 1,
RM4JA3dielectric strength | IEC60255-27,Supply / Output 2,
RM4JA3dielectric strength | IEC60255-27,Output 1 / Output 2,
RM4JA3dielectric strength | IEC60255-27,Input 1 / Output 1,
RM4JA3dielectric strength | IEC60255-27,Input 1 / Output 2,
RM4JA3dielectric strength | IEC60255-27,Input 2 / Output 1,
RM4JA3dielectric strength | IEC60255-27,Input 2 / Output 2,
RM4JA3dielectric strength | IEC60255-27,Input 3 / Output 1,
RM4JA3dielectric strength | IEC60255-27,Input 3 / Output 2,
RM4JA3dielectric strength | IEC60255-27,Input 1 / Input 2,
RM4JA3dielectric strength | IEC60255-27,Input 2 / Input 3,
RM4JA3dielectric strength | IEC60255-27,Input 1 / Input 3,
RM4JA3insulation resistance | IEC60255-27,Supply / Input 1,
RM4JA3insulation resistance | IEC60255-27,Supply / Input 2,
RM4JA3insulation resistance | IEC60255-27,Supply / Input 3,
RM4JA3insulation resistance | IEC60255-27,Supply / Output 1,
RM4JA3insulation resistance | IEC60255-27,Supply / Output 2,
RM4JA3insulation resistance | IEC60255-27,Output 1 / Output 2,
RM4JA3insulation resistance | IEC60255-27,Input 1 / Output 1,
RM4JA3insulation resistance | IEC60255-27,Input 1 / Output 2,
RM4JA3insulation resistance | IEC60255-27,Input 2 / Output 1,
RM4JA3insulation resistance | IEC60255-27,Input 2 / Output 2,
RM4JA3insulation resistance | IEC60255-27,Input 3 / Output 1,
RM4JA3insulation resistance | IEC60255-27,Input 3 / Output 2,
RM4JA3insulation resistance | IEC60255-27,Input 1 / Input 2,
RM4JA3insulation resistance | IEC60255-27,Input 2 / Input 3,
RM4JA3insulation resistance | IEC60255-27,Input 1 / Input 3,
RM4JA3
RM4JA3[Us] rated supply voltage | RM4JA3xMW: ~/-- 24…240 RM4JA3xF: ~110…130 RM4JA3xM: ~220…240 RM4JA3xQ: ~380…415
RM4JA3supply voltage limits | 0.85…1.1 Un
RM4JA3polarity
RM4JA3supply frequency | 50 / 60
RM4JA3supply frequency | Not specified
RM4JA3power consumption | RM4JA3xMW: ~ 3.3VA, -- 1.2W RM4JA3xF: ~ 3.3VA RM4JA3xM: ~ 3.4VA RM4JA3xQ: ~ 3VA
RM4JA3immunity to microbreaks | Not specified
RM4JA3supply terminal | A1-A2
RM4JA3on-load factor
RM4JA3release of input voltage
RM4JA3
RM4JA3 | - ¦ ,Over / undercurrent (windows mode),
RM4JA3 | Without memory ¦ ,Over current,
RM4JA3 | Without memory ¦ ,Under current,
RM4JA3 | RM4JA31xx: ~/-- 3…1000 RM4JA32xx: ~/-- 300…15000
RM4JA3 | RM4JA31xx: 33 RM4JA32xx: ~/-- 0.06 ¦ ,E1-M / B1-C,
RM4JA3 | RM4JA31xx: 10 RM4JA32xx: ~/-- 0.02 ¦ ,E2-M / B2-C,
RM4JA3 | RM4JA31xx: 1 RM4JA32xx: ~/-- 0.006 ¦ ,E3-M / B3-C,
RM4JA3 | A1+ / A2-,
RM4JA3 | - ¦ ,Built in current transformer,
RM4JA3 | RM4JA31xx: ~/-- 3…30 RM4JA32xx: ~/-- 300…1500 ¦ ,E1-M / B1-C,
RM4JA3 | RM4JA31xx: ~/-- 10…1000 RM4JA32xx: ~/-- 1000…5000 ¦ ,E2-M / B2-C,
RM4JA3 | RM4JA31xx: ~/-- 100…1000 RM4JA32xx: ~/-- 3000…15000 ¦ ,E3-M / B3-C,
RM4JA3 | A1+ / A2-,
RM4JA3 | - ¦ ,Built in current transformer,
RM4JA3 | - ¦ ,E1-M / B1-C,
RM4JA3 | Adjustable 10%...100% ¦ ,E2-M / B2-C,
RM4JA3 | Adjustable 10%...100% ¦ ,E3-M / B3-C,
RM4JA3 | A1+ / A2-,
RM4JA3 | - ¦ ,Built in current transformer,
RM4JA3 | Adjustable 5%...30% of threshold setting ¦ ,E1-M / B1-C,
RM4JA3 | Adjustable 5%...30% of threshold setting ¦ ,E2-M / B2-C,
RM4JA3 | Adjustable 5%...30% of threshold setting ¦ ,E3-M / B3-C,
RM4JA3 | A1+ / A2-,
RM4JA3 | - ¦ ,Built in current transformer,
RM4JA3 | Shunt resistor
RM4JA3 | B1-C, B2-C, B3-C
RM4JA3 | 50 / 60
RM4JA3 | Not specified
RM4JA3 | +/- 10% of full scale value
RM4JA3 | Not specified
RM4JA3 | < 0.5% over whole range
RM4JA3 | 0.06% / oC
RM4JA3 | 80
RM4JA3 | True RMS
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3
RM4JA3output type | 2 x C/O relay contacts
RM4JA3output terminal | 11-12-14, 21-22-24
RM4JA3output logic | De-Energized on fault-free ¦ ,R1 (11-12-14),
RM4JA3output logic | R2 (21-22-24),
RM4JA3contacts material | Cadmium free
RM4JA3mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM4JA3electrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1,
RM4JA3electrical durability | IEC60947-4-1,DC-1,
RM4JA3electrical durability | IEC60947-5-1,AC-15,
RM4JA3electrical durability | IEC60947-5-1,DC-13,
RM4JA3[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4JA3[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4JA3maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM4JA3maximum switching capacity | ~ 5 ¦ ,Maximum switching current,
RM4JA3maximum switching capacity | 1250 ¦ ,Maximum switching capacity,
RM4JA3minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
RM4JA3minimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM4JA3minimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM4JA3maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM4JA3maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM4JA3thermal current | IEC60947-5-1
RM4JA3short circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM4JA3short circuit protection | IEC62314,Solid State Output by external fuse,
RM4JA3
RM4JA3time delay type | · ¦ ,"OFF" delay,
RM4JA3time delay type | - ¦ ,"ON" delay,
RM4JA3time delay type | · ¦ ,Inhibition,
RM4JA3time delay range | Adjustable 0…30 ¦ ,"OFF" delay,
RM4JA3time delay range | - ¦ ,"ON" delay,
RM4JA3time delay range | Adjustable 1…20 ¦ ,Inhibition,
RM4JA3response time | Not specified ¦ ,on crossing the threshold,
RM4JA3response time
RM4JA3response time
RM4JA3response time
RM4JA3response time
RM4JA3power on delay | 0
RM4JA3reset time | 0
RM4JA3reset time | through front panel reset,
RM4JA3reset time | through input control reset,
RM4JA3setting accuracy of time delay | +/- 10% of full scales
RM4JA3repeat accuracy of time delay | +/- 0.5%
RM4JA3time delay drift | < 0.5% over whole range
RM4JA3time delay drift | 0.07% / oC
RM4JA3
RM4JA3status LED
RM4JA3local signalling | Power supply availability,
RM4JA3local signalling | Power supply not availability,
RM4JA3local signalling | Timing in-progress,
RM4JA3local signalling | Output is energized,
RM4JA3local signalling | Output is de-energized,
RM4JA3local signalling | Range Setting Changes,
RM4JA3local signalling
RM4JA3local signalling
RM4JA3local signalling
RM4JA3local signalling
RM4JA3local signalling
RM4JA3local signalling
RM4JA3local signalling
RM4JA3local signalling
RM4JA3local signalling
RM4JA3
RM4JA3
RM4JA3
RM4JA3diagnostic button
RM4JA3
RM4JA3
RM4JA3
RM4JA3safety reliability data | MTTF,
RM4JA3safety reliability data | B10,
RM4JA3 | MTTFd,
RM4JA3 | B10d,
RM4JA3
RM4JA01
RM4JA01standards | EN60255-6, IEC60255-6
RM4JA01product certifications | UL, CSA, GL, C-Tick, GOST, CCC
RM4JA01marking | UL, CSA, GL, C-Tick, GOST, CE, CCC
RM4JA01directives
RM4JA01directives
RM4JA01directives
RM4JA01
RM4JA01 | Not specified ¦ IEC60721-3-3,Climatic category,
RM4JA01 | Germanisher Lloyd,Environmental category,
RM4JA01ambient air temperature for storage | Not specified ¦ ,Storage,
RM4JA01ambient air temperature for operation | Not specified ¦ ,Operation,
RM4JA01relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
RM4JA01 | IEC60947-5-1,Cyclic Damp Heat Test,
RM4JA01vibration resistance | Not specified ¦ IEC60068-2-6
RM4JA01shock resistance | Not specified ¦ IEC60068-2-27
RM4JA01bump resistance | IEC60068-2-29
RM4JA01seismic resistance | IEC60068-3-3
RM4JA01IP degree of protection | Not specified ¦ IEC60529,Terminal Block,
RM4JA01IP degree of protection | Not specified ¦ IEC60529,Housing,
RM4JA01IP degree of protection | IEC60529,Front Panel,
RM4JA01
RM4JA01width | 22.5 x 78 x 80 ¦ ,Width,
RM4JA01height | Height,
RM4JA01depth | Depth,
RM4JA01net weight | Not specified
RM4JA01mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM4JA01mounting support | - ¦ IEC/EN 60715,With socket,
RM4JA01mounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
RM4JA01Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM4JA01Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM4JA01connections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM4JA01connections - terminals | Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM4JA01connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM4JA01connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4JA01tightening torque | Not specified ¦ IEC60947-1,Tightening torque,
RM4JA01cable stripping length | Not specified ¦ ,Cable stripping length,
RM4JA01duty time | Not specified
RM4JA01
RM4JA01electromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard,
RM4JA01electromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM4JA01electromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM4JA01electromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM4JA01electromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM4JA01electromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM4JA01electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM4JA01electromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM4JA01electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM4JA01electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM4JA01electromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM4JA01electromagnetic compatibility | ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM4JA01electromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM4JA01electromagnetic compatibility | Class B Group1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM4JA01electromagnetic compatibility | Class B Group1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM4JA01electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM4JA01electromagnetic compatibility | Class B Group1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM4JA01electromagnetic compatibility | Class B Group1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM4JA01electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4JA01
RM4JA01pollution degree | Not specified ¦ IEC60664-1
RM4JA01overvoltage category | Not specified ¦ IEC60664-1
RM4JA01circuit group | Supply,Terminal
RM4JA01circuit group | Input 1,
RM4JA01circuit group | Input 2,
RM4JA01circuit group | Input 3,
RM4JA01circuit group | Output 1,
RM4JA01circuit group | Not specified ¦ ,Output 2,
RM4JA01 | Not specified ¦ ,Supply,Rated
RM4JA01 | Not specified ¦ ,Input 1,Voltage
RM4JA01 | Input 2,Spec
RM4JA01 | Input 3,
RM4JA01 | Output 1,
RM4JA01 | Output 2,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Supply,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM4JA01[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Output 1,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM4JA01[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM4JA01[Uimp] rated impulse withstand voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM4JA01dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM4JA01dielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM4JA01dielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM4JA01dielectric strength | IEC60255-27,Supply / Output 1,
RM4JA01dielectric strength | IEC60255-27,Supply / Output 2,
RM4JA01dielectric strength | IEC60255-27,Output 1 / Output 2,
RM4JA01dielectric strength | IEC60255-27,Input 1 / Output 1,
RM4JA01dielectric strength | IEC60255-27,Input 1 / Output 2,
RM4JA01dielectric strength | IEC60255-27,Input 2 / Output 1,
RM4JA01dielectric strength | IEC60255-27,Input 2 / Output 2,
RM4JA01dielectric strength | IEC60255-27,Input 3 / Output 1,
RM4JA01dielectric strength | IEC60255-27,Input 3 / Output 2,
RM4JA01dielectric strength | IEC60255-27,Input 1 / Input 2,
RM4JA01dielectric strength | IEC60255-27,Input 2 / Input 3,
RM4JA01dielectric strength | IEC60255-27,Input 1 / Input 3,
RM4JA01insulation resistance | IEC60255-27,Supply / Input 1,
RM4JA01insulation resistance | IEC60255-27,Supply / Input 2,
RM4JA01insulation resistance | IEC60255-27,Supply / Input 3,
RM4JA01insulation resistance | IEC60255-27,Supply / Output 1,
RM4JA01insulation resistance | IEC60255-27,Supply / Output 2,
RM4JA01insulation resistance | IEC60255-27,Output 1 / Output 2,
RM4JA01insulation resistance | IEC60255-27,Input 1 / Output 1,
RM4JA01insulation resistance | IEC60255-27,Input 1 / Output 2,
RM4JA01insulation resistance | IEC60255-27,Input 2 / Output 1,
RM4JA01insulation resistance | IEC60255-27,Input 2 / Output 2,
RM4JA01insulation resistance | IEC60255-27,Input 3 / Output 1,
RM4JA01insulation resistance | IEC60255-27,Input 3 / Output 2,
RM4JA01insulation resistance | IEC60255-27,Input 1 / Input 2,
RM4JA01insulation resistance | IEC60255-27,Input 2 / Input 3,
RM4JA01insulation resistance | IEC60255-27,Input 1 / Input 3,
RM4JA01
RM4JA01[Us] rated supply voltage | RM4JA01B: ~ 24 RM4JA01F: ~110…130 RM4JA01M: ~220…240
RM4JA01supply voltage limits | 0.85…1.1 Un
RM4JA01polarity
RM4JA01supply frequency | 50 / 60
RM4JA01supply frequency | Not specified
RM4JA01power consumption | RM4JA01B: ~ 2VA RM4JA01F: ~ 3.3VA RM4JA01M: ~ 3.5VA
RM4JA01immunity to microbreaks | Not specified
RM4JA01supply terminal | A1-A2
RM4JA01on-load factor
RM4JA01release of input voltage
RM4JA01
RM4JA01 | - ¦ ,Over / undercurrent (windows mode),
RM4JA01 | Without memory ¦ ,Over current,
RM4JA01 | Without memory ¦ ,Under current,
RM4JA01 | ~/-- 3…1000
RM4JA01 | 33 ¦ ,E1-M / B1-C,
RM4JA01 | 10 ¦ ,E2-M / B2-C,
RM4JA01 | 1 ¦ ,E3-M / B3-C,
RM4JA01 | A1+ / A2-,
RM4JA01 | - ¦ ,Built in current transformer,
RM4JA01 | ~/-- 3…30 ¦ ,E1-M / B1-C,
RM4JA01 | ~/-- 10…1000 ¦ ,E2-M / B2-C,
RM4JA01 | ~/-- 100…1000 ¦ ,E3-M / B3-C,
RM4JA01 | A1+ / A2-,
RM4JA01 | - ¦ ,Built in current transformer,
RM4JA01 | - ¦ ,E1-M / B1-C,
RM4JA01 | Adjustable 10%...100% ¦ ,E2-M / B2-C,
RM4JA01 | Adjustable 10%...100% ¦ ,E3-M / B3-C,
RM4JA01 | A1+ / A2-,
RM4JA01 | - ¦ ,Built in current transformer,
RM4JA01 | Adjustable 5%...30% of threshold setting ¦ ,E1-M / B1-C,
RM4JA01 | Adjustable 5%...30% of threshold setting ¦ ,E2-M / B2-C,
RM4JA01 | Adjustable 5%...30% of threshold setting ¦ ,E3-M / B3-C,
RM4JA01 | A1+ / A2-,
RM4JA01 | - ¦ ,Built in current transformer,
RM4JA01 | Shunt resistor
RM4JA01 | B1-C, B2-C, B3-C
RM4JA01 | 50 / 60
RM4JA01 | Not specified
RM4JA01 | +/- 10% of full scale value
RM4JA01 | Not specified
RM4JA01 | < 0.5% over whole range
RM4JA01 | 0.06% / oC
RM4JA01 | 80
RM4JA01 | True RMS
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01
RM4JA01output type | 2 x C/O relay contacts
RM4JA01output terminal | 11-12-14, 21-22-24
RM4JA01output logic | De-Energized on fault-free ¦ ,R1 (11-12-14),
RM4JA01output logic | R2 (21-22-24),
RM4JA01contacts material | Cadmium free
RM4JA01mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM4JA01electrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1,
RM4JA01electrical durability | IEC60947-4-1,DC-1,
RM4JA01electrical durability | IEC60947-5-1,AC-15,
RM4JA01electrical durability | IEC60947-5-1,DC-13,
RM4JA01[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4JA01[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4JA01maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM4JA01maximum switching capacity | 8 ¦ ,Maximum switching current,
RM4JA01maximum switching capacity | 2000 ¦ ,Maximum switching capacity,
RM4JA01minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
RM4JA01minimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM4JA01minimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM4JA01maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM4JA01maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM4JA01thermal current | IEC60947-5-1
RM4JA01short circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM4JA01short circuit protection | IEC62314,Solid State Output by external fuse,
RM4JA01
RM4JA01time delay type | · ¦ ,"OFF" delay,
RM4JA01time delay type | - ¦ ,"ON" delay,
RM4JA01time delay type | · ¦ ,Inhibition,
RM4JA01time delay range | Adjustable 0…30 ¦ ,"OFF" delay,
RM4JA01time delay range | - ¦ ,"ON" delay,
RM4JA01time delay range | Adjustable 1…20 ¦ ,Inhibition,
RM4JA01response time | Not specified ¦ ,on crossing the threshold,
RM4JA01response time
RM4JA01response time
RM4JA01response time
RM4JA01response time
RM4JA01power on delay | 0
RM4JA01reset time | 0
RM4JA01reset time | through front panel reset,
RM4JA01reset time | through input control reset,
RM4JA01setting accuracy of time delay | +/- 10% of full scales
RM4JA01repeat accuracy of time delay | +/- 0.5%
RM4JA01time delay drift | < 0.5% over whole range
RM4JA01time delay drift | 0.07% / oC
RM4JA01
RM4JA01status LED
RM4JA01local signalling | Power supply availability,
RM4JA01local signalling | Power supply not availability,
RM4JA01local signalling | Timing in-progress,
RM4JA01local signalling | Output is energized,
RM4JA01local signalling | Output is de-energized,
RM4JA01local signalling | Range Setting Changes,
RM4JA01local signalling
RM4JA01local signalling
RM4JA01local signalling
RM4JA01local signalling
RM4JA01local signalling
RM4JA01local signalling
RM4JA01local signalling
RM4JA01local signalling
RM4JA01local signalling
RM4JA01
RM4JA01
RM4JA01
RM4JA01diagnostic button
RM4JA01
RM4JA01
RM4JA01
RM4JA01safety reliability data | MTTF,
RM4JA01safety reliability data | B10,
RM4JA01 | MTTFd,
RM4JA01 | B10d,
RM4JA01
RM17JC00MW
RM17JC00MWstandards | EN60255-6, IEC60255-6
RM17JC00MWproduct certifications | UL, CSA, GL, C-Tick, GOST, CCC
RM17JC00MWmarking | UL, CSA, GL, C-Tick, GOST, CE, CCC
RM17JC00MWdirectives | No 73/23/EEC + 93/68/EEC
RM17JC00MWdirectives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
RM17JC00MWdirectives | 2002/95/EC
RM17JC00MW
RM17JC00MW | Not specified ¦ IEC60721-3-3,Climatic category,
RM17JC00MW | Germanisher Lloyd,Environmental category,
RM17JC00MWambient air temperature for storage | -40…+70 ¦ ,Storage,
RM17JC00MWambient air temperature for operation | -20…+50 ¦ ,Operation,
RM17JC00MWrelative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM17JC00MW | IEC60947-5-1,Cyclic Damp Heat Test,
RM17JC00MWvibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM17JC00MWshock resistance | 5 gn ¦ IEC60068-2-27
RM17JC00MWbump resistance | IEC60068-2-29
RM17JC00MWseismic resistance | IEC60068-3-3
RM17JC00MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM17JC00MWIP degree of protection | IP30 ¦ IEC60529,Housing,
RM17JC00MWIP degree of protection | IEC60529,Front Panel,
RM17JC00MW
RM17JC00MWwidth | 17.5 x 90 x 72 ¦ ,Width,
RM17JC00MWheight | Height,
RM17JC00MWdepth | Depth,
RM17JC00MWnet weight | 110
RM17JC00MWmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM17JC00MWmounting support | - ¦ IEC/EN 60715,With socket,
RM17JC00MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM17JC00MWMinimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM17JC00MWMinimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM17JC00MWconnections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM17JC00MWconnections - terminals | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM17JC00MWconnections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM17JC00MWconnections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM17JC00MWtightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM17JC00MWcable stripping length | Not specified ¦ ,Cable stripping length,
RM17JC00MWduty time | Not specified
RM17JC00MW
RM17JC00MWelectromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard,
RM17JC00MWelectromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM17JC00MWelectromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM17JC00MWelectromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM17JC00MWelectromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM17JC00MWelectromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM17JC00MWelectromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM17JC00MWelectromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM17JC00MWelectromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM17JC00MWelectromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM17JC00MWelectromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM17JC00MWelectromagnetic compatibility | · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM17JC00MWelectromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM17JC00MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM17JC00MWelectromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM17JC00MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM17JC00MWelectromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM17JC00MWelectromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM17JC00MWelectromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM17JC00MW
RM17JC00MWpollution degree | 3 ¦ IEC60664-1
RM17JC00MWovervoltage category | III ¦ IEC60664-1
RM17JC00MWcircuit group | Supply,Terminal
RM17JC00MWcircuit group | Input 1,
RM17JC00MWcircuit group | Input 2,
RM17JC00MWcircuit group | Input 3,
RM17JC00MWcircuit group | Output 1,
RM17JC00MWcircuit group | 600 ¦ ,Output 2,
RM17JC00MW | 600 ¦ ,Supply,Rated
RM17JC00MW | 600 ¦ ,Input 1,Voltage
RM17JC00MW | Input 2,Spec
RM17JC00MW | Input 3,
RM17JC00MW | Output 1,
RM17JC00MW | Output 2,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Supply,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM17JC00MW[Ui] rated insulation voltage | 4 ¦ IEC60664-1,Output 1,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM17JC00MW[Ui] rated insulation voltage | 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM17JC00MW[Uimp] rated impulse withstand voltage | > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM17JC00MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM17JC00MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM17JC00MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM17JC00MWdielectric strength | IEC60255-27,Supply / Output 1,
RM17JC00MWdielectric strength | IEC60255-27,Supply / Output 2,
RM17JC00MWdielectric strength | IEC60255-27,Output 1 / Output 2,
RM17JC00MWdielectric strength | IEC60255-27,Input 1 / Output 1,
RM17JC00MWdielectric strength | IEC60255-27,Input 1 / Output 2,
RM17JC00MWdielectric strength | IEC60255-27,Input 2 / Output 1,
RM17JC00MWdielectric strength | IEC60255-27,Input 2 / Output 2,
RM17JC00MWdielectric strength | IEC60255-27,Input 3 / Output 1,
RM17JC00MWdielectric strength | IEC60255-27,Input 3 / Output 2,
RM17JC00MWdielectric strength | IEC60255-27,Input 1 / Input 2,
RM17JC00MWdielectric strength | IEC60255-27,Input 2 / Input 3,
RM17JC00MWdielectric strength | IEC60255-27,Input 1 / Input 3,
RM17JC00MWinsulation resistance | IEC60255-27,Supply / Input 1,
RM17JC00MWinsulation resistance | IEC60255-27,Supply / Input 2,
RM17JC00MWinsulation resistance | IEC60255-27,Supply / Input 3,
RM17JC00MWinsulation resistance | IEC60255-27,Supply / Output 1,
RM17JC00MWinsulation resistance | IEC60255-27,Supply / Output 2,
RM17JC00MWinsulation resistance | IEC60255-27,Output 1 / Output 2,
RM17JC00MWinsulation resistance | IEC60255-27,Input 1 / Output 1,
RM17JC00MWinsulation resistance | IEC60255-27,Input 1 / Output 2,
RM17JC00MWinsulation resistance | IEC60255-27,Input 2 / Output 1,
RM17JC00MWinsulation resistance | IEC60255-27,Input 2 / Output 2,
RM17JC00MWinsulation resistance | IEC60255-27,Input 3 / Output 1,
RM17JC00MWinsulation resistance | IEC60255-27,Input 3 / Output 2,
RM17JC00MWinsulation resistance | IEC60255-27,Input 1 / Input 2,
RM17JC00MWinsulation resistance | IEC60255-27,Input 2 / Input 3,
RM17JC00MWinsulation resistance | IEC60255-27,Input 1 / Input 3,
RM17JC00MW
RM17JC00MW[Us] rated supply voltage | ~/-- 24…240
RM17JC00MWsupply voltage limits | ~/-- 20.4…264
RM17JC00MWpolarity
RM17JC00MWsupply frequency | 50 / 60
RM17JC00MWsupply frequency | 45…66
RM17JC00MWpower consumption | ~ 3VA, -- 1W
RM17JC00MWimmunity to microbreaks | 10
RM17JC00MWsupply terminal | A1-A2
RM17JC00MWon-load factor
RM17JC00MWrelease of input voltage
RM17JC00MW
RM17JC00MW | - ¦ ,Over / undercurrent (windows mode),
RM17JC00MW | · ¦ ,Over current,
RM17JC00MW | - ¦ ,Under current,
RM17JC00MW | ~ 2000…20000
RM17JC00MW | - ¦ ,E1-M / B1-C,
RM17JC00MW | - ¦ ,E2-M / B2-C,
RM17JC00MW | - ¦ ,E3-M / B3-C,
RM17JC00MW | A1+ / A2-,
RM17JC00MW | · ¦ ,Built in current transformer,
RM17JC00MW | - ¦ ,E1-M / B1-C,
RM17JC00MW | - ¦ ,E2-M / B2-C,
RM17JC00MW | - ¦ ,E3-M / B3-C,
RM17JC00MW | A1+ / A2-,
RM17JC00MW | ~ 2000…20000 ¦ ,Built in current transformer,
RM17JC00MW | - ¦ ,E1-M / B1-C,
RM17JC00MW | - ¦ ,E2-M / B2-C,
RM17JC00MW | - ¦ ,E3-M / B3-C,
RM17JC00MW | A1+ / A2-,
RM17JC00MW | Adjustable 10%...100% of 20000 ¦ ,Built in current transformer,
RM17JC00MW | - ¦ ,E1-M / B1-C,
RM17JC00MW | - ¦ ,E2-M / B2-C,
RM17JC00MW | - ¦ ,E3-M / B3-C,
RM17JC00MW | A1+ / A2-,
RM17JC00MW | Fixed 15% of threshold setting ¦ ,Built in current transformer,
RM17JC00MW | Current transformer
RM17JC00MW | Turning conductor around current transformer
RM17JC00MW | 50 / 60
RM17JC00MW | 40…70
RM17JC00MW | +/- 10% of full scale value
RM17JC00MW | +/- 0.5%
RM17JC00MW | < 1% over whole range
RM17JC00MW | 0.05% / oC
RM17JC00MW | 30
RM17JC00MW | True RMS
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MWoutput type | 1 x C/O relay contacts
RM17JC00MWoutput terminal | 11-12-14
RM17JC00MWoutput logic | Selectable energized/de-energized on fault-free ¦ ,R1 (11-12-14),
RM17JC00MWoutput logic | R2 (21-22-24),
RM17JC00MWcontacts material | Cadmium free
RM17JC00MWmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM17JC00MWelectrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1,
RM17JC00MWelectrical durability | IEC60947-4-1,DC-1,
RM17JC00MWelectrical durability | IEC60947-5-1,AC-15,
RM17JC00MWelectrical durability | IEC60947-5-1,DC-13,
RM17JC00MW[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM17JC00MW[Ie] rated operational current | IEC61810-1,Rated switching current,
RM17JC00MWmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM17JC00MWmaximum switching capacity | 8 ¦ ,Maximum switching current,
RM17JC00MWmaximum switching capacity | 2000 ¦ ,Maximum switching capacity,
RM17JC00MWminimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
RM17JC00MWminimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM17JC00MWminimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM17JC00MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM17JC00MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM17JC00MWthermal current | IEC60947-5-1
RM17JC00MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM17JC00MWshort circuit protection | IEC62314,Solid State Output by external fuse,
RM17JC00MW
RM17JC00MWtime delay type | - ¦ ,"OFF" delay,
RM17JC00MWtime delay type | - ¦ ,"ON" delay,
RM17JC00MWtime delay type | - ¦ ,Inhibition,
RM17JC00MWtime delay range | - ¦ ,"OFF" delay,
RM17JC00MWtime delay range | - ¦ ,"ON" delay,
RM17JC00MWtime delay range | - ¦ ,Inhibition,
RM17JC00MWresponse time | 0
RM17JC00MWresponse time
RM17JC00MWresponse time
RM17JC00MWresponse time
RM17JC00MWresponse time
RM17JC00MWpower on delay | 0
RM17JC00MWreset time | - ¦ ,through Un power reset,
RM17JC00MWreset time | through front panel reset,
RM17JC00MWreset time | through input control reset,
RM17JC00MWsetting accuracy of time delay | -
RM17JC00MWrepeat accuracy of time delay | -
RM17JC00MWtime delay drift | -
RM17JC00MWtime delay drift | -
RM17JC00MW
RM17JC00MWstatus LED
RM17JC00MWlocal signalling | Power supply availability,
RM17JC00MWlocal signalling | Power supply not availability,
RM17JC00MWlocal signalling | Timing in-progress,
RM17JC00MWlocal signalling | Output is energized,
RM17JC00MWlocal signalling | Output is de-energized,
RM17JC00MWlocal signalling | Range Setting Changes,
RM17JC00MWlocal signalling
RM17JC00MWlocal signalling
RM17JC00MWlocal signalling
RM17JC00MWlocal signalling
RM17JC00MWlocal signalling
RM17JC00MWlocal signalling
RM17JC00MWlocal signalling
RM17JC00MWlocal signalling
RM17JC00MWlocal signalling
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MWdiagnostic button
RM17JC00MW
RM17JC00MW
RM17JC00MW
RM17JC00MWsafety reliability data | MTTF,
RM17JC00MWsafety reliability data | B10,
RM17JC00MW | MTTFd,
RM17JC00MW | B10d,
RM17JC00MW
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)standards | EN60255-6, IEC60255-6
RM22JA31MW (Catch Up)product certifications | UL, CSA, GL, C-Tick, GOST, CCC
RM22JA31MW (Catch Up)marking | UL, CSA, GL, C-Tick, GOST, CE, CCC
RM22JA31MW (Catch Up)directives | No 73/23/EEC + 93/68/EEC
RM22JA31MW (Catch Up)directives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
RM22JA31MW (Catch Up)directives | 2002/95/EC
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up) | Not specified ¦ IEC60721-3-3,Climatic category,
RM22JA31MW (Catch Up) | Germanisher Lloyd,Environmental category,
RM22JA31MW (Catch Up)ambient air temperature for storage | -40…+70 ¦ ,Storage,
RM22JA31MW (Catch Up)ambient air temperature for operation | -20…+50 ¦ ,Operation,
RM22JA31MW (Catch Up)relative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM22JA31MW (Catch Up) | IEC60947-5-1,Cyclic Damp Heat Test,
RM22JA31MW (Catch Up)vibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM22JA31MW (Catch Up)shock resistance | 5 gn ¦ IEC60068-2-27
RM22JA31MW (Catch Up)bump resistance | IEC60068-2-29
RM22JA31MW (Catch Up)seismic resistance | IEC60068-3-3
RM22JA31MW (Catch Up)IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
RM22JA31MW (Catch Up)IP degree of protection | IP30 ¦ IEC60529,Housing,
RM22JA31MW (Catch Up)IP degree of protection | IEC60529,Front Panel,
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)width | 22.5 x ? x ? ¦ ,Width,
RM22JA31MW (Catch Up)height | Height,
RM22JA31MW (Catch Up)depth | Depth,
RM22JA31MW (Catch Up)net weight | ?
RM22JA31MW (Catch Up)mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
RM22JA31MW (Catch Up)mounting support | - ¦ IEC/EN 60715,With socket,
RM22JA31MW (Catch Up)mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22JA31MW (Catch Up)Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
RM22JA31MW (Catch Up)Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
RM22JA31MW (Catch Up)connections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
RM22JA31MW (Catch Up)connections - terminals | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
RM22JA31MW (Catch Up)connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
RM22JA31MW (Catch Up)connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22JA31MW (Catch Up)tightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM22JA31MW (Catch Up)cable stripping length | Not specified ¦ ,Cable stripping length,
RM22JA31MW (Catch Up)duty time | Not specified
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)electromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard,
RM22JA31MW (Catch Up)electromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
RM22JA31MW (Catch Up)electromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
RM22JA31MW (Catch Up)electromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
RM22JA31MW (Catch Up)electromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
RM22JA31MW (Catch Up)electromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
RM22JA31MW (Catch Up)electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
RM22JA31MW (Catch Up)electromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
RM22JA31MW (Catch Up)electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
RM22JA31MW (Catch Up)electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
RM22JA31MW (Catch Up)electromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
RM22JA31MW (Catch Up)electromagnetic compatibility | · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
RM22JA31MW (Catch Up)electromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
RM22JA31MW (Catch Up)electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
RM22JA31MW (Catch Up)electromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
RM22JA31MW (Catch Up)electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
RM22JA31MW (Catch Up)electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
RM22JA31MW (Catch Up)electromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
RM22JA31MW (Catch Up)electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)pollution degree | 3 ¦ IEC60664-1
RM22JA31MW (Catch Up)overvoltage category | III ¦ IEC60664-1
RM22JA31MW (Catch Up)circuit group | Supply,Terminal
RM22JA31MW (Catch Up)circuit group | Input 1,
RM22JA31MW (Catch Up)circuit group | Input 2,
RM22JA31MW (Catch Up)circuit group | Input 3,
RM22JA31MW (Catch Up)circuit group | Output 1,
RM22JA31MW (Catch Up)circuit group | 600 ¦ ,Output 2,
RM22JA31MW (Catch Up) | 600 ¦ ,Supply,Rated
RM22JA31MW (Catch Up) | 600 ¦ ,Input 1,Voltage
RM22JA31MW (Catch Up) | Input 2,Spec
RM22JA31MW (Catch Up) | Input 3,
RM22JA31MW (Catch Up) | Output 1,
RM22JA31MW (Catch Up) | Output 2,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 2,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 3,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | 4 ¦ IEC60664-1,Output 1,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Output 2,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
RM22JA31MW (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
RM22JA31MW (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
RM22JA31MW (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
RM22JA31MW (Catch Up)dielectric strength | IEC60255-27,Supply / Output 1,
RM22JA31MW (Catch Up)dielectric strength | IEC60255-27,Supply / Output 2,
RM22JA31MW (Catch Up)dielectric strength | IEC60255-27,Output 1 / Output 2,
RM22JA31MW (Catch Up)dielectric strength | IEC60255-27,Input 1 / Output 1,
RM22JA31MW (Catch Up)dielectric strength | IEC60255-27,Input 1 / Output 2,
RM22JA31MW (Catch Up)dielectric strength | IEC60255-27,Input 2 / Output 1,
RM22JA31MW (Catch Up)dielectric strength | IEC60255-27,Input 2 / Output 2,
RM22JA31MW (Catch Up)dielectric strength | IEC60255-27,Input 3 / Output 1,
RM22JA31MW (Catch Up)dielectric strength | IEC60255-27,Input 3 / Output 2,
RM22JA31MW (Catch Up)dielectric strength | IEC60255-27,Input 1 / Input 2,
RM22JA31MW (Catch Up)dielectric strength | IEC60255-27,Input 2 / Input 3,
RM22JA31MW (Catch Up)dielectric strength | IEC60255-27,Input 1 / Input 3,
RM22JA31MW (Catch Up)insulation resistance | IEC60255-27,Supply / Input 1,
RM22JA31MW (Catch Up)insulation resistance | IEC60255-27,Supply / Input 2,
RM22JA31MW (Catch Up)insulation resistance | IEC60255-27,Supply / Input 3,
RM22JA31MW (Catch Up)insulation resistance | IEC60255-27,Supply / Output 1,
RM22JA31MW (Catch Up)insulation resistance | IEC60255-27,Supply / Output 2,
RM22JA31MW (Catch Up)insulation resistance | IEC60255-27,Output 1 / Output 2,
RM22JA31MW (Catch Up)insulation resistance | IEC60255-27,Input 1 / Output 1,
RM22JA31MW (Catch Up)insulation resistance | IEC60255-27,Input 1 / Output 2,
RM22JA31MW (Catch Up)insulation resistance | IEC60255-27,Input 2 / Output 1,
RM22JA31MW (Catch Up)insulation resistance | IEC60255-27,Input 2 / Output 2,
RM22JA31MW (Catch Up)insulation resistance | IEC60255-27,Input 3 / Output 1,
RM22JA31MW (Catch Up)insulation resistance | IEC60255-27,Input 3 / Output 2,
RM22JA31MW (Catch Up)insulation resistance | IEC60255-27,Input 1 / Input 2,
RM22JA31MW (Catch Up)insulation resistance | IEC60255-27,Input 2 / Input 3,
RM22JA31MW (Catch Up)insulation resistance | IEC60255-27,Input 1 / Input 3,
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)[Us] rated supply voltage | ~/-- 24…240
RM22JA31MW (Catch Up)supply voltage limits | ~/-- 20.4…264
RM22JA31MW (Catch Up)polarity
RM22JA31MW (Catch Up)supply frequency | 50 / 60
RM22JA31MW (Catch Up)supply frequency | 45…66
RM22JA31MW (Catch Up)power consumption | ~ 3.5VA, -- 0.6W
RM22JA31MW (Catch Up)immunity to microbreaks | 10
RM22JA31MW (Catch Up)supply terminal | A1-A2
RM22JA31MW (Catch Up)on-load factor
RM22JA31MW (Catch Up)release of input voltage
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up) | - ¦ ,Over / undercurrent (windows mode),
RM22JA31MW (Catch Up) | Selectable with memory / without memory ¦ ,Over current,
RM22JA31MW (Catch Up) | Selectable with memory / without memory ¦ ,Under current,
RM22JA31MW (Catch Up) | ~/-- 2…500
RM22JA31MW (Catch Up) | 5 ¦ ,E1-M / B1-C,
RM22JA31MW (Catch Up) | 1 ¦ ,E2-M / B2-C,
RM22JA31MW (Catch Up) | 0.2 ¦ ,E3-M / B3-C,
RM22JA31MW (Catch Up) | A1+ / A2-,
RM22JA31MW (Catch Up) | - ¦ ,Built in current transformer,
RM22JA31MW (Catch Up) | ~/-- 2…20 ¦ ,E1-M / B1-C,
RM22JA31MW (Catch Up) | ~/-- 10…100 ¦ ,E2-M / B2-C,
RM22JA31MW (Catch Up) | ~/-- 50…500 ¦ ,E3-M / B3-C,
RM22JA31MW (Catch Up) | A1+ / A2-,
RM22JA31MW (Catch Up) | - ¦ ,Built in current transformer,
RM22JA31MW (Catch Up) | Adjustable 10%...100% of 20 ¦ ,E1-M / B1-C,
RM22JA31MW (Catch Up) | Adjustable 10%...100% of 100 ¦ ,E2-M / B2-C,
RM22JA31MW (Catch Up) | Adjustable 10%...100% of 500 ¦ ,E3-M / B3-C,
RM22JA31MW (Catch Up) | A1+ / A2-,
RM22JA31MW (Catch Up) | - ¦ ,Built in current transformer,
RM22JA31MW (Catch Up) | Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C,
RM22JA31MW (Catch Up) | Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C,
RM22JA31MW (Catch Up) | Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C,
RM22JA31MW (Catch Up) | A1+ / A2-,
RM22JA31MW (Catch Up) | - ¦ ,Built in current transformer,
RM22JA31MW (Catch Up) | Shunt resistor
RM22JA31MW (Catch Up) | E1-M, E2-M, E3-M
RM22JA31MW (Catch Up) | 50 / 60
RM22JA31MW (Catch Up) | 36…77
RM22JA31MW (Catch Up) | +/- 10% of full scale value
RM22JA31MW (Catch Up) | +/- 0.5%
RM22JA31MW (Catch Up) | < 1% over whole range
RM22JA31MW (Catch Up) | 0.05% / oC
RM22JA31MW (Catch Up) | 30
RM22JA31MW (Catch Up) | True RMS
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)output type | 2 x C/O relay contacts
RM22JA31MW (Catch Up)output terminal | 11-12-14, 21-22-24
RM22JA31MW (Catch Up)output logic | Energized on fault-free ¦ ,R1 (11-12-14),
RM22JA31MW (Catch Up)output logic | R2 (21-22-24),
RM22JA31MW (Catch Up)contacts material | Cadmium free
RM22JA31MW (Catch Up)mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM22JA31MW (Catch Up)electrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1,
RM22JA31MW (Catch Up)electrical durability | IEC60947-4-1,DC-1,
RM22JA31MW (Catch Up)electrical durability | IEC60947-5-1,AC-15,
RM22JA31MW (Catch Up)electrical durability | IEC60947-5-1,DC-13,
RM22JA31MW (Catch Up)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM22JA31MW (Catch Up)[Ie] rated operational current | IEC61810-1,Rated switching current,
RM22JA31MW (Catch Up)maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
RM22JA31MW (Catch Up)maximum switching capacity | ~ 8 ¦ ,Maximum switching current,
RM22JA31MW (Catch Up)maximum switching capacity | 2000 ¦ ,Maximum switching capacity,
RM22JA31MW (Catch Up)minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
RM22JA31MW (Catch Up)minimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
RM22JA31MW (Catch Up)minimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM22JA31MW (Catch Up)maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22JA31MW (Catch Up)maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22JA31MW (Catch Up)thermal current | IEC60947-5-1
RM22JA31MW (Catch Up)short circuit protection | IEC60947-5-1,Relay Output by external fuse,
RM22JA31MW (Catch Up)short circuit protection | IEC62314,Solid State Output by external fuse,
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)time delay type | · ¦ ,"OFF" delay,
RM22JA31MW (Catch Up)time delay type | - ¦ ,"ON" delay,
RM22JA31MW (Catch Up)time delay type | · ¦ ,Inhibition,
RM22JA31MW (Catch Up)time delay range | Adjustable 0.3…30 ¦ ,"OFF" delay,
RM22JA31MW (Catch Up)time delay range | - ¦ ,"ON" delay,
RM22JA31MW (Catch Up)time delay range | Adjustable 1…20 ¦ ,Inhibition,
RM22JA31MW (Catch Up)response time | Not specified ¦ ,on crossing the threshold,
RM22JA31MW (Catch Up)response time
RM22JA31MW (Catch Up)response time
RM22JA31MW (Catch Up)response time
RM22JA31MW (Catch Up)response time
RM22JA31MW (Catch Up)power on delay | 0
RM22JA31MW (Catch Up)reset time | 0
RM22JA31MW (Catch Up)reset time | through front panel reset,
RM22JA31MW (Catch Up)reset time | through input control reset,
RM22JA31MW (Catch Up)setting accuracy of time delay | +/- 10% of full scales
RM22JA31MW (Catch Up)repeat accuracy of time delay | +/- 2%
RM22JA31MW (Catch Up)time delay drift | Not specified
RM22JA31MW (Catch Up)time delay drift | Not specified
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)status LED
RM22JA31MW (Catch Up)local signalling | Power supply availability,
RM22JA31MW (Catch Up)local signalling | Power supply not availability,
RM22JA31MW (Catch Up)local signalling | Timing in-progress,
RM22JA31MW (Catch Up)local signalling | Output is energized,
RM22JA31MW (Catch Up)local signalling | Output is de-energized,
RM22JA31MW (Catch Up)local signalling | Range Setting Changes,
RM22JA31MW (Catch Up)local signalling
RM22JA31MW (Catch Up)local signalling
RM22JA31MW (Catch Up)local signalling
RM22JA31MW (Catch Up)local signalling
RM22JA31MW (Catch Up)local signalling
RM22JA31MW (Catch Up)local signalling
RM22JA31MW (Catch Up)local signalling
RM22JA31MW (Catch Up)local signalling
RM22JA31MW (Catch Up)local signalling
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)diagnostic button
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)
RM22JA31MW (Catch Up)safety reliability data | MTTF,
RM22JA31MW (Catch Up)safety reliability data | B10,
RM22JA31MW (Catch Up) | MTTFd,
RM22JA31MW (Catch Up) | B10d,
RM22JA31MW (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)standards | EN60255-6, IEC60255-6
84893852 (Catch Up)product certifications | UL, CSA, GL, C-Tick, GOST, CCC
84893852 (Catch Up)marking | UL, CSA, GL, C-Tick, GOST, CE, CCC
84893852 (Catch Up)directives | No 73/23/EEC + 93/68/EEC
84893852 (Catch Up)directives | No 89/336/EEC + 92/31/EEC + 93/68/EEC
84893852 (Catch Up)directives | 2002/95/EC
84893852 (Catch Up)
84893852 (Catch Up) | Not specified ¦ IEC60721-3-3,Climatic category,
84893852 (Catch Up) | Germanisher Lloyd,Environmental category,
84893852 (Catch Up)ambient air temperature for storage | -40…+70 ¦ ,Storage,
84893852 (Catch Up)ambient air temperature for operation | -20…+50 ¦ ,Operation,
84893852 (Catch Up)relative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
84893852 (Catch Up) | IEC60947-5-1,Cyclic Damp Heat Test,
84893852 (Catch Up)vibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
84893852 (Catch Up)shock resistance | 5 gn ¦ IEC60068-2-27
84893852 (Catch Up)bump resistance | IEC60068-2-29
84893852 (Catch Up)seismic resistance | IEC60068-3-3
84893852 (Catch Up)IP degree of protection | IP20 ¦ IEC60529,Terminal Block,
84893852 (Catch Up)IP degree of protection | IP30 ¦ IEC60529,Housing,
84893852 (Catch Up)IP degree of protection | IEC60529,Front Panel,
84893852 (Catch Up)
84893852 (Catch Up)width | 22.5 x ? x ? ¦ ,Width,
84893852 (Catch Up)height | Height,
84893852 (Catch Up)depth | Depth,
84893852 (Catch Up)net weight | ?
84893852 (Catch Up)mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket,
84893852 (Catch Up)mounting support | - ¦ IEC/EN 60715,With socket,
84893852 (Catch Up)mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
84893852 (Catch Up)Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
84893852 (Catch Up)Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
84893852 (Catch Up)connections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84893852 (Catch Up)connections - terminals | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84893852 (Catch Up)connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
84893852 (Catch Up)connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
84893852 (Catch Up)tightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
84893852 (Catch Up)cable stripping length | Not specified ¦ ,Cable stripping length,
84893852 (Catch Up)duty time | Not specified
84893852 (Catch Up)
84893852 (Catch Up)electromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard,
84893852 (Catch Up)electromagnetic compatibility | Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge,
84893852 (Catch Up)electromagnetic compatibility | Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84893852 (Catch Up)electromagnetic compatibility | Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst,
84893852 (Catch Up)electromagnetic compatibility | Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge,
84893852 (Catch Up)electromagnetic compatibility | Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance,
84893852 (Catch Up)electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
84893852 (Catch Up)electromagnetic compatibility | Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84893852 (Catch Up)electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
84893852 (Catch Up)electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
84893852 (Catch Up)electromagnetic compatibility | Not tested ¦ IEC61000-4-13,Low frequency harmonics,
84893852 (Catch Up)electromagnetic compatibility | · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84893852 (Catch Up)electromagnetic compatibility | IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard,
84893852 (Catch Up)electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84893852 (Catch Up)electromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84893852 (Catch Up)electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84893852 (Catch Up)electromagnetic compatibility | Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84893852 (Catch Up)electromagnetic compatibility | Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84893852 (Catch Up)electromagnetic compatibility | EMC 2 ¦ Germanisher Lloyd,Conducted emission,
84893852 (Catch Up)
84893852 (Catch Up)pollution degree | 3 ¦ IEC60664-1
84893852 (Catch Up)overvoltage category | III ¦ IEC60664-1
84893852 (Catch Up)circuit group | Supply,Terminal
84893852 (Catch Up)circuit group | Input 1,
84893852 (Catch Up)circuit group | Input 2,
84893852 (Catch Up)circuit group | Input 3,
84893852 (Catch Up)circuit group | Output 1,
84893852 (Catch Up)circuit group | 600 ¦ ,Output 2,
84893852 (Catch Up) | 600 ¦ ,Supply,Rated
84893852 (Catch Up) | 600 ¦ ,Input 1,Voltage
84893852 (Catch Up) | Input 2,Spec
84893852 (Catch Up) | Input 3,
84893852 (Catch Up) | Output 1,
84893852 (Catch Up) | Output 2,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 2,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 3,
84893852 (Catch Up)[Ui] rated insulation voltage | 4 ¦ IEC60664-1,Output 1,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Output 2,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
84893852 (Catch Up)[Ui] rated insulation voltage | 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
84893852 (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1,
84893852 (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 2,
84893852 (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 3,
84893852 (Catch Up)dielectric strength | IEC60255-27,Supply / Output 1,
84893852 (Catch Up)dielectric strength | IEC60255-27,Supply / Output 2,
84893852 (Catch Up)dielectric strength | IEC60255-27,Output 1 / Output 2,
84893852 (Catch Up)dielectric strength | IEC60255-27,Input 1 / Output 1,
84893852 (Catch Up)dielectric strength | IEC60255-27,Input 1 / Output 2,
84893852 (Catch Up)dielectric strength | IEC60255-27,Input 2 / Output 1,
84893852 (Catch Up)dielectric strength | IEC60255-27,Input 2 / Output 2,
84893852 (Catch Up)dielectric strength | IEC60255-27,Input 3 / Output 1,
84893852 (Catch Up)dielectric strength | IEC60255-27,Input 3 / Output 2,
84893852 (Catch Up)dielectric strength | IEC60255-27,Input 1 / Input 2,
84893852 (Catch Up)dielectric strength | IEC60255-27,Input 2 / Input 3,
84893852 (Catch Up)dielectric strength | IEC60255-27,Input 1 / Input 3,
84893852 (Catch Up)insulation resistance | IEC60255-27,Supply / Input 1,
84893852 (Catch Up)insulation resistance | IEC60255-27,Supply / Input 2,
84893852 (Catch Up)insulation resistance | IEC60255-27,Supply / Input 3,
84893852 (Catch Up)insulation resistance | IEC60255-27,Supply / Output 1,
84893852 (Catch Up)insulation resistance | IEC60255-27,Supply / Output 2,
84893852 (Catch Up)insulation resistance | IEC60255-27,Output 1 / Output 2,
84893852 (Catch Up)insulation resistance | IEC60255-27,Input 1 / Output 1,
84893852 (Catch Up)insulation resistance | IEC60255-27,Input 1 / Output 2,
84893852 (Catch Up)insulation resistance | IEC60255-27,Input 2 / Output 1,
84893852 (Catch Up)insulation resistance | IEC60255-27,Input 2 / Output 2,
84893852 (Catch Up)insulation resistance | IEC60255-27,Input 3 / Output 1,
84893852 (Catch Up)insulation resistance | IEC60255-27,Input 3 / Output 2,
84893852 (Catch Up)insulation resistance | IEC60255-27,Input 1 / Input 2,
84893852 (Catch Up)insulation resistance | IEC60255-27,Input 2 / Input 3,
84893852 (Catch Up)insulation resistance | IEC60255-27,Input 1 / Input 3,
84893852 (Catch Up)
84893852 (Catch Up)[Us] rated supply voltage | ~/-- 24…240
84893852 (Catch Up)supply voltage limits | ~/-- 20.4…264
84893852 (Catch Up)polarity
84893852 (Catch Up)supply frequency | 50 / 60
84893852 (Catch Up)supply frequency | 45…66
84893852 (Catch Up)power consumption | ~ 3.5VA, -- 0.6W
84893852 (Catch Up)immunity to microbreaks | 10
84893852 (Catch Up)supply terminal | A1-A2
84893852 (Catch Up)on-load factor
84893852 (Catch Up)release of input voltage
84893852 (Catch Up)
84893852 (Catch Up) | - ¦ ,Over / undercurrent (windows mode),
84893852 (Catch Up) | - ¦ ,Over current,
84893852 (Catch Up) | · ¦ ,Under current,
84893852 (Catch Up) | Fix 0.7A
84893852 (Catch Up) | - ¦ ,E1-M / B1-C,
84893852 (Catch Up) | 0.015 ¦ ,E2-M / B2-C,
84893852 (Catch Up) | - ¦ ,E3-M / B3-C,
84893852 (Catch Up) | A1+ / A2-,
84893852 (Catch Up) | - ¦ ,Built in current transformer,
84893852 (Catch Up) | - ¦ ,E1-M / B1-C,
84893852 (Catch Up) | Max 12A ¦ ,E2-M / B2-C,
84893852 (Catch Up) | - ¦ ,E3-M / B3-C,
84893852 (Catch Up) | A1+ / A2-,
84893852 (Catch Up) | - ¦ ,Built in current transformer,
84893852 (Catch Up) | - ¦ ,E1-M / B1-C,
84893852 (Catch Up) | - ¦ ,E2-M / B2-C,
84893852 (Catch Up) | - ¦ ,E3-M / B3-C,
84893852 (Catch Up) | A1+ / A2-,
84893852 (Catch Up) | - ¦ ,Built in current transformer,
84893852 (Catch Up) | - ¦ ,E1-M / B1-C,
84893852 (Catch Up) | - ¦ ,E2-M / B2-C,
84893852 (Catch Up) | - ¦ ,E3-M / B3-C,
84893852 (Catch Up) | A1+ / A2-,
84893852 (Catch Up) | - ¦ ,Built in current transformer,
84893852 (Catch Up) | Shunt resistor
84893852 (Catch Up) | E2-M
84893852 (Catch Up) | 50 / 60
84893852 (Catch Up) | 36…77
84893852 (Catch Up) | +/- 10% of full scale value
84893852 (Catch Up) | +/- 0.5%
84893852 (Catch Up) | < 1% over whole range
84893852 (Catch Up) | 0.05% / oC
84893852 (Catch Up) | 30
84893852 (Catch Up) | True RMS
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)output type | 21x C/O relay contacts
84893852 (Catch Up)output terminal | 2014-11-12 00:00:00
84893852 (Catch Up)output logic | Energized on fault-free ¦ ,R1 (11-12-14),
84893852 (Catch Up)output logic | R2 (21-22-24),
84893852 (Catch Up)contacts material | Cadmium free
84893852 (Catch Up)mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
84893852 (Catch Up)electrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1,
84893852 (Catch Up)electrical durability | IEC60947-4-1,DC-1,
84893852 (Catch Up)electrical durability | IEC60947-5-1,AC-15,
84893852 (Catch Up)electrical durability | IEC60947-5-1,DC-13,
84893852 (Catch Up)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
84893852 (Catch Up)[Ie] rated operational current | IEC61810-1,Rated switching current,
84893852 (Catch Up)maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
84893852 (Catch Up)maximum switching capacity | ~ 5 ¦ ,Maximum switching current,
84893852 (Catch Up)maximum switching capacity | 1250 ¦ ,Maximum switching capacity,
84893852 (Catch Up)minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage,
84893852 (Catch Up)minimum switching capacity | 10 ¦ IEC60947-5-4,Minimum switching current,
84893852 (Catch Up)minimum switching capacity | 50 ¦ IEC60947-5-4,Minimum switching capacity,
84893852 (Catch Up)maximum voltage drop | - ¦ IEC62314,Only for solid state output,
84893852 (Catch Up)maximum leakage current | - ¦ IEC62314,Only for solid state output,
84893852 (Catch Up)thermal current | IEC60947-5-1
84893852 (Catch Up)short circuit protection | IEC60947-5-1,Relay Output by external fuse,
84893852 (Catch Up)short circuit protection | IEC62314,Solid State Output by external fuse,
84893852 (Catch Up)
84893852 (Catch Up)time delay type | - ¦ ,"OFF" delay,
84893852 (Catch Up)time delay type | - ¦ ,"ON" delay,
84893852 (Catch Up)time delay type | - ¦ ,Inhibition,
84893852 (Catch Up)time delay range | - ¦ ,"OFF" delay,
84893852 (Catch Up)time delay range | - ¦ ,"ON" delay,
84893852 (Catch Up)time delay range | - ¦ ,Inhibition,
84893852 (Catch Up)response time | Not specified ¦ ,on crossing the threshold,
84893852 (Catch Up)response time
84893852 (Catch Up)response time
84893852 (Catch Up)response time
84893852 (Catch Up)response time
84893852 (Catch Up)power on delay | 0
84893852 (Catch Up)reset time | 0
84893852 (Catch Up)reset time | through front panel reset,
84893852 (Catch Up)reset time | through input control reset,
84893852 (Catch Up)setting accuracy of time delay | +/- 10% of full scales
84893852 (Catch Up)repeat accuracy of time delay | +/- 2%
84893852 (Catch Up)time delay drift | Not specified
84893852 (Catch Up)time delay drift | Not specified
84893852 (Catch Up)
84893852 (Catch Up)status LED
84893852 (Catch Up)local signalling | Power supply availability,
84893852 (Catch Up)local signalling | Power supply not availability,
84893852 (Catch Up)local signalling | Timing in-progress,
84893852 (Catch Up)local signalling | Output is energized,
84893852 (Catch Up)local signalling | Output is de-energized,
84893852 (Catch Up)local signalling | Range Setting Changes,
84893852 (Catch Up)local signalling
84893852 (Catch Up)local signalling
84893852 (Catch Up)local signalling
84893852 (Catch Up)local signalling
84893852 (Catch Up)local signalling
84893852 (Catch Up)local signalling
84893852 (Catch Up)local signalling
84893852 (Catch Up)local signalling
84893852 (Catch Up)local signalling
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)diagnostic button
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)
84893852 (Catch Up)safety reliability data | MTTF,
84893852 (Catch Up)safety reliability data | B10,
84893852 (Catch Up) | MTTFd,
84893852 (Catch Up) | B10d,
84893852 (Catch Up)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)standards | Not specified
84893852 (Autelec Distribution)product certifications | Not specified
84893852 (Autelec Distribution)marking | CE
84893852 (Autelec Distribution)directives | Not specified
84893852 (Autelec Distribution)directives | Not specified
84893852 (Autelec Distribution)directives | Not specified
84893852 (Autelec Distribution)
84893852 (Autelec Distribution) | Not specified ¦ IEC60721-3-3,Climatic category,
84893852 (Autelec Distribution) | Germanisher Lloyd,Environmental category,
84893852 (Autelec Distribution)ambient air temperature for storage | Not specified ¦ ,Storage,
84893852 (Autelec Distribution)ambient air temperature for operation | Not specified ¦ ,Operation,
84893852 (Autelec Distribution)relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
84893852 (Autelec Distribution) | IEC60947-5-1,Cyclic Damp Heat Test,
84893852 (Autelec Distribution)vibration resistance | Not specified ¦ IEC60068-2-6
84893852 (Autelec Distribution)shock resistance | Not specified ¦ IEC60068-2-27
84893852 (Autelec Distribution)bump resistance | IEC60068-2-29
84893852 (Autelec Distribution)seismic resistance | IEC60068-3-3
84893852 (Autelec Distribution)IP degree of protection | Not specified ¦ IEC60529,Terminal Block,
84893852 (Autelec Distribution)IP degree of protection | Not specified ¦ IEC60529,Housing,
84893852 (Autelec Distribution)IP degree of protection | IEC60529,Front Panel,
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)width | 22.5 x 78.5 x 100 ¦ ,Width,
84893852 (Autelec Distribution)height | Height,
84893852 (Autelec Distribution)depth | Depth,
84893852 (Autelec Distribution)net weight | Not specified
84893852 (Autelec Distribution)mounting support | Not specified ¦ IEC/EN 60715,Without socket,
84893852 (Autelec Distribution)mounting support | - ¦ IEC/EN 60715,With socket,
84893852 (Autelec Distribution)mounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
84893852 (Autelec Distribution)Minimum distance to adjacent devices | Not specified ¦ ,Horizontal,
84893852 (Autelec Distribution)Minimum distance to adjacent devices | Not specified ¦ ,Vertical,
84893852 (Autelec Distribution)connections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal),
84893852 (Autelec Distribution)connections - terminals | Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal),
84893852 (Autelec Distribution)connections - terminals | - ¦ IEC60947-1,Solid cable (spring terminal),
84893852 (Autelec Distribution)connections - terminals | - ¦ IEC60947-1,Flexible cable (spring terminal),
84893852 (Autelec Distribution)tightening torque | Not specified ¦ IEC60947-1,Tightening torque,
84893852 (Autelec Distribution)cable stripping length | Not specified ¦ ,Cable stripping length,
84893852 (Autelec Distribution)duty time | Not specified
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ ,Generic immunity standard,
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ IEC61000-4-2,Electrostatic discharge,
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ IEC61000-4-3,Radiated RF & electromagnetic field,
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ IEC61000-4-4,Fast transient / burst,
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ IEC61000-4-5,Surge,
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ IEC61000-4-6,Conducted RF disturbance,
84893852 (Autelec Distribution)electromagnetic compatibility | IEC61000-4-8,Power frequency magnetic field,
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line,
84893852 (Autelec Distribution)electromagnetic compatibility | IEC61000-4-18,1 MHz oscillation wave,
84893852 (Autelec Distribution)electromagnetic compatibility | IEC61000-4-29,DC voltage interruption,
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ IEC61000-4-13,Low frequency harmonics,
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics),
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ ,Generic emission standard,
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment),
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment),
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Radiated emission from enclosure port,
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment),
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment),
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ Germanisher Lloyd,Conducted emission,
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)pollution degree | Not specified ¦ IEC60664-1
84893852 (Autelec Distribution)overvoltage category | Not specified ¦ IEC60664-1
84893852 (Autelec Distribution)circuit group | Supply,Terminal
84893852 (Autelec Distribution)circuit group | Input 1,
84893852 (Autelec Distribution)circuit group | Input 2,
84893852 (Autelec Distribution)circuit group | Input 3,
84893852 (Autelec Distribution)circuit group | Output 1,
84893852 (Autelec Distribution)circuit group | Not specified ¦ ,Output 2,
84893852 (Autelec Distribution) | Not specified ¦ ,Supply,Rated
84893852 (Autelec Distribution) | Not specified ¦ ,Input 1,Voltage
84893852 (Autelec Distribution) | Input 2,Spec
84893852 (Autelec Distribution) | Input 3,
84893852 (Autelec Distribution) | Output 1,
84893852 (Autelec Distribution) | Output 2,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Supply,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Input 1,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Input 2,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Input 3,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Output 1,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Output 2,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 1,Galvanic
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 2,Isolated
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Supply / Input 3,Circuit
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 1,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Supply / Output 2,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Output 1 / Output 2,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 1,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Output 2,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Output 1,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 1,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Input 3 / Output 2,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 2,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Input 2 / Input 3,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Input 1 / Input 3,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 2,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 1,Galvanic
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 2,Isolated
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Input 3,Circuit
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 1,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply / Output 2,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Output 1 / Output 2,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 1,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Output 2,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Output 1,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | Not specified ¦ IEC60664-1,Input 2 / Output 2,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 1,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 3 / Output 2,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 2,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 2 / Input 3,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Input 1 / Input 3,
84893852 (Autelec Distribution)dielectric strength | Not specified ¦ IEC60255-27,Supply / Input 1,
84893852 (Autelec Distribution)dielectric strength | Not specified ¦ IEC60255-27,Supply / Input 2,
84893852 (Autelec Distribution)dielectric strength | Not specified ¦ IEC60255-27,Supply / Input 3,
84893852 (Autelec Distribution)dielectric strength | IEC60255-27,Supply / Output 1,
84893852 (Autelec Distribution)dielectric strength | IEC60255-27,Supply / Output 2,
84893852 (Autelec Distribution)dielectric strength | IEC60255-27,Output 1 / Output 2,
84893852 (Autelec Distribution)dielectric strength | IEC60255-27,Input 1 / Output 1,
84893852 (Autelec Distribution)dielectric strength | IEC60255-27,Input 1 / Output 2,
84893852 (Autelec Distribution)dielectric strength | IEC60255-27,Input 2 / Output 1,
84893852 (Autelec Distribution)dielectric strength | IEC60255-27,Input 2 / Output 2,
84893852 (Autelec Distribution)dielectric strength | IEC60255-27,Input 3 / Output 1,
84893852 (Autelec Distribution)dielectric strength | IEC60255-27,Input 3 / Output 2,
84893852 (Autelec Distribution)dielectric strength | IEC60255-27,Input 1 / Input 2,
84893852 (Autelec Distribution)dielectric strength | IEC60255-27,Input 2 / Input 3,
84893852 (Autelec Distribution)dielectric strength | IEC60255-27,Input 1 / Input 3,
84893852 (Autelec Distribution)insulation resistance | IEC60255-27,Supply / Input 1,
84893852 (Autelec Distribution)insulation resistance | IEC60255-27,Supply / Input 2,
84893852 (Autelec Distribution)insulation resistance | IEC60255-27,Supply / Input 3,
84893852 (Autelec Distribution)insulation resistance | IEC60255-27,Supply / Output 1,
84893852 (Autelec Distribution)insulation resistance | IEC60255-27,Supply / Output 2,
84893852 (Autelec Distribution)insulation resistance | IEC60255-27,Output 1 / Output 2,
84893852 (Autelec Distribution)insulation resistance | IEC60255-27,Input 1 / Output 1,
84893852 (Autelec Distribution)insulation resistance | IEC60255-27,Input 1 / Output 2,
84893852 (Autelec Distribution)insulation resistance | IEC60255-27,Input 2 / Output 1,
84893852 (Autelec Distribution)insulation resistance | IEC60255-27,Input 2 / Output 2,
84893852 (Autelec Distribution)insulation resistance | IEC60255-27,Input 3 / Output 1,
84893852 (Autelec Distribution)insulation resistance | IEC60255-27,Input 3 / Output 2,
84893852 (Autelec Distribution)insulation resistance | IEC60255-27,Input 1 / Input 2,
84893852 (Autelec Distribution)insulation resistance | IEC60255-27,Input 2 / Input 3,
84893852 (Autelec Distribution)insulation resistance | IEC60255-27,Input 1 / Input 3,
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)[Us] rated supply voltage | ~ 24…240
84893852 (Autelec Distribution)supply voltage limits | Not specified
84893852 (Autelec Distribution)polarity
84893852 (Autelec Distribution)supply frequency | Not specified
84893852 (Autelec Distribution)supply frequency | Not specified
84893852 (Autelec Distribution)power consumption | Not specified
84893852 (Autelec Distribution)immunity to microbreaks | Not specified
84893852 (Autelec Distribution)supply terminal | A1-A2
84893852 (Autelec Distribution)on-load factor
84893852 (Autelec Distribution)release of input voltage
84893852 (Autelec Distribution)
84893852 (Autelec Distribution) | - ¦ ,Over / undercurrent (windows mode),
84893852 (Autelec Distribution) | - ¦ ,Over current,
84893852 (Autelec Distribution) | · ¦ ,Under current,
84893852 (Autelec Distribution) | Fix 0.7A
84893852 (Autelec Distribution) | Not specified ¦ ,E1-M / B1-C,
84893852 (Autelec Distribution) | Not specified ¦ ,E2-M / B2-C,
84893852 (Autelec Distribution) | Not specified ¦ ,E3-M / B3-C,
84893852 (Autelec Distribution) | A1+ / A2-,
84893852 (Autelec Distribution) | Not specified ¦ ,Built in current transformer,
84893852 (Autelec Distribution) | Not specified ¦ ,E1-M / B1-C,
84893852 (Autelec Distribution) | Max 12A ¦ ,E2-M / B2-C,
84893852 (Autelec Distribution) | Not specified ¦ ,E3-M / B3-C,
84893852 (Autelec Distribution) | A1+ / A2-,
84893852 (Autelec Distribution) | Not specified ¦ ,Built in current transformer,
84893852 (Autelec Distribution) | Not specified ¦ ,E1-M / B1-C,
84893852 (Autelec Distribution) | Not specified ¦ ,E2-M / B2-C,
84893852 (Autelec Distribution) | Not specified ¦ ,E3-M / B3-C,
84893852 (Autelec Distribution) | A1+ / A2-,
84893852 (Autelec Distribution) | Not specified ¦ ,Built in current transformer,
84893852 (Autelec Distribution) | Not specified ¦ ,E1-M / B1-C,
84893852 (Autelec Distribution) | Not specified ¦ ,E2-M / B2-C,
84893852 (Autelec Distribution) | Not specified ¦ ,E3-M / B3-C,
84893852 (Autelec Distribution) | A1+ / A2-,
84893852 (Autelec Distribution) | Not specified ¦ ,Built in current transformer,
84893852 (Autelec Distribution) | Not specified
84893852 (Autelec Distribution) | Not specified
84893852 (Autelec Distribution) | Not specified
84893852 (Autelec Distribution) | Not specified
84893852 (Autelec Distribution) | Not specified
84893852 (Autelec Distribution) | Not specified
84893852 (Autelec Distribution) | Not specified
84893852 (Autelec Distribution) | Not specified
84893852 (Autelec Distribution) | Not specified
84893852 (Autelec Distribution) | Not specified
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)output type | 1 x C/O relay contacts
84893852 (Autelec Distribution)output terminal | 11-12-14
84893852 (Autelec Distribution)output logic | De-Energized on fault-free ¦ ,R1 (11-12-14),
84893852 (Autelec Distribution)output logic | R2 (21-22-24),
84893852 (Autelec Distribution)contacts material | Not specified
84893852 (Autelec Distribution)mechanical durability | Not specified ¦ IEC61810-1
84893852 (Autelec Distribution)electrical durability | Not specified ¦ IEC60947-4-1,AC-1,
84893852 (Autelec Distribution)electrical durability | IEC60947-4-1,DC-1,
84893852 (Autelec Distribution)electrical durability | IEC60947-5-1,AC-15,
84893852 (Autelec Distribution)electrical durability | IEC60947-5-1,DC-13,
84893852 (Autelec Distribution)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
84893852 (Autelec Distribution)[Ie] rated operational current | IEC61810-1,Rated switching current,
84893852 (Autelec Distribution)maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage,
84893852 (Autelec Distribution)maximum switching capacity | ~ 5 ¦ ,Maximum switching current,
84893852 (Autelec Distribution)maximum switching capacity | 1250 ¦ ,Maximum switching capacity,
84893852 (Autelec Distribution)minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching voltage,
84893852 (Autelec Distribution)minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching current,
84893852 (Autelec Distribution)minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching capacity,
84893852 (Autelec Distribution)maximum voltage drop | - ¦ IEC62314,Only for solid state output,
84893852 (Autelec Distribution)maximum leakage current | - ¦ IEC62314,Only for solid state output,
84893852 (Autelec Distribution)thermal current | IEC60947-5-1
84893852 (Autelec Distribution)short circuit protection | IEC60947-5-1,Relay Output by external fuse,
84893852 (Autelec Distribution)short circuit protection | IEC62314,Solid State Output by external fuse,
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)time delay type | - ¦ ,"OFF" delay,
84893852 (Autelec Distribution)time delay type | - ¦ ,"ON" delay,
84893852 (Autelec Distribution)time delay type | - ¦ ,Inhibition,
84893852 (Autelec Distribution)time delay range | - ¦ ,"OFF" delay,
84893852 (Autelec Distribution)time delay range | - ¦ ,"ON" delay,
84893852 (Autelec Distribution)time delay range | - ¦ ,Inhibition,
84893852 (Autelec Distribution)response time | Not specified ¦ ,on crossing the threshold,
84893852 (Autelec Distribution)response time
84893852 (Autelec Distribution)response time
84893852 (Autelec Distribution)response time
84893852 (Autelec Distribution)response time
84893852 (Autelec Distribution)power on delay | Not specified
84893852 (Autelec Distribution)reset time | Not specified ¦ ,through Un power reset,
84893852 (Autelec Distribution)reset time | through front panel reset,
84893852 (Autelec Distribution)reset time | through input control reset,
84893852 (Autelec Distribution)setting accuracy of time delay | Not specified
84893852 (Autelec Distribution)repeat accuracy of time delay | Not specified
84893852 (Autelec Distribution)time delay drift | Not specified
84893852 (Autelec Distribution)time delay drift | Not specified
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)status LED
84893852 (Autelec Distribution)local signalling | Power supply availability,
84893852 (Autelec Distribution)local signalling | Power supply not availability,
84893852 (Autelec Distribution)local signalling | Timing in-progress,
84893852 (Autelec Distribution)local signalling | Output is energized,
84893852 (Autelec Distribution)local signalling | Output is de-energized,
84893852 (Autelec Distribution)local signalling | Range Setting Changes,
84893852 (Autelec Distribution)local signalling
84893852 (Autelec Distribution)local signalling
84893852 (Autelec Distribution)local signalling
84893852 (Autelec Distribution)local signalling
84893852 (Autelec Distribution)local signalling
84893852 (Autelec Distribution)local signalling
84893852 (Autelec Distribution)local signalling
84893852 (Autelec Distribution)local signalling
84893852 (Autelec Distribution)local signalling
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)diagnostic button
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)
84893852 (Autelec Distribution)safety reliability data | MTTF,
84893852 (Autelec Distribution)safety reliability data | B10,
84893852 (Autelec Distribution) | MTTFd,
84893852 (Autelec Distribution) | B10d,
84893852 (Autelec Distribution)

## spec2
Param_ID | Value
Competitor Spec Reference | IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d, IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d, IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Over / undervoltage (windows mode), Over voltage, Undervoltage , E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, MTTFd, B10d, IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Over / undercurrent (windows mode), Over current, Under current, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, MTTFd, B10d,
Competitor Spec ReferenceIP degree of protection | IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel, IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel, IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel, IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel,
Competitor Spec ReferenceInput nominal voltage selection | Input nominal voltage selection,
Competitor Spec ReferenceMaximum length of probes cable | Maximum length of probes cable,
Competitor Spec ReferenceMaximum probe supplied current | Maximum probe supplied current,
Competitor Spec ReferenceMaximum probe supplied voltage | Maximum probe supplied voltage,
Competitor Spec ReferenceMinimum distance to adjacent devices | Horizontal, Vertical, Horizontal, Vertical, Horizontal, Vertical, Horizontal, Vertical,
Competitor Spec Reference[Ie] rated operational current | IEC61810-1,Rated switching current, IEC61810-1,Rated switching current, IEC61810-1,Rated switching current, IEC61810-1,Rated switching current,
Competitor Spec Reference[Ue] rated operational voltage | IEC61810-1,Rated switching voltage, IEC61810-1,Rated switching voltage, IEC61810-1,Rated switching voltage, IEC61810-1,Rated switching voltage,
Competitor Spec Reference[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3, IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3, IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3, IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
Competitor Spec Reference[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3, IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3, IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3, IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
Competitor Spec Reference[Us] rated supply voltage
Competitor Spec Referenceambient air temperature for operation | Operation, Operation, Operation, Operation,
Competitor Spec Referenceambient air temperature for storage | Storage, Storage, Storage, Storage,
Competitor Spec Referencebump resistance | IEC60068-2-29 IEC60068-2-29 IEC60068-2-29 IEC60068-2-29
Competitor Spec Referencecable stripping length | Cable stripping length, Cable stripping length, Cable stripping length, Cable stripping length,
Competitor Spec Referencecircuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2, Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2, Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2, Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
Competitor Spec Referenceconnections - terminals | IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal), IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal), IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal), IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal),
Competitor Spec Referencecontacts material
Competitor Spec Referencedepth | Depth, Depth, Depth, Depth,
Competitor Spec Referencediagnostic button
Competitor Spec Referencedielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3, IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3, IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3, IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
Competitor Spec Referencedirectives
Competitor Spec Referenceduty time
Competitor Spec Referenceelectrical durability | IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13, IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13, IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13, IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
Competitor Spec Referenceelectromagnetic compatibility | Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission, Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission, Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission, Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission,
Competitor Spec Referenceheight | Height, Height, Height, Height,
Competitor Spec Referencehysteresis | Phase cut, Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry, 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
Competitor Spec Referenceimmunity to microbreaks
Competitor Spec Referenceinput frequency | Rated frequency, Frequency operating range, Maximum cable capacitance,
Competitor Spec Referenceinput terminal | Input terminal, Input terminal,
Competitor Spec Referenceinsulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3, IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3, IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3, IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
Competitor Spec Referenceinternal input resistance | Internal input resistance, Internal input resistance,
Competitor Spec Referencelocal signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Phase Cut, Phase Sequence Swap, Undervoltage <U, Overvoltage >U, Phase Asymmetry, Voltage Regeneration, Extreme Undervoltage <U (Phase loss), Extreme Overvoltage >U, Extreme Phase Asymmetry, Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
Competitor Spec Referencemarking
Competitor Spec Referencemaximum leakage current | IEC62314,Only for solid state output, IEC62314,Only for solid state output, IEC62314,Only for solid state output, IEC62314,Only for solid state output,
Competitor Spec Referencemaximum measuring cycle | Maximum measuring cycles, Maximum measuring cycles,
Competitor Spec Referencemaximum switching capacity | Maximum switching voltage, Maximum switching current, Maximum switching capacity, Maximum switching voltage, Maximum switching current, Maximum switching capacity, Maximum switching voltage, Maximum switching current, Maximum switching capacity, Maximum switching voltage, Maximum switching current, Maximum switching capacity,
Competitor Spec Referencemaximum voltage drop | IEC62314,Only for solid state output, IEC62314,Only for solid state output, IEC62314,Only for solid state output, IEC62314,Only for solid state output,
Competitor Spec Referencemeasurement method | Measurement method, Measurement method,
Competitor Spec Referencemeasurement range | Phase lost , Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme Overvoltage, Extreme Asymmetry, 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
Competitor Spec Referencemechanical durability | IEC61810-1 IEC61810-1 IEC61810-1 IEC61810-1
Competitor Spec Referenceminimum switching capacity | IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity, IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity, IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity, IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity,
Competitor Spec Referencemonitoring functions | Phase lost , Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry, 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
Competitor Spec Referencemounting position | In relation to normal vertical mounting plane, In relation to normal vertical mounting plane, In relation to normal vertical mounting plane, In relation to normal vertical mounting plane,
Competitor Spec Referencemounting support | IEC/EN 60715,Without socket, IEC/EN 60715,With socket, IEC/EN 60715,Without socket, IEC/EN 60715,With socket, IEC/EN 60715,Without socket, IEC/EN 60715,With socket, IEC/EN 60715,Without socket, IEC/EN 60715,With socket,
Competitor Spec Referencenet weight
Competitor Spec Referenceon-load factor
Competitor Spec Referenceoutput logic | R1 (11-12-14), R2 (21-22-24), R1 (11-12-14), R2 (21-22-24), R1 (11-12-14), R2 (21-22-24), R1 (11-12-14), R2 (21-22-24),
Competitor Spec Referenceoutput terminal
Competitor Spec Referenceoutput type
Competitor Spec Referenceovervoltage category | IEC60664-1 IEC60664-1 IEC60664-1 IEC60664-1
Competitor Spec Referencepermissible input overload | permissible input overload,
Competitor Spec Referencepolarity
Competitor Spec Referencepollution degree | IEC60664-1 IEC60664-1 IEC60664-1 IEC60664-1
Competitor Spec Referencepower consumption
Competitor Spec Referencepower on delay
Competitor Spec Referenceproduct certifications
Competitor Spec Referencerelative humidity | IEC60068-2-30,Damp heat,XX IEC60068-2-30,Damp heat, IEC60068-2-30,Damp heat, IEC60068-2-30,Damp heat,
Competitor Spec Referencerelease of input voltage
Competitor Spec Referencerepeat accuracy of the switching threshold | Repeat accuracy (constant parameters), Repeat accuracy (constant parameters),
Competitor Spec Referencerepeat accuracy of time delay
Competitor Spec Referencereset time | through Un power reset, through front panel reset, through input control reset, through Un power reset, through front panel reset, through input control reset, through Un power reset, through front panel reset, through input control reset, through Un power reset, through front panel reset, through input control reset,
Competitor Spec Referenceresponse time | on crossing the threshold, on crossing the threshold, on crossing the threshold, on crossing the threshold,
Competitor Spec Referencesafety reliability data | MTTF, B10, MTTF, B10, MTTF, B10, MTTF, B10,
Competitor Spec Referenceseismic resistance | IEC60068-3-3 IEC60068-3-3 IEC60068-3-3 IEC60068-3-3
Competitor Spec Referencesetting accuracy of the switching threshold | Setting accuracy, Setting accuracy,
Competitor Spec Referencesetting accuracy of time delay
Competitor Spec Referenceshock resistance | IEC60068-2-27 IEC60068-2-27 IEC60068-2-27 IEC60068-2-27
Competitor Spec Referenceshort circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse, IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse, IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse, IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
Competitor Spec Referencestandards
Competitor Spec Referencestatus LED
Competitor Spec Referencesupply frequency
Competitor Spec Referencesupply terminal
Competitor Spec Referencesupply voltage limits
Competitor Spec Referenceswitching threshold drift | Measurement error with supply voltage variation, Measurement error with temperature variation, Measurement error with supply voltage variation, Measurement error with temperature variation,
Competitor Spec Referencethermal current | IEC60947-5-1 IEC60947-5-1 IEC60947-5-1 IEC60947-5-1
Competitor Spec Referencetightening torque | IEC60947-1,Tightening torque, IEC60947-1,Tightening torque, IEC60947-1,Tightening torque, IEC60947-1,Tightening torque,
Competitor Spec Referencetime delay drift
Competitor Spec Referencetime delay range | "OFF" delay, "ON" delay, Inhibition, "OFF" delay, "ON" delay, Inhibition, "OFF" delay, "ON" delay, Inhibition, "OFF" delay, "ON" delay, Inhibition,
Competitor Spec Referencetime delay type | "OFF" delay, "ON" delay, Inhibition, "OFF" delay, "ON" delay, Inhibition, "OFF" delay, "ON" delay, Inhibition, "OFF" delay, "ON" delay, Inhibition,
Competitor Spec Referencetripping threshold | Phase cut, Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry, 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
Competitor Spec Referencevibration resistance | IEC60068-2-6 IEC60068-2-6 IEC60068-2-6 IEC60068-2-6
Competitor Spec Referencewidth | Width, Width, Width, Width,
1SVR 630 794 R3300 | 3K3 ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, MTTFd, B10d,
1SVR 630 794 R3300IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP50 ¦ IEC60529,Housing, Not specified ¦ IEC60529,Front Panel,
1SVR 630 794 R3300Input nominal voltage selection | Fixed @ ~ 3 x 255…3 x 550 ¦ ,Input nominal voltage selection,
1SVR 630 794 R3300Minimum distance to adjacent devices | None ¦ ,Horizontal, None ¦ ,Vertical,
1SVR 630 794 R3300[Ie] rated operational current | IEC61810-1,Rated switching current,
1SVR 630 794 R3300[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
1SVR 630 794 R3300[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
1SVR 630 794 R3300[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
1SVR 630 794 R3300[Us] rated supply voltage | ~ 3 x 300…3 x 500
1SVR 630 794 R3300ambient air temperature for operation | -25…+60 ¦ ,Operation,
1SVR 630 794 R3300ambient air temperature for storage | -40…+85 ¦ ,Storage,
1SVR 630 794 R3300bump resistance | IEC60068-2-29
1SVR 630 794 R3300cable stripping length | 7 ¦ ,Cable stripping length,
1SVR 630 794 R3300circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
1SVR 630 794 R3300connections - terminals | 2 conductor:0.75…2.5 (AWG18…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 2 conductor:0.5…4 (AWG20…AWG12) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
1SVR 630 794 R3300contacts material | AgNi alloy, Cadmium free
1SVR 630 794 R3300depth | Depth,
1SVR 630 794 R3300diagnostic button
1SVR 630 794 R3300dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
1SVR 630 794 R3300directives | 2006/95/EG 2004/108/EG 2002/95/EC
1SVR 630 794 R3300duty time | 100
1SVR 630 794 R3300electrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
1SVR 630 794 R3300electromagnetic compatibility | IEC61000-6-1, IEC61000-6-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV / 2kHz) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (2kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Not specified ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Class 3 ¦ IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), - ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Not specified ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), - ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Not specified ¦ Germanisher Lloyd,Conducted emission,
1SVR 630 794 R3300height | Height,
1SVR 630 794 R3300hysteresis | - ¦ ,Phase cut, - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Fixed 5% ¦ ,Over voltage, Fixed 5% ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
1SVR 630 794 R3300immunity to microbreaks | -
1SVR 630 794 R3300input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
1SVR 630 794 R3300input terminal | L1-L2-L3 ¦ ,Input terminal,
1SVR 630 794 R3300insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
1SVR 630 794 R3300internal input resistance | Not specified ¦ ,Internal input resistance,
1SVR 630 794 R3300local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Phase Cut, Phase Sequence Swap, Undervoltage <U, Overvoltage >U, Phase Asymmetry, Voltage Regeneration, Extreme Undervoltage <U (Phase loss), Extreme Overvoltage >U, Extreme Phase Asymmetry,
1SVR 630 794 R3300marking | cULus, CSA, GL, C-Tick, GOST, CCC, CB, CE
1SVR 630 794 R3300maximum leakage current | IEC62314,Only for solid state output,
1SVR 630 794 R3300maximum measuring cycle | 100 ¦ ,Maximum measuring cycles,
1SVR 630 794 R3300maximum switching capacity | ~/-- 250 ¦ ,Maximum switching voltage, - ¦ ,Maximum switching current, Maximum switching capacity,
1SVR 630 794 R3300maximum voltage drop | IEC62314,Only for solid state output,
1SVR 630 794 R3300measurement method | True RMS ¦ ,Measurement method,
1SVR 630 794 R3300measurement range | Not specified ¦ ,Phase lost , Not specified ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), ~ 3 x 420…3 x 500 ¦ ,Over voltage, ~ 3 x 300…3 x 380 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme Overvoltage, Extreme Asymmetry,
1SVR 630 794 R3300mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
1SVR 630 794 R3300minimum switching capacity | 24 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 240 ¦ IEC60947-5-4,Minimum switching capacity,
1SVR 630 794 R3300monitoring functions | · ¦ ,Phase lost , can be switched off ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), · ¦ ,Over voltage, · ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry,
1SVR 630 794 R3300mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
1SVR 630 794 R3300mounting support | DIN rail snap-on mounting without any tool ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
1SVR 630 794 R3300net weight | 130
1SVR 630 794 R3300on-load factor
1SVR 630 794 R3300output logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
1SVR 630 794 R3300output terminal
1SVR 630 794 R3300output type | 2 x C/O relay contacts
1SVR 630 794 R3300overvoltage category | IEC60664-1
1SVR 630 794 R3300permissible input overload | Not specified ¦ ,permissible input overload,
1SVR 630 794 R3300polarity
1SVR 630 794 R3300pollution degree | IEC60664-1
1SVR 630 794 R3300power consumption | 25mA / 18VA (400VAC)
1SVR 630 794 R3300power on delay | Fixed 200
1SVR 630 794 R3300product certifications | cULus, CSA, GL, C-Tick, GOST, CCC, CB
1SVR 630 794 R3300relative humidity | +55°C, 6 cycles ¦ IEC60068-2-30,Damp heat,XX
1SVR 630 794 R3300release of input voltage
1SVR 630 794 R3300repeat accuracy of the switching threshold | < +/- 0.2% ¦ ,Repeat accuracy (constant parameters),
1SVR 630 794 R3300repeat accuracy of time delay | < +/- 0.2%
1SVR 630 794 R3300reset time | - ¦ ,through Un power reset, through front panel reset, through input control reset,
1SVR 630 794 R3300response time | - ¦ ,on crossing the threshold,
1SVR 630 794 R3300safety reliability data | MTTF, B10,
1SVR 630 794 R3300seismic resistance | IEC60068-3-3
1SVR 630 794 R3300setting accuracy of the switching threshold | Not specified ¦ ,Setting accuracy,
1SVR 630 794 R3300setting accuracy of time delay | -
1SVR 630 794 R3300shock resistance | Class 2 ¦ IEC60068-2-27
1SVR 630 794 R3300short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
1SVR 630 794 R3300standards | EN60255-6, IEC60255-6, EN50178
1SVR 630 794 R3300status LED
1SVR 630 794 R3300supply frequency | 50 / 60 45…66
1SVR 630 794 R3300supply terminal | L1-L2-L3
1SVR 630 794 R3300supply voltage limits | ~ 3 x 255…3 x 550
1SVR 630 794 R3300switching threshold drift | < 0.5% ¦ ,Measurement error with supply voltage variation, =< 0.06% / oC ¦ ,Measurement error with temperature variation,
1SVR 630 794 R3300thermal current | IEC60947-5-1
1SVR 630 794 R3300tightening torque | 0.6…0.8 ¦ IEC60947-1,Tightening torque,
1SVR 630 794 R3300time delay drift | < 0.5% =< 0.06% / oC
1SVR 630 794 R3300time delay range | Adjustable 0.1…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
1SVR 630 794 R3300time delay type | · ¦ ,"OFF" delay, · ¦ ,"ON" delay, - ¦ ,Inhibition,
1SVR 630 794 R3300tripping threshold | - ¦ ,Phase cut, - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Adjustable within measurement range ¦ ,Over voltage, Adjustable within measurement range ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
1SVR 630 794 R3300vibration resistance | Class 2 ¦ IEC60068-2-6
1SVR 630 794 R3300width | 22.5 x 78 x 100 ¦ ,Width,
8487020x | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Not specified ¦ ,Supply,Rated Not specified ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d,
8487020xIP degree of protection | Not specified ¦ IEC60529,Terminal Block, Not specified ¦ IEC60529,Housing, IEC60529,Front Panel,
8487020xMaximum length of probes cable | Not specified ¦ ,Maximum length of probes cable,
8487020xMaximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
8487020xMaximum probe supplied voltage | 24 ¦ ,Maximum probe supplied voltage,
8487020xMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
8487020x[Ie] rated operational current | IEC61810-1,Rated switching current,
8487020x[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
8487020x[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, Not specified ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
8487020x[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
8487020x[Us] rated supply voltage | 84870201: ~ 24 84870203: ~120 84870204: ~230
8487020xambient air temperature for operation | -20…+50 ¦ ,Operation,
8487020xambient air temperature for storage | -40…+70 ¦ ,Storage,
8487020xbump resistance | IEC60068-2-29
8487020xcable stripping length | Not specified ¦ ,Cable stripping length,
8487020xcircuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Not specified ¦ ,Output 2,
8487020xconnections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal), Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
8487020xcontacts material | Cadmium free
8487020xdepth | Depth,
8487020xdiagnostic button
8487020xdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
8487020xdirectives | Not specified Not specified Not specified
8487020xduty time | Not specified
8487020xelectrical durability | Not specified ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
8487020xelectromagnetic compatibility | Not specified ¦ ,Generic immunity standard, Not specified ¦ IEC61000-4-2,Electrostatic discharge, Not specified ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Not specified ¦ IEC61000-4-4,Fast transient / burst, Not specified ¦ IEC61000-4-5,Surge, Not specified ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Not specified ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not specified ¦ IEC61000-4-13,Low frequency harmonics, Not specified ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Not specified ¦ ,Generic emission standard, Not specified ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Not specified ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Not specified ¦ Germanisher Lloyd,Radiated emission from enclosure port, Not specified ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Not specified ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Not specified ¦ Germanisher Lloyd,Conducted emission,
8487020xheight | Height,
8487020xhysteresis | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
8487020ximmunity to microbreaks | Not specified
8487020xinput frequency | 10 ¦ ,Maximum cable capacitance,
8487020xinput terminal | Input terminal,
8487020xinsulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
8487020xinternal input resistance | Internal input resistance,
8487020xlocal signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
8487020xmarking | cULus, CE, CSA
8487020xmaximum leakage current | - ¦ IEC62314,Only for solid state output,
8487020xmaximum measuring cycle | Maximum measuring cycles,
8487020xmaximum switching capacity | Not specified ¦ ,Maximum switching voltage, Not specified ¦ ,Maximum switching current, Not specified ¦ ,Maximum switching capacity,
8487020xmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
8487020xmeasurement method | Liquid level probe ¦ ,Measurement method,
8487020xmeasurement range | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
8487020xmechanical durability | Not specified ¦ IEC61810-1
8487020xminimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching voltage, Not specified ¦ IEC60947-5-4,Minimum switching current, Not specified ¦ IEC60947-5-4,Minimum switching capacity,
8487020xmonitoring functions | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
8487020xmounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
8487020xmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
8487020xnet weight | 150
8487020xon-load factor
8487020xoutput logic | Not specified ¦ ,R1 (11-12-14), R2 (21-22-24),
8487020xoutput terminal | 11-12-14
8487020xoutput type | 1 x C/O relay contacts
8487020xovervoltage category | Not specified ¦ IEC60664-1
8487020xpolarity
8487020xpollution degree | Not specified ¦ IEC60664-1
8487020xpower consumption | 3VA
8487020xpower on delay | Not specified
8487020xproduct certifications | cULus, CE, CSA
8487020xrelative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
8487020xrelease of input voltage
8487020xrepeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
8487020xrepeat accuracy of time delay | Not specified
8487020xreset time | Not specified ¦ ,through Un power reset, through front panel reset, through input control reset,
8487020xresponse time | 300 high level; 500 low level ¦ ,on crossing the threshold,
8487020xsafety reliability data | MTTF, B10,
8487020xseismic resistance | IEC60068-3-3
8487020xsetting accuracy of the switching threshold | +/- 30% at max sensitivity ¦ ,Setting accuracy,
8487020xsetting accuracy of time delay | Not specified
8487020xshock resistance | Not specified ¦ IEC60068-2-27
8487020xshort circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
8487020xstandards | Not specified
8487020xstatus LED
8487020xsupply frequency | 50 / 60 Not specified
8487020xsupply terminal | A1-A2
8487020xsupply voltage limits | Not specified
8487020xswitching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation, Not specified ¦ ,Measurement error with temperature variation,
8487020xthermal current | IEC60947-5-1
8487020xtightening torque | Not specified ¦ IEC60947-1,Tightening torque,
8487020xtime delay drift | Not specified Not specified
8487020xtime delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
8487020xtime delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
8487020xtripping threshold | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
8487020xvibration resistance | Not specified ¦ IEC60068-2-6
8487020xwidth | 22.5 x 78.5 x 100 ¦ ,Width,
8487021x | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Not specified ¦ ,Supply,Rated Not specified ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d,
8487021xIP degree of protection | Not specified ¦ IEC60529,Terminal Block, Not specified ¦ IEC60529,Housing, IEC60529,Front Panel,
8487021xMaximum length of probes cable | Not specified ¦ ,Maximum length of probes cable,
8487021xMaximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
8487021xMaximum probe supplied voltage | 24 ¦ ,Maximum probe supplied voltage,
8487021xMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
8487021x[Ie] rated operational current | IEC61810-1,Rated switching current,
8487021x[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
8487021x[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, Not specified ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
8487021x[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
8487021x[Us] rated supply voltage | 84870211: ~ 24 84870213: ~120 84870214: ~230
8487021xambient air temperature for operation | -20…+50 ¦ ,Operation,
8487021xambient air temperature for storage | -40…+70 ¦ ,Storage,
8487021xbump resistance | IEC60068-2-29
8487021xcable stripping length | Not specified ¦ ,Cable stripping length,
8487021xcircuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Not specified ¦ ,Output 2,
8487021xconnections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal), Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
8487021xcontacts material | Cadmium free
8487021xdepth | Depth,
8487021xdiagnostic button
8487021xdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
8487021xdirectives | Not specified Not specified Not specified
8487021xduty time | Not specified
8487021xelectrical durability | Not specified ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
8487021xelectromagnetic compatibility | Not specified ¦ ,Generic immunity standard, Not specified ¦ IEC61000-4-2,Electrostatic discharge, Not specified ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Not specified ¦ IEC61000-4-4,Fast transient / burst, Not specified ¦ IEC61000-4-5,Surge, Not specified ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Not specified ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not specified ¦ IEC61000-4-13,Low frequency harmonics, Not specified ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Not specified ¦ ,Generic emission standard, Not specified ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Not specified ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Not specified ¦ Germanisher Lloyd,Radiated emission from enclosure port, Not specified ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Not specified ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Not specified ¦ Germanisher Lloyd,Conducted emission,
8487021xheight | Height,
8487021xhysteresis | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
8487021ximmunity to microbreaks | Not specified
8487021xinput frequency | 10 ¦ ,Maximum cable capacitance,
8487021xinput terminal | Input terminal,
8487021xinsulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
8487021xinternal input resistance | Internal input resistance,
8487021xlocal signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
8487021xmarking | cULus, CE, CSA
8487021xmaximum leakage current | - ¦ IEC62314,Only for solid state output,
8487021xmaximum measuring cycle | Maximum measuring cycles,
8487021xmaximum switching capacity | Not specified ¦ ,Maximum switching voltage, Not specified ¦ ,Maximum switching current, Not specified ¦ ,Maximum switching capacity,
8487021xmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
8487021xmeasurement method | Liquid level probe ¦ ,Measurement method,
8487021xmeasurement range | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
8487021xmechanical durability | Not specified ¦ IEC61810-1
8487021xminimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching voltage, Not specified ¦ IEC60947-5-4,Minimum switching current, Not specified ¦ IEC60947-5-4,Minimum switching capacity,
8487021xmonitoring functions | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
8487021xmounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
8487021xmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
8487021xnet weight | 150
8487021xon-load factor
8487021xoutput logic | Not specified ¦ ,R1 (11-12-14), R2 (21-22-24),
8487021xoutput terminal | 11-12-14
8487021xoutput type | 1 x C/O relay contacts
8487021xovervoltage category | Not specified ¦ IEC60664-1
8487021xpolarity
8487021xpollution degree | Not specified ¦ IEC60664-1
8487021xpower consumption | 3VA
8487021xpower on delay | Not specified
8487021xproduct certifications | cULus, CE, CSA
8487021xrelative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
8487021xrelease of input voltage
8487021xrepeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
8487021xrepeat accuracy of time delay | Not specified
8487021xreset time | Not specified ¦ ,through Un power reset, through front panel reset, through input control reset,
8487021xresponse time | 300 high level; 500 low level ¦ ,on crossing the threshold,
8487021xsafety reliability data | MTTF, B10,
8487021xseismic resistance | IEC60068-3-3
8487021xsetting accuracy of the switching threshold | +/- 30% at max sensitivity ¦ ,Setting accuracy,
8487021xsetting accuracy of time delay | Not specified
8487021xshock resistance | Not specified ¦ IEC60068-2-27
8487021xshort circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
8487021xstandards | Not specified
8487021xstatus LED
8487021xsupply frequency | 50 / 60 Not specified
8487021xsupply terminal | A1-A2
8487021xsupply voltage limits | Not specified
8487021xswitching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation, Not specified ¦ ,Measurement error with temperature variation,
8487021xthermal current | IEC60947-5-1
8487021xtightening torque | Not specified ¦ IEC60947-1,Tightening torque,
8487021xtime delay drift | Not specified Not specified
8487021xtime delay range | Adjustable 0.1…5 ¦ ,"OFF" delay, Adjustable 0.1…5 ¦ ,"ON" delay, - ¦ ,Inhibition,
8487021xtime delay type | · ¦ ,"OFF" delay, · ¦ ,"ON" delay, - ¦ ,Inhibition,
8487021xtripping threshold | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
8487021xvibration resistance | Not specified ¦ IEC60068-2-6
8487021xwidth | 22.5 x 78.5 x 100 ¦ ,Width,
84873004 | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d,
84873004IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, Not specified ¦ IEC60529,Front Panel,
84873004Input nominal voltage selection | Fixed @ ~ 3 x 230…3 x 440 ¦ ,Input nominal voltage selection,
84873004Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
84873004[Ie] rated operational current | IEC61810-1,Rated switching current,
84873004[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
84873004[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
84873004[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
84873004[Us] rated supply voltage | ~ 3 x 230…3 x 440
84873004ambient air temperature for operation | Not specified ¦ ,Operation,
84873004ambient air temperature for storage | -30…+70 ¦ ,Storage,
84873004bump resistance | IEC60068-2-29
84873004cable stripping length | Cable stripping length,
84873004circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
84873004connections - terminals | 1 conductor: 4 (AWG11) 2 conductor:2.5 (AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 2 conductor: 1.5 (AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
84873004contacts material | Cadmium free
84873004depth | Depth,
84873004diagnostic button
84873004dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
84873004directives | Not specified Not specified Not specified
84873004duty time
84873004electrical durability | Not specified ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
84873004electromagnetic compatibility | Not specified ¦ ,Generic immunity standard, Not specified ¦ IEC61000-4-2,Electrostatic discharge, Not specified ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Not specified ¦ IEC61000-4-4,Fast transient / burst, Not specified ¦ IEC61000-4-5,Surge, Not specified ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Not specified ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not specified ¦ IEC61000-4-13,Low frequency harmonics, Not specified ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Not specified ¦ ,Generic emission standard, Not specified ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Not specified ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Not specified ¦ Germanisher Lloyd,Radiated emission from enclosure port, Not specified ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Not specified ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Not specified ¦ Germanisher Lloyd,Conducted emission,
84873004height | Height,
84873004hysteresis | Not specified ¦ ,Phase cut, Not specified ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
84873004immunity to microbreaks | Not specified
84873004input frequency | 50 / 60 ¦ ,Rated frequency, 49…61 ¦ ,Frequency operating range,
84873004input terminal | L1-L2-L3 ¦ ,Input terminal,
84873004insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
84873004internal input resistance | Not specified ¦ ,Internal input resistance,
84873004local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Phase Cut, Phase Sequence Swap, Undervoltage <U, Overvoltage >U, Phase Asymmetry, Voltage Regeneration, Extreme Undervoltage <U (Phase loss), Extreme Overvoltage >U, Extreme Phase Asymmetry,
84873004marking | cULus, CE
84873004maximum leakage current | IEC62314,Only for solid state output,
84873004maximum measuring cycle | Not specified ¦ ,Maximum measuring cycles,
84873004maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 8 ¦ ,Maximum switching current, 2000 ¦ ,Maximum switching capacity,
84873004maximum voltage drop | IEC62314,Only for solid state output,
84873004measurement method | Not specified ¦ ,Measurement method,
84873004measurement range | Not specified ¦ ,Phase lost , Not specified ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme Overvoltage, Extreme Asymmetry,
84873004mechanical durability | 20 x 106 switching cycles ¦ IEC61810-1
84873004minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
84873004monitoring functions | · ¦ ,Phase lost , · ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry,
84873004mounting position | In relation to normal vertical mounting plane,
84873004mounting support | IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
84873004net weight | 110
84873004on-load factor
84873004output logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
84873004output terminal | 11-12-14, 21-22-24
84873004output type | 2 x C/O relay contacts
84873004overvoltage category | IEC60664-1
84873004permissible input overload | Not specified ¦ ,permissible input overload,
84873004polarity
84873004pollution degree | IEC60664-1
84873004power consumption | 25
84873004power on delay | 0
84873004product certifications | cULus, CE
84873004relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,XX
84873004release of input voltage
84873004repeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
84873004repeat accuracy of time delay | -
84873004reset time | - ¦ ,through Un power reset, through front panel reset, through input control reset,
84873004response time | 0
84873004safety reliability data | MTTF, B10,
84873004seismic resistance | IEC60068-3-3
84873004setting accuracy of the switching threshold | - ¦ ,Setting accuracy,
84873004setting accuracy of time delay | -
84873004shock resistance | Not specified ¦ IEC60068-2-27
84873004short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
84873004standards | Not specified
84873004status LED
84873004supply frequency | 50 / 60 49…61
84873004supply terminal | Not specified
84873004supply voltage limits | Not specified
84873004switching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation, Not specified ¦ ,Measurement error with temperature variation,
84873004thermal current | IEC60947-5-1
84873004tightening torque | Max 1 ¦ IEC60947-1,Tightening torque,
84873004time delay drift | - -
84873004time delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
84873004time delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
84873004tripping threshold | Not specified ¦ ,Phase cut, Not specified ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
84873004vibration resistance | Not specified ¦ IEC60068-2-6
84873004width | 22.5 x 78.5 x 100 ¦ ,Width,
84873021 | Same as RM17TG20 ¦ IEC60721-3-3,Climatic category, Same as RM17TG20 ¦ Germanisher Lloyd,Environmental category, Same as RM17TG20 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM17TG20 ¦ ,Supply,Rated Same as RM17TG20 ¦ ,Input 1,Voltage Same as RM17TG20 ¦ ,Input 2,Spec Same as RM17TG20 ¦ ,Input 3, Same as RM17TG20 ¦ ,Output 1, Same as RM17TG20 ¦ ,Output 2, Same as RM17TG20 ¦ ,Measurement mode, Same as RM17TG20 Same as RM17TG20 Same as RM17TG20 Same as RM17TG20 Same as RM17TG20 ¦ ,MTTFd, Same as RM17TG20 ¦ ,B10d, Drawing / Diagram
84873021IP degree of protection | Same as RM17TG20 ¦ IEC60529,Terminal Block, Same as RM17TG20 ¦ IEC60529,Housing, Same as RM17TG20 ¦ IEC60529,Front Panel,
84873021Input nominal voltage selection | Same as RM17TG20 ¦ ,Input nominal voltage selection,
84873021Minimum distance to adjacent devices | Same as RM17TG20 ¦ ,Horizontal, Same as RM17TG20 ¦ ,Vertical,
84873021[Ie] rated operational current | Same as RM17TG20 ¦ IEC61810-1,Rated switching current,
84873021[Ue] rated operational voltage | Same as RM17TG20 ¦ IEC61810-1,Rated switching voltage,
84873021[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply, Same as RM17TG20 ¦ IEC60664-1,Input 1, Same as RM17TG20 ¦ IEC60664-1,Input 2, Same as RM17TG20 ¦ IEC60664-1,Input 3, Same as RM17TG20 ¦ IEC60664-1,Output 1, Same as RM17TG20 ¦ IEC60664-1,Output 2, Same as RM17TG20 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TG20 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TG20 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TG20 ¦ IEC60664-1,Supply / Output 1, Same as RM17TG20 ¦ IEC60664-1,Supply / Output 2, Same as RM17TG20 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 3,
84873021[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply, Same as RM17TG20 ¦ IEC60664-1,Input 1, Same as RM17TG20 ¦ IEC60664-1,Input 2, Same as RM17TG20 ¦ IEC60664-1,Input 3, Same as RM17TG20 ¦ IEC60664-1,Output 1, Same as RM17TG20 ¦ IEC60664-1,Output 2, Same as RM17TG20 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TG20 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TG20 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TG20 ¦ IEC60664-1,Supply / Output 1, Same as RM17TG20 ¦ IEC60664-1,Supply / Output 2, Same as RM17TG20 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 3,
84873021[Us] rated supply voltage | Same as RM17TG20
84873021ambient air temperature for operation | Same as RM17TG20 ¦ ,Operation,
84873021ambient air temperature for storage | Same as RM17TG20 ¦ ,Storage,
84873021bump resistance | Same as RM17TG20 ¦ IEC60068-2-29
84873021cable stripping length | Same as RM17TG20 ¦ ,Cable stripping length,
84873021circuit group | Same as RM17TG20 ¦ ,Supply,Terminal Same as RM17TG20 ¦ ,Input 1, Same as RM17TG20 ¦ ,Input 2, Same as RM17TG20 ¦ ,Input 3, Same as RM17TG20 ¦ ,Output 1, Same as RM17TG20 ¦ ,Output 2,
84873021connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17TG20 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17TG20 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17TG20 ¦ IEC60947-1,Flexible cable (spring terminal),
84873021contacts material | Same as RM17TG20
84873021depth | Same as RM17TG20 ¦ ,Depth,
84873021diagnostic button | Same as RM17TG20
84873021dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 1, Same as RM17TG20 ¦ IEC60255-27,Supply / Input 2, Same as RM17TG20 ¦ IEC60255-27,Supply / Input 3, Same as RM17TG20 ¦ IEC60255-27,Supply / Output 1, Same as RM17TG20 ¦ IEC60255-27,Supply / Output 2, Same as RM17TG20 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 3,
84873021directives | Same as RM17TG20 Same as RM17TG20 Same as RM17TG20
84873021duty time | Same as RM17TG20
84873021electrical durability | Same as RM17TG20 ¦ IEC60947-4-1,AC-1, Same as RM17TG20 ¦ IEC60947-4-1,DC-1, Same as RM17TG20 ¦ IEC60947-5-1,AC-15, Same as RM17TG20 ¦ IEC60947-5-1,DC-13,
84873021electromagnetic compatibility | Same as RM17TG20 ¦ ,Generic immunity standard, Same as RM17TG20 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17TG20 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17TG20 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17TG20 ¦ IEC61000-4-5,Surge, Same as RM17TG20 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17TG20 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17TG20 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17TG20 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17TG20 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17TG20 ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17TG20 ¦ ,Generic emission standard, Same as RM17TG20 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17TG20 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17TG20 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17TG20 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17TG20 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17TG20 ¦ Germanisher Lloyd,Conducted emission,
84873021height | Same as RM17TG20 ¦ ,Height,
84873021hysteresis | Same as RM17TG20 ¦ ,Phase cut, Same as RM17TG20 ¦ ,Phase sequence, Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG20 ¦ ,Over voltage, Same as RM17TG20 ¦ ,Undervoltage , Same as RM17TG20 ¦ ,Phase asymmetry, Same as RM17TG20 ¦ ,Disconnection of neutral, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TG20 ¦ ,Extreme Overvoltage, Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873021immunity to microbreaks | Same as RM17TG20
84873021input frequency | Same as RM17TG20 ¦ ,Rated frequency, Same as RM17TG20 ¦ ,Frequency operating range,
84873021input terminal | Same as RM17TG20 ¦ ,Input terminal,
84873021insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 1, Same as RM17TG20 ¦ IEC60255-27,Supply / Input 2, Same as RM17TG20 ¦ IEC60255-27,Supply / Input 3, Same as RM17TG20 ¦ IEC60255-27,Supply / Output 1, Same as RM17TG20 ¦ IEC60255-27,Supply / Output 2, Same as RM17TG20 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 3,
84873021internal input resistance | Same as RM17TG20 ¦ ,Internal input resistance,
84873021local signalling | Same as RM17TG20 ¦ ,Power supply availability, Same as RM17TG20 ¦ ,Power supply not availability, Same as RM17TG20 ¦ ,Timing in-progress, Same as RM17TG20 ¦ ,Output is energized, Same as RM17TG20 ¦ ,Output is de-energized, Same as RM17TG20 ¦ ,Range Setting Changes, Same as RM17TG20 ¦ ,Phase Cut, Same as RM17TG20 ¦ ,Phase Sequence Swap, Same as RM17TG20 ¦ ,Undervoltage <U, Same as RM17TG20 ¦ ,Overvoltage >U, Same as RM17TG20 ¦ ,Phase Asymmetry, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17TG20 ¦ ,Extreme Overvoltage >U, Same as RM17TG20 ¦ ,Extreme Phase Asymmetry,
84873021marking | UL, CSA, GL, CCC, CE, China ROHS
84873021maximum leakage current | Same as RM17TG20 ¦ IEC62314,Only for solid state output,
84873021maximum measuring cycle | Same as RM17TG20 ¦ ,Maximum measuring cycles,
84873021maximum switching capacity | Same as RM17TG20 ¦ ,Maximum switching voltage, Same as RM17TG20 ¦ ,Maximum switching current, Same as RM17TG20 ¦ ,Maximum switching capacity,
84873021maximum voltage drop | Same as RM17TG20 ¦ IEC62314,Only for solid state output,
84873021measurement method | Same as RM17TG20 ¦ ,Measurement method,
84873021measurement range | Same as RM17TG20 ¦ ,Phase lost , Same as RM17TG20 ¦ ,Phase sequence, Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG20 ¦ ,Over voltage, Same as RM17TG20 ¦ ,Undervoltage , Same as RM17TG20 ¦ ,Phase asymmetry, Same as RM17TG20 ¦ ,Disconnection of neutral, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme undervoltage, Same as RM17TG20 ¦ ,Extreme Overvoltage, Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873021mechanical durability | Same as RM17TG20 ¦ IEC61810-1
84873021minimum switching capacity | Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching current, Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching capacity,
84873021monitoring functions | Same as RM17TG20 ¦ ,Phase lost , Same as RM17TG20 ¦ ,Phase sequence, Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG20 ¦ ,Over voltage, Same as RM17TG20 ¦ ,Undervoltage , Same as RM17TG20 ¦ ,Phase asymmetry, Same as RM17TG20 ¦ ,Disconnection of neutral, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme undervoltage, Same as RM17TG20 ¦ ,Extreme overvoltage, Same as RM17TG20 ¦ ,Extreme asymmetry,
84873021mounting position | Same as RM17TG20 ¦ ,In relation to normal vertical mounting plane,
84873021mounting support | Same as RM17TG20 ¦ IEC/EN 60715,Without socket, Same as RM17TG20 ¦ IEC/EN 60715,With socket,
84873021net weight | Same as RM17TG20
84873021on-load factor | Same as RM17TG20
84873021output logic | Same as RM17TG20 ¦ ,R1 (11-12-14), Same as RM17TG20 ¦ ,R2 (21-22-24),
84873021output terminal | Same as RM17TG20
84873021output type | Same as RM17TG20
84873021overvoltage category | Same as RM17TG20 ¦ IEC60664-1
84873021permissible input overload | Same as RM17TG20 ¦ ,permissible input overload,
84873021polarity | Same as RM17TG20
84873021pollution degree | Same as RM17TG20 ¦ IEC60664-1
84873021power consumption | Same as RM17TG20
84873021power on delay | Same as RM17TG20
84873021product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873021relative humidity | Same as RM17TG20 ¦ IEC60068-2-30,Damp heat,XX
84873021release of input voltage | Same as RM17TG20
84873021repeat accuracy of the switching threshold | Same as RM17TG20 ¦ ,Repeat accuracy (constant parameters),
84873021repeat accuracy of time delay | Same as RM17TG20
84873021reset time | Same as RM17TG20 ¦ ,through Un power reset, Same as RM17TG20 ¦ ,through front panel reset, Same as RM17TG20 ¦ ,through input control reset,
84873021response time | Same as RM17TG20 ¦ ,on crossing the threshold, Same as RM17TG20 Same as RM17TG20 Same as RM17TG20 Same as RM17TG20
84873021safety reliability data | Same as RM17TG20 ¦ ,MTTF, Same as RM17TG20 ¦ ,B10,
84873021seismic resistance | Same as RM17TG20 ¦ IEC60068-3-3
84873021setting accuracy of the switching threshold | Same as RM17TG20 ¦ ,Setting accuracy,
84873021setting accuracy of time delay | Same as RM17TG20
84873021shock resistance | Same as RM17TG20 ¦ IEC60068-2-27
84873021short circuit protection | Same as RM17TG20 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17TG20 ¦ IEC62314,Solid State Output by external fuse,
84873021standards | Same as RM17TG20
84873021status LED | Same as RM17TG20
84873021supply frequency | Same as RM17TG20 Same as RM17TG20
84873021supply terminal | Same as RM17TG20
84873021supply voltage limits | Same as RM17TG20
84873021switching threshold drift | Same as RM17TG20 ¦ ,Measurement error with supply voltage variation, Same as RM17TG20 ¦ ,Measurement error with temperature variation,
84873021thermal current | Same as RM17TG20 ¦ IEC60947-5-1
84873021tightening torque | Same as RM17TG20 ¦ IEC60947-1,Tightening torque,
84873021time delay drift | Same as RM17TG20 Same as RM17TG20
84873021time delay range | Same as RM17TG20 ¦ ,"OFF" delay, Same as RM17TG20 ¦ ,"ON" delay, Same as RM17TG20 ¦ ,Inhibition,
84873021time delay type | Same as RM17TG20 ¦ ,"OFF" delay, Same as RM17TG20 ¦ ,"ON" delay, Same as RM17TG20 ¦ ,Inhibition,
84873021tripping threshold | Same as RM17TG20 ¦ ,Phase cut, Same as RM17TG20 ¦ ,Phase sequence, Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG20 ¦ ,Over voltage, Same as RM17TG20 ¦ ,Undervoltage , Same as RM17TG20 ¦ ,Phase asymmetry, Same as RM17TG20 ¦ ,Disconnection of neutral, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TG20 ¦ ,Extreme Overvoltage, Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873021vibration resistance | Same as RM17TG20 ¦ IEC60068-2-6
84873021width | Same as RM17TG20 ¦ ,Width,
84873022 | Same as RM17TT00 ¦ IEC60721-3-3,Climatic category, Same as RM17TT00 ¦ Germanisher Lloyd,Environmental category, Same as RM17TT00 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM17TT00 ¦ ,Supply,Rated Same as RM17TT00 ¦ ,Input 1,Voltage Same as RM17TT00 ¦ ,Input 2,Spec Same as RM17TT00 ¦ ,Input 3, Same as RM17TT00 ¦ ,Output 1, Same as RM17TT00 ¦ ,Output 2, Same as RM17TT00 ¦ ,Measurement mode, Same as RM17TT00 Same as RM17TT00 Same as RM17TT00 Same as RM17TT00 Same as RM17TT00 ¦ ,MTTFd, Same as RM17TT00 ¦ ,B10d, Drawing / Diagram
84873022IP degree of protection | Same as RM17TT00 ¦ IEC60529,Terminal Block, Same as RM17TT00 ¦ IEC60529,Housing, Same as RM17TT00 ¦ IEC60529,Front Panel,
84873022Input nominal voltage selection | Same as RM17TT00 ¦ ,Input nominal voltage selection,
84873022Minimum distance to adjacent devices | Same as RM17TT00 ¦ ,Horizontal, Same as RM17TT00 ¦ ,Vertical,
84873022[Ie] rated operational current | Same as RM17TT00 ¦ IEC61810-1,Rated switching current,
84873022[Ue] rated operational voltage | Same as RM17TT00 ¦ IEC61810-1,Rated switching voltage,
84873022[Ui] rated insulation voltage | Same as RM17TT00 ¦ IEC60664-1,Supply, Same as RM17TT00 ¦ IEC60664-1,Input 1, Same as RM17TT00 ¦ IEC60664-1,Input 2, Same as RM17TT00 ¦ IEC60664-1,Input 3, Same as RM17TT00 ¦ IEC60664-1,Output 1, Same as RM17TT00 ¦ IEC60664-1,Output 2, Same as RM17TT00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TT00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TT00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TT00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TT00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TT00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TT00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TT00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TT00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TT00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TT00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TT00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TT00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TT00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TT00 ¦ IEC60664-1,Input 1 / Input 3,
84873022[Uimp] rated impulse withstand voltage | Same as RM17TT00 ¦ IEC60664-1,Supply, Same as RM17TT00 ¦ IEC60664-1,Input 1, Same as RM17TT00 ¦ IEC60664-1,Input 2, Same as RM17TT00 ¦ IEC60664-1,Input 3, Same as RM17TT00 ¦ IEC60664-1,Output 1, Same as RM17TT00 ¦ IEC60664-1,Output 2, Same as RM17TT00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TT00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TT00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TT00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TT00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TT00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TT00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TT00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TT00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TT00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TT00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TT00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TT00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TT00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TT00 ¦ IEC60664-1,Input 1 / Input 3,
84873022[Us] rated supply voltage | Same as RM17TT00
84873022ambient air temperature for operation | Same as RM17TT00 ¦ ,Operation,
84873022ambient air temperature for storage | Same as RM17TT00 ¦ ,Storage,
84873022bump resistance | Same as RM17TT00 ¦ IEC60068-2-29
84873022cable stripping length | Same as RM17TT00 ¦ ,Cable stripping length,
84873022circuit group | Same as RM17TT00 ¦ ,Supply,Terminal Same as RM17TT00 ¦ ,Input 1, Same as RM17TT00 ¦ ,Input 2, Same as RM17TT00 ¦ ,Input 3, Same as RM17TT00 ¦ ,Output 1, Same as RM17TT00 ¦ ,Output 2,
84873022connections - terminals | Same as RM17TT00 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17TT00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17TT00 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17TT00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873022contacts material | Same as RM17TT00
84873022depth | Same as RM17TT00 ¦ ,Depth,
84873022diagnostic button | Same as RM17TT00
84873022dielectric strength | Same as RM17TT00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TT00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TT00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TT00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TT00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TT00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TT00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TT00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TT00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TT00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TT00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TT00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TT00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TT00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TT00 ¦ IEC60255-27,Input 1 / Input 3,
84873022directives | Same as RM17TT00 Same as RM17TT00 Same as RM17TT00
84873022duty time | Same as RM17TT00
84873022electrical durability | Same as RM17TT00 ¦ IEC60947-4-1,AC-1, Same as RM17TT00 ¦ IEC60947-4-1,DC-1, Same as RM17TT00 ¦ IEC60947-5-1,AC-15, Same as RM17TT00 ¦ IEC60947-5-1,DC-13,
84873022electromagnetic compatibility | Same as RM17TT00 ¦ ,Generic immunity standard, Same as RM17TT00 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17TT00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17TT00 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17TT00 ¦ IEC61000-4-5,Surge, Same as RM17TT00 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17TT00 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17TT00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17TT00 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17TT00 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17TT00 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM17TT00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17TT00 ¦ ,Generic emission standard, Same as RM17TT00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17TT00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17TT00 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17TT00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17TT00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17TT00 ¦ Germanisher Lloyd,Conducted emission,
84873022height | Same as RM17TT00 ¦ ,Height,
84873022hysteresis | Same as RM17TT00 ¦ ,Phase cut, Same as RM17TT00 ¦ ,Phase sequence, Same as RM17TT00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TT00 ¦ ,Over voltage, Same as RM17TT00 ¦ ,Undervoltage , Same as RM17TT00 ¦ ,Phase asymmetry, Same as RM17TT00 ¦ ,Disconnection of neutral, Same as RM17TT00 ¦ ,Voltage Regeneration, Same as RM17TT00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TT00 ¦ ,Extreme Overvoltage, Same as RM17TT00 ¦ ,Extreme Asymmetry,
84873022immunity to microbreaks | Same as RM17TT00
84873022input frequency | Same as RM17TT00 ¦ ,Rated frequency, Same as RM17TT00 ¦ ,Frequency operating range,
84873022input terminal | Same as RM17TT00 ¦ ,Input terminal,
84873022insulation resistance | Same as RM17TT00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TT00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TT00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TT00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TT00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TT00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TT00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TT00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TT00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TT00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TT00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TT00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TT00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TT00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TT00 ¦ IEC60255-27,Input 1 / Input 3,
84873022internal input resistance | Same as RM17TT00 ¦ ,Internal input resistance,
84873022local signalling | Same as RM17TT00 ¦ ,Power supply availability, Same as RM17TT00 ¦ ,Power supply not availability, Same as RM17TT00 ¦ ,Timing in-progress, Same as RM17TT00 ¦ ,Output is energized, Same as RM17TT00 ¦ ,Output is de-energized, Same as RM17TT00 ¦ ,Range Setting Changes, Same as RM17TT00 ¦ ,Phase Cut, Same as RM17TT00 ¦ ,Phase Sequence Swap, Same as RM17TT00 ¦ ,Undervoltage <U, Same as RM17TT00 ¦ ,Overvoltage >U, Same as RM17TT00 ¦ ,Phase Asymmetry, Same as RM17TT00 ¦ ,Voltage Regeneration, Same as RM17TT00 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17TT00 ¦ ,Extreme Overvoltage >U, Same as RM17TT00 ¦ ,Extreme Phase Asymmetry,
84873022marking | UL, CSA, GL, CCC, CE, China ROHS
84873022maximum leakage current | Same as RM17TT00 ¦ IEC62314,Only for solid state output,
84873022maximum measuring cycle | Same as RM17TT00 ¦ ,Maximum measuring cycles,
84873022maximum switching capacity | Same as RM17TT00 ¦ ,Maximum switching voltage, Same as RM17TT00 ¦ ,Maximum switching current, Same as RM17TT00 ¦ ,Maximum switching capacity,
84873022maximum voltage drop | Same as RM17TT00 ¦ IEC62314,Only for solid state output,
84873022measurement method | Same as RM17TT00 ¦ ,Measurement method,
84873022measurement range | Same as RM17TT00 ¦ ,Phase lost , Same as RM17TT00 ¦ ,Phase sequence, Same as RM17TT00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TT00 ¦ ,Over voltage, Same as RM17TT00 ¦ ,Undervoltage , Same as RM17TT00 ¦ ,Phase asymmetry, Same as RM17TT00 ¦ ,Disconnection of neutral, Same as RM17TT00 ¦ ,Voltage Regeneration, Same as RM17TT00 ¦ ,Extreme undervoltage, Same as RM17TT00 ¦ ,Extreme Overvoltage, Same as RM17TT00 ¦ ,Extreme Asymmetry,
84873022mechanical durability | Same as RM17TT00 ¦ IEC61810-1
84873022minimum switching capacity | Same as RM17TT00 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17TT00 ¦ IEC60947-5-4,Minimum switching current, Same as RM17TT00 ¦ IEC60947-5-4,Minimum switching capacity,
84873022monitoring functions | Same as RM17TT00 ¦ ,Phase lost , Same as RM17TT00 ¦ ,Phase sequence, Same as RM17TT00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TT00 ¦ ,Over voltage, Same as RM17TT00 ¦ ,Undervoltage , Same as RM17TT00 ¦ ,Phase asymmetry, Same as RM17TT00 ¦ ,Disconnection of neutral, Same as RM17TT00 ¦ ,Voltage Regeneration, Same as RM17TT00 ¦ ,Extreme undervoltage, Same as RM17TT00 ¦ ,Extreme overvoltage, Same as RM17TT00 ¦ ,Extreme asymmetry,
84873022mounting position | Same as RM17TT00 ¦ ,In relation to normal vertical mounting plane,
84873022mounting support | Same as RM17TT00 ¦ IEC/EN 60715,Without socket, Same as RM17TT00 ¦ IEC/EN 60715,With socket,
84873022net weight | Same as RM17TT00
84873022on-load factor | Same as RM17TT00
84873022output logic | Same as RM17TT00 ¦ ,R1 (11-12-14), Same as RM17TT00 ¦ ,R2 (21-22-24),
84873022output terminal | Same as RM17TT00
84873022output type | Same as RM17TT00
84873022overvoltage category | Same as RM17TT00 ¦ IEC60664-1
84873022permissible input overload | Same as RM17TT00 ¦ ,permissible input overload,
84873022polarity | Same as RM17TT00
84873022pollution degree | Same as RM17TT00 ¦ IEC60664-1
84873022power consumption | Same as RM17TT00
84873022power on delay | Same as RM17TT00
84873022product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873022relative humidity | Same as RM17TT00 ¦ IEC60068-2-30,Damp heat,XX
84873022release of input voltage | Same as RM17TT00
84873022repeat accuracy of the switching threshold | Same as RM17TT00 ¦ ,Repeat accuracy (constant parameters),
84873022repeat accuracy of time delay | Same as RM17TT00
84873022reset time | Same as RM17TT00 ¦ ,through Un power reset, Same as RM17TT00 ¦ ,through front panel reset, Same as RM17TT00 ¦ ,through input control reset,
84873022response time | Same as RM17TT00 ¦ ,on crossing the threshold, Same as RM17TT00 Same as RM17TT00 Same as RM17TT00 Same as RM17TT00
84873022safety reliability data | Same as RM17TT00 ¦ ,MTTF, Same as RM17TT00 ¦ ,B10,
84873022seismic resistance | Same as RM17TT00 ¦ IEC60068-3-3
84873022setting accuracy of the switching threshold | Same as RM17TT00 ¦ ,Setting accuracy,
84873022setting accuracy of time delay | Same as RM17TT00
84873022shock resistance | Same as RM17TT00 ¦ IEC60068-2-27
84873022short circuit protection | Same as RM17TT00 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17TT00 ¦ IEC62314,Solid State Output by external fuse,
84873022standards | Same as RM17TT00
84873022status LED | Same as RM17TT00
84873022supply frequency | Same as RM17TT00 Same as RM17TT00
84873022supply terminal | Same as RM17TT00
84873022supply voltage limits | Same as RM17TT00
84873022switching threshold drift | Same as RM17TT00 ¦ ,Measurement error with supply voltage variation, Same as RM17TT00 ¦ ,Measurement error with temperature variation,
84873022thermal current | Same as RM17TT00 ¦ IEC60947-5-1
84873022tightening torque | Same as RM17TT00 ¦ IEC60947-1,Tightening torque,
84873022time delay drift | Same as RM17TT00 Same as RM17TT00
84873022time delay range | Same as RM17TT00 ¦ ,"OFF" delay, Same as RM17TT00 ¦ ,"ON" delay, Same as RM17TT00 ¦ ,Inhibition,
84873022time delay type | Same as RM17TT00 ¦ ,"OFF" delay, Same as RM17TT00 ¦ ,"ON" delay, Same as RM17TT00 ¦ ,Inhibition,
84873022tripping threshold | Same as RM17TT00 ¦ ,Phase cut, Same as RM17TT00 ¦ ,Phase sequence, Same as RM17TT00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TT00 ¦ ,Over voltage, Same as RM17TT00 ¦ ,Undervoltage , Same as RM17TT00 ¦ ,Phase asymmetry, Same as RM17TT00 ¦ ,Disconnection of neutral, Same as RM17TT00 ¦ ,Voltage Regeneration, Same as RM17TT00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TT00 ¦ ,Extreme Overvoltage, Same as RM17TT00 ¦ ,Extreme Asymmetry,
84873022vibration resistance | Same as RM17TT00 ¦ IEC60068-2-6
84873022width | Same as RM17TT00 ¦ ,Width,
84873023 | Same as RM17TU00 ¦ IEC60721-3-3,Climatic category, Same as RM17TU00 ¦ Germanisher Lloyd,Environmental category, Same as RM17TU00 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM17TU00 ¦ ,Supply,Rated Same as RM17TU00 ¦ ,Input 1,Voltage Same as RM17TU00 ¦ ,Input 2,Spec Same as RM17TU00 ¦ ,Input 3, Same as RM17TU00 ¦ ,Output 1, Same as RM17TU00 ¦ ,Output 2, Same as RM17TU00 ¦ ,Measurement mode, Same as RM17TU00 Same as RM17TU00 Same as RM17TU00 Same as RM17TU00 Same as RM17TU00 ¦ ,MTTFd, Same as RM17TU00 ¦ ,B10d, Drawing / Diagram
84873023IP degree of protection | Same as RM17TU00 ¦ IEC60529,Terminal Block, Same as RM17TU00 ¦ IEC60529,Housing, Same as RM17TU00 ¦ IEC60529,Front Panel,
84873023Input nominal voltage selection | Same as RM17TU00 ¦ ,Input nominal voltage selection,
84873023Minimum distance to adjacent devices | Same as RM17TU00 ¦ ,Horizontal, Same as RM17TU00 ¦ ,Vertical,
84873023[Ie] rated operational current | Same as RM17TU00 ¦ IEC61810-1,Rated switching current,
84873023[Ue] rated operational voltage | Same as RM17TU00 ¦ IEC61810-1,Rated switching voltage,
84873023[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Supply, Same as RM17TU00 ¦ IEC60664-1,Input 1, Same as RM17TU00 ¦ IEC60664-1,Input 2, Same as RM17TU00 ¦ IEC60664-1,Input 3, Same as RM17TU00 ¦ IEC60664-1,Output 1, Same as RM17TU00 ¦ IEC60664-1,Output 2, Same as RM17TU00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TU00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TU00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TU00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TU00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TU00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TU00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TU00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TU00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TU00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TU00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TU00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TU00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TU00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TU00 ¦ IEC60664-1,Input 1 / Input 3,
84873023[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Supply, Same as RM17TU00 ¦ IEC60664-1,Input 1, Same as RM17TU00 ¦ IEC60664-1,Input 2, Same as RM17TU00 ¦ IEC60664-1,Input 3, Same as RM17TU00 ¦ IEC60664-1,Output 1, Same as RM17TU00 ¦ IEC60664-1,Output 2, Same as RM17TU00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TU00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TU00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TU00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TU00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TU00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TU00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TU00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TU00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TU00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TU00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TU00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TU00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TU00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TU00 ¦ IEC60664-1,Input 1 / Input 3,
84873023[Us] rated supply voltage | Same as RM17TU00
84873023ambient air temperature for operation | Same as RM17TU00 ¦ ,Operation,
84873023ambient air temperature for storage | Same as RM17TU00 ¦ ,Storage,
84873023bump resistance | Same as RM17TU00 ¦ IEC60068-2-29
84873023cable stripping length | Same as RM17TU00 ¦ ,Cable stripping length,
84873023circuit group | Same as RM17TU00 ¦ ,Supply,Terminal Same as RM17TU00 ¦ ,Input 1, Same as RM17TU00 ¦ ,Input 2, Same as RM17TU00 ¦ ,Input 3, Same as RM17TU00 ¦ ,Output 1, Same as RM17TU00 ¦ ,Output 2,
84873023connections - terminals | Same as RM17TU00 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17TU00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17TU00 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17TU00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873023contacts material | Same as RM17TU00
84873023depth | Same as RM17TU00 ¦ ,Depth,
84873023diagnostic button | Same as RM17TU00
84873023dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TU00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TU00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TU00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TU00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TU00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TU00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TU00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TU00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TU00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TU00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TU00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TU00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TU00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TU00 ¦ IEC60255-27,Input 1 / Input 3,
84873023directives | Same as RM17TU00 Same as RM17TU00 Same as RM17TU00
84873023duty time | Same as RM17TU00
84873023electrical durability | Same as RM17TU00 ¦ IEC60947-4-1,AC-1, Same as RM17TU00 ¦ IEC60947-4-1,DC-1, Same as RM17TU00 ¦ IEC60947-5-1,AC-15, Same as RM17TU00 ¦ IEC60947-5-1,DC-13,
84873023electromagnetic compatibility | Same as RM17TU00 ¦ ,Generic immunity standard, Same as RM17TU00 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17TU00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17TU00 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17TU00 ¦ IEC61000-4-5,Surge, Same as RM17TU00 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17TU00 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17TU00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17TU00 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17TU00 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17TU00 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM17TU00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17TU00 ¦ ,Generic emission standard, Same as RM17TU00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17TU00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17TU00 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17TU00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17TU00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17TU00 ¦ Germanisher Lloyd,Conducted emission,
84873023height | Same as RM17TU00 ¦ ,Height,
84873023hysteresis | Same as RM17TU00 ¦ ,Phase cut, Same as RM17TU00 ¦ ,Phase sequence, Same as RM17TU00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TU00 ¦ ,Over voltage, Same as RM17TU00 ¦ ,Undervoltage , Same as RM17TU00 ¦ ,Phase asymmetry, Same as RM17TU00 ¦ ,Disconnection of neutral, Same as RM17TU00 ¦ ,Voltage Regeneration, Same as RM17TU00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TU00 ¦ ,Extreme Overvoltage, Same as RM17TU00 ¦ ,Extreme Asymmetry,
84873023immunity to microbreaks | Same as RM17TU00
84873023input frequency | Same as RM17TU00 ¦ ,Rated frequency, Same as RM17TU00 ¦ ,Frequency operating range,
84873023input terminal | Same as RM17TU00 ¦ ,Input terminal,
84873023insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TU00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TU00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TU00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TU00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TU00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TU00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TU00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TU00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TU00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TU00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TU00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TU00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TU00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TU00 ¦ IEC60255-27,Input 1 / Input 3,
84873023internal input resistance | Same as RM17TU00 ¦ ,Internal input resistance,
84873023local signalling | Same as RM17TU00 ¦ ,Power supply availability, Same as RM17TU00 ¦ ,Power supply not availability, Same as RM17TU00 ¦ ,Timing in-progress, Same as RM17TU00 ¦ ,Output is energized, Same as RM17TU00 ¦ ,Output is de-energized, Same as RM17TU00 ¦ ,Range Setting Changes, Same as RM17TU00 ¦ ,Phase Cut, Same as RM17TU00 ¦ ,Phase Sequence Swap, Same as RM17TU00 ¦ ,Undervoltage <U, Same as RM17TU00 ¦ ,Overvoltage >U, Same as RM17TU00 ¦ ,Phase Asymmetry, Same as RM17TU00 ¦ ,Voltage Regeneration, Same as RM17TU00 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17TU00 ¦ ,Extreme Overvoltage >U, Same as RM17TU00 ¦ ,Extreme Phase Asymmetry,
84873023marking | UL, CSA, GL, CCC, CE, China ROHS
84873023maximum leakage current | Same as RM17TU00 ¦ IEC62314,Only for solid state output,
84873023maximum measuring cycle | Same as RM17TU00 ¦ ,Maximum measuring cycles,
84873023maximum switching capacity | Same as RM17TU00 ¦ ,Maximum switching voltage, Same as RM17TU00 ¦ ,Maximum switching current, Same as RM17TU00 ¦ ,Maximum switching capacity,
84873023maximum voltage drop | Same as RM17TU00 ¦ IEC62314,Only for solid state output,
84873023measurement method | Same as RM17TU00 ¦ ,Measurement method,
84873023measurement range | Same as RM17TU00 ¦ ,Phase lost , Same as RM17TU00 ¦ ,Phase sequence, Same as RM17TU00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TU00 ¦ ,Over voltage, Same as RM17TU00 ¦ ,Undervoltage , Same as RM17TU00 ¦ ,Phase asymmetry, Same as RM17TU00 ¦ ,Disconnection of neutral, Same as RM17TU00 ¦ ,Voltage Regeneration, Same as RM17TU00 ¦ ,Extreme undervoltage, Same as RM17TU00 ¦ ,Extreme Overvoltage, Same as RM17TU00 ¦ ,Extreme Asymmetry,
84873023mechanical durability | Same as RM17TU00 ¦ IEC61810-1
84873023minimum switching capacity | Same as RM17TU00 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17TU00 ¦ IEC60947-5-4,Minimum switching current, Same as RM17TU00 ¦ IEC60947-5-4,Minimum switching capacity,
84873023monitoring functions | Same as RM17TU00 ¦ ,Phase lost , Same as RM17TU00 ¦ ,Phase sequence, Same as RM17TU00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TU00 ¦ ,Over voltage, Same as RM17TU00 ¦ ,Undervoltage , Same as RM17TU00 ¦ ,Phase asymmetry, Same as RM17TU00 ¦ ,Disconnection of neutral, Same as RM17TU00 ¦ ,Voltage Regeneration, Same as RM17TU00 ¦ ,Extreme undervoltage, Same as RM17TU00 ¦ ,Extreme overvoltage, Same as RM17TU00 ¦ ,Extreme asymmetry,
84873023mounting position | Same as RM17TU00 ¦ ,In relation to normal vertical mounting plane,
84873023mounting support | Same as RM17TU00 ¦ IEC/EN 60715,Without socket, Same as RM17TU00 ¦ IEC/EN 60715,With socket,
84873023net weight | Same as RM17TU00
84873023on-load factor | Same as RM17TU00
84873023output logic | Same as RM17TU00 ¦ ,R1 (11-12-14), Same as RM17TU00 ¦ ,R2 (21-22-24),
84873023output terminal | Same as RM17TU00
84873023output type | Same as RM17TU00
84873023overvoltage category | Same as RM17TU00 ¦ IEC60664-1
84873023permissible input overload | Same as RM17TU00 ¦ ,permissible input overload,
84873023polarity | Same as RM17TU00
84873023pollution degree | Same as RM17TU00 ¦ IEC60664-1
84873023power consumption | Same as RM17TU00
84873023power on delay | Same as RM17TU00
84873023product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873023relative humidity | Same as RM17TU00 ¦ IEC60068-2-30,Damp heat,XX
84873023release of input voltage | Same as RM17TU00
84873023repeat accuracy of the switching threshold | Same as RM17TU00 ¦ ,Repeat accuracy (constant parameters),
84873023repeat accuracy of time delay | Same as RM17TU00
84873023reset time | Same as RM17TU00 ¦ ,through Un power reset, Same as RM17TU00 ¦ ,through front panel reset, Same as RM17TU00 ¦ ,through input control reset,
84873023response time | Same as RM17TU00 ¦ ,on crossing the threshold, Same as RM17TU00 Same as RM17TU00 Same as RM17TU00 Same as RM17TU00
84873023safety reliability data | Same as RM17TU00 ¦ ,MTTF, Same as RM17TU00 ¦ ,B10,
84873023seismic resistance | Same as RM17TU00 ¦ IEC60068-3-3
84873023setting accuracy of the switching threshold | Same as RM17TU00 ¦ ,Setting accuracy,
84873023setting accuracy of time delay | Same as RM17TU00
84873023shock resistance | Same as RM17TU00 ¦ IEC60068-2-27
84873023short circuit protection | Same as RM17TU00 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17TU00 ¦ IEC62314,Solid State Output by external fuse,
84873023standards | Same as RM17TU00
84873023status LED | Same as RM17TU00
84873023supply frequency | Same as RM17TU00 Same as RM17TU00
84873023supply terminal | Same as RM17TU00
84873023supply voltage limits | Same as RM17TU00
84873023switching threshold drift | Same as RM17TU00 ¦ ,Measurement error with supply voltage variation, Same as RM17TU00 ¦ ,Measurement error with temperature variation,
84873023thermal current | Same as RM17TU00 ¦ IEC60947-5-1
84873023tightening torque | Same as RM17TU00 ¦ IEC60947-1,Tightening torque,
84873023time delay drift | Same as RM17TU00 Same as RM17TU00
84873023time delay range | Same as RM17TU00 ¦ ,"OFF" delay, Same as RM17TU00 ¦ ,"ON" delay, Same as RM17TU00 ¦ ,Inhibition,
84873023time delay type | Same as RM17TU00 ¦ ,"OFF" delay, Same as RM17TU00 ¦ ,"ON" delay, Same as RM17TU00 ¦ ,Inhibition,
84873023tripping threshold | Same as RM17TU00 ¦ ,Phase cut, Same as RM17TU00 ¦ ,Phase sequence, Same as RM17TU00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TU00 ¦ ,Over voltage, Same as RM17TU00 ¦ ,Undervoltage , Same as RM17TU00 ¦ ,Phase asymmetry, Same as RM17TU00 ¦ ,Disconnection of neutral, Same as RM17TU00 ¦ ,Voltage Regeneration, Same as RM17TU00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TU00 ¦ ,Extreme Overvoltage, Same as RM17TU00 ¦ ,Extreme Asymmetry,
84873023vibration resistance | Same as RM17TU00 ¦ IEC60068-2-6
84873023width | Same as RM17TU00 ¦ ,Width,
84873024 | Same as RM17TA00 ¦ IEC60721-3-3,Climatic category, Same as RM17TA00 ¦ Germanisher Lloyd,Environmental category, Same as RM17TA00 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM17TA00 ¦ ,Supply,Rated Same as RM17TA00 ¦ ,Input 1,Voltage Same as RM17TA00 ¦ ,Input 2,Spec Same as RM17TA00 ¦ ,Input 3, Same as RM17TA00 ¦ ,Output 1, Same as RM17TA00 ¦ ,Output 2, Same as RM17TA00 ¦ ,Measurement mode, Same as RM17TA00 Same as RM17TA00 Same as RM17TA00 Same as RM17TA00 Same as RM17TA00 ¦ ,MTTFd, Same as RM17TA00 ¦ ,B10d, Drawing / Diagram
84873024IP degree of protection | Same as RM17TA00 ¦ IEC60529,Terminal Block, Same as RM17TA00 ¦ IEC60529,Housing, Same as RM17TA00 ¦ IEC60529,Front Panel,
84873024Input nominal voltage selection | Same as RM17TA00 ¦ ,Input nominal voltage selection,
84873024Minimum distance to adjacent devices | Same as RM17TA00 ¦ ,Horizontal, Same as RM17TA00 ¦ ,Vertical,
84873024[Ie] rated operational current | Same as RM17TA00 ¦ IEC61810-1,Rated switching current,
84873024[Ue] rated operational voltage | Same as RM17TA00 ¦ IEC61810-1,Rated switching voltage,
84873024[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply, Same as RM17TA00 ¦ IEC60664-1,Input 1, Same as RM17TA00 ¦ IEC60664-1,Input 2, Same as RM17TA00 ¦ IEC60664-1,Input 3, Same as RM17TA00 ¦ IEC60664-1,Output 1, Same as RM17TA00 ¦ IEC60664-1,Output 2, Same as RM17TA00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TA00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TA00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TA00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TA00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TA00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 3,
84873024[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply, Same as RM17TA00 ¦ IEC60664-1,Input 1, Same as RM17TA00 ¦ IEC60664-1,Input 2, Same as RM17TA00 ¦ IEC60664-1,Input 3, Same as RM17TA00 ¦ IEC60664-1,Output 1, Same as RM17TA00 ¦ IEC60664-1,Output 2, Same as RM17TA00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TA00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TA00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TA00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TA00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TA00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 3,
84873024[Us] rated supply voltage | Same as RM17TA00
84873024ambient air temperature for operation | Same as RM17TA00 ¦ ,Operation,
84873024ambient air temperature for storage | Same as RM17TA00 ¦ ,Storage,
84873024bump resistance | Same as RM17TA00 ¦ IEC60068-2-29
84873024cable stripping length | Same as RM17TA00 ¦ ,Cable stripping length,
84873024circuit group | Same as RM17TA00 ¦ ,Supply,Terminal Same as RM17TA00 ¦ ,Input 1, Same as RM17TA00 ¦ ,Input 2, Same as RM17TA00 ¦ ,Input 3, Same as RM17TA00 ¦ ,Output 1, Same as RM17TA00 ¦ ,Output 2,
84873024connections - terminals | Same as RM17TA00 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17TA00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17TA00 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17TA00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873024contacts material | Same as RM17TA00
84873024depth | Same as RM17TA00 ¦ ,Depth,
84873024diagnostic button | Same as RM17TA00
84873024dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TA00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TA00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TA00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TA00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TA00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 3,
84873024directives | Same as RM17TA00 Same as RM17TA00 Same as RM17TA00
84873024duty time | Same as RM17TA00
84873024electrical durability | Same as RM17TA00 ¦ IEC60947-4-1,AC-1, Same as RM17TA00 ¦ IEC60947-4-1,DC-1, Same as RM17TA00 ¦ IEC60947-5-1,AC-15, Same as RM17TA00 ¦ IEC60947-5-1,DC-13,
84873024electromagnetic compatibility | Same as RM17TA00 ¦ ,Generic immunity standard, Same as RM17TA00 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17TA00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17TA00 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17TA00 ¦ IEC61000-4-5,Surge, Same as RM17TA00 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17TA00 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17TA00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17TA00 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17TA00 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17TA00 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM17TA00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17TA00 ¦ ,Generic emission standard, Same as RM17TA00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17TA00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17TA00 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17TA00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17TA00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17TA00 ¦ Germanisher Lloyd,Conducted emission,
84873024height | Same as RM17TA00 ¦ ,Height,
84873024hysteresis | Same as RM17TA00 ¦ ,Phase cut, Same as RM17TA00 ¦ ,Phase sequence, Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TA00 ¦ ,Over voltage, Same as RM17TA00 ¦ ,Undervoltage , Same as RM17TA00 ¦ ,Phase asymmetry, Same as RM17TA00 ¦ ,Disconnection of neutral, Same as RM17TA00 ¦ ,Voltage Regeneration, Same as RM17TA00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TA00 ¦ ,Extreme Overvoltage, Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873024immunity to microbreaks | Same as RM17TA00
84873024input frequency | Same as RM17TA00 ¦ ,Rated frequency, Same as RM17TA00 ¦ ,Frequency operating range,
84873024input terminal | Same as RM17TA00 ¦ ,Input terminal,
84873024insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TA00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TA00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TA00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TA00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TA00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 3,
84873024internal input resistance | Same as RM17TA00 ¦ ,Internal input resistance,
84873024local signalling | Same as RM17TA00 ¦ ,Power supply availability, Same as RM17TA00 ¦ ,Power supply not availability, Same as RM17TA00 ¦ ,Timing in-progress, Same as RM17TA00 ¦ ,Output is energized, Same as RM17TA00 ¦ ,Output is de-energized, Same as RM17TA00 ¦ ,Range Setting Changes, Same as RM17TA00 ¦ ,Phase Cut, Same as RM17TA00 ¦ ,Phase Sequence Swap, Same as RM17TA00 ¦ ,Undervoltage <U, Same as RM17TA00 ¦ ,Overvoltage >U, Same as RM17TA00 ¦ ,Phase Asymmetry, Same as RM17TA00 ¦ ,Voltage Regeneration, Same as RM17TA00 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17TA00 ¦ ,Extreme Overvoltage >U, Same as RM17TA00 ¦ ,Extreme Phase Asymmetry,
84873024marking | UL, CSA, GL, CCC, CE, China ROHS
84873024maximum leakage current | Same as RM17TA00 ¦ IEC62314,Only for solid state output,
84873024maximum measuring cycle | Same as RM17TA00 ¦ ,Maximum measuring cycles,
84873024maximum switching capacity | Same as RM17TA00 ¦ ,Maximum switching voltage, Same as RM17TA00 ¦ ,Maximum switching current, Same as RM17TA00 ¦ ,Maximum switching capacity,
84873024maximum voltage drop | Same as RM17TA00 ¦ IEC62314,Only for solid state output,
84873024measurement method | Same as RM17TA00 ¦ ,Measurement method,
84873024measurement range | Same as RM17TA00 ¦ ,Phase lost , Same as RM17TA00 ¦ ,Phase sequence, Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TA00 ¦ ,Over voltage, Same as RM17TA00 ¦ ,Undervoltage , Same as RM17TA00 ¦ ,Phase asymmetry, Same as RM17TA00 ¦ ,Disconnection of neutral, Same as RM17TA00 ¦ ,Voltage Regeneration, Same as RM17TA00 ¦ ,Extreme undervoltage, Same as RM17TA00 ¦ ,Extreme Overvoltage, Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873024mechanical durability | Same as RM17TA00 ¦ IEC61810-1
84873024minimum switching capacity | Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching current, Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching capacity,
84873024monitoring functions | Same as RM17TA00 ¦ ,Phase lost , Same as RM17TA00 ¦ ,Phase sequence, Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TA00 ¦ ,Over voltage, Same as RM17TA00 ¦ ,Undervoltage , Same as RM17TA00 ¦ ,Phase asymmetry, Same as RM17TA00 ¦ ,Disconnection of neutral, Same as RM17TA00 ¦ ,Voltage Regeneration, Same as RM17TA00 ¦ ,Extreme undervoltage, Same as RM17TA00 ¦ ,Extreme overvoltage, Same as RM17TA00 ¦ ,Extreme asymmetry,
84873024mounting position | Same as RM17TA00 ¦ ,In relation to normal vertical mounting plane,
84873024mounting support | Same as RM17TA00 ¦ IEC/EN 60715,Without socket, Same as RM17TA00 ¦ IEC/EN 60715,With socket,
84873024net weight | Same as RM17TA00
84873024on-load factor | Same as RM17TA00
84873024output logic | Same as RM17TA00 ¦ ,R1 (11-12-14), Same as RM17TA00 ¦ ,R2 (21-22-24),
84873024output terminal | Same as RM17TA00
84873024output type | Same as RM17TA00
84873024overvoltage category | Same as RM17TA00 ¦ IEC60664-1
84873024permissible input overload | Same as RM17TA00 ¦ ,permissible input overload,
84873024polarity | Same as RM17TA00
84873024pollution degree | Same as RM17TA00 ¦ IEC60664-1
84873024power consumption | Same as RM17TA00
84873024power on delay | Same as RM17TA00
84873024product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873024relative humidity | Same as RM17TA00 ¦ IEC60068-2-30,Damp heat,XX
84873024release of input voltage | Same as RM17TA00
84873024repeat accuracy of the switching threshold | Same as RM17TA00 ¦ ,Repeat accuracy (constant parameters),
84873024repeat accuracy of time delay | Same as RM17TA00
84873024reset time | Same as RM17TA00 ¦ ,through Un power reset, Same as RM17TA00 ¦ ,through front panel reset, Same as RM17TA00 ¦ ,through input control reset,
84873024response time | Same as RM17TA00 ¦ ,on crossing the threshold, Same as RM17TA00 Same as RM17TA00 Same as RM17TA00 Same as RM17TA00
84873024safety reliability data | Same as RM17TA00 ¦ ,MTTF, Same as RM17TA00 ¦ ,B10,
84873024seismic resistance | Same as RM17TA00 ¦ IEC60068-3-3
84873024setting accuracy of the switching threshold | Same as RM17TA00 ¦ ,Setting accuracy,
84873024setting accuracy of time delay | Same as RM17TA00
84873024shock resistance | Same as RM17TA00 ¦ IEC60068-2-27
84873024short circuit protection | Same as RM17TA00 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17TA00 ¦ IEC62314,Solid State Output by external fuse,
84873024standards | Same as RM17TA00
84873024status LED | Same as RM17TA00
84873024supply frequency | Same as RM17TA00 Same as RM17TA00
84873024supply terminal | Same as RM17TA00
84873024supply voltage limits | Same as RM17TA00
84873024switching threshold drift | Same as RM17TA00 ¦ ,Measurement error with supply voltage variation, Same as RM17TA00 ¦ ,Measurement error with temperature variation,
84873024thermal current | Same as RM17TA00 ¦ IEC60947-5-1
84873024tightening torque | Same as RM17TA00 ¦ IEC60947-1,Tightening torque,
84873024time delay drift | Same as RM17TA00 Same as RM17TA00
84873024time delay range | Same as RM17TA00 ¦ ,"OFF" delay, Same as RM17TA00 ¦ ,"ON" delay, Same as RM17TA00 ¦ ,Inhibition,
84873024time delay type | Same as RM17TA00 ¦ ,"OFF" delay, Same as RM17TA00 ¦ ,"ON" delay, Same as RM17TA00 ¦ ,Inhibition,
84873024tripping threshold | Same as RM17TA00 ¦ ,Phase cut, Same as RM17TA00 ¦ ,Phase sequence, Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TA00 ¦ ,Over voltage, Same as RM17TA00 ¦ ,Undervoltage , Same as RM17TA00 ¦ ,Phase asymmetry, Same as RM17TA00 ¦ ,Disconnection of neutral, Same as RM17TA00 ¦ ,Voltage Regeneration, Same as RM17TA00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TA00 ¦ ,Extreme Overvoltage, Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873024vibration resistance | Same as RM17TA00 ¦ IEC60068-2-6
84873024width | Same as RM17TA00 ¦ ,Width,
84873025 | Same as RM17TE00 ¦ IEC60721-3-3,Climatic category, Same as RM17TE00 ¦ Germanisher Lloyd,Environmental category, Same as RM17TE00 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM17TE00 ¦ ,Supply,Rated Same as RM17TE00 ¦ ,Input 1,Voltage Same as RM17TE00 ¦ ,Input 2,Spec Same as RM17TE00 ¦ ,Input 3, Same as RM17TE00 ¦ ,Output 1, Same as RM17TE00 ¦ ,Output 2, Same as RM17TE00 ¦ ,Measurement mode, Same as RM17TE00 Same as RM17TE00 Same as RM17TE00 Same as RM17TE00 Same as RM17TE00 ¦ ,MTTFd, Same as RM17TE00 ¦ ,B10d, Drawing / Diagram
84873025IP degree of protection | Same as RM17TE00 ¦ IEC60529,Terminal Block, Same as RM17TE00 ¦ IEC60529,Housing, Same as RM17TE00 ¦ IEC60529,Front Panel,
84873025Input nominal voltage selection | Same as RM17TE00 ¦ ,Input nominal voltage selection,
84873025Minimum distance to adjacent devices | Same as RM17TE00 ¦ ,Horizontal, Same as RM17TE00 ¦ ,Vertical,
84873025[Ie] rated operational current | Same as RM17TE00 ¦ IEC61810-1,Rated switching current,
84873025[Ue] rated operational voltage | Same as RM17TE00 ¦ IEC61810-1,Rated switching voltage,
84873025[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Supply, Same as RM17TE00 ¦ IEC60664-1,Input 1, Same as RM17TE00 ¦ IEC60664-1,Input 2, Same as RM17TE00 ¦ IEC60664-1,Input 3, Same as RM17TE00 ¦ IEC60664-1,Output 1, Same as RM17TE00 ¦ IEC60664-1,Output 2, Same as RM17TE00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TE00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TE00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TE00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TE00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TE00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TE00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TE00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TE00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TE00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TE00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TE00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TE00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TE00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TE00 ¦ IEC60664-1,Input 1 / Input 3,
84873025[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Supply, Same as RM17TE00 ¦ IEC60664-1,Input 1, Same as RM17TE00 ¦ IEC60664-1,Input 2, Same as RM17TE00 ¦ IEC60664-1,Input 3, Same as RM17TE00 ¦ IEC60664-1,Output 1, Same as RM17TE00 ¦ IEC60664-1,Output 2, Same as RM17TE00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TE00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TE00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TE00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TE00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TE00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TE00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TE00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TE00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TE00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TE00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TE00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TE00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TE00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TE00 ¦ IEC60664-1,Input 1 / Input 3,
84873025[Us] rated supply voltage | Same as RM17TE00
84873025ambient air temperature for operation | Same as RM17TE00 ¦ ,Operation,
84873025ambient air temperature for storage | Same as RM17TE00 ¦ ,Storage,
84873025bump resistance | Same as RM17TE00 ¦ IEC60068-2-29
84873025cable stripping length | Same as RM17TE00 ¦ ,Cable stripping length,
84873025circuit group | Same as RM17TE00 ¦ ,Supply,Terminal Same as RM17TE00 ¦ ,Input 1, Same as RM17TE00 ¦ ,Input 2, Same as RM17TE00 ¦ ,Input 3, Same as RM17TE00 ¦ ,Output 1, Same as RM17TE00 ¦ ,Output 2,
84873025connections - terminals | Same as RM17TE00 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17TE00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17TE00 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17TE00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873025contacts material | Same as RM17TE00
84873025depth | Same as RM17TE00 ¦ ,Depth,
84873025diagnostic button | Same as RM17TE00
84873025dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TE00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TE00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TE00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TE00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TE00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TE00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TE00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TE00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TE00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TE00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TE00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TE00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TE00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TE00 ¦ IEC60255-27,Input 1 / Input 3,
84873025directives | Same as RM17TE00 Same as RM17TE00 Same as RM17TE00
84873025duty time | Same as RM17TE00
84873025electrical durability | Same as RM17TE00 ¦ IEC60947-4-1,AC-1, Same as RM17TE00 ¦ IEC60947-4-1,DC-1, Same as RM17TE00 ¦ IEC60947-5-1,AC-15, Same as RM17TE00 ¦ IEC60947-5-1,DC-13,
84873025electromagnetic compatibility | Same as RM17TE00 ¦ ,Generic immunity standard, Same as RM17TE00 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17TE00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17TE00 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17TE00 ¦ IEC61000-4-5,Surge, Same as RM17TE00 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17TE00 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17TE00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17TE00 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17TE00 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17TE00 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM17TE00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17TE00 ¦ ,Generic emission standard, Same as RM17TE00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17TE00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17TE00 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17TE00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17TE00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17TE00 ¦ Germanisher Lloyd,Conducted emission,
84873025height | Same as RM17TE00 ¦ ,Height,
84873025hysteresis | Same as RM17TE00 ¦ ,Phase cut, Same as RM17TE00 ¦ ,Phase sequence, Same as RM17TE00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TE00 ¦ ,Over voltage, Same as RM17TE00 ¦ ,Undervoltage , Same as RM17TE00 ¦ ,Phase asymmetry, Same as RM17TE00 ¦ ,Disconnection of neutral, Same as RM17TE00 ¦ ,Voltage Regeneration, Same as RM17TE00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TE00 ¦ ,Extreme Overvoltage, Same as RM17TE00 ¦ ,Extreme Asymmetry,
84873025immunity to microbreaks | Same as RM17TE00
84873025input frequency | Same as RM17TE00 ¦ ,Rated frequency, Same as RM17TE00 ¦ ,Frequency operating range,
84873025input terminal | Same as RM17TE00 ¦ ,Input terminal,
84873025insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TE00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TE00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TE00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TE00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TE00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TE00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TE00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TE00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TE00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TE00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TE00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TE00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TE00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TE00 ¦ IEC60255-27,Input 1 / Input 3,
84873025internal input resistance | Same as RM17TE00 ¦ ,Internal input resistance,
84873025local signalling | Same as RM17TE00 ¦ ,Power supply availability, Same as RM17TE00 ¦ ,Power supply not availability, Same as RM17TE00 ¦ ,Timing in-progress, Same as RM17TE00 ¦ ,Output is energized, Same as RM17TE00 ¦ ,Output is de-energized, Same as RM17TE00 ¦ ,Range Setting Changes, Same as RM17TE00 ¦ ,Phase Cut, Same as RM17TE00 ¦ ,Phase Sequence Swap, Same as RM17TE00 ¦ ,Undervoltage <U, Same as RM17TE00 ¦ ,Overvoltage >U, Same as RM17TE00 ¦ ,Phase Asymmetry, Same as RM17TE00 ¦ ,Voltage Regeneration, Same as RM17TE00 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17TE00 ¦ ,Extreme Overvoltage >U, Same as RM17TE00 ¦ ,Extreme Phase Asymmetry,
84873025marking | UL, CSA, GL, CCC, CE, China ROHS
84873025maximum leakage current | Same as RM17TE00 ¦ IEC62314,Only for solid state output,
84873025maximum measuring cycle | Same as RM17TE00 ¦ ,Maximum measuring cycles,
84873025maximum switching capacity | Same as RM17TE00 ¦ ,Maximum switching voltage, Same as RM17TE00 ¦ ,Maximum switching current, Same as RM17TE00 ¦ ,Maximum switching capacity,
84873025maximum voltage drop | Same as RM17TE00 ¦ IEC62314,Only for solid state output,
84873025measurement method | Same as RM17TE00 ¦ ,Measurement method,
84873025measurement range | Same as RM17TE00 ¦ ,Phase lost , Same as RM17TE00 ¦ ,Phase sequence, Same as RM17TE00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TE00 ¦ ,Over voltage, Same as RM17TE00 ¦ ,Undervoltage , Same as RM17TE00 ¦ ,Phase asymmetry, Same as RM17TE00 ¦ ,Disconnection of neutral, Same as RM17TE00 ¦ ,Voltage Regeneration, Same as RM17TE00 ¦ ,Extreme undervoltage, Same as RM17TE00 ¦ ,Extreme Overvoltage, Same as RM17TE00 ¦ ,Extreme Asymmetry,
84873025mechanical durability | Same as RM17TE00 ¦ IEC61810-1
84873025minimum switching capacity | Same as RM17TE00 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17TE00 ¦ IEC60947-5-4,Minimum switching current, Same as RM17TE00 ¦ IEC60947-5-4,Minimum switching capacity,
84873025monitoring functions | Same as RM17TE00 ¦ ,Phase lost , Same as RM17TE00 ¦ ,Phase sequence, Same as RM17TE00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TE00 ¦ ,Over voltage, Same as RM17TE00 ¦ ,Undervoltage , Same as RM17TE00 ¦ ,Phase asymmetry, Same as RM17TE00 ¦ ,Disconnection of neutral, Same as RM17TE00 ¦ ,Voltage Regeneration, Same as RM17TE00 ¦ ,Extreme undervoltage, Same as RM17TE00 ¦ ,Extreme overvoltage, Same as RM17TE00 ¦ ,Extreme asymmetry,
84873025mounting position | Same as RM17TE00 ¦ ,In relation to normal vertical mounting plane,
84873025mounting support | Same as RM17TE00 ¦ IEC/EN 60715,Without socket, Same as RM17TE00 ¦ IEC/EN 60715,With socket,
84873025net weight | Same as RM17TE00
84873025on-load factor | Same as RM17TE00
84873025output logic | Same as RM17TE00 ¦ ,R1 (11-12-14), Same as RM17TE00 ¦ ,R2 (21-22-24),
84873025output terminal | Same as RM17TE00
84873025output type | Same as RM17TE00
84873025overvoltage category | Same as RM17TE00 ¦ IEC60664-1
84873025permissible input overload | Same as RM17TE00 ¦ ,permissible input overload,
84873025polarity | Same as RM17TE00
84873025pollution degree | Same as RM17TE00 ¦ IEC60664-1
84873025power consumption | Same as RM17TE00
84873025power on delay | Same as RM17TE00
84873025product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873025relative humidity | Same as RM17TE00 ¦ IEC60068-2-30,Damp heat,XX
84873025release of input voltage | Same as RM17TE00
84873025repeat accuracy of the switching threshold | Same as RM17TE00 ¦ ,Repeat accuracy (constant parameters),
84873025repeat accuracy of time delay | Same as RM17TE00
84873025reset time | Same as RM17TE00 ¦ ,through Un power reset, Same as RM17TE00 ¦ ,through front panel reset, Same as RM17TE00 ¦ ,through input control reset,
84873025response time | Same as RM17TE00 ¦ ,on crossing the threshold, Same as RM17TE00 Same as RM17TE00 Same as RM17TE00 Same as RM17TE00
84873025safety reliability data | Same as RM17TE00 ¦ ,MTTF, Same as RM17TE00 ¦ ,B10,
84873025seismic resistance | Same as RM17TE00 ¦ IEC60068-3-3
84873025setting accuracy of the switching threshold | Same as RM17TE00 ¦ ,Setting accuracy,
84873025setting accuracy of time delay | Same as RM17TE00
84873025shock resistance | Same as RM17TE00 ¦ IEC60068-2-27
84873025short circuit protection | Same as RM17TE00 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17TE00 ¦ IEC62314,Solid State Output by external fuse,
84873025standards | Same as RM17TE00
84873025status LED | Same as RM17TE00
84873025supply frequency | Same as RM17TE00 Same as RM17TE00
84873025supply terminal | Same as RM17TE00
84873025supply voltage limits | Same as RM17TE00
84873025switching threshold drift | Same as RM17TE00 ¦ ,Measurement error with supply voltage variation, Same as RM17TE00 ¦ ,Measurement error with temperature variation,
84873025thermal current | Same as RM17TE00 ¦ IEC60947-5-1
84873025tightening torque | Same as RM17TE00 ¦ IEC60947-1,Tightening torque,
84873025time delay drift | Same as RM17TE00 Same as RM17TE00
84873025time delay range | Same as RM17TE00 ¦ ,"OFF" delay, Same as RM17TE00 ¦ ,"ON" delay, Same as RM17TE00 ¦ ,Inhibition,
84873025time delay type | Same as RM17TE00 ¦ ,"OFF" delay, Same as RM17TE00 ¦ ,"ON" delay, Same as RM17TE00 ¦ ,Inhibition,
84873025tripping threshold | Same as RM17TE00 ¦ ,Phase cut, Same as RM17TE00 ¦ ,Phase sequence, Same as RM17TE00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TE00 ¦ ,Over voltage, Same as RM17TE00 ¦ ,Undervoltage , Same as RM17TE00 ¦ ,Phase asymmetry, Same as RM17TE00 ¦ ,Disconnection of neutral, Same as RM17TE00 ¦ ,Voltage Regeneration, Same as RM17TE00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TE00 ¦ ,Extreme Overvoltage, Same as RM17TE00 ¦ ,Extreme Asymmetry,
84873025vibration resistance | Same as RM17TE00 ¦ IEC60068-2-6
84873025width | Same as RM17TE00 ¦ ,Width,
84873026 | Same as RM35TF30 ¦ IEC60721-3-3,Climatic category, Same as RM35TF30 ¦ Germanisher Lloyd,Environmental category, Same as RM35TF30 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM35TF30 ¦ ,Supply,Rated Same as RM35TF30 ¦ ,Input 1,Voltage Same as RM35TF30 ¦ ,Input 2,Spec Same as RM35TF30 ¦ ,Input 3, Same as RM35TF30 ¦ ,Output 1, Same as RM35TF30 ¦ ,Output 2, Same as RM35TF30 ¦ ,Measurement mode, Same as RM35TF30 Same as RM35TF30 Same as RM35TF30 Same as RM35TF30 Same as RM35TF30 ¦ ,MTTFd, Same as RM35TF30 ¦ ,B10d, Drawing / Diagram
84873026IP degree of protection | Same as RM35TF30 ¦ IEC60529,Terminal Block, Same as RM35TF30 ¦ IEC60529,Housing, Same as RM35TF30 ¦ IEC60529,Front Panel,
84873026Input nominal voltage selection | Same as RM35TF30 ¦ ,Input nominal voltage selection,
84873026Minimum distance to adjacent devices | Same as RM35TF30 ¦ ,Horizontal, Same as RM35TF30 ¦ ,Vertical,
84873026[Ie] rated operational current | Same as RM35TF30 ¦ IEC61810-1,Rated switching current,
84873026[Ue] rated operational voltage | Same as RM35TF30 ¦ IEC61810-1,Rated switching voltage,
84873026[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply, Same as RM35TF30 ¦ IEC60664-1,Input 1, Same as RM35TF30 ¦ IEC60664-1,Input 2, Same as RM35TF30 ¦ IEC60664-1,Input 3, Same as RM35TF30 ¦ IEC60664-1,Output 1, Same as RM35TF30 ¦ IEC60664-1,Output 2, Same as RM35TF30 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM35TF30 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM35TF30 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM35TF30 ¦ IEC60664-1,Supply / Output 1, Same as RM35TF30 ¦ IEC60664-1,Supply / Output 2, Same as RM35TF30 ¦ IEC60664-1,Output 1 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 2, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Input 3, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 3,
84873026[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply, Same as RM35TF30 ¦ IEC60664-1,Input 1, Same as RM35TF30 ¦ IEC60664-1,Input 2, Same as RM35TF30 ¦ IEC60664-1,Input 3, Same as RM35TF30 ¦ IEC60664-1,Output 1, Same as RM35TF30 ¦ IEC60664-1,Output 2, Same as RM35TF30 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM35TF30 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM35TF30 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM35TF30 ¦ IEC60664-1,Supply / Output 1, Same as RM35TF30 ¦ IEC60664-1,Supply / Output 2, Same as RM35TF30 ¦ IEC60664-1,Output 1 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 2, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Input 3, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 3,
84873026[Us] rated supply voltage | Same as RM35TF30
84873026ambient air temperature for operation | Same as RM35TF30 ¦ ,Operation,
84873026ambient air temperature for storage | Same as RM35TF30 ¦ ,Storage,
84873026bump resistance | Same as RM35TF30 ¦ IEC60068-2-29
84873026cable stripping length | Same as RM35TF30 ¦ ,Cable stripping length,
84873026circuit group | Same as RM35TF30 ¦ ,Supply,Terminal Same as RM35TF30 ¦ ,Input 1, Same as RM35TF30 ¦ ,Input 2, Same as RM35TF30 ¦ ,Input 3, Same as RM35TF30 ¦ ,Output 1, Same as RM35TF30 ¦ ,Output 2,
84873026connections - terminals | Same as RM35TF30 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM35TF30 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM35TF30 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM35TF30 ¦ IEC60947-1,Flexible cable (spring terminal),
84873026contacts material | Same as RM35TF30
84873026depth | Same as RM35TF30 ¦ ,Depth,
84873026diagnostic button | Same as RM35TF30
84873026dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 1, Same as RM35TF30 ¦ IEC60255-27,Supply / Input 2, Same as RM35TF30 ¦ IEC60255-27,Supply / Input 3, Same as RM35TF30 ¦ IEC60255-27,Supply / Output 1, Same as RM35TF30 ¦ IEC60255-27,Supply / Output 2, Same as RM35TF30 ¦ IEC60255-27,Output 1 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 2, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Input 3, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 3,
84873026directives | Same as RM35TF30 Same as RM35TF30 Same as RM35TF30
84873026duty time | Same as RM35TF30
84873026electrical durability | Same as RM35TF30 ¦ IEC60947-4-1,AC-1, Same as RM35TF30 ¦ IEC60947-4-1,DC-1, Same as RM35TF30 ¦ IEC60947-5-1,AC-15, Same as RM35TF30 ¦ IEC60947-5-1,DC-13,
84873026electromagnetic compatibility | Same as RM35TF30 ¦ ,Generic immunity standard, Same as RM35TF30 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM35TF30 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM35TF30 ¦ IEC61000-4-4,Fast transient / burst, Same as RM35TF30 ¦ IEC61000-4-5,Surge, Same as RM35TF30 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM35TF30 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM35TF30 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM35TF30 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM35TF30 ¦ IEC61000-4-29,DC voltage interruption, Same as RM35TF30 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM35TF30 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM35TF30 ¦ ,Generic emission standard, Same as RM35TF30 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM35TF30 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM35TF30 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM35TF30 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM35TF30 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM35TF30 ¦ Germanisher Lloyd,Conducted emission,
84873026height | Same as RM35TF30 ¦ ,Height,
84873026hysteresis | Same as RM35TF30 ¦ ,Phase cut, Same as RM35TF30 ¦ ,Phase sequence, Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35TF30 ¦ ,Over voltage, Same as RM35TF30 ¦ ,Undervoltage , Same as RM35TF30 ¦ ,Phase asymmetry, Same as RM35TF30 ¦ ,Disconnection of neutral, Same as RM35TF30 ¦ ,Voltage Regeneration, Same as RM35TF30 ¦ ,Extreme undervoltage (Phase loss), Same as RM35TF30 ¦ ,Extreme Overvoltage, Same as RM35TF30 ¦ ,Extreme Asymmetry,
84873026immunity to microbreaks | Same as RM35TF30
84873026input frequency | Same as RM35TF30 ¦ ,Rated frequency, Same as RM35TF30 ¦ ,Frequency operating range,
84873026input terminal | Same as RM35TF30 ¦ ,Input terminal,
84873026insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 1, Same as RM35TF30 ¦ IEC60255-27,Supply / Input 2, Same as RM35TF30 ¦ IEC60255-27,Supply / Input 3, Same as RM35TF30 ¦ IEC60255-27,Supply / Output 1, Same as RM35TF30 ¦ IEC60255-27,Supply / Output 2, Same as RM35TF30 ¦ IEC60255-27,Output 1 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 2, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Input 3, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 3,
84873026internal input resistance | Same as RM35TF30 ¦ ,Internal input resistance,
84873026local signalling | Same as RM35TF30 ¦ ,Power supply availability, Same as RM35TF30 ¦ ,Power supply not availability, Same as RM35TF30 ¦ ,Timing in-progress, Same as RM35TF30 ¦ ,Output is energized, Same as RM35TF30 ¦ ,Output is de-energized, Same as RM35TF30 ¦ ,Range Setting Changes, Same as RM35TF30 ¦ ,Phase Cut, Same as RM35TF30 ¦ ,Phase Sequence Swap, Same as RM35TF30 ¦ ,Undervoltage <U, Same as RM35TF30 ¦ ,Overvoltage >U, Same as RM35TF30 ¦ ,Phase Asymmetry, Same as RM35TF30 ¦ ,Voltage Regeneration, Same as RM35TF30 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM35TF30 ¦ ,Extreme Overvoltage >U, Same as RM35TF30 ¦ ,Extreme Phase Asymmetry,
84873026marking | UL, CSA, GL, CCC, CE, China ROHS
84873026maximum leakage current | Same as RM35TF30 ¦ IEC62314,Only for solid state output,
84873026maximum measuring cycle | Same as RM35TF30 ¦ ,Maximum measuring cycles,
84873026maximum switching capacity | Same as RM35TF30 ¦ ,Maximum switching voltage, Same as RM35TF30 ¦ ,Maximum switching current, Same as RM35TF30 ¦ ,Maximum switching capacity,
84873026maximum voltage drop | Same as RM35TF30 ¦ IEC62314,Only for solid state output,
84873026measurement method | Same as RM35TF30 ¦ ,Measurement method,
84873026measurement range | Same as RM35TF30 ¦ ,Phase lost , Same as RM35TF30 ¦ ,Phase sequence, Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35TF30 ¦ ,Over voltage, Same as RM35TF30 ¦ ,Undervoltage , Same as RM35TF30 ¦ ,Phase asymmetry, Same as RM35TF30 ¦ ,Disconnection of neutral, Same as RM35TF30 ¦ ,Voltage Regeneration, Same as RM35TF30 ¦ ,Extreme undervoltage, Same as RM35TF30 ¦ ,Extreme Overvoltage, Same as RM35TF30 ¦ ,Extreme Asymmetry,
84873026mechanical durability | Same as RM35TF30 ¦ IEC61810-1
84873026minimum switching capacity | Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching current, Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching capacity,
84873026monitoring functions | Same as RM35TF30 ¦ ,Phase lost , Same as RM35TF30 ¦ ,Phase sequence, Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35TF30 ¦ ,Over voltage, Same as RM35TF30 ¦ ,Undervoltage , Same as RM35TF30 ¦ ,Phase asymmetry, Same as RM35TF30 ¦ ,Disconnection of neutral, Same as RM35TF30 ¦ ,Voltage Regeneration, Same as RM35TF30 ¦ ,Extreme undervoltage, Same as RM35TF30 ¦ ,Extreme overvoltage, Same as RM35TF30 ¦ ,Extreme asymmetry,
84873026mounting position | Same as RM35TF30 ¦ ,In relation to normal vertical mounting plane,
84873026mounting support | Same as RM35TF30 ¦ IEC/EN 60715,Without socket, Same as RM35TF30 ¦ IEC/EN 60715,With socket,
84873026net weight | Same as RM35TF30
84873026on-load factor | Same as RM35TF30
84873026output logic | Same as RM35TF30 ¦ ,R1 (11-12-14), Same as RM35TF30 ¦ ,R2 (21-22-24),
84873026output terminal | Same as RM35TF30
84873026output type | Same as RM35TF30
84873026overvoltage category | Same as RM35TF30 ¦ IEC60664-1
84873026permissible input overload | Same as RM35TF30 ¦ ,permissible input overload,
84873026polarity | Same as RM35TF30
84873026pollution degree | Same as RM35TF30 ¦ IEC60664-1
84873026power consumption | Same as RM35TF30
84873026power on delay | Same as RM35TF30
84873026product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873026relative humidity | Same as RM35TF30 ¦ IEC60068-2-30,Damp heat,XX
84873026release of input voltage | Same as RM35TF30
84873026repeat accuracy of the switching threshold | Same as RM35TF30 ¦ ,Repeat accuracy (constant parameters),
84873026repeat accuracy of time delay | Same as RM35TF30
84873026reset time | Same as RM35TF30 ¦ ,through Un power reset, Same as RM35TF30 ¦ ,through front panel reset, Same as RM35TF30 ¦ ,through input control reset,
84873026response time | Same as RM35TF30 ¦ ,on crossing the threshold, Same as RM35TF30 Same as RM35TF30 Same as RM35TF30 Same as RM35TF30
84873026safety reliability data | Same as RM35TF30 ¦ ,MTTF, Same as RM35TF30 ¦ ,B10,
84873026seismic resistance | Same as RM35TF30 ¦ IEC60068-3-3
84873026setting accuracy of the switching threshold | Same as RM35TF30 ¦ ,Setting accuracy,
84873026setting accuracy of time delay | Same as RM35TF30
84873026shock resistance | Same as RM35TF30 ¦ IEC60068-2-27
84873026short circuit protection | Same as RM35TF30 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM35TF30 ¦ IEC62314,Solid State Output by external fuse,
84873026standards | Same as RM35TF30
84873026status LED | Same as RM35TF30
84873026supply frequency | Same as RM35TF30 Same as RM35TF30
84873026supply terminal | Same as RM35TF30
84873026supply voltage limits | Same as RM35TF30
84873026switching threshold drift | Same as RM35TF30 ¦ ,Measurement error with supply voltage variation, Same as RM35TF30 ¦ ,Measurement error with temperature variation,
84873026thermal current | Same as RM35TF30 ¦ IEC60947-5-1
84873026tightening torque | Same as RM35TF30 ¦ IEC60947-1,Tightening torque,
84873026time delay drift | Same as RM35TF30 Same as RM35TF30
84873026time delay range | Same as RM35TF30 ¦ ,"OFF" delay, Same as RM35TF30 ¦ ,"ON" delay, Same as RM35TF30 ¦ ,Inhibition,
84873026time delay type | Same as RM35TF30 ¦ ,"OFF" delay, Same as RM35TF30 ¦ ,"ON" delay, Same as RM35TF30 ¦ ,Inhibition,
84873026tripping threshold | Same as RM35TF30 ¦ ,Phase cut, Same as RM35TF30 ¦ ,Phase sequence, Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35TF30 ¦ ,Over voltage, Same as RM35TF30 ¦ ,Undervoltage , Same as RM35TF30 ¦ ,Phase asymmetry, Same as RM35TF30 ¦ ,Disconnection of neutral, Same as RM35TF30 ¦ ,Voltage Regeneration, Same as RM35TF30 ¦ ,Extreme undervoltage (Phase loss), Same as RM35TF30 ¦ ,Extreme Overvoltage, Same as RM35TF30 ¦ ,Extreme Asymmetry,
84873026vibration resistance | Same as RM35TF30 ¦ IEC60068-2-6
84873026width | Same as RM35TF30 ¦ ,Width,
84873029 | Same as RM17TG00 ¦ IEC60721-3-3,Climatic category, Same as RM17TG00 ¦ Germanisher Lloyd,Environmental category, Same as RM17TG00 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM17TG00 ¦ ,Supply,Rated Same as RM17TG00 ¦ ,Input 1,Voltage Same as RM17TG00 ¦ ,Input 2,Spec Same as RM17TG00 ¦ ,Input 3, Same as RM17TG00 ¦ ,Output 1, Same as RM17TG00 ¦ ,Output 2, Same as RM17TG00 ¦ ,Measurement mode, Same as RM17TG00 Same as RM17TG00 Same as RM17TG00 Same as RM17TG00 Same as RM17TG00 ¦ ,MTTFd, Same as RM17TG00 ¦ ,B10d, Drawing / Diagram
84873029IP degree of protection | Same as RM17TG00 ¦ IEC60529,Terminal Block, Same as RM17TG00 ¦ IEC60529,Housing, Same as RM17TG00 ¦ IEC60529,Front Panel,
84873029Input nominal voltage selection | Same as RM17TG00 ¦ ,Input nominal voltage selection,
84873029Minimum distance to adjacent devices | Same as RM17TG00 ¦ ,Horizontal, Same as RM17TG00 ¦ ,Vertical,
84873029[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
84873029[Ue] rated operational voltage | Same as RM17TG00 ¦ IEC61810-1,Rated switching voltage,
84873029[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply, Same as RM17TG00 ¦ IEC60664-1,Input 1, Same as RM17TG00 ¦ IEC60664-1,Input 2, Same as RM17TG00 ¦ IEC60664-1,Input 3, Same as RM17TG00 ¦ IEC60664-1,Output 1, Same as RM17TG00 ¦ IEC60664-1,Output 2, Same as RM17TG00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TG00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TG00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TG00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TG00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TG00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 3,
84873029[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply, Same as RM17TG00 ¦ IEC60664-1,Input 1, Same as RM17TG00 ¦ IEC60664-1,Input 2, Same as RM17TG00 ¦ IEC60664-1,Input 3, Same as RM17TG00 ¦ IEC60664-1,Output 1, Same as RM17TG00 ¦ IEC60664-1,Output 2, Same as RM17TG00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TG00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TG00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TG00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TG00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TG00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 3,
84873029[Us] rated supply voltage | Same as RM17TG00
84873029ambient air temperature for operation | Same as RM17TG00 ¦ ,Operation,
84873029ambient air temperature for storage | Same as RM17TG00 ¦ ,Storage,
84873029bump resistance | Same as RM17TG00 ¦ IEC60068-2-29
84873029cable stripping length | Same as RM17TG00 ¦ ,Cable stripping length,
84873029circuit group | Same as RM17TG00 ¦ ,Supply,Terminal Same as RM17TG00 ¦ ,Input 1, Same as RM17TG00 ¦ ,Input 2, Same as RM17TG00 ¦ ,Input 3, Same as RM17TG00 ¦ ,Output 1, Same as RM17TG00 ¦ ,Output 2,
84873029connections - terminals | Same as RM17TG00 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17TG00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17TG00 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17TG00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873029contacts material | Same as RM17TG00
84873029depth | Same as RM17TG00 ¦ ,Depth,
84873029diagnostic button | Same as RM17TG00
84873029dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TG00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TG00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TG00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TG00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TG00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 3,
84873029directives | Same as RM17TG00 Same as RM17TG00 Same as RM17TG00
84873029duty time | Same as RM17TG00
84873029electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, Same as RM17TG00 ¦ IEC60947-4-1,DC-1, Same as RM17TG00 ¦ IEC60947-5-1,AC-15, Same as RM17TG00 ¦ IEC60947-5-1,DC-13,
84873029electromagnetic compatibility | Same as RM17TG00 ¦ ,Generic immunity standard, Same as RM17TG00 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17TG00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17TG00 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17TG00 ¦ IEC61000-4-5,Surge, Same as RM17TG00 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17TG00 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17TG00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17TG00 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17TG00 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17TG00 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM17TG00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17TG00 ¦ ,Generic emission standard, Same as RM17TG00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17TG00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17TG00 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17TG00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17TG00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17TG00 ¦ Germanisher Lloyd,Conducted emission,
84873029height | Same as RM17TG00 ¦ ,Height,
84873029hysteresis | Same as RM17TG00 ¦ ,Phase cut, Same as RM17TG00 ¦ ,Phase sequence, Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG00 ¦ ,Over voltage, Same as RM17TG00 ¦ ,Undervoltage , Same as RM17TG00 ¦ ,Phase asymmetry, Same as RM17TG00 ¦ ,Disconnection of neutral, Same as RM17TG00 ¦ ,Voltage Regeneration, Same as RM17TG00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TG00 ¦ ,Extreme Overvoltage, Same as RM17TG00 ¦ ,Extreme Asymmetry,
84873029immunity to microbreaks | Same as RM17TG00
84873029input frequency | Same as RM17TG00 ¦ ,Rated frequency, Same as RM17TG00 ¦ ,Frequency operating range,
84873029input terminal | Same as RM17TG00 ¦ ,Input terminal,
84873029insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TG00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TG00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TG00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TG00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TG00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 3,
84873029internal input resistance | Same as RM17TG00 ¦ ,Internal input resistance,
84873029local signalling | Same as RM17TG00 ¦ ,Power supply availability, Same as RM17TG00 ¦ ,Power supply not availability, Same as RM17TG00 ¦ ,Timing in-progress, Same as RM17TG00 ¦ ,Output is energized, Same as RM17TG00 ¦ ,Output is de-energized, Same as RM17TG00 ¦ ,Range Setting Changes, Same as RM17TG00 ¦ ,Phase Cut, Same as RM17TG00 ¦ ,Phase Sequence Swap, Same as RM17TG00 ¦ ,Undervoltage <U, Same as RM17TG00 ¦ ,Overvoltage >U, Same as RM17TG00 ¦ ,Phase Asymmetry, Same as RM17TG00 ¦ ,Voltage Regeneration, Same as RM17TG00 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17TG00 ¦ ,Extreme Overvoltage >U, Same as RM17TG00 ¦ ,Extreme Phase Asymmetry,
84873029marking | UL, CSA, CCC, CE, China ROHS
84873029maximum leakage current | Same as RM17TG00 ¦ IEC62314,Only for solid state output,
84873029maximum measuring cycle | Same as RM17TG00 ¦ ,Maximum measuring cycles,
84873029maximum switching capacity | Same as RM17TG00 ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, Same as RM17TG00 ¦ ,Maximum switching capacity,
84873029maximum voltage drop | Same as RM17TG00 ¦ IEC62314,Only for solid state output,
84873029measurement method | Same as RM17TG00 ¦ ,Measurement method,
84873029measurement range | Same as RM17TG00 ¦ ,Phase lost , Same as RM17TG00 ¦ ,Phase sequence, Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG00 ¦ ,Over voltage, Same as RM17TG00 ¦ ,Undervoltage , Same as RM17TG00 ¦ ,Phase asymmetry, Same as RM17TG00 ¦ ,Disconnection of neutral, Same as RM17TG00 ¦ ,Voltage Regeneration, Same as RM17TG00 ¦ ,Extreme undervoltage, Same as RM17TG00 ¦ ,Extreme Overvoltage, Same as RM17TG00 ¦ ,Extreme Asymmetry,
84873029mechanical durability | Same as RM17TG00 ¦ IEC61810-1
84873029minimum switching capacity | Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching current, Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching capacity,
84873029monitoring functions | Same as RM17TG00 ¦ ,Phase lost , Same as RM17TG00 ¦ ,Phase sequence, Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG00 ¦ ,Over voltage, Same as RM17TG00 ¦ ,Undervoltage , Same as RM17TG00 ¦ ,Phase asymmetry, Same as RM17TG00 ¦ ,Disconnection of neutral, Same as RM17TG00 ¦ ,Voltage Regeneration, Same as RM17TG00 ¦ ,Extreme undervoltage, Same as RM17TG00 ¦ ,Extreme overvoltage, Same as RM17TG00 ¦ ,Extreme asymmetry,
84873029mounting position | Same as RM17TG00 ¦ ,In relation to normal vertical mounting plane,
84873029mounting support | Same as RM17TG00 ¦ IEC/EN 60715,Without socket, Same as RM17TG00 ¦ IEC/EN 60715,With socket,
84873029net weight | Same as RM17TG00
84873029on-load factor | Same as RM17TG00
84873029output logic | Same as RM17TG00 ¦ ,R1 (11-12-14), Same as RM17TG00 ¦ ,R2 (21-22-24),
84873029output terminal | Same as RM17TG00
84873029output type | Same as RM17TG00
84873029overvoltage category | Same as RM17TG00 ¦ IEC60664-1
84873029permissible input overload | Same as RM17TG00 ¦ ,permissible input overload,
84873029polarity | Same as RM17TG00
84873029pollution degree | Same as RM17TG00 ¦ IEC60664-1
84873029power consumption | Same as RM17TG00
84873029power on delay | Same as RM17TG00
84873029product certifications | UL, CSA, CCC, CE, China ROHS
84873029relative humidity | Same as RM17TG00 ¦ IEC60068-2-30,Damp heat,XX
84873029release of input voltage | Same as RM17TG00
84873029repeat accuracy of the switching threshold | Same as RM17TG00 ¦ ,Repeat accuracy (constant parameters),
84873029repeat accuracy of time delay | Same as RM17TG00
84873029reset time | Same as RM17TG00 ¦ ,through Un power reset, Same as RM17TG00 ¦ ,through front panel reset, Same as RM17TG00 ¦ ,through input control reset,
84873029response time | Same as RM17TG00 ¦ ,on crossing the threshold, Same as RM17TG00 Same as RM17TG00 Same as RM17TG00 Same as RM17TG00
84873029safety reliability data | Same as RM17TG00 ¦ ,MTTF, Same as RM17TG00 ¦ ,B10,
84873029seismic resistance | Same as RM17TG00 ¦ IEC60068-3-3
84873029setting accuracy of the switching threshold | Same as RM17TG00 ¦ ,Setting accuracy,
84873029setting accuracy of time delay | Same as RM17TG00
84873029shock resistance | Same as RM17TG00 ¦ IEC60068-2-27
84873029short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17TG00 ¦ IEC62314,Solid State Output by external fuse,
84873029standards | Same as RM17TG00
84873029status LED | Same as RM17TG00
84873029supply frequency | Same as RM17TG00 Same as RM17TG00
84873029supply terminal | Same as RM17TG00
84873029supply voltage limits | Same as RM17TG00
84873029switching threshold drift | Same as RM17TG00 ¦ ,Measurement error with supply voltage variation, Same as RM17TG00 ¦ ,Measurement error with temperature variation,
84873029thermal current | 8A ¦ IEC60947-5-1
84873029tightening torque | Same as RM17TG00 ¦ IEC60947-1,Tightening torque,
84873029time delay drift | Same as RM17TG00 Same as RM17TG00
84873029time delay range | Same as RM17TG00 ¦ ,"OFF" delay, Same as RM17TG00 ¦ ,"ON" delay, Same as RM17TG00 ¦ ,Inhibition,
84873029time delay type | Same as RM17TG00 ¦ ,"OFF" delay, Same as RM17TG00 ¦ ,"ON" delay, Same as RM17TG00 ¦ ,Inhibition,
84873029tripping threshold | Same as RM17TG00 ¦ ,Phase cut, Same as RM17TG00 ¦ ,Phase sequence, Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG00 ¦ ,Over voltage, Same as RM17TG00 ¦ ,Undervoltage , Same as RM17TG00 ¦ ,Phase asymmetry, Same as RM17TG00 ¦ ,Disconnection of neutral, Same as RM17TG00 ¦ ,Voltage Regeneration, Same as RM17TG00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TG00 ¦ ,Extreme Overvoltage, Same as RM17TG00 ¦ ,Extreme Asymmetry,
84873029vibration resistance | Same as RM17TG00 ¦ IEC60068-2-6
84873029width | Same as RM17TG00 ¦ ,Width,
84873034 | Same as RM17TG20 ¦ IEC60721-3-3,Climatic category, Same as RM17TG20 ¦ Germanisher Lloyd,Environmental category, - ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM17TG20 ¦ ,Supply,Rated Same as RM17TG20 ¦ ,Input 1,Voltage Same as RM17TG20 ¦ ,Input 2,Spec Same as RM17TG20 ¦ ,Input 3, Same as RM17TG20 ¦ ,Output 1, Same as RM17TG20 ¦ ,Output 2, Same as RM17TG20 ¦ ,Measurement mode, Same as RM17TG20 Same as RM17TG20 Same as RM17TG20 Same as RM17TG20 Same as RM17TG20 ¦ ,MTTFd, Same as RM17TG20 ¦ ,B10d, Drawing / Diagram
84873034 (Catch-Up Juret - Actual) | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, Not specified ¦ IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, MTTFd, B10d,
84873034 (Catch-Up Juret - Actual)IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP40 ¦ IEC60529,Front Panel,
84873034 (Catch-Up Juret - Actual)Input nominal voltage selection | Fixed @ ~ 3 x 183…3 x 528 ¦ ,Input nominal voltage selection,
84873034 (Catch-Up Juret - Actual)Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
84873034 (Catch-Up Juret - Actual)[Ie] rated operational current | IEC61810-1,Rated switching current,
84873034 (Catch-Up Juret - Actual)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
84873034 (Catch-Up Juret - Actual)[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
84873034 (Catch-Up Juret - Actual)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
84873034 (Catch-Up Juret - Actual)[Us] rated supply voltage | ~ 3 x 208…3 x 480
84873034 (Catch-Up Juret - Actual)ambient air temperature for operation | -20…+50 ¦ ,Operation,
84873034 (Catch-Up Juret - Actual)ambient air temperature for storage | -30…+70 ¦ ,Storage,
84873034 (Catch-Up Juret - Actual)bump resistance | IEC60068-2-29
84873034 (Catch-Up Juret - Actual)cable stripping length | Not specified ¦ ,Cable stripping length,
84873034 (Catch-Up Juret - Actual)circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
84873034 (Catch-Up Juret - Actual)connections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
84873034 (Catch-Up Juret - Actual)contacts material | Cadmium free
84873034 (Catch-Up Juret - Actual)depth | Depth,
84873034 (Catch-Up Juret - Actual)diagnostic button
84873034 (Catch-Up Juret - Actual)dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
84873034 (Catch-Up Juret - Actual)directives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
84873034 (Catch-Up Juret - Actual)duty time | Not specified
84873034 (Catch-Up Juret - Actual)electrical durability | 1 x 104 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
84873034 (Catch-Up Juret - Actual)electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (Supply: 2kV, 5kHx / 100kHz) (I/O: 2kV, 5kHx / 100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, - ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, - ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 2 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, - ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 2 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
84873034 (Catch-Up Juret - Actual)height | Height,
84873034 (Catch-Up Juret - Actual)hysteresis | - ¦ ,Phase cut, (L2-L1) leads (L3-L1) >=15o or (L2-L1) leads (L3-L1) =< 135o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
84873034 (Catch-Up Juret - Actual)immunity to microbreaks | 10
84873034 (Catch-Up Juret - Actual)input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
84873034 (Catch-Up Juret - Actual)input terminal | L1-L2-L3 ¦ ,Input terminal,
84873034 (Catch-Up Juret - Actual)insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
84873034 (Catch-Up Juret - Actual)internal input resistance | Not specified ¦ ,Internal input resistance,
84873034 (Catch-Up Juret - Actual)local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Phase Cut, Phase Sequence Swap, Undervoltage <U, Overvoltage >U, Phase Asymmetry, Voltage Regeneration, Extreme Undervoltage <U (Phase loss), Extreme Overvoltage >U, Extreme Phase Asymmetry,
84873034 (Catch-Up Juret - Actual)marking | UL, CSA, CE, EAC
84873034 (Catch-Up Juret - Actual)maximum leakage current | IEC62314,Only for solid state output,
84873034 (Catch-Up Juret - Actual)maximum measuring cycle | Not specified ¦ ,Maximum measuring cycles,
84873034 (Catch-Up Juret - Actual)maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 8 ¦ ,Maximum switching current, 2000 ¦ ,Maximum switching capacity,
84873034 (Catch-Up Juret - Actual)maximum voltage drop | IEC62314,Only for solid state output,
84873034 (Catch-Up Juret - Actual)measurement method | Not specified ¦ ,Measurement method,
84873034 (Catch-Up Juret - Actual)measurement range | Fixed value ¦ ,Phase lost , Fixed value ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme Overvoltage, Extreme Asymmetry,
84873034 (Catch-Up Juret - Actual)mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
84873034 (Catch-Up Juret - Actual)minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
84873034 (Catch-Up Juret - Actual)monitoring functions | · ¦ ,Phase lost , · ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry,
84873034 (Catch-Up Juret - Actual)mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
84873034 (Catch-Up Juret - Actual)mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
84873034 (Catch-Up Juret - Actual)net weight | ?
84873034 (Catch-Up Juret - Actual)on-load factor
84873034 (Catch-Up Juret - Actual)output logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
84873034 (Catch-Up Juret - Actual)output terminal | 11-12-14, 21-22-24
84873034 (Catch-Up Juret - Actual)output type | 2 x C/O relay contacts
84873034 (Catch-Up Juret - Actual)overvoltage category | IEC60664-1
84873034 (Catch-Up Juret - Actual)permissible input overload | Not specified ¦ ,permissible input overload,
84873034 (Catch-Up Juret - Actual)polarity
84873034 (Catch-Up Juret - Actual)pollution degree | IEC60664-1
84873034 (Catch-Up Juret - Actual)power consumption | 25
84873034 (Catch-Up Juret - Actual)power on delay | 0
84873034 (Catch-Up Juret - Actual)product certifications | UL, CSA, CE, EAC
84873034 (Catch-Up Juret - Actual)relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
84873034 (Catch-Up Juret - Actual)release of input voltage
84873034 (Catch-Up Juret - Actual)repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
84873034 (Catch-Up Juret - Actual)repeat accuracy of time delay | -
84873034 (Catch-Up Juret - Actual)reset time | - ¦ ,through Un power reset, through front panel reset, through input control reset,
84873034 (Catch-Up Juret - Actual)response time | 0
84873034 (Catch-Up Juret - Actual)safety reliability data | MTTF, B10,
84873034 (Catch-Up Juret - Actual)seismic resistance | IEC60068-3-3
84873034 (Catch-Up Juret - Actual)setting accuracy of the switching threshold | - ¦ ,Setting accuracy,
84873034 (Catch-Up Juret - Actual)setting accuracy of time delay | -
84873034 (Catch-Up Juret - Actual)shock resistance | 15gn - 11ms ¦ IEC60068-2-27
84873034 (Catch-Up Juret - Actual)short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
84873034 (Catch-Up Juret - Actual)standards | EN60255-1, IEC60255-1
84873034 (Catch-Up Juret - Actual)status LED
84873034 (Catch-Up Juret - Actual)supply frequency | 50 / 60 45…66
84873034 (Catch-Up Juret - Actual)supply terminal | L1-L3
84873034 (Catch-Up Juret - Actual)supply voltage limits | ~ 3 x 183…3 x 528
84873034 (Catch-Up Juret - Actual)switching threshold drift | < 1% over whole range ¦ ,Measurement error with supply voltage variation, 0.05% / oC ¦ ,Measurement error with temperature variation,
84873034 (Catch-Up Juret - Actual)thermal current | IEC60947-5-1
84873034 (Catch-Up Juret - Actual)tightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
84873034 (Catch-Up Juret - Actual)time delay drift | - -
84873034 (Catch-Up Juret - Actual)time delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
84873034 (Catch-Up Juret - Actual)time delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
84873034 (Catch-Up Juret - Actual)tripping threshold | (L2-L1) or (L3-L1) or (L2-L3) < 100 ¦ ,Phase cut, (L2-L1) leads (L3-L1) < 10o or (L2-L1) leads (L3-L1) > 150o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
84873034 (Catch-Up Juret - Actual)vibration resistance | ±0.35mm from 5Hz…57.6Hz 1g from 57.6Hz..150Hz ¦ IEC60068-2-6
84873034 (Catch-Up Juret - Actual)width | 22.5 x 90 x 73 ¦ ,Width,
84873034 (Catch-Up Juret - For Crouzet) | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, Not specified ¦ IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, MTTFd, B10d,
84873034 (Catch-Up Juret - For Crouzet)IP degree of protection | IP40 ¦ IEC60529,Terminal Block, IP20 ¦ IEC60529,Housing, Not specified ¦ IEC60529,Front Panel,
84873034 (Catch-Up Juret - For Crouzet)Input nominal voltage selection | Fixed @ ~ 3 x 230…3 x 440 ¦ ,Input nominal voltage selection,
84873034 (Catch-Up Juret - For Crouzet)Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
84873034 (Catch-Up Juret - For Crouzet)[Ie] rated operational current | IEC61810-1,Rated switching current,
84873034 (Catch-Up Juret - For Crouzet)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
84873034 (Catch-Up Juret - For Crouzet)[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
84873034 (Catch-Up Juret - For Crouzet)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
84873034 (Catch-Up Juret - For Crouzet)[Us] rated supply voltage | ~ 3 x 230…3 x 440
84873034 (Catch-Up Juret - For Crouzet)ambient air temperature for operation | -20…+50 ¦ ,Operation,
84873034 (Catch-Up Juret - For Crouzet)ambient air temperature for storage | -30…+70 ¦ ,Storage,
84873034 (Catch-Up Juret - For Crouzet)bump resistance | IEC60068-2-29
84873034 (Catch-Up Juret - For Crouzet)cable stripping length | Not specified ¦ ,Cable stripping length,
84873034 (Catch-Up Juret - For Crouzet)circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
84873034 (Catch-Up Juret - For Crouzet)connections - terminals | 1 conductor:0.5…4 2 conductor:0.5…2.5 ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor:0.2…2.5 2 conductor:0.2…1.5 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
84873034 (Catch-Up Juret - For Crouzet)contacts material | Cadmium free
84873034 (Catch-Up Juret - For Crouzet)depth | Depth,
84873034 (Catch-Up Juret - For Crouzet)diagnostic button
84873034 (Catch-Up Juret - For Crouzet)dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
84873034 (Catch-Up Juret - For Crouzet)directives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
84873034 (Catch-Up Juret - For Crouzet)duty time | Not specified
84873034 (Catch-Up Juret - For Crouzet)electrical durability | 1 x 104 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
84873034 (Catch-Up Juret - For Crouzet)electromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, - ¦ IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, - ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
84873034 (Catch-Up Juret - For Crouzet)height | Height,
84873034 (Catch-Up Juret - For Crouzet)hysteresis | Not specified ¦ ,Phase cut, (L2-L1) leads (L3-L1) >=15o or (L2-L1) leads (L3-L1) =< 135o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
84873034 (Catch-Up Juret - For Crouzet)immunity to microbreaks
84873034 (Catch-Up Juret - For Crouzet)input frequency | 50 / 60 ¦ ,Rated frequency, 49…61 ¦ ,Frequency operating range,
84873034 (Catch-Up Juret - For Crouzet)input terminal | L1-L2-L3 ¦ ,Input terminal,
84873034 (Catch-Up Juret - For Crouzet)insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
84873034 (Catch-Up Juret - For Crouzet)internal input resistance | - ¦ ,Internal input resistance,
84873034 (Catch-Up Juret - For Crouzet)local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Phase Cut, Phase Sequence Swap, Undervoltage <U, Overvoltage >U, Phase Asymmetry, Voltage Regeneration, Extreme Undervoltage <U (Phase loss), Extreme Overvoltage >U, Extreme Phase Asymmetry,
84873034 (Catch-Up Juret - For Crouzet)marking | UL, CSA, CE, EAC
84873034 (Catch-Up Juret - For Crouzet)maximum leakage current | - ¦ IEC62314,Only for solid state output,
84873034 (Catch-Up Juret - For Crouzet)maximum measuring cycle | Not specified ¦ ,Maximum measuring cycles,
84873034 (Catch-Up Juret - For Crouzet)maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 8 ¦ ,Maximum switching current, 2000 ¦ ,Maximum switching capacity,
84873034 (Catch-Up Juret - For Crouzet)maximum voltage drop | - ¦ IEC62314,Only for solid state output,
84873034 (Catch-Up Juret - For Crouzet)measurement method | Not specified ¦ ,Measurement method,
84873034 (Catch-Up Juret - For Crouzet)measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme Overvoltage, Extreme Asymmetry,
84873034 (Catch-Up Juret - For Crouzet)mechanical durability | 20 x 106 switching cycles ¦ IEC61810-1
84873034 (Catch-Up Juret - For Crouzet)minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
84873034 (Catch-Up Juret - For Crouzet)monitoring functions | · ¦ ,Phase lost , · ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry,
84873034 (Catch-Up Juret - For Crouzet)mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
84873034 (Catch-Up Juret - For Crouzet)mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
84873034 (Catch-Up Juret - For Crouzet)net weight | To be updated
84873034 (Catch-Up Juret - For Crouzet)on-load factor | Not specified
84873034 (Catch-Up Juret - For Crouzet)output logic | Energized on fault-free ¦ ,R1 (11-12-14), - ¦ ,R2 (21-22-24),
84873034 (Catch-Up Juret - For Crouzet)output terminal | 11-12-14, 21-22-24
84873034 (Catch-Up Juret - For Crouzet)output type | 2 x C/O relay contacts
84873034 (Catch-Up Juret - For Crouzet)overvoltage category | IEC60664-1
84873034 (Catch-Up Juret - For Crouzet)permissible input overload | Not specified ¦ ,permissible input overload,
84873034 (Catch-Up Juret - For Crouzet)polarity
84873034 (Catch-Up Juret - For Crouzet)pollution degree | IEC60664-1
84873034 (Catch-Up Juret - For Crouzet)power consumption | 25
84873034 (Catch-Up Juret - For Crouzet)power on delay | 0
84873034 (Catch-Up Juret - For Crouzet)product certifications | UL, CSA, CE, EAC
84873034 (Catch-Up Juret - For Crouzet)relative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,XX
84873034 (Catch-Up Juret - For Crouzet)release of input voltage | Not specified
84873034 (Catch-Up Juret - For Crouzet)repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
84873034 (Catch-Up Juret - For Crouzet)repeat accuracy of time delay | -
84873034 (Catch-Up Juret - For Crouzet)reset time | - ¦ ,through Un power reset, through front panel reset, through input control reset,
84873034 (Catch-Up Juret - For Crouzet)response time | 0
84873034 (Catch-Up Juret - For Crouzet)safety reliability data | MTTF, B10,
84873034 (Catch-Up Juret - For Crouzet)seismic resistance | IEC60068-3-3
84873034 (Catch-Up Juret - For Crouzet)setting accuracy of the switching threshold | - ¦ ,Setting accuracy,
84873034 (Catch-Up Juret - For Crouzet)setting accuracy of time delay | -
84873034 (Catch-Up Juret - For Crouzet)shock resistance | 5 gn ¦ IEC60068-2-27
84873034 (Catch-Up Juret - For Crouzet)short circuit protection | - ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
84873034 (Catch-Up Juret - For Crouzet)standards | EN60255-1, IEC60255-1
84873034 (Catch-Up Juret - For Crouzet)status LED
84873034 (Catch-Up Juret - For Crouzet)supply frequency | 50 / 60 49…61
84873034 (Catch-Up Juret - For Crouzet)supply terminal | L1-L3
84873034 (Catch-Up Juret - For Crouzet)supply voltage limits | ~ 3 x 207…3 x 484
84873034 (Catch-Up Juret - For Crouzet)switching threshold drift | < 1% over whole range ¦ ,Measurement error with supply voltage variation, 0.05% / oC ¦ ,Measurement error with temperature variation,
84873034 (Catch-Up Juret - For Crouzet)thermal current | - ¦ IEC60947-5-1
84873034 (Catch-Up Juret - For Crouzet)tightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
84873034 (Catch-Up Juret - For Crouzet)time delay drift | - -
84873034 (Catch-Up Juret - For Crouzet)time delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
84873034 (Catch-Up Juret - For Crouzet)time delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
84873034 (Catch-Up Juret - For Crouzet)tripping threshold | (L2-L1) or (L3-L1) or (L2-L3) < 100 ¦ ,Phase cut, (L2-L1) leads (L3-L1) < 10o or (L2-L1) leads (L3-L1) > 150o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
84873034 (Catch-Up Juret - For Crouzet)vibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
84873034 (Catch-Up Juret - For Crouzet)width | 22.5 x 90 x 73 ¦ ,Width,
84873034IP degree of protection | Same as RM17TG20 ¦ IEC60529,Terminal Block, Same as RM17TG20 ¦ IEC60529,Housing, Same as RM17TG20 ¦ IEC60529,Front Panel,
84873034Input nominal voltage selection | Same as RM17TG21 ¦ ,Input nominal voltage selection,
84873034Minimum distance to adjacent devices | Same as RM17TG20 ¦ ,Horizontal, Same as RM17TG20 ¦ ,Vertical,
84873034[Ie] rated operational current | Same as RM17TG20 ¦ IEC61810-1,Rated switching current,
84873034[Ue] rated operational voltage | Same as RM17TG20 ¦ IEC61810-1,Rated switching voltage,
84873034[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply, Same as RM17TG20 ¦ IEC60664-1,Input 1, Same as RM17TG20 ¦ IEC60664-1,Input 2, Same as RM17TG20 ¦ IEC60664-1,Input 3, Same as RM17TG20 ¦ IEC60664-1,Output 1, Same as RM17TG20 ¦ IEC60664-1,Output 2, Same as RM17TG20 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TG20 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TG20 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TG20 ¦ IEC60664-1,Supply / Output 1, Same as RM17TG20 ¦ IEC60664-1,Supply / Output 2, Same as RM17TG20 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 3,
84873034[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply, Same as RM17TG20 ¦ IEC60664-1,Input 1, Same as RM17TG20 ¦ IEC60664-1,Input 2, Same as RM17TG20 ¦ IEC60664-1,Input 3, Same as RM17TG20 ¦ IEC60664-1,Output 1, Same as RM17TG20 ¦ IEC60664-1,Output 2, Same as RM17TG20 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TG20 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TG20 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TG20 ¦ IEC60664-1,Supply / Output 1, Same as RM17TG20 ¦ IEC60664-1,Supply / Output 2, Same as RM17TG20 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 3,
84873034[Us] rated supply voltage | ~ 3 x 230…3 x 440
84873034ambient air temperature for operation | Same as RM17TG20 ¦ ,Operation,
84873034ambient air temperature for storage | -30oC..+70oC ¦ ,Storage,
84873034bump resistance | Same as RM17TG20 ¦ IEC60068-2-29
84873034cable stripping length | Same as RM17TG20 ¦ ,Cable stripping length,
84873034circuit group | Same as RM17TG20 ¦ ,Supply,Terminal Same as RM17TG20 ¦ ,Input 1, Same as RM17TG20 ¦ ,Input 2, Same as RM17TG20 ¦ ,Input 3, Same as RM17TG20 ¦ ,Output 1, Same as RM17TG20 ¦ ,Output 2,
84873034connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17TG20 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17TG20 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17TG20 ¦ IEC60947-1,Flexible cable (spring terminal),
84873034contacts material | Same as RM17TG20
84873034depth | 73 ¦ ,Depth,
84873034diagnostic button | Same as RM17TG20
84873034dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 1, Same as RM17TG20 ¦ IEC60255-27,Supply / Input 2, Same as RM17TG20 ¦ IEC60255-27,Supply / Input 3, Same as RM17TG20 ¦ IEC60255-27,Supply / Output 1, Same as RM17TG20 ¦ IEC60255-27,Supply / Output 2, Same as RM17TG20 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 3,
84873034directives | Same as RM17TG20 Same as RM17TG20 Same as RM17TG20
84873034duty time | Same as RM17TG20
84873034electrical durability | Same as RM17TG20 ¦ IEC60947-4-1,AC-1, Same as RM17TG20 ¦ IEC60947-4-1,DC-1, Same as RM17TG20 ¦ IEC60947-5-1,AC-15, Same as RM17TG20 ¦ IEC60947-5-1,DC-13,
84873034electromagnetic compatibility | Same as RM17TG20 ¦ ,Generic immunity standard, Same as RM17TG20 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17TG20 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17TG20 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17TG20 ¦ IEC61000-4-5,Surge, Same as RM17TG20 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17TG20 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17TG20 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17TG20 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17TG20 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17TG20 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM17TG20 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17TG20 ¦ ,Generic emission standard, Same as RM17TG20 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17TG20 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17TG20 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17TG20 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17TG20 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17TG20 ¦ Germanisher Lloyd,Conducted emission,
84873034height | 90 ¦ ,Height,
84873034hysteresis | Same as RM17TG20 ¦ ,Phase cut, Same as RM17TG20 ¦ ,Phase sequence, Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG20 ¦ ,Over voltage, Same as RM17TG20 ¦ ,Undervoltage , Same as RM17TG20 ¦ ,Phase asymmetry, Same as RM17TG20 ¦ ,Disconnection of neutral, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TG20 ¦ ,Extreme Overvoltage, Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873034immunity to microbreaks | Same as RM17TG20
84873034input frequency | Same as RM17TG20 ¦ ,Rated frequency, Same as RM17TG20 ¦ ,Frequency operating range,
84873034input terminal | Same as RM17TG20 ¦ ,Input terminal,
84873034insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 1, Same as RM17TG20 ¦ IEC60255-27,Supply / Input 2, Same as RM17TG20 ¦ IEC60255-27,Supply / Input 3, Same as RM17TG20 ¦ IEC60255-27,Supply / Output 1, Same as RM17TG20 ¦ IEC60255-27,Supply / Output 2, Same as RM17TG20 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 3,
84873034internal input resistance | Same as RM17TG20 ¦ ,Internal input resistance,
84873034local signalling | - ¦ ,Power supply availability, - ¦ ,Power supply not availability, - ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, - ¦ ,Range Setting Changes, Same as RM17TG20 ¦ ,Phase Cut, Same as RM17TG20 ¦ ,Phase Sequence Swap, Same as RM17TG20 ¦ ,Undervoltage <U, Same as RM17TG20 ¦ ,Overvoltage >U, Same as RM17TG20 ¦ ,Phase Asymmetry, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17TG20 ¦ ,Extreme Overvoltage >U, Same as RM17TG20 ¦ ,Extreme Phase Asymmetry,
84873034marking | UL, CE, China ROHS
84873034maximum leakage current | Same as RM17TG20 ¦ IEC62314,Only for solid state output,
84873034maximum measuring cycle | Same as RM17TG20 ¦ ,Maximum measuring cycles,
84873034maximum switching capacity | Same as RM17TG20 ¦ ,Maximum switching voltage, Same as RM17TG20 ¦ ,Maximum switching current, Same as RM17TG20 ¦ ,Maximum switching capacity,
84873034maximum voltage drop | Same as RM17TG20 ¦ IEC62314,Only for solid state output,
84873034measurement method | Same as RM17TG20 ¦ ,Measurement method,
84873034measurement range | Same as RM17TG20 ¦ ,Phase lost , Same as RM17TG20 ¦ ,Phase sequence, Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG20 ¦ ,Over voltage, Same as RM17TG20 ¦ ,Undervoltage , Same as RM17TG20 ¦ ,Phase asymmetry, Same as RM17TG20 ¦ ,Disconnection of neutral, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme undervoltage, Same as RM17TG20 ¦ ,Extreme Overvoltage, Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873034mechanical durability | Same as RM17TG20 ¦ IEC61810-1
84873034minimum switching capacity | Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching current, Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching capacity,
84873034monitoring functions | Same as RM17TG20 ¦ ,Phase lost , Same as RM17TG20 ¦ ,Phase sequence, Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG20 ¦ ,Over voltage, Same as RM17TG20 ¦ ,Undervoltage , Same as RM17TG20 ¦ ,Phase asymmetry, Same as RM17TG20 ¦ ,Disconnection of neutral, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme undervoltage, Same as RM17TG20 ¦ ,Extreme overvoltage, Same as RM17TG20 ¦ ,Extreme asymmetry,
84873034mounting position | Same as RM17TG20 ¦ ,In relation to normal vertical mounting plane,
84873034mounting support | Same as RM17TG20 ¦ IEC/EN 60715,Without socket, Same as RM17TG20 ¦ IEC/EN 60715,With socket,
84873034net weight | Same as RM17TG20
84873034on-load factor | Same as RM17TG20
84873034output logic | Same as RM17TG20 ¦ ,R1 (11-12-14), Same as RM17TG20 ¦ ,R2 (21-22-24),
84873034output terminal | Same as RM17TG20
84873034output type | Same as RM17TG20
84873034overvoltage category | Same as RM17TG20 ¦ IEC60664-1
84873034permissible input overload | Same as RM17TG22 ¦ ,permissible input overload,
84873034polarity | -
84873034pollution degree | Same as RM17TG20 ¦ IEC60664-1
84873034power consumption | Same as RM17TG20
84873034power on delay | Same as RM17TG20
84873034product certifications | UL, CE, China ROHS
84873034relative humidity | Same as RM17TG20 ¦ IEC60068-2-30,Damp heat,XX
84873034release of input voltage | Same as RM17TG20
84873034repeat accuracy of the switching threshold | Same as RM17TG20 ¦ ,Repeat accuracy (constant parameters),
84873034repeat accuracy of time delay | Same as RM17TG20
84873034reset time | Same as RM17TG20 ¦ ,through Un power reset, Same as RM17TG20 ¦ ,through front panel reset, Same as RM17TG20 ¦ ,through input control reset,
84873034response time | Same as RM17TG20 ¦ ,on crossing the threshold, Same as RM17TG20 Same as RM17TG20 Same as RM17TG20 Same as RM17TG20
84873034safety reliability data | Same as RM17TG20 ¦ ,MTTF, Same as RM17TG20 ¦ ,B10,
84873034seismic resistance | Same as RM17TG20 ¦ IEC60068-3-3
84873034setting accuracy of the switching threshold | Same as RM17TG20 ¦ ,Setting accuracy,
84873034setting accuracy of time delay | Same as RM17TG20
84873034shock resistance | Same as RM17TG20 ¦ IEC60068-2-27
84873034short circuit protection | Same as RM17TG20 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17TG20 ¦ IEC62314,Solid State Output by external fuse,
84873034standards | Same as RM17TG20
84873034status LED | R (Amber)
84873034supply frequency | Same as RM17TG20 Same as RM17TG20
84873034supply terminal | Same as RM17TG20
84873034supply voltage limits | ~ 3 x 200…3 x 460
84873034switching threshold drift | Same as RM17TG20 ¦ ,Measurement error with supply voltage variation, Same as RM17TG20 ¦ ,Measurement error with temperature variation,
84873034thermal current | Same as RM17TG20 ¦ IEC60947-5-1
84873034tightening torque | Same as RM17TG20 ¦ IEC60947-1,Tightening torque,
84873034time delay drift | Same as RM17TG20 Same as RM17TG20
84873034time delay range | Same as RM17TG20 ¦ ,"OFF" delay, Same as RM17TG20 ¦ ,"ON" delay, Same as RM17TG20 ¦ ,Inhibition,
84873034time delay type | Same as RM17TG20 ¦ ,"OFF" delay, Same as RM17TG20 ¦ ,"ON" delay, Same as RM17TG20 ¦ ,Inhibition,
84873034tripping threshold | Same as RM17TG20 ¦ ,Phase cut, Same as RM17TG20 ¦ ,Phase sequence, Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG20 ¦ ,Over voltage, Same as RM17TG20 ¦ ,Undervoltage , Same as RM17TG20 ¦ ,Phase asymmetry, Same as RM17TG20 ¦ ,Disconnection of neutral, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TG20 ¦ ,Extreme Overvoltage, Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873034vibration resistance | Same as RM17TG20 ¦ IEC60068-2-6
84873034width | 22.5 ¦ ,Width,
84873195 | Same as 84873034 ¦ IEC60721-3-3,Climatic category, Same as 84873034 ¦ Germanisher Lloyd,Environmental category, Same as 84873034 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as 84873034 ¦ ,Supply,Rated Same as 84873034 ¦ ,Input 1,Voltage Same as 84873034 ¦ ,Input 2,Spec Same as 84873034 ¦ ,Input 3, Same as 84873034 ¦ ,Output 1, Same as 84873034 ¦ ,Output 2, Same as 84873034 ¦ ,Measurement mode, Same as 84873034 Same as 84873034 Same as 84873034 Same as 84873034 Same as 84873034 ¦ ,MTTFd, Same as 84873034 ¦ ,B10d, Drawing / Diagram
84873195IP degree of protection | Same as 84873034 ¦ IEC60529,Terminal Block, Same as 84873034 ¦ IEC60529,Housing, Same as 84873034 ¦ IEC60529,Front Panel,
84873195Input nominal voltage selection | Same as 84873034 ¦ ,Input nominal voltage selection,
84873195Minimum distance to adjacent devices | Same as 84873034 ¦ ,Horizontal, Same as 84873034 ¦ ,Vertical,
84873195[Ie] rated operational current | Same as 84873034 ¦ IEC61810-1,Rated switching current,
84873195[Ue] rated operational voltage | Same as 84873034 ¦ IEC61810-1,Rated switching voltage,
84873195[Ui] rated insulation voltage | Same as 84873034 ¦ IEC60664-1,Supply, Same as 84873034 ¦ IEC60664-1,Input 1, Same as 84873034 ¦ IEC60664-1,Input 2, Same as 84873034 ¦ IEC60664-1,Input 3, Same as 84873034 ¦ IEC60664-1,Output 1, Same as 84873034 ¦ IEC60664-1,Output 2, Same as 84873034 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as 84873034 ¦ IEC60664-1,Supply / Input 2,Isolated Same as 84873034 ¦ IEC60664-1,Supply / Input 3,Circuit Same as 84873034 ¦ IEC60664-1,Supply / Output 1, Same as 84873034 ¦ IEC60664-1,Supply / Output 2, Same as 84873034 ¦ IEC60664-1,Output 1 / Output 2, Same as 84873034 ¦ IEC60664-1,Input 1 / Output 1, Same as 84873034 ¦ IEC60664-1,Input 1 / Output 2, Same as 84873034 ¦ IEC60664-1,Input 2 / Output 1, Same as 84873034 ¦ IEC60664-1,Input 2 / Output 2, Same as 84873034 ¦ IEC60664-1,Input 3 / Output 1, Same as 84873034 ¦ IEC60664-1,Input 3 / Output 2, Same as 84873034 ¦ IEC60664-1,Input 1 / Input 2, Same as 84873034 ¦ IEC60664-1,Input 2 / Input 3, Same as 84873034 ¦ IEC60664-1,Input 1 / Input 3,
84873195[Uimp] rated impulse withstand voltage | Same as 84873034 ¦ IEC60664-1,Supply, Same as 84873034 ¦ IEC60664-1,Input 1, Same as 84873034 ¦ IEC60664-1,Input 2, Same as 84873034 ¦ IEC60664-1,Input 3, Same as 84873034 ¦ IEC60664-1,Output 1, Same as 84873034 ¦ IEC60664-1,Output 2, Same as 84873034 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as 84873034 ¦ IEC60664-1,Supply / Input 2,Isolated Same as 84873034 ¦ IEC60664-1,Supply / Input 3,Circuit Same as 84873034 ¦ IEC60664-1,Supply / Output 1, Same as 84873034 ¦ IEC60664-1,Supply / Output 2, Same as 84873034 ¦ IEC60664-1,Output 1 / Output 2, Same as 84873034 ¦ IEC60664-1,Input 1 / Output 1, Same as 84873034 ¦ IEC60664-1,Input 1 / Output 2, Same as 84873034 ¦ IEC60664-1,Input 2 / Output 1, Same as 84873034 ¦ IEC60664-1,Input 2 / Output 2, Same as 84873034 ¦ IEC60664-1,Input 3 / Output 1, Same as 84873034 ¦ IEC60664-1,Input 3 / Output 2, Same as 84873034 ¦ IEC60664-1,Input 1 / Input 2, Same as 84873034 ¦ IEC60664-1,Input 2 / Input 3, Same as 84873034 ¦ IEC60664-1,Input 1 / Input 3,
84873195[Us] rated supply voltage | Same as 84873034
84873195ambient air temperature for operation | Same as 84873034 ¦ ,Operation,
84873195ambient air temperature for storage | Same as 84873034 ¦ ,Storage,
84873195bump resistance | Same as 84873034 ¦ IEC60068-2-29
84873195cable stripping length | Same as 84873034 ¦ ,Cable stripping length,
84873195circuit group | Same as 84873034 ¦ ,Supply,Terminal Same as 84873034 ¦ ,Input 1, Same as 84873034 ¦ ,Input 2, Same as 84873034 ¦ ,Input 3, Same as 84873034 ¦ ,Output 1, Same as 84873034 ¦ ,Output 2,
84873195connections - terminals | Same as 84873034 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as 84873034 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as 84873034 ¦ IEC60947-1,Solid cable (spring terminal), Same as 84873034 ¦ IEC60947-1,Flexible cable (spring terminal),
84873195contacts material | Same as 84873034
84873195depth | Same as 84873034 ¦ ,Depth,
84873195diagnostic button | Same as 84873034
84873195dielectric strength | Same as 84873034 ¦ IEC60255-27,Supply / Input 1, Same as 84873034 ¦ IEC60255-27,Supply / Input 2, Same as 84873034 ¦ IEC60255-27,Supply / Input 3, Same as 84873034 ¦ IEC60255-27,Supply / Output 1, Same as 84873034 ¦ IEC60255-27,Supply / Output 2, Same as 84873034 ¦ IEC60255-27,Output 1 / Output 2, Same as 84873034 ¦ IEC60255-27,Input 1 / Output 1, Same as 84873034 ¦ IEC60255-27,Input 1 / Output 2, Same as 84873034 ¦ IEC60255-27,Input 2 / Output 1, Same as 84873034 ¦ IEC60255-27,Input 2 / Output 2, Same as 84873034 ¦ IEC60255-27,Input 3 / Output 1, Same as 84873034 ¦ IEC60255-27,Input 3 / Output 2, Same as 84873034 ¦ IEC60255-27,Input 1 / Input 2, Same as 84873034 ¦ IEC60255-27,Input 2 / Input 3, Same as 84873034 ¦ IEC60255-27,Input 1 / Input 3,
84873195directives | Same as 84873034 Same as 84873034 Same as 84873034
84873195duty time | Same as 84873034
84873195electrical durability | Same as 84873034 ¦ IEC60947-4-1,AC-1, Same as 84873034 ¦ IEC60947-4-1,DC-1, Same as 84873034 ¦ IEC60947-5-1,AC-15, Same as 84873034 ¦ IEC60947-5-1,DC-13,
84873195electromagnetic compatibility | Same as 84873034 ¦ ,Generic immunity standard, Same as 84873034 ¦ IEC61000-4-2,Electrostatic discharge, Same as 84873034 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as 84873034 ¦ IEC61000-4-4,Fast transient / burst, Same as 84873034 ¦ IEC61000-4-5,Surge, Same as 84873034 ¦ IEC61000-4-6,Conducted RF disturbance, Same as 84873034 ¦ IEC61000-4-8,Power frequency magnetic field, Same as 84873034 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as 84873034 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as 84873034 ¦ IEC61000-4-29,DC voltage interruption, Same as 84873034 ¦ IEC61000-4-13,Low frequency harmonics, Same as 84873034 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as 84873034 ¦ ,Generic emission standard, Same as 84873034 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as 84873034 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as 84873034 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as 84873034 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as 84873034 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as 84873034 ¦ Germanisher Lloyd,Conducted emission,
84873195height | Same as 84873034 ¦ ,Height,
84873195hysteresis | Same as 84873034 ¦ ,Phase cut, Same as 84873034 ¦ ,Phase sequence, Same as 84873034 ¦ ,Over / undervoltage (symmetry windows mode), Same as 84873034 ¦ ,Over voltage, Same as 84873034 ¦ ,Undervoltage , Same as 84873034 ¦ ,Phase asymmetry, Same as 84873034 ¦ ,Disconnection of neutral, Same as 84873034 ¦ ,Voltage Regeneration, Same as 84873034 ¦ ,Extreme undervoltage (Phase loss), Same as 84873034 ¦ ,Extreme Overvoltage, Same as 84873034 ¦ ,Extreme Asymmetry,
84873195immunity to microbreaks | Same as 84873034
84873195input frequency | Same as 84873034 ¦ ,Rated frequency, Same as 84873034 ¦ ,Frequency operating range,
84873195input terminal | Same as 84873034 ¦ ,Input terminal,
84873195insulation resistance | Same as 84873034 ¦ IEC60255-27,Supply / Input 1, Same as 84873034 ¦ IEC60255-27,Supply / Input 2, Same as 84873034 ¦ IEC60255-27,Supply / Input 3, Same as 84873034 ¦ IEC60255-27,Supply / Output 1, Same as 84873034 ¦ IEC60255-27,Supply / Output 2, Same as 84873034 ¦ IEC60255-27,Output 1 / Output 2, Same as 84873034 ¦ IEC60255-27,Input 1 / Output 1, Same as 84873034 ¦ IEC60255-27,Input 1 / Output 2, Same as 84873034 ¦ IEC60255-27,Input 2 / Output 1, Same as 84873034 ¦ IEC60255-27,Input 2 / Output 2, Same as 84873034 ¦ IEC60255-27,Input 3 / Output 1, Same as 84873034 ¦ IEC60255-27,Input 3 / Output 2, Same as 84873034 ¦ IEC60255-27,Input 1 / Input 2, Same as 84873034 ¦ IEC60255-27,Input 2 / Input 3, Same as 84873034 ¦ IEC60255-27,Input 1 / Input 3,
84873195internal input resistance | Same as 84873034 ¦ ,Internal input resistance,
84873195local signalling | - ¦ ,Power supply availability, - ¦ ,Power supply not availability, - ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, - ¦ ,Range Setting Changes, Same as 84873034 ¦ ,Phase Cut, Same as 84873034 ¦ ,Phase Sequence Swap, Same as 84873034 ¦ ,Undervoltage <U, Same as 84873034 ¦ ,Overvoltage >U, Same as 84873034 ¦ ,Phase Asymmetry, Same as 84873034 ¦ ,Voltage Regeneration, Same as 84873034 ¦ ,Extreme Undervoltage <U (Phase loss), Same as 84873034 ¦ ,Extreme Overvoltage >U, Same as 84873034 ¦ ,Extreme Phase Asymmetry,
84873195marking | Same as 84873034
84873195maximum leakage current | Same as 84873034 ¦ IEC62314,Only for solid state output,
84873195maximum measuring cycle | Same as 84873034 ¦ ,Maximum measuring cycles,
84873195maximum switching capacity | Same as 84873034 ¦ ,Maximum switching voltage, Same as 84873034 ¦ ,Maximum switching current, Same as 84873034 ¦ ,Maximum switching capacity,
84873195maximum voltage drop | Same as 84873034 ¦ IEC62314,Only for solid state output,
84873195measurement method | Same as 84873034 ¦ ,Measurement method,
84873195measurement range | Same as 84873034 ¦ ,Phase lost , Same as 84873034 ¦ ,Phase sequence, Same as 84873034 ¦ ,Over / undervoltage (symmetry windows mode), Same as 84873034 ¦ ,Over voltage, Same as 84873034 ¦ ,Undervoltage , Same as 84873034 ¦ ,Phase asymmetry, Same as 84873034 ¦ ,Disconnection of neutral, Same as 84873034 ¦ ,Voltage Regeneration, Same as 84873034 ¦ ,Extreme undervoltage, Same as 84873034 ¦ ,Extreme Overvoltage, Same as 84873034 ¦ ,Extreme Asymmetry,
84873195mechanical durability | Same as 84873034 ¦ IEC61810-1
84873195minimum switching capacity | Same as 84873034 ¦ IEC60947-5-4,Minimum switching voltage, Same as 84873034 ¦ IEC60947-5-4,Minimum switching current, Same as 84873034 ¦ IEC60947-5-4,Minimum switching capacity,
84873195monitoring functions | Same as 84873034 ¦ ,Phase lost , Same as 84873034 ¦ ,Phase sequence, Same as 84873034 ¦ ,Over / undervoltage (symmetry windows mode), Same as 84873034 ¦ ,Over voltage, Same as 84873034 ¦ ,Undervoltage , Same as 84873034 ¦ ,Phase asymmetry, Same as 84873034 ¦ ,Disconnection of neutral, Same as 84873034 ¦ ,Voltage Regeneration, Same as 84873034 ¦ ,Extreme undervoltage, Same as 84873034 ¦ ,Extreme overvoltage, Same as 84873034 ¦ ,Extreme asymmetry,
84873195mounting position | Same as 84873034 ¦ ,In relation to normal vertical mounting plane,
84873195mounting support | Same as 84873034 ¦ IEC/EN 60715,Without socket, Same as 84873034 ¦ IEC/EN 60715,With socket,
84873195net weight | Same as 84873034
84873195on-load factor | Same as 84873034
84873195output logic | Same as 84873034 ¦ ,R1 (11-12-14), Same as 84873034 ¦ ,R2 (21-22-24),
84873195output terminal | Same as 84873034
84873195output type | Same as 84873034
84873195overvoltage category | Same as 84873034 ¦ IEC60664-1
84873195permissible input overload | Same as 84873034 ¦ ,permissible input overload,
84873195polarity | Same as 84873034
84873195pollution degree | Same as 84873034 ¦ IEC60664-1
84873195power consumption | 28VA @ 480VAC, 60Hz 18VA @ 415VAC, 50Hz
84873195power on delay | Same as 84873034
84873195product certifications | Same as 84873034
84873195relative humidity | Same as 84873034 ¦ IEC60068-2-30,Damp heat,XX
84873195release of input voltage | Same as 84873034
84873195repeat accuracy of the switching threshold | Same as 84873034 ¦ ,Repeat accuracy (constant parameters),
84873195repeat accuracy of time delay | Same as 84873034
84873195reset time | Same as 84873034 ¦ ,through Un power reset, Same as 84873034 ¦ ,through front panel reset, Same as 84873034 ¦ ,through input control reset,
84873195response time | Same as 84873034 ¦ ,on crossing the threshold, Same as 84873034 Same as 84873034 Same as 84873034 Same as 84873034
84873195safety reliability data | Same as 84873034 ¦ ,MTTF, Same as 84873034 ¦ ,B10,
84873195seismic resistance | Same as 84873034 ¦ IEC60068-3-3
84873195setting accuracy of the switching threshold | Same as 84873034 ¦ ,Setting accuracy,
84873195setting accuracy of time delay | Same as 84873034
84873195shock resistance | Same as 84873034 ¦ IEC60068-2-27
84873195short circuit protection | Same as 84873034 ¦ IEC60947-5-1,Relay Output by external fuse, Same as 84873034 ¦ IEC62314,Solid State Output by external fuse,
84873195standards | Same as 84873034
84873195status LED | Rel (Amber)
84873195supply frequency | Same as 84873034 Same as 84873034
84873195supply terminal | Same as 84873034
84873195supply voltage limits | Same as 84873034
84873195switching threshold drift | Same as 84873034 ¦ ,Measurement error with supply voltage variation, Same as 84873034 ¦ ,Measurement error with temperature variation,
84873195thermal current | Same as 84873034 ¦ IEC60947-5-1
84873195tightening torque | Same as 84873034 ¦ IEC60947-1,Tightening torque,
84873195time delay drift | Same as 84873034 Same as 84873034
84873195time delay range | Same as 84873034 ¦ ,"OFF" delay, Same as 84873034 ¦ ,"ON" delay, Same as 84873034 ¦ ,Inhibition,
84873195time delay type | Same as 84873034 ¦ ,"OFF" delay, Same as 84873034 ¦ ,"ON" delay, Same as 84873034 ¦ ,Inhibition,
84873195tripping threshold | Same as 84873034 ¦ ,Phase cut, Same as 84873034 ¦ ,Phase sequence, Same as 84873034 ¦ ,Over / undervoltage (symmetry windows mode), Same as 84873034 ¦ ,Over voltage, Same as 84873034 ¦ ,Undervoltage , Same as 84873034 ¦ ,Phase asymmetry, Same as 84873034 ¦ ,Disconnection of neutral, Same as 84873034 ¦ ,Voltage Regeneration, Same as 84873034 ¦ ,Extreme undervoltage (Phase loss), Same as 84873034 ¦ ,Extreme Overvoltage, Same as 84873034 ¦ ,Extreme Asymmetry,
84873195vibration resistance | Same as 84873034 ¦ IEC60068-2-6
84873195width | Same as 84873034 ¦ ,Width,
84873220 | Same as RM35UB330 ¦ IEC60721-3-3,Climatic category, Same as RM35UB330 ¦ Germanisher Lloyd,Environmental category, Same as RM35UB330 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM35UB330 ¦ ,Supply,Rated Same as RM35UB330 ¦ ,Input 1,Voltage Same as RM35UB330 ¦ ,Input 2,Spec Same as RM35UB330 ¦ ,Input 3, Same as RM35UB330 ¦ ,Output 1, Same as RM35UB330 ¦ ,Output 2, Same as RM35UB330 ¦ ,Measurement mode, Same as RM35UB330 Same as RM35UB330 Same as RM35UB330 Same as RM35UB330 Same as RM35UB330 ¦ ,MTTFd, Same as RM35UB330 ¦ ,B10d, Drawing / Diagram
84873220IP degree of protection | Same as RM35UB330 ¦ IEC60529,Terminal Block, Same as RM35UB330 ¦ IEC60529,Housing, Same as RM35UB330 ¦ IEC60529,Front Panel,
84873220Input nominal voltage selection | Same as RM35UB330 ¦ ,Input nominal voltage selection,
84873220Minimum distance to adjacent devices | Same as RM35UB330 ¦ ,Horizontal, Same as RM35UB330 ¦ ,Vertical,
84873220[Ie] rated operational current | Same as RM35UB330 ¦ IEC61810-1,Rated switching current,
84873220[Ue] rated operational voltage | Same as RM35UB330 ¦ IEC61810-1,Rated switching voltage,
84873220[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Supply, Same as RM35UB330 ¦ IEC60664-1,Input 1, Same as RM35UB330 ¦ IEC60664-1,Input 2, Same as RM35UB330 ¦ IEC60664-1,Input 3, Same as RM35UB330 ¦ IEC60664-1,Output 1, Same as RM35UB330 ¦ IEC60664-1,Output 2, Same as RM35UB330 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM35UB330 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM35UB330 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM35UB330 ¦ IEC60664-1,Supply / Output 1, Same as RM35UB330 ¦ IEC60664-1,Supply / Output 2, Same as RM35UB330 ¦ IEC60664-1,Output 1 / Output 2, Same as RM35UB330 ¦ IEC60664-1,Input 1 / Output 1, Same as RM35UB330 ¦ IEC60664-1,Input 1 / Output 2, Same as RM35UB330 ¦ IEC60664-1,Input 2 / Output 1, Same as RM35UB330 ¦ IEC60664-1,Input 2 / Output 2, Same as RM35UB330 ¦ IEC60664-1,Input 3 / Output 1, Same as RM35UB330 ¦ IEC60664-1,Input 3 / Output 2, Same as RM35UB330 ¦ IEC60664-1,Input 1 / Input 2, Same as RM35UB330 ¦ IEC60664-1,Input 2 / Input 3, Same as RM35UB330 ¦ IEC60664-1,Input 1 / Input 3,
84873220[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Supply, Same as RM35UB330 ¦ IEC60664-1,Input 1, Same as RM35UB330 ¦ IEC60664-1,Input 2, Same as RM35UB330 ¦ IEC60664-1,Input 3, Same as RM35UB330 ¦ IEC60664-1,Output 1, Same as RM35UB330 ¦ IEC60664-1,Output 2, Same as RM35UB330 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM35UB330 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM35UB330 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM35UB330 ¦ IEC60664-1,Supply / Output 1, Same as RM35UB330 ¦ IEC60664-1,Supply / Output 2, Same as RM35UB330 ¦ IEC60664-1,Output 1 / Output 2, Same as RM35UB330 ¦ IEC60664-1,Input 1 / Output 1, Same as RM35UB330 ¦ IEC60664-1,Input 1 / Output 2, Same as RM35UB330 ¦ IEC60664-1,Input 2 / Output 1, Same as RM35UB330 ¦ IEC60664-1,Input 2 / Output 2, Same as RM35UB330 ¦ IEC60664-1,Input 3 / Output 1, Same as RM35UB330 ¦ IEC60664-1,Input 3 / Output 2, Same as RM35UB330 ¦ IEC60664-1,Input 1 / Input 2, Same as RM35UB330 ¦ IEC60664-1,Input 2 / Input 3, Same as RM35UB330 ¦ IEC60664-1,Input 1 / Input 3,
84873220[Us] rated supply voltage | Same as RM35UB330
84873220ambient air temperature for operation | Same as RM35UB330 ¦ ,Operation,
84873220ambient air temperature for storage | Same as RM35UB330 ¦ ,Storage,
84873220bump resistance | Same as RM35UB330 ¦ IEC60068-2-29
84873220cable stripping length | Same as RM35UB330 ¦ ,Cable stripping length,
84873220circuit group | Same as RM35UB330 ¦ ,Supply,Terminal Same as RM35UB330 ¦ ,Input 1, Same as RM35UB330 ¦ ,Input 2, Same as RM35UB330 ¦ ,Input 3, Same as RM35UB330 ¦ ,Output 1, Same as RM35UB330 ¦ ,Output 2,
84873220connections - terminals | Same as RM35UB330 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM35UB330 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM35UB330 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM35UB330 ¦ IEC60947-1,Flexible cable (spring terminal),
84873220contacts material | Same as RM35UB330
84873220depth | Same as RM35UB330 ¦ ,Depth,
84873220diagnostic button | Same as RM35UB330
84873220dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Supply / Input 1, Same as RM35UB330 ¦ IEC60255-27,Supply / Input 2, Same as RM35UB330 ¦ IEC60255-27,Supply / Input 3, Same as RM35UB330 ¦ IEC60255-27,Supply / Output 1, Same as RM35UB330 ¦ IEC60255-27,Supply / Output 2, Same as RM35UB330 ¦ IEC60255-27,Output 1 / Output 2, Same as RM35UB330 ¦ IEC60255-27,Input 1 / Output 1, Same as RM35UB330 ¦ IEC60255-27,Input 1 / Output 2, Same as RM35UB330 ¦ IEC60255-27,Input 2 / Output 1, Same as RM35UB330 ¦ IEC60255-27,Input 2 / Output 2, Same as RM35UB330 ¦ IEC60255-27,Input 3 / Output 1, Same as RM35UB330 ¦ IEC60255-27,Input 3 / Output 2, Same as RM35UB330 ¦ IEC60255-27,Input 1 / Input 2, Same as RM35UB330 ¦ IEC60255-27,Input 2 / Input 3, Same as RM35UB330 ¦ IEC60255-27,Input 1 / Input 3,
84873220directives | Same as RM35UB330 Same as RM35UB330 Same as RM35UB330
84873220duty time | Same as RM35UB330
84873220electrical durability | Same as RM35UB330 ¦ IEC60947-4-1,AC-1, Same as RM35UB330 ¦ IEC60947-4-1,DC-1, Same as RM35UB330 ¦ IEC60947-5-1,AC-15, Same as RM35UB330 ¦ IEC60947-5-1,DC-13,
84873220electromagnetic compatibility | Same as RM35UB330 ¦ ,Generic immunity standard, Same as RM35UB330 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM35UB330 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM35UB330 ¦ IEC61000-4-4,Fast transient / burst, Same as RM35UB330 ¦ IEC61000-4-5,Surge, Same as RM35UB330 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM35UB330 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM35UB330 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM35UB330 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM35UB330 ¦ IEC61000-4-29,DC voltage interruption, Same as RM35UB330 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM35UB330 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM35UB330 ¦ ,Generic emission standard, Same as RM35UB330 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM35UB330 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM35UB330 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM35UB330 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM35UB330 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM35UB330 ¦ Germanisher Lloyd,Conducted emission,
84873220height | Same as RM35UB330 ¦ ,Height,
84873220hysteresis | Same as RM35UB330 ¦ ,Phase cut, Same as RM35UB330 ¦ ,Phase sequence, Same as RM35UB330 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35UB330 ¦ ,Over voltage, Same as RM35UB330 ¦ ,Undervoltage , Same as RM35UB330 ¦ ,Phase asymmetry, Same as RM35UB330 ¦ ,Disconnection of neutral, Same as RM35UB330 ¦ ,Voltage Regeneration, Same as RM35UB330 ¦ ,Extreme undervoltage (Phase loss), Same as RM35UB330 ¦ ,Extreme Overvoltage, Same as RM35UB330 ¦ ,Extreme Asymmetry,
84873220immunity to microbreaks | Same as RM35UB330
84873220input frequency | Same as RM35UB330 ¦ ,Rated frequency, Same as RM35UB330 ¦ ,Frequency operating range,
84873220input terminal | Same as RM35UB330 ¦ ,Input terminal,
84873220insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Supply / Input 1, Same as RM35UB330 ¦ IEC60255-27,Supply / Input 2, Same as RM35UB330 ¦ IEC60255-27,Supply / Input 3, Same as RM35UB330 ¦ IEC60255-27,Supply / Output 1, Same as RM35UB330 ¦ IEC60255-27,Supply / Output 2, Same as RM35UB330 ¦ IEC60255-27,Output 1 / Output 2, Same as RM35UB330 ¦ IEC60255-27,Input 1 / Output 1, Same as RM35UB330 ¦ IEC60255-27,Input 1 / Output 2, Same as RM35UB330 ¦ IEC60255-27,Input 2 / Output 1, Same as RM35UB330 ¦ IEC60255-27,Input 2 / Output 2, Same as RM35UB330 ¦ IEC60255-27,Input 3 / Output 1, Same as RM35UB330 ¦ IEC60255-27,Input 3 / Output 2, Same as RM35UB330 ¦ IEC60255-27,Input 1 / Input 2, Same as RM35UB330 ¦ IEC60255-27,Input 2 / Input 3, Same as RM35UB330 ¦ IEC60255-27,Input 1 / Input 3,
84873220internal input resistance | Same as RM35UB330 ¦ ,Internal input resistance,
84873220local signalling | Same as RM35UB330 ¦ ,Power supply availability, Same as RM35UB330 ¦ ,Power supply not availability, Same as RM35UB330 ¦ ,Timing in-progress, Same as RM35UB330 ¦ ,Output is energized, Same as RM35UB330 ¦ ,Output is de-energized, Same as RM35UB330 ¦ ,Range Setting Changes, Same as RM35UB330 ¦ ,Phase Cut, Same as RM35UB330 ¦ ,Phase Sequence Swap, Same as RM35UB330 ¦ ,Undervoltage <U, Same as RM35UB330 ¦ ,Overvoltage >U, Same as RM35UB330 ¦ ,Phase Asymmetry, Same as RM35UB330 ¦ ,Voltage Regeneration, Same as RM35UB330 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM35UB330 ¦ ,Extreme Overvoltage >U, Same as RM35UB330 ¦ ,Extreme Phase Asymmetry,
84873220marking | UL, CSA, GL, CCC, CE, China ROHS
84873220maximum leakage current | Same as RM35UB330 ¦ IEC62314,Only for solid state output,
84873220maximum measuring cycle | Same as RM35UB330 ¦ ,Maximum measuring cycles,
84873220maximum switching capacity | Same as RM35UB330 ¦ ,Maximum switching voltage, Same as RM35UB330 ¦ ,Maximum switching current, Same as RM35UB330 ¦ ,Maximum switching capacity,
84873220maximum voltage drop | Same as RM35UB330 ¦ IEC62314,Only for solid state output,
84873220measurement method | Same as RM35UB330 ¦ ,Measurement method,
84873220measurement range | Same as RM35UB330 ¦ ,Phase lost , Same as RM35UB330 ¦ ,Phase sequence, Same as RM35UB330 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35UB330 ¦ ,Over voltage, Same as RM35UB330 ¦ ,Undervoltage , Same as RM35UB330 ¦ ,Phase asymmetry, Same as RM35UB330 ¦ ,Disconnection of neutral, Same as RM35UB330 ¦ ,Voltage Regeneration, Same as RM35UB330 ¦ ,Extreme undervoltage, Same as RM35UB330 ¦ ,Extreme Overvoltage, Same as RM35UB330 ¦ ,Extreme Asymmetry,
84873220mechanical durability | Same as RM35UB330 ¦ IEC61810-1
84873220minimum switching capacity | Same as RM35UB330 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM35UB330 ¦ IEC60947-5-4,Minimum switching current, Same as RM35UB330 ¦ IEC60947-5-4,Minimum switching capacity,
84873220monitoring functions | Same as RM35UB330 ¦ ,Phase lost , Same as RM35UB330 ¦ ,Phase sequence, Same as RM35UB330 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35UB330 ¦ ,Over voltage, Same as RM35UB330 ¦ ,Undervoltage , Same as RM35UB330 ¦ ,Phase asymmetry, Same as RM35UB330 ¦ ,Disconnection of neutral, Same as RM35UB330 ¦ ,Voltage Regeneration, Same as RM35UB330 ¦ ,Extreme undervoltage, Same as RM35UB330 ¦ ,Extreme overvoltage, Same as RM35UB330 ¦ ,Extreme asymmetry,
84873220mounting position | Same as RM35UB330 ¦ ,In relation to normal vertical mounting plane,
84873220mounting support | Same as RM35UB330 ¦ IEC/EN 60715,Without socket, Same as RM35UB330 ¦ IEC/EN 60715,With socket,
84873220net weight | Same as RM35UB330
84873220on-load factor | Same as RM35UB330
84873220output logic | Same as RM35UB330 ¦ ,R1 (11-12-14), Same as RM35UB330 ¦ ,R2 (21-22-24),
84873220output terminal | Same as RM35UB330
84873220output type | Same as RM35UB330
84873220overvoltage category | Same as RM35UB330 ¦ IEC60664-1
84873220permissible input overload | Same as RM35UB330 ¦ ,permissible input overload,
84873220polarity | Same as RM35UB330
84873220pollution degree | Same as RM35UB330 ¦ IEC60664-1
84873220power consumption | Same as RM35UB330
84873220power on delay | Same as RM35UB330
84873220product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873220relative humidity | Same as RM35UB330 ¦ IEC60068-2-30,Damp heat,XX
84873220release of input voltage | Same as RM35UB330
84873220repeat accuracy of the switching threshold | Same as RM35UB330 ¦ ,Repeat accuracy (constant parameters),
84873220repeat accuracy of time delay | Same as RM35UB330
84873220reset time | Same as RM35UB330 ¦ ,through Un power reset, Same as RM35UB330 ¦ ,through front panel reset, Same as RM35UB330 ¦ ,through input control reset,
84873220response time | Same as RM35UB330 ¦ ,on crossing the threshold, Same as RM35UB330 Same as RM35UB330 Same as RM35UB330 Same as RM35UB330
84873220safety reliability data | Same as RM35UB330 ¦ ,MTTF, Same as RM35UB330 ¦ ,B10,
84873220seismic resistance | Same as RM35UB330 ¦ IEC60068-3-3
84873220setting accuracy of the switching threshold | Same as RM35UB330 ¦ ,Setting accuracy,
84873220setting accuracy of time delay | Same as RM35UB330
84873220shock resistance | Same as RM35UB330 ¦ IEC60068-2-27
84873220short circuit protection | Same as RM35UB330 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM35UB330 ¦ IEC62314,Solid State Output by external fuse,
84873220standards | Same as RM35UB330
84873220status LED | Same as RM35UB330
84873220supply frequency | Same as RM35UB330 Same as RM35UB330
84873220supply terminal | Same as RM35UB330
84873220supply voltage limits | Same as RM35UB330
84873220switching threshold drift | Same as RM35UB330 ¦ ,Measurement error with supply voltage variation, Same as RM35UB330 ¦ ,Measurement error with temperature variation,
84873220thermal current | Same as RM35UB330 ¦ IEC60947-5-1
84873220tightening torque | Same as RM35UB330 ¦ IEC60947-1,Tightening torque,
84873220time delay drift | Same as RM35UB330 Same as RM35UB330
84873220time delay range | Same as RM35UB330 ¦ ,"OFF" delay, Same as RM35UB330 ¦ ,"ON" delay, Same as RM35UB330 ¦ ,Inhibition,
84873220time delay type | Same as RM35UB330 ¦ ,"OFF" delay, Same as RM35UB330 ¦ ,"ON" delay, Same as RM35UB330 ¦ ,Inhibition,
84873220tripping threshold | Same as RM35UB330 ¦ ,Phase cut, Same as RM35UB330 ¦ ,Phase sequence, Same as RM35UB330 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35UB330 ¦ ,Over voltage, Same as RM35UB330 ¦ ,Undervoltage , Same as RM35UB330 ¦ ,Phase asymmetry, Same as RM35UB330 ¦ ,Disconnection of neutral, Same as RM35UB330 ¦ ,Voltage Regeneration, Same as RM35UB330 ¦ ,Extreme undervoltage (Phase loss), Same as RM35UB330 ¦ ,Extreme Overvoltage, Same as RM35UB330 ¦ ,Extreme Asymmetry,
84873220vibration resistance | Same as RM35UB330 ¦ IEC60068-2-6
84873220width | Same as RM35UB330 ¦ ,Width,
84873221 | Same as RM35UB3N30 ¦ IEC60721-3-3,Climatic category, Same as RM35UB3N30 ¦ Germanisher Lloyd,Environmental category, Same as RM35UB3N30 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM35UB3N30 ¦ ,Supply,Rated Same as RM35UB3N30 ¦ ,Input 1,Voltage Same as RM35UB3N30 ¦ ,Input 2,Spec Same as RM35UB3N30 ¦ ,Input 3, Same as RM35UB3N30 ¦ ,Output 1, Same as RM35UB3N30 ¦ ,Output 2, Same as RM35UB3N30 ¦ ,Measurement mode, Same as RM35UB3N30 Same as RM35UB3N30 Same as RM35UB3N30 Same as RM35UB3N30 Same as RM35UB3N30 Same as RM35UB3N30 ¦ ,MTTFd, Same as RM35UB3N30 ¦ ,B10d, Drawing / Diagram
84873221IP degree of protection | Same as RM35UB3N30 ¦ IEC60529,Terminal Block, Same as RM35UB3N30 ¦ IEC60529,Housing, Same as RM35UB3N30 ¦ IEC60529,Front Panel,
84873221Input nominal voltage selection | Same as RM35UB3N30 ¦ ,Input nominal voltage selection,
84873221Minimum distance to adjacent devices | Same as RM35UB3N30 ¦ ,Horizontal, Same as RM35UB3N30 ¦ ,Vertical,
84873221[Ie] rated operational current | Same as RM35UB3N30 ¦ IEC61810-1,Rated switching current,
84873221[Ue] rated operational voltage | Same as RM35UB3N30 ¦ IEC61810-1,Rated switching voltage,
84873221[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply, Same as RM35UB3N30 ¦ IEC60664-1,Input 1, Same as RM35UB3N30 ¦ IEC60664-1,Input 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 3, Same as RM35UB3N30 ¦ IEC60664-1,Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM35UB3N30 ¦ IEC60664-1,Supply / Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Supply / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Output 1 / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 3 / Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Input 3 / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Input 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Input 3, Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Input 3,
84873221[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply, Same as RM35UB3N30 ¦ IEC60664-1,Input 1, Same as RM35UB3N30 ¦ IEC60664-1,Input 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 3, Same as RM35UB3N30 ¦ IEC60664-1,Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM35UB3N30 ¦ IEC60664-1,Supply / Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Supply / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Output 1 / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 3 / Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Input 3 / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Input 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Input 3, Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Input 3,
84873221[Us] rated supply voltage | Same as RM35UB3N30
84873221ambient air temperature for operation | Same as RM35UB3N30 ¦ ,Operation,
84873221ambient air temperature for storage | Same as RM35UB3N30 ¦ ,Storage,
84873221bump resistance | Same as RM35UB3N30 ¦ IEC60068-2-29
84873221cable stripping length | Same as RM35UB3N30 ¦ ,Cable stripping length,
84873221circuit group | Same as RM35UB3N30 ¦ ,Supply,Terminal Same as RM35UB3N30 ¦ ,Input 1, Same as RM35UB3N30 ¦ ,Input 2, Same as RM35UB3N30 ¦ ,Input 3, Same as RM35UB3N30 ¦ ,Output 1, Same as RM35UB3N30 ¦ ,Output 2,
84873221connections - terminals | Same as RM35UB3N30 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM35UB3N30 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM35UB3N30 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM35UB3N30 ¦ IEC60947-1,Flexible cable (spring terminal),
84873221contacts material | Same as RM35UB3N30
84873221depth | Same as RM35UB3N30 ¦ ,Depth,
84873221diagnostic button | Same as RM35UB3N30
84873221dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 1, Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 2, Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 3, Same as RM35UB3N30 ¦ IEC60255-27,Supply / Output 1, Same as RM35UB3N30 ¦ IEC60255-27,Supply / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Output 1 / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Output 1, Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Output 1, Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 3 / Output 1, Same as RM35UB3N30 ¦ IEC60255-27,Input 3 / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Input 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Input 3, Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Input 3,
84873221directives | Same as RM35UB3N30 Same as RM35UB3N30 Same as RM35UB3N30
84873221duty time | Same as RM35UB3N30
84873221electrical durability | Same as RM35UB3N30 ¦ IEC60947-4-1,AC-1, Same as RM35UB3N30 ¦ IEC60947-4-1,DC-1, Same as RM35UB3N30 ¦ IEC60947-5-1,AC-15, Same as RM35UB3N30 ¦ IEC60947-5-1,DC-13,
84873221electromagnetic compatibility | Same as RM35UB3N30 ¦ ,Generic immunity standard, Same as RM35UB3N30 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM35UB3N30 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM35UB3N30 ¦ IEC61000-4-4,Fast transient / burst, Same as RM35UB3N30 ¦ IEC61000-4-5,Surge, Same as RM35UB3N30 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM35UB3N30 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM35UB3N30 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM35UB3N30 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM35UB3N30 ¦ IEC61000-4-29,DC voltage interruption, Same as RM35UB3N30 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM35UB3N30 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM35UB3N30 ¦ ,Generic emission standard, Same as RM35UB3N30 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM35UB3N30 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM35UB3N30 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM35UB3N30 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM35UB3N30 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM35UB3N30 ¦ Germanisher Lloyd,Conducted emission,
84873221height | Same as RM35UB3N30 ¦ ,Height,
84873221hysteresis | Same as RM35UB3N30 ¦ ,Phase cut, Same as RM35UB3N30 ¦ ,Phase sequence, Same as RM35UB3N30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35UB3N30 ¦ ,Over voltage, Same as RM35UB3N30 ¦ ,Undervoltage , Same as RM35UB3N30 ¦ ,Phase asymmetry, Same as RM35UB3N30 ¦ ,Disconnection of neutral, Same as RM35UB3N30 ¦ ,Voltage Regeneration, Same as RM35UB3N30 ¦ ,Extreme undervoltage (Phase loss), Same as RM35UB3N30 ¦ ,Extreme Overvoltage, Same as RM35UB3N30 ¦ ,Extreme Asymmetry,
84873221immunity to microbreaks | Same as RM35UB3N30
84873221input frequency | Same as RM35UB3N30 ¦ ,Rated frequency, Same as RM35UB3N30 ¦ ,Frequency operating range,
84873221input terminal | Same as RM35UB3N30 ¦ ,Input terminal,
84873221insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 1, Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 2, Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 3, Same as RM35UB3N30 ¦ IEC60255-27,Supply / Output 1, Same as RM35UB3N30 ¦ IEC60255-27,Supply / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Output 1 / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Output 1, Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Output 1, Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 3 / Output 1, Same as RM35UB3N30 ¦ IEC60255-27,Input 3 / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Input 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Input 3, Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Input 3,
84873221internal input resistance | Same as RM35UB3N30 ¦ ,Internal input resistance,
84873221local signalling | Same as RM35UB3N30 ¦ ,Power supply availability, Same as RM35UB3N30 ¦ ,Power supply not availability, Same as RM35UB3N30 ¦ ,Timing in-progress, Same as RM35UB3N30 ¦ ,Output is energized, Same as RM35UB3N30 ¦ ,Output is de-energized, Same as RM35UB3N30 ¦ ,Range Setting Changes, Same as RM35UB3N30 ¦ ,Phase Cut, Same as RM35UB3N30 ¦ ,Phase Sequence Swap, Same as RM35UB3N30 ¦ ,Undervoltage <U, Same as RM35UB3N30 ¦ ,Overvoltage >U, Same as RM35UB3N30 ¦ ,Phase Asymmetry, Same as RM35UB3N30 ¦ ,Voltage Regeneration, Same as RM35UB3N30 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM35UB3N30 ¦ ,Extreme Overvoltage >U, Same as RM35UB3N30 ¦ ,Extreme Phase Asymmetry,
84873221marking | UL, CSA, GL, CCC, CE, China ROHS
84873221maximum leakage current | Same as RM35UB3N30 ¦ IEC62314,Only for solid state output,
84873221maximum measuring cycle | Same as RM35UB3N30 ¦ ,Maximum measuring cycles,
84873221maximum switching capacity | Same as RM35UB3N30 ¦ ,Maximum switching voltage, Same as RM35UB3N30 ¦ ,Maximum switching current, Same as RM35UB3N30 ¦ ,Maximum switching capacity,
84873221maximum voltage drop | Same as RM35UB3N30 ¦ IEC62314,Only for solid state output,
84873221measurement method | Same as RM35UB3N30 ¦ ,Measurement method,
84873221measurement range | Same as RM35UB3N30 ¦ ,Phase lost , Same as RM35UB3N30 ¦ ,Phase sequence, Same as RM35UB3N30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35UB3N30 ¦ ,Over voltage, Same as RM35UB3N30 ¦ ,Undervoltage , Same as RM35UB3N30 ¦ ,Phase asymmetry, Same as RM35UB3N30 ¦ ,Disconnection of neutral, Same as RM35UB3N30 ¦ ,Voltage Regeneration, Same as RM35UB3N30 ¦ ,Extreme undervoltage, Same as RM35UB3N30 ¦ ,Extreme Overvoltage, Same as RM35UB3N30 ¦ ,Extreme Asymmetry,
84873221mechanical durability | Same as RM35UB3N30 ¦ IEC61810-1
84873221minimum switching capacity | Same as RM35UB3N30 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM35UB3N30 ¦ IEC60947-5-4,Minimum switching current, Same as RM35UB3N30 ¦ IEC60947-5-4,Minimum switching capacity,
84873221monitoring functions | Same as RM35UB3N30 ¦ ,Phase lost , Same as RM35UB3N30 ¦ ,Phase sequence, Same as RM35UB3N30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35UB3N30 ¦ ,Over voltage, Same as RM35UB3N30 ¦ ,Undervoltage , Same as RM35UB3N30 ¦ ,Phase asymmetry, Same as RM35UB3N30 ¦ ,Disconnection of neutral, Same as RM35UB3N30 ¦ ,Voltage Regeneration, Same as RM35UB3N30 ¦ ,Extreme undervoltage, Same as RM35UB3N30 ¦ ,Extreme overvoltage, Same as RM35UB3N30 ¦ ,Extreme asymmetry,
84873221mounting position | Same as RM35UB3N30 ¦ ,In relation to normal vertical mounting plane,
84873221mounting support | Same as RM35UB3N30 ¦ IEC/EN 60715,Without socket, Same as RM35UB3N30 ¦ IEC/EN 60715,With socket,
84873221net weight | Same as RM35UB3N30
84873221on-load factor | Same as RM35UB3N30
84873221output logic | Same as RM35UB3N30 ¦ ,R1 (11-12-14), Same as RM35UB3N30 ¦ ,R2 (21-22-24),
84873221output terminal | Same as RM35UB3N30
84873221output type | Same as RM35UB3N30
84873221overvoltage category | Same as RM35UB3N30 ¦ IEC60664-1
84873221permissible input overload | Same as RM35UB3N30 ¦ ,permissible input overload,
84873221polarity | Same as RM35UB3N30
84873221pollution degree | Same as RM35UB3N30 ¦ IEC60664-1
84873221power consumption | Same as RM35UB3N30
84873221power on delay | Same as RM35UB3N30
84873221product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873221relative humidity | Same as RM35UB3N30 ¦ IEC60068-2-30,Damp heat,XX
84873221release of input voltage | Same as RM35UB3N30
84873221repeat accuracy of the switching threshold | Same as RM35UB3N30 ¦ ,Repeat accuracy (constant parameters),
84873221repeat accuracy of time delay | Same as RM35UB3N30
84873221reset time | Same as RM35UB3N30 ¦ ,through Un power reset, Same as RM35UB3N30 ¦ ,through front panel reset, Same as RM35UB3N30 ¦ ,through input control reset,
84873221response time | Same as RM35UB3N30 ¦ ,on crossing the threshold, Same as RM35UB3N30 Same as RM35UB3N30 Same as RM35UB3N30 Same as RM35UB3N30
84873221safety reliability data | Same as RM35UB3N30 ¦ ,MTTF, Same as RM35UB3N30 ¦ ,B10,
84873221seismic resistance | Same as RM35UB3N30 ¦ IEC60068-3-3
84873221setting accuracy of the switching threshold | Same as RM35UB3N30 ¦ ,Setting accuracy,
84873221setting accuracy of time delay | Same as RM35UB3N30
84873221shock resistance | Same as RM35UB3N30 ¦ IEC60068-2-27
84873221short circuit protection | Same as RM35UB3N30 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM35UB3N30 ¦ IEC62314,Solid State Output by external fuse,
84873221standards | Same as RM35UB3N30
84873221status LED | Same as RM35UB3N30
84873221supply frequency | Same as RM35UB3N30 Same as RM35UB3N30
84873221supply terminal | Same as RM35UB3N30
84873221supply voltage limits | Same as RM35UB3N30
84873221switching threshold drift | Same as RM35UB3N30 ¦ ,Measurement error with supply voltage variation, Same as RM35UB3N30 ¦ ,Measurement error with temperature variation,
84873221thermal current | Same as RM35UB3N30 ¦ IEC60947-5-1
84873221tightening torque | Same as RM35UB3N30 ¦ IEC60947-1,Tightening torque,
84873221time delay drift | Same as RM35UB3N30 Same as RM35UB3N30
84873221time delay range | Same as RM35UB3N30 ¦ ,"OFF" delay, Same as RM35UB3N30 ¦ ,"ON" delay, Same as RM35UB3N30 ¦ ,Inhibition,
84873221time delay type | Same as RM35UB3N30 ¦ ,"OFF" delay, Same as RM35UB3N30 ¦ ,"ON" delay, Same as RM35UB3N30 ¦ ,Inhibition,
84873221tripping threshold | Same as RM35UB3N30 ¦ ,Phase cut, Same as RM35UB3N30 ¦ ,Phase sequence, Same as RM35UB3N30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35UB3N30 ¦ ,Over voltage, Same as RM35UB3N30 ¦ ,Undervoltage , Same as RM35UB3N30 ¦ ,Phase asymmetry, Same as RM35UB3N30 ¦ ,Disconnection of neutral, Same as RM35UB3N30 ¦ ,Voltage Regeneration, Same as RM35UB3N30 ¦ ,Extreme undervoltage (Phase loss), Same as RM35UB3N30 ¦ ,Extreme Overvoltage, Same as RM35UB3N30 ¦ ,Extreme Asymmetry,
84873221vibration resistance | Same as RM35UB3N30 ¦ IEC60068-2-6
84873221width | Same as RM35UB3N30 ¦ ,Width,
84873222 | Same as RM17UB310 ¦ IEC60721-3-3,Climatic category, Same as RM17UB310 ¦ Germanisher Lloyd,Environmental category, Same as RM17UB310 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM17UB310 ¦ ,Supply,Rated Same as RM17UB310 ¦ ,Input 1,Voltage Same as RM17UB310 ¦ ,Input 2,Spec Same as RM17UB310 ¦ ,Input 3, Same as RM17UB310 ¦ ,Output 1, Same as RM17UB310 ¦ ,Output 2, Same as RM17UB310 ¦ ,Measurement mode, Same as RM17UB310 Same as RM17UB310 Same as RM17UB310 Same as RM17UB310 Same as RM17UB310 ¦ ,MTTFd, Same as RM17UB310 ¦ ,B10d, Drawing / Diagram
84873222IP degree of protection | Same as RM17UB310 ¦ IEC60529,Terminal Block, Same as RM17UB310 ¦ IEC60529,Housing, Same as RM17UB310 ¦ IEC60529,Front Panel,
84873222Input nominal voltage selection | Same as RM17UB310 ¦ ,Input nominal voltage selection,
84873222Minimum distance to adjacent devices | Same as RM17UB310 ¦ ,Horizontal, Same as RM17UB310 ¦ ,Vertical,
84873222[Ie] rated operational current | Same as RM17UB310 ¦ IEC61810-1,Rated switching current,
84873222[Ue] rated operational voltage | Same as RM17UB310 ¦ IEC61810-1,Rated switching voltage,
84873222[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Supply, Same as RM17UB310 ¦ IEC60664-1,Input 1, Same as RM17UB310 ¦ IEC60664-1,Input 2, Same as RM17UB310 ¦ IEC60664-1,Input 3, Same as RM17UB310 ¦ IEC60664-1,Output 1, Same as RM17UB310 ¦ IEC60664-1,Output 2, Same as RM17UB310 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17UB310 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17UB310 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17UB310 ¦ IEC60664-1,Supply / Output 1, Same as RM17UB310 ¦ IEC60664-1,Supply / Output 2, Same as RM17UB310 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17UB310 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17UB310 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17UB310 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17UB310 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17UB310 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17UB310 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17UB310 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17UB310 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17UB310 ¦ IEC60664-1,Input 1 / Input 3,
84873222[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Supply, Same as RM17UB310 ¦ IEC60664-1,Input 1, Same as RM17UB310 ¦ IEC60664-1,Input 2, Same as RM17UB310 ¦ IEC60664-1,Input 3, Same as RM17UB310 ¦ IEC60664-1,Output 1, Same as RM17UB310 ¦ IEC60664-1,Output 2, Same as RM17UB310 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17UB310 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17UB310 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17UB310 ¦ IEC60664-1,Supply / Output 1, Same as RM17UB310 ¦ IEC60664-1,Supply / Output 2, Same as RM17UB310 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17UB310 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17UB310 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17UB310 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17UB310 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17UB310 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17UB310 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17UB310 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17UB310 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17UB310 ¦ IEC60664-1,Input 1 / Input 3,
84873222[Us] rated supply voltage | Same as RM17UB310
84873222ambient air temperature for operation | Same as RM17UB310 ¦ ,Operation,
84873222ambient air temperature for storage | Same as RM17UB310 ¦ ,Storage,
84873222bump resistance | Same as RM17UB310 ¦ IEC60068-2-29
84873222cable stripping length | Same as RM17UB310 ¦ ,Cable stripping length,
84873222circuit group | Same as RM17UB310 ¦ ,Supply,Terminal Same as RM17UB310 ¦ ,Input 1, Same as RM17UB310 ¦ ,Input 2, Same as RM17UB310 ¦ ,Input 3, Same as RM17UB310 ¦ ,Output 1, Same as RM17UB310 ¦ ,Output 2,
84873222connections - terminals | Same as RM17UB310 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17UB310 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17UB310 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17UB310 ¦ IEC60947-1,Flexible cable (spring terminal),
84873222contacts material | Same as RM17UB310
84873222depth | Same as RM17UB310 ¦ ,Depth,
84873222diagnostic button | Same as RM17UB310
84873222dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Supply / Input 1, Same as RM17UB310 ¦ IEC60255-27,Supply / Input 2, Same as RM17UB310 ¦ IEC60255-27,Supply / Input 3, Same as RM17UB310 ¦ IEC60255-27,Supply / Output 1, Same as RM17UB310 ¦ IEC60255-27,Supply / Output 2, Same as RM17UB310 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17UB310 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17UB310 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17UB310 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17UB310 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17UB310 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17UB310 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17UB310 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17UB310 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17UB310 ¦ IEC60255-27,Input 1 / Input 3,
84873222directives | Same as RM17UB310 Same as RM17UB310 Same as RM17UB310
84873222duty time | Same as RM17UB310
84873222electrical durability | Same as RM17UB310 ¦ IEC60947-4-1,AC-1, Same as RM17UB310 ¦ IEC60947-4-1,DC-1, Same as RM17UB310 ¦ IEC60947-5-1,AC-15, Same as RM17UB310 ¦ IEC60947-5-1,DC-13,
84873222electromagnetic compatibility | Same as RM17UB310 ¦ ,Generic immunity standard, Same as RM17UB310 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17UB310 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17UB310 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17UB310 ¦ IEC61000-4-5,Surge, Same as RM17UB310 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17UB310 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17UB310 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17UB310 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17UB310 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17UB310 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM17UB310 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17UB310 ¦ ,Generic emission standard, Same as RM17UB310 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17UB310 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17UB310 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17UB310 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17UB310 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17UB310 ¦ Germanisher Lloyd,Conducted emission,
84873222height | Same as RM17UB310 ¦ ,Height,
84873222hysteresis | Same as RM17UB310 ¦ ,Phase cut, Same as RM17UB310 ¦ ,Phase sequence, Same as RM17UB310 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17UB310 ¦ ,Over voltage, Same as RM17UB310 ¦ ,Undervoltage , Same as RM17UB310 ¦ ,Phase asymmetry, Same as RM17UB310 ¦ ,Disconnection of neutral, Same as RM17UB310 ¦ ,Voltage Regeneration, Same as RM17UB310 ¦ ,Extreme undervoltage (Phase loss), Same as RM17UB310 ¦ ,Extreme Overvoltage, Same as RM17UB310 ¦ ,Extreme Asymmetry,
84873222immunity to microbreaks | Same as RM17UB310
84873222input frequency | Same as RM17UB310 ¦ ,Rated frequency, Same as RM17UB310 ¦ ,Frequency operating range,
84873222input terminal | Same as RM17UB310 ¦ ,Input terminal,
84873222insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Supply / Input 1, Same as RM17UB310 ¦ IEC60255-27,Supply / Input 2, Same as RM17UB310 ¦ IEC60255-27,Supply / Input 3, Same as RM17UB310 ¦ IEC60255-27,Supply / Output 1, Same as RM17UB310 ¦ IEC60255-27,Supply / Output 2, Same as RM17UB310 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17UB310 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17UB310 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17UB310 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17UB310 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17UB310 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17UB310 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17UB310 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17UB310 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17UB310 ¦ IEC60255-27,Input 1 / Input 3,
84873222internal input resistance | Same as RM17UB310 ¦ ,Internal input resistance,
84873222local signalling | Same as RM17UB310 ¦ ,Power supply availability, Same as RM17UB310 ¦ ,Power supply not availability, Same as RM17UB310 ¦ ,Timing in-progress, Same as RM17UB310 ¦ ,Output is energized, Same as RM17UB310 ¦ ,Output is de-energized, Same as RM17UB310 ¦ ,Range Setting Changes, Same as RM17UB310 ¦ ,Phase Cut, Same as RM17UB310 ¦ ,Phase Sequence Swap, Same as RM17UB310 ¦ ,Undervoltage <U, Same as RM17UB310 ¦ ,Overvoltage >U, Same as RM17UB310 ¦ ,Phase Asymmetry, Same as RM17UB310 ¦ ,Voltage Regeneration, Same as RM17UB310 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17UB310 ¦ ,Extreme Overvoltage >U, Same as RM17UB310 ¦ ,Extreme Phase Asymmetry,
84873222marking | UL, CSA, GL, CCC, CE, China ROHS
84873222maximum leakage current | Same as RM17UB310 ¦ IEC62314,Only for solid state output,
84873222maximum measuring cycle | Same as RM17UB310 ¦ ,Maximum measuring cycles,
84873222maximum switching capacity | Same as RM17UB310 ¦ ,Maximum switching voltage, Same as RM17UB310 ¦ ,Maximum switching current, Same as RM17UB310 ¦ ,Maximum switching capacity,
84873222maximum voltage drop | Same as RM17UB310 ¦ IEC62314,Only for solid state output,
84873222measurement method | Same as RM17UB310 ¦ ,Measurement method,
84873222measurement range | Same as RM17UB310 ¦ ,Phase lost , Same as RM17UB310 ¦ ,Phase sequence, Same as RM17UB310 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17UB310 ¦ ,Over voltage, Same as RM17UB310 ¦ ,Undervoltage , Same as RM17UB310 ¦ ,Phase asymmetry, Same as RM17UB310 ¦ ,Disconnection of neutral, Same as RM17UB310 ¦ ,Voltage Regeneration, Same as RM17UB310 ¦ ,Extreme undervoltage, Same as RM17UB310 ¦ ,Extreme Overvoltage, Same as RM17UB310 ¦ ,Extreme Asymmetry,
84873222mechanical durability | Same as RM17UB310 ¦ IEC61810-1
84873222minimum switching capacity | Same as RM17UB310 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17UB310 ¦ IEC60947-5-4,Minimum switching current, Same as RM17UB310 ¦ IEC60947-5-4,Minimum switching capacity,
84873222monitoring functions | Same as RM17UB310 ¦ ,Phase lost , Same as RM17UB310 ¦ ,Phase sequence, Same as RM17UB310 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17UB310 ¦ ,Over voltage, Same as RM17UB310 ¦ ,Undervoltage , Same as RM17UB310 ¦ ,Phase asymmetry, Same as RM17UB310 ¦ ,Disconnection of neutral, Same as RM17UB310 ¦ ,Voltage Regeneration, Same as RM17UB310 ¦ ,Extreme undervoltage, Same as RM17UB310 ¦ ,Extreme overvoltage, Same as RM17UB310 ¦ ,Extreme asymmetry,
84873222mounting position | Same as RM17UB310 ¦ ,In relation to normal vertical mounting plane,
84873222mounting support | Same as RM17UB310 ¦ IEC/EN 60715,Without socket, Same as RM17UB310 ¦ IEC/EN 60715,With socket,
84873222net weight | Same as RM17UB310
84873222on-load factor | Same as RM17UB310
84873222output logic | Same as RM17UB310 ¦ ,R1 (11-12-14), Same as RM17UB310 ¦ ,R2 (21-22-24),
84873222output terminal | Same as RM17UB310
84873222output type | Same as RM17UB310
84873222overvoltage category | Same as RM17UB310 ¦ IEC60664-1
84873222permissible input overload | Same as RM17UB310 ¦ ,permissible input overload,
84873222polarity | Same as RM17UB310
84873222pollution degree | Same as RM17UB310 ¦ IEC60664-1
84873222power consumption | Same as RM17UB310
84873222power on delay | Same as RM17UB310
84873222product certifications | UL, CSA, GL, CCC, CE, China ROHS
84873222relative humidity | Same as RM17UB310 ¦ IEC60068-2-30,Damp heat,XX
84873222release of input voltage | Same as RM17UB310
84873222repeat accuracy of the switching threshold | Same as RM17UB310 ¦ ,Repeat accuracy (constant parameters),
84873222repeat accuracy of time delay | Same as RM17UB310
84873222reset time | Same as RM17UB310 ¦ ,through Un power reset, Same as RM17UB310 ¦ ,through front panel reset, Same as RM17UB310 ¦ ,through input control reset,
84873222response time | Same as RM17UB310 ¦ ,on crossing the threshold, Same as RM17UB310 Same as RM17UB310 Same as RM17UB310 Same as RM17UB310
84873222safety reliability data | Same as RM17UB310 ¦ ,MTTF, Same as RM17UB310 ¦ ,B10,
84873222seismic resistance | Same as RM17UB310 ¦ IEC60068-3-3
84873222setting accuracy of the switching threshold | Same as RM17UB310 ¦ ,Setting accuracy,
84873222setting accuracy of time delay | Same as RM17UB310
84873222shock resistance | Same as RM17UB310 ¦ IEC60068-2-27
84873222short circuit protection | Same as RM17UB310 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17UB310 ¦ IEC62314,Solid State Output by external fuse,
84873222standards | Same as RM17UB310
84873222status LED | Same as RM17UB310
84873222supply frequency | Same as RM17UB310 Same as RM17UB310
84873222supply terminal | Same as RM17UB310
84873222supply voltage limits | Same as RM17UB310
84873222switching threshold drift | Same as RM17UB310 ¦ ,Measurement error with supply voltage variation, Same as RM17UB310 ¦ ,Measurement error with temperature variation,
84873222thermal current | Same as RM17UB310 ¦ IEC60947-5-1
84873222tightening torque | Same as RM17UB310 ¦ IEC60947-1,Tightening torque,
84873222time delay drift | Same as RM17UB310 Same as RM17UB310
84873222time delay range | Same as RM17UB310 ¦ ,"OFF" delay, Same as RM17UB310 ¦ ,"ON" delay, Same as RM17UB310 ¦ ,Inhibition,
84873222time delay type | Same as RM17UB310 ¦ ,"OFF" delay, Same as RM17UB310 ¦ ,"ON" delay, Same as RM17UB310 ¦ ,Inhibition,
84873222tripping threshold | Same as RM17UB310 ¦ ,Phase cut, Same as RM17UB310 ¦ ,Phase sequence, Same as RM17UB310 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17UB310 ¦ ,Over voltage, Same as RM17UB310 ¦ ,Undervoltage , Same as RM17UB310 ¦ ,Phase asymmetry, Same as RM17UB310 ¦ ,Disconnection of neutral, Same as RM17UB310 ¦ ,Voltage Regeneration, Same as RM17UB310 ¦ ,Extreme undervoltage (Phase loss), Same as RM17UB310 ¦ ,Extreme Overvoltage, Same as RM17UB310 ¦ ,Extreme Asymmetry,
84873222vibration resistance | Same as RM17UB310 ¦ IEC60068-2-6
84873222width | Same as RM17UB310 ¦ ,Width,
84873804 | Same as RM17TA00 ¦ IEC60721-3-3,Climatic category, Same as RM17TA00 ¦ Germanisher Lloyd,Environmental category, Same as RM17TA00 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM17TA00 ¦ ,Supply,Rated Same as RM17TA00 ¦ ,Input 1,Voltage Same as RM17TA00 ¦ ,Input 2,Spec Same as RM17TA00 ¦ ,Input 3, Same as RM17TA00 ¦ ,Output 1, Same as RM17TA00 ¦ ,Output 2, Same as RM17TA00 ¦ ,Measurement mode, Same as RM17TA00 Same as RM17TA00 Same as RM17TA00 Same as RM17TA00 Same as RM17TA00 ¦ ,MTTFd, Same as RM17TA00 ¦ ,B10d, Drawing / Diagram
84873804IP degree of protection | Same as RM17TA00 ¦ IEC60529,Terminal Block, Same as RM17TA00 ¦ IEC60529,Housing, Same as RM17TA00 ¦ IEC60529,Front Panel,
84873804Input nominal voltage selection | Same as RM17TA00 ¦ ,Input nominal voltage selection,
84873804Minimum distance to adjacent devices | Same as RM17TA00 ¦ ,Horizontal, Same as RM17TA00 ¦ ,Vertical,
84873804[Ie] rated operational current | Same as RM17TA00 ¦ IEC61810-1,Rated switching current,
84873804[Ue] rated operational voltage | Same as RM17TA00 ¦ IEC61810-1,Rated switching voltage,
84873804[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply, Same as RM17TA00 ¦ IEC60664-1,Input 1, Same as RM17TA00 ¦ IEC60664-1,Input 2, Same as RM17TA00 ¦ IEC60664-1,Input 3, Same as RM17TA00 ¦ IEC60664-1,Output 1, Same as RM17TA00 ¦ IEC60664-1,Output 2, Same as RM17TA00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TA00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TA00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TA00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TA00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TA00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 3,
84873804[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply, Same as RM17TA00 ¦ IEC60664-1,Input 1, Same as RM17TA00 ¦ IEC60664-1,Input 2, Same as RM17TA00 ¦ IEC60664-1,Input 3, Same as RM17TA00 ¦ IEC60664-1,Output 1, Same as RM17TA00 ¦ IEC60664-1,Output 2, Same as RM17TA00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TA00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TA00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TA00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TA00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TA00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 3,
84873804[Us] rated supply voltage | Same as RM17TA00
84873804ambient air temperature for operation | Same as RM17TA00 ¦ ,Operation,
84873804ambient air temperature for storage | Same as RM17TA00 ¦ ,Storage,
84873804bump resistance | Same as RM17TA00 ¦ IEC60068-2-29
84873804cable stripping length | Same as RM17TA00 ¦ ,Cable stripping length,
84873804circuit group | Same as RM17TA00 ¦ ,Supply,Terminal Same as RM17TA00 ¦ ,Input 1, Same as RM17TA00 ¦ ,Input 2, Same as RM17TA00 ¦ ,Input 3, Same as RM17TA00 ¦ ,Output 1, Same as RM17TA00 ¦ ,Output 2,
84873804connections - terminals | Same as RM17TA00 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17TA00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17TA00 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17TA00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873804contacts material | Same as RM17TA00
84873804depth | Same as RM17TA00 ¦ ,Depth,
84873804diagnostic button | Same as RM17TA00
84873804dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TA00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TA00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TA00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TA00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TA00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 3,
84873804directives | Same as RM17TA00 Same as RM17TA00 Same as RM17TA00
84873804duty time | Same as RM17TA00
84873804electrical durability | Same as RM17TA00 ¦ IEC60947-4-1,AC-1, Same as RM17TA00 ¦ IEC60947-4-1,DC-1, Same as RM17TA00 ¦ IEC60947-5-1,AC-15, Same as RM17TA00 ¦ IEC60947-5-1,DC-13,
84873804electromagnetic compatibility | Same as RM17TA00 ¦ ,Generic immunity standard, Same as RM17TA00 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17TA00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17TA00 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17TA00 ¦ IEC61000-4-5,Surge, Same as RM17TA00 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17TA00 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17TA00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17TA00 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17TA00 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17TA00 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM17TA00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17TA00 ¦ ,Generic emission standard, Same as RM17TA00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17TA00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17TA00 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17TA00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17TA00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17TA00 ¦ Germanisher Lloyd,Conducted emission,
84873804height | Same as RM17TA00 ¦ ,Height,
84873804hysteresis | Same as RM17TA00 ¦ ,Phase cut, Same as RM17TA00 ¦ ,Phase sequence, Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TA00 ¦ ,Over voltage, Same as RM17TA00 ¦ ,Undervoltage , Same as RM17TA00 ¦ ,Phase asymmetry, Same as RM17TA00 ¦ ,Disconnection of neutral, Same as RM17TA00 ¦ ,Voltage Regeneration, Same as RM17TA00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TA00 ¦ ,Extreme Overvoltage, Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873804immunity to microbreaks | Same as RM17TA00
84873804input frequency | Same as RM17TA00 ¦ ,Rated frequency, Same as RM17TA00 ¦ ,Frequency operating range,
84873804input terminal | Same as RM17TA00 ¦ ,Input terminal,
84873804insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TA00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TA00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TA00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TA00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TA00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 3,
84873804internal input resistance | Same as RM17TA00 ¦ ,Internal input resistance,
84873804local signalling | Same as RM17TA00 ¦ ,Power supply availability, Same as RM17TA00 ¦ ,Power supply not availability, Same as RM17TA00 ¦ ,Timing in-progress, Same as RM17TA00 ¦ ,Output is energized, Same as RM17TA00 ¦ ,Output is de-energized, Same as RM17TA00 ¦ ,Range Setting Changes, Same as RM17TA00 ¦ ,Phase Cut, Same as RM17TA00 ¦ ,Phase Sequence Swap, Same as RM17TA00 ¦ ,Undervoltage <U, Same as RM17TA00 ¦ ,Overvoltage >U, Same as RM17TA00 ¦ ,Phase Asymmetry, Same as RM17TA00 ¦ ,Voltage Regeneration, Same as RM17TA00 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17TA00 ¦ ,Extreme Overvoltage >U, Same as RM17TA00 ¦ ,Extreme Phase Asymmetry,
84873804marking | UL, CSA, CE, China ROHS
84873804maximum leakage current | Same as RM17TA00 ¦ IEC62314,Only for solid state output,
84873804maximum measuring cycle | Same as RM17TA00 ¦ ,Maximum measuring cycles,
84873804maximum switching capacity | Same as RM17TA00 ¦ ,Maximum switching voltage, Same as RM17TA00 ¦ ,Maximum switching current, Same as RM17TA00 ¦ ,Maximum switching capacity,
84873804maximum voltage drop | Same as RM17TA00 ¦ IEC62314,Only for solid state output,
84873804measurement method | Same as RM17TA00 ¦ ,Measurement method,
84873804measurement range | Same as RM17TA00 ¦ ,Phase lost , Same as RM17TA00 ¦ ,Phase sequence, Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TA00 ¦ ,Over voltage, Same as RM17TA00 ¦ ,Undervoltage , Same as RM17TA00 ¦ ,Phase asymmetry, Same as RM17TA00 ¦ ,Disconnection of neutral, Same as RM17TA00 ¦ ,Voltage Regeneration, Same as RM17TA00 ¦ ,Extreme undervoltage, Same as RM17TA00 ¦ ,Extreme Overvoltage, Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873804mechanical durability | Same as RM17TA00 ¦ IEC61810-1
84873804minimum switching capacity | Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching current, Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching capacity,
84873804monitoring functions | Same as RM17TA00 ¦ ,Phase lost , Same as RM17TA00 ¦ ,Phase sequence, Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TA00 ¦ ,Over voltage, Same as RM17TA00 ¦ ,Undervoltage , Same as RM17TA00 ¦ ,Phase asymmetry, Same as RM17TA00 ¦ ,Disconnection of neutral, Same as RM17TA00 ¦ ,Voltage Regeneration, Same as RM17TA00 ¦ ,Extreme undervoltage, Same as RM17TA00 ¦ ,Extreme overvoltage, Same as RM17TA00 ¦ ,Extreme asymmetry,
84873804mounting position | Same as RM17TA00 ¦ ,In relation to normal vertical mounting plane,
84873804mounting support | Same as RM17TA00 ¦ IEC/EN 60715,Without socket, Same as RM17TA00 ¦ IEC/EN 60715,With socket,
84873804net weight | Same as RM17TA00
84873804on-load factor | Same as RM17TA00
84873804output logic | Same as RM17TA00 ¦ ,R1 (11-12-14), Same as RM17TA00 ¦ ,R2 (21-22-24),
84873804output terminal | Same as RM17TA00
84873804output type | Same as RM17TA00
84873804overvoltage category | Same as RM17TA00 ¦ IEC60664-1
84873804permissible input overload | Same as RM17TA00 ¦ ,permissible input overload,
84873804polarity | Same as RM17TA00
84873804pollution degree | Same as RM17TA00 ¦ IEC60664-1
84873804power consumption | Same as RM17TA00
84873804power on delay | Same as RM17TA00
84873804product certifications | UL, CSA, CE, China ROHS
84873804relative humidity | Same as RM17TA00 ¦ IEC60068-2-30,Damp heat,XX
84873804release of input voltage | Same as RM17TA00
84873804repeat accuracy of the switching threshold | Same as RM17TA00 ¦ ,Repeat accuracy (constant parameters),
84873804repeat accuracy of time delay | Same as RM17TA00
84873804reset time | Same as RM17TA00 ¦ ,through Un power reset, Same as RM17TA00 ¦ ,through front panel reset, Same as RM17TA00 ¦ ,through input control reset,
84873804response time | Same as RM17TA00 ¦ ,on crossing the threshold, Same as RM17TA00 Same as RM17TA00 Same as RM17TA00 Same as RM17TA00
84873804safety reliability data | Same as RM17TA00 ¦ ,MTTF, Same as RM17TA00 ¦ ,B10,
84873804seismic resistance | Same as RM17TA00 ¦ IEC60068-3-3
84873804setting accuracy of the switching threshold | Same as RM17TA00 ¦ ,Setting accuracy,
84873804setting accuracy of time delay | Same as RM17TA00
84873804shock resistance | Same as RM17TA00 ¦ IEC60068-2-27
84873804short circuit protection | Same as RM17TA00 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17TA00 ¦ IEC62314,Solid State Output by external fuse,
84873804standards | Same as RM17TA00
84873804status LED | Same as RM17TA00
84873804supply frequency | Same as RM17TA00 Same as RM17TA00
84873804supply terminal | Same as RM17TA00
84873804supply voltage limits | Same as RM17TA00
84873804switching threshold drift | Same as RM17TA00 ¦ ,Measurement error with supply voltage variation, Same as RM17TA00 ¦ ,Measurement error with temperature variation,
84873804thermal current | Same as RM17TA00 ¦ IEC60947-5-1
84873804tightening torque | Same as RM17TA00 ¦ IEC60947-1,Tightening torque,
84873804time delay drift | Same as RM17TA00 Same as RM17TA00
84873804time delay range | Same as RM17TA00 ¦ ,"OFF" delay, Same as RM17TA00 ¦ ,"ON" delay, Same as RM17TA00 ¦ ,Inhibition,
84873804time delay type | Same as RM17TA00 ¦ ,"OFF" delay, Same as RM17TA00 ¦ ,"ON" delay, Same as RM17TA00 ¦ ,Inhibition,
84873804tripping threshold | Same as RM17TA00 ¦ ,Phase cut, Same as RM17TA00 ¦ ,Phase sequence, Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TA00 ¦ ,Over voltage, Same as RM17TA00 ¦ ,Undervoltage , Same as RM17TA00 ¦ ,Phase asymmetry, Same as RM17TA00 ¦ ,Disconnection of neutral, Same as RM17TA00 ¦ ,Voltage Regeneration, Same as RM17TA00 ¦ ,Extreme undervoltage (Phase loss), When > 543V +/- 5% last longer than 2s +/- 10% , output de-energized When > 543V +/- 5% last shorter than 2s +/- 10% , output energized ¦ ,Extreme Overvoltage, Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873804vibration resistance | Same as RM17TA00 ¦ IEC60068-2-6
84873804width | Same as RM17TA00 ¦ ,Width,
84873805 | Same as RM17TU00 ¦ IEC60721-3-3,Climatic category, Same as RM17TU00 ¦ Germanisher Lloyd,Environmental category, Same as RM17TU00 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM17TU00 ¦ ,Supply,Rated Same as RM17TU00 ¦ ,Input 1,Voltage Same as RM17TU00 ¦ ,Input 2,Spec Same as RM17TU00 ¦ ,Input 3, Same as RM17TU00 ¦ ,Output 1, Same as RM17TU00 ¦ ,Output 2, Same as RM17TU00 ¦ ,Measurement mode, Same as RM17TU00 Same as RM17TU00 Same as RM17TU00 Same as RM17TU00 Same as RM17TU00 ¦ ,MTTFd, Same as RM17TU00 ¦ ,B10d, Drawing / Diagram
84873805IP degree of protection | Same as RM17TU00 ¦ IEC60529,Terminal Block, Same as RM17TU00 ¦ IEC60529,Housing, Same as RM17TU00 ¦ IEC60529,Front Panel,
84873805Input nominal voltage selection | - ¦ ,Input nominal voltage selection,
84873805Minimum distance to adjacent devices | Same as RM17TU00 ¦ ,Horizontal, Same as RM17TU00 ¦ ,Vertical,
84873805[Ie] rated operational current | Same as RM17TU00 ¦ IEC61810-1,Rated switching current,
84873805[Ue] rated operational voltage | Same as RM17TU00 ¦ IEC61810-1,Rated switching voltage,
84873805[Ui] rated insulation voltage | Same as RM17TU00 ¦ IEC60664-1,Supply, Same as RM17TU00 ¦ IEC60664-1,Input 1, Same as RM17TU00 ¦ IEC60664-1,Input 2, Same as RM17TU00 ¦ IEC60664-1,Input 3, Same as RM17TU00 ¦ IEC60664-1,Output 1, Same as RM17TU00 ¦ IEC60664-1,Output 2, Same as RM17TU00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TU00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TU00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TU00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TU00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TU00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TU00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TU00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TU00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TU00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TU00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TU00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TU00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TU00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TU00 ¦ IEC60664-1,Input 1 / Input 3,
84873805[Uimp] rated impulse withstand voltage | Same as RM17TU00 ¦ IEC60664-1,Supply, Same as RM17TU00 ¦ IEC60664-1,Input 1, Same as RM17TU00 ¦ IEC60664-1,Input 2, Same as RM17TU00 ¦ IEC60664-1,Input 3, Same as RM17TU00 ¦ IEC60664-1,Output 1, Same as RM17TU00 ¦ IEC60664-1,Output 2, Same as RM17TU00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TU00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TU00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TU00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TU00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TU00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TU00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TU00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TU00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TU00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TU00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TU00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TU00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TU00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TU00 ¦ IEC60664-1,Input 1 / Input 3,
84873805[Us] rated supply voltage | Same as RM17TU00
84873805ambient air temperature for operation | Same as RM17TU00 ¦ ,Operation,
84873805ambient air temperature for storage | Same as RM17TU00 ¦ ,Storage,
84873805bump resistance | Same as RM17TU00 ¦ IEC60068-2-29
84873805cable stripping length | Same as RM17TU00 ¦ ,Cable stripping length,
84873805circuit group | Same as RM17TU00 ¦ ,Supply,Terminal Same as RM17TU00 ¦ ,Input 1, Same as RM17TU00 ¦ ,Input 2, Same as RM17TU00 ¦ ,Input 3, Same as RM17TU00 ¦ ,Output 1, Same as RM17TU00 ¦ ,Output 2,
84873805connections - terminals | Same as RM17TU00 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17TU00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17TU00 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17TU00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873805contacts material | Same as RM17TU00
84873805depth | Same as RM17TU00 ¦ ,Depth,
84873805diagnostic button | Same as RM17TU00
84873805dielectric strength | Same as RM17TU00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TU00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TU00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TU00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TU00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TU00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TU00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TU00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TU00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TU00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TU00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TU00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TU00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TU00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TU00 ¦ IEC60255-27,Input 1 / Input 3,
84873805directives | Same as RM17TU00 Same as RM17TU00 Same as RM17TU00
84873805duty time | Same as RM17TU00
84873805electrical durability | Same as RM17TU00 ¦ IEC60947-4-1,AC-1, Same as RM17TU00 ¦ IEC60947-4-1,DC-1, Same as RM17TU00 ¦ IEC60947-5-1,AC-15, Same as RM17TU00 ¦ IEC60947-5-1,DC-13,
84873805electromagnetic compatibility | Same as RM17TU00 ¦ ,Generic immunity standard, Same as RM17TU00 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17TU00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17TU00 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17TU00 ¦ IEC61000-4-5,Surge, Same as RM17TU00 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17TU00 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17TU00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17TU00 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17TU00 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17TU00 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM17TU00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17TU00 ¦ ,Generic emission standard, Same as RM17TU00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17TU00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17TU00 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17TU00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17TU00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17TU00 ¦ Germanisher Lloyd,Conducted emission,
84873805height | Same as RM17TU00 ¦ ,Height,
84873805hysteresis | Same as RM17TU00 ¦ ,Phase cut, Same as RM17TU00 ¦ ,Phase sequence, Same as RM17TU00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TU00 ¦ ,Over voltage, Fixed 5% of selected Un Internal design spec: 5% +/- 1.5% ¦ ,Undervoltage , Same as RM17TU00 ¦ ,Phase asymmetry, Same as RM17TU00 ¦ ,Disconnection of neutral, Same as RM17TU00 ¦ ,Voltage Regeneration, Same as RM17TU00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TU00 ¦ ,Extreme Overvoltage, Same as RM17TU00 ¦ ,Extreme Asymmetry,
84873805immunity to microbreaks | Same as RM17TU00
84873805input frequency | Same as RM17TU00 ¦ ,Rated frequency, Same as RM17TU00 ¦ ,Frequency operating range,
84873805input terminal | Same as RM17TU00 ¦ ,Input terminal,
84873805insulation resistance | Same as RM17TU00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TU00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TU00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TU00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TU00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TU00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TU00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TU00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TU00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TU00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TU00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TU00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TU00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TU00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TU00 ¦ IEC60255-27,Input 1 / Input 3,
84873805internal input resistance | Same as RM17TU00 ¦ ,Internal input resistance,
84873805local signalling | - ¦ ,Power supply availability, - ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, - ¦ ,Range Setting Changes, Same as RM17TU00 ¦ ,Phase Cut, Same as RM17TU00 ¦ ,Phase Sequence Swap, Same as RM17TU00 ¦ ,Undervoltage <U, Same as RM17TU00 ¦ ,Overvoltage >U, Same as RM17TU00 ¦ ,Phase Asymmetry, Same as RM17TU00 ¦ ,Voltage Regeneration, Same as RM17TU00 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17TU00 ¦ ,Extreme Overvoltage >U, Same as RM17TU00 ¦ ,Extreme Phase Asymmetry,
84873805marking | UL, CSA, CE, China ROHS
84873805maximum leakage current | Same as RM17TU00 ¦ IEC62314,Only for solid state output,
84873805maximum measuring cycle | Same as RM17TU00 ¦ ,Maximum measuring cycles,
84873805maximum switching capacity | Same as RM17TU00 ¦ ,Maximum switching voltage, Same as RM17TU00 ¦ ,Maximum switching current, Same as RM17TU00 ¦ ,Maximum switching capacity,
84873805maximum voltage drop | Same as RM17TU00 ¦ IEC62314,Only for solid state output,
84873805measurement method | Same as RM17TU00 ¦ ,Measurement method,
84873805measurement range | Same as RM17TU00 ¦ ,Phase lost , Same as RM17TU00 ¦ ,Phase sequence, Same as RM17TU00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TU00 ¦ ,Over voltage, Fixed 400 ¦ ,Undervoltage , Same as RM17TU00 ¦ ,Phase asymmetry, Same as RM17TU00 ¦ ,Disconnection of neutral, Same as RM17TU00 ¦ ,Voltage Regeneration, Same as RM17TU00 ¦ ,Extreme undervoltage, Same as RM17TU00 ¦ ,Extreme Overvoltage, Same as RM17TU00 ¦ ,Extreme Asymmetry,
84873805mechanical durability | Same as RM17TU00 ¦ IEC61810-1
84873805minimum switching capacity | Same as RM17TU00 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17TU00 ¦ IEC60947-5-4,Minimum switching current, Same as RM17TU00 ¦ IEC60947-5-4,Minimum switching capacity,
84873805monitoring functions | Same as RM17TU00 ¦ ,Phase lost , Same as RM17TU00 ¦ ,Phase sequence, Same as RM17TU00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TU00 ¦ ,Over voltage, Same as RM17TU00 ¦ ,Undervoltage , Same as RM17TU00 ¦ ,Phase asymmetry, Same as RM17TU00 ¦ ,Disconnection of neutral, Same as RM17TU00 ¦ ,Voltage Regeneration, Same as RM17TU00 ¦ ,Extreme undervoltage, Same as RM17TU00 ¦ ,Extreme overvoltage, Same as RM17TU00 ¦ ,Extreme asymmetry,
84873805mounting position | Same as RM17TU00 ¦ ,In relation to normal vertical mounting plane,
84873805mounting support | Same as RM17TU00 ¦ IEC/EN 60715,Without socket, Same as RM17TU00 ¦ IEC/EN 60715,With socket,
84873805net weight | Same as RM17TU00
84873805on-load factor | Same as RM17TU00
84873805output logic | Same as RM17TU00 ¦ ,R1 (11-12-14), Same as RM17TU00 ¦ ,R2 (21-22-24),
84873805output terminal | Same as RM17TU00
84873805output type | Same as RM17TU00
84873805overvoltage category | Same as RM17TU00 ¦ IEC60664-1
84873805permissible input overload | Same as RM17TU00 ¦ ,permissible input overload,
84873805polarity | Same as RM17TU00
84873805pollution degree | Same as RM17TU00 ¦ IEC60664-1
84873805power consumption | Same as RM17TU00
84873805power on delay | Same as RM17TU00
84873805product certifications | UL, CSA, CE, China ROHS
84873805relative humidity | Same as RM17TU00 ¦ IEC60068-2-30,Damp heat,XX
84873805release of input voltage | Same as RM17TU00
84873805repeat accuracy of the switching threshold | Same as RM17TU00 ¦ ,Repeat accuracy (constant parameters),
84873805repeat accuracy of time delay | Same as RM17TU00
84873805reset time | Same as RM17TU00 ¦ ,through Un power reset, Same as RM17TU00 ¦ ,through front panel reset, Same as RM17TU00 ¦ ,through input control reset,
84873805response time | Same as RM17TU00 ¦ ,on crossing the threshold, Same as RM17TU00 Same as RM17TU00 Same as RM17TU00 Same as RM17TU00
84873805safety reliability data | Same as RM17TU00 ¦ ,MTTF, Same as RM17TU00 ¦ ,B10,
84873805seismic resistance | Same as RM17TU00 ¦ IEC60068-3-3
84873805setting accuracy of the switching threshold | Same as RM17TU00 ¦ ,Setting accuracy,
84873805setting accuracy of time delay | Same as RM17TU00
84873805shock resistance | Same as RM17TU00 ¦ IEC60068-2-27
84873805short circuit protection | Same as RM17TU00 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17TU00 ¦ IEC62314,Solid State Output by external fuse,
84873805standards | Same as RM17TU00
84873805status LED | R (Amber)
84873805supply frequency | Same as RM17TU00 Same as RM17TU00
84873805supply terminal | Same as RM17TU00
84873805supply voltage limits | Same as RM17TU00
84873805switching threshold drift | Same as RM17TU00 ¦ ,Measurement error with supply voltage variation, Same as RM17TU00 ¦ ,Measurement error with temperature variation,
84873805thermal current | Same as RM17TU00 ¦ IEC60947-5-1
84873805tightening torque | Same as RM17TU00 ¦ IEC60947-1,Tightening torque,
84873805time delay drift | Same as RM17TU00 Same as RM17TU00
84873805time delay range | Fixed 3.5s +/- 5% ¦ ,"OFF" delay, Same as RM17TU00 ¦ ,"ON" delay, Same as RM17TU00 ¦ ,Inhibition,
84873805time delay type | Same as RM17TU00 ¦ ,"OFF" delay, Same as RM17TU00 ¦ ,"ON" delay, Same as RM17TU00 ¦ ,Inhibition,
84873805tripping threshold | Same as RM17TU00 ¦ ,Phase cut, Same as RM17TU00 ¦ ,Phase sequence, Same as RM17TU00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TU00 ¦ ,Over voltage, Fixed -10% of Un ¦ ,Undervoltage , Same as RM17TU00 ¦ ,Phase asymmetry, Same as RM17TU00 ¦ ,Disconnection of neutral, Same as RM17TU00 ¦ ,Voltage Regeneration, Same as RM17TU00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TU00 ¦ ,Extreme Overvoltage, Same as RM17TU00 ¦ ,Extreme Asymmetry,
84873805vibration resistance | Same as RM17TU00 ¦ IEC60068-2-6
84873805width | Same as RM17TU00 ¦ ,Width,
84873890 | Same as RM17TG00 ¦ IEC60721-3-3,Climatic category, Same as RM17TG00 ¦ Germanisher Lloyd,Environmental category, Same as RM17TG00 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM17TG00 ¦ ,Supply,Rated Same as RM17TG00 ¦ ,Input 1,Voltage Same as RM17TG00 ¦ ,Input 2,Spec Same as RM17TG00 ¦ ,Input 3, Same as RM17TG00 ¦ ,Output 1, Same as RM17TG00 ¦ ,Output 2, Same as RM17TG00 ¦ ,Measurement mode, Same as RM17TG00 Same as RM17TG00 Same as RM17TG00 Same as RM17TG00 Same as RM17TG00 ¦ ,MTTFd, Same as RM17TG00 ¦ ,B10d, Drawing / Diagram
84873890IP degree of protection | Same as RM17TG00 ¦ IEC60529,Terminal Block, Same as RM17TG00 ¦ IEC60529,Housing, Same as RM17TG00 ¦ IEC60529,Front Panel,
84873890Input nominal voltage selection | Same as RM17TG00 ¦ ,Input nominal voltage selection,
84873890Minimum distance to adjacent devices | Same as RM17TG00 ¦ ,Horizontal, Same as RM17TG00 ¦ ,Vertical,
84873890[Ie] rated operational current | Same as RM17TG00 ¦ IEC61810-1,Rated switching current,
84873890[Ue] rated operational voltage | Same as RM17TG00 ¦ IEC61810-1,Rated switching voltage,
84873890[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply, Same as RM17TG00 ¦ IEC60664-1,Input 1, Same as RM17TG00 ¦ IEC60664-1,Input 2, Same as RM17TG00 ¦ IEC60664-1,Input 3, Same as RM17TG00 ¦ IEC60664-1,Output 1, Same as RM17TG00 ¦ IEC60664-1,Output 2, Same as RM17TG00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TG00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TG00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TG00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TG00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TG00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 3,
84873890[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply, Same as RM17TG00 ¦ IEC60664-1,Input 1, Same as RM17TG00 ¦ IEC60664-1,Input 2, Same as RM17TG00 ¦ IEC60664-1,Input 3, Same as RM17TG00 ¦ IEC60664-1,Output 1, Same as RM17TG00 ¦ IEC60664-1,Output 2, Same as RM17TG00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TG00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TG00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TG00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TG00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TG00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 3,
84873890[Us] rated supply voltage | Same as RM17TG00
84873890ambient air temperature for operation | Same as RM17TG00 ¦ ,Operation,
84873890ambient air temperature for storage | Same as RM17TG00 ¦ ,Storage,
84873890bump resistance | Same as RM17TG00 ¦ IEC60068-2-29
84873890cable stripping length | Same as RM17TG00 ¦ ,Cable stripping length,
84873890circuit group | Same as RM17TG00 ¦ ,Supply,Terminal Same as RM17TG00 ¦ ,Input 1, Same as RM17TG00 ¦ ,Input 2, Same as RM17TG00 ¦ ,Input 3, Same as RM17TG00 ¦ ,Output 1, Same as RM17TG00 ¦ ,Output 2,
84873890connections - terminals | Same as RM17TG00 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17TG00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17TG00 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17TG00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873890contacts material | Same as RM17TG00
84873890depth | Same as RM17TG00 ¦ ,Depth,
84873890diagnostic button | Same as RM17TG00
84873890dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TG00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TG00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TG00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TG00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TG00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 3,
84873890directives | Same as RM17TG00 Same as RM17TG00 Same as RM17TG00
84873890duty time | Same as RM17TG00
84873890electrical durability | Same as RM17TG00 ¦ IEC60947-4-1,AC-1, Same as RM17TG00 ¦ IEC60947-4-1,DC-1, Same as RM17TG00 ¦ IEC60947-5-1,AC-15, Same as RM17TG00 ¦ IEC60947-5-1,DC-13,
84873890electromagnetic compatibility | Same as RM17TG00 ¦ ,Generic immunity standard, Same as RM17TG00 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17TG00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17TG00 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17TG00 ¦ IEC61000-4-5,Surge, Same as RM17TG00 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17TG00 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17TG00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17TG00 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17TG00 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17TG00 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM17TG00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17TG00 ¦ ,Generic emission standard, Same as RM17TG00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17TG00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17TG00 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17TG00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17TG00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17TG00 ¦ Germanisher Lloyd,Conducted emission,
84873890height | Same as RM17TG00 ¦ ,Height,
84873890hysteresis | Same as RM17TG00 ¦ ,Phase cut, Same as RM17TG00 ¦ ,Phase sequence, Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG00 ¦ ,Over voltage, Same as RM17TG00 ¦ ,Undervoltage , Same as RM17TG00 ¦ ,Phase asymmetry, Same as RM17TG00 ¦ ,Disconnection of neutral, Same as RM17TG00 ¦ ,Voltage Regeneration, Same as RM17TG00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TG00 ¦ ,Extreme Overvoltage, Same as RM17TG00 ¦ ,Extreme Asymmetry,
84873890immunity to microbreaks | Same as RM17TG00
84873890input frequency | Same as RM17TG00 ¦ ,Rated frequency, Same as RM17TG00 ¦ ,Frequency operating range,
84873890input terminal | Same as RM17TG00 ¦ ,Input terminal,
84873890insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TG00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TG00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TG00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TG00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TG00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 3,
84873890internal input resistance | Same as RM17TG00 ¦ ,Internal input resistance,
84873890local signalling | Same as RM17TG00 ¦ ,Power supply availability, Same as RM17TG00 ¦ ,Power supply not availability, Same as RM17TG00 ¦ ,Timing in-progress, Same as RM17TG00 ¦ ,Output is energized, Same as RM17TG00 ¦ ,Output is de-energized, Same as RM17TG00 ¦ ,Range Setting Changes, Same as RM17TG00 ¦ ,Phase Cut, Same as RM17TG00 ¦ ,Phase Sequence Swap, Same as RM17TG00 ¦ ,Undervoltage <U, Same as RM17TG00 ¦ ,Overvoltage >U, Same as RM17TG00 ¦ ,Phase Asymmetry, Same as RM17TG00 ¦ ,Voltage Regeneration, Same as RM17TG00 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17TG00 ¦ ,Extreme Overvoltage >U, Same as RM17TG00 ¦ ,Extreme Phase Asymmetry,
84873890marking | UL, CSA, CE, China ROHS
84873890maximum leakage current | Same as RM17TG00 ¦ IEC62314,Only for solid state output,
84873890maximum measuring cycle | Same as RM17TG00 ¦ ,Maximum measuring cycles,
84873890maximum switching capacity | Same as RM17TG00 ¦ ,Maximum switching voltage, Same as RM17TG00 ¦ ,Maximum switching current, Same as RM17TG00 ¦ ,Maximum switching capacity,
84873890maximum voltage drop | Same as RM17TG00 ¦ IEC62314,Only for solid state output,
84873890measurement method | Same as RM17TG00 ¦ ,Measurement method,
84873890measurement range | Same as RM17TG00 ¦ ,Phase lost , Same as RM17TG00 ¦ ,Phase sequence, Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG00 ¦ ,Over voltage, Same as RM17TG00 ¦ ,Undervoltage , Same as RM17TG00 ¦ ,Phase asymmetry, Same as RM17TG00 ¦ ,Disconnection of neutral, Same as RM17TG00 ¦ ,Voltage Regeneration, Same as RM17TG00 ¦ ,Extreme undervoltage, Same as RM17TG00 ¦ ,Extreme Overvoltage, Same as RM17TG00 ¦ ,Extreme Asymmetry,
84873890mechanical durability | Same as RM17TG00 ¦ IEC61810-1
84873890minimum switching capacity | Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching current, Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching capacity,
84873890monitoring functions | Same as RM17TG00 ¦ ,Phase lost , Same as RM17TG00 ¦ ,Phase sequence, Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG00 ¦ ,Over voltage, Same as RM17TG00 ¦ ,Undervoltage , Same as RM17TG00 ¦ ,Phase asymmetry, Same as RM17TG00 ¦ ,Disconnection of neutral, Same as RM17TG00 ¦ ,Voltage Regeneration, Same as RM17TG00 ¦ ,Extreme undervoltage, Same as RM17TG00 ¦ ,Extreme overvoltage, Same as RM17TG00 ¦ ,Extreme asymmetry,
84873890mounting position | Same as RM17TG00 ¦ ,In relation to normal vertical mounting plane,
84873890mounting support | Same as RM17TG00 ¦ IEC/EN 60715,Without socket, Same as RM17TG00 ¦ IEC/EN 60715,With socket,
84873890net weight | Same as RM17TG00
84873890on-load factor | Same as RM17TG00
84873890output logic | Same as RM17TG00 ¦ ,R1 (11-12-14), Same as RM17TG00 ¦ ,R2 (21-22-24),
84873890output terminal | Same as RM17TG00
84873890output type | Same as RM17TG00
84873890overvoltage category | Same as RM17TG00 ¦ IEC60664-1
84873890permissible input overload | Same as RM17TG00 ¦ ,permissible input overload,
84873890polarity | Same as RM17TG00
84873890pollution degree | Same as RM17TG00 ¦ IEC60664-1
84873890power consumption | Same as RM17TG00
84873890power on delay | Same as RM17TG00
84873890product certifications | UL, CSA, CE, China ROHS
84873890relative humidity | Same as RM17TG00 ¦ IEC60068-2-30,Damp heat,XX
84873890release of input voltage | Same as RM17TG00
84873890repeat accuracy of the switching threshold | Same as RM17TG00 ¦ ,Repeat accuracy (constant parameters),
84873890repeat accuracy of time delay | Same as RM17TG00
84873890reset time | Same as RM17TG00 ¦ ,through Un power reset, Same as RM17TG00 ¦ ,through front panel reset, Same as RM17TG00 ¦ ,through input control reset,
84873890response time | Same as RM17TG00 ¦ ,on crossing the threshold, Same as RM17TG00 Same as RM17TG00 Same as RM17TG00 Same as RM17TG00
84873890safety reliability data | Same as RM17TG00 ¦ ,MTTF, Same as RM17TG00 ¦ ,B10,
84873890seismic resistance | Same as RM17TG00 ¦ IEC60068-3-3
84873890setting accuracy of the switching threshold | Same as RM17TG00 ¦ ,Setting accuracy,
84873890setting accuracy of time delay | Same as RM17TG00
84873890shock resistance | Same as RM17TG00 ¦ IEC60068-2-27
84873890short circuit protection | Same as RM17TG00 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17TG00 ¦ IEC62314,Solid State Output by external fuse,
84873890standards | Same as RM17TG00
84873890status LED | Same as RM17TG00
84873890supply frequency | Same as RM17TG00 Same as RM17TG00
84873890supply terminal | Same as RM17TG00
84873890supply voltage limits | Same as RM17TG00
84873890switching threshold drift | Same as RM17TG00 ¦ ,Measurement error with supply voltage variation, Same as RM17TG00 ¦ ,Measurement error with temperature variation,
84873890thermal current | Same as RM17TG00 ¦ IEC60947-5-1
84873890tightening torque | Same as RM17TG00 ¦ IEC60947-1,Tightening torque,
84873890time delay drift | Same as RM17TG00 Same as RM17TG00
84873890time delay range | Same as RM17TG00 ¦ ,"OFF" delay, Same as RM17TG00 ¦ ,"ON" delay, Same as RM17TG00 ¦ ,Inhibition,
84873890time delay type | Same as RM17TG00 ¦ ,"OFF" delay, Same as RM17TG00 ¦ ,"ON" delay, Same as RM17TG00 ¦ ,Inhibition,
84873890tripping threshold | Same as RM17TG00 ¦ ,Phase cut, Same as RM17TG00 ¦ ,Phase sequence, Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG00 ¦ ,Over voltage, Same as RM17TG00 ¦ ,Undervoltage , Same as RM17TG00 ¦ ,Phase asymmetry, Same as RM17TG00 ¦ ,Disconnection of neutral, Same as RM17TG00 ¦ ,Voltage Regeneration, Same as RM17TG00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TG00 ¦ ,Extreme Overvoltage, Same as RM17TG00 ¦ ,Extreme Asymmetry,
84873890vibration resistance | Same as RM17TG00 ¦ IEC60068-2-6
84873890width | Same as RM17TG00 ¦ ,Width,
84873891 | Same as RM17TG20 ¦ IEC60721-3-3,Climatic category, Same as RM17TG20 ¦ Germanisher Lloyd,Environmental category, Same as RM17TG20 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM17TG20 ¦ ,Supply,Rated Same as RM17TG20 ¦ ,Input 1,Voltage Same as RM17TG20 ¦ ,Input 2,Spec Same as RM17TG20 ¦ ,Input 3, Same as RM17TG20 ¦ ,Output 1, Same as RM17TG20 ¦ ,Output 2, Same as RM17TG20 ¦ ,Measurement mode, Same as RM17TG20 Same as RM17TG20 Same as RM17TG20 Same as RM17TG20 Same as RM17TG20 ¦ ,MTTFd, Same as RM17TG20 ¦ ,B10d, Drawing / Diagram
84873891IP degree of protection | Same as RM17TG20 ¦ IEC60529,Terminal Block, Same as RM17TG20 ¦ IEC60529,Housing, - ¦ IEC60529,Front Panel,
84873891Input nominal voltage selection | Same as RM17TG20 ¦ ,Input nominal voltage selection,
84873891Minimum distance to adjacent devices | Same as RM17TG20 ¦ ,Horizontal, Same as RM17TG20 ¦ ,Vertical,
84873891[Ie] rated operational current | Same as RM17TG20 ¦ IEC61810-1,Rated switching current,
84873891[Ue] rated operational voltage | Same as RM17TG20 ¦ IEC61810-1,Rated switching voltage,
84873891[Ui] rated insulation voltage | Same as RM17TG20 ¦ IEC60664-1,Supply, Same as RM17TG20 ¦ IEC60664-1,Input 1, Same as RM17TG20 ¦ IEC60664-1,Input 2, Same as RM17TG20 ¦ IEC60664-1,Input 3, Same as RM17TG20 ¦ IEC60664-1,Output 1, Same as RM17TG20 ¦ IEC60664-1,Output 2, Same as RM17TG20 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TG20 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TG20 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TG20 ¦ IEC60664-1,Supply / Output 1, Same as RM17TG20 ¦ IEC60664-1,Supply / Output 2, Same as RM17TG20 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 3,
84873891[Uimp] rated impulse withstand voltage | Same as RM17TG20 ¦ IEC60664-1,Supply, Same as RM17TG20 ¦ IEC60664-1,Input 1, Same as RM17TG20 ¦ IEC60664-1,Input 2, Same as RM17TG20 ¦ IEC60664-1,Input 3, Same as RM17TG20 ¦ IEC60664-1,Output 1, Same as RM17TG20 ¦ IEC60664-1,Output 2, Same as RM17TG20 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TG20 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TG20 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TG20 ¦ IEC60664-1,Supply / Output 1, Same as RM17TG20 ¦ IEC60664-1,Supply / Output 2, Same as RM17TG20 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 3,
84873891[Us] rated supply voltage | Same as RM17TG20
84873891ambient air temperature for operation | Same as RM17TG20 ¦ ,Operation,
84873891ambient air temperature for storage | Same as RM17TG20 ¦ ,Storage,
84873891bump resistance | Same as RM17TG20 ¦ IEC60068-2-29
84873891cable stripping length | Same as RM17TG20 ¦ ,Cable stripping length,
84873891circuit group | Same as RM17TG20 ¦ ,Supply,Terminal Same as RM17TG20 ¦ ,Input 1, Same as RM17TG20 ¦ ,Input 2, Same as RM17TG20 ¦ ,Input 3, Same as RM17TG20 ¦ ,Output 1, Same as RM17TG20 ¦ ,Output 2,
84873891connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17TG20 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17TG20 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17TG20 ¦ IEC60947-1,Flexible cable (spring terminal),
84873891contacts material | Same as RM17TG20
84873891depth | Same as RM17TG20 ¦ ,Depth,
84873891diagnostic button | Same as RM17TG20
84873891dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 1, Same as RM17TG20 ¦ IEC60255-27,Supply / Input 2, Same as RM17TG20 ¦ IEC60255-27,Supply / Input 3, Same as RM17TG20 ¦ IEC60255-27,Supply / Output 1, Same as RM17TG20 ¦ IEC60255-27,Supply / Output 2, Same as RM17TG20 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 3,
84873891directives | Same as RM17TG20 Same as RM17TG20 Same as RM17TG20
84873891duty time | Same as RM17TG20
84873891electrical durability | Same as RM17TG20 ¦ IEC60947-4-1,AC-1, Same as RM17TG20 ¦ IEC60947-4-1,DC-1, Same as RM17TG20 ¦ IEC60947-5-1,AC-15, Same as RM17TG20 ¦ IEC60947-5-1,DC-13,
84873891electromagnetic compatibility | Same as RM17TG20 ¦ ,Generic immunity standard, Same as RM17TG20 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17TG20 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17TG20 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17TG20 ¦ IEC61000-4-5,Surge, Same as RM17TG20 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17TG20 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17TG20 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17TG20 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17TG20 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17TG20 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM17TG20 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17TG20 ¦ ,Generic emission standard, Same as RM17TG20 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17TG20 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17TG20 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17TG20 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17TG20 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17TG20 ¦ Germanisher Lloyd,Conducted emission,
84873891height | Same as RM17TG20 ¦ ,Height,
84873891hysteresis | Same as RM17TG20 ¦ ,Phase cut, Same as RM17TG20 ¦ ,Phase sequence, Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG20 ¦ ,Over voltage, Same as RM17TG20 ¦ ,Undervoltage , Same as RM17TG20 ¦ ,Phase asymmetry, Same as RM17TG20 ¦ ,Disconnection of neutral, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TG20 ¦ ,Extreme Overvoltage, Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873891immunity to microbreaks | Same as RM17TG20
84873891input frequency | Same as RM17TG20 ¦ ,Rated frequency, Same as RM17TG20 ¦ ,Frequency operating range,
84873891input terminal | Same as RM17TG20 ¦ ,Input terminal,
84873891insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 1, Same as RM17TG20 ¦ IEC60255-27,Supply / Input 2, Same as RM17TG20 ¦ IEC60255-27,Supply / Input 3, Same as RM17TG20 ¦ IEC60255-27,Supply / Output 1, Same as RM17TG20 ¦ IEC60255-27,Supply / Output 2, Same as RM17TG20 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 3,
84873891internal input resistance | Same as RM17TG20 ¦ ,Internal input resistance,
84873891local signalling | Same as RM17TG20 ¦ ,Power supply availability, Same as RM17TG20 ¦ ,Power supply not availability, Same as RM17TG20 ¦ ,Timing in-progress, Same as RM17TG20 ¦ ,Output is energized, Same as RM17TG20 ¦ ,Output is de-energized, Same as RM17TG20 ¦ ,Range Setting Changes, Same as RM17TG20 ¦ ,Phase Cut, Same as RM17TG20 ¦ ,Phase Sequence Swap, Same as RM17TG20 ¦ ,Undervoltage <U, Same as RM17TG20 ¦ ,Overvoltage >U, Same as RM17TG20 ¦ ,Phase Asymmetry, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17TG20 ¦ ,Extreme Overvoltage >U, Same as RM17TG20 ¦ ,Extreme Phase Asymmetry,
84873891marking | UL, CSA, CE, China ROHS
84873891maximum leakage current | Same as RM17TG20 ¦ IEC62314,Only for solid state output,
84873891maximum measuring cycle | Same as RM17TG20 ¦ ,Maximum measuring cycles,
84873891maximum switching capacity | Same as RM17TG20 ¦ ,Maximum switching voltage, Same as RM17TG20 ¦ ,Maximum switching current, Same as RM17TG20 ¦ ,Maximum switching capacity,
84873891maximum voltage drop | Same as RM17TG20 ¦ IEC62314,Only for solid state output,
84873891measurement method | Same as RM17TG20 ¦ ,Measurement method,
84873891measurement range | Same as RM17TG20 ¦ ,Phase lost , Same as RM17TG20 ¦ ,Phase sequence, Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG20 ¦ ,Over voltage, Same as RM17TG20 ¦ ,Undervoltage , Same as RM17TG20 ¦ ,Phase asymmetry, Same as RM17TG20 ¦ ,Disconnection of neutral, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme undervoltage, Same as RM17TG20 ¦ ,Extreme Overvoltage, Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873891mechanical durability | Same as RM17TG20 ¦ IEC61810-1
84873891minimum switching capacity | Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching current, Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching capacity,
84873891monitoring functions | Same as RM17TG20 ¦ ,Phase lost , Same as RM17TG20 ¦ ,Phase sequence, Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG20 ¦ ,Over voltage, Same as RM17TG20 ¦ ,Undervoltage , Same as RM17TG20 ¦ ,Phase asymmetry, Same as RM17TG20 ¦ ,Disconnection of neutral, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme undervoltage, Same as RM17TG20 ¦ ,Extreme overvoltage, Same as RM17TG20 ¦ ,Extreme asymmetry,
84873891mounting position | Same as RM17TG20 ¦ ,In relation to normal vertical mounting plane,
84873891mounting support | Same as RM17TG20 ¦ IEC/EN 60715,Without socket, Same as RM17TG20 ¦ IEC/EN 60715,With socket,
84873891net weight | Same as RM17TG20
84873891on-load factor | Same as RM17TG20
84873891output logic | Same as RM17TG20 ¦ ,R1 (11-12-14), Same as RM17TG20 ¦ ,R2 (21-22-24),
84873891output terminal | Same as RM17TG20
84873891output type | Same as RM17TG20
84873891overvoltage category | Same as RM17TG20 ¦ IEC60664-1
84873891permissible input overload | Same as RM17TG20 ¦ ,permissible input overload,
84873891polarity | Same as RM17TG20
84873891pollution degree | Same as RM17TG20 ¦ IEC60664-1
84873891power consumption | Same as RM17TG20
84873891power on delay | Same as RM17TG20
84873891product certifications | UL, CSA, CE, China ROHS
84873891relative humidity | Same as RM17TG20 ¦ IEC60068-2-30,Damp heat,XX
84873891release of input voltage | Same as RM17TG20
84873891repeat accuracy of the switching threshold | Same as RM17TG20 ¦ ,Repeat accuracy (constant parameters),
84873891repeat accuracy of time delay | Same as RM17TG20
84873891reset time | Same as RM17TG20 ¦ ,through Un power reset, Same as RM17TG20 ¦ ,through front panel reset, Same as RM17TG20 ¦ ,through input control reset,
84873891response time | Same as RM17TG20 ¦ ,on crossing the threshold, Same as RM17TG20 Same as RM17TG20 Same as RM17TG20 Same as RM17TG20
84873891safety reliability data | Same as RM17TG20 ¦ ,MTTF, Same as RM17TG20 ¦ ,B10,
84873891seismic resistance | Same as RM17TG20 ¦ IEC60068-3-3
84873891setting accuracy of the switching threshold | Same as RM17TG20 ¦ ,Setting accuracy,
84873891setting accuracy of time delay | Same as RM17TG20
84873891shock resistance | Same as RM17TG20 ¦ IEC60068-2-27
84873891short circuit protection | Same as RM17TG20 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17TG20 ¦ IEC62314,Solid State Output by external fuse,
84873891standards | Same as RM17TG20
84873891status LED | Same as RM17TG20
84873891supply frequency | Same as RM17TG20 Same as RM17TG20
84873891supply terminal | Same as RM17TG20
84873891supply voltage limits | Same as RM17TG20
84873891switching threshold drift | Same as RM17TG20 ¦ ,Measurement error with supply voltage variation, Same as RM17TG20 ¦ ,Measurement error with temperature variation,
84873891thermal current | Same as RM17TG20 ¦ IEC60947-5-1
84873891tightening torque | Same as RM17TG20 ¦ IEC60947-1,Tightening torque,
84873891time delay drift | Same as RM17TG20 Same as RM17TG20
84873891time delay range | Same as RM17TG20 ¦ ,"OFF" delay, Same as RM17TG20 ¦ ,"ON" delay, Same as RM17TG20 ¦ ,Inhibition,
84873891time delay type | Same as RM17TG20 ¦ ,"OFF" delay, Same as RM17TG20 ¦ ,"ON" delay, Same as RM17TG20 ¦ ,Inhibition,
84873891tripping threshold | Same as RM17TG20 ¦ ,Phase cut, Same as RM17TG20 ¦ ,Phase sequence, Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG20 ¦ ,Over voltage, Same as RM17TG20 ¦ ,Undervoltage , Same as RM17TG20 ¦ ,Phase asymmetry, Same as RM17TG20 ¦ ,Disconnection of neutral, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TG20 ¦ ,Extreme Overvoltage, Same as RM17TG20 ¦ ,Extreme Asymmetry,
84873891vibration resistance | Same as RM17TG20 ¦ IEC60068-2-6
84873891width | Same as RM17TG20 ¦ ,Width,
84873892 | Same as RM17TA00 ¦ IEC60721-3-3,Climatic category, Same as RM17TA00 ¦ Germanisher Lloyd,Environmental category, Same as RM17TA00 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM17TA00 ¦ ,Supply,Rated Same as RM17TA00 ¦ ,Input 1,Voltage Same as RM17TA00 ¦ ,Input 2,Spec Same as RM17TA00 ¦ ,Input 3, Same as RM17TA00 ¦ ,Output 1, Same as RM17TA00 ¦ ,Output 2, Same as RM17TA00 ¦ ,Measurement mode, Same as RM17TA00 Same as RM17TA00 Same as RM17TA00 Same as RM17TA00 Same as RM17TA00 ¦ ,MTTFd, Same as RM17TA00 ¦ ,B10d, Drawing / Diagram
84873892IP degree of protection | Same as RM17TA00 ¦ IEC60529,Terminal Block, Same as RM17TA00 ¦ IEC60529,Housing, Same as RM17TA00 ¦ IEC60529,Front Panel,
84873892Input nominal voltage selection | Same as RM17TA00 ¦ ,Input nominal voltage selection,
84873892Minimum distance to adjacent devices | Same as RM17TA00 ¦ ,Horizontal, Same as RM17TA00 ¦ ,Vertical,
84873892[Ie] rated operational current | Same as RM17TA00 ¦ IEC61810-1,Rated switching current,
84873892[Ue] rated operational voltage | Same as RM17TA00 ¦ IEC61810-1,Rated switching voltage,
84873892[Ui] rated insulation voltage | Same as RM17TA00 ¦ IEC60664-1,Supply, Same as RM17TA00 ¦ IEC60664-1,Input 1, Same as RM17TA00 ¦ IEC60664-1,Input 2, Same as RM17TA00 ¦ IEC60664-1,Input 3, Same as RM17TA00 ¦ IEC60664-1,Output 1, Same as RM17TA00 ¦ IEC60664-1,Output 2, Same as RM17TA00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TA00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TA00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TA00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TA00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TA00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 3,
84873892[Uimp] rated impulse withstand voltage | Same as RM17TA00 ¦ IEC60664-1,Supply, Same as RM17TA00 ¦ IEC60664-1,Input 1, Same as RM17TA00 ¦ IEC60664-1,Input 2, Same as RM17TA00 ¦ IEC60664-1,Input 3, Same as RM17TA00 ¦ IEC60664-1,Output 1, Same as RM17TA00 ¦ IEC60664-1,Output 2, Same as RM17TA00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TA00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TA00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TA00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TA00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TA00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TA00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TA00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TA00 ¦ IEC60664-1,Input 1 / Input 3,
84873892[Us] rated supply voltage | Same as RM17TA00
84873892ambient air temperature for operation | Same as RM17TA00 ¦ ,Operation,
84873892ambient air temperature for storage | Same as RM17TA00 ¦ ,Storage,
84873892bump resistance | Same as RM17TA00 ¦ IEC60068-2-29
84873892cable stripping length | Same as RM17TA00 ¦ ,Cable stripping length,
84873892circuit group | Same as RM17TA00 ¦ ,Supply,Terminal Same as RM17TA00 ¦ ,Input 1, Same as RM17TA00 ¦ ,Input 2, Same as RM17TA00 ¦ ,Input 3, Same as RM17TA00 ¦ ,Output 1, Same as RM17TA00 ¦ ,Output 2,
84873892connections - terminals | Same as RM17TA00 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17TA00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17TA00 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17TA00 ¦ IEC60947-1,Flexible cable (spring terminal),
84873892contacts material | Same as RM17TA00
84873892depth | Same as RM17TA00 ¦ ,Depth,
84873892diagnostic button | Same as RM17TA00
84873892dielectric strength | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TA00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TA00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TA00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TA00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TA00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 3,
84873892directives | Same as RM17TA00 Same as RM17TA00 Same as RM17TA00
84873892duty time | Same as RM17TA00
84873892electrical durability | Same as RM17TA00 ¦ IEC60947-4-1,AC-1, Same as RM17TA00 ¦ IEC60947-4-1,DC-1, Same as RM17TA00 ¦ IEC60947-5-1,AC-15, Same as RM17TA00 ¦ IEC60947-5-1,DC-13,
84873892electromagnetic compatibility | Same as RM17TA00 ¦ ,Generic immunity standard, Same as RM17TA00 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17TA00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17TA00 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17TA00 ¦ IEC61000-4-5,Surge, Same as RM17TA00 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17TA00 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17TA00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17TA00 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17TA00 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17TA00 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM17TA00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17TA00 ¦ ,Generic emission standard, Same as RM17TA00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17TA00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17TA00 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17TA00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17TA00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17TA00 ¦ Germanisher Lloyd,Conducted emission,
84873892height | Same as RM17TA00 ¦ ,Height,
84873892hysteresis | Same as RM17TA00 ¦ ,Phase cut, Same as RM17TA00 ¦ ,Phase sequence, Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TA00 ¦ ,Over voltage, Same as RM17TA00 ¦ ,Undervoltage , Same as RM17TA00 ¦ ,Phase asymmetry, Same as RM17TA00 ¦ ,Disconnection of neutral, Same as RM17TA00 ¦ ,Voltage Regeneration, Same as RM17TA00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TA00 ¦ ,Extreme Overvoltage, Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873892immunity to microbreaks | Same as RM17TA00
84873892input frequency | Same as RM17TA00 ¦ ,Rated frequency, Same as RM17TA00 ¦ ,Frequency operating range,
84873892input terminal | Same as RM17TA00 ¦ ,Input terminal,
84873892insulation resistance | Same as RM17TA00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TA00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TA00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TA00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TA00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TA00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TA00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TA00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TA00 ¦ IEC60255-27,Input 1 / Input 3,
84873892internal input resistance | Same as RM17TA00 ¦ ,Internal input resistance,
84873892local signalling | Same as RM17TA00 ¦ ,Power supply availability, Same as RM17TA00 ¦ ,Power supply not availability, Same as RM17TA00 ¦ ,Timing in-progress, Same as RM17TA00 ¦ ,Output is energized, Same as RM17TA00 ¦ ,Output is de-energized, Same as RM17TA00 ¦ ,Range Setting Changes, Same as RM17TA00 ¦ ,Phase Cut, Same as RM17TA00 ¦ ,Phase Sequence Swap, Same as RM17TA00 ¦ ,Undervoltage <U, Same as RM17TA00 ¦ ,Overvoltage >U, Same as RM17TA00 ¦ ,Phase Asymmetry, Same as RM17TA00 ¦ ,Voltage Regeneration, Same as RM17TA00 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17TA00 ¦ ,Extreme Overvoltage >U, Same as RM17TA00 ¦ ,Extreme Phase Asymmetry,
84873892marking | UL, CSA, CE, China ROHS
84873892maximum leakage current | Same as RM17TA00 ¦ IEC62314,Only for solid state output,
84873892maximum measuring cycle | Same as RM17TA00 ¦ ,Maximum measuring cycles,
84873892maximum switching capacity | Same as RM17TA00 ¦ ,Maximum switching voltage, Same as RM17TA00 ¦ ,Maximum switching current, Same as RM17TA00 ¦ ,Maximum switching capacity,
84873892maximum voltage drop | Same as RM17TA00 ¦ IEC62314,Only for solid state output,
84873892measurement method | Same as RM17TA00 ¦ ,Measurement method,
84873892measurement range | Same as RM17TA00 ¦ ,Phase lost , Same as RM17TA00 ¦ ,Phase sequence, Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TA00 ¦ ,Over voltage, Same as RM17TA00 ¦ ,Undervoltage , Same as RM17TA00 ¦ ,Phase asymmetry, Same as RM17TA00 ¦ ,Disconnection of neutral, Same as RM17TA00 ¦ ,Voltage Regeneration, Same as RM17TA00 ¦ ,Extreme undervoltage, Same as RM17TA00 ¦ ,Extreme Overvoltage, Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873892mechanical durability | Same as RM17TA00 ¦ IEC61810-1
84873892minimum switching capacity | Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching current, Same as RM17TA00 ¦ IEC60947-5-4,Minimum switching capacity,
84873892monitoring functions | Same as RM17TA00 ¦ ,Phase lost , Same as RM17TA00 ¦ ,Phase sequence, Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TA00 ¦ ,Over voltage, Same as RM17TA00 ¦ ,Undervoltage , Same as RM17TA00 ¦ ,Phase asymmetry, Same as RM17TA00 ¦ ,Disconnection of neutral, Same as RM17TA00 ¦ ,Voltage Regeneration, Same as RM17TA00 ¦ ,Extreme undervoltage, Same as RM17TA00 ¦ ,Extreme overvoltage, Same as RM17TA00 ¦ ,Extreme asymmetry,
84873892mounting position | Same as RM17TA00 ¦ ,In relation to normal vertical mounting plane,
84873892mounting support | Same as RM17TA00 ¦ IEC/EN 60715,Without socket, Same as RM17TA00 ¦ IEC/EN 60715,With socket,
84873892net weight | Same as RM17TA00
84873892on-load factor | Same as RM17TA00
84873892output logic | Same as RM17TA00 ¦ ,R1 (11-12-14), Same as RM17TA00 ¦ ,R2 (21-22-24),
84873892output terminal | Same as RM17TA00
84873892output type | Same as RM17TA00
84873892overvoltage category | Same as RM17TA00 ¦ IEC60664-1
84873892permissible input overload | Same as RM17TA00 ¦ ,permissible input overload,
84873892polarity | Same as RM17TA00
84873892pollution degree | Same as RM17TA00 ¦ IEC60664-1
84873892power consumption | Same as RM17TA00
84873892power on delay | Same as RM17TA00
84873892product certifications | UL, CSA, CE, China ROHS
84873892relative humidity | Same as RM17TA00 ¦ IEC60068-2-30,Damp heat,XX
84873892release of input voltage | Same as RM17TA00
84873892repeat accuracy of the switching threshold | Same as RM17TA00 ¦ ,Repeat accuracy (constant parameters),
84873892repeat accuracy of time delay | Same as RM17TA00
84873892reset time | Same as RM17TA00 ¦ ,through Un power reset, Same as RM17TA00 ¦ ,through front panel reset, Same as RM17TA00 ¦ ,through input control reset,
84873892response time | Same as RM17TA00 ¦ ,on crossing the threshold, Same as RM17TA00 Same as RM17TA00 Same as RM17TA00 Same as RM17TA00
84873892safety reliability data | Same as RM17TA00 ¦ ,MTTF, Same as RM17TA00 ¦ ,B10,
84873892seismic resistance | Same as RM17TA00 ¦ IEC60068-3-3
84873892setting accuracy of the switching threshold | Same as RM17TA00 ¦ ,Setting accuracy,
84873892setting accuracy of time delay | Same as RM17TA00
84873892shock resistance | Same as RM17TA00 ¦ IEC60068-2-27
84873892short circuit protection | Same as RM17TA00 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17TA00 ¦ IEC62314,Solid State Output by external fuse,
84873892standards | Same as RM17TA00
84873892status LED | Same as RM17TA00
84873892supply frequency | Same as RM17TA00 Same as RM17TA00
84873892supply terminal | Same as RM17TA00
84873892supply voltage limits | Same as RM17TA00
84873892switching threshold drift | Same as RM17TA00 ¦ ,Measurement error with supply voltage variation, Same as RM17TA00 ¦ ,Measurement error with temperature variation,
84873892thermal current | Same as RM17TA00 ¦ IEC60947-5-1
84873892tightening torque | Same as RM17TA00 ¦ IEC60947-1,Tightening torque,
84873892time delay drift | Same as RM17TA00 Same as RM17TA00
84873892time delay range | Same as RM17TA00 ¦ ,"OFF" delay, Same as RM17TA00 ¦ ,"ON" delay, Same as RM17TA00 ¦ ,Inhibition,
84873892time delay type | Same as RM17TA00 ¦ ,"OFF" delay, Same as RM17TA00 ¦ ,"ON" delay, Same as RM17TA00 ¦ ,Inhibition,
84873892tripping threshold | Same as RM17TA00 ¦ ,Phase cut, Same as RM17TA00 ¦ ,Phase sequence, Same as RM17TA00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TA00 ¦ ,Over voltage, Same as RM17TA00 ¦ ,Undervoltage , Same as RM17TA00 ¦ ,Phase asymmetry, Same as RM17TA00 ¦ ,Disconnection of neutral, Same as RM17TA00 ¦ ,Voltage Regeneration, Same as RM17TA00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TA00 ¦ ,Extreme Overvoltage, Same as RM17TA00 ¦ ,Extreme Asymmetry,
84873892vibration resistance | Same as RM17TA00 ¦ IEC60068-2-6
84873892width | Same as RM17TA00 ¦ ,Width,
84873893 | Same as RM35TF30 ¦ IEC60721-3-3,Climatic category, Same as RM35TF30 ¦ Germanisher Lloyd,Environmental category, Same as RM35TF30 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM35TF30 ¦ ,Supply,Rated Same as RM35TF30 ¦ ,Input 1,Voltage Same as RM35TF30 ¦ ,Input 2,Spec Same as RM35TF30 ¦ ,Input 3, Same as RM35TF30 ¦ ,Output 1, Same as RM35TF30 ¦ ,Output 2, Same as RM35TF30 ¦ ,Measurement mode, Same as RM35TF30 Same as RM35TF30 Same as RM35TF30 Same as RM35TF30 Same as RM35TF30 ¦ ,MTTFd, Same as RM35TF30 ¦ ,B10d, Drawing / Diagram
84873893IP degree of protection | Same as RM35TF30 ¦ IEC60529,Terminal Block, Same as RM35TF30 ¦ IEC60529,Housing, Same as RM35TF30 ¦ IEC60529,Front Panel,
84873893Input nominal voltage selection | Same as RM35TF30 ¦ ,Input nominal voltage selection,
84873893Minimum distance to adjacent devices | Same as RM35TF30 ¦ ,Horizontal, Same as RM35TF30 ¦ ,Vertical,
84873893[Ie] rated operational current | Same as RM35TF30 ¦ IEC61810-1,Rated switching current,
84873893[Ue] rated operational voltage | Same as RM35TF30 ¦ IEC61810-1,Rated switching voltage,
84873893[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply, Same as RM35TF30 ¦ IEC60664-1,Input 1, Same as RM35TF30 ¦ IEC60664-1,Input 2, Same as RM35TF30 ¦ IEC60664-1,Input 3, Same as RM35TF30 ¦ IEC60664-1,Output 1, Same as RM35TF30 ¦ IEC60664-1,Output 2, Same as RM35TF30 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM35TF30 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM35TF30 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM35TF30 ¦ IEC60664-1,Supply / Output 1, Same as RM35TF30 ¦ IEC60664-1,Supply / Output 2, Same as RM35TF30 ¦ IEC60664-1,Output 1 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 2, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Input 3, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 3,
84873893[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply, Same as RM35TF30 ¦ IEC60664-1,Input 1, Same as RM35TF30 ¦ IEC60664-1,Input 2, Same as RM35TF30 ¦ IEC60664-1,Input 3, Same as RM35TF30 ¦ IEC60664-1,Output 1, Same as RM35TF30 ¦ IEC60664-1,Output 2, Same as RM35TF30 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM35TF30 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM35TF30 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM35TF30 ¦ IEC60664-1,Supply / Output 1, Same as RM35TF30 ¦ IEC60664-1,Supply / Output 2, Same as RM35TF30 ¦ IEC60664-1,Output 1 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 2, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Input 3, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 3,
84873893[Us] rated supply voltage | Same as RM35TF30
84873893ambient air temperature for operation | Same as RM35TF30 ¦ ,Operation,
84873893ambient air temperature for storage | Same as RM35TF30 ¦ ,Storage,
84873893bump resistance | Same as RM35TF30 ¦ IEC60068-2-29
84873893cable stripping length | Same as RM35TF30 ¦ ,Cable stripping length,
84873893circuit group | Same as RM35TF30 ¦ ,Supply,Terminal Same as RM35TF30 ¦ ,Input 1, Same as RM35TF30 ¦ ,Input 2, Same as RM35TF30 ¦ ,Input 3, Same as RM35TF30 ¦ ,Output 1, Same as RM35TF30 ¦ ,Output 2,
84873893connections - terminals | Same as RM35TF30 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM35TF30 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM35TF30 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM35TF30 ¦ IEC60947-1,Flexible cable (spring terminal),
84873893contacts material | Same as RM35TF30
84873893depth | Same as RM35TF30 ¦ ,Depth,
84873893diagnostic button | Same as RM35TF30
84873893dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 1, Same as RM35TF30 ¦ IEC60255-27,Supply / Input 2, Same as RM35TF30 ¦ IEC60255-27,Supply / Input 3, Same as RM35TF30 ¦ IEC60255-27,Supply / Output 1, Same as RM35TF30 ¦ IEC60255-27,Supply / Output 2, Same as RM35TF30 ¦ IEC60255-27,Output 1 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 2, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Input 3, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 3,
84873893directives | Same as RM35TF30 Same as RM35TF30 Same as RM35TF30
84873893duty time | Same as RM35TF30
84873893electrical durability | Same as RM35TF30 ¦ IEC60947-4-1,AC-1, Same as RM35TF30 ¦ IEC60947-4-1,DC-1, Same as RM35TF30 ¦ IEC60947-5-1,AC-15, Same as RM35TF30 ¦ IEC60947-5-1,DC-13,
84873893electromagnetic compatibility | Same as RM35TF30 ¦ ,Generic immunity standard, Same as RM35TF30 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM35TF30 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM35TF30 ¦ IEC61000-4-4,Fast transient / burst, Same as RM35TF30 ¦ IEC61000-4-5,Surge, Same as RM35TF30 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM35TF30 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM35TF30 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM35TF30 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM35TF30 ¦ IEC61000-4-29,DC voltage interruption, Same as RM35TF30 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM35TF30 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM35TF30 ¦ ,Generic emission standard, Same as RM35TF30 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM35TF30 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM35TF30 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM35TF30 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM35TF30 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM35TF30 ¦ Germanisher Lloyd,Conducted emission,
84873893height | Same as RM35TF30 ¦ ,Height,
84873893hysteresis | Same as RM35TF30 ¦ ,Phase cut, Same as RM35TF30 ¦ ,Phase sequence, Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35TF30 ¦ ,Over voltage, Same as RM35TF30 ¦ ,Undervoltage , Same as RM35TF30 ¦ ,Phase asymmetry, Same as RM35TF30 ¦ ,Disconnection of neutral, Same as RM35TF30 ¦ ,Voltage Regeneration, Same as RM35TF30 ¦ ,Extreme undervoltage (Phase loss), Same as RM35TF30 ¦ ,Extreme Overvoltage, Same as RM35TF30 ¦ ,Extreme Asymmetry,
84873893immunity to microbreaks | Same as RM35TF30
84873893input frequency | Same as RM35TF30 ¦ ,Rated frequency, Same as RM35TF30 ¦ ,Frequency operating range,
84873893input terminal | Same as RM35TF30 ¦ ,Input terminal,
84873893insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 1, Same as RM35TF30 ¦ IEC60255-27,Supply / Input 2, Same as RM35TF30 ¦ IEC60255-27,Supply / Input 3, Same as RM35TF30 ¦ IEC60255-27,Supply / Output 1, Same as RM35TF30 ¦ IEC60255-27,Supply / Output 2, Same as RM35TF30 ¦ IEC60255-27,Output 1 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 2, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Input 3, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 3,
84873893internal input resistance | Same as RM35TF30 ¦ ,Internal input resistance,
84873893local signalling | Same as RM35TF30 ¦ ,Power supply availability, Same as RM35TF30 ¦ ,Power supply not availability, Same as RM35TF30 ¦ ,Timing in-progress, Same as RM35TF30 ¦ ,Output is energized, Same as RM35TF30 ¦ ,Output is de-energized, Same as RM35TF30 ¦ ,Range Setting Changes, Same as RM35TF30 ¦ ,Phase Cut, Same as RM35TF30 ¦ ,Phase Sequence Swap, Same as RM35TF30 ¦ ,Undervoltage <U, Same as RM35TF30 ¦ ,Overvoltage >U, Same as RM35TF30 ¦ ,Phase Asymmetry, Same as RM35TF30 ¦ ,Voltage Regeneration, Same as RM35TF30 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM35TF30 ¦ ,Extreme Overvoltage >U, Same as RM35TF30 ¦ ,Extreme Phase Asymmetry,
84873893marking | UL, CSA, CE, China ROHS
84873893maximum leakage current | Same as RM35TF30 ¦ IEC62314,Only for solid state output,
84873893maximum measuring cycle | Same as RM35TF30 ¦ ,Maximum measuring cycles,
84873893maximum switching capacity | Same as RM35TF30 ¦ ,Maximum switching voltage, Same as RM35TF30 ¦ ,Maximum switching current, Same as RM35TF30 ¦ ,Maximum switching capacity,
84873893maximum voltage drop | Same as RM35TF30 ¦ IEC62314,Only for solid state output,
84873893measurement method | Same as RM35TF30 ¦ ,Measurement method,
84873893measurement range | Same as RM35TF30 ¦ ,Phase lost , Same as RM35TF30 ¦ ,Phase sequence, Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35TF30 ¦ ,Over voltage, Same as RM35TF30 ¦ ,Undervoltage , Same as RM35TF30 ¦ ,Phase asymmetry, Same as RM35TF30 ¦ ,Disconnection of neutral, Same as RM35TF30 ¦ ,Voltage Regeneration, Same as RM35TF30 ¦ ,Extreme undervoltage, Same as RM35TF30 ¦ ,Extreme Overvoltage, Same as RM35TF30 ¦ ,Extreme Asymmetry,
84873893mechanical durability | Same as RM35TF30 ¦ IEC61810-1
84873893minimum switching capacity | Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching current, Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching capacity,
84873893monitoring functions | Same as RM35TF30 ¦ ,Phase lost , Same as RM35TF30 ¦ ,Phase sequence, Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35TF30 ¦ ,Over voltage, Same as RM35TF30 ¦ ,Undervoltage , Same as RM35TF30 ¦ ,Phase asymmetry, Same as RM35TF30 ¦ ,Disconnection of neutral, Same as RM35TF30 ¦ ,Voltage Regeneration, Same as RM35TF30 ¦ ,Extreme undervoltage, Same as RM35TF30 ¦ ,Extreme overvoltage, Same as RM35TF30 ¦ ,Extreme asymmetry,
84873893mounting position | Same as RM35TF30 ¦ ,In relation to normal vertical mounting plane,
84873893mounting support | Same as RM35TF30 ¦ IEC/EN 60715,Without socket, Same as RM35TF30 ¦ IEC/EN 60715,With socket,
84873893net weight | Same as RM35TF30
84873893on-load factor | Same as RM35TF30
84873893output logic | Same as RM35TF30 ¦ ,R1 (11-12-14), Same as RM35TF30 ¦ ,R2 (21-22-24),
84873893output terminal | Same as RM35TF30
84873893output type | Same as RM35TF30
84873893overvoltage category | Same as RM35TF30 ¦ IEC60664-1
84873893permissible input overload | Same as RM35TF30 ¦ ,permissible input overload,
84873893polarity | Same as RM35TF30
84873893pollution degree | Same as RM35TF30 ¦ IEC60664-1
84873893power consumption | Same as RM35TF30
84873893power on delay | Same as RM35TF30
84873893product certifications | UL, CSA, CE, China ROHS
84873893relative humidity | Same as RM35TF30 ¦ IEC60068-2-30,Damp heat,XX
84873893release of input voltage | Same as RM35TF30
84873893repeat accuracy of the switching threshold | Same as RM35TF30 ¦ ,Repeat accuracy (constant parameters),
84873893repeat accuracy of time delay | Same as RM35TF30
84873893reset time | Same as RM35TF30 ¦ ,through Un power reset, Same as RM35TF30 ¦ ,through front panel reset, Same as RM35TF30 ¦ ,through input control reset,
84873893response time | Same as RM35TF30 ¦ ,on crossing the threshold, Same as RM35TF30 Same as RM35TF30 Same as RM35TF30 Same as RM35TF30
84873893safety reliability data | Same as RM35TF30 ¦ ,MTTF, Same as RM35TF30 ¦ ,B10,
84873893seismic resistance | Same as RM35TF30 ¦ IEC60068-3-3
84873893setting accuracy of the switching threshold | Same as RM35TF30 ¦ ,Setting accuracy,
84873893setting accuracy of time delay | Same as RM35TF30
84873893shock resistance | Same as RM35TF30 ¦ IEC60068-2-27
84873893short circuit protection | Same as RM35TF30 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM35TF30 ¦ IEC62314,Solid State Output by external fuse,
84873893standards | Same as RM35TF30
84873893status LED | Same as RM35TF30
84873893supply frequency | Same as RM35TF30 Same as RM35TF30
84873893supply terminal | Same as RM35TF30
84873893supply voltage limits | Same as RM35TF30
84873893switching threshold drift | Same as RM35TF30 ¦ ,Measurement error with supply voltage variation, Same as RM35TF30 ¦ ,Measurement error with temperature variation,
84873893thermal current | Same as RM35TF30 ¦ IEC60947-5-1
84873893tightening torque | Same as RM35TF30 ¦ IEC60947-1,Tightening torque,
84873893time delay drift | Same as RM35TF30 Same as RM35TF30
84873893time delay range | Same as RM35TF30 ¦ ,"OFF" delay, Same as RM35TF30 ¦ ,"ON" delay, Same as RM35TF30 ¦ ,Inhibition,
84873893time delay type | Same as RM35TF30 ¦ ,"OFF" delay, Same as RM35TF30 ¦ ,"ON" delay, Same as RM35TF30 ¦ ,Inhibition,
84873893tripping threshold | Same as RM35TF30 ¦ ,Phase cut, Same as RM35TF30 ¦ ,Phase sequence, Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35TF30 ¦ ,Over voltage, Same as RM35TF30 ¦ ,Undervoltage , Same as RM35TF30 ¦ ,Phase asymmetry, Same as RM35TF30 ¦ ,Disconnection of neutral, Same as RM35TF30 ¦ ,Voltage Regeneration, Same as RM35TF30 ¦ ,Extreme undervoltage (Phase loss), Same as RM35TF30 ¦ ,Extreme Overvoltage, Same as RM35TF30 ¦ ,Extreme Asymmetry,
84873893vibration resistance | Same as RM35TF30 ¦ IEC60068-2-6
84873893width | Same as RM35TF30 ¦ ,Width,
84873894 | Same as RM35UB330 ¦ IEC60721-3-3,Climatic category, Same as RM35UB330 ¦ Germanisher Lloyd,Environmental category, Same as RM35UB330 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM35UB330 ¦ ,Supply,Rated Same as RM35UB330 ¦ ,Input 1,Voltage Same as RM35UB330 ¦ ,Input 2,Spec Same as RM35UB330 ¦ ,Input 3, Same as RM35UB330 ¦ ,Output 1, Same as RM35UB330 ¦ ,Output 2, Same as RM35UB330 ¦ ,Measurement mode, Same as RM35UB330 Same as RM35UB330 Same as RM35UB330 Same as RM35UB330 Same as RM35UB330 ¦ ,MTTFd, Same as RM35UB330 ¦ ,B10d, Drawing / Diagram
84873894IP degree of protection | Same as RM35UB330 ¦ IEC60529,Terminal Block, Same as RM35UB330 ¦ IEC60529,Housing, Same as RM35UB330 ¦ IEC60529,Front Panel,
84873894Input nominal voltage selection | Same as RM35UB330 ¦ ,Input nominal voltage selection,
84873894Minimum distance to adjacent devices | Same as RM35UB330 ¦ ,Horizontal, Same as RM35UB330 ¦ ,Vertical,
84873894[Ie] rated operational current | Same as RM35UB330 ¦ IEC61810-1,Rated switching current,
84873894[Ue] rated operational voltage | Same as RM35UB330 ¦ IEC61810-1,Rated switching voltage,
84873894[Ui] rated insulation voltage | Same as RM35UB330 ¦ IEC60664-1,Supply, Same as RM35UB330 ¦ IEC60664-1,Input 1, Same as RM35UB330 ¦ IEC60664-1,Input 2, Same as RM35UB330 ¦ IEC60664-1,Input 3, Same as RM35UB330 ¦ IEC60664-1,Output 1, Same as RM35UB330 ¦ IEC60664-1,Output 2, Same as RM35UB330 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM35UB330 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM35UB330 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM35UB330 ¦ IEC60664-1,Supply / Output 1, Same as RM35UB330 ¦ IEC60664-1,Supply / Output 2, Same as RM35UB330 ¦ IEC60664-1,Output 1 / Output 2, Same as RM35UB330 ¦ IEC60664-1,Input 1 / Output 1, Same as RM35UB330 ¦ IEC60664-1,Input 1 / Output 2, Same as RM35UB330 ¦ IEC60664-1,Input 2 / Output 1, Same as RM35UB330 ¦ IEC60664-1,Input 2 / Output 2, Same as RM35UB330 ¦ IEC60664-1,Input 3 / Output 1, Same as RM35UB330 ¦ IEC60664-1,Input 3 / Output 2, Same as RM35UB330 ¦ IEC60664-1,Input 1 / Input 2, Same as RM35UB330 ¦ IEC60664-1,Input 2 / Input 3, Same as RM35UB330 ¦ IEC60664-1,Input 1 / Input 3,
84873894[Uimp] rated impulse withstand voltage | Same as RM35UB330 ¦ IEC60664-1,Supply, Same as RM35UB330 ¦ IEC60664-1,Input 1, Same as RM35UB330 ¦ IEC60664-1,Input 2, Same as RM35UB330 ¦ IEC60664-1,Input 3, Same as RM35UB330 ¦ IEC60664-1,Output 1, Same as RM35UB330 ¦ IEC60664-1,Output 2, Same as RM35UB330 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM35UB330 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM35UB330 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM35UB330 ¦ IEC60664-1,Supply / Output 1, Same as RM35UB330 ¦ IEC60664-1,Supply / Output 2, Same as RM35UB330 ¦ IEC60664-1,Output 1 / Output 2, Same as RM35UB330 ¦ IEC60664-1,Input 1 / Output 1, Same as RM35UB330 ¦ IEC60664-1,Input 1 / Output 2, Same as RM35UB330 ¦ IEC60664-1,Input 2 / Output 1, Same as RM35UB330 ¦ IEC60664-1,Input 2 / Output 2, Same as RM35UB330 ¦ IEC60664-1,Input 3 / Output 1, Same as RM35UB330 ¦ IEC60664-1,Input 3 / Output 2, Same as RM35UB330 ¦ IEC60664-1,Input 1 / Input 2, Same as RM35UB330 ¦ IEC60664-1,Input 2 / Input 3, Same as RM35UB330 ¦ IEC60664-1,Input 1 / Input 3,
84873894[Us] rated supply voltage | Same as RM35UB330
84873894ambient air temperature for operation | Same as RM35UB330 ¦ ,Operation,
84873894ambient air temperature for storage | Same as RM35UB330 ¦ ,Storage,
84873894bump resistance | Same as RM35UB330 ¦ IEC60068-2-29
84873894cable stripping length | Same as RM35UB330 ¦ ,Cable stripping length,
84873894circuit group | Same as RM35UB330 ¦ ,Supply,Terminal Same as RM35UB330 ¦ ,Input 1, Same as RM35UB330 ¦ ,Input 2, Same as RM35UB330 ¦ ,Input 3, Same as RM35UB330 ¦ ,Output 1, Same as RM35UB330 ¦ ,Output 2,
84873894connections - terminals | Same as RM35UB330 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM35UB330 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM35UB330 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM35UB330 ¦ IEC60947-1,Flexible cable (spring terminal),
84873894contacts material | Same as RM35UB330
84873894depth | Same as RM35UB330 ¦ ,Depth,
84873894diagnostic button | Same as RM35UB330
84873894dielectric strength | Same as RM35UB330 ¦ IEC60255-27,Supply / Input 1, Same as RM35UB330 ¦ IEC60255-27,Supply / Input 2, Same as RM35UB330 ¦ IEC60255-27,Supply / Input 3, Same as RM35UB330 ¦ IEC60255-27,Supply / Output 1, Same as RM35UB330 ¦ IEC60255-27,Supply / Output 2, Same as RM35UB330 ¦ IEC60255-27,Output 1 / Output 2, Same as RM35UB330 ¦ IEC60255-27,Input 1 / Output 1, Same as RM35UB330 ¦ IEC60255-27,Input 1 / Output 2, Same as RM35UB330 ¦ IEC60255-27,Input 2 / Output 1, Same as RM35UB330 ¦ IEC60255-27,Input 2 / Output 2, Same as RM35UB330 ¦ IEC60255-27,Input 3 / Output 1, Same as RM35UB330 ¦ IEC60255-27,Input 3 / Output 2, Same as RM35UB330 ¦ IEC60255-27,Input 1 / Input 2, Same as RM35UB330 ¦ IEC60255-27,Input 2 / Input 3, Same as RM35UB330 ¦ IEC60255-27,Input 1 / Input 3,
84873894directives | Same as RM35UB330 Same as RM35UB330 Same as RM35UB330
84873894duty time | Same as RM35UB330
84873894electrical durability | Same as RM35UB330 ¦ IEC60947-4-1,AC-1, Same as RM35UB330 ¦ IEC60947-4-1,DC-1, Same as RM35UB330 ¦ IEC60947-5-1,AC-15, Same as RM35UB330 ¦ IEC60947-5-1,DC-13,
84873894electromagnetic compatibility | Same as RM35UB330 ¦ ,Generic immunity standard, Same as RM35UB330 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM35UB330 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM35UB330 ¦ IEC61000-4-4,Fast transient / burst, Same as RM35UB330 ¦ IEC61000-4-5,Surge, Same as RM35UB330 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM35UB330 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM35UB330 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM35UB330 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM35UB330 ¦ IEC61000-4-29,DC voltage interruption, Same as RM35UB330 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM35UB330 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM35UB330 ¦ ,Generic emission standard, Same as RM35UB330 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM35UB330 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM35UB330 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM35UB330 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM35UB330 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM35UB330 ¦ Germanisher Lloyd,Conducted emission,
84873894height | Same as RM35UB330 ¦ ,Height,
84873894hysteresis | Same as RM35UB330 ¦ ,Phase cut, Same as RM35UB330 ¦ ,Phase sequence, Same as RM35UB330 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35UB330 ¦ ,Over voltage, Same as RM35UB330 ¦ ,Undervoltage , Same as RM35UB330 ¦ ,Phase asymmetry, Same as RM35UB330 ¦ ,Disconnection of neutral, Same as RM35UB330 ¦ ,Voltage Regeneration, Same as RM35UB330 ¦ ,Extreme undervoltage (Phase loss), Same as RM35UB330 ¦ ,Extreme Overvoltage, Same as RM35UB330 ¦ ,Extreme Asymmetry,
84873894immunity to microbreaks | Same as RM35UB330
84873894input frequency | Same as RM35UB330 ¦ ,Rated frequency, Same as RM35UB330 ¦ ,Frequency operating range,
84873894input terminal | Same as RM35UB330 ¦ ,Input terminal,
84873894insulation resistance | Same as RM35UB330 ¦ IEC60255-27,Supply / Input 1, Same as RM35UB330 ¦ IEC60255-27,Supply / Input 2, Same as RM35UB330 ¦ IEC60255-27,Supply / Input 3, Same as RM35UB330 ¦ IEC60255-27,Supply / Output 1, Same as RM35UB330 ¦ IEC60255-27,Supply / Output 2, Same as RM35UB330 ¦ IEC60255-27,Output 1 / Output 2, Same as RM35UB330 ¦ IEC60255-27,Input 1 / Output 1, Same as RM35UB330 ¦ IEC60255-27,Input 1 / Output 2, Same as RM35UB330 ¦ IEC60255-27,Input 2 / Output 1, Same as RM35UB330 ¦ IEC60255-27,Input 2 / Output 2, Same as RM35UB330 ¦ IEC60255-27,Input 3 / Output 1, Same as RM35UB330 ¦ IEC60255-27,Input 3 / Output 2, Same as RM35UB330 ¦ IEC60255-27,Input 1 / Input 2, Same as RM35UB330 ¦ IEC60255-27,Input 2 / Input 3, Same as RM35UB330 ¦ IEC60255-27,Input 1 / Input 3,
84873894internal input resistance | Same as RM35UB330 ¦ ,Internal input resistance,
84873894local signalling | Same as RM35UB330 ¦ ,Power supply availability, Same as RM35UB330 ¦ ,Power supply not availability, Same as RM35UB330 ¦ ,Timing in-progress, Same as RM35UB330 ¦ ,Output is energized, Same as RM35UB330 ¦ ,Output is de-energized, Same as RM35UB330 ¦ ,Range Setting Changes, Same as RM35UB330 ¦ ,Phase Cut, Same as RM35UB330 ¦ ,Phase Sequence Swap, Same as RM35UB330 ¦ ,Undervoltage <U, Same as RM35UB330 ¦ ,Overvoltage >U, Same as RM35UB330 ¦ ,Phase Asymmetry, Same as RM35UB330 ¦ ,Voltage Regeneration, Same as RM35UB330 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM35UB330 ¦ ,Extreme Overvoltage >U, Same as RM35UB330 ¦ ,Extreme Phase Asymmetry,
84873894marking | UL, CSA, CE, China ROHS
84873894maximum leakage current | Same as RM35UB330 ¦ IEC62314,Only for solid state output,
84873894maximum measuring cycle | Same as RM35UB330 ¦ ,Maximum measuring cycles,
84873894maximum switching capacity | Same as RM35UB330 ¦ ,Maximum switching voltage, Same as RM35UB330 ¦ ,Maximum switching current, Same as RM35UB330 ¦ ,Maximum switching capacity,
84873894maximum voltage drop | Same as RM35UB330 ¦ IEC62314,Only for solid state output,
84873894measurement method | Same as RM35UB330 ¦ ,Measurement method,
84873894measurement range | Same as RM35UB330 ¦ ,Phase lost , Same as RM35UB330 ¦ ,Phase sequence, Same as RM35UB330 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35UB330 ¦ ,Over voltage, Same as RM35UB330 ¦ ,Undervoltage , Same as RM35UB330 ¦ ,Phase asymmetry, Same as RM35UB330 ¦ ,Disconnection of neutral, Same as RM35UB330 ¦ ,Voltage Regeneration, Same as RM35UB330 ¦ ,Extreme undervoltage, Same as RM35UB330 ¦ ,Extreme Overvoltage, Same as RM35UB330 ¦ ,Extreme Asymmetry,
84873894mechanical durability | Same as RM35UB330 ¦ IEC61810-1
84873894minimum switching capacity | Same as RM35UB330 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM35UB330 ¦ IEC60947-5-4,Minimum switching current, Same as RM35UB330 ¦ IEC60947-5-4,Minimum switching capacity,
84873894monitoring functions | Same as RM35UB330 ¦ ,Phase lost , Same as RM35UB330 ¦ ,Phase sequence, Same as RM35UB330 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35UB330 ¦ ,Over voltage, Same as RM35UB330 ¦ ,Undervoltage , Same as RM35UB330 ¦ ,Phase asymmetry, Same as RM35UB330 ¦ ,Disconnection of neutral, Same as RM35UB330 ¦ ,Voltage Regeneration, Same as RM35UB330 ¦ ,Extreme undervoltage, Same as RM35UB330 ¦ ,Extreme overvoltage, Same as RM35UB330 ¦ ,Extreme asymmetry,
84873894mounting position | Same as RM35UB330 ¦ ,In relation to normal vertical mounting plane,
84873894mounting support | Same as RM35UB330 ¦ IEC/EN 60715,Without socket, Same as RM35UB330 ¦ IEC/EN 60715,With socket,
84873894net weight | Same as RM35UB330
84873894on-load factor | Same as RM35UB330
84873894output logic | Same as RM35UB330 ¦ ,R1 (11-12-14), Same as RM35UB330 ¦ ,R2 (21-22-24),
84873894output terminal | Same as RM35UB330
84873894output type | Same as RM35UB330
84873894overvoltage category | Same as RM35UB330 ¦ IEC60664-1
84873894permissible input overload | Same as RM35UB330 ¦ ,permissible input overload,
84873894polarity | Same as RM35UB330
84873894pollution degree | Same as RM35UB330 ¦ IEC60664-1
84873894power consumption | Same as RM35UB330
84873894power on delay | Same as RM35UB330
84873894product certifications | UL, CSA, CE, China ROHS
84873894relative humidity | Same as RM35UB330 ¦ IEC60068-2-30,Damp heat,XX
84873894release of input voltage | Same as RM35UB330
84873894repeat accuracy of the switching threshold | Same as RM35UB330 ¦ ,Repeat accuracy (constant parameters),
84873894repeat accuracy of time delay | Same as RM35UB330
84873894reset time | Same as RM35UB330 ¦ ,through Un power reset, Same as RM35UB330 ¦ ,through front panel reset, Same as RM35UB330 ¦ ,through input control reset,
84873894response time | Same as RM35UB330 ¦ ,on crossing the threshold, Same as RM35UB330 Same as RM35UB330 Same as RM35UB330 Same as RM35UB330
84873894safety reliability data | Same as RM35UB330 ¦ ,MTTF, Same as RM35UB330 ¦ ,B10,
84873894seismic resistance | Same as RM35UB330 ¦ IEC60068-3-3
84873894setting accuracy of the switching threshold | Same as RM35UB330 ¦ ,Setting accuracy,
84873894setting accuracy of time delay | Same as RM35UB330
84873894shock resistance | Same as RM35UB330 ¦ IEC60068-2-27
84873894short circuit protection | Same as RM35UB330 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM35UB330 ¦ IEC62314,Solid State Output by external fuse,
84873894standards | Same as RM35UB330
84873894status LED | Same as RM35UB330
84873894supply frequency | Same as RM35UB330 Same as RM35UB330
84873894supply terminal | Same as RM35UB330
84873894supply voltage limits | Same as RM35UB330
84873894switching threshold drift | Same as RM35UB330 ¦ ,Measurement error with supply voltage variation, Same as RM35UB330 ¦ ,Measurement error with temperature variation,
84873894thermal current | Same as RM35UB330 ¦ IEC60947-5-1
84873894tightening torque | Same as RM35UB330 ¦ IEC60947-1,Tightening torque,
84873894time delay drift | Same as RM35UB330 Same as RM35UB330
84873894time delay range | Same as RM35UB330 ¦ ,"OFF" delay, Same as RM35UB330 ¦ ,"ON" delay, Same as RM35UB330 ¦ ,Inhibition,
84873894time delay type | Same as RM35UB330 ¦ ,"OFF" delay, Same as RM35UB330 ¦ ,"ON" delay, Same as RM35UB330 ¦ ,Inhibition,
84873894tripping threshold | Same as RM35UB330 ¦ ,Phase cut, Same as RM35UB330 ¦ ,Phase sequence, Same as RM35UB330 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35UB330 ¦ ,Over voltage, Same as RM35UB330 ¦ ,Undervoltage , Same as RM35UB330 ¦ ,Phase asymmetry, Same as RM35UB330 ¦ ,Disconnection of neutral, Same as RM35UB330 ¦ ,Voltage Regeneration, Same as RM35UB330 ¦ ,Extreme undervoltage (Phase loss), Same as RM35UB330 ¦ ,Extreme Overvoltage, Same as RM35UB330 ¦ ,Extreme Asymmetry,
84873894vibration resistance | Same as RM35UB330 ¦ IEC60068-2-6
84873894width | Same as RM35UB330 ¦ ,Width,
84873895 | Same as RM35UB3N30 ¦ IEC60721-3-3,Climatic category, Same as RM35UB3N30 ¦ Germanisher Lloyd,Environmental category, Same as RM35UB3N30 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM35UB3N30 ¦ ,Supply,Rated Same as RM35UB3N30 ¦ ,Input 1,Voltage Same as RM35UB3N30 ¦ ,Input 2,Spec Same as RM35UB3N30 ¦ ,Input 3, Same as RM35UB3N30 ¦ ,Output 1, Same as RM35UB3N30 ¦ ,Output 2, Same as RM35UB3N30 ¦ ,Measurement mode, Same as RM35UB3N30 Same as RM35UB3N30 Same as RM35UB3N30 Same as RM35UB3N30 Same as RM35UB3N30 Same as RM35UB3N30 ¦ ,MTTFd, Same as RM35UB3N30 ¦ ,B10d, Drawing / Diagram
84873895IP degree of protection | Same as RM35UB3N30 ¦ IEC60529,Terminal Block, Same as RM35UB3N30 ¦ IEC60529,Housing, Same as RM35UB3N30 ¦ IEC60529,Front Panel,
84873895Input nominal voltage selection | Same as RM35UB3N30 ¦ ,Input nominal voltage selection,
84873895Minimum distance to adjacent devices | Same as RM35UB3N30 ¦ ,Horizontal, Same as RM35UB3N30 ¦ ,Vertical,
84873895[Ie] rated operational current | Same as RM35UB3N30 ¦ IEC61810-1,Rated switching current,
84873895[Ue] rated operational voltage | Same as RM35UB3N30 ¦ IEC61810-1,Rated switching voltage,
84873895[Ui] rated insulation voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply, Same as RM35UB3N30 ¦ IEC60664-1,Input 1, Same as RM35UB3N30 ¦ IEC60664-1,Input 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 3, Same as RM35UB3N30 ¦ IEC60664-1,Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM35UB3N30 ¦ IEC60664-1,Supply / Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Supply / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Output 1 / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 3 / Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Input 3 / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Input 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Input 3, Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Input 3,
84873895[Uimp] rated impulse withstand voltage | Same as RM35UB3N30 ¦ IEC60664-1,Supply, Same as RM35UB3N30 ¦ IEC60664-1,Input 1, Same as RM35UB3N30 ¦ IEC60664-1,Input 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 3, Same as RM35UB3N30 ¦ IEC60664-1,Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM35UB3N30 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM35UB3N30 ¦ IEC60664-1,Supply / Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Supply / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Output 1 / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 3 / Output 1, Same as RM35UB3N30 ¦ IEC60664-1,Input 3 / Output 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Input 2, Same as RM35UB3N30 ¦ IEC60664-1,Input 2 / Input 3, Same as RM35UB3N30 ¦ IEC60664-1,Input 1 / Input 3,
84873895[Us] rated supply voltage | Same as RM35UB3N30
84873895ambient air temperature for operation | Same as RM35UB3N30 ¦ ,Operation,
84873895ambient air temperature for storage | Same as RM35UB3N30 ¦ ,Storage,
84873895bump resistance | Same as RM35UB3N30 ¦ IEC60068-2-29
84873895cable stripping length | Same as RM35UB3N30 ¦ ,Cable stripping length,
84873895circuit group | Same as RM35UB3N30 ¦ ,Supply,Terminal Same as RM35UB3N30 ¦ ,Input 1, Same as RM35UB3N30 ¦ ,Input 2, Same as RM35UB3N30 ¦ ,Input 3, Same as RM35UB3N30 ¦ ,Output 1, Same as RM35UB3N30 ¦ ,Output 2,
84873895connections - terminals | Same as RM35UB3N30 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM35UB3N30 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM35UB3N30 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM35UB3N30 ¦ IEC60947-1,Flexible cable (spring terminal),
84873895contacts material | Same as RM35UB3N30
84873895depth | Same as RM35UB3N30 ¦ ,Depth,
84873895diagnostic button | Same as RM35UB3N30
84873895dielectric strength | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 1, Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 2, Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 3, Same as RM35UB3N30 ¦ IEC60255-27,Supply / Output 1, Same as RM35UB3N30 ¦ IEC60255-27,Supply / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Output 1 / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Output 1, Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Output 1, Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 3 / Output 1, Same as RM35UB3N30 ¦ IEC60255-27,Input 3 / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Input 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Input 3, Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Input 3,
84873895directives | Same as RM35UB3N30 Same as RM35UB3N30 Same as RM35UB3N30
84873895duty time | Same as RM35UB3N30
84873895electrical durability | Same as RM35UB3N30 ¦ IEC60947-4-1,AC-1, Same as RM35UB3N30 ¦ IEC60947-4-1,DC-1, Same as RM35UB3N30 ¦ IEC60947-5-1,AC-15, Same as RM35UB3N30 ¦ IEC60947-5-1,DC-13,
84873895electromagnetic compatibility | Same as RM35UB3N30 ¦ ,Generic immunity standard, Same as RM35UB3N30 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM35UB3N30 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM35UB3N30 ¦ IEC61000-4-4,Fast transient / burst, Same as RM35UB3N30 ¦ IEC61000-4-5,Surge, Same as RM35UB3N30 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM35UB3N30 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM35UB3N30 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM35UB3N30 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM35UB3N30 ¦ IEC61000-4-29,DC voltage interruption, Same as RM35UB3N30 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM35UB3N30 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM35UB3N30 ¦ ,Generic emission standard, Same as RM35UB3N30 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM35UB3N30 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM35UB3N30 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM35UB3N30 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM35UB3N30 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM35UB3N30 ¦ Germanisher Lloyd,Conducted emission,
84873895height | Same as RM35UB3N30 ¦ ,Height,
84873895hysteresis | Same as RM35UB3N30 ¦ ,Phase cut, Same as RM35UB3N30 ¦ ,Phase sequence, Same as RM35UB3N30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35UB3N30 ¦ ,Over voltage, Same as RM35UB3N30 ¦ ,Undervoltage , Same as RM35UB3N30 ¦ ,Phase asymmetry, Same as RM35UB3N30 ¦ ,Disconnection of neutral, Same as RM35UB3N30 ¦ ,Voltage Regeneration, Same as RM35UB3N30 ¦ ,Extreme undervoltage (Phase loss), Same as RM35UB3N30 ¦ ,Extreme Overvoltage, Same as RM35UB3N30 ¦ ,Extreme Asymmetry,
84873895immunity to microbreaks | Same as RM35UB3N30
84873895input frequency | Same as RM35UB3N30 ¦ ,Rated frequency, Same as RM35UB3N30 ¦ ,Frequency operating range,
84873895input terminal | Same as RM35UB3N30 ¦ ,Input terminal,
84873895insulation resistance | Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 1, Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 2, Same as RM35UB3N30 ¦ IEC60255-27,Supply / Input 3, Same as RM35UB3N30 ¦ IEC60255-27,Supply / Output 1, Same as RM35UB3N30 ¦ IEC60255-27,Supply / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Output 1 / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Output 1, Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Output 1, Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 3 / Output 1, Same as RM35UB3N30 ¦ IEC60255-27,Input 3 / Output 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Input 2, Same as RM35UB3N30 ¦ IEC60255-27,Input 2 / Input 3, Same as RM35UB3N30 ¦ IEC60255-27,Input 1 / Input 3,
84873895internal input resistance | Same as RM35UB3N30 ¦ ,Internal input resistance,
84873895local signalling | Same as RM35UB3N30 ¦ ,Power supply availability, Same as RM35UB3N30 ¦ ,Power supply not availability, Same as RM35UB3N30 ¦ ,Timing in-progress, Same as RM35UB3N30 ¦ ,Output is energized, Same as RM35UB3N30 ¦ ,Output is de-energized, Same as RM35UB3N30 ¦ ,Range Setting Changes, Same as RM35UB3N30 ¦ ,Phase Cut, Same as RM35UB3N30 ¦ ,Phase Sequence Swap, Same as RM35UB3N30 ¦ ,Undervoltage <U, Same as RM35UB3N30 ¦ ,Overvoltage >U, Same as RM35UB3N30 ¦ ,Phase Asymmetry, Same as RM35UB3N30 ¦ ,Voltage Regeneration, Same as RM35UB3N30 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM35UB3N30 ¦ ,Extreme Overvoltage >U, Same as RM35UB3N30 ¦ ,Extreme Phase Asymmetry,
84873895marking | UL, CSA, CE, China ROHS
84873895maximum leakage current | Same as RM35UB3N30 ¦ IEC62314,Only for solid state output,
84873895maximum measuring cycle | Same as RM35UB3N30 ¦ ,Maximum measuring cycles,
84873895maximum switching capacity | Same as RM35UB3N30 ¦ ,Maximum switching voltage, Same as RM35UB3N30 ¦ ,Maximum switching current, Same as RM35UB3N30 ¦ ,Maximum switching capacity,
84873895maximum voltage drop | Same as RM35UB3N30 ¦ IEC62314,Only for solid state output,
84873895measurement method | Same as RM35UB3N30 ¦ ,Measurement method,
84873895measurement range | Same as RM35UB3N30 ¦ ,Phase lost , Same as RM35UB3N30 ¦ ,Phase sequence, Same as RM35UB3N30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35UB3N30 ¦ ,Over voltage, Same as RM35UB3N30 ¦ ,Undervoltage , Same as RM35UB3N30 ¦ ,Phase asymmetry, Same as RM35UB3N30 ¦ ,Disconnection of neutral, Same as RM35UB3N30 ¦ ,Voltage Regeneration, Same as RM35UB3N30 ¦ ,Extreme undervoltage, Same as RM35UB3N30 ¦ ,Extreme Overvoltage, Same as RM35UB3N30 ¦ ,Extreme Asymmetry,
84873895mechanical durability | Same as RM35UB3N30 ¦ IEC61810-1
84873895minimum switching capacity | Same as RM35UB3N30 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM35UB3N30 ¦ IEC60947-5-4,Minimum switching current, Same as RM35UB3N30 ¦ IEC60947-5-4,Minimum switching capacity,
84873895monitoring functions | Same as RM35UB3N30 ¦ ,Phase lost , Same as RM35UB3N30 ¦ ,Phase sequence, Same as RM35UB3N30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35UB3N30 ¦ ,Over voltage, Same as RM35UB3N30 ¦ ,Undervoltage , Same as RM35UB3N30 ¦ ,Phase asymmetry, Same as RM35UB3N30 ¦ ,Disconnection of neutral, Same as RM35UB3N30 ¦ ,Voltage Regeneration, Same as RM35UB3N30 ¦ ,Extreme undervoltage, Same as RM35UB3N30 ¦ ,Extreme overvoltage, Same as RM35UB3N30 ¦ ,Extreme asymmetry,
84873895mounting position | Same as RM35UB3N30 ¦ ,In relation to normal vertical mounting plane,
84873895mounting support | Same as RM35UB3N30 ¦ IEC/EN 60715,Without socket, Same as RM35UB3N30 ¦ IEC/EN 60715,With socket,
84873895net weight | Same as RM35UB3N30
84873895on-load factor | Same as RM35UB3N30
84873895output logic | Same as RM35UB3N30 ¦ ,R1 (11-12-14), Same as RM35UB3N30 ¦ ,R2 (21-22-24),
84873895output terminal | Same as RM35UB3N30
84873895output type | Same as RM35UB3N30
84873895overvoltage category | Same as RM35UB3N30 ¦ IEC60664-1
84873895permissible input overload | Same as RM35UB3N30 ¦ ,permissible input overload,
84873895polarity | Same as RM35UB3N30
84873895pollution degree | Same as RM35UB3N30 ¦ IEC60664-1
84873895power consumption | Same as RM35UB3N30
84873895power on delay | Same as RM35UB3N30
84873895product certifications | UL, CSA, CE, China ROHS
84873895relative humidity | Same as RM35UB3N30 ¦ IEC60068-2-30,Damp heat,XX
84873895release of input voltage | Same as RM35UB3N30
84873895repeat accuracy of the switching threshold | Same as RM35UB3N30 ¦ ,Repeat accuracy (constant parameters),
84873895repeat accuracy of time delay | Same as RM35UB3N30
84873895reset time | Same as RM35UB3N30 ¦ ,through Un power reset, Same as RM35UB3N30 ¦ ,through front panel reset, Same as RM35UB3N30 ¦ ,through input control reset,
84873895response time | Same as RM35UB3N30 ¦ ,on crossing the threshold, Same as RM35UB3N30 Same as RM35UB3N30 Same as RM35UB3N30 Same as RM35UB3N30
84873895safety reliability data | Same as RM35UB3N30 ¦ ,MTTF, Same as RM35UB3N30 ¦ ,B10,
84873895seismic resistance | Same as RM35UB3N30 ¦ IEC60068-3-3
84873895setting accuracy of the switching threshold | Same as RM35UB3N30 ¦ ,Setting accuracy,
84873895setting accuracy of time delay | Same as RM35UB3N30
84873895shock resistance | Same as RM35UB3N30 ¦ IEC60068-2-27
84873895short circuit protection | Same as RM35UB3N30 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM35UB3N30 ¦ IEC62314,Solid State Output by external fuse,
84873895standards | Same as RM35UB3N30
84873895status LED | Same as RM35UB3N30
84873895supply frequency | Same as RM35UB3N30 Same as RM35UB3N30
84873895supply terminal | Same as RM35UB3N30
84873895supply voltage limits | Same as RM35UB3N30
84873895switching threshold drift | Same as RM35UB3N30 ¦ ,Measurement error with supply voltage variation, Same as RM35UB3N30 ¦ ,Measurement error with temperature variation,
84873895thermal current | Same as RM35UB3N30 ¦ IEC60947-5-1
84873895tightening torque | Same as RM35UB3N30 ¦ IEC60947-1,Tightening torque,
84873895time delay drift | Same as RM35UB3N30 Same as RM35UB3N30
84873895time delay range | Same as RM35UB3N30 ¦ ,"OFF" delay, Same as RM35UB3N30 ¦ ,"ON" delay, Same as RM35UB3N30 ¦ ,Inhibition,
84873895time delay type | Same as RM35UB3N30 ¦ ,"OFF" delay, Same as RM35UB3N30 ¦ ,"ON" delay, Same as RM35UB3N30 ¦ ,Inhibition,
84873895tripping threshold | Same as RM35UB3N30 ¦ ,Phase cut, Same as RM35UB3N30 ¦ ,Phase sequence, Same as RM35UB3N30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35UB3N30 ¦ ,Over voltage, Same as RM35UB3N30 ¦ ,Undervoltage , Same as RM35UB3N30 ¦ ,Phase asymmetry, Same as RM35UB3N30 ¦ ,Disconnection of neutral, Same as RM35UB3N30 ¦ ,Voltage Regeneration, Same as RM35UB3N30 ¦ ,Extreme undervoltage (Phase loss), Same as RM35UB3N30 ¦ ,Extreme Overvoltage, Same as RM35UB3N30 ¦ ,Extreme Asymmetry,
84873895vibration resistance | Same as RM35UB3N30 ¦ IEC60068-2-6
84873895width | Same as RM35UB3N30 ¦ ,Width,
84873896 | Same as RM17UB310 ¦ IEC60721-3-3,Climatic category, Same as RM17UB310 ¦ Germanisher Lloyd,Environmental category, Same as RM17UB310 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM17UB310 ¦ ,Supply,Rated Same as RM17UB310 ¦ ,Input 1,Voltage Same as RM17UB310 ¦ ,Input 2,Spec Same as RM17UB310 ¦ ,Input 3, Same as RM17UB310 ¦ ,Output 1, Same as RM17UB310 ¦ ,Output 2, Same as RM17UB310 ¦ ,Measurement mode, Same as RM17UB310 Same as RM17UB310 Same as RM17UB310 Same as RM17UB310 Same as RM17UB310 ¦ ,MTTFd, Same as RM17UB310 ¦ ,B10d, Drawing / Diagram
84873896IP degree of protection | Same as RM17UB310 ¦ IEC60529,Terminal Block, Same as RM17UB310 ¦ IEC60529,Housing, Same as RM17UB310 ¦ IEC60529,Front Panel,
84873896Input nominal voltage selection | Same as RM17UB310 ¦ ,Input nominal voltage selection,
84873896Minimum distance to adjacent devices | Same as RM17UB310 ¦ ,Horizontal, Same as RM17UB310 ¦ ,Vertical,
84873896[Ie] rated operational current | Same as RM17UB310 ¦ IEC61810-1,Rated switching current,
84873896[Ue] rated operational voltage | Same as RM17UB310 ¦ IEC61810-1,Rated switching voltage,
84873896[Ui] rated insulation voltage | Same as RM17UB310 ¦ IEC60664-1,Supply, Same as RM17UB310 ¦ IEC60664-1,Input 1, Same as RM17UB310 ¦ IEC60664-1,Input 2, Same as RM17UB310 ¦ IEC60664-1,Input 3, Same as RM17UB310 ¦ IEC60664-1,Output 1, Same as RM17UB310 ¦ IEC60664-1,Output 2, Same as RM17UB310 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17UB310 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17UB310 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17UB310 ¦ IEC60664-1,Supply / Output 1, Same as RM17UB310 ¦ IEC60664-1,Supply / Output 2, Same as RM17UB310 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17UB310 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17UB310 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17UB310 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17UB310 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17UB310 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17UB310 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17UB310 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17UB310 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17UB310 ¦ IEC60664-1,Input 1 / Input 3,
84873896[Uimp] rated impulse withstand voltage | Same as RM17UB310 ¦ IEC60664-1,Supply, Same as RM17UB310 ¦ IEC60664-1,Input 1, Same as RM17UB310 ¦ IEC60664-1,Input 2, Same as RM17UB310 ¦ IEC60664-1,Input 3, Same as RM17UB310 ¦ IEC60664-1,Output 1, Same as RM17UB310 ¦ IEC60664-1,Output 2, Same as RM17UB310 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17UB310 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17UB310 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17UB310 ¦ IEC60664-1,Supply / Output 1, Same as RM17UB310 ¦ IEC60664-1,Supply / Output 2, Same as RM17UB310 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17UB310 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17UB310 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17UB310 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17UB310 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17UB310 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17UB310 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17UB310 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17UB310 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17UB310 ¦ IEC60664-1,Input 1 / Input 3,
84873896[Us] rated supply voltage | Same as RM17UB310
84873896ambient air temperature for operation | Same as RM17UB310 ¦ ,Operation,
84873896ambient air temperature for storage | Same as RM17UB310 ¦ ,Storage,
84873896bump resistance | Same as RM17UB310 ¦ IEC60068-2-29
84873896cable stripping length | Same as RM17UB310 ¦ ,Cable stripping length,
84873896circuit group | Same as RM17UB310 ¦ ,Supply,Terminal Same as RM17UB310 ¦ ,Input 1, Same as RM17UB310 ¦ ,Input 2, Same as RM17UB310 ¦ ,Input 3, Same as RM17UB310 ¦ ,Output 1, Same as RM17UB310 ¦ ,Output 2,
84873896connections - terminals | Same as RM17UB310 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17UB310 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17UB310 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17UB310 ¦ IEC60947-1,Flexible cable (spring terminal),
84873896contacts material | Same as RM17UB310
84873896depth | Same as RM17UB310 ¦ ,Depth,
84873896diagnostic button | Same as RM17UB310
84873896dielectric strength | Same as RM17UB310 ¦ IEC60255-27,Supply / Input 1, Same as RM17UB310 ¦ IEC60255-27,Supply / Input 2, Same as RM17UB310 ¦ IEC60255-27,Supply / Input 3, Same as RM17UB310 ¦ IEC60255-27,Supply / Output 1, Same as RM17UB310 ¦ IEC60255-27,Supply / Output 2, Same as RM17UB310 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17UB310 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17UB310 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17UB310 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17UB310 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17UB310 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17UB310 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17UB310 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17UB310 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17UB310 ¦ IEC60255-27,Input 1 / Input 3,
84873896directives | Same as RM17UB310 Same as RM17UB310 Same as RM17UB310
84873896duty time | Same as RM17UB310
84873896electrical durability | Same as RM17UB310 ¦ IEC60947-4-1,AC-1, Same as RM17UB310 ¦ IEC60947-4-1,DC-1, Same as RM17UB310 ¦ IEC60947-5-1,AC-15, Same as RM17UB310 ¦ IEC60947-5-1,DC-13,
84873896electromagnetic compatibility | Same as RM17UB310 ¦ ,Generic immunity standard, Same as RM17UB310 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17UB310 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17UB310 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17UB310 ¦ IEC61000-4-5,Surge, Same as RM17UB310 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17UB310 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17UB310 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17UB310 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17UB310 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17UB310 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM17UB310 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17UB310 ¦ ,Generic emission standard, Same as RM17UB310 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17UB310 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17UB310 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17UB310 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17UB310 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17UB310 ¦ Germanisher Lloyd,Conducted emission,
84873896height | Same as RM17UB310 ¦ ,Height,
84873896hysteresis | Same as RM17UB310 ¦ ,Phase cut, Same as RM17UB310 ¦ ,Phase sequence, Same as RM17UB310 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17UB310 ¦ ,Over voltage, Same as RM17UB310 ¦ ,Undervoltage , Same as RM17UB310 ¦ ,Phase asymmetry, Same as RM17UB310 ¦ ,Disconnection of neutral, Same as RM17UB310 ¦ ,Voltage Regeneration, Same as RM17UB310 ¦ ,Extreme undervoltage (Phase loss), Same as RM17UB310 ¦ ,Extreme Overvoltage, Same as RM17UB310 ¦ ,Extreme Asymmetry,
84873896immunity to microbreaks | Same as RM17UB310
84873896input frequency | Same as RM17UB310 ¦ ,Rated frequency, Same as RM17UB310 ¦ ,Frequency operating range,
84873896input terminal | Same as RM17UB310 ¦ ,Input terminal,
84873896insulation resistance | Same as RM17UB310 ¦ IEC60255-27,Supply / Input 1, Same as RM17UB310 ¦ IEC60255-27,Supply / Input 2, Same as RM17UB310 ¦ IEC60255-27,Supply / Input 3, Same as RM17UB310 ¦ IEC60255-27,Supply / Output 1, Same as RM17UB310 ¦ IEC60255-27,Supply / Output 2, Same as RM17UB310 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17UB310 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17UB310 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17UB310 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17UB310 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17UB310 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17UB310 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17UB310 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17UB310 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17UB310 ¦ IEC60255-27,Input 1 / Input 3,
84873896internal input resistance | Same as RM17UB310 ¦ ,Internal input resistance,
84873896local signalling | Same as RM17UB310 ¦ ,Power supply availability, Same as RM17UB310 ¦ ,Power supply not availability, Same as RM17UB310 ¦ ,Timing in-progress, Same as RM17UB310 ¦ ,Output is energized, Same as RM17UB310 ¦ ,Output is de-energized, Same as RM17UB310 ¦ ,Range Setting Changes, Same as RM17UB310 ¦ ,Phase Cut, Same as RM17UB310 ¦ ,Phase Sequence Swap, Same as RM17UB310 ¦ ,Undervoltage <U, Same as RM17UB310 ¦ ,Overvoltage >U, Same as RM17UB310 ¦ ,Phase Asymmetry, Same as RM17UB310 ¦ ,Voltage Regeneration, Same as RM17UB310 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17UB310 ¦ ,Extreme Overvoltage >U, Same as RM17UB310 ¦ ,Extreme Phase Asymmetry,
84873896marking | UL, CSA, CE, China ROHS
84873896maximum leakage current | Same as RM17UB310 ¦ IEC62314,Only for solid state output,
84873896maximum measuring cycle | Same as RM17UB310 ¦ ,Maximum measuring cycles,
84873896maximum switching capacity | Same as RM17UB310 ¦ ,Maximum switching voltage, Same as RM17UB310 ¦ ,Maximum switching current, Same as RM17UB310 ¦ ,Maximum switching capacity,
84873896maximum voltage drop | Same as RM17UB310 ¦ IEC62314,Only for solid state output,
84873896measurement method | Same as RM17UB310 ¦ ,Measurement method,
84873896measurement range | Same as RM17UB310 ¦ ,Phase lost , Same as RM17UB310 ¦ ,Phase sequence, Same as RM17UB310 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17UB310 ¦ ,Over voltage, Same as RM17UB310 ¦ ,Undervoltage , Same as RM17UB310 ¦ ,Phase asymmetry, Same as RM17UB310 ¦ ,Disconnection of neutral, Same as RM17UB310 ¦ ,Voltage Regeneration, Same as RM17UB310 ¦ ,Extreme undervoltage, Same as RM17UB310 ¦ ,Extreme Overvoltage, Same as RM17UB310 ¦ ,Extreme Asymmetry,
84873896mechanical durability | Same as RM17UB310 ¦ IEC61810-1
84873896minimum switching capacity | Same as RM17UB310 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17UB310 ¦ IEC60947-5-4,Minimum switching current, Same as RM17UB310 ¦ IEC60947-5-4,Minimum switching capacity,
84873896monitoring functions | Same as RM17UB310 ¦ ,Phase lost , Same as RM17UB310 ¦ ,Phase sequence, Same as RM17UB310 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17UB310 ¦ ,Over voltage, Same as RM17UB310 ¦ ,Undervoltage , Same as RM17UB310 ¦ ,Phase asymmetry, Same as RM17UB310 ¦ ,Disconnection of neutral, Same as RM17UB310 ¦ ,Voltage Regeneration, Same as RM17UB310 ¦ ,Extreme undervoltage, Same as RM17UB310 ¦ ,Extreme overvoltage, Same as RM17UB310 ¦ ,Extreme asymmetry,
84873896mounting position | Same as RM17UB310 ¦ ,In relation to normal vertical mounting plane,
84873896mounting support | Same as RM17UB310 ¦ IEC/EN 60715,Without socket, Same as RM17UB310 ¦ IEC/EN 60715,With socket,
84873896net weight | Same as RM17UB310
84873896on-load factor | Same as RM17UB310
84873896output logic | Same as RM17UB310 ¦ ,R1 (11-12-14), Same as RM17UB310 ¦ ,R2 (21-22-24),
84873896output terminal | Same as RM17UB310
84873896output type | Same as RM17UB310
84873896overvoltage category | Same as RM17UB310 ¦ IEC60664-1
84873896permissible input overload | Same as RM17UB310 ¦ ,permissible input overload,
84873896polarity | Same as RM17UB310
84873896pollution degree | Same as RM17UB310 ¦ IEC60664-1
84873896power consumption | Same as RM17UB310
84873896power on delay | Same as RM17UB310
84873896product certifications | UL, CSA, CE, China ROHS
84873896relative humidity | Same as RM17UB310 ¦ IEC60068-2-30,Damp heat,XX
84873896release of input voltage | Same as RM17UB310
84873896repeat accuracy of the switching threshold | Same as RM17UB310 ¦ ,Repeat accuracy (constant parameters),
84873896repeat accuracy of time delay | Same as RM17UB310
84873896reset time | Same as RM17UB310 ¦ ,through Un power reset, Same as RM17UB310 ¦ ,through front panel reset, Same as RM17UB310 ¦ ,through input control reset,
84873896response time | Same as RM17UB310 ¦ ,on crossing the threshold, Same as RM17UB310 Same as RM17UB310 Same as RM17UB310 Same as RM17UB310
84873896safety reliability data | Same as RM17UB310 ¦ ,MTTF, Same as RM17UB310 ¦ ,B10,
84873896seismic resistance | Same as RM17UB310 ¦ IEC60068-3-3
84873896setting accuracy of the switching threshold | Same as RM17UB310 ¦ ,Setting accuracy,
84873896setting accuracy of time delay | Same as RM17UB310
84873896shock resistance | Same as RM17UB310 ¦ IEC60068-2-27
84873896short circuit protection | Same as RM17UB310 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17UB310 ¦ IEC62314,Solid State Output by external fuse,
84873896standards | Same as RM17UB310
84873896status LED | Same as RM17UB310
84873896supply frequency | Same as RM17UB310 Same as RM17UB310
84873896supply terminal | Same as RM17UB310
84873896supply voltage limits | Same as RM17UB310
84873896switching threshold drift | Same as RM17UB310 ¦ ,Measurement error with supply voltage variation, Same as RM17UB310 ¦ ,Measurement error with temperature variation,
84873896thermal current | Same as RM17UB310 ¦ IEC60947-5-1
84873896tightening torque | Same as RM17UB310 ¦ IEC60947-1,Tightening torque,
84873896time delay drift | Same as RM17UB310 Same as RM17UB310
84873896time delay range | Same as RM17UB310 ¦ ,"OFF" delay, Same as RM17UB310 ¦ ,"ON" delay, Same as RM17UB310 ¦ ,Inhibition,
84873896time delay type | Same as RM17UB310 ¦ ,"OFF" delay, Same as RM17UB310 ¦ ,"ON" delay, Same as RM17UB310 ¦ ,Inhibition,
84873896tripping threshold | Same as RM17UB310 ¦ ,Phase cut, Same as RM17UB310 ¦ ,Phase sequence, Same as RM17UB310 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17UB310 ¦ ,Over voltage, Same as RM17UB310 ¦ ,Undervoltage , Same as RM17UB310 ¦ ,Phase asymmetry, Same as RM17UB310 ¦ ,Disconnection of neutral, Same as RM17UB310 ¦ ,Voltage Regeneration, Same as RM17UB310 ¦ ,Extreme undervoltage (Phase loss), Same as RM17UB310 ¦ ,Extreme Overvoltage, Same as RM17UB310 ¦ ,Extreme Asymmetry,
84873896vibration resistance | Same as RM17UB310 ¦ IEC60068-2-6
84873896width | Same as RM17UB310 ¦ ,Width,
848792299 | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d,
848792299IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, Not specified ¦ IEC60529,Front Panel,
848792299Input nominal voltage selection | Fixed @ ~ 3 x 230…3 x 440 ¦ ,Input nominal voltage selection,
848792299Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
848792299[Ie] rated operational current | IEC61810-1,Rated switching current,
848792299[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
848792299[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
848792299[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
848792299[Us] rated supply voltage | ~ 3 x 230…3 x 440
848792299ambient air temperature for operation | Not specified ¦ ,Operation,
848792299ambient air temperature for storage | -30…+70 ¦ ,Storage,
848792299bump resistance | IEC60068-2-29
848792299cable stripping length | Cable stripping length,
848792299circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
848792299connections - terminals | 1 conductor: 4 (AWG11) 2 conductor:2.5 (AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 2 conductor: 1.5 (AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
848792299contacts material | Cadmium free
848792299depth | Depth,
848792299diagnostic button
848792299dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
848792299directives | Not specified Not specified Not specified
848792299duty time
848792299electrical durability | Not specified ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
848792299electromagnetic compatibility | Not specified ¦ ,Generic immunity standard, Not specified ¦ IEC61000-4-2,Electrostatic discharge, Not specified ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Not specified ¦ IEC61000-4-4,Fast transient / burst, Not specified ¦ IEC61000-4-5,Surge, Not specified ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Not specified ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not specified ¦ IEC61000-4-13,Low frequency harmonics, Not specified ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Not specified ¦ ,Generic emission standard, Not specified ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Not specified ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Not specified ¦ Germanisher Lloyd,Radiated emission from enclosure port, Not specified ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Not specified ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Not specified ¦ Germanisher Lloyd,Conducted emission,
848792299height | Height,
848792299hysteresis | Not specified ¦ ,Phase cut, Not specified ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
848792299immunity to microbreaks | Not specified
848792299input frequency | 50 / 60 ¦ ,Rated frequency, 49…61 ¦ ,Frequency operating range,
848792299input terminal | L1-L2-L3 ¦ ,Input terminal,
848792299insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
848792299internal input resistance | Not specified ¦ ,Internal input resistance,
848792299local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Phase Cut, Phase Sequence Swap, Undervoltage <U, Overvoltage >U, Phase Asymmetry, Voltage Regeneration, Extreme Undervoltage <U (Phase loss), Extreme Overvoltage >U, Extreme Phase Asymmetry,
848792299marking | cULus, CE
848792299maximum leakage current | IEC62314,Only for solid state output,
848792299maximum measuring cycle | Not specified ¦ ,Maximum measuring cycles,
848792299maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 8 ¦ ,Maximum switching current, 2000 ¦ ,Maximum switching capacity,
848792299maximum voltage drop | IEC62314,Only for solid state output,
848792299measurement method | Not specified ¦ ,Measurement method,
848792299measurement range | Not specified ¦ ,Phase lost , Not specified ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme Overvoltage, Extreme Asymmetry,
848792299mechanical durability | 20 x 106 switching cycles ¦ IEC61810-1
848792299minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
848792299monitoring functions | · ¦ ,Phase lost , · ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry,
848792299mounting position | In relation to normal vertical mounting plane,
848792299mounting support | IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
848792299net weight | 110
848792299on-load factor
848792299output logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
848792299output terminal | 2014-11-12 00:00:00
848792299output type | 1 x C/O relay contacts
848792299overvoltage category | IEC60664-1
848792299permissible input overload | Not specified ¦ ,permissible input overload,
848792299polarity
848792299pollution degree | IEC60664-1
848792299power consumption | 25
848792299power on delay | 0
848792299product certifications | cULus, CE
848792299relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,XX
848792299release of input voltage
848792299repeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
848792299repeat accuracy of time delay | -
848792299reset time | - ¦ ,through Un power reset, through front panel reset, through input control reset,
848792299response time | 0
848792299safety reliability data | MTTF, B10,
848792299seismic resistance | IEC60068-3-3
848792299setting accuracy of the switching threshold | - ¦ ,Setting accuracy,
848792299setting accuracy of time delay | -
848792299shock resistance | Not specified ¦ IEC60068-2-27
848792299short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
848792299standards | Not specified
848792299status LED
848792299supply frequency | 50 / 60 49…61
848792299supply terminal | Not specified
848792299supply voltage limits | Not specified
848792299switching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation, Not specified ¦ ,Measurement error with temperature variation,
848792299thermal current | IEC60947-5-1
848792299tightening torque | Max 1 ¦ IEC60947-1,Tightening torque,
848792299time delay drift | - -
848792299time delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
848792299time delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
848792299tripping threshold | Not specified ¦ ,Phase cut, Not specified ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
848792299vibration resistance | Not specified ¦ IEC60068-2-6
848792299width | 22.5 x 78.5 x 100 ¦ ,Width,
84893852 (Autelec Distribution) | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Not specified ¦ ,Supply,Rated Not specified ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, - ¦ ,Over / undercurrent (windows mode), - ¦ ,Over current, · ¦ ,Under current, Fix 0.7A Not specified ¦ ,E1-M / B1-C, Not specified ¦ ,E2-M / B2-C, Not specified ¦ ,E3-M / B3-C, A1+ / A2-, Not specified ¦ ,Built in current transformer, Not specified ¦ ,E1-M / B1-C, Max 12A ¦ ,E2-M / B2-C, Not specified ¦ ,E3-M / B3-C, A1+ / A2-, Not specified ¦ ,Built in current transformer, Not specified ¦ ,E1-M / B1-C, Not specified ¦ ,E2-M / B2-C, Not specified ¦ ,E3-M / B3-C, A1+ / A2-, Not specified ¦ ,Built in current transformer, Not specified ¦ ,E1-M / B1-C, Not specified ¦ ,E2-M / B2-C, Not specified ¦ ,E3-M / B3-C, A1+ / A2-, Not specified ¦ ,Built in current transformer, Not specified Not specified Not specified Not specified Not specified Not specified Not specified Not specified Not specified Not specified MTTFd, B10d,
84893852 (Autelec Distribution)IP degree of protection | Not specified ¦ IEC60529,Terminal Block, Not specified ¦ IEC60529,Housing, IEC60529,Front Panel,
84893852 (Autelec Distribution)Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
84893852 (Autelec Distribution)[Ie] rated operational current | IEC61810-1,Rated switching current,
84893852 (Autelec Distribution)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
84893852 (Autelec Distribution)[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, Not specified ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
84893852 (Autelec Distribution)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
84893852 (Autelec Distribution)[Us] rated supply voltage | ~ 24…240
84893852 (Autelec Distribution)ambient air temperature for operation | Not specified ¦ ,Operation,
84893852 (Autelec Distribution)ambient air temperature for storage | Not specified ¦ ,Storage,
84893852 (Autelec Distribution)bump resistance | IEC60068-2-29
84893852 (Autelec Distribution)cable stripping length | Not specified ¦ ,Cable stripping length,
84893852 (Autelec Distribution)circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Not specified ¦ ,Output 2,
84893852 (Autelec Distribution)connections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal), Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
84893852 (Autelec Distribution)contacts material | Not specified
84893852 (Autelec Distribution)depth | Depth,
84893852 (Autelec Distribution)diagnostic button
84893852 (Autelec Distribution)dielectric strength | Not specified ¦ IEC60255-27,Supply / Input 1, Not specified ¦ IEC60255-27,Supply / Input 2, Not specified ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
84893852 (Autelec Distribution)directives | Not specified Not specified Not specified
84893852 (Autelec Distribution)duty time | Not specified
84893852 (Autelec Distribution)electrical durability | Not specified ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
84893852 (Autelec Distribution)electromagnetic compatibility | Not specified ¦ ,Generic immunity standard, Not specified ¦ IEC61000-4-2,Electrostatic discharge, Not specified ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Not specified ¦ IEC61000-4-4,Fast transient / burst, Not specified ¦ IEC61000-4-5,Surge, Not specified ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Not specified ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not specified ¦ IEC61000-4-13,Low frequency harmonics, Not specified ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Not specified ¦ ,Generic emission standard, Not specified ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Not specified ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Not specified ¦ Germanisher Lloyd,Radiated emission from enclosure port, Not specified ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Not specified ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Not specified ¦ Germanisher Lloyd,Conducted emission,
84893852 (Autelec Distribution)height | Height,
84893852 (Autelec Distribution)immunity to microbreaks | Not specified
84893852 (Autelec Distribution)insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
84893852 (Autelec Distribution)local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
84893852 (Autelec Distribution)marking | CE
84893852 (Autelec Distribution)maximum leakage current | - ¦ IEC62314,Only for solid state output,
84893852 (Autelec Distribution)maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, ~ 5 ¦ ,Maximum switching current, 1250 ¦ ,Maximum switching capacity,
84893852 (Autelec Distribution)maximum voltage drop | - ¦ IEC62314,Only for solid state output,
84893852 (Autelec Distribution)mechanical durability | Not specified ¦ IEC61810-1
84893852 (Autelec Distribution)minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching voltage, Not specified ¦ IEC60947-5-4,Minimum switching current, Not specified ¦ IEC60947-5-4,Minimum switching capacity,
84893852 (Autelec Distribution)mounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
84893852 (Autelec Distribution)mounting support | Not specified ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
84893852 (Autelec Distribution)net weight | Not specified
84893852 (Autelec Distribution)on-load factor
84893852 (Autelec Distribution)output logic | De-Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
84893852 (Autelec Distribution)output terminal | 11-12-14
84893852 (Autelec Distribution)output type | 1 x C/O relay contacts
84893852 (Autelec Distribution)overvoltage category | Not specified ¦ IEC60664-1
84893852 (Autelec Distribution)polarity
84893852 (Autelec Distribution)pollution degree | Not specified ¦ IEC60664-1
84893852 (Autelec Distribution)power consumption | Not specified
84893852 (Autelec Distribution)power on delay | Not specified
84893852 (Autelec Distribution)product certifications | Not specified
84893852 (Autelec Distribution)relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
84893852 (Autelec Distribution)release of input voltage
84893852 (Autelec Distribution)repeat accuracy of time delay | Not specified
84893852 (Autelec Distribution)reset time | Not specified ¦ ,through Un power reset, through front panel reset, through input control reset,
84893852 (Autelec Distribution)response time | Not specified ¦ ,on crossing the threshold,
84893852 (Autelec Distribution)safety reliability data | MTTF, B10,
84893852 (Autelec Distribution)seismic resistance | IEC60068-3-3
84893852 (Autelec Distribution)setting accuracy of time delay | Not specified
84893852 (Autelec Distribution)shock resistance | Not specified ¦ IEC60068-2-27
84893852 (Autelec Distribution)short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
84893852 (Autelec Distribution)standards | Not specified
84893852 (Autelec Distribution)status LED
84893852 (Autelec Distribution)supply frequency | Not specified Not specified
84893852 (Autelec Distribution)supply terminal | A1-A2
84893852 (Autelec Distribution)supply voltage limits | Not specified
84893852 (Autelec Distribution)thermal current | IEC60947-5-1
84893852 (Autelec Distribution)tightening torque | Not specified ¦ IEC60947-1,Tightening torque,
84893852 (Autelec Distribution)time delay drift | Not specified Not specified
84893852 (Autelec Distribution)time delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
84893852 (Autelec Distribution)time delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
84893852 (Autelec Distribution)vibration resistance | Not specified ¦ IEC60068-2-6
84893852 (Autelec Distribution)width | 22.5 x 78.5 x 100 ¦ ,Width,
84893852 (Catch Up) | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, 600 ¦ ,Supply,Rated 600 ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, - ¦ ,Over / undercurrent (windows mode), - ¦ ,Over current, · ¦ ,Under current, Fix 0.7A - ¦ ,E1-M / B1-C, 0.015 ¦ ,E2-M / B2-C, - ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, - ¦ ,E1-M / B1-C, Max 12A ¦ ,E2-M / B2-C, - ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, - ¦ ,E1-M / B1-C, - ¦ ,E2-M / B2-C, - ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, - ¦ ,E1-M / B1-C, - ¦ ,E2-M / B2-C, - ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Shunt resistor E2-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 True RMS MTTFd, B10d,
84893852 (Catch Up)IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IEC60529,Front Panel,
84893852 (Catch Up)Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
84893852 (Catch Up)[Ie] rated operational current | IEC61810-1,Rated switching current,
84893852 (Catch Up)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
84893852 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, 4 ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
84893852 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
84893852 (Catch Up)[Us] rated supply voltage | ~/-- 24…240
84893852 (Catch Up)ambient air temperature for operation | -20…+50 ¦ ,Operation,
84893852 (Catch Up)ambient air temperature for storage | -40…+70 ¦ ,Storage,
84893852 (Catch Up)bump resistance | IEC60068-2-29
84893852 (Catch Up)cable stripping length | Not specified ¦ ,Cable stripping length,
84893852 (Catch Up)circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, 600 ¦ ,Output 2,
84893852 (Catch Up)connections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
84893852 (Catch Up)contacts material | Cadmium free
84893852 (Catch Up)depth | Depth,
84893852 (Catch Up)diagnostic button
84893852 (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
84893852 (Catch Up)directives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
84893852 (Catch Up)duty time | Not specified
84893852 (Catch Up)electrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
84893852 (Catch Up)electromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
84893852 (Catch Up)height | Height,
84893852 (Catch Up)immunity to microbreaks | 10
84893852 (Catch Up)insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
84893852 (Catch Up)local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
84893852 (Catch Up)marking | UL, CSA, GL, C-Tick, GOST, CE, CCC
84893852 (Catch Up)maximum leakage current | - ¦ IEC62314,Only for solid state output,
84893852 (Catch Up)maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, ~ 5 ¦ ,Maximum switching current, 1250 ¦ ,Maximum switching capacity,
84893852 (Catch Up)maximum voltage drop | - ¦ IEC62314,Only for solid state output,
84893852 (Catch Up)mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
84893852 (Catch Up)minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
84893852 (Catch Up)mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
84893852 (Catch Up)mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
84893852 (Catch Up)net weight | ?
84893852 (Catch Up)on-load factor
84893852 (Catch Up)output logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
84893852 (Catch Up)output terminal | 2014-11-12 00:00:00
84893852 (Catch Up)output type | 21x C/O relay contacts
84893852 (Catch Up)overvoltage category | III ¦ IEC60664-1
84893852 (Catch Up)polarity
84893852 (Catch Up)pollution degree | 3 ¦ IEC60664-1
84893852 (Catch Up)power consumption | ~ 3.5VA, -- 0.6W
84893852 (Catch Up)power on delay | 0
84893852 (Catch Up)product certifications | UL, CSA, GL, C-Tick, GOST, CCC
84893852 (Catch Up)relative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
84893852 (Catch Up)release of input voltage
84893852 (Catch Up)repeat accuracy of time delay | +/- 2%
84893852 (Catch Up)reset time | 0
84893852 (Catch Up)response time | Not specified ¦ ,on crossing the threshold,
84893852 (Catch Up)safety reliability data | MTTF, B10,
84893852 (Catch Up)seismic resistance | IEC60068-3-3
84893852 (Catch Up)setting accuracy of time delay | +/- 10% of full scales
84893852 (Catch Up)shock resistance | 5 gn ¦ IEC60068-2-27
84893852 (Catch Up)short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
84893852 (Catch Up)standards | EN60255-6, IEC60255-6
84893852 (Catch Up)status LED
84893852 (Catch Up)supply frequency | 50 / 60 45…66
84893852 (Catch Up)supply terminal | A1-A2
84893852 (Catch Up)supply voltage limits | ~/-- 20.4…264
84893852 (Catch Up)thermal current | IEC60947-5-1
84893852 (Catch Up)tightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
84893852 (Catch Up)time delay drift | Not specified Not specified
84893852 (Catch Up)time delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
84893852 (Catch Up)time delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
84893852 (Catch Up)vibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
84893852 (Catch Up)width | 22.5 x ? x ? ¦ ,Width,
DPA51CM44 | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, MTTFd, B10d,
DPA51CM44IP degree of protection | IP20 ¦ IEC60529,Terminal Block, Not specified ¦ IEC60529,Housing, Not specified ¦ IEC60529,Front Panel,
DPA51CM44Input nominal voltage selection | Fixed @ ~ 3 x 177…3 x 550 ¦ ,Input nominal voltage selection,
DPA51CM44Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
DPA51CM44[Ie] rated operational current | IEC61810-1,Rated switching current,
DPA51CM44[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
DPA51CM44[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
DPA51CM44[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
DPA51CM44[Us] rated supply voltage | ~ 3 x 208…3 x 480
DPA51CM44ambient air temperature for operation | -20…+50, R.H. < 95% ¦ ,Operation,
DPA51CM44ambient air temperature for storage | -30…+80, R.H. < 95% ¦ ,Storage,
DPA51CM44bump resistance | IEC60068-2-29
DPA51CM44cable stripping length | Not specified ¦ ,Cable stripping length,
DPA51CM44circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
DPA51CM44connections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal), Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
DPA51CM44contacts material | AgSnO2
DPA51CM44depth | Depth,
DPA51CM44diagnostic button
DPA51CM44dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
DPA51CM44directives | Not specified Not specified Not specified
DPA51CM44duty time | Not specified
DPA51CM44electrical durability | >= 1 x 105 switching cycles @ 5A, 250VAC ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
DPA51CM44electromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard, Not specified ¦ IEC61000-4-2,Electrostatic discharge, Not specified ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Not specified ¦ IEC61000-4-4,Fast transient / burst, Not specified ¦ IEC61000-4-5,Surge, Not specified ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Not specified ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not specified ¦ IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC50081-1 ¦ ,Generic emission standard, Not specified ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Not specified ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), - ¦ Germanisher Lloyd,Radiated emission from enclosure port, Not specified ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Not specified ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), - ¦ Germanisher Lloyd,Conducted emission,
DPA51CM44height | Height,
DPA51CM44hysteresis | - ¦ ,Phase cut, - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
DPA51CM44immunity to microbreaks | -
DPA51CM44input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
DPA51CM44input terminal | L1-L2-L3 ¦ ,Input terminal,
DPA51CM44insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
DPA51CM44internal input resistance | Not specified ¦ ,Internal input resistance,
DPA51CM44local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Phase Cut, Phase Sequence Swap, Undervoltage <U, Overvoltage >U, Phase Asymmetry, Voltage Regeneration, Extreme Undervoltage <U (Phase loss), Extreme Overvoltage >U, Extreme Phase Asymmetry,
DPA51CM44marking | UL, CSA, CE
DPA51CM44maximum leakage current | IEC62314,Only for solid state output,
DPA51CM44maximum measuring cycle | - ¦ ,Maximum measuring cycles,
DPA51CM44maximum switching capacity | - ¦ ,Maximum switching voltage, - ¦ ,Maximum switching current, Maximum switching capacity,
DPA51CM44maximum voltage drop | IEC62314,Only for solid state output,
DPA51CM44measurement method | Not specified ¦ ,Measurement method,
DPA51CM44measurement range | Not specified ¦ ,Phase lost , Not specified ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme Overvoltage, Extreme Asymmetry,
DPA51CM44mechanical durability | >= 30 x 106 switching cycles ¦ IEC61810-1
DPA51CM44minimum switching capacity | IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity,
DPA51CM44monitoring functions | · ¦ ,Phase lost , · ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry,
DPA51CM44mounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
DPA51CM44mounting support | Mounting in DIN rail according EN50022 ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
DPA51CM44net weight | 75
DPA51CM44on-load factor
DPA51CM44output logic | - ¦ ,R1 (11-12-14), R2 (21-22-24),
DPA51CM44output terminal
DPA51CM44output type | 1 x C/O relay contact
DPA51CM44overvoltage category | IEC60664-1
DPA51CM44permissible input overload | Not specified ¦ ,permissible input overload,
DPA51CM44polarity
DPA51CM44pollution degree | IEC60664-1
DPA51CM44power consumption | 13VA (400VAC, 50Hz) by L2, L3
DPA51CM44power on delay | -
DPA51CM44product certifications | UL, CSA
DPA51CM44relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,XX
DPA51CM44release of input voltage
DPA51CM44repeat accuracy of the switching threshold | +/- 0.5% on full scale ¦ ,Repeat accuracy (constant parameters),
DPA51CM44repeat accuracy of time delay | -
DPA51CM44reset time | - ¦ ,through Un power reset, through front panel reset, through input control reset,
DPA51CM44response time | < 100 for ON delay ; < 300 for OFF delay ¦ ,on crossing the threshold,
DPA51CM44safety reliability data | MTTF, B10,
DPA51CM44seismic resistance | IEC60068-3-3
DPA51CM44setting accuracy of the switching threshold | - ¦ ,Setting accuracy,
DPA51CM44setting accuracy of time delay | -
DPA51CM44shock resistance | Not specified ¦ IEC60068-2-27
DPA51CM44short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
DPA51CM44standards | Not specified
DPA51CM44status LED
DPA51CM44supply frequency | 50 / 60 45…66
DPA51CM44supply terminal | L1-L2-L3
DPA51CM44supply voltage limits | ~ 3 x 177…3 x 550
DPA51CM44switching threshold drift | - ¦ ,Measurement error with supply voltage variation, 0.1% / oC ¦ ,Measurement error with temperature variation,
DPA51CM44thermal current | IEC60947-5-1
DPA51CM44tightening torque | 0.5Nm (Max) ¦ IEC60947-1,Tightening torque,
DPA51CM44time delay drift | - -
DPA51CM44time delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
DPA51CM44time delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
DPA51CM44tripping threshold | 1 phase below 85% of other phase ¦ ,Phase cut, - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
DPA51CM44vibration resistance | Not specified ¦ IEC60068-2-6
DPA51CM44width | 17.5 x 81 x 67.2 ¦ ,Width,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O) | IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)IP degree of protection | IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)Input nominal voltage selection | Input nominal voltage selection,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)Minimum distance to adjacent devices | Horizontal, Vertical,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ie] rated operational current | IEC61810-1,Rated switching current,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)[Us] rated supply voltage
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)ambient air temperature for operation | -20…+60 ¦ ,Operation,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)ambient air temperature for storage | -25…+65 ¦ ,Storage,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)bump resistance | IEC60068-2-29
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)cable stripping length | Cable stripping length,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)contacts material
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)depth | Depth,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)diagnostic button
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)directives
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)duty time
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electrical durability | - ¦ IEC60947-4-1,AC-1, - ¦ IEC60947-4-1,DC-1, - ¦ IEC60947-5-1,AC-15, - ¦ IEC60947-5-1,DC-13,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)electromagnetic compatibility | Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)height | Height,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)hysteresis | Phase cut, Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)immunity to microbreaks
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)input frequency | Rated frequency, Frequency operating range,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)input terminal | Input terminal,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)internal input resistance | Internal input resistance,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Phase Cut, Phase Sequence Swap, Undervoltage <U, Overvoltage >U, Phase Asymmetry, Voltage Regeneration, Extreme Undervoltage <U (Phase loss), Extreme Overvoltage >U, Extreme Phase Asymmetry,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)marking
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)maximum leakage current | IEC62314,Only for solid state output,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)maximum measuring cycle | Maximum measuring cycles,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)maximum switching capacity | Maximum switching voltage, Maximum switching current, Maximum switching capacity,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)maximum voltage drop | IEC62314,Only for solid state output,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)measurement method | Measurement method,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)measurement range | Phase lost , Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme Overvoltage, Extreme Asymmetry,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)mechanical durability | IEC61810-1
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)minimum switching capacity | IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)monitoring functions | Phase lost , Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)mounting position | In relation to normal vertical mounting plane,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)mounting support | IEC/EN 60715,Without socket, IEC/EN 60715,With socket,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)net weight
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)on-load factor
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)output logic | R1 (11-12-14), R2 (21-22-24),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)output terminal
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)output type
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)overvoltage category | IEC60664-1
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)permissible input overload | permissible input overload,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)polarity
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)pollution degree | IEC60664-1
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)power consumption
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)power on delay
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)product certifications
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)relative humidity | IEC60068-2-30,Damp heat,XX
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)release of input voltage
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)repeat accuracy of the switching threshold | Repeat accuracy (constant parameters),
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)repeat accuracy of time delay
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)reset time | through Un power reset, through front panel reset, through input control reset,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)response time | on crossing the threshold,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)safety reliability data | MTTF, B10,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)seismic resistance | IEC60068-3-3
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)setting accuracy of the switching threshold | Setting accuracy,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)setting accuracy of time delay
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)shock resistance | IEC60068-2-27
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)standards | EN60947-5-1
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)status LED
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)supply frequency
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)supply terminal
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)supply voltage limits
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)switching threshold drift | Measurement error with supply voltage variation, Measurement error with temperature variation,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)thermal current | IEC60947-5-1
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)tightening torque | 0.54Nm (Rec) 0.59Nm (Max) ¦ IEC60947-1,Tightening torque,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)time delay drift
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)time delay range | "OFF" delay, "ON" delay, Inhibition,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)time delay type | "OFF" delay, "ON" delay, Inhibition,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)tripping threshold | Phase cut, Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)vibration resistance | IEC60068-2-6
K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O)width | Width,
RM10TE00 | Same as RM17TE00 ¦ IEC60721-3-3,Climatic category, Same as RM17TE00 ¦ Germanisher Lloyd,Environmental category, Same as RM17TE00 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM17TE00 ¦ ,Supply,Rated Same as RM17TE00 ¦ ,Input 1,Voltage Same as RM17TE00 ¦ ,Input 2,Spec Same as RM17TE00 ¦ ,Input 3, Same as RM17TE00 ¦ ,Output 1, Same as RM17TE00 ¦ ,Output 2, Same as RM17TE00 ¦ ,Measurement mode, Same as RM17TE00 Same as RM17TE00 Same as RM17TE00 Same as RM17TE00 Same as RM17TE00 ¦ ,MTTFd, Same as RM17TE00 ¦ ,B10d, Drawing / Diagram
RM10TE00IP degree of protection | Same as RM17TE00 ¦ IEC60529,Terminal Block, Same as RM17TE00 ¦ IEC60529,Housing, Same as RM17TE00 ¦ IEC60529,Front Panel,
RM10TE00Input nominal voltage selection | Same as RM17TE00 ¦ ,Input nominal voltage selection,
RM10TE00Minimum distance to adjacent devices | Same as RM17TE00 ¦ ,Horizontal, Same as RM17TE00 ¦ ,Vertical,
RM10TE00[Ie] rated operational current | Same as RM17TE00 ¦ IEC61810-1,Rated switching current,
RM10TE00[Ue] rated operational voltage | Same as RM17TE00 ¦ IEC61810-1,Rated switching voltage,
RM10TE00[Ui] rated insulation voltage | Same as RM17TE00 ¦ IEC60664-1,Supply, Same as RM17TE00 ¦ IEC60664-1,Input 1, Same as RM17TE00 ¦ IEC60664-1,Input 2, Same as RM17TE00 ¦ IEC60664-1,Input 3, Same as RM17TE00 ¦ IEC60664-1,Output 1, Same as RM17TE00 ¦ IEC60664-1,Output 2, Same as RM17TE00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TE00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TE00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TE00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TE00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TE00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TE00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TE00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TE00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TE00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TE00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TE00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TE00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TE00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TE00 ¦ IEC60664-1,Input 1 / Input 3,
RM10TE00[Uimp] rated impulse withstand voltage | Same as RM17TE00 ¦ IEC60664-1,Supply, Same as RM17TE00 ¦ IEC60664-1,Input 1, Same as RM17TE00 ¦ IEC60664-1,Input 2, Same as RM17TE00 ¦ IEC60664-1,Input 3, Same as RM17TE00 ¦ IEC60664-1,Output 1, Same as RM17TE00 ¦ IEC60664-1,Output 2, Same as RM17TE00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TE00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TE00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TE00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TE00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TE00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TE00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TE00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TE00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TE00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TE00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TE00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TE00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TE00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TE00 ¦ IEC60664-1,Input 1 / Input 3,
RM10TE00[Us] rated supply voltage | Same as RM17TE00
RM10TE00ambient air temperature for operation | Same as RM17TE00 ¦ ,Operation,
RM10TE00ambient air temperature for storage | Same as RM17TE00 ¦ ,Storage,
RM10TE00bump resistance | Same as RM17TE00 ¦ IEC60068-2-29
RM10TE00cable stripping length | Same as RM17TE00 ¦ ,Cable stripping length,
RM10TE00circuit group | Same as RM17TE00 ¦ ,Supply,Terminal Same as RM17TE00 ¦ ,Input 1, Same as RM17TE00 ¦ ,Input 2, Same as RM17TE00 ¦ ,Input 3, Same as RM17TE00 ¦ ,Output 1, Same as RM17TE00 ¦ ,Output 2,
RM10TE00connections - terminals | Same as RM17TE00 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17TE00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17TE00 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17TE00 ¦ IEC60947-1,Flexible cable (spring terminal),
RM10TE00contacts material | Same as RM17TE00
RM10TE00depth | Same as RM17TE00 ¦ ,Depth,
RM10TE00diagnostic button | Same as RM17TE00
RM10TE00dielectric strength | Same as RM17TE00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TE00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TE00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TE00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TE00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TE00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TE00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TE00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TE00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TE00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TE00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TE00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TE00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TE00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TE00 ¦ IEC60255-27,Input 1 / Input 3,
RM10TE00directives | Same as RM17TE00 Same as RM17TE00 Same as RM17TE00
RM10TE00duty time | Same as RM17TE00
RM10TE00electrical durability | Same as RM17TE00 ¦ IEC60947-4-1,AC-1, Same as RM17TE00 ¦ IEC60947-4-1,DC-1, Same as RM17TE00 ¦ IEC60947-5-1,AC-15, Same as RM17TE00 ¦ IEC60947-5-1,DC-13,
RM10TE00electromagnetic compatibility | Same as RM17TE00 ¦ ,Generic immunity standard, Same as RM17TE00 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17TE00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17TE00 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17TE00 ¦ IEC61000-4-5,Surge, Same as RM17TE00 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17TE00 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17TE00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17TE00 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17TE00 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17TE00 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM17TE00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17TE00 ¦ ,Generic emission standard, Same as RM17TE00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17TE00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17TE00 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17TE00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17TE00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17TE00 ¦ Germanisher Lloyd,Conducted emission,
RM10TE00height | Same as RM17TE00 ¦ ,Height,
RM10TE00hysteresis | Same as RM17TE00 ¦ ,Phase cut, Same as RM17TE00 ¦ ,Phase sequence, Same as RM17TE00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TE00 ¦ ,Over voltage, Same as RM17TE00 ¦ ,Undervoltage , Same as RM17TE00 ¦ ,Phase asymmetry, Same as RM17TE00 ¦ ,Disconnection of neutral, Same as RM17TE00 ¦ ,Voltage Regeneration, Same as RM17TE00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TE00 ¦ ,Extreme Overvoltage, Same as RM17TE00 ¦ ,Extreme Asymmetry,
RM10TE00immunity to microbreaks | Same as RM17TE00
RM10TE00input frequency | Same as RM17TE00 ¦ ,Rated frequency, Same as RM17TE00 ¦ ,Frequency operating range,
RM10TE00input terminal | Same as RM17TE00 ¦ ,Input terminal,
RM10TE00insulation resistance | Same as RM17TE00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TE00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TE00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TE00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TE00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TE00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TE00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TE00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TE00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TE00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TE00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TE00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TE00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TE00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TE00 ¦ IEC60255-27,Input 1 / Input 3,
RM10TE00internal input resistance | Same as RM17TE00 ¦ ,Internal input resistance,
RM10TE00local signalling | Same as RM17TE00 ¦ ,Power supply availability, Same as RM17TE00 ¦ ,Power supply not availability, Same as RM17TE00 ¦ ,Timing in-progress, Same as RM17TE00 ¦ ,Output is energized, Same as RM17TE00 ¦ ,Output is de-energized, Same as RM17TE00 ¦ ,Range Setting Changes, Same as RM17TE00 ¦ ,Phase Cut, Same as RM17TE00 ¦ ,Phase Sequence Swap, Same as RM17TE00 ¦ ,Undervoltage <U, Same as RM17TE00 ¦ ,Overvoltage >U, Same as RM17TE00 ¦ ,Phase Asymmetry, Same as RM17TE00 ¦ ,Voltage Regeneration, Same as RM17TE00 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17TE00 ¦ ,Extreme Overvoltage >U, Same as RM17TE00 ¦ ,Extreme Phase Asymmetry,
RM10TE00marking | CCC, CE, China ROHS
RM10TE00maximum leakage current | Same as RM17TE00 ¦ IEC62314,Only for solid state output,
RM10TE00maximum measuring cycle | Same as RM17TE00 ¦ ,Maximum measuring cycles,
RM10TE00maximum switching capacity | Same as RM17TE00 ¦ ,Maximum switching voltage, Same as RM17TE00 ¦ ,Maximum switching current, Same as RM17TE00 ¦ ,Maximum switching capacity,
RM10TE00maximum voltage drop | Same as RM17TE00 ¦ IEC62314,Only for solid state output,
RM10TE00measurement method | Same as RM17TE00 ¦ ,Measurement method,
RM10TE00measurement range | Same as RM17TE00 ¦ ,Phase lost , Same as RM17TE00 ¦ ,Phase sequence, Same as RM17TE00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TE00 ¦ ,Over voltage, Same as RM17TE00 ¦ ,Undervoltage , Same as RM17TE00 ¦ ,Phase asymmetry, Same as RM17TE00 ¦ ,Disconnection of neutral, Same as RM17TE00 ¦ ,Voltage Regeneration, Same as RM17TE00 ¦ ,Extreme undervoltage, Same as RM17TE00 ¦ ,Extreme Overvoltage, Same as RM17TE00 ¦ ,Extreme Asymmetry,
RM10TE00mechanical durability | Same as RM17TE00 ¦ IEC61810-1
RM10TE00minimum switching capacity | Same as RM17TE00 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17TE00 ¦ IEC60947-5-4,Minimum switching current, Same as RM17TE00 ¦ IEC60947-5-4,Minimum switching capacity,
RM10TE00monitoring functions | Same as RM17TE00 ¦ ,Phase lost , Same as RM17TE00 ¦ ,Phase sequence, Same as RM17TE00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TE00 ¦ ,Over voltage, Same as RM17TE00 ¦ ,Undervoltage , Same as RM17TE00 ¦ ,Phase asymmetry, Same as RM17TE00 ¦ ,Disconnection of neutral, Same as RM17TE00 ¦ ,Voltage Regeneration, Same as RM17TE00 ¦ ,Extreme undervoltage, Same as RM17TE00 ¦ ,Extreme overvoltage, Same as RM17TE00 ¦ ,Extreme asymmetry,
RM10TE00mounting position | Same as RM17TE00 ¦ ,In relation to normal vertical mounting plane,
RM10TE00mounting support | Same as RM17TE00 ¦ IEC/EN 60715,Without socket, Same as RM17TE00 ¦ IEC/EN 60715,With socket,
RM10TE00net weight | Same as RM17TE00
RM10TE00on-load factor | Same as RM17TE00
RM10TE00output logic | Same as RM17TE00 ¦ ,R1 (11-12-14), Same as RM17TE00 ¦ ,R2 (21-22-24),
RM10TE00output terminal | Same as RM17TE00
RM10TE00output type | Same as RM17TE00
RM10TE00overvoltage category | Same as RM17TE00 ¦ IEC60664-1
RM10TE00permissible input overload | Same as RM17TE00 ¦ ,permissible input overload,
RM10TE00polarity | Same as RM17TE00
RM10TE00pollution degree | Same as RM17TE00 ¦ IEC60664-1
RM10TE00power consumption | Same as RM17TE00
RM10TE00power on delay | Same as RM17TE00
RM10TE00product certifications | CCC, CE, China ROHS
RM10TE00relative humidity | Same as RM17TE00 ¦ IEC60068-2-30,Damp heat,XX
RM10TE00release of input voltage | Same as RM17TE00
RM10TE00repeat accuracy of the switching threshold | Same as RM17TE00 ¦ ,Repeat accuracy (constant parameters),
RM10TE00repeat accuracy of time delay | Same as RM17TE00
RM10TE00reset time | Same as RM17TE00 ¦ ,through Un power reset, Same as RM17TE00 ¦ ,through front panel reset, Same as RM17TE00 ¦ ,through input control reset,
RM10TE00response time | Same as RM17TE00 ¦ ,on crossing the threshold, Same as RM17TE00 Same as RM17TE00 Same as RM17TE00 Same as RM17TE00
RM10TE00safety reliability data | Same as RM17TE00 ¦ ,MTTF, Same as RM17TE00 ¦ ,B10,
RM10TE00seismic resistance | Same as RM17TE00 ¦ IEC60068-3-3
RM10TE00setting accuracy of the switching threshold | Same as RM17TE00 ¦ ,Setting accuracy,
RM10TE00setting accuracy of time delay | Same as RM17TE00
RM10TE00shock resistance | Same as RM17TE00 ¦ IEC60068-2-27
RM10TE00short circuit protection | Same as RM17TE00 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17TE00 ¦ IEC62314,Solid State Output by external fuse,
RM10TE00standards | Same as RM17TE00
RM10TE00status LED | Same as RM17TE00
RM10TE00supply frequency | Same as RM17TE00 Same as RM17TE00
RM10TE00supply terminal | Same as RM17TE00
RM10TE00supply voltage limits | Same as RM17TE00
RM10TE00switching threshold drift | Same as RM17TE00 ¦ ,Measurement error with supply voltage variation, Same as RM17TE00 ¦ ,Measurement error with temperature variation,
RM10TE00thermal current | Same as RM17TE00 ¦ IEC60947-5-1
RM10TE00tightening torque | Same as RM17TE00 ¦ IEC60947-1,Tightening torque,
RM10TE00time delay drift | Same as RM17TE00 Same as RM17TE00
RM10TE00time delay range | Same as RM17TE00 ¦ ,"OFF" delay, Same as RM17TE00 ¦ ,"ON" delay, Same as RM17TE00 ¦ ,Inhibition,
RM10TE00time delay type | Same as RM17TE00 ¦ ,"OFF" delay, Same as RM17TE00 ¦ ,"ON" delay, Same as RM17TE00 ¦ ,Inhibition,
RM10TE00tripping threshold | Same as RM17TE00 ¦ ,Phase cut, Same as RM17TE00 ¦ ,Phase sequence, Same as RM17TE00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TE00 ¦ ,Over voltage, Same as RM17TE00 ¦ ,Undervoltage , Same as RM17TE00 ¦ ,Phase asymmetry, Same as RM17TE00 ¦ ,Disconnection of neutral, Same as RM17TE00 ¦ ,Voltage Regeneration, Same as RM17TE00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TE00 ¦ ,Extreme Overvoltage, Same as RM17TE00 ¦ ,Extreme Asymmetry,
RM10TE00vibration resistance | Same as RM17TE00 ¦ IEC60068-2-6
RM10TE00width | Same as RM17TE00 ¦ ,Width,
RM10TG00 | Same as RM17TG00 ¦ IEC60721-3-3,Climatic category, Same as RM17TG00 ¦ Germanisher Lloyd,Environmental category, Same as RM17TG00 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM17TG00 ¦ ,Supply,Rated Same as RM17TG00 ¦ ,Input 1,Voltage Same as RM17TG00 ¦ ,Input 2,Spec Same as RM17TG00 ¦ ,Input 3, Same as RM17TG00 ¦ ,Output 1, Same as RM17TG00 ¦ ,Output 2, Same as RM17TG00 ¦ ,Measurement mode, Same as RM17TG00 Same as RM17TG00 Same as RM17TG00 Same as RM17TG00 Same as RM17TG00 ¦ ,MTTFd, Same as RM17TG00 ¦ ,B10d, Drawing / Diagram
RM10TG00IP degree of protection | Same as RM17TG00 ¦ IEC60529,Terminal Block, Same as RM17TG00 ¦ IEC60529,Housing, Same as RM17TG00 ¦ IEC60529,Front Panel,
RM10TG00Input nominal voltage selection | Same as RM17TG00 ¦ ,Input nominal voltage selection,
RM10TG00Minimum distance to adjacent devices | Same as RM17TG00 ¦ ,Horizontal, Same as RM17TG00 ¦ ,Vertical,
RM10TG00[Ie] rated operational current | Same as RM17TG00 ¦ IEC61810-1,Rated switching current,
RM10TG00[Ue] rated operational voltage | Same as RM17TG00 ¦ IEC61810-1,Rated switching voltage,
RM10TG00[Ui] rated insulation voltage | Same as RM17TG00 ¦ IEC60664-1,Supply, Same as RM17TG00 ¦ IEC60664-1,Input 1, Same as RM17TG00 ¦ IEC60664-1,Input 2, Same as RM17TG00 ¦ IEC60664-1,Input 3, Same as RM17TG00 ¦ IEC60664-1,Output 1, Same as RM17TG00 ¦ IEC60664-1,Output 2, Same as RM17TG00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TG00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TG00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TG00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TG00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TG00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 3,
RM10TG00[Uimp] rated impulse withstand voltage | Same as RM17TG00 ¦ IEC60664-1,Supply, Same as RM17TG00 ¦ IEC60664-1,Input 1, Same as RM17TG00 ¦ IEC60664-1,Input 2, Same as RM17TG00 ¦ IEC60664-1,Input 3, Same as RM17TG00 ¦ IEC60664-1,Output 1, Same as RM17TG00 ¦ IEC60664-1,Output 2, Same as RM17TG00 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TG00 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TG00 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM17TG00 ¦ IEC60664-1,Supply / Output 1, Same as RM17TG00 ¦ IEC60664-1,Supply / Output 2, Same as RM17TG00 ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TG00 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TG00 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TG00 ¦ IEC60664-1,Input 1 / Input 3,
RM10TG00[Us] rated supply voltage | Same as RM17TG00
RM10TG00ambient air temperature for operation | Same as RM17TG00 ¦ ,Operation,
RM10TG00ambient air temperature for storage | Same as RM17TG00 ¦ ,Storage,
RM10TG00bump resistance | Same as RM17TG00 ¦ IEC60068-2-29
RM10TG00cable stripping length | Same as RM17TG00 ¦ ,Cable stripping length,
RM10TG00circuit group | Same as RM17TG00 ¦ ,Supply,Terminal Same as RM17TG00 ¦ ,Input 1, Same as RM17TG00 ¦ ,Input 2, Same as RM17TG00 ¦ ,Input 3, Same as RM17TG00 ¦ ,Output 1, Same as RM17TG00 ¦ ,Output 2,
RM10TG00connections - terminals | Same as RM17TG00 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17TG00 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17TG00 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17TG00 ¦ IEC60947-1,Flexible cable (spring terminal),
RM10TG00contacts material | Same as RM17TG00
RM10TG00depth | Same as RM17TG00 ¦ ,Depth,
RM10TG00diagnostic button | Same as RM17TG00
RM10TG00dielectric strength | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TG00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TG00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TG00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TG00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TG00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 3,
RM10TG00directives | Same as RM17TG00 Same as RM17TG00 Same as RM17TG00
RM10TG00duty time | Same as RM17TG00
RM10TG00electrical durability | Same as RM17TG00 ¦ IEC60947-4-1,AC-1, Same as RM17TG00 ¦ IEC60947-4-1,DC-1, Same as RM17TG00 ¦ IEC60947-5-1,AC-15, Same as RM17TG00 ¦ IEC60947-5-1,DC-13,
RM10TG00electromagnetic compatibility | Same as RM17TG00 ¦ ,Generic immunity standard, Same as RM17TG00 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17TG00 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17TG00 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17TG00 ¦ IEC61000-4-5,Surge, Same as RM17TG00 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17TG00 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17TG00 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17TG00 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17TG00 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17TG00 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM17TG00 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17TG00 ¦ ,Generic emission standard, Same as RM17TG00 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17TG00 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17TG00 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17TG00 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17TG00 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17TG00 ¦ Germanisher Lloyd,Conducted emission,
RM10TG00height | Same as RM17TG00 ¦ ,Height,
RM10TG00hysteresis | Same as RM17TG00 ¦ ,Phase cut, Same as RM17TG00 ¦ ,Phase sequence, Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG00 ¦ ,Over voltage, Same as RM17TG00 ¦ ,Undervoltage , Same as RM17TG00 ¦ ,Phase asymmetry, Same as RM17TG00 ¦ ,Disconnection of neutral, Same as RM17TG00 ¦ ,Voltage Regeneration, Same as RM17TG00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TG00 ¦ ,Extreme Overvoltage, Same as RM17TG00 ¦ ,Extreme Asymmetry,
RM10TG00immunity to microbreaks | Same as RM17TG00
RM10TG00input frequency | Same as RM17TG00 ¦ ,Rated frequency, Same as RM17TG00 ¦ ,Frequency operating range,
RM10TG00input terminal | Same as RM17TG00 ¦ ,Input terminal,
RM10TG00insulation resistance | Same as RM17TG00 ¦ IEC60255-27,Supply / Input 1, Same as RM17TG00 ¦ IEC60255-27,Supply / Input 2, Same as RM17TG00 ¦ IEC60255-27,Supply / Input 3, Same as RM17TG00 ¦ IEC60255-27,Supply / Output 1, Same as RM17TG00 ¦ IEC60255-27,Supply / Output 2, Same as RM17TG00 ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TG00 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TG00 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TG00 ¦ IEC60255-27,Input 1 / Input 3,
RM10TG00internal input resistance | Same as RM17TG00 ¦ ,Internal input resistance,
RM10TG00local signalling | Same as RM17TG00 ¦ ,Power supply availability, Same as RM17TG00 ¦ ,Power supply not availability, Same as RM17TG00 ¦ ,Timing in-progress, Same as RM17TG00 ¦ ,Output is energized, Same as RM17TG00 ¦ ,Output is de-energized, Same as RM17TG00 ¦ ,Range Setting Changes, Same as RM17TG00 ¦ ,Phase Cut, Same as RM17TG00 ¦ ,Phase Sequence Swap, Same as RM17TG00 ¦ ,Undervoltage <U, Same as RM17TG00 ¦ ,Overvoltage >U, Same as RM17TG00 ¦ ,Phase Asymmetry, Same as RM17TG00 ¦ ,Voltage Regeneration, Same as RM17TG00 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17TG00 ¦ ,Extreme Overvoltage >U, Same as RM17TG00 ¦ ,Extreme Phase Asymmetry,
RM10TG00marking | CCC, CE, China ROHS
RM10TG00maximum leakage current | Same as RM17TG00 ¦ IEC62314,Only for solid state output,
RM10TG00maximum measuring cycle | Same as RM17TG00 ¦ ,Maximum measuring cycles,
RM10TG00maximum switching capacity | Same as RM17TG00 ¦ ,Maximum switching voltage, Same as RM17TG00 ¦ ,Maximum switching current, Same as RM17TG00 ¦ ,Maximum switching capacity,
RM10TG00maximum voltage drop | Same as RM17TG00 ¦ IEC62314,Only for solid state output,
RM10TG00measurement method | Same as RM17TG00 ¦ ,Measurement method,
RM10TG00measurement range | Same as RM17TG00 ¦ ,Phase lost , Same as RM17TG00 ¦ ,Phase sequence, Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG00 ¦ ,Over voltage, Same as RM17TG00 ¦ ,Undervoltage , Same as RM17TG00 ¦ ,Phase asymmetry, Same as RM17TG00 ¦ ,Disconnection of neutral, Same as RM17TG00 ¦ ,Voltage Regeneration, Same as RM17TG00 ¦ ,Extreme undervoltage, Same as RM17TG00 ¦ ,Extreme Overvoltage, Same as RM17TG00 ¦ ,Extreme Asymmetry,
RM10TG00mechanical durability | Same as RM17TG00 ¦ IEC61810-1
RM10TG00minimum switching capacity | Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching current, Same as RM17TG00 ¦ IEC60947-5-4,Minimum switching capacity,
RM10TG00monitoring functions | Same as RM17TG00 ¦ ,Phase lost , Same as RM17TG00 ¦ ,Phase sequence, Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG00 ¦ ,Over voltage, Same as RM17TG00 ¦ ,Undervoltage , Same as RM17TG00 ¦ ,Phase asymmetry, Same as RM17TG00 ¦ ,Disconnection of neutral, Same as RM17TG00 ¦ ,Voltage Regeneration, Same as RM17TG00 ¦ ,Extreme undervoltage, Same as RM17TG00 ¦ ,Extreme overvoltage, Same as RM17TG00 ¦ ,Extreme asymmetry,
RM10TG00mounting position | Same as RM17TG00 ¦ ,In relation to normal vertical mounting plane,
RM10TG00mounting support | Same as RM17TG00 ¦ IEC/EN 60715,Without socket, Same as RM17TG00 ¦ IEC/EN 60715,With socket,
RM10TG00net weight | Same as RM17TG00
RM10TG00on-load factor | Same as RM17TG00
RM10TG00output logic | Same as RM17TG00 ¦ ,R1 (11-12-14), Same as RM17TG00 ¦ ,R2 (21-22-24),
RM10TG00output terminal | Same as RM17TG00
RM10TG00output type | Same as RM17TG00
RM10TG00overvoltage category | Same as RM17TG00 ¦ IEC60664-1
RM10TG00permissible input overload | Same as RM17TG00 ¦ ,permissible input overload,
RM10TG00polarity | Same as RM17TG00
RM10TG00pollution degree | Same as RM17TG00 ¦ IEC60664-1
RM10TG00power consumption | Same as RM17TG00
RM10TG00power on delay | Same as RM17TG00
RM10TG00product certifications | CCC, CE, China ROHS
RM10TG00relative humidity | Same as RM17TG00 ¦ IEC60068-2-30,Damp heat,XX
RM10TG00release of input voltage | Same as RM17TG00
RM10TG00repeat accuracy of the switching threshold | Same as RM17TG00 ¦ ,Repeat accuracy (constant parameters),
RM10TG00repeat accuracy of time delay | Same as RM17TG00
RM10TG00reset time | Same as RM17TG00 ¦ ,through Un power reset, Same as RM17TG00 ¦ ,through front panel reset, Same as RM17TG00 ¦ ,through input control reset,
RM10TG00response time | Same as RM17TG00 ¦ ,on crossing the threshold, Same as RM17TG00 Same as RM17TG00 Same as RM17TG00 Same as RM17TG00
RM10TG00safety reliability data | Same as RM17TG00 ¦ ,MTTF, Same as RM17TG00 ¦ ,B10,
RM10TG00seismic resistance | Same as RM17TG00 ¦ IEC60068-3-3
RM10TG00setting accuracy of the switching threshold | Same as RM17TG00 ¦ ,Setting accuracy,
RM10TG00setting accuracy of time delay | Same as RM17TG00
RM10TG00shock resistance | Same as RM17TG00 ¦ IEC60068-2-27
RM10TG00short circuit protection | Same as RM17TG00 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17TG00 ¦ IEC62314,Solid State Output by external fuse,
RM10TG00standards | Same as RM17TG00
RM10TG00status LED | Same as RM17TG00
RM10TG00supply frequency | Same as RM17TG00 Same as RM17TG00
RM10TG00supply terminal | Same as RM17TG00
RM10TG00supply voltage limits | Same as RM17TG00
RM10TG00switching threshold drift | Same as RM17TG00 ¦ ,Measurement error with supply voltage variation, Same as RM17TG00 ¦ ,Measurement error with temperature variation,
RM10TG00thermal current | Same as RM17TG00 ¦ IEC60947-5-1
RM10TG00tightening torque | Same as RM17TG00 ¦ IEC60947-1,Tightening torque,
RM10TG00time delay drift | Same as RM17TG00 Same as RM17TG00
RM10TG00time delay range | Same as RM17TG00 ¦ ,"OFF" delay, Same as RM17TG00 ¦ ,"ON" delay, Same as RM17TG00 ¦ ,Inhibition,
RM10TG00time delay type | Same as RM17TG00 ¦ ,"OFF" delay, Same as RM17TG00 ¦ ,"ON" delay, Same as RM17TG00 ¦ ,Inhibition,
RM10TG00tripping threshold | Same as RM17TG00 ¦ ,Phase cut, Same as RM17TG00 ¦ ,Phase sequence, Same as RM17TG00 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG00 ¦ ,Over voltage, Same as RM17TG00 ¦ ,Undervoltage , Same as RM17TG00 ¦ ,Phase asymmetry, Same as RM17TG00 ¦ ,Disconnection of neutral, Same as RM17TG00 ¦ ,Voltage Regeneration, Same as RM17TG00 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TG00 ¦ ,Extreme Overvoltage, Same as RM17TG00 ¦ ,Extreme Asymmetry,
RM10TG00vibration resistance | Same as RM17TG00 ¦ IEC60068-2-6
RM10TG00width | Same as RM17TG00 ¦ ,Width,
RM17JC00MW | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, 600 ¦ ,Supply,Rated 600 ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, - ¦ ,Over / undercurrent (windows mode), · ¦ ,Over current, - ¦ ,Under current, ~ 2000…20000 - ¦ ,E1-M / B1-C, - ¦ ,E2-M / B2-C, - ¦ ,E3-M / B3-C, A1+ / A2-, · ¦ ,Built in current transformer, - ¦ ,E1-M / B1-C, - ¦ ,E2-M / B2-C, - ¦ ,E3-M / B3-C, A1+ / A2-, ~ 2000…20000 ¦ ,Built in current transformer, - ¦ ,E1-M / B1-C, - ¦ ,E2-M / B2-C, - ¦ ,E3-M / B3-C, A1+ / A2-, Adjustable 10%...100% of 20000 ¦ ,Built in current transformer, - ¦ ,E1-M / B1-C, - ¦ ,E2-M / B2-C, - ¦ ,E3-M / B3-C, A1+ / A2-, Fixed 15% of threshold setting ¦ ,Built in current transformer, Current transformer Turning conductor around current transformer 50 / 60 40…70 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 True RMS MTTFd, B10d,
RM17JC00MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IEC60529,Front Panel,
RM17JC00MWMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM17JC00MW[Ie] rated operational current | IEC61810-1,Rated switching current,
RM17JC00MW[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM17JC00MW[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, 4 ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM17JC00MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM17JC00MW[Us] rated supply voltage | ~/-- 24…240
RM17JC00MWambient air temperature for operation | -20…+50 ¦ ,Operation,
RM17JC00MWambient air temperature for storage | -40…+70 ¦ ,Storage,
RM17JC00MWbump resistance | IEC60068-2-29
RM17JC00MWcable stripping length | Not specified ¦ ,Cable stripping length,
RM17JC00MWcircuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, 600 ¦ ,Output 2,
RM17JC00MWconnections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM17JC00MWcontacts material | Cadmium free
RM17JC00MWdepth | Depth,
RM17JC00MWdiagnostic button
RM17JC00MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM17JC00MWdirectives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
RM17JC00MWduty time | Not specified
RM17JC00MWelectrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM17JC00MWelectromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM17JC00MWheight | Height,
RM17JC00MWimmunity to microbreaks | 10
RM17JC00MWinsulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM17JC00MWlocal signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM17JC00MWmarking | UL, CSA, GL, C-Tick, GOST, CE, CCC
RM17JC00MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM17JC00MWmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 8 ¦ ,Maximum switching current, 2000 ¦ ,Maximum switching capacity,
RM17JC00MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM17JC00MWmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM17JC00MWminimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM17JC00MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM17JC00MWmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM17JC00MWnet weight | 110
RM17JC00MWon-load factor
RM17JC00MWoutput logic | Selectable energized/de-energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
RM17JC00MWoutput terminal | 11-12-14
RM17JC00MWoutput type | 1 x C/O relay contacts
RM17JC00MWovervoltage category | III ¦ IEC60664-1
RM17JC00MWpolarity
RM17JC00MWpollution degree | 3 ¦ IEC60664-1
RM17JC00MWpower consumption | ~ 3VA, -- 1W
RM17JC00MWpower on delay | 0
RM17JC00MWproduct certifications | UL, CSA, GL, C-Tick, GOST, CCC
RM17JC00MWrelative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM17JC00MWrelease of input voltage
RM17JC00MWrepeat accuracy of time delay | -
RM17JC00MWreset time | - ¦ ,through Un power reset, through front panel reset, through input control reset,
RM17JC00MWresponse time | 0
RM17JC00MWsafety reliability data | MTTF, B10,
RM17JC00MWseismic resistance | IEC60068-3-3
RM17JC00MWsetting accuracy of time delay | -
RM17JC00MWshock resistance | 5 gn ¦ IEC60068-2-27
RM17JC00MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM17JC00MWstandards | EN60255-6, IEC60255-6
RM17JC00MWstatus LED
RM17JC00MWsupply frequency | 50 / 60 45…66
RM17JC00MWsupply terminal | A1-A2
RM17JC00MWsupply voltage limits | ~/-- 20.4…264
RM17JC00MWthermal current | IEC60947-5-1
RM17JC00MWtightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM17JC00MWtime delay drift | - -
RM17JC00MWtime delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM17JC00MWtime delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM17JC00MWvibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM17JC00MWwidth | 17.5 x 90 x 72 ¦ ,Width,
RM17TA00 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 208..480 AC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, - ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, Yes - - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d, Drawing / Diagram
RM17TA00IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, - ¦ IEC60529,Front Panel,
RM17TA00Input nominal voltage selection | 208, 220, 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM17TA00Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM17TA00[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM17TA00[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM17TA00[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, - ¦ IEC60664-1,Supply / Output 2, - ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM17TA00[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, - ¦ IEC60664-1,Supply / Output 2, - ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM17TA00[Us] rated supply voltage | ~ 3 x 208…3 x 480
RM17TA00ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM17TA00ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM17TA00bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM17TA00cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM17TA00circuit group | L1, L2, L3 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, - ¦ ,Output 2,
RM17TA00connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM17TA00contacts material | Cadmium free
RM17TA00depth | 72 ¦ ,Depth,
RM17TA00diagnostic button | -
RM17TA00dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, - ¦ IEC60255-27,Supply / Output 2, - ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM17TA00directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM17TA00duty time | 1
RM17TA00electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM17TA00electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM17TA00height | 90 ¦ ,Height,
RM17TA00hysteresis | All phase cut recover ¦ ,Phase cut, Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, All phases >195V Internal design spec: All phases >180V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: All phases <533V +/- 5% ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM17TA00immunity to microbreaks | 0
RM17TA00input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
RM17TA00input terminal | L1-L2-L3 ¦ ,Input terminal,
RM17TA00insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, - ¦ IEC60255-27,Supply / Output 2, - ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM17TA00internal input resistance | - ¦ ,Internal input resistance,
RM17TA00local signalling | Un - ON ¦ ,Power supply availability, Un - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes, - ¦ ,Phase Cut, - ¦ ,Phase Sequence Swap, - ¦ ,Undervoltage <U, - ¦ ,Overvoltage >U, - ¦ ,Phase Asymmetry, - ¦ ,Voltage Regeneration, - ¦ ,Extreme Undervoltage <U (Phase loss), - ¦ ,Extreme Overvoltage >U, - ¦ ,Extreme Phase Asymmetry,
RM17TA00marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TA00maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM17TA00maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM17TA00maximum switching capacity | 250V ¦ ,Maximum switching voltage, 5A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM17TA00maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM17TA00measurement method | True RMS ¦ ,Measurement method,
RM17TA00measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , +5…+15 % in the ranges 3 x ~ 208…480 ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, - ¦ ,Extreme undervoltage, - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM17TA00mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM17TA00minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM17TA00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost , governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , governed by time delay, status reflects to both R1 & R2 ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM17TA00mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM17TA00mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM17TA00net weight | 80
RM17TA00on-load factor | 1
RM17TA00output logic | Energized on fault-free ¦ ,R1 (11-12-14), - ¦ ,R2 (21-22-24),
RM17TA00output terminal | 11-12-14
RM17TA00output type | 1 x C/O relay contacts
RM17TA00overvoltage category | 3 ¦ IEC60664-1
RM17TA00permissible input overload | - ¦ ,permissible input overload,
RM17TA00polarity | -
RM17TA00pollution degree | 3 ¦ IEC60664-1
RM17TA00power consumption | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz
RM17TA00power on delay | 0
RM17TA00product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TA00relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM17TA00release of input voltage | -
RM17TA00repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM17TA00repeat accuracy of time delay | +/- 3%
RM17TA00reset time | 0
RM17TA00response time | 0
RM17TA00safety reliability data | 4,400,000 hours ¦ ,MTTF, 470,000 hours ¦ ,B10,
RM17TA00seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM17TA00setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM17TA00setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM17TA00shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM17TA00short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM17TA00standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM17TA00status LED | Un (Green) R (Amber)
RM17TA00supply frequency | 50 / 60 45…66
RM17TA00supply terminal | L1-L3
RM17TA00supply voltage limits | ~ 3 x 183…3 x 528
RM17TA00switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation, < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM17TA00thermal current | 5A ¦ IEC60947-5-1
RM17TA00tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM17TA00time delay drift | - -
RM17TA00time delay range | Adjustable 0.1…10 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM17TA00time delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM17TA00tripping threshold | 1 or more phase cut ¦ ,Phase cut, Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , Adjustable 5%...15% of selected Un ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: 543V +/- 5% ¦ ,Extreme Overvoltage, Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM17TA00vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM17TA00width | 17.5 ¦ ,Width,
RM17TE00 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 208..480 AC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, - ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, Yes - - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d, Drawing / Diagram
RM17TE00IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, - ¦ IEC60529,Front Panel,
RM17TE00Input nominal voltage selection | 208, 220, 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM17TE00Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM17TE00[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM17TE00[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM17TE00[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, - ¦ IEC60664-1,Supply / Output 2, - ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM17TE00[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, - ¦ IEC60664-1,Supply / Output 2, - ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM17TE00[Us] rated supply voltage | ~ 3 x 208…3 x 480
RM17TE00ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM17TE00ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM17TE00bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM17TE00cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM17TE00circuit group | L1, L2, L3 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, - ¦ ,Output 2,
RM17TE00connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM17TE00contacts material | Cadmium free
RM17TE00depth | 72 ¦ ,Depth,
RM17TE00diagnostic button | -
RM17TE00dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, - ¦ IEC60255-27,Supply / Output 2, - ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM17TE00directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM17TE00duty time | 1
RM17TE00electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM17TE00electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM17TE00height | 90 ¦ ,Height,
RM17TE00hysteresis | All phase cut recover ¦ ,Phase cut, Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence, Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, All phases > 195V Internal design spec: All phases >180V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: All phases <533V +/- 5% ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM17TE00immunity to microbreaks | 0
RM17TE00input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
RM17TE00input terminal | L1-L2-L3 ¦ ,Input terminal,
RM17TE00insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, - ¦ IEC60255-27,Supply / Output 2, - ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM17TE00internal input resistance | - ¦ ,Internal input resistance,
RM17TE00local signalling | Un - ON ¦ ,Power supply availability, Un - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes, - ¦ ,Phase Cut, - ¦ ,Phase Sequence Swap, - ¦ ,Undervoltage <U, - ¦ ,Overvoltage >U, - ¦ ,Phase Asymmetry, - ¦ ,Voltage Regeneration, - ¦ ,Extreme Undervoltage <U (Phase loss), - ¦ ,Extreme Overvoltage >U, - ¦ ,Extreme Phase Asymmetry,
RM17TE00marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TE00maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM17TE00maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM17TE00maximum switching capacity | 250V ¦ ,Maximum switching voltage, 5A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM17TE00maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM17TE00measurement method | True RMS ¦ ,Measurement method,
RM17TE00measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, -2…-20 % in the ranges 3 x ~ 380…480 -2…-12 % in the range 3 x ~ 208 -2…-17 % in the range 3 x ~ 220 +2…+20 % in the ranges 3 x ~ 208…440 +2…+10 % in the range 3 x ~ 480 ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , +5…+15 % in the ranges 3 x ~ 208…480 ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, - ¦ ,Extreme undervoltage, - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM17TE00mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM17TE00minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM17TE00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost , governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence, governed by time delay, status reflects to both R1 & R2 ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , governed by time delay, status reflects to both R1 & R2 ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM17TE00mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM17TE00mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM17TE00net weight | 80
RM17TE00on-load factor | 1
RM17TE00output logic | Energized on fault-free ¦ ,R1 (11-12-14), - ¦ ,R2 (21-22-24),
RM17TE00output terminal | 11-12-14
RM17TE00output type | 1 x C/O relay contacts
RM17TE00overvoltage category | 3 ¦ IEC60664-1
RM17TE00permissible input overload | - ¦ ,permissible input overload,
RM17TE00polarity | -
RM17TE00pollution degree | 3 ¦ IEC60664-1
RM17TE00power consumption | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz
RM17TE00power on delay | 0
RM17TE00product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TE00relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM17TE00release of input voltage | -
RM17TE00repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM17TE00repeat accuracy of time delay | +/- 3%
RM17TE00reset time | 0
RM17TE00response time | 0
RM17TE00safety reliability data | 4,400,000 hours ¦ ,MTTF, 470,000 hours ¦ ,B10,
RM17TE00seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM17TE00setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM17TE00setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM17TE00shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM17TE00short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM17TE00standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM17TE00status LED | Un (Green) R (Amber)
RM17TE00supply frequency | 50 / 60 45…66
RM17TE00supply terminal | L1-L3
RM17TE00supply voltage limits | ~ 3 x 183…3 x 528
RM17TE00switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation, < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM17TE00thermal current | 5A ¦ IEC60947-5-1
RM17TE00tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM17TE00time delay drift | - -
RM17TE00time delay range | Adjustable 0.1…10 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM17TE00time delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM17TE00tripping threshold | 1 or more phase cut ¦ ,Phase cut, Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence, Adjustable 2%...20% of selected Un ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , Adjustable 5%...15% of selected Un ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: 543V +/- 5% ¦ ,Extreme Overvoltage, Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM17TE00vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM17TE00width | 17.5 ¦ ,Width,
RM17TG00 | Same as RM17TG20 ¦ IEC60721-3-3,Climatic category, Same as RM17TG20 ¦ Germanisher Lloyd,Environmental category, Same as RM17TG20 ¦ IEC60947-5-1,Cyclic Damp Heat Test, 208..480 AC ¦ ,Supply,Rated Same as RM17TG20 ¦ ,Input 1,Voltage Same as RM17TG20 ¦ ,Input 2,Spec Same as RM17TG20 ¦ ,Input 3, 250V ¦ ,Output 1, - ¦ ,Output 2, Same as RM17TG20 ¦ ,Measurement mode, Same as RM17TG20 Same as RM17TG20 Same as RM17TG20 Same as RM17TG20 Same as RM17TG20 ¦ ,MTTFd, Same as RM17TG20 ¦ ,B10d, Drawing / Diagram
RM17TG00IP degree of protection | Same as RM17TG20 ¦ IEC60529,Terminal Block, Same as RM17TG20 ¦ IEC60529,Housing, Same as RM17TG20 ¦ IEC60529,Front Panel,
RM17TG00Input nominal voltage selection | - ¦ ,Input nominal voltage selection,
RM17TG00Minimum distance to adjacent devices | Same as RM17TG20 ¦ ,Horizontal, Same as RM17TG20 ¦ ,Vertical,
RM17TG00[Ie] rated operational current | Same as RM17TG20 ¦ IEC61810-1,Rated switching current,
RM17TG00[Ue] rated operational voltage | Same as RM17TG20 ¦ IEC61810-1,Rated switching voltage,
RM17TG00[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, Same as RM17TG20 ¦ IEC60664-1,Input 1, Same as RM17TG20 ¦ IEC60664-1,Input 2, Same as RM17TG20 ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, Same as RM17TG20 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TG20 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TG20 ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, - ¦ IEC60664-1,Supply / Output 2, - ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 3,
RM17TG00[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, Same as RM17TG20 ¦ IEC60664-1,Input 1, Same as RM17TG20 ¦ IEC60664-1,Input 2, Same as RM17TG20 ¦ IEC60664-1,Input 3, Same as RM17TG20 ¦ IEC60664-1,Output 1, Same as RM17TG20 ¦ IEC60664-1,Output 2, Same as RM17TG20 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM17TG20 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM17TG20 ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, - ¦ IEC60664-1,Supply / Output 2, - ¦ IEC60664-1,Output 1 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 1, Same as RM17TG20 ¦ IEC60664-1,Input 3 / Output 2, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 2, Same as RM17TG20 ¦ IEC60664-1,Input 2 / Input 3, Same as RM17TG20 ¦ IEC60664-1,Input 1 / Input 3,
RM17TG00[Us] rated supply voltage | ~ 3 x 208…3 x 480
RM17TG00ambient air temperature for operation | Same as RM17TG20 ¦ ,Operation,
RM17TG00ambient air temperature for storage | Same as RM17TG20 ¦ ,Storage,
RM17TG00bump resistance | Same as RM17TG20 ¦ IEC60068-2-29
RM17TG00cable stripping length | Same as RM17TG20 ¦ ,Cable stripping length,
RM17TG00circuit group | Same as RM17TG20 ¦ ,Supply,Terminal Same as RM17TG20 ¦ ,Input 1, Same as RM17TG20 ¦ ,Input 2, Same as RM17TG20 ¦ ,Input 3, Same as RM17TG20 ¦ ,Output 1, Same as RM17TG20 ¦ ,Output 2,
RM17TG00connections - terminals | Same as RM17TG20 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM17TG20 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM17TG20 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM17TG20 ¦ IEC60947-1,Flexible cable (spring terminal),
RM17TG00contacts material | Same as RM17TG20
RM17TG00depth | Same as RM17TG20 ¦ ,Depth,
RM17TG00diagnostic button | Same as RM17TG20
RM17TG00dielectric strength | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 1, Same as RM17TG20 ¦ IEC60255-27,Supply / Input 2, Same as RM17TG20 ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, - ¦ IEC60255-27,Supply / Output 2, - ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 3,
RM17TG00directives | Same as RM17TG20 Same as RM17TG20 Same as RM17TG20
RM17TG00duty time | Same as RM17TG20
RM17TG00electrical durability | Same as RM17TG20 ¦ IEC60947-4-1,AC-1, Same as RM17TG20 ¦ IEC60947-4-1,DC-1, Same as RM17TG20 ¦ IEC60947-5-1,AC-15, Same as RM17TG20 ¦ IEC60947-5-1,DC-13,
RM17TG00electromagnetic compatibility | Same as RM17TG20 ¦ ,Generic immunity standard, Same as RM17TG20 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM17TG20 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM17TG20 ¦ IEC61000-4-4,Fast transient / burst, Same as RM17TG20 ¦ IEC61000-4-5,Surge, Same as RM17TG20 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM17TG20 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM17TG20 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM17TG20 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM17TG20 ¦ IEC61000-4-29,DC voltage interruption, Same as RM17TG20 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM17TG20 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM17TG20 ¦ ,Generic emission standard, Same as RM17TG20 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM17TG20 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM17TG20 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM17TG20 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM17TG20 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM17TG20 ¦ Germanisher Lloyd,Conducted emission,
RM17TG00height | Same as RM17TG20 ¦ ,Height,
RM17TG00hysteresis | Same as RM17TG20 ¦ ,Phase cut, Same as RM17TG20 ¦ ,Phase sequence, Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG20 ¦ ,Over voltage, Same as RM17TG20 ¦ ,Undervoltage , Same as RM17TG20 ¦ ,Phase asymmetry, Same as RM17TG20 ¦ ,Disconnection of neutral, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TG20 ¦ ,Extreme Overvoltage, Same as RM17TG20 ¦ ,Extreme Asymmetry,
RM17TG00immunity to microbreaks | Same as RM17TG20
RM17TG00input frequency | Same as RM17TG20 ¦ ,Rated frequency, Same as RM17TG20 ¦ ,Frequency operating range,
RM17TG00input terminal | Same as RM17TG20 ¦ ,Input terminal,
RM17TG00insulation resistance | Same as RM17TG20 ¦ IEC60255-27,Supply / Input 1, Same as RM17TG20 ¦ IEC60255-27,Supply / Input 2, Same as RM17TG20 ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, - ¦ IEC60255-27,Supply / Output 2, - ¦ IEC60255-27,Output 1 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 1, Same as RM17TG20 ¦ IEC60255-27,Input 3 / Output 2, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 2, Same as RM17TG20 ¦ IEC60255-27,Input 2 / Input 3, Same as RM17TG20 ¦ IEC60255-27,Input 1 / Input 3,
RM17TG00internal input resistance | - ¦ ,Internal input resistance,
RM17TG00local signalling | Same as RM17TG20 ¦ ,Power supply availability, Same as RM17TG20 ¦ ,Power supply not availability, Same as RM17TG20 ¦ ,Timing in-progress, Same as RM17TG20 ¦ ,Output is energized, Same as RM17TG20 ¦ ,Output is de-energized, Same as RM17TG20 ¦ ,Range Setting Changes, Same as RM17TG20 ¦ ,Phase Cut, Same as RM17TG20 ¦ ,Phase Sequence Swap, Same as RM17TG20 ¦ ,Undervoltage <U, Same as RM17TG20 ¦ ,Overvoltage >U, Same as RM17TG20 ¦ ,Phase Asymmetry, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM17TG20 ¦ ,Extreme Overvoltage >U, Same as RM17TG20 ¦ ,Extreme Phase Asymmetry,
RM17TG00marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TG00maximum leakage current | Same as RM17TG20 ¦ IEC62314,Only for solid state output,
RM17TG00maximum measuring cycle | Same as RM17TG20 ¦ ,Maximum measuring cycles,
RM17TG00maximum switching capacity | Same as RM17TG20 ¦ ,Maximum switching voltage, Same as RM17TG20 ¦ ,Maximum switching current, Same as RM17TG20 ¦ ,Maximum switching capacity,
RM17TG00maximum voltage drop | Same as RM17TG20 ¦ IEC62314,Only for solid state output,
RM17TG00measurement method | Same as RM17TG20 ¦ ,Measurement method,
RM17TG00measurement range | Same as RM17TG20 ¦ ,Phase lost , Same as RM17TG20 ¦ ,Phase sequence, Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG20 ¦ ,Over voltage, Same as RM17TG20 ¦ ,Undervoltage , Same as RM17TG20 ¦ ,Phase asymmetry, Same as RM17TG20 ¦ ,Disconnection of neutral, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme undervoltage, Same as RM17TG20 ¦ ,Extreme Overvoltage, Same as RM17TG20 ¦ ,Extreme Asymmetry,
RM17TG00mechanical durability | Same as RM17TG20 ¦ IEC61810-1
RM17TG00minimum switching capacity | Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching current, Same as RM17TG20 ¦ IEC60947-5-4,Minimum switching capacity,
RM17TG00monitoring functions | Same as RM17TG20 ¦ ,Phase lost , Same as RM17TG20 ¦ ,Phase sequence, Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG20 ¦ ,Over voltage, Same as RM17TG20 ¦ ,Undervoltage , Same as RM17TG20 ¦ ,Phase asymmetry, Same as RM17TG20 ¦ ,Disconnection of neutral, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme undervoltage, Same as RM17TG20 ¦ ,Extreme overvoltage, Same as RM17TG20 ¦ ,Extreme asymmetry,
RM17TG00mounting position | Same as RM17TG20 ¦ ,In relation to normal vertical mounting plane,
RM17TG00mounting support | Same as RM17TG20 ¦ IEC/EN 60715,Without socket, Same as RM17TG20 ¦ IEC/EN 60715,With socket,
RM17TG00net weight | Same as RM17TG20
RM17TG00on-load factor | Same as RM17TG20
RM17TG00output logic | Same as RM17TG20 ¦ ,R1 (11-12-14), Same as RM17TG20 ¦ ,R2 (21-22-24),
RM17TG00output terminal | Same as RM17TG20
RM17TG00output type | 1 x C/O relay contacts
RM17TG00overvoltage category | Same as RM17TG20 ¦ IEC60664-1
RM17TG00permissible input overload | - ¦ ,permissible input overload,
RM17TG00polarity | -
RM17TG00pollution degree | Same as RM17TG20 ¦ IEC60664-1
RM17TG00power consumption | Same as RM17TG20
RM17TG00power on delay | Same as RM17TG20
RM17TG00product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TG00relative humidity | Same as RM17TG20 ¦ IEC60068-2-30,Damp heat,XX
RM17TG00release of input voltage | Same as RM17TG20
RM17TG00repeat accuracy of the switching threshold | Same as RM17TG20 ¦ ,Repeat accuracy (constant parameters),
RM17TG00repeat accuracy of time delay | Same as RM17TG20
RM17TG00reset time | Same as RM17TG20 ¦ ,through Un power reset, Same as RM17TG20 ¦ ,through front panel reset, Same as RM17TG20 ¦ ,through input control reset,
RM17TG00response time | Same as RM17TG20 ¦ ,on crossing the threshold, Same as RM17TG20 Same as RM17TG20 Same as RM17TG20 Same as RM17TG20
RM17TG00safety reliability data | Same as RM17TG20 ¦ ,MTTF, Same as RM17TG20 ¦ ,B10,
RM17TG00seismic resistance | Same as RM17TG20 ¦ IEC60068-3-3
RM17TG00setting accuracy of the switching threshold | Same as RM17TG20 ¦ ,Setting accuracy,
RM17TG00setting accuracy of time delay | Same as RM17TG20
RM17TG00shock resistance | Same as RM17TG20 ¦ IEC60068-2-27
RM17TG00short circuit protection | Same as RM17TG20 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM17TG20 ¦ IEC62314,Solid State Output by external fuse,
RM17TG00standards | Same as RM17TG20
RM17TG00status LED | Same as RM17TG20
RM17TG00supply frequency | Same as RM17TG20 Same as RM17TG20
RM17TG00supply terminal | Same as RM17TG20
RM17TG00supply voltage limits | ~ 3 x 183…3 x 528
RM17TG00switching threshold drift | Same as RM17TG20 ¦ ,Measurement error with supply voltage variation, Same as RM17TG20 ¦ ,Measurement error with temperature variation,
RM17TG00thermal current | Same as RM17TG20 ¦ IEC60947-5-1
RM17TG00tightening torque | Same as RM17TG20 ¦ IEC60947-1,Tightening torque,
RM17TG00time delay drift | Same as RM17TG20 Same as RM17TG20
RM17TG00time delay range | Same as RM17TG20 ¦ ,"OFF" delay, Same as RM17TG20 ¦ ,"ON" delay, Same as RM17TG20 ¦ ,Inhibition,
RM17TG00time delay type | Same as RM17TG20 ¦ ,"OFF" delay, Same as RM17TG20 ¦ ,"ON" delay, Same as RM17TG20 ¦ ,Inhibition,
RM17TG00tripping threshold | Same as RM17TG20 ¦ ,Phase cut, Same as RM17TG20 ¦ ,Phase sequence, Same as RM17TG20 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM17TG20 ¦ ,Over voltage, Same as RM17TG20 ¦ ,Undervoltage , Same as RM17TG20 ¦ ,Phase asymmetry, Same as RM17TG20 ¦ ,Disconnection of neutral, Same as RM17TG20 ¦ ,Voltage Regeneration, Same as RM17TG20 ¦ ,Extreme undervoltage (Phase loss), Same as RM17TG20 ¦ ,Extreme Overvoltage, Same as RM17TG20 ¦ ,Extreme Asymmetry,
RM17TG00vibration resistance | Same as RM17TG20 ¦ IEC60068-2-6
RM17TG00width | Same as RM17TG20 ¦ ,Width,
RM17TG20 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 208..440 AC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, No - - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d, Drawing / Diagram
RM17TG20IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, - ¦ IEC60529,Front Panel,
RM17TG20Input nominal voltage selection | - ¦ ,Input nominal voltage selection,
RM17TG20Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM17TG20[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM17TG20[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM17TG20[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, 500V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM17TG20[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM17TG20[Us] rated supply voltage | ~ 3 x 208…3 x 440
RM17TG20ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM17TG20ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM17TG20bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM17TG20cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM17TG20circuit group | L1, L2, L3 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM17TG20connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM17TG20contacts material | Cadmium free
RM17TG20depth | 72 ¦ ,Depth,
RM17TG20diagnostic button | -
RM17TG20dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM17TG20directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM17TG20duty time | 1
RM17TG20electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM17TG20electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM17TG20height | 90 ¦ ,Height,
RM17TG20hysteresis | All phase cut recover ¦ ,Phase cut, Total phase swap recover Internal design spec: L31 lag L21 >= 15o or L31 lag L21 <= 135o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, All phases > 183V Internal design spec: All phases >153V +/- 10% ¦ ,Extreme undervoltage (Phase loss), - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM17TG20immunity to microbreaks | 0
RM17TG20input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
RM17TG20input terminal | L1-L2-L3 ¦ ,Input terminal,
RM17TG20insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM17TG20internal input resistance | - ¦ ,Internal input resistance,
RM17TG20local signalling | - ¦ ,Power supply availability, - ¦ ,Power supply not availability, - ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, - ¦ ,Range Setting Changes, - ¦ ,Phase Cut, - ¦ ,Phase Sequence Swap, - ¦ ,Undervoltage <U, - ¦ ,Overvoltage >U, - ¦ ,Phase Asymmetry, - ¦ ,Voltage Regeneration, - ¦ ,Extreme Undervoltage <U (Phase loss), - ¦ ,Extreme Overvoltage >U, - ¦ ,Extreme Phase Asymmetry,
RM17TG20marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TG20maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM17TG20maximum measuring cycle | - ¦ ,Maximum measuring cycles,
RM17TG20maximum switching capacity | 250V ¦ ,Maximum switching voltage, 5A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM17TG20maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM17TG20measurement method | Non True RMS ¦ ,Measurement method,
RM17TG20measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, - ¦ ,Extreme undervoltage, - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM17TG20mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM17TG20minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM17TG20monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost , governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage, - ¦ ,Extreme overvoltage, - ¦ ,Extreme asymmetry,
RM17TG20mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM17TG20mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM17TG20net weight | 85
RM17TG20on-load factor | 1
RM17TG20output logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM17TG20output terminal | 11-12-14, 21-22-24
RM17TG20output type | 2 x C/O relay contacts
RM17TG20overvoltage category | 3 ¦ IEC60664-1
RM17TG20permissible input overload | - ¦ ,permissible input overload,
RM17TG20polarity | -
RM17TG20pollution degree | 3 ¦ IEC60664-1
RM17TG20power consumption | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz
RM17TG20power on delay | 0
RM17TG20product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TG20relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM17TG20release of input voltage | -
RM17TG20repeat accuracy of the switching threshold | - ¦ ,Repeat accuracy (constant parameters),
RM17TG20repeat accuracy of time delay | -
RM17TG20reset time | 0
RM17TG20response time | 0
RM17TG20safety reliability data | 8,100,000 hours ¦ ,MTTF, 850,000 hours ¦ ,B10,
RM17TG20seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM17TG20setting accuracy of the switching threshold | - ¦ ,Setting accuracy,
RM17TG20setting accuracy of time delay | -
RM17TG20shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM17TG20short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM17TG20standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM17TG20status LED | R (Amber)
RM17TG20supply frequency | 50 / 60 45…66
RM17TG20supply terminal | L1-L3
RM17TG20supply voltage limits | ~ 3 x 183…3 x 484
RM17TG20switching threshold drift | - ¦ ,Measurement error with supply voltage variation, - ¦ ,Measurement error with temperature variation,
RM17TG20thermal current | 5A ¦ IEC60947-5-1
RM17TG20tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM17TG20time delay drift | - -
RM17TG20time delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM17TG20time delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM17TG20tripping threshold | 1 or more phase cut ¦ ,Phase cut, Total swap of phase Internal design spec: L31 lag L21 =< 10o or L31 lag L21 >= 150o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, 2 or more phase < 100V Internal design spec: 2 or more phase <150V +/- 10% ¦ ,Extreme undervoltage (Phase loss), - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM17TG20vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM17TG20width | 17.5 ¦ ,Width,
RM17TT00 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 208..480 AC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, - ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, Yes - - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d, Drawing / Diagram
RM17TT00IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, - ¦ IEC60529,Front Panel,
RM17TT00Input nominal voltage selection | 208, 220, 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM17TT00Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM17TT00[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM17TT00[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM17TT00[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, - ¦ IEC60664-1,Supply / Output 2, - ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM17TT00[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, - ¦ IEC60664-1,Supply / Output 2, - ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM17TT00[Us] rated supply voltage | ~ 3 x 208…3 x 480
RM17TT00ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM17TT00ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM17TT00bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM17TT00cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM17TT00circuit group | L1, L2, L3 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, - ¦ ,Output 2,
RM17TT00connections - terminals | 1 conductor: 0.5…4 (AWG 20…AWG 11) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM17TT00contacts material | Cadmium free
RM17TT00depth | 72 ¦ ,Depth,
RM17TT00diagnostic button | -
RM17TT00dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, - ¦ IEC60255-27,Supply / Output 2, - ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM17TT00directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM17TT00duty time | 1
RM17TT00electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM17TT00electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM17TT00height | 90 ¦ ,Height,
RM17TT00hysteresis | All phase cut recover ¦ ,Phase cut, Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, 0.3 ¦ ,Voltage Regeneration, All phases > 195V Internal design spec: All phases >180V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: All phases <533V +/- 5% ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM17TT00immunity to microbreaks | 0
RM17TT00input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
RM17TT00input terminal | L1-L2-L3 ¦ ,Input terminal,
RM17TT00insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, - ¦ IEC60255-27,Supply / Output 2, - ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM17TT00internal input resistance | - ¦ ,Internal input resistance,
RM17TT00local signalling | Un - ON ¦ ,Power supply availability, Un - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes, - ¦ ,Phase Cut, - ¦ ,Phase Sequence Swap, - ¦ ,Undervoltage <U, - ¦ ,Overvoltage >U, - ¦ ,Phase Asymmetry, - ¦ ,Voltage Regeneration, - ¦ ,Extreme Undervoltage <U (Phase loss), - ¦ ,Extreme Overvoltage >U, - ¦ ,Extreme Phase Asymmetry,
RM17TT00marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TT00maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM17TT00maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM17TT00maximum switching capacity | 250V ¦ ,Maximum switching voltage, 5A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM17TT00maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM17TT00measurement method | True RMS ¦ ,Measurement method,
RM17TT00measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, - ¦ ,Extreme undervoltage, - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM17TT00mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM17TT00minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM17TT00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost , governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, governed by response time only, status reflects to both R1 & R2 ¦ ,Voltage Regeneration, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM17TT00mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM17TT00mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM17TT00net weight | 80
RM17TT00on-load factor | 1
RM17TT00output logic | Energized on fault-free ¦ ,R1 (11-12-14), - ¦ ,R2 (21-22-24),
RM17TT00output terminal | 11-12-14
RM17TT00output type | 1 x C/O relay contacts
RM17TT00overvoltage category | 3 ¦ IEC60664-1
RM17TT00permissible input overload | - ¦ ,permissible input overload,
RM17TT00polarity | -
RM17TT00pollution degree | 3 ¦ IEC60664-1
RM17TT00power consumption | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz
RM17TT00power on delay | 0
RM17TT00product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TT00relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM17TT00release of input voltage | -
RM17TT00repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM17TT00repeat accuracy of time delay | -
RM17TT00reset time | 0
RM17TT00response time | 0
RM17TT00safety reliability data | 4,400,000 hours ¦ ,MTTF, 470,000 hours ¦ ,B10,
RM17TT00seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM17TT00setting accuracy of the switching threshold | - ¦ ,Setting accuracy,
RM17TT00setting accuracy of time delay | -
RM17TT00shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM17TT00short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM17TT00standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM17TT00status LED | Un (Green) R (Amber)
RM17TT00supply frequency | 50 / 60 45…66
RM17TT00supply terminal | L1-L3
RM17TT00supply voltage limits | ~ 3 x 183…3 x 528
RM17TT00switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation, < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM17TT00thermal current | 5A ¦ IEC60947-5-1
RM17TT00tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM17TT00time delay drift | - -
RM17TT00time delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM17TT00time delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM17TT00tripping threshold | 1 or more phase cut ¦ ,Phase cut, Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, 1 or more phase < 70% of selected Un Internal design spec: 30% +/- 5% ¦ ,Voltage Regeneration, 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: 543V +/- 5% ¦ ,Extreme Overvoltage, Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM17TT00vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM17TT00width | 17.5 ¦ ,Width,
RM17TU00 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 208..480 AC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, - ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, Yes - - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d, Drawing / Diagram
RM17TU00IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, - ¦ IEC60529,Front Panel,
RM17TU00Input nominal voltage selection | 208, 220, 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM17TU00Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM17TU00[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM17TU00[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM17TU00[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, - ¦ IEC60664-1,Supply / Output 2, - ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM17TU00[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, - ¦ IEC60664-1,Supply / Output 2, - ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM17TU00[Us] rated supply voltage | ~ 3 x 208…3 x 480
RM17TU00ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM17TU00ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM17TU00bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM17TU00cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM17TU00circuit group | L1, L2, L3 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, - ¦ ,Output 2,
RM17TU00connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM17TU00contacts material | Cadmium free
RM17TU00depth | 72 ¦ ,Depth,
RM17TU00diagnostic button | -
RM17TU00dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, - ¦ IEC60255-27,Supply / Output 2, - ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM17TU00directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM17TU00duty time | 1
RM17TU00electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM17TU00electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM17TU00height | 90 ¦ ,Height,
RM17TU00hysteresis | All phase cut recover ¦ ,Phase cut, Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, All phases > 195V Internal design spec: All phases >180V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: All phases <533V +/- 5% ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM17TU00immunity to microbreaks | 0
RM17TU00input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
RM17TU00input terminal | L1-L2-L3 ¦ ,Input terminal,
RM17TU00insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, - ¦ IEC60255-27,Supply / Output 2, - ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM17TU00internal input resistance | - ¦ ,Internal input resistance,
RM17TU00local signalling | Un - ON ¦ ,Power supply availability, Un - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes, - ¦ ,Phase Cut, - ¦ ,Phase Sequence Swap, - ¦ ,Undervoltage <U, - ¦ ,Overvoltage >U, - ¦ ,Phase Asymmetry, - ¦ ,Voltage Regeneration, - ¦ ,Extreme Undervoltage <U (Phase loss), - ¦ ,Extreme Overvoltage >U, - ¦ ,Extreme Phase Asymmetry,
RM17TU00marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TU00maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM17TU00maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM17TU00maximum switching capacity | 250V ¦ ,Maximum switching voltage, 5A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM17TU00maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM17TU00measurement method | True RMS ¦ ,Measurement method,
RM17TU00measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, -2…-20 % in the ranges 3 x ~ 380…480 -2…-12 % in the range 3 x ~ 208 -2…-17 % in the range 3 x ~ 220 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, - ¦ ,Extreme undervoltage, - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM17TU00mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM17TU00minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM17TU00monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost , governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, governed by time delay, status reflects to both R1 & R2 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage, - ¦ ,Extreme asymmetry,
RM17TU00mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM17TU00mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM17TU00net weight | 80
RM17TU00on-load factor | 1
RM17TU00output logic | Energized on fault-free ¦ ,R1 (11-12-14), - ¦ ,R2 (21-22-24),
RM17TU00output terminal | 11-12-14
RM17TU00output type | 1 x C/O relay contacts
RM17TU00overvoltage category | 3 ¦ IEC60664-1
RM17TU00permissible input overload | - ¦ ,permissible input overload,
RM17TU00polarity | -
RM17TU00pollution degree | 3 ¦ IEC60664-1
RM17TU00power consumption | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz
RM17TU00power on delay | 0
RM17TU00product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17TU00relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM17TU00release of input voltage | -
RM17TU00repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM17TU00repeat accuracy of time delay | +/- 3%
RM17TU00reset time | 0
RM17TU00response time | 0
RM17TU00safety reliability data | 4,400,000 hours ¦ ,MTTF, 470,000 hours ¦ ,B10,
RM17TU00seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM17TU00setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM17TU00setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM17TU00shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM17TU00short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM17TU00standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM17TU00status LED | Un (Green) R (Amber)
RM17TU00supply frequency | 50 / 60 45…66
RM17TU00supply terminal | L1-L3
RM17TU00supply voltage limits | ~ 3 x 183…3 x 528
RM17TU00switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation, < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM17TU00thermal current | 5A ¦ IEC60947-5-1
RM17TU00tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM17TU00time delay drift | - -
RM17TU00time delay range | Adjustable 0.1…10 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM17TU00time delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM17TU00tripping threshold | 1 or more phase cut ¦ ,Phase cut, Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, Adjustable 2%...20% of selected Un ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: 543V +/- 5% ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM17TU00vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM17TU00width | 17.5 ¦ ,Width,
RM17UB310 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 208..480 AC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, - ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, Yes - - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d, Drawing / Diagram
RM17UB310IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, - ¦ IEC60529,Front Panel,
RM17UB310Input nominal voltage selection | 208, 220, 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM17UB310Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM17UB310[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM17UB310[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM17UB310[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, - ¦ IEC60664-1,Supply / Output 2, - ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM17UB310[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, - ¦ IEC60664-1,Supply / Output 2, - ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM17UB310[Us] rated supply voltage | ~ 3 x 208…3 x 480
RM17UB310ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM17UB310ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM17UB310bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM17UB310cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM17UB310circuit group | L1, L2, L3 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, - ¦ ,Output 2,
RM17UB310connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM17UB310contacts material | Cadmium free
RM17UB310depth | 72 ¦ ,Depth,
RM17UB310diagnostic button | -
RM17UB310dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, - ¦ IEC60255-27,Supply / Output 2, - ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM17UB310directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM17UB310duty time | 1
RM17UB310electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM17UB310electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM17UB310height | 90 ¦ ,Height,
RM17UB310hysteresis | All phase cut recover ¦ ,Phase cut, Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Over voltage, Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, All phases > 195V Internal design spec: All phases >180V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: All phases <533V +/- 5% ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM17UB310immunity to microbreaks | 0
RM17UB310input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
RM17UB310input terminal | L1-L2-L3 ¦ ,Input terminal,
RM17UB310insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, - ¦ IEC60255-27,Supply / Output 2, - ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM17UB310internal input resistance | - ¦ ,Internal input resistance,
RM17UB310local signalling | Un - ON ¦ ,Power supply availability, Un - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes, - ¦ ,Phase Cut, - ¦ ,Phase Sequence Swap, - ¦ ,Undervoltage <U, - ¦ ,Overvoltage >U, - ¦ ,Phase Asymmetry, - ¦ ,Voltage Regeneration, - ¦ ,Extreme Undervoltage <U (Phase loss), - ¦ ,Extreme Overvoltage >U, - ¦ ,Extreme Phase Asymmetry,
RM17UB310marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17UB310maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM17UB310maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM17UB310maximum switching capacity | 250V ¦ ,Maximum switching voltage, 5A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM17UB310maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM17UB310measurement method | True RMS ¦ ,Measurement method,
RM17UB310measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), +2…+20 % in the ranges 3 x ~ 208…440 +2…+10 % in the range 3 x ~ 480 ¦ ,Over voltage, -2…-20 % in the ranges 3 x ~ 380…480 -2…-12 % in the range 3 x ~ 208 -2…-17 % in the range 3 x ~ 220 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, - ¦ ,Extreme undervoltage, - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM17UB310mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM17UB310minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM17UB310monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost , governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), governed by time delay, status reflects to both R1 & R2 ¦ ,Over voltage, governed by time delay, status reflects to both R1 & R2 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM17UB310mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM17UB310mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM17UB310net weight | 80
RM17UB310on-load factor | 1
RM17UB310output logic | Energized on fault-free ¦ ,R1 (11-12-14), - ¦ ,R2 (21-22-24),
RM17UB310output terminal | 11-12-14
RM17UB310output type | 1 x C/O relay contacts
RM17UB310overvoltage category | 3 ¦ IEC60664-1
RM17UB310permissible input overload | - ¦ ,permissible input overload,
RM17UB310polarity | -
RM17UB310pollution degree | 3 ¦ IEC60664-1
RM17UB310power consumption | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz
RM17UB310power on delay | 0
RM17UB310product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM17UB310relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM17UB310release of input voltage | -
RM17UB310repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM17UB310repeat accuracy of time delay | +/- 3%
RM17UB310reset time | 0
RM17UB310response time | 0
RM17UB310safety reliability data | 4,400,000 hours ¦ ,MTTF, 470,000 hours ¦ ,B10,
RM17UB310seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM17UB310setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM17UB310setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM17UB310shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM17UB310short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM17UB310standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM17UB310status LED | Un (Green) R (Amber)
RM17UB310supply frequency | 50 / 60 45…66
RM17UB310supply terminal | L1-L3
RM17UB310supply voltage limits | ~ 3 x 183…3 x 528
RM17UB310switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation, < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM17UB310thermal current | 5A ¦ IEC60947-5-1
RM17UB310tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM17UB310time delay drift | - -
RM17UB310time delay range | Adjustable 0.1…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM17UB310time delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM17UB310tripping threshold | 1 or more phase cut ¦ ,Phase cut, Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Adjustable 2%...20% of selected Un ¦ ,Over voltage, Adjustable 2%...20% of selected Un ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: 543V +/- 5% ¦ ,Extreme Overvoltage, Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM17UB310vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM17UB310width | 17.5 ¦ ,Width,
RM22 (Catch Up) | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, 600 ¦ ,Supply,Rated 600 ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d, Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, 600 ¦ ,Supply,Rated 600 ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d,
RM22 (Catch Up)IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IEC60529,Front Panel, IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IEC60529,Front Panel,
RM22 (Catch Up)Maximum length of probes cable | 100 ¦ ,Maximum length of probes cable, 100 ¦ ,Maximum length of probes cable,
RM22 (Catch Up)Maximum probe supplied current | 1 ¦ ,Maximum probe supplied current, 1 ¦ ,Maximum probe supplied current,
RM22 (Catch Up)Maximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage, 12 ¦ ,Maximum probe supplied voltage,
RM22 (Catch Up)Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical, Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22 (Catch Up)[Ie] rated operational current | IEC61810-1,Rated switching current, IEC61810-1,Rated switching current,
RM22 (Catch Up)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage, IEC61810-1,Rated switching voltage,
RM22 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, 4 ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3, IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, 4 ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM22 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3, IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM22 (Catch Up)[Us] rated supply voltage | ~/-- 24…240 ~/-- 24…240
RM22 (Catch Up)ambient air temperature for operation | -20…+50 ¦ ,Operation, -20…+50 ¦ ,Operation,
RM22 (Catch Up)ambient air temperature for storage | -40…+70 ¦ ,Storage, -40…+70 ¦ ,Storage,
RM22 (Catch Up)bump resistance | IEC60068-2-29 IEC60068-2-29
RM22 (Catch Up)cable stripping length | Not specified ¦ ,Cable stripping length, Not specified ¦ ,Cable stripping length,
RM22 (Catch Up)circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, 600 ¦ ,Output 2, Supply,Terminal Input 1, Input 2, Input 3, Output 1, 600 ¦ ,Output 2,
RM22 (Catch Up)connections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal), 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22 (Catch Up)contacts material | Cadmium free Cadmium free
RM22 (Catch Up)depth | Depth, Depth,
RM22 (Catch Up)diagnostic button
RM22 (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3, Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM22 (Catch Up)directives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
RM22 (Catch Up)duty time | Not specified Not specified
RM22 (Catch Up)electrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13, 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM22 (Catch Up)electromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission, IEC61000-6-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22 (Catch Up)height | Height, Height,
RM22 (Catch Up)hysteresis | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation, 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM22 (Catch Up)immunity to microbreaks | 90 (AC), 100 (DC) 90 (AC), 100 (DC)
RM22 (Catch Up)input frequency | Maximum cable capacitance, Maximum cable capacitance,
RM22 (Catch Up)input terminal | Input terminal, Input terminal,
RM22 (Catch Up)insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3, IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM22 (Catch Up)internal input resistance | Internal input resistance, Internal input resistance,
RM22 (Catch Up)local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM22 (Catch Up)marking | UL, CSA, GL, C-Tick, GOST, CE UL, CSA, GL, C-Tick, GOST, CE
RM22 (Catch Up)maximum leakage current | - ¦ IEC62314,Only for solid state output, - ¦ IEC62314,Only for solid state output,
RM22 (Catch Up)maximum measuring cycle | Maximum measuring cycles, Maximum measuring cycles,
RM22 (Catch Up)maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, ~ 8 ¦ ,Maximum switching current, 2000 ¦ ,Maximum switching capacity, ~ 250 ¦ ,Maximum switching voltage, ~ 5 ¦ ,Maximum switching current, 1250 ¦ ,Maximum switching capacity,
RM22 (Catch Up)maximum voltage drop | - ¦ IEC62314,Only for solid state output, - ¦ IEC62314,Only for solid state output,
RM22 (Catch Up)measurement method | Liquid level probe ¦ ,Measurement method, Liquid level probe ¦ ,Measurement method,
RM22 (Catch Up)measurement range | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation, 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM22 (Catch Up)mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1 30 x 106 switching cycles ¦ IEC61810-1
RM22 (Catch Up)minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity, 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM22 (Catch Up)monitoring functions | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation, 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM22 (Catch Up)mounting position | Any position ¦ ,In relation to normal vertical mounting plane, Any position ¦ ,In relation to normal vertical mounting plane,
RM22 (Catch Up)mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket, On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22 (Catch Up)net weight | ? ?
RM22 (Catch Up)on-load factor
RM22 (Catch Up)output logic | Not specified ¦ ,R1 (11-12-14), R2 (21-22-24), Not specified ¦ ,R1 (11-12-14), R2 (21-22-24),
RM22 (Catch Up)output terminal | 11-12-14 11-12-14, 21-22-24
RM22 (Catch Up)output type | 1 x C/O relay contacts 2 x C/O relay contacts
RM22 (Catch Up)overvoltage category | III ¦ IEC60664-1 III ¦ IEC60664-1
RM22 (Catch Up)polarity
RM22 (Catch Up)pollution degree | 3 ¦ IEC60664-1 3 ¦ IEC60664-1
RM22 (Catch Up)power consumption | ~ 5VA, -- 1.5W ~ 5VA, -- 1.5W
RM22 (Catch Up)power on delay | 0
RM22 (Catch Up)product certifications | UL, CSA, GL, C-Tick, GOST UL, CSA, GL, C-Tick, GOST
RM22 (Catch Up)relative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat, 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM22 (Catch Up)release of input voltage
RM22 (Catch Up)repeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters), Not specified ¦ ,Repeat accuracy (constant parameters),
RM22 (Catch Up)repeat accuracy of time delay | +/- 2% +/- 2%
RM22 (Catch Up)reset time | 0
RM22 (Catch Up)response time | Not specified ¦ ,on crossing the threshold, Not specified ¦ ,on crossing the threshold,
RM22 (Catch Up)safety reliability data | MTTF, B10, MTTF, B10,
RM22 (Catch Up)seismic resistance | IEC60068-3-3 IEC60068-3-3
RM22 (Catch Up)setting accuracy of the switching threshold | +/- 10% of full scale value, +/- 20% for HS range ¦ ,Setting accuracy, +/- 10% of full scale value, +/- 20% for HS range ¦ ,Setting accuracy,
RM22 (Catch Up)setting accuracy of time delay | +/- 10% of full scales +/- 10% of full scales
RM22 (Catch Up)shock resistance | 5 gn ¦ IEC60068-2-27 5 gn ¦ IEC60068-2-27
RM22 (Catch Up)short circuit protection | 8 ¦ IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse, IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM22 (Catch Up)standards | EN60255-6, IEC60255-6 EN60255-6, IEC60255-6
RM22 (Catch Up)status LED
RM22 (Catch Up)supply frequency | 50 / 60 45…66 50 / 60 45…66
RM22 (Catch Up)supply terminal | A1-A2 A1-A2
RM22 (Catch Up)supply voltage limits | ~/-- 20.4…264 ~/-- 20.4…264
RM22 (Catch Up)switching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation, 0.5% / oC ¦ ,Measurement error with temperature variation, Not specified ¦ ,Measurement error with supply voltage variation, 0.5% / oC ¦ ,Measurement error with temperature variation,
RM22 (Catch Up)thermal current | 8 ¦ IEC60947-5-1 IEC60947-5-1
RM22 (Catch Up)tightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque, 0.6…1 ¦ IEC60947-1,Tightening torque,
RM22 (Catch Up)time delay drift | Not specified Not specified Not specified Not specified
RM22 (Catch Up)time delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition, Adjustable 0.1…5 ¦ ,"OFF" delay, Adjustable 0.1…5 ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22 (Catch Up)time delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition, · ¦ ,"OFF" delay, · ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22 (Catch Up)tripping threshold | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation, 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM22 (Catch Up)vibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM22 (Catch Up)width | 22.5 x ? x ? ¦ ,Width, 22.5 x ? x ? ¦ ,Width,
RM22JA21MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 24…240 AC/DC ¦ ,Supply,Rated 4..40mA AC/DC [full: 4..40mA AC/DC ] ¦ ,Input 1,Voltage 20..200mA AC/DC [full: 20..200mA AC/DC] ¦ ,Input 2,Spec 100..1000mA AC/DC [full: 100..1000mA AC/DC] ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, - ¦ ,Over / undercurrent (windows mode), Selectable with memory / without memory ¦ ,Over current, - ¦ ,Under current, ~/-- 4…1000 2.5 ¦ ,E1-M / B1-C, 0.5 ¦ ,E2-M / B2-C, 0.1 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 4…40 ¦ ,E1-M / B1-C, ~/-- 20…200 ¦ ,E2-M / B2-C, ~/-- 100…1000 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of 40 ¦ ,E1-M / B1-C, Adjustable 10%...100% of 200 ¦ ,E2-M / B2-C, Adjustable 10%...100% of 1000 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C, Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C, Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Shunt resistor E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 100 True RMS Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22JA21MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22JA21MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22JA21MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22JA21MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22JA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply, 10V ¦ IEC60664-1,Input 1, 10V ¦ IEC60664-1,Input 2, 10V ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, 250V ¦ IEC60664-1,Supply / Input 1,Galvanic 250V ¦ IEC60664-1,Supply / Input 2,Isolated 250V ¦ IEC60664-1,Supply / Input 3,Circuit 250V ¦ IEC60664-1,Supply / Output 1, 250V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, 250V ¦ IEC60664-1,Input 1 / Output 1, 250V ¦ IEC60664-1,Input 1 / Output 2, 250V ¦ IEC60664-1,Input 2 / Output 1, 250V ¦ IEC60664-1,Input 2 / Output 2, 250V ¦ IEC60664-1,Input 3 / Output 1, 250V ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22JA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22JA21MR[Us] rated supply voltage | ~/-- 24…240
RM22JA21MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22JA21MRambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22JA21MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22JA21MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22JA21MRcircuit group | A1, A2 ¦ ,Supply,Terminal E1, M ¦ ,Input 1, E2, M ¦ ,Input 2, E3, M ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22JA21MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22JA21MRcontacts material | Cadmium free
RM22JA21MRdepth | Depth,
RM22JA21MRdiagnostic button | Output will be de-energized when activated
RM22JA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22JA21MRdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22JA21MRduty time | 1
RM22JA21MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22JA21MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22JA21MRheight | Height,
RM22JA21MRimmunity to microbreaks | 50
RM22JA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22JA21MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22JA21MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22JA21MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22JA21MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22JA21MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22JA21MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22JA21MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22JA21MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22JA21MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22JA21MRnet weight | 110
RM22JA21MRon-load factor | 1
RM22JA21MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22JA21MRoutput terminal | 11-12-14, 21-22-24
RM22JA21MRoutput type | 2 x C/O relay contacts
RM22JA21MRovervoltage category | 3 ¦ IEC60664-1
RM22JA21MRpolarity
RM22JA21MRpollution degree | 3 ¦ IEC60664-1
RM22JA21MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM22JA21MRpower on delay | 0
RM22JA21MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22JA21MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22JA21MRrelease of input voltage | -
RM22JA21MRrepeat accuracy of time delay | +/- 2%
RM22JA21MRreset time | 0
RM22JA21MRresponse time | Not specified =< 500ms ¦ ,on crossing the threshold,
RM22JA21MRsafety reliability data | 2,600,000 hours ¦ ,MTTF, 270,000 hours ¦ ,B10,
RM22JA21MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22JA21MRsetting accuracy of time delay | +/- 10% of full scales
RM22JA21MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22JA21MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22JA21MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22JA21MRstatus LED | Dial pointer (Green) R (Amber)
RM22JA21MRsupply frequency | 50 / 60 45…66
RM22JA21MRsupply terminal | A1-A2
RM22JA21MRsupply voltage limits | ~/-- 20.4…264
RM22JA21MRthermal current | 8A ¦ IEC60947-5-1
RM22JA21MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22JA21MRtime delay drift | < 1 < 0.05
RM22JA21MRtime delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22JA21MRtime delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22JA21MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22JA21MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22JA31MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 24…240 AC/DC ¦ ,Supply,Rated 4..40mA AC/DC [full: 4..40mA AC/DC ] ¦ ,Input 1,Voltage 20..200mA AC/DC [full: 20..200mA AC/DC] ¦ ,Input 2,Spec 100..1000mA AC/DC [full: 100..1000mA AC/DC] ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Selectable with memory / without memory ¦ ,Over / undercurrent (windows mode), Selectable with memory / without memory ¦ ,Over current, Selectable with memory / without memory ¦ ,Under current, ~/-- 4…1000 2.5 ¦ ,E1-M / B1-C, 0.5 ¦ ,E2-M / B2-C, 0.1 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 4…40 ¦ ,E1-M / B1-C, ~/-- 20…200 ¦ ,E2-M / B2-C, ~/-- 100…1000 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of 40 ¦ ,E1-M / B1-C, Adjustable 10%...100% of 200 ¦ ,E2-M / B2-C, Adjustable 10%...100% of 1000 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E1-M / B1-C, Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E2-M / B2-C, Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Shunt resistor E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 100 True RMS Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22JA31MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22JA31MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22JA31MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22JA31MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22JA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply, 10V ¦ IEC60664-1,Input 1, 10V ¦ IEC60664-1,Input 2, 10V ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, 250V ¦ IEC60664-1,Supply / Input 1,Galvanic 250V ¦ IEC60664-1,Supply / Input 2,Isolated 250V ¦ IEC60664-1,Supply / Input 3,Circuit 250V ¦ IEC60664-1,Supply / Output 1, 250V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, 250V ¦ IEC60664-1,Input 1 / Output 1, 250V ¦ IEC60664-1,Input 1 / Output 2, 250V ¦ IEC60664-1,Input 2 / Output 1, 250V ¦ IEC60664-1,Input 2 / Output 2, 250V ¦ IEC60664-1,Input 3 / Output 1, 250V ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22JA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22JA31MR[Us] rated supply voltage | ~/-- 24…240
RM22JA31MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22JA31MRambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22JA31MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22JA31MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22JA31MRcircuit group | A1, A2 ¦ ,Supply,Terminal E1, M ¦ ,Input 1, E2, M ¦ ,Input 2, E3, M ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22JA31MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22JA31MRcontacts material | Cadmium free
RM22JA31MRdepth | Depth,
RM22JA31MRdiagnostic button | Output will be de-energized when activated
RM22JA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22JA31MRdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22JA31MRduty time | 1
RM22JA31MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22JA31MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22JA31MRheight | Height,
RM22JA31MRimmunity to microbreaks | 50
RM22JA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22JA31MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22JA31MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22JA31MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22JA31MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22JA31MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22JA31MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22JA31MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22JA31MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22JA31MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22JA31MRnet weight | 110
RM22JA31MRon-load factor | 1
RM22JA31MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22JA31MRoutput terminal | 11-12-14, 21-22-24
RM22JA31MRoutput type | 2 x C/O relay contacts
RM22JA31MRovervoltage category | 3 ¦ IEC60664-1
RM22JA31MRpolarity
RM22JA31MRpollution degree | 3 ¦ IEC60664-1
RM22JA31MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM22JA31MRpower on delay | 0
RM22JA31MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22JA31MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22JA31MRrelease of input voltage | -
RM22JA31MRrepeat accuracy of time delay | +/- 2%
RM22JA31MRreset time | 0
RM22JA31MRresponse time | Not specified =< 500ms ¦ ,on crossing the threshold,
RM22JA31MRsafety reliability data | 2,600,000 hours ¦ ,MTTF, 270,000 hours ¦ ,B10,
RM22JA31MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22JA31MRsetting accuracy of time delay | +/- 10% of full scales
RM22JA31MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22JA31MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22JA31MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22JA31MRstatus LED | Dial pointer (Green) R (Amber)
RM22JA31MRsupply frequency | 50 / 60 45…66
RM22JA31MRsupply terminal | A1-A2
RM22JA31MRsupply voltage limits | ~/-- 20.4…264
RM22JA31MRthermal current | 8A ¦ IEC60947-5-1
RM22JA31MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22JA31MRtime delay drift | < 1 < 0.05
RM22JA31MRtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22JA31MRtime delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22JA31MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22JA31MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22JA31MW (Catch Up) | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, 600 ¦ ,Supply,Rated 600 ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, - ¦ ,Over / undercurrent (windows mode), Selectable with memory / without memory ¦ ,Over current, Selectable with memory / without memory ¦ ,Under current, ~/-- 2…500 5 ¦ ,E1-M / B1-C, 1 ¦ ,E2-M / B2-C, 0.2 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 2…20 ¦ ,E1-M / B1-C, ~/-- 10…100 ¦ ,E2-M / B2-C, ~/-- 50…500 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of 20 ¦ ,E1-M / B1-C, Adjustable 10%...100% of 100 ¦ ,E2-M / B2-C, Adjustable 10%...100% of 500 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C, Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C, Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Shunt resistor E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 True RMS MTTFd, B10d,
RM22JA31MW (Catch Up)IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IEC60529,Front Panel,
RM22JA31MW (Catch Up)Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22JA31MW (Catch Up)[Ie] rated operational current | IEC61810-1,Rated switching current,
RM22JA31MW (Catch Up)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM22JA31MW (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, 4 ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM22JA31MW (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM22JA31MW (Catch Up)[Us] rated supply voltage | ~/-- 24…240
RM22JA31MW (Catch Up)ambient air temperature for operation | -20…+50 ¦ ,Operation,
RM22JA31MW (Catch Up)ambient air temperature for storage | -40…+70 ¦ ,Storage,
RM22JA31MW (Catch Up)bump resistance | IEC60068-2-29
RM22JA31MW (Catch Up)cable stripping length | Not specified ¦ ,Cable stripping length,
RM22JA31MW (Catch Up)circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, 600 ¦ ,Output 2,
RM22JA31MW (Catch Up)connections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22JA31MW (Catch Up)contacts material | Cadmium free
RM22JA31MW (Catch Up)depth | Depth,
RM22JA31MW (Catch Up)diagnostic button
RM22JA31MW (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM22JA31MW (Catch Up)directives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
RM22JA31MW (Catch Up)duty time | Not specified
RM22JA31MW (Catch Up)electrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM22JA31MW (Catch Up)electromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22JA31MW (Catch Up)height | Height,
RM22JA31MW (Catch Up)immunity to microbreaks | 10
RM22JA31MW (Catch Up)insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM22JA31MW (Catch Up)local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM22JA31MW (Catch Up)marking | UL, CSA, GL, C-Tick, GOST, CE, CCC
RM22JA31MW (Catch Up)maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22JA31MW (Catch Up)maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, ~ 8 ¦ ,Maximum switching current, 2000 ¦ ,Maximum switching capacity,
RM22JA31MW (Catch Up)maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22JA31MW (Catch Up)mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM22JA31MW (Catch Up)minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM22JA31MW (Catch Up)mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22JA31MW (Catch Up)mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22JA31MW (Catch Up)net weight | ?
RM22JA31MW (Catch Up)on-load factor
RM22JA31MW (Catch Up)output logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
RM22JA31MW (Catch Up)output terminal | 11-12-14, 21-22-24
RM22JA31MW (Catch Up)output type | 2 x C/O relay contacts
RM22JA31MW (Catch Up)overvoltage category | III ¦ IEC60664-1
RM22JA31MW (Catch Up)polarity
RM22JA31MW (Catch Up)pollution degree | 3 ¦ IEC60664-1
RM22JA31MW (Catch Up)power consumption | ~ 3.5VA, -- 0.6W
RM22JA31MW (Catch Up)power on delay | 0
RM22JA31MW (Catch Up)product certifications | UL, CSA, GL, C-Tick, GOST, CCC
RM22JA31MW (Catch Up)relative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM22JA31MW (Catch Up)release of input voltage
RM22JA31MW (Catch Up)repeat accuracy of time delay | +/- 2%
RM22JA31MW (Catch Up)reset time | 0
RM22JA31MW (Catch Up)response time | Not specified ¦ ,on crossing the threshold,
RM22JA31MW (Catch Up)safety reliability data | MTTF, B10,
RM22JA31MW (Catch Up)seismic resistance | IEC60068-3-3
RM22JA31MW (Catch Up)setting accuracy of time delay | +/- 10% of full scales
RM22JA31MW (Catch Up)shock resistance | 5 gn ¦ IEC60068-2-27
RM22JA31MW (Catch Up)short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM22JA31MW (Catch Up)standards | EN60255-6, IEC60255-6
RM22JA31MW (Catch Up)status LED
RM22JA31MW (Catch Up)supply frequency | 50 / 60 45…66
RM22JA31MW (Catch Up)supply terminal | A1-A2
RM22JA31MW (Catch Up)supply voltage limits | ~/-- 20.4…264
RM22JA31MW (Catch Up)thermal current | IEC60947-5-1
RM22JA31MW (Catch Up)tightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM22JA31MW (Catch Up)time delay drift | Not specified Not specified
RM22JA31MW (Catch Up)time delay range | Adjustable 0.3…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, Adjustable 1…20 ¦ ,Inhibition,
RM22JA31MW (Catch Up)time delay type | · ¦ ,"OFF" delay, - ¦ ,"ON" delay, · ¦ ,Inhibition,
RM22JA31MW (Catch Up)vibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM22JA31MW (Catch Up)width | 22.5 x ? x ? ¦ ,Width,
RM22LA32MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 24…240 AC/DC ¦ ,Supply,Rated Level probe ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Measurement mode, - 1) Will always illuminated when power is supplied to the product - 1) Output is energized/ de-energized according to function diagram 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22LA32MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22LA32MRMaximum length of probes cable | 100 ¦ ,Maximum length of probes cable,
RM22LA32MRMaximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
RM22LA32MRMaximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage,
RM22LA32MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22LA32MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22LA32MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22LA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply, 10V ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, 250V ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 250V ¦ IEC60664-1,Supply / Output 1, 250V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, 250V ¦ IEC60664-1,Input 1 / Output 1, 250V ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22LA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22LA32MR[Us] rated supply voltage | ~/-- 24…240
RM22LA32MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22LA32MRambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22LA32MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22LA32MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22LA32MRcircuit group | A1, A2 ¦ ,Supply,Terminal Min, Max, C ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22LA32MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22LA32MRcontacts material | Cadmium free
RM22LA32MRdepth | Depth,
RM22LA32MRdiagnostic button | Output will be de-energized when activated
RM22LA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22LA32MRdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22LA32MRduty time | 1
RM22LA32MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22LA32MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22LA32MRheight | Height,
RM22LA32MRhysteresis | - ¦ ,1 level - Fill operation, - ¦ ,1 level - Empty operation, - ¦ ,2 level - Fill operation, - ¦ ,2 level - Empty operation,
RM22LA32MRimmunity to microbreaks | ~ 90, -- 100
RM22LA32MRinput frequency | 1 for LS 2.2 for St 4.7 for HS ¦ ,Maximum cable capacitance,
RM22LA32MRinput terminal | Min-Max-C ¦ ,Input terminal,
RM22LA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22LA32MRinternal input resistance | - ¦ ,Internal input resistance,
RM22LA32MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22LA32MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22LA32MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22LA32MRmaximum measuring cycle | Maximum measuring cycles,
RM22LA32MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22LA32MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22LA32MRmeasurement method | Liquid level resistive probe ¦ ,Measurement method,
RM22LA32MRmeasurement range | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS ¦ ,1 level - Fill operation, 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS ¦ ,1 level - Empty operation, 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS ¦ ,2 level - Fill operation, 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS ¦ ,2 level - Empty operation,
RM22LA32MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22LA32MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22LA32MRmonitoring functions | - governed by time delay - status reflects to both R1 & R2 ¦ ,1 level - Fill operation, - governed by time delay - status reflects to both R1 & R2 ¦ ,1 level - Empty operation, - governed by time delay - status reflects to both R1 & R2 ¦ ,2 level - Fill operation, - governed by time delay - status reflects to both R1 & R2 ¦ ,2 level - Empty operation,
RM22LA32MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22LA32MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22LA32MRnet weight | 110
RM22LA32MRon-load factor | 1
RM22LA32MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22LA32MRoutput terminal | 11-12-14, 21-22-24
RM22LA32MRoutput type | 2 x C/O relay contacts
RM22LA32MRovervoltage category | 3 ¦ IEC60664-1
RM22LA32MRpolarity
RM22LA32MRpollution degree | 3 ¦ IEC60664-1
RM22LA32MRpower consumption | ~ 3.5VA, ~5VA, 1.5W
RM22LA32MRpower on delay | 0
RM22LA32MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22LA32MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22LA32MRrelease of input voltage | -
RM22LA32MRrepeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22LA32MRrepeat accuracy of time delay | +/- 2%
RM22LA32MRreset time | 0
RM22LA32MRresponse time | 0
RM22LA32MRsafety reliability data | 1,600,000 hours ¦ ,MTTF, 170,000 hours ¦ ,B10,
RM22LA32MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22LA32MRsetting accuracy of the switching threshold | +/- 10% of full scale value for LS '+/- 10% of full scale value for St '+/- 35% of full scale value for HS ¦ ,Setting accuracy,
RM22LA32MRsetting accuracy of time delay | +/- 10% of full scales
RM22LA32MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22LA32MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22LA32MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22LA32MRstatus LED | Dial pointer (Green) R (Amber)
RM22LA32MRsupply frequency | 50 / 60 45…66
RM22LA32MRsupply terminal | A1-A2
RM22LA32MRsupply voltage limits | ~/-- 20.4…264
RM22LA32MRswitching threshold drift | < 1% over whole range ¦ ,Measurement error with supply voltage variation, 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22LA32MRthermal current | 8A ¦ IEC60947-5-1
RM22LA32MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22LA32MRtime delay drift | < 1 < 0.05
RM22LA32MRtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay, Adjustable 0.1…30 ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22LA32MRtime delay type | Yes ¦ ,"OFF" delay, Yes ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22LA32MRtripping threshold | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS ¦ ,1 level - Fill operation, Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS ¦ ,1 level - Empty operation, Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS ¦ ,2 level - Fill operation, Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS ¦ ,2 level - Empty operation,
RM22LA32MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22LA32MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22LA32MT | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 380…415 AC ¦ ,Supply,Rated Level probe ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Measurement mode, - 1) Will always illuminated when power is supplied to the product - 1) Output is energized/ de-energized according to function diagram 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22LA32MTIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22LA32MTMaximum length of probes cable | 100 ¦ ,Maximum length of probes cable,
RM22LA32MTMaximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
RM22LA32MTMaximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage,
RM22LA32MTMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22LA32MT[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22LA32MT[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22LA32MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply, 10V ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, 400V ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 400V ¦ IEC60664-1,Supply / Output 1, 400V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, 250V ¦ IEC60664-1,Input 1 / Output 1, 250V ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22LA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22LA32MT[Us] rated supply voltage | ~380…415
RM22LA32MTambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22LA32MTambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22LA32MTbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22LA32MTcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22LA32MTcircuit group | A1, A2 ¦ ,Supply,Terminal Min, Max, C ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22LA32MTconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22LA32MTcontacts material | Cadmium free
RM22LA32MTdepth | Depth,
RM22LA32MTdiagnostic button | Output will be de-energized when activated
RM22LA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22LA32MTdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22LA32MTduty time | 1
RM22LA32MTelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22LA32MTelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22LA32MTheight | Height,
RM22LA32MThysteresis | - ¦ ,1 level - Fill operation, - ¦ ,1 level - Empty operation, - ¦ ,2 level - Fill operation, - ¦ ,2 level - Empty operation,
RM22LA32MTimmunity to microbreaks | ~ 90, -- 100
RM22LA32MTinput frequency | 1 for LS 2.2 for St 4.7 for HS ¦ ,Maximum cable capacitance,
RM22LA32MTinput terminal | Min-Max-C ¦ ,Input terminal,
RM22LA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22LA32MTinternal input resistance | - ¦ ,Internal input resistance,
RM22LA32MTlocal signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22LA32MTmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22LA32MTmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22LA32MTmaximum measuring cycle | Maximum measuring cycles,
RM22LA32MTmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22LA32MTmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22LA32MTmeasurement method | Liquid level resistive probe ¦ ,Measurement method,
RM22LA32MTmeasurement range | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS ¦ ,1 level - Fill operation, 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS ¦ ,1 level - Empty operation, 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS ¦ ,2 level - Fill operation, 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS ¦ ,2 level - Empty operation,
RM22LA32MTmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22LA32MTminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22LA32MTmonitoring functions | - governed by time delay - status reflects to both R1 & R2 ¦ ,1 level - Fill operation, - governed by time delay - status reflects to both R1 & R2 ¦ ,1 level - Empty operation, - governed by time delay - status reflects to both R1 & R2 ¦ ,2 level - Fill operation, - governed by time delay - status reflects to both R1 & R2 ¦ ,2 level - Empty operation,
RM22LA32MTmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22LA32MTmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22LA32MTnet weight | 110
RM22LA32MTon-load factor | 1
RM22LA32MToutput logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22LA32MToutput terminal | 11-12-14, 21-22-24
RM22LA32MToutput type | 2 x C/O relay contacts
RM22LA32MTovervoltage category | 3 ¦ IEC60664-1
RM22LA32MTpolarity
RM22LA32MTpollution degree | 3 ¦ IEC60664-1
RM22LA32MTpower consumption | ~ 10VA ~ 8VA
RM22LA32MTpower on delay | 0
RM22LA32MTproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22LA32MTrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22LA32MTrelease of input voltage | -
RM22LA32MTrepeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22LA32MTrepeat accuracy of time delay | +/- 2%
RM22LA32MTreset time | 0
RM22LA32MTresponse time | 0
RM22LA32MTsafety reliability data | 1,600,000 hours ¦ ,MTTF, 170,000 hours ¦ ,B10,
RM22LA32MTseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22LA32MTsetting accuracy of the switching threshold | +/- 10% of full scale value for LS '+/- 10% of full scale value for St '+/- 35% of full scale value for HS ¦ ,Setting accuracy,
RM22LA32MTsetting accuracy of time delay | +/- 10% of full scales
RM22LA32MTshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22LA32MTshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22LA32MTstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22LA32MTstatus LED | Dial pointer (Green) R (Amber)
RM22LA32MTsupply frequency | 50 / 60 45…66
RM22LA32MTsupply terminal | A1-A2
RM22LA32MTsupply voltage limits | ~323…456.5
RM22LA32MTswitching threshold drift | < 1% over whole range ¦ ,Measurement error with supply voltage variation, 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22LA32MTthermal current | 8A ¦ IEC60947-5-1
RM22LA32MTtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22LA32MTtime delay drift | < 1 < 0.05
RM22LA32MTtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay, Adjustable 0.1…30 ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22LA32MTtime delay type | Yes ¦ ,"OFF" delay, Yes ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22LA32MTtripping threshold | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS ¦ ,1 level - Fill operation, Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS ¦ ,1 level - Empty operation, Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS ¦ ,2 level - Fill operation, Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS ¦ ,2 level - Empty operation,
RM22LA32MTvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22LA32MTwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22LG11MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 24…240 AC/DC ¦ ,Supply,Rated Level probe ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, - ¦ ,Output 2, Measurement mode, - 1) Will always illuminated when power is supplied to the product - 1) Output is energized/ de-energized according to function diagram 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22LG11MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22LG11MRMaximum length of probes cable | 100 ¦ ,Maximum length of probes cable,
RM22LG11MRMaximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
RM22LG11MRMaximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage,
RM22LG11MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22LG11MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22LG11MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22LG11MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply, 10V ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 250V ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 250V ¦ IEC60664-1,Supply / Output 1, - ¦ IEC60664-1,Supply / Output 2, - ¦ IEC60664-1,Output 1 / Output 2, 250V ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22LG11MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, - ¦ IEC60664-1,Supply / Output 2, - ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22LG11MR[Us] rated supply voltage | ~/-- 24…240
RM22LG11MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22LG11MRambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22LG11MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22LG11MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22LG11MRcircuit group | A1, A2 ¦ ,Supply,Terminal Min, Max, C ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, - ¦ ,Output 2,
RM22LG11MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22LG11MRcontacts material | Cadmium free
RM22LG11MRdepth | Depth,
RM22LG11MRdiagnostic button | Output will be de-energized when activated
RM22LG11MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, - ¦ IEC60255-27,Supply / Output 2, - ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22LG11MRdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22LG11MRduty time | 1
RM22LG11MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22LG11MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22LG11MRheight | Height,
RM22LG11MRhysteresis | - ¦ ,1 level - Fill operation, - ¦ ,1 level - Empty operation, - ¦ ,2 level - Fill operation, - ¦ ,2 level - Empty operation,
RM22LG11MRimmunity to microbreaks | ~ 90, -- 100
RM22LG11MRinput frequency | 1 for LS 2.2 for St 4.7 for HS ¦ ,Maximum cable capacitance,
RM22LG11MRinput terminal | Min-Max-C ¦ ,Input terminal,
RM22LG11MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, - ¦ IEC60255-27,Supply / Output 2, - ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22LG11MRinternal input resistance | - ¦ ,Internal input resistance,
RM22LG11MRlocal signalling | - ¦ ,Power supply availability, - ¦ ,Power supply not availability, - ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, - ¦ ,Range Setting Changes,
RM22LG11MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22LG11MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22LG11MRmaximum measuring cycle | Maximum measuring cycles,
RM22LG11MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22LG11MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22LG11MRmeasurement method | Liquid level resistive probe ¦ ,Measurement method,
RM22LG11MRmeasurement range | 5kW…100kW ¦ ,1 level - Fill operation, 5kW…100kW ¦ ,1 level - Empty operation, 5kW…100kW ¦ ,2 level - Fill operation, 5kW…100kW ¦ ,2 level - Empty operation,
RM22LG11MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22LG11MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22LG11MRmonitoring functions | - governed by response time - status reflects to both R1 & R2 ¦ ,1 level - Fill operation, - governed by response time - status reflects to both R1 & R2 ¦ ,1 level - Empty operation, - governed by response time - status reflects to both R1 & R2 ¦ ,2 level - Fill operation, - governed by response time - status reflects to both R1 & R2 ¦ ,2 level - Empty operation,
RM22LG11MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22LG11MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22LG11MRnet weight | 100
RM22LG11MRon-load factor | 1
RM22LG11MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), - ¦ ,R2 (21-22-24),
RM22LG11MRoutput terminal | 11/12/14,
RM22LG11MRoutput type | 1 x C/O relay contacts
RM22LG11MRovervoltage category | 3 ¦ IEC60664-1
RM22LG11MRpolarity
RM22LG11MRpollution degree | 3 ¦ IEC60664-1
RM22LG11MRpower consumption | ~ 3.5VA, ~5VA, 1.5W
RM22LG11MRpower on delay | 0
RM22LG11MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22LG11MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22LG11MRrelease of input voltage | -
RM22LG11MRrepeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22LG11MRrepeat accuracy of time delay | +/- 2%
RM22LG11MRreset time | 0
RM22LG11MRresponse time | 0
RM22LG11MRsafety reliability data | 1,100,000 hours ¦ ,MTTF, 120,000 hours ¦ ,B10,
RM22LG11MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22LG11MRsetting accuracy of the switching threshold | +/- 10% of full scale value ¦ ,Setting accuracy,
RM22LG11MRsetting accuracy of time delay | +/- 10% of full scales
RM22LG11MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22LG11MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22LG11MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22LG11MRstatus LED | R (Amber)
RM22LG11MRsupply frequency | 50 / 60 45…66
RM22LG11MRsupply terminal | A1-A2
RM22LG11MRsupply voltage limits | ~/-- 20.4…264
RM22LG11MRswitching threshold drift | < 1% over whole range ¦ ,Measurement error with supply voltage variation, 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22LG11MRthermal current | 8A ¦ IEC60947-5-1
RM22LG11MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22LG11MRtime delay drift | < 1 < 0.05
RM22LG11MRtime delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22LG11MRtime delay type | - ¦ ,"OFF" delay, Yes ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22LG11MRtripping threshold | Adjustable 5%...100% of 100kW ¦ ,1 level - Fill operation, Adjustable 5%...100% of 100kW ¦ ,1 level - Empty operation, Adjustable 5%...100% of 100kW ¦ ,2 level - Fill operation, Adjustable 5%...100% of 100kW ¦ ,2 level - Empty operation,
RM22LG11MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22LG11MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22LG11MT | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 380…415 AC ¦ ,Supply,Rated Level probe ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, - ¦ ,Output 2, Measurement mode, - 1) Will always illuminated when power is supplied to the product - 1) Output is energized/ de-energized according to function diagram 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22LG11MTIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22LG11MTMaximum length of probes cable | 100 ¦ ,Maximum length of probes cable,
RM22LG11MTMaximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
RM22LG11MTMaximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage,
RM22LG11MTMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22LG11MT[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22LG11MT[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22LG11MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply, 10V ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 400V ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 400V ¦ IEC60664-1,Supply / Output 1, - ¦ IEC60664-1,Supply / Output 2, - ¦ IEC60664-1,Output 1 / Output 2, 250V ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22LG11MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, - ¦ IEC60664-1,Supply / Output 2, - ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22LG11MT[Us] rated supply voltage | ~380…415
RM22LG11MTambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22LG11MTambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22LG11MTbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22LG11MTcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22LG11MTcircuit group | A1, A2 ¦ ,Supply,Terminal Min, Max, C ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, - ¦ ,Output 2,
RM22LG11MTconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22LG11MTcontacts material | Cadmium free
RM22LG11MTdepth | Depth,
RM22LG11MTdiagnostic button | Output will be de-energized when activated
RM22LG11MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, - ¦ IEC60255-27,Supply / Output 2, - ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22LG11MTdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22LG11MTduty time | 1
RM22LG11MTelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22LG11MTelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22LG11MTheight | Height,
RM22LG11MThysteresis | - ¦ ,1 level - Fill operation, - ¦ ,1 level - Empty operation, - ¦ ,2 level - Fill operation, - ¦ ,2 level - Empty operation,
RM22LG11MTimmunity to microbreaks | ~ 90, -- 100
RM22LG11MTinput frequency | 1 for LS 2.2 for St 4.7 for HS ¦ ,Maximum cable capacitance,
RM22LG11MTinput terminal | Min-Max-C ¦ ,Input terminal,
RM22LG11MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, - ¦ IEC60255-27,Supply / Output 2, - ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22LG11MTinternal input resistance | - ¦ ,Internal input resistance,
RM22LG11MTlocal signalling | - ¦ ,Power supply availability, - ¦ ,Power supply not availability, - ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, - ¦ ,Range Setting Changes,
RM22LG11MTmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22LG11MTmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22LG11MTmaximum measuring cycle | Maximum measuring cycles,
RM22LG11MTmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22LG11MTmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22LG11MTmeasurement method | Liquid level resistive probe ¦ ,Measurement method,
RM22LG11MTmeasurement range | 5kW…100kW ¦ ,1 level - Fill operation, 5kW…100kW ¦ ,1 level - Empty operation, 5kW…100kW ¦ ,2 level - Fill operation, 5kW…100kW ¦ ,2 level - Empty operation,
RM22LG11MTmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22LG11MTminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22LG11MTmonitoring functions | - governed by response time - status reflects to both R1 & R2 ¦ ,1 level - Fill operation, - governed by response time - status reflects to both R1 & R2 ¦ ,1 level - Empty operation, - governed by response time - status reflects to both R1 & R2 ¦ ,2 level - Fill operation, - governed by response time - status reflects to both R1 & R2 ¦ ,2 level - Empty operation,
RM22LG11MTmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22LG11MTmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22LG11MTnet weight | 100
RM22LG11MTon-load factor | 1
RM22LG11MToutput logic | Energized on fault-free ¦ ,R1 (11-12-14), - ¦ ,R2 (21-22-24),
RM22LG11MToutput terminal | 11/12/14,
RM22LG11MToutput type | 1 x C/O relay contacts
RM22LG11MTovervoltage category | 3 ¦ IEC60664-1
RM22LG11MTpolarity
RM22LG11MTpollution degree | 3 ¦ IEC60664-1
RM22LG11MTpower consumption | ~ 10VA ~ 8VA
RM22LG11MTpower on delay | 0
RM22LG11MTproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22LG11MTrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22LG11MTrelease of input voltage | -
RM22LG11MTrepeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22LG11MTrepeat accuracy of time delay | +/- 2%
RM22LG11MTreset time | 0
RM22LG11MTresponse time | 0
RM22LG11MTsafety reliability data | 1,100,000 hours ¦ ,MTTF, 120,000 hours ¦ ,B10,
RM22LG11MTseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22LG11MTsetting accuracy of the switching threshold | +/- 10% of full scale value ¦ ,Setting accuracy,
RM22LG11MTsetting accuracy of time delay | +/- 10% of full scales
RM22LG11MTshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22LG11MTshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22LG11MTstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22LG11MTstatus LED | R (Amber)
RM22LG11MTsupply frequency | 50 / 60 45…66
RM22LG11MTsupply terminal | A1-A2
RM22LG11MTsupply voltage limits | ~323…456.5
RM22LG11MTswitching threshold drift | < 1% over whole range ¦ ,Measurement error with supply voltage variation, 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22LG11MTthermal current | 8A ¦ IEC60947-5-1
RM22LG11MTtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22LG11MTtime delay drift | < 1 < 0.05
RM22LG11MTtime delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22LG11MTtime delay type | - ¦ ,"OFF" delay, Yes ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22LG11MTtripping threshold | Adjustable 5%...100% of 100kW ¦ ,1 level - Fill operation, Adjustable 5%...100% of 100kW ¦ ,1 level - Empty operation, Adjustable 5%...100% of 100kW ¦ ,2 level - Fill operation, Adjustable 5%...100% of 100kW ¦ ,2 level - Empty operation,
RM22LG11MTvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22LG11MTwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22TA31 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 208..240 AC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d, Drawing / Diagram
RM22TA31IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22TA31Input nominal voltage selection | 200, 208, 220, 240 ¦ ,Input nominal voltage selection,
RM22TA31Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM22TA31[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22TA31[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22TA31[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, 500V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22TA31[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22TA31[Us] rated supply voltage | ~ 3 x 200…3 x 240
RM22TA31ambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM22TA31ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22TA31bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22TA31cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM22TA31circuit group | L1, L2, L3 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22TA31connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22TA31contacts material | Cadmium free
RM22TA31depth | 73 ¦ ,Depth,
RM22TA31diagnostic button | Output will be de-energized when activated
RM22TA31dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22TA31directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22TA31duty time | 1
RM22TA31electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22TA31electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22TA31height | 90 ¦ ,Height,
RM22TA31hysteresis | All phase cut recover ¦ ,Phase cut, Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Voltage Regeneration, All phases > 175V Internal design spec: All phases >163V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: All phases <287V +/- 5% ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM22TA31immunity to microbreaks | 0
RM22TA31input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
RM22TA31input terminal | L1-L2-L3 ¦ ,Input terminal,
RM22TA31insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22TA31internal input resistance | - ¦ ,Internal input resistance,
RM22TA31local signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes, Def - Permanent OFF ¦ ,Phase Cut, Def - Permanent ON ¦ ,Phase Sequence Swap, - ¦ ,Undervoltage <U, - ¦ ,Overvoltage >U, Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Phase Asymmetry, Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Voltage Regeneration, Def - Permanent OFF ¦ ,Extreme Undervoltage <U (Phase loss), Def - Permanent ON ¦ ,Extreme Overvoltage >U, Def - Permanent OFF ¦ ,Extreme Phase Asymmetry,
RM22TA31marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TA31maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22TA31maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM22TA31maximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22TA31maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22TA31measurement method | True RMS ¦ ,Measurement method,
RM22TA31measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , +5…+15 % in the ranges 3 x ~ 200…240 ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, - ¦ ,Extreme undervoltage, - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM22TA31mechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22TA31minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22TA31monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost , governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , governed by time delay, status reflects to both R1 & R2 ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, governed by time delay, status reflects to both R1 & R2 ¦ ,Voltage Regeneration, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM22TA31mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22TA31mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22TA31net weight | 95
RM22TA31on-load factor | 1
RM22TA31output logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22TA31output terminal | 15-16-18, 25-26-28
RM22TA31output type | 2 x C/O relay contacts
RM22TA31overvoltage category | 3 ¦ IEC60664-1
RM22TA31permissible input overload | - ¦ ,permissible input overload,
RM22TA31polarity | -
RM22TA31pollution degree | 3 ¦ IEC60664-1
RM22TA31power consumption | 10VA
RM22TA31power on delay | 0
RM22TA31product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TA31relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM22TA31release of input voltage | -
RM22TA31repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22TA31repeat accuracy of time delay | +/- 3%
RM22TA31reset time | 0
RM22TA31response time | 0
RM22TA31safety reliability data | 3,400,000 hours ¦ ,MTTF, 350,000 hours ¦ ,B10,
RM22TA31seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22TA31setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM22TA31setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM22TA31shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22TA31short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22TA31standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22TA31status LED | Dial pointer (Green) R (Amber) Def (Red)
RM22TA31supply frequency | 50 / 60 45…66
RM22TA31supply terminal | L1-L3
RM22TA31supply voltage limits | ~ 3 x 160…3 x 288
RM22TA31switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation, < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22TA31thermal current | 8A ¦ IEC60947-5-1
RM22TA31tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM22TA31time delay drift | < 1 < 0.05
RM22TA31time delay range | Adjustable 0.1…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22TA31time delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22TA31tripping threshold | 1 or more phase cut ¦ ,Phase cut, Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , Adjustable 5%...15% of selected Un ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, 1 or more phase < 70% of selected Un Internal design spec: 30% +/- 5% ¦ ,Voltage Regeneration, 1 or more phase < 150V Internal design spec: 1 or more phase <160V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: 297V +/- 5% ¦ ,Extreme Overvoltage, Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM22TA31vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22TA31width | 22.5 ¦ ,Width,
RM22TA33 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 380..480 AC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d, Drawing / Diagram
RM22TA33IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22TA33Input nominal voltage selection | 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM22TA33Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM22TA33[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22TA33[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22TA33[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, 500V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22TA33[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22TA33[Us] rated supply voltage | ~ 3 x 380… 3 x 480
RM22TA33ambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM22TA33ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22TA33bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22TA33cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM22TA33circuit group | L1, L2, L3 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22TA33connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22TA33contacts material | Cadmium free
RM22TA33depth | 73 ¦ ,Depth,
RM22TA33diagnostic button | Output will be de-energized when activated
RM22TA33dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22TA33directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22TA33duty time | 1
RM22TA33electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22TA33electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22TA33height | 90 ¦ ,Height,
RM22TA33hysteresis | All phase cut recover ¦ ,Phase cut, Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Voltage Regeneration, All phases > 315V Internal design spec: All phases >296V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: All phases <583V +/- 5% ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM22TA33immunity to microbreaks | 0
RM22TA33input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
RM22TA33input terminal | L1-L2-L3 ¦ ,Input terminal,
RM22TA33insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22TA33internal input resistance | - ¦ ,Internal input resistance,
RM22TA33local signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes, Def - Permanent OFF ¦ ,Phase Cut, Def - Permanent ON ¦ ,Phase Sequence Swap, - ¦ ,Undervoltage <U, - ¦ ,Overvoltage >U, Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Phase Asymmetry, Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Voltage Regeneration, Def - Permanent OFF ¦ ,Extreme Undervoltage <U (Phase loss), Def - Permanent ON ¦ ,Extreme Overvoltage >U, Def - Permanent OFF ¦ ,Extreme Phase Asymmetry,
RM22TA33marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TA33maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22TA33maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM22TA33maximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22TA33maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22TA33measurement method | True RMS ¦ ,Measurement method,
RM22TA33measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , +5…+15 % in the ranges 3 x ~ 380…480 ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, - ¦ ,Extreme undervoltage, - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM22TA33mechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22TA33minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22TA33monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost , governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , governed by time delay, status reflects to both R1 & R2 ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, governed by time delay, status reflects to both R1 & R2 ¦ ,Voltage Regeneration, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM22TA33mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22TA33mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22TA33net weight | 95
RM22TA33on-load factor | 1
RM22TA33output logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22TA33output terminal | 15-16-18, 25-26-28
RM22TA33output type | 2 x C/O relay contacts
RM22TA33overvoltage category | 3 ¦ IEC60664-1
RM22TA33permissible input overload | - ¦ ,permissible input overload,
RM22TA33polarity | -
RM22TA33pollution degree | 3 ¦ IEC60664-1
RM22TA33power consumption | 15VA
RM22TA33power on delay | 0
RM22TA33product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TA33relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM22TA33release of input voltage | -
RM22TA33repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22TA33repeat accuracy of time delay | +/- 3%
RM22TA33reset time | 0
RM22TA33response time | 0
RM22TA33safety reliability data | 3,400,000 hours ¦ ,MTTF, 350,000 hours ¦ ,B10,
RM22TA33seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22TA33setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM22TA33setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM22TA33shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22TA33short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22TA33standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22TA33status LED | Dial pointer (Green) R (Amber) Def (Red)
RM22TA33supply frequency | 50 / 60 45…66
RM22TA33supply terminal | L1-L3
RM22TA33supply voltage limits | ~ 3 x 304…3 x 576
RM22TA33switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation, < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22TA33thermal current | 8A ¦ IEC60947-5-1
RM22TA33tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM22TA33time delay drift | < 1 < 0.05
RM22TA33time delay range | Adjustable 0.1…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22TA33time delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22TA33tripping threshold | 1 or more phase cut ¦ ,Phase cut, Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , Adjustable 5%...15% of selected Un ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, 1 or more phase < 70% of selected Un Internal design spec: 30% +/- 5% ¦ ,Voltage Regeneration, 1 or more phase < 250V Internal design spec: 1 or more phase <290V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: 593V +/- 5% ¦ ,Extreme Overvoltage, Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM22TA33vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22TA33width | 22.5 ¦ ,Width,
RM22TG20 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 208..480 AC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, No 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d, Drawing / Diagram
RM22TG20IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22TG20Input nominal voltage selection | - ¦ ,Input nominal voltage selection,
RM22TG20Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM22TG20[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22TG20[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22TG20[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, 500V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22TG20[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22TG20[Us] rated supply voltage | ~ 3 x 208…3 x 480
RM22TG20ambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM22TG20ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22TG20bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22TG20cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM22TG20circuit group | L1, L2, L3 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22TG20connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22TG20contacts material | Cadmium free
RM22TG20depth | 73 ¦ ,Depth,
RM22TG20diagnostic button | Output will be de-energized when activated
RM22TG20dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22TG20directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22TG20duty time | 1
RM22TG20electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22TG20electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22TG20height | 90 ¦ ,Height,
RM22TG20hysteresis | All phase cut recover ¦ ,Phase cut, Total phase swap recover Internal design spec: L31 lag L21 >= 15o or L31 lag L21 <= 135o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, All phases > 183V Internal design spec: All phases >153V +/- 10% ¦ ,Extreme undervoltage (Phase loss), - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM22TG20immunity to microbreaks | 0
RM22TG20input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
RM22TG20input terminal | L1-L2-L3 ¦ ,Input terminal,
RM22TG20insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22TG20internal input resistance | - ¦ ,Internal input resistance,
RM22TG20local signalling | Un - ON ¦ ,Power supply availability, Un - OFF ¦ ,Power supply not availability, - ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, - ¦ ,Range Setting Changes, - ¦ ,Phase Cut, - ¦ ,Phase Sequence Swap, - ¦ ,Undervoltage <U, - ¦ ,Overvoltage >U, - ¦ ,Phase Asymmetry, - ¦ ,Voltage Regeneration, - ¦ ,Extreme Undervoltage <U (Phase loss), - ¦ ,Extreme Overvoltage >U, - ¦ ,Extreme Phase Asymmetry,
RM22TG20marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TG20maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22TG20maximum measuring cycle | - ¦ ,Maximum measuring cycles,
RM22TG20maximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22TG20maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22TG20measurement method | Non True RMS ¦ ,Measurement method,
RM22TG20measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, - ¦ ,Extreme undervoltage, - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM22TG20mechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22TG20minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22TG20monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost , governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage, - ¦ ,Extreme overvoltage, - ¦ ,Extreme asymmetry,
RM22TG20mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22TG20mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22TG20net weight | 95
RM22TG20on-load factor | 1
RM22TG20output logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22TG20output terminal | 15-16-18, 25-26-28
RM22TG20output type | 2 x C/O relay contacts
RM22TG20overvoltage category | 3 ¦ IEC60664-1
RM22TG20permissible input overload | - ¦ ,permissible input overload,
RM22TG20polarity | -
RM22TG20pollution degree | 3 ¦ IEC60664-1
RM22TG20power consumption | 18VA @ 480VAC, 60Hz 12VA @ 400VAC, 50Hz
RM22TG20power on delay | 0
RM22TG20product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TG20relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM22TG20release of input voltage | -
RM22TG20repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22TG20repeat accuracy of time delay | -
RM22TG20reset time | 0
RM22TG20response time | 0
RM22TG20safety reliability data | 8,100,000 hours ¦ ,MTTF, 850,000 hours ¦ ,B10,
RM22TG20seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22TG20setting accuracy of the switching threshold | - ¦ ,Setting accuracy,
RM22TG20setting accuracy of time delay | -
RM22TG20shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22TG20short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22TG20standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22TG20status LED | Un (Green) R (Amber)
RM22TG20supply frequency | 50 / 60 45…66
RM22TG20supply terminal | L1-L3
RM22TG20supply voltage limits | ~ 3 x 183…3 x 528
RM22TG20switching threshold drift | - ¦ ,Measurement error with supply voltage variation, - ¦ ,Measurement error with temperature variation,
RM22TG20thermal current | 8A ¦ IEC60947-5-1
RM22TG20tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM22TG20time delay drift | - -
RM22TG20time delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22TG20time delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22TG20tripping threshold | 1 or more phase cut ¦ ,Phase cut, Total swap of phase Internal design spec: L31 lag L21 =< 10o or L31 lag L21 >= 150o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, 2 or more phase < 100V Internal design spec: 2 or more phase <150V +/- 10% ¦ ,Extreme undervoltage (Phase loss), - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM22TG20vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22TG20width | 22.5 ¦ ,Width,
RM22TR31 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 208..240 AC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d, Drawing / Diagram
RM22TR31IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22TR31Input nominal voltage selection | 200, 208, 220, 240 ¦ ,Input nominal voltage selection,
RM22TR31Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM22TR31[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22TR31[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22TR31[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, 500V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22TR31[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22TR31[Us] rated supply voltage | ~ 3 x 200…3 x 240
RM22TR31ambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM22TR31ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22TR31bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22TR31cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM22TR31circuit group | L1, L2, L3 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22TR31connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22TR31contacts material | Cadmium free
RM22TR31depth | 73 ¦ ,Depth,
RM22TR31diagnostic button | Output will be de-energized when activated
RM22TR31dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22TR31directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22TR31duty time | 1
RM22TR31electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22TR31electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22TR31height | 90 ¦ ,Height,
RM22TR31hysteresis | All phase cut recover ¦ ,Phase cut, Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Over voltage, Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, All phases > 175V Internal design spec: All phases >163V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: All phases <287V +/- 5% ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM22TR31immunity to microbreaks | 0
RM22TR31input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
RM22TR31input terminal | L1-L2-L3 ¦ ,Input terminal,
RM22TR31insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22TR31internal input resistance | - ¦ ,Internal input resistance,
RM22TR31local signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes, Def - Permanent OFF ¦ ,Phase Cut, Def - Permanent ON ¦ ,Phase Sequence Swap, Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Undervoltage <U, Def - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Overvoltage >U, - ¦ ,Phase Asymmetry, - ¦ ,Voltage Regeneration, Def - Permanent OFF ¦ ,Extreme Undervoltage <U (Phase loss), Def - Permanent ON ¦ ,Extreme Overvoltage >U, - ¦ ,Extreme Phase Asymmetry,
RM22TR31marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TR31maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22TR31maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM22TR31maximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22TR31maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22TR31measurement method | True RMS ¦ ,Measurement method,
RM22TR31measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), +2…+20 % in the ranges 3 x ~200…240 ¦ ,Over voltage, -2…-20 % in the ranges 3 x ~ 200…240 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, - ¦ ,Extreme undervoltage, - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM22TR31mechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22TR31minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22TR31monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost , governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence, governed by time delay, status reflects to both R1 & R2 ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM22TR31mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22TR31mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22TR31net weight | 95
RM22TR31on-load factor | 1
RM22TR31output logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22TR31output terminal | 15-16-18, 25-26-28
RM22TR31output type | 2 x C/O relay contacts
RM22TR31overvoltage category | 3 ¦ IEC60664-1
RM22TR31permissible input overload | - ¦ ,permissible input overload,
RM22TR31polarity | -
RM22TR31pollution degree | 3 ¦ IEC60664-1
RM22TR31power consumption | 10VA @ 240VAC, 60Hz
RM22TR31power on delay | 0
RM22TR31product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TR31relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM22TR31release of input voltage | -
RM22TR31repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22TR31repeat accuracy of time delay | +/- 3%
RM22TR31reset time | 0
RM22TR31response time | 0
RM22TR31safety reliability data | 3,400,000 hours ¦ ,MTTF, 350,000 hours ¦ ,B10,
RM22TR31seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22TR31setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM22TR31setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM22TR31shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22TR31short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22TR31standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22TR31status LED | Dial pointer (Green) R (Amber) Def (Red)
RM22TR31supply frequency | 50 / 60 45…66
RM22TR31supply terminal | L1-L3
RM22TR31supply voltage limits | ~ 3 x 160…3 x 288
RM22TR31switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation, < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22TR31thermal current | 8A ¦ IEC60947-5-1
RM22TR31tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM22TR31time delay drift | < 1 < 0.05
RM22TR31time delay range | Adjustable 0.1…30 ¦ ,"OFF" delay, Adjustable 0.1…30 ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22TR31time delay type | Yes ¦ ,"OFF" delay, Yes ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22TR31tripping threshold | 1 or more phase cut ¦ ,Phase cut, Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Adjustable 2%...20% of selected Un ¦ ,Over voltage, Adjustable 2%...20% of selected Un ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, 1 or more phase < 150V Internal design spec: 1 or more phase <160V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: 297V +/- 5% ¦ ,Extreme Overvoltage, Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM22TR31vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22TR31width | 22.5 ¦ ,Width,
RM22TR33 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 380..480 AC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d, Drawing / Diagram
RM22TR33IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22TR33Input nominal voltage selection | 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM22TR33Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM22TR33[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22TR33[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22TR33[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, 500V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22TR33[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22TR33[Us] rated supply voltage | ~ 3 x 380… 3 x 480
RM22TR33ambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM22TR33ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22TR33bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22TR33cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM22TR33circuit group | L1, L2, L3 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22TR33connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22TR33contacts material | Cadmium free
RM22TR33depth | 73 ¦ ,Depth,
RM22TR33diagnostic button | Output will be de-energized when activated
RM22TR33dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22TR33directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22TR33duty time | 1
RM22TR33electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22TR33electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22TR33height | 90 ¦ ,Height,
RM22TR33hysteresis | All phase cut recover ¦ ,Phase cut, Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Over voltage, Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, All phases > 315V Internal design spec: All phases >296V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: All phases <583V +/- 5% ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM22TR33immunity to microbreaks | 0
RM22TR33input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
RM22TR33input terminal | L1-L2-L3 ¦ ,Input terminal,
RM22TR33insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22TR33internal input resistance | - ¦ ,Internal input resistance,
RM22TR33local signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes, Def - Permanent OFF ¦ ,Phase Cut, Def - Permanent ON ¦ ,Phase Sequence Swap, Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Undervoltage <U, Def - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Overvoltage >U, - ¦ ,Phase Asymmetry, - ¦ ,Voltage Regeneration, Def - Permanent OFF ¦ ,Extreme Undervoltage <U (Phase loss), Def - Permanent ON ¦ ,Extreme Overvoltage >U, - ¦ ,Extreme Phase Asymmetry,
RM22TR33marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TR33maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22TR33maximum measuring cycle | 170ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM22TR33maximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22TR33maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22TR33measurement method | True RMS ¦ ,Measurement method,
RM22TR33measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), +2…+20 % in the ranges 3 x 380…480 ¦ ,Over voltage, -2…-20 % in the ranges 3 x 380…480 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, - ¦ ,Extreme undervoltage, - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM22TR33mechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22TR33minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22TR33monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost , governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence, governed by time delay, status reflects to both R1 & R2 ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM22TR33mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22TR33mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22TR33net weight | 95
RM22TR33on-load factor | 1
RM22TR33output logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22TR33output terminal | 15-16-18, 25-26-28
RM22TR33output type | 2 x C/O relay contacts
RM22TR33overvoltage category | 3 ¦ IEC60664-1
RM22TR33permissible input overload | - ¦ ,permissible input overload,
RM22TR33polarity | -
RM22TR33pollution degree | 3 ¦ IEC60664-1
RM22TR33power consumption | 18VA @ 480VAC, 60Hz 12VA @ 400VAC, 50Hz
RM22TR33power on delay | 0
RM22TR33product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TR33relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM22TR33release of input voltage | -
RM22TR33repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22TR33repeat accuracy of time delay | +/- 3%
RM22TR33reset time | 0
RM22TR33response time | 0
RM22TR33safety reliability data | 3,400,000 hours ¦ ,MTTF, 350,000 hours ¦ ,B10,
RM22TR33seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22TR33setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM22TR33setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM22TR33shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22TR33short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22TR33standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22TR33status LED | Dial pointer (Green) R (Amber) Def (Red)
RM22TR33supply frequency | 50 / 60 45…66
RM22TR33supply terminal | L1-L3
RM22TR33supply voltage limits | ~ 3 x 304…3 x 576
RM22TR33switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation, < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22TR33thermal current | 8A ¦ IEC60947-5-1
RM22TR33tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM22TR33time delay drift | < 1 < 0.05
RM22TR33time delay range | Adjustable 0.1…30 ¦ ,"OFF" delay, Adjustable 0.1…30 ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22TR33time delay type | Yes ¦ ,"OFF" delay, Yes ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22TR33tripping threshold | 1 or more phase cut ¦ ,Phase cut, Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Adjustable 2%...20% of selected Un ¦ ,Over voltage, Adjustable 2%...20% of selected Un ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, 1 or more phase < 250V Internal design spec: 1 or more phase <290V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: 593V +/- 5% ¦ ,Extreme Overvoltage, Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM22TR33vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22TR33width | 22.5 ¦ ,Width,
RM22TU21 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 208..240 AC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d, Drawing / Diagram
RM22TU21IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22TU21Input nominal voltage selection | 200, 208, 220, 240 ¦ ,Input nominal voltage selection,
RM22TU21Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM22TU21[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22TU21[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22TU21[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, 500V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22TU21[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22TU21[Us] rated supply voltage | ~ 3 x 200…3 x 240
RM22TU21ambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM22TU21ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22TU21bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22TU21cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM22TU21circuit group | L1, L2, L3 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22TU21connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22TU21contacts material | Cadmium free
RM22TU21depth | 73 ¦ ,Depth,
RM22TU21diagnostic button | Output will be de-energized when activated
RM22TU21dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22TU21directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22TU21duty time | 1
RM22TU21electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22TU21electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22TU21height | 90 ¦ ,Height,
RM22TU21hysteresis | All phase cut recover ¦ ,Phase cut, Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, All phases > 175V Internal design spec: All phases >163V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: All phases <287V +/- 5% ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM22TU21immunity to microbreaks | 0
RM22TU21input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
RM22TU21input terminal | L1-L2-L3 ¦ ,Input terminal,
RM22TU21insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22TU21internal input resistance | - ¦ ,Internal input resistance,
RM22TU21local signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes, Def - Permanent OFF ¦ ,Phase Cut, Def - Permanent ON ¦ ,Phase Sequence Swap, Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Undervoltage <U, - ¦ ,Overvoltage >U, - ¦ ,Phase Asymmetry, - ¦ ,Voltage Regeneration, Def - Permanent OFF ¦ ,Extreme Undervoltage <U (Phase loss), Def - Permanent ON ¦ ,Extreme Overvoltage >U, - ¦ ,Extreme Phase Asymmetry,
RM22TU21marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TU21maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22TU21maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM22TU21maximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22TU21maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22TU21measurement method | True RMS ¦ ,Measurement method,
RM22TU21measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, -2…-20 % in the ranges 3 x ~ 200…240 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, - ¦ ,Extreme undervoltage, - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM22TU21mechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22TU21minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22TU21monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost , governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, governed by time delay, status reflects to both R1 & R2 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM22TU21mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22TU21mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22TU21net weight | 95
RM22TU21on-load factor | 1
RM22TU21output logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22TU21output terminal | 15-16-18, 25-26-28
RM22TU21output type | 2 x C/O relay contacts
RM22TU21overvoltage category | 3 ¦ IEC60664-1
RM22TU21permissible input overload | - ¦ ,permissible input overload,
RM22TU21polarity | -
RM22TU21pollution degree | 3 ¦ IEC60664-1
RM22TU21power consumption | 10VA
RM22TU21power on delay | 0
RM22TU21product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TU21relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM22TU21release of input voltage | -
RM22TU21repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22TU21repeat accuracy of time delay | -
RM22TU21reset time | 0
RM22TU21response time | 0
RM22TU21safety reliability data | 3,400,000 hours ¦ ,MTTF, 350,000 hours ¦ ,B10,
RM22TU21seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22TU21setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM22TU21setting accuracy of time delay | -
RM22TU21shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22TU21short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22TU21standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22TU21status LED | Dial pointer (Green) R (Amber) Def (Red)
RM22TU21supply frequency | 50 / 60 45…66
RM22TU21supply terminal | L1-L3
RM22TU21supply voltage limits | ~ 3 x 160…3 x 288
RM22TU21switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation, < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22TU21thermal current | 8A ¦ IEC60947-5-1
RM22TU21tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM22TU21time delay drift | - -
RM22TU21time delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22TU21time delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22TU21tripping threshold | 1 or more phase cut ¦ ,Phase cut, Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, Adjustable 2%...20% of selected Un ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, 1 or more phase < 150V Internal design spec: 1 or more phase <160V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: 297V +/- 5% ¦ ,Extreme Overvoltage, Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM22TU21vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22TU21width | 22.5 ¦ ,Width,
RM22TU23 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 380..480 AC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d, Drawing / Diagram
RM22TU23IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22TU23Input nominal voltage selection | 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM22TU23Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM22TU23[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22TU23[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22TU23[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, 500V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22TU23[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22TU23[Us] rated supply voltage | ~ 3 x 380… 3 x 480
RM22TU23ambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM22TU23ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22TU23bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22TU23cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM22TU23circuit group | L1, L2, L3 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22TU23connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22TU23contacts material | Cadmium free
RM22TU23depth | 73 ¦ ,Depth,
RM22TU23diagnostic button | Output will be de-energized when activated
RM22TU23dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22TU23directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22TU23duty time | 1
RM22TU23electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22TU23electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22TU23height | 90 ¦ ,Height,
RM22TU23hysteresis | All phase cut recover ¦ ,Phase cut, Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, All phases > 315V Internal design spec: All phases >296V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: All phases <583V +/- 5% ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM22TU23immunity to microbreaks | 0
RM22TU23input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
RM22TU23input terminal | L1-L2-L3 ¦ ,Input terminal,
RM22TU23insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22TU23internal input resistance | - ¦ ,Internal input resistance,
RM22TU23local signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes, Def - Permanent OFF ¦ ,Phase Cut, Def - Permanent ON ¦ ,Phase Sequence Swap, Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Undervoltage <U, - ¦ ,Overvoltage >U, - ¦ ,Phase Asymmetry, - ¦ ,Voltage Regeneration, Def - Permanent OFF ¦ ,Extreme Undervoltage <U (Phase loss), Def - Permanent ON ¦ ,Extreme Overvoltage >U, - ¦ ,Extreme Phase Asymmetry,
RM22TU23marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TU23maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22TU23maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM22TU23maximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22TU23maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22TU23measurement method | True RMS ¦ ,Measurement method,
RM22TU23measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, -2…-20 % in the ranges 3 x 380…480 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, - ¦ ,Extreme undervoltage, - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM22TU23mechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22TU23minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22TU23monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost , governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, governed by time delay, status reflects to both R1 & R2 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM22TU23mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22TU23mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22TU23net weight | 95
RM22TU23on-load factor | 1
RM22TU23output logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22TU23output terminal | 15-16-18, 25-26-28
RM22TU23output type | 2 x C/O relay contacts
RM22TU23overvoltage category | 3 ¦ IEC60664-1
RM22TU23permissible input overload | - ¦ ,permissible input overload,
RM22TU23polarity | -
RM22TU23pollution degree | 3 ¦ IEC60664-1
RM22TU23power consumption | 15VA
RM22TU23power on delay | 0
RM22TU23product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22TU23relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM22TU23release of input voltage | -
RM22TU23repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM22TU23repeat accuracy of time delay | -
RM22TU23reset time | 0
RM22TU23response time | 0
RM22TU23safety reliability data | 3,400,000 hours ¦ ,MTTF, 350,000 hours ¦ ,B10,
RM22TU23seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22TU23setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM22TU23setting accuracy of time delay | -
RM22TU23shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22TU23short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22TU23standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22TU23status LED | Dial pointer (Green) R (Amber) Def (Red)
RM22TU23supply frequency | 50 / 60 45…66
RM22TU23supply terminal | L1-L3
RM22TU23supply voltage limits | ~ 3 x 304…3 x 576
RM22TU23switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation, < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM22TU23thermal current | 8A ¦ IEC60947-5-1
RM22TU23tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM22TU23time delay drift | - -
RM22TU23time delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22TU23time delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22TU23tripping threshold | 1 or more phase cut ¦ ,Phase cut, Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, Adjustable 2%...20% of selected Un ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, 1 or more phase < 250V Internal design spec: 1 or more phase <290V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: 593V +/- 5% ¦ ,Extreme Overvoltage, Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM22TU23vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22TU23width | 22.5 ¦ ,Width,
RM22UA21MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 24…240 AC/DC ¦ ,Supply,Rated 0.05..0.5 AC/DC [full: 0.05..0.5 AC/DC] ¦ ,Input 1,Voltage 0.3..3 AC/DC [full: 0.3..3 AC/DC] ¦ ,Input 2,Spec 0.5..5 AC/DC [full: 0.5..5 AC/DC] ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, - ¦ ,Over / undervoltage (windows mode), Without memory ¦ ,Over voltage, - ¦ ,Undervoltage , ~/-- 0.05…5 5 ¦ ,E1-M / B1-C, 30 ¦ ,E2-M / B2-C, 50 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 0.05…0.5 ¦ ,E1-M / B1-C, ~/-- 0.3…3 ¦ ,E2-M / B2-C, ~/-- 0.5…5 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of 0.5V ¦ ,E1-M / B1-C, Adjustable 10%...100% of 3V ¦ ,E2-M / B2-C, Adjustable 10%...100% of 5V ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C, Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C, Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Resistive Voltage Step Down E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 100 True RMS Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22UA21MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22UA21MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22UA21MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22UA21MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22UA21MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply, 12.5 ¦ IEC60664-1,Input 1, 12.5 ¦ IEC60664-1,Input 2, 12.5 ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, 250V ¦ IEC60664-1,Supply / Input 1,Galvanic 250V ¦ IEC60664-1,Supply / Input 2,Isolated 250V ¦ IEC60664-1,Supply / Input 3,Circuit 250V ¦ IEC60664-1,Supply / Output 1, 250V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, 250V ¦ IEC60664-1,Input 1 / Output 1, 250V ¦ IEC60664-1,Input 1 / Output 2, 250V ¦ IEC60664-1,Input 2 / Output 1, 250V ¦ IEC60664-1,Input 2 / Output 2, 250V ¦ IEC60664-1,Input 3 / Output 1, 250V ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA21MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, 0.8kV, OVC3 ¦ IEC60664-1,Input 1, 0.8kV, OVC3 ¦ IEC60664-1,Input 2, 0.8kV, OVC3 ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA21MR[Us] rated supply voltage | ~/-- 24…240
RM22UA21MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22UA21MRambient air temperature for storage | -40oC..+80oC ¦ ,Storage,
RM22UA21MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22UA21MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22UA21MRcircuit group | A1, A2 ¦ ,Supply,Terminal E1, M ¦ ,Input 1, E2, M ¦ ,Input 2, E3, M ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22UA21MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UA21MRcontacts material | Cadmium free
RM22UA21MRdepth | Depth,
RM22UA21MRdiagnostic button | Output will be de-energized when activated
RM22UA21MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA21MRdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22UA21MRduty time | 1
RM22UA21MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22UA21MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UA21MRheight | Height,
RM22UA21MRimmunity to microbreaks | 10
RM22UA21MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA21MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22UA21MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA21MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UA21MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22UA21MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UA21MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22UA21MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UA21MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UA21MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22UA21MRnet weight | 110
RM22UA21MRon-load factor | 1
RM22UA21MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22UA21MRoutput terminal | 11-12-14, 21-22-24
RM22UA21MRoutput type | 2 x C/O relay contacts
RM22UA21MRovervoltage category | 3 ¦ IEC60664-1
RM22UA21MRpolarity
RM22UA21MRpollution degree | 3 ¦ IEC60664-1
RM22UA21MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM22UA21MRpower on delay | 0
RM22UA21MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA21MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22UA21MRrelease of input voltage | -
RM22UA21MRrepeat accuracy of time delay | +/- 2%
RM22UA21MRreset time | 0
RM22UA21MRresponse time | Not specified =< 300ms ¦ ,on crossing the threshold,
RM22UA21MRsafety reliability data | 2,700,000 hours ¦ ,MTTF, 290,000 hours ¦ ,B10,
RM22UA21MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22UA21MRsetting accuracy of time delay | +/- 10% of full scales
RM22UA21MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22UA21MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22UA21MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22UA21MRstatus LED | Dial pointer (Green) R (Amber)
RM22UA21MRsupply frequency | 50 / 60 45…66
RM22UA21MRsupply terminal | A1-A2
RM22UA21MRsupply voltage limits | ~/-- 20.4…264
RM22UA21MRthermal current | 8A ¦ IEC60947-5-1
RM22UA21MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22UA21MRtime delay drift | < 1 < 0.05
RM22UA21MRtime delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UA21MRtime delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UA21MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22UA21MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22UA22MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 24…240 AC/DC ¦ ,Supply,Rated 1..10 AC/DC [full: 1..10 AC/DC] ¦ ,Input 1,Voltage 5..50 AC/DC [full: 5..50 AC/DC] ¦ ,Input 2,Spec 10..100 AC/DC [full: 10..100 AC/DC] ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, - ¦ ,Over / undervoltage (windows mode), Without memory ¦ ,Over voltage, - ¦ ,Undervoltage , ~/-- 1…100 22 ¦ ,E1-M / B1-C, 110 ¦ ,E2-M / B2-C, 220 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 1…10 ¦ ,E1-M / B1-C, ~/-- 5…50 ¦ ,E2-M / B2-C, ~/-- 10…100 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of 10V ¦ ,E1-M / B1-C, Adjustable 10%...100% of 50V ¦ ,E2-M / B2-C, Adjustable 10%...100% of 100V ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C, Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C, Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Resistive Voltage Step Down E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 100 True RMS Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22UA22MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22UA22MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22UA22MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22UA22MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22UA22MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply, 12.5 ¦ IEC60664-1,Input 1, 50 ¦ IEC60664-1,Input 2, 100 ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, 250V ¦ IEC60664-1,Supply / Input 1,Galvanic 250V ¦ IEC60664-1,Supply / Input 2,Isolated 250V ¦ IEC60664-1,Supply / Input 3,Circuit 250V ¦ IEC60664-1,Supply / Output 1, 250V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, 250V ¦ IEC60664-1,Input 1 / Output 1, 250V ¦ IEC60664-1,Input 1 / Output 2, 250V ¦ IEC60664-1,Input 2 / Output 1, 250V ¦ IEC60664-1,Input 2 / Output 2, 250V ¦ IEC60664-1,Input 3 / Output 1, 250V ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA22MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, 0.8kV, OVC3 ¦ IEC60664-1,Input 1, 0.8kV, OVC3 ¦ IEC60664-1,Input 2, 1.5kV, OVC3 ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA22MR[Us] rated supply voltage | ~/-- 24…240
RM22UA22MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22UA22MRambient air temperature for storage | -40oC..+80oC ¦ ,Storage,
RM22UA22MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22UA22MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22UA22MRcircuit group | A1, A2 ¦ ,Supply,Terminal E1, M ¦ ,Input 1, E2, M ¦ ,Input 2, E3, M ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22UA22MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UA22MRcontacts material | Cadmium free
RM22UA22MRdepth | Depth,
RM22UA22MRdiagnostic button | Output will be de-energized when activated
RM22UA22MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA22MRdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22UA22MRduty time | 1
RM22UA22MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22UA22MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UA22MRheight | Height,
RM22UA22MRimmunity to microbreaks | 10
RM22UA22MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA22MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22UA22MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA22MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UA22MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22UA22MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UA22MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22UA22MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UA22MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UA22MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22UA22MRnet weight | 110
RM22UA22MRon-load factor | 1
RM22UA22MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22UA22MRoutput terminal | 11-12-14, 21-22-24
RM22UA22MRoutput type | 2 x C/O relay contacts
RM22UA22MRovervoltage category | 3 ¦ IEC60664-1
RM22UA22MRpolarity
RM22UA22MRpollution degree | 3 ¦ IEC60664-1
RM22UA22MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM22UA22MRpower on delay | 0
RM22UA22MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA22MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22UA22MRrelease of input voltage | -
RM22UA22MRrepeat accuracy of time delay | +/- 2%
RM22UA22MRreset time | 0
RM22UA22MRresponse time | Not specified =< 300ms ¦ ,on crossing the threshold,
RM22UA22MRsafety reliability data | 2,700,000 hours ¦ ,MTTF, 290,000 hours ¦ ,B10,
RM22UA22MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22UA22MRsetting accuracy of time delay | +/- 10% of full scales
RM22UA22MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22UA22MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22UA22MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22UA22MRstatus LED | Dial pointer (Green) R (Amber)
RM22UA22MRsupply frequency | 50 / 60 45…66
RM22UA22MRsupply terminal | A1-A2
RM22UA22MRsupply voltage limits | ~/-- 20.4…264
RM22UA22MRthermal current | 8A ¦ IEC60947-5-1
RM22UA22MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22UA22MRtime delay drift | < 1 < 0.05
RM22UA22MRtime delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UA22MRtime delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UA22MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22UA22MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22UA23MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 24…240 AC/DC ¦ ,Supply,Rated 18..125 AC/DC [full: 15..150 AC/DC] ¦ ,Input 1,Voltage 37..250 AC/DC [full: 30..300 AC/DC] ¦ ,Input 2,Spec 75..440 AC/DC [full: 50..500 AC/DC] ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, - ¦ ,Over / undervoltage (windows mode), Without memory ¦ ,Over voltage, - ¦ ,Undervoltage , ~/-- 15…500 150 ¦ ,E1-M / B1-C, 300 ¦ ,E2-M / B2-C, 500 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 15…150 ¦ ,E1-M / B1-C, ~/-- 30…300 ¦ ,E2-M / B2-C, ~/-- 50…500 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of 150V ¦ ,E1-M / B1-C, Adjustable 10%...100% of 300V ¦ ,E2-M / B2-C, Adjustable 10%...100% of 500V ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C, Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C, Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Resistive Voltage Step Down E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 100 True RMS Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22UA23MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22UA23MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22UA23MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22UA23MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22UA23MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply, 125V ¦ IEC60664-1,Input 1, 250V ¦ IEC60664-1,Input 2, 500V ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, 250V ¦ IEC60664-1,Supply / Input 1,Galvanic 250V ¦ IEC60664-1,Supply / Input 2,Isolated 500V ¦ IEC60664-1,Supply / Input 3,Circuit 250V ¦ IEC60664-1,Supply / Output 1, 250V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, 250V ¦ IEC60664-1,Input 1 / Output 1, 250V ¦ IEC60664-1,Input 1 / Output 2, 250V ¦ IEC60664-1,Input 2 / Output 1, 250V ¦ IEC60664-1,Input 2 / Output 2, 500V ¦ IEC60664-1,Input 3 / Output 1, 500V ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA23MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, 2.5kV, OVC3 ¦ IEC60664-1,Input 1, 4kV, OVC3 ¦ IEC60664-1,Input 2, 4kV, OVC3 ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA23MR[Us] rated supply voltage | ~/-- 24…240
RM22UA23MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22UA23MRambient air temperature for storage | -40oC..+80oC ¦ ,Storage,
RM22UA23MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22UA23MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22UA23MRcircuit group | A1, A2 ¦ ,Supply,Terminal E1, M ¦ ,Input 1, E2, M ¦ ,Input 2, E3, M ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22UA23MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UA23MRcontacts material | Cadmium free
RM22UA23MRdepth | Depth,
RM22UA23MRdiagnostic button | Output will be de-energized when activated
RM22UA23MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA23MRdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22UA23MRduty time | 1
RM22UA23MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22UA23MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UA23MRheight | Height,
RM22UA23MRimmunity to microbreaks | 10
RM22UA23MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA23MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22UA23MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA23MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UA23MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22UA23MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UA23MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22UA23MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UA23MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UA23MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22UA23MRnet weight | 110
RM22UA23MRon-load factor | 1
RM22UA23MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22UA23MRoutput terminal | 11-12-14, 21-22-24
RM22UA23MRoutput type | 2 x C/O relay contacts
RM22UA23MRovervoltage category | 3 ¦ IEC60664-1
RM22UA23MRpolarity
RM22UA23MRpollution degree | 3 ¦ IEC60664-1
RM22UA23MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM22UA23MRpower on delay | 0
RM22UA23MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA23MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22UA23MRrelease of input voltage | -
RM22UA23MRrepeat accuracy of time delay | +/- 2%
RM22UA23MRreset time | 0
RM22UA23MRresponse time | Not specified =< 300ms ¦ ,on crossing the threshold,
RM22UA23MRsafety reliability data | 2,700,000 hours ¦ ,MTTF, 290,000 hours ¦ ,B10,
RM22UA23MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22UA23MRsetting accuracy of time delay | +/- 10% of full scales
RM22UA23MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22UA23MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22UA23MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22UA23MRstatus LED | Dial pointer (Green) R (Amber)
RM22UA23MRsupply frequency | 50 / 60 45…66
RM22UA23MRsupply terminal | A1-A2
RM22UA23MRsupply voltage limits | ~/-- 20.4…264
RM22UA23MRthermal current | 8A ¦ IEC60947-5-1
RM22UA23MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22UA23MRtime delay drift | < 1 < 0.05
RM22UA23MRtime delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UA23MRtime delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UA23MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22UA23MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22UA3 (Catch Up) | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, 600 ¦ ,Supply,Rated 600 ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, - ¦ ,Over / undervoltage (windows mode), Selectable with memory / without memory ¦ ,Over voltage, Selectable with memory / without memory ¦ ,Undervoltage , ~/-- 0.05…5 RM22UA31MW: 5 RM22UA32MW: 22 RM22UA33MW: 150 ¦ ,E1-M / B1-C, RM22UA31MW: 30 RM22UA32MW: 110 RM22UA33MW: 300 ¦ ,E2-M / B2-C, RM22UA31MW: 50 RM22UA32MW: 220 RM22UA33MW: 600 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, RM22UA31MW: ~/-- 0.05…0.5 RM22UA32MW: ~/-- 1…10 RM22UA33MW: ~/-- 15…150 ¦ ,E1-M / B1-C, RM22UA31MW: ~/-- 0.5…3 RM22UA32MW: ~/-- 5…50 RM22UA33MW: ~/-- 30…300 ¦ ,E2-M / B2-C, RM22UA31MW: ~/-- 0.5…5 RM22UA32MW: ~/-- 10…100 RM22UA33MW: ~/-- 60…600 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of full range ¦ ,E1-M / B1-C, Adjustable 10%...100% of full range ¦ ,E2-M / B2-C, Adjustable 10%...100% of full range ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C, Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C, Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Resistive Voltage Step Down E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 True RMS MTTFd, B10d,
RM22UA3 (Catch Up)IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IEC60529,Front Panel,
RM22UA3 (Catch Up)Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22UA3 (Catch Up)[Ie] rated operational current | IEC61810-1,Rated switching current,
RM22UA3 (Catch Up)[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM22UA3 (Catch Up)[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, 4 ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM22UA3 (Catch Up)[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM22UA3 (Catch Up)[Us] rated supply voltage | ~/-- 24…240
RM22UA3 (Catch Up)ambient air temperature for operation | -20…+50 ¦ ,Operation,
RM22UA3 (Catch Up)ambient air temperature for storage | -40…+70 ¦ ,Storage,
RM22UA3 (Catch Up)bump resistance | IEC60068-2-29
RM22UA3 (Catch Up)cable stripping length | Not specified ¦ ,Cable stripping length,
RM22UA3 (Catch Up)circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, 600 ¦ ,Output 2,
RM22UA3 (Catch Up)connections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UA3 (Catch Up)contacts material | Cadmium-free
RM22UA3 (Catch Up)depth | Depth,
RM22UA3 (Catch Up)diagnostic button
RM22UA3 (Catch Up)dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM22UA3 (Catch Up)directives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
RM22UA3 (Catch Up)duty time | Not specified
RM22UA3 (Catch Up)electrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM22UA3 (Catch Up)electromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UA3 (Catch Up)height | Height,
RM22UA3 (Catch Up)immunity to microbreaks | 10
RM22UA3 (Catch Up)insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM22UA3 (Catch Up)local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM22UA3 (Catch Up)marking | UL, CSA, GL, C-Tick, GOST, CE
RM22UA3 (Catch Up)maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UA3 (Catch Up)maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, ~ 8 ¦ ,Maximum switching current, 2000 ¦ ,Maximum switching capacity,
RM22UA3 (Catch Up)maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UA3 (Catch Up)mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM22UA3 (Catch Up)minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UA3 (Catch Up)mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UA3 (Catch Up)mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22UA3 (Catch Up)net weight | ?
RM22UA3 (Catch Up)on-load factor
RM22UA3 (Catch Up)output logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
RM22UA3 (Catch Up)output terminal | 11-12-14, 21-22-24
RM22UA3 (Catch Up)output type | 2 x C/O relay contacts
RM22UA3 (Catch Up)overvoltage category | III ¦ IEC60664-1
RM22UA3 (Catch Up)polarity
RM22UA3 (Catch Up)pollution degree | 3 ¦ IEC60664-1
RM22UA3 (Catch Up)power consumption | ~ 3.5VA, -- 0.6W
RM22UA3 (Catch Up)power on delay | 0
RM22UA3 (Catch Up)product certifications | UL, CSA, GL, C-Tick, GOST
RM22UA3 (Catch Up)relative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM22UA3 (Catch Up)release of input voltage
RM22UA3 (Catch Up)repeat accuracy of time delay | +/- 2%
RM22UA3 (Catch Up)reset time | 0
RM22UA3 (Catch Up)response time | Not specified ¦ ,on crossing the threshold,
RM22UA3 (Catch Up)safety reliability data | MTTF, B10,
RM22UA3 (Catch Up)seismic resistance | IEC60068-3-3
RM22UA3 (Catch Up)setting accuracy of time delay | +/- 10% of full scales
RM22UA3 (Catch Up)shock resistance | 5 gn ¦ IEC60068-2-27
RM22UA3 (Catch Up)short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM22UA3 (Catch Up)standards | EN60255-6, IEC60255-6
RM22UA3 (Catch Up)status LED
RM22UA3 (Catch Up)supply frequency | 50 / 60 45…66
RM22UA3 (Catch Up)supply terminal | A1-A2
RM22UA3 (Catch Up)supply voltage limits | ~/-- 20.4…264
RM22UA3 (Catch Up)thermal current | IEC60947-5-1
RM22UA3 (Catch Up)tightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM22UA3 (Catch Up)time delay drift | Not specified Not specified
RM22UA3 (Catch Up)time delay range | Adjustable 0.3…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UA3 (Catch Up)time delay type | · ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UA3 (Catch Up)vibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM22UA3 (Catch Up)width | 22.5 x ? x ? ¦ ,Width,
RM22UA31MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 24…240 AC/DC ¦ ,Supply,Rated 0.05..0.5 AC/DC [full: 0.05..0.5 AC/DC] ¦ ,Input 1,Voltage 0.3..3 AC/DC [full: 0.3..3 AC/DC] ¦ ,Input 2,Spec 0.5..5 AC/DC [full: 0.5..5 AC/DC] ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Selectable with memory / without memory ¦ ,Over / undervoltage (windows mode), Selectable with memory / without memory ¦ ,Over voltage, Selectable with memory / without memory ¦ ,Undervoltage , ~/-- 0.05…5 5 ¦ ,E1-M / B1-C, 30 ¦ ,E2-M / B2-C, 50 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 0.05…0.5 ¦ ,E1-M / B1-C, ~/-- 0.3…3 ¦ ,E2-M / B2-C, ~/-- 0.5…5 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of 0.5V ¦ ,E1-M / B1-C, Adjustable 10%...100% of 3V ¦ ,E2-M / B2-C, Adjustable 10%...100% of 5V ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E1-M / B1-C, Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E2-M / B2-C, Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Resistive Voltage Step Down E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 100 True RMS Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22UA31MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22UA31MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22UA31MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22UA31MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22UA31MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply, 12.5 ¦ IEC60664-1,Input 1, 12.5 ¦ IEC60664-1,Input 2, 12.5 ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, 250V ¦ IEC60664-1,Supply / Input 1,Galvanic 250V ¦ IEC60664-1,Supply / Input 2,Isolated 250V ¦ IEC60664-1,Supply / Input 3,Circuit 250V ¦ IEC60664-1,Supply / Output 1, 250V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, 250V ¦ IEC60664-1,Input 1 / Output 1, 250V ¦ IEC60664-1,Input 1 / Output 2, 250V ¦ IEC60664-1,Input 2 / Output 1, 250V ¦ IEC60664-1,Input 2 / Output 2, 250V ¦ IEC60664-1,Input 3 / Output 1, 250V ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA31MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, 0.8kV, OVC3 ¦ IEC60664-1,Input 1, 0.8kV, OVC3 ¦ IEC60664-1,Input 2, 0.8kV, OVC3 ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA31MR[Us] rated supply voltage | ~/-- 24…240
RM22UA31MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22UA31MRambient air temperature for storage | -40oC..+80oC ¦ ,Storage,
RM22UA31MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22UA31MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22UA31MRcircuit group | A1, A2 ¦ ,Supply,Terminal E1, M ¦ ,Input 1, E2, M ¦ ,Input 2, E3, M ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22UA31MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UA31MRcontacts material | Cadmium free
RM22UA31MRdepth | Depth,
RM22UA31MRdiagnostic button | Output will be de-energized when activated
RM22UA31MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA31MRdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22UA31MRduty time | 1
RM22UA31MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22UA31MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UA31MRheight | Height,
RM22UA31MRimmunity to microbreaks | 10
RM22UA31MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA31MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22UA31MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA31MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UA31MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22UA31MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UA31MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22UA31MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UA31MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UA31MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22UA31MRnet weight | 110
RM22UA31MRon-load factor | 1
RM22UA31MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22UA31MRoutput terminal | 11-12-14, 21-22-24
RM22UA31MRoutput type | 2 x C/O relay contacts
RM22UA31MRovervoltage category | 3 ¦ IEC60664-1
RM22UA31MRpolarity
RM22UA31MRpollution degree | 3 ¦ IEC60664-1
RM22UA31MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM22UA31MRpower on delay | 0
RM22UA31MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA31MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22UA31MRrelease of input voltage | -
RM22UA31MRrepeat accuracy of time delay | +/- 2%
RM22UA31MRreset time | 0
RM22UA31MRresponse time | Not specified =< 300ms ¦ ,on crossing the threshold,
RM22UA31MRsafety reliability data | 2,700,000 hours ¦ ,MTTF, 290,000 hours ¦ ,B10,
RM22UA31MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22UA31MRsetting accuracy of time delay | +/- 10% of full scales
RM22UA31MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22UA31MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22UA31MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22UA31MRstatus LED | Dial pointer (Green) R (Amber)
RM22UA31MRsupply frequency | 50 / 60 45…66
RM22UA31MRsupply terminal | A1-A2
RM22UA31MRsupply voltage limits | ~/-- 20.4…264
RM22UA31MRthermal current | 8A ¦ IEC60947-5-1
RM22UA31MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22UA31MRtime delay drift | < 1 < 0.05
RM22UA31MRtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UA31MRtime delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UA31MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22UA31MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22UA32MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 24…240 AC/DC ¦ ,Supply,Rated 1..10 AC/DC [full: 1..10 AC/DC] ¦ ,Input 1,Voltage 5..50 AC/DC [full: 5..50 AC/DC] ¦ ,Input 2,Spec 10..100 AC/DC [full: 10..100 AC/DC] ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Selectable with memory / without memory ¦ ,Over / undervoltage (windows mode), Selectable with memory / without memory ¦ ,Over voltage, Selectable with memory / without memory ¦ ,Undervoltage , ~/-- 1…100 22 ¦ ,E1-M / B1-C, 110 ¦ ,E2-M / B2-C, 220 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 1…10 ¦ ,E1-M / B1-C, ~/-- 5…50 ¦ ,E2-M / B2-C, ~/-- 10…100 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of 10V ¦ ,E1-M / B1-C, Adjustable 10%...100% of 50V ¦ ,E2-M / B2-C, Adjustable 10%...100% of 100V ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E1-M / B1-C, Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E2-M / B2-C, Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Resistive Voltage Step Down E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 100 True RMS Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22UA32MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22UA32MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22UA32MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22UA32MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22UA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply, 12.5 ¦ IEC60664-1,Input 1, 50 ¦ IEC60664-1,Input 2, 100 ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, 250V ¦ IEC60664-1,Supply / Input 1,Galvanic 250V ¦ IEC60664-1,Supply / Input 2,Isolated 250V ¦ IEC60664-1,Supply / Input 3,Circuit 250V ¦ IEC60664-1,Supply / Output 1, 250V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, 250V ¦ IEC60664-1,Input 1 / Output 1, 250V ¦ IEC60664-1,Input 1 / Output 2, 250V ¦ IEC60664-1,Input 2 / Output 1, 250V ¦ IEC60664-1,Input 2 / Output 2, 250V ¦ IEC60664-1,Input 3 / Output 1, 250V ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, 0.8kV, OVC3 ¦ IEC60664-1,Input 1, 0.8kV, OVC3 ¦ IEC60664-1,Input 2, 1.5kV, OVC3 ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA32MR[Us] rated supply voltage | ~/-- 24…240
RM22UA32MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22UA32MRambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22UA32MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22UA32MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22UA32MRcircuit group | A1, A2 ¦ ,Supply,Terminal E1, M ¦ ,Input 1, E2, M ¦ ,Input 2, E3, M ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22UA32MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UA32MRcontacts material | Cadmium free
RM22UA32MRdepth | Depth,
RM22UA32MRdiagnostic button | Output will be de-energized when activated
RM22UA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA32MRdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22UA32MRduty time | 1
RM22UA32MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22UA32MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UA32MRheight | Height,
RM22UA32MRimmunity to microbreaks | 10
RM22UA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA32MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22UA32MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA32MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UA32MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22UA32MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UA32MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22UA32MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UA32MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UA32MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22UA32MRnet weight | 110
RM22UA32MRon-load factor | 1
RM22UA32MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22UA32MRoutput terminal | 11-12-14, 21-22-24
RM22UA32MRoutput type | 2 x C/O relay contacts
RM22UA32MRovervoltage category | 3 ¦ IEC60664-1
RM22UA32MRpolarity
RM22UA32MRpollution degree | 3 ¦ IEC60664-1
RM22UA32MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM22UA32MRpower on delay | 0
RM22UA32MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA32MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22UA32MRrelease of input voltage | -
RM22UA32MRrepeat accuracy of time delay | +/- 2%
RM22UA32MRreset time | 0
RM22UA32MRresponse time | Not specified =< 300ms ¦ ,on crossing the threshold,
RM22UA32MRsafety reliability data | 2,700,000 hours ¦ ,MTTF, 290,000 hours ¦ ,B10,
RM22UA32MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22UA32MRsetting accuracy of time delay | +/- 10% of full scales
RM22UA32MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22UA32MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22UA32MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22UA32MRstatus LED | Dial pointer (Green) R (Amber)
RM22UA32MRsupply frequency | 50 / 60 45…66
RM22UA32MRsupply terminal | A1-A2
RM22UA32MRsupply voltage limits | ~/-- 20.4…264
RM22UA32MRthermal current | 8A ¦ IEC60947-5-1
RM22UA32MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22UA32MRtime delay drift | < 1 < 0.05
RM22UA32MRtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UA32MRtime delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UA32MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22UA32MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22UA33MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 24…240 AC/DC ¦ ,Supply,Rated 18..125 AC/DC [full: 15..150 AC/DC] ¦ ,Input 1,Voltage 37..250 AC/DC [full: 30..300 AC/DC] ¦ ,Input 2,Spec 75..440 AC/DC [full: 50..500 AC/DC] ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Selectable with memory / without memory ¦ ,Over / undervoltage (windows mode), Selectable with memory / without memory ¦ ,Over voltage, Selectable with memory / without memory ¦ ,Undervoltage , ~/-- 15…500 150 ¦ ,E1-M / B1-C, 300 ¦ ,E2-M / B2-C, 500 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 15…150 ¦ ,E1-M / B1-C, ~/-- 30…300 ¦ ,E2-M / B2-C, ~/-- 50…500 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of 150V ¦ ,E1-M / B1-C, Adjustable 10%...100% of 300V ¦ ,E2-M / B2-C, Adjustable 10%...100% of 500V ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E1-M / B1-C, Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E2-M / B2-C, Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Resistive Voltage Step Down E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 100 True RMS Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22UA33MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22UA33MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22UA33MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22UA33MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22UA33MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply, 125V ¦ IEC60664-1,Input 1, 250V ¦ IEC60664-1,Input 2, 500V ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, 250V ¦ IEC60664-1,Supply / Input 1,Galvanic 250V ¦ IEC60664-1,Supply / Input 2,Isolated 500V ¦ IEC60664-1,Supply / Input 3,Circuit 250V ¦ IEC60664-1,Supply / Output 1, 250V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, 250V ¦ IEC60664-1,Input 1 / Output 1, 250V ¦ IEC60664-1,Input 1 / Output 2, 250V ¦ IEC60664-1,Input 2 / Output 1, 250V ¦ IEC60664-1,Input 2 / Output 2, 500V ¦ IEC60664-1,Input 3 / Output 1, 500V ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA33MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, 2.5kV, OVC3 ¦ IEC60664-1,Input 1, 4kV, OVC3 ¦ IEC60664-1,Input 2, 4kV, OVC3 ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA33MR[Us] rated supply voltage | ~/-- 24…240
RM22UA33MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22UA33MRambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22UA33MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22UA33MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22UA33MRcircuit group | A1, A2 ¦ ,Supply,Terminal E1, M ¦ ,Input 1, E2, M ¦ ,Input 2, E3, M ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22UA33MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UA33MRcontacts material | Cadmium free
RM22UA33MRdepth | Depth,
RM22UA33MRdiagnostic button | Output will be de-energized when activated
RM22UA33MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA33MRdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22UA33MRduty time | 1
RM22UA33MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22UA33MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UA33MRheight | Height,
RM22UA33MRimmunity to microbreaks | 10
RM22UA33MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA33MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22UA33MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA33MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UA33MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22UA33MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UA33MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22UA33MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UA33MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UA33MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22UA33MRnet weight | 110
RM22UA33MRon-load factor | 1
RM22UA33MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22UA33MRoutput terminal | 11-12-14, 21-22-24
RM22UA33MRoutput type | 2 x C/O relay contacts
RM22UA33MRovervoltage category | 3 ¦ IEC60664-1
RM22UA33MRpolarity
RM22UA33MRpollution degree | 3 ¦ IEC60664-1
RM22UA33MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM22UA33MRpower on delay | 0
RM22UA33MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA33MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22UA33MRrelease of input voltage | -
RM22UA33MRrepeat accuracy of time delay | +/- 2%
RM22UA33MRreset time | 0
RM22UA33MRresponse time | Not specified =< 300ms ¦ ,on crossing the threshold,
RM22UA33MRsafety reliability data | 2,700,000 hours ¦ ,MTTF, 290,000 hours ¦ ,B10,
RM22UA33MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22UA33MRsetting accuracy of time delay | +/- 10% of full scales
RM22UA33MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22UA33MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22UA33MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22UA33MRstatus LED | Dial pointer (Green) R (Amber)
RM22UA33MRsupply frequency | 50 / 60 45…66
RM22UA33MRsupply terminal | A1-A2
RM22UA33MRsupply voltage limits | ~/-- 20.4…264
RM22UA33MRthermal current | 8A ¦ IEC60947-5-1
RM22UA33MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22UA33MRtime delay drift | < 1 < 0.05
RM22UA33MRtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UA33MRtime delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UA33MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22UA33MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22UA33MT | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 380…415 AC ¦ ,Supply,Rated 18..125 AC/DC [full: 15..150 AC/DC] ¦ ,Input 1,Voltage 37..250 AC/DC [full: 30..300 AC/DC] ¦ ,Input 2,Spec 75..440 AC/DC [full: 50..500 AC/DC] ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Selectable with memory / without memory ¦ ,Over / undervoltage (windows mode), Selectable with memory / without memory ¦ ,Over voltage, Selectable with memory / without memory ¦ ,Undervoltage , ~/-- 15…500 150 ¦ ,E1-M / B1-C, 300 ¦ ,E2-M / B2-C, 500 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 15…150 ¦ ,E1-M / B1-C, ~/-- 30…300 ¦ ,E2-M / B2-C, ~/-- 50…500 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of 150V ¦ ,E1-M / B1-C, Adjustable 10%...100% of 300V ¦ ,E2-M / B2-C, Adjustable 10%...100% of 500V ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E1-M / B1-C, Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E2-M / B2-C, Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Resistive Voltage Step Down E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 100 True RMS Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22UA33MTIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22UA33MTMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22UA33MT[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22UA33MT[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22UA33MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply, 125V ¦ IEC60664-1,Input 1, 250V ¦ IEC60664-1,Input 2, 500V ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, 400V ¦ IEC60664-1,Supply / Input 1,Galvanic 400V ¦ IEC60664-1,Supply / Input 2,Isolated 500V ¦ IEC60664-1,Supply / Input 3,Circuit 400V ¦ IEC60664-1,Supply / Output 1, 400V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, 250V ¦ IEC60664-1,Input 1 / Output 1, 250V ¦ IEC60664-1,Input 1 / Output 2, 250V ¦ IEC60664-1,Input 2 / Output 1, 250V ¦ IEC60664-1,Input 2 / Output 2, 500V ¦ IEC60664-1,Input 3 / Output 1, 500V ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA33MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, 2.5kV, OVC3 ¦ IEC60664-1,Input 1, 4kV, OVC3 ¦ IEC60664-1,Input 2, 4kV, OVC3 ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22UA33MT[Us] rated supply voltage | ~380…415
RM22UA33MTambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22UA33MTambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22UA33MTbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22UA33MTcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22UA33MTcircuit group | A1, A2 ¦ ,Supply,Terminal E1, M ¦ ,Input 1, E2, M ¦ ,Input 2, E3, M ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22UA33MTconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UA33MTcontacts material | Cadmium free
RM22UA33MTdepth | Depth,
RM22UA33MTdiagnostic button | Output will be de-energized when activated
RM22UA33MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA33MTdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22UA33MTduty time | 1
RM22UA33MTelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22UA33MTelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 (Except Radiared RF IEC 61000-6-4 only) ¦ ,Generic emission standard, Class A ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class A, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UA33MTheight | Height,
RM22UA33MTimmunity to microbreaks | 10
RM22UA33MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22UA33MTlocal signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22UA33MTmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA33MTmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UA33MTmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22UA33MTmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UA33MTmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22UA33MTminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UA33MTmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UA33MTmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22UA33MTnet weight | 110
RM22UA33MTon-load factor | 1
RM22UA33MToutput logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22UA33MToutput terminal | 11-12-14, 21-22-24
RM22UA33MToutput type | 2 x C/O relay contacts
RM22UA33MTovervoltage category | 3 ¦ IEC60664-1
RM22UA33MTpolarity
RM22UA33MTpollution degree | 3 ¦ IEC60664-1
RM22UA33MTpower consumption | ~ 10VA ~ 8VA
RM22UA33MTpower on delay | 0
RM22UA33MTproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UA33MTrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22UA33MTrelease of input voltage | -
RM22UA33MTrepeat accuracy of time delay | +/- 2%
RM22UA33MTreset time | 0
RM22UA33MTresponse time | Not specified =< 300ms ¦ ,on crossing the threshold,
RM22UA33MTsafety reliability data | 2,700,000 hours ¦ ,MTTF, 290,000 hours ¦ ,B10,
RM22UA33MTseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22UA33MTsetting accuracy of time delay | +/- 10% of full scales
RM22UA33MTshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22UA33MTshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22UA33MTstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22UA33MTstatus LED | Dial pointer (Green) R (Amber)
RM22UA33MTsupply frequency | 50 / 60 45…66
RM22UA33MTsupply terminal | A1-A2
RM22UA33MTsupply voltage limits | ~323…456.5
RM22UA33MTthermal current | 8A ¦ IEC60947-5-1
RM22UA33MTtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22UA33MTtime delay drift | < 1 < 0.05
RM22UA33MTtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UA33MTtime delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UA33MTvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22UA33MTwidth | 22.5 x 90 x 73 ¦ ,Width,
RM22UB34 | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 110…240 AC/DC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Selectable threshold ¦ ,Over / undervoltage (windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , ~60…280 (F0) ~60…300 (F1) ~/--80…300 (F1) - ¦ ,E1-M / B1-C, - ¦ ,E2-M / B2-C, - ¦ ,E3-M / B3-C, Not specified ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, - ¦ ,E1-M / B1-C, - ¦ ,E2-M / B2-C, - ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, - ¦ ,E1-M / B1-C, - ¦ ,E2-M / B2-C, - ¦ ,E3-M / B3-C, Adjustable <U : 80…300 Adjustable >U : 80…300 ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, - ¦ ,E1-M / B1-C, - ¦ ,E2-M / B2-C, - ¦ ,E3-M / B3-C, Fixed 3% of threshold setting ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Resistive Voltage Step Down A1+ / A2- 50 / 60 45…66 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.2% / oC 250 True RMS Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM22UB34IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP40 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM22UB34Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM22UB34[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM22UB34[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM22UB34[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 250V ¦ IEC60664-1,Supply / Output 1, 250V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22UB34[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM22UB34[Us] rated supply voltage | ~/--110…240
RM22UB34ambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM22UB34ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM22UB34bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM22UB34cable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM22UB34circuit group | A1, A2 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM22UB34connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM22UB34contacts material | Cadmium free
RM22UB34depth | Depth,
RM22UB34diagnostic button | Output will be de-energized when activated
RM22UB34dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22UB34directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM22UB34duty time | 1
RM22UB34electrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM22UB34electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM22UB34height | Height,
RM22UB34immunity to microbreaks | 20
RM22UB34insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM22UB34local signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM22UB34marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UB34maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM22UB34maximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM22UB34maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM22UB34mechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM22UB34minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM22UB34mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM22UB34mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM22UB34net weight | 90
RM22UB34on-load factor | 1
RM22UB34output logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM22UB34output terminal | 11-12-14, 21-22-24
RM22UB34output type | 2 x C/O relay contacts
RM22UB34overvoltage category | 3 ¦ IEC60664-1
RM22UB34polarity
RM22UB34pollution degree | 3 ¦ IEC60664-1
RM22UB34power consumption | ~ 3.5VA, -- 1.5W ~ 5VA, -- 2W
RM22UB34power on delay | 0
RM22UB34product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM22UB34relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM22UB34release of input voltage | -
RM22UB34repeat accuracy of time delay | +/- 2%
RM22UB34reset time | 0
RM22UB34response time | Not specified =< 300ms ¦ ,on crossing the threshold,
RM22UB34safety reliability data | 3,800,000 hours ¦ ,MTTF, 400,000 hours ¦ ,B10,
RM22UB34seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM22UB34setting accuracy of time delay | +/- 10% of full scales
RM22UB34shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM22UB34short circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM22UB34standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM22UB34status LED | Dial pointer (Green) R (Amber)
RM22UB34supply frequency | 50 / 60 45…66
RM22UB34supply terminal | A1+ - A2-
RM22UB34supply voltage limits | ~60…280 (F0) ~80…300 (F1)
RM22UB34thermal current | 8A ¦ IEC60947-5-1
RM22UB34tightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM22UB34time delay drift | < 1 < 0.05
RM22UB34time delay range | Adjustable 0.1…30 ¦ ,"OFF" delay, Adjustable 0.1…30 ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UB34time delay type | Yes ¦ ,"OFF" delay, Yes ¦ ,"ON" delay, - ¦ ,Inhibition,
RM22UB34vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM22UB34width | 22.5 x 90 x 73 ¦ ,Width,
RM35HZ21FM | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 120…277 AC/DC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, - - - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM35HZ21FMIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM35HZ21FMInput nominal frequency selection | 50, 60 ¦ ,Input nominal frequency selection,
RM35HZ21FMMinimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM35HZ21FM[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM35HZ21FM[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM35HZ21FM[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 250V ¦ IEC60664-1,Supply / Output 1, 250V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM35HZ21FM[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM35HZ21FM[Us] rated supply voltage | ~ 120…277
RM35HZ21FMambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM35HZ21FMambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM35HZ21FMbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM35HZ21FMcable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM35HZ21FMcircuit group | A1, A2 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM35HZ21FMconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35HZ21FMcontacts material | Cadmium free
RM35HZ21FMdepth | 72 ¦ ,Depth,
RM35HZ21FMdiagnostic button | -
RM35HZ21FMdielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM35HZ21FMdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM35HZ21FMduty time | 1
RM35HZ21FMelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM35HZ21FMelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35HZ21FMheight | 90 ¦ ,Height,
RM35HZ21FMhysteresis | Fixed +/- 0.3Hz Internal design spec: Fixed +/- 0.2Hz ¦ ,Over frequency @ 50Hz, With Memory, same as above ¦ ,Over frequency @ 50Hz, Without Memory, same as above ¦ ,Over frequency @ 60Hz, With Memory, same as above ¦ ,Over frequency @ 60Hz, Without Memory, same as above ¦ ,Under frequency @ 50Hz, With Memory, same as above ¦ ,Under frequency @ 50Hz, Without Memory, same as above ¦ ,Under frequency @ 60Hz, With Memory, same as above ¦ ,Under frequency @ 60Hz, Without Memory,
RM35HZ21FMimmunity to microbreaks | 10
RM35HZ21FMinput frequency | 50 / 60 ¦ ,Rated frequency, 40…70 ¦ ,Frequency operating range,
RM35HZ21FMinput terminal | A1-A2 ¦ ,Input terminal,
RM35HZ21FMinsulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM35HZ21FMinternal input resistance | - ¦ ,Internal input resistance,
RM35HZ21FMlocal signalling | Un - ON ¦ ,Power supply availability, Un - OFF ¦ ,Power supply not availability, Rx - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, Rx - ON ¦ ,Output is energized, Rx - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM35HZ21FMmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35HZ21FMmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35HZ21FMmaximum measuring cycle | 200ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM35HZ21FMmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM35HZ21FMmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35HZ21FMmeasurement method | - ¦ ,Measurement method,
RM35HZ21FMmeasurement range | 40...70 ¦ ,Over frequency @ 50Hz, With Memory, same as above ¦ ,Over frequency @ 50Hz, Without Memory, same as above ¦ ,Over frequency @ 60Hz, With Memory, same as above ¦ ,Over frequency @ 60Hz, Without Memory, same as above ¦ ,Under frequency @ 50Hz, With Memory, same as above ¦ ,Under frequency @ 50Hz, Without Memory, same as above ¦ ,Under frequency @ 60Hz, With Memory, same as above ¦ ,Under frequency @ 60Hz, Without Memory,
RM35HZ21FMmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM35HZ21FMminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM35HZ21FMmonitoring functions | - governed by time delay - status reflects to R1 - fault status will be memorized and only resetable through power cycle ¦ ,Over frequency @ 50Hz, With Memory, - governed by time delay - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis ¦ ,Over frequency @ 50Hz, Without Memory, - governed by time delay - status reflects to R1 - fault status will be memorized and only resetable through power cycle ¦ ,Over frequency @ 60Hz, With Memory, - governed by time delay - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis ¦ ,Over frequency @ 60Hz, Without Memory, - governed by time delay - status reflects to R2 - fault status will be memorized and only resetable through power cycle ¦ ,Under frequency @ 50Hz, With Memory, - governed by time delay - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis ¦ ,Under frequency @ 50Hz, Without Memory, - governed by time delay - status reflects to R2 - fault status will be memorized and only resetable through power cycle ¦ ,Under frequency @ 60Hz, With Memory, - governed by time delay - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis ¦ ,Under frequency @ 60Hz, Without Memory,
RM35HZ21FMmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35HZ21FMmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM35HZ21FMnet weight | 95
RM35HZ21FMon-load factor | 1
RM35HZ21FMoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM35HZ21FMoutput terminal | 15-16-18, 25-26-28
RM35HZ21FMoutput type | 2 x C/O relay contacts
RM35HZ21FMovervoltage category | 3 ¦ IEC60664-1
RM35HZ21FMpermissible input overload | 70 ¦ ,permissible input overload,
RM35HZ21FMpolarity | -
RM35HZ21FMpollution degree | 3 ¦ IEC60664-1
RM35HZ21FMpower consumption | 6
RM35HZ21FMpower on delay | 0
RM35HZ21FMproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35HZ21FMrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM35HZ21FMrelease of input voltage | -
RM35HZ21FMrepeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM35HZ21FMrepeat accuracy of time delay | +/- 0.5%
RM35HZ21FMreset time | 0
RM35HZ21FMresponse time | TBD ¦ ,on crossing the threshold (all monitoring functions), - ¦ ,on crossing the hysteresis (all monitoring functions), - ¦ ,on crossing the threshold (specific monitoring functions 1), - ¦ ,on crossing the threshold (specific monitoring functions 2), - ¦ ,on crossing the threshold (specific monitoring functions 3),
RM35HZ21FMsafety reliability data | TBD ¦ ,MTTF, TBD ¦ ,B10,
RM35HZ21FMseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM35HZ21FMsetting accuracy of the switching threshold | ± 10 % of the full scale value ¦ ,Setting accuracy,
RM35HZ21FMsetting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM35HZ21FMshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM35HZ21FMshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM35HZ21FMstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM35HZ21FMstatus LED | Un (Green) R1 (Amber) R2 (Amber)
RM35HZ21FMsupply frequency | 50 / 60 45…66
RM35HZ21FMsupply terminal | A1-A2
RM35HZ21FMsupply voltage limits | ~ 102…308
RM35HZ21FMswitching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation, < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM35HZ21FMthermal current | 8A ¦ IEC60947-5-1
RM35HZ21FMtightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM35HZ21FMtime delay drift | - -
RM35HZ21FMtime delay range | Adjustable 0.1…10 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35HZ21FMtime delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35HZ21FMtripping threshold | Adjustable -1 Hz…5 Hz for x1 scale Adjustable -2 Hz…10 Hz for x2 scale ¦ ,Over frequency @ 50Hz, With Memory, same as above ¦ ,Over frequency @ 50Hz, Without Memory, same as above ¦ ,Over frequency @ 60Hz, With Memory, same as above ¦ ,Over frequency @ 60Hz, Without Memory, Adjustable -5 Hz…1 Hz for x1 scale Adjustable -10 Hz…2 Hz for x2 scale ¦ ,Under frequency @ 50Hz, With Memory, same as above ¦ ,Under frequency @ 50Hz, Without Memory, same as above ¦ ,Under frequency @ 60Hz, With Memory, same as above ¦ ,Under frequency @ 60Hz, Without Memory,
RM35HZ21FMvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM35HZ21FMwidth | 35 ¦ ,Width,
RM35JA31MW | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, 600 ¦ ,Supply,Rated 600 ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, - ¦ ,Over / undercurrent (windows mode), Selectable with memory / without memory ¦ ,Over current, Selectable with memory / without memory ¦ ,Under current, ~/-- 2…500 5 ¦ ,E1-M / B1-C, 1 ¦ ,E2-M / B2-C, 0.2 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 2…20 ¦ ,E1-M / B1-C, ~/-- 10…100 ¦ ,E2-M / B2-C, ~/-- 50…500 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of 20 ¦ ,E1-M / B1-C, Adjustable 10%...100% of 100 ¦ ,E2-M / B2-C, Adjustable 10%...100% of 500 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C, Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C, Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Shunt resistor E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 True RMS MTTFd, B10d,
RM35JA31MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IEC60529,Front Panel,
RM35JA31MWMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM35JA31MW[Ie] rated operational current | IEC61810-1,Rated switching current,
RM35JA31MW[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM35JA31MW[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, 4 ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM35JA31MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM35JA31MW[Us] rated supply voltage | ~/-- 24…240
RM35JA31MWambient air temperature for operation | -20…+50 ¦ ,Operation,
RM35JA31MWambient air temperature for storage | -40…+70 ¦ ,Storage,
RM35JA31MWbump resistance | IEC60068-2-29
RM35JA31MWcable stripping length | Not specified ¦ ,Cable stripping length,
RM35JA31MWcircuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, 600 ¦ ,Output 2,
RM35JA31MWconnections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35JA31MWcontacts material | Cadmium free
RM35JA31MWdepth | Depth,
RM35JA31MWdiagnostic button
RM35JA31MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM35JA31MWdirectives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
RM35JA31MWduty time | Not specified
RM35JA31MWelectrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM35JA31MWelectromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35JA31MWheight | Height,
RM35JA31MWimmunity to microbreaks | 50
RM35JA31MWinsulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM35JA31MWlocal signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM35JA31MWmarking | UL, CSA, GL, C-Tick, GOST, CE
RM35JA31MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35JA31MWmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 5 ¦ ,Maximum switching current, 1250 ¦ ,Maximum switching capacity,
RM35JA31MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35JA31MWmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM35JA31MWminimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM35JA31MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35JA31MWmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM35JA31MWnet weight | 130
RM35JA31MWon-load factor
RM35JA31MWoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
RM35JA31MWoutput terminal | 11-12-14, 21-22-24
RM35JA31MWoutput type | 2 x C/O relay contacts
RM35JA31MWovervoltage category | III ¦ IEC60664-1
RM35JA31MWpolarity
RM35JA31MWpollution degree | 3 ¦ IEC60664-1
RM35JA31MWpower consumption | ~ 3.5VA, -- 0.6W
RM35JA31MWpower on delay | 0
RM35JA31MWproduct certifications | UL, CSA, GL, C-Tick, GOST
RM35JA31MWrelative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM35JA31MWrelease of input voltage
RM35JA31MWrepeat accuracy of time delay | +/- 2%
RM35JA31MWreset time | 0
RM35JA31MWresponse time | Not specified ¦ ,on crossing the threshold,
RM35JA31MWsafety reliability data | MTTF, B10,
RM35JA31MWseismic resistance | IEC60068-3-3
RM35JA31MWsetting accuracy of time delay | +/- 10% of full scales
RM35JA31MWshock resistance | 5 gn ¦ IEC60068-2-27
RM35JA31MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM35JA31MWstandards | EN60255-6, IEC60255-6
RM35JA31MWstatus LED
RM35JA31MWsupply frequency | 50 / 60 45…66
RM35JA31MWsupply terminal | A1-A2
RM35JA31MWsupply voltage limits | ~/-- 20.4…264
RM35JA31MWthermal current | IEC60947-5-1
RM35JA31MWtightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM35JA31MWtime delay drift | Not specified Not specified
RM35JA31MWtime delay range | Adjustable 0.3…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, Adjustable 1…20 ¦ ,Inhibition,
RM35JA31MWtime delay type | · ¦ ,"OFF" delay, - ¦ ,"ON" delay, · ¦ ,Inhibition,
RM35JA31MWvibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM35JA31MWwidth | 35 x 90 x 72 ¦ ,Width,
RM35JA32MR | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 24…240 AC/DC ¦ ,Supply,Rated 0.15..1.5A AC/DC [full: 0.18..1.2A AC/DC] ¦ ,Input 1,Voltage 0.5..5A AC/DC [full: 6..4A AC/DC] ¦ ,Input 2,Spec 1.8..12A AC/DC [full: 1.5..15A AC/DC] ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Selectable with memory / without memory ¦ ,Over / undercurrent (windows mode), Selectable with memory / without memory ¦ ,Over current, Selectable with memory / without memory ¦ ,Under current, ~/-- 150…15000 0.05 ¦ ,E1-M / B1-C, 0.015 ¦ ,E2-M / B2-C, 0.005 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, Built in current transformer, ~/-- 150…1500 ¦ ,E1-M / B1-C, ~/-- 500…5000 ¦ ,E2-M / B2-C, ~/-- 1500…15000 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of 1500 ¦ ,E1-M / B1-C, Adjustable 10%...100% of 5000 ¦ ,E2-M / B2-C, Adjustable 10%...100% of 15000 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E1-M / B1-C, Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E2-M / B2-C, Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Shunt resistor E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 100 True RMS Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM35JA32MRIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM35JA32MRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM35JA32MR[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM35JA32MR[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM35JA32MR[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply, 10V ¦ IEC60664-1,Input 1, 10V ¦ IEC60664-1,Input 2, 10V ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, 250V ¦ IEC60664-1,Supply / Input 1,Galvanic 250V ¦ IEC60664-1,Supply / Input 2,Isolated 250V ¦ IEC60664-1,Supply / Input 3,Circuit 250V ¦ IEC60664-1,Supply / Output 1, 250V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, 250V ¦ IEC60664-1,Input 1 / Output 1, 250V ¦ IEC60664-1,Input 1 / Output 2, 250V ¦ IEC60664-1,Input 2 / Output 1, 250V ¦ IEC60664-1,Input 2 / Output 2, 250V ¦ IEC60664-1,Input 3 / Output 1, 250V ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM35JA32MR[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM35JA32MR[Us] rated supply voltage | ~/-- 24…240
RM35JA32MRambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM35JA32MRambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM35JA32MRbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM35JA32MRcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM35JA32MRcircuit group | A1, A2 ¦ ,Supply,Terminal E1, M ¦ ,Input 1, E2, M ¦ ,Input 2, E3, M ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM35JA32MRconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35JA32MRcontacts material | Cadmium free
RM35JA32MRdepth | Depth,
RM35JA32MRdiagnostic button | Output will be de-energized when activated
RM35JA32MRdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM35JA32MRdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM35JA32MRduty time | 1
RM35JA32MRelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM35JA32MRelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35JA32MRheight | Height,
RM35JA32MRimmunity to microbreaks | 50
RM35JA32MRinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM35JA32MRlocal signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM35JA32MRmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35JA32MRmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35JA32MRmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM35JA32MRmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35JA32MRmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM35JA32MRminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM35JA32MRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35JA32MRmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM35JA32MRnet weight | 120
RM35JA32MRon-load factor | 1
RM35JA32MRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM35JA32MRoutput terminal | 11-12-14, 21-22-24
RM35JA32MRoutput type | 2 x C/O relay contacts
RM35JA32MRovervoltage category | 3 ¦ IEC60664-1
RM35JA32MRpolarity
RM35JA32MRpollution degree | 3 ¦ IEC60664-1
RM35JA32MRpower consumption | ~ 3.5VA, -- 0.6W 1.5W
RM35JA32MRpower on delay | 0
RM35JA32MRproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35JA32MRrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM35JA32MRrelease of input voltage | -
RM35JA32MRrepeat accuracy of time delay | +/- 2%
RM35JA32MRreset time | 0
RM35JA32MRresponse time | Not specified =< 500ms ¦ ,on crossing the threshold,
RM35JA32MRsafety reliability data | 2,600,000 hours ¦ ,MTTF, 270,000 hours ¦ ,B10,
RM35JA32MRseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM35JA32MRsetting accuracy of time delay | +/- 10% of full scales
RM35JA32MRshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM35JA32MRshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM35JA32MRstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM35JA32MRstatus LED | Dial pointer (Green) R (Amber)
RM35JA32MRsupply frequency | 50 / 60 45…66
RM35JA32MRsupply terminal | A1-A2
RM35JA32MRsupply voltage limits | ~/-- 20.4…264
RM35JA32MRthermal current | 8A ¦ IEC60947-5-1
RM35JA32MRtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM35JA32MRtime delay drift | < 1 < 0.05
RM35JA32MRtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35JA32MRtime delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35JA32MRvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM35JA32MRwidth | 22.5 x 90 x 73 ¦ ,Width,
RM35JA32MT | 3K3 (No Condensation & No Formation of Ice) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 380…415 AC ¦ ,Supply,Rated 0.15..1.5A AC/DC [full: 0.18..1.2A AC/DC] ¦ ,Input 1,Voltage 0.5..5A AC/DC [full: 6..4A AC/DC] ¦ ,Input 2,Spec 1.8..12A AC/DC [full: 1.5..15A AC/DC] ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Selectable with memory / without memory ¦ ,Over / undercurrent (windows mode), Selectable with memory / without memory ¦ ,Over current, Selectable with memory / without memory ¦ ,Under current, ~/-- 150…15000 0.05 ¦ ,E1-M / B1-C, 0.015 ¦ ,E2-M / B2-C, 0.005 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 150…1500 ¦ ,E1-M / B1-C, ~/-- 500…5000 ¦ ,E2-M / B2-C, ~/-- 1500…15000 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of 1500 ¦ ,E1-M / B1-C, Adjustable 10%...100% of 5000 ¦ ,E2-M / B2-C, Adjustable 10%...100% of 15000 ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E1-M / B1-C, Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E2-M / B2-C, Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value ¦ ,E3-M / B3-C, - ¦ ,A1+ / A2-, - ¦ ,Built in current transformer, Shunt resistor E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value (For 1.5A and 5A) +/- 20% of full scale value (For 15A) +/- 0.5% < 1% over whole range 0.05% / oC 30 100 True RMS Yes 1) Will always illuminated when power is supplied to the product - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM35JA32MTIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM35JA32MTMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM35JA32MT[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM35JA32MT[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM35JA32MT[Ui] rated insulation voltage | 400V ¦ IEC60664-1,Supply, 10V ¦ IEC60664-1,Input 1, 10V ¦ IEC60664-1,Input 2, 10V ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, 400V ¦ IEC60664-1,Supply / Input 1,Galvanic 400V ¦ IEC60664-1,Supply / Input 2,Isolated 250V ¦ IEC60664-1,Supply / Input 3,Circuit 400V ¦ IEC60664-1,Supply / Output 1, 400V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, 250V ¦ IEC60664-1,Input 1 / Output 1, 250V ¦ IEC60664-1,Input 1 / Output 2, 250V ¦ IEC60664-1,Input 2 / Output 1, 250V ¦ IEC60664-1,Input 2 / Output 2, 250V ¦ IEC60664-1,Input 3 / Output 1, 250V ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM35JA32MT[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM35JA32MT[Us] rated supply voltage | ~380…415
RM35JA32MTambient air temperature for operation | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) ¦ ,Operation,
RM35JA32MTambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM35JA32MTbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM35JA32MTcable stripping length | 6 (Screw Terminal) 8 (Spring Terminal) ¦ ,Cable stripping length,
RM35JA32MTcircuit group | A1, A2 ¦ ,Supply,Terminal E1, M ¦ ,Input 1, E2, M ¦ ,Input 2, E3, M ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM35JA32MTconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35JA32MTcontacts material | Cadmium free
RM35JA32MTdepth | Depth,
RM35JA32MTdiagnostic button | Output will be de-energized when activated
RM35JA32MTdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM35JA32MTdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM35JA32MTduty time | 1
RM35JA32MTelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM35JA32MTelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, - ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35JA32MTheight | Height,
RM35JA32MTimmunity to microbreaks | 50
RM35JA32MTinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM35JA32MTlocal signalling | Dial pointer - ON ¦ ,Power supply availability, Dial pointer - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM35JA32MTmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35JA32MTmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35JA32MTmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM35JA32MTmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35JA32MTmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM35JA32MTminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM35JA32MTmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35JA32MTmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM35JA32MTnet weight | 120
RM35JA32MTon-load factor | 1
RM35JA32MToutput logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM35JA32MToutput terminal | 11-12-14, 21-22-24
RM35JA32MToutput type | 2 x C/O relay contacts
RM35JA32MTovervoltage category | 3 ¦ IEC60664-1
RM35JA32MTpolarity
RM35JA32MTpollution degree | 3 ¦ IEC60664-1
RM35JA32MTpower consumption | ~ 10VA ~ 8VA
RM35JA32MTpower on delay | 0
RM35JA32MTproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35JA32MTrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM35JA32MTrelease of input voltage | -
RM35JA32MTrepeat accuracy of time delay | +/- 2%
RM35JA32MTreset time | 0
RM35JA32MTresponse time | Not specified =< 500ms ¦ ,on crossing the threshold,
RM35JA32MTsafety reliability data | 2,600,000 hours ¦ ,MTTF, 270,000 hours ¦ ,B10,
RM35JA32MTseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM35JA32MTsetting accuracy of time delay | +/- 10% of full scales
RM35JA32MTshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM35JA32MTshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM35JA32MTstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM35JA32MTstatus LED | Dial pointer (Green) R (Amber)
RM35JA32MTsupply frequency | 50 / 60 45…66
RM35JA32MTsupply terminal | A1-A2
RM35JA32MTsupply voltage limits | ~323…456.5
RM35JA32MTthermal current | 8A ¦ IEC60947-5-1
RM35JA32MTtightening torque | 0.6…1.0 ¦ IEC60947-1,Tightening torque,
RM35JA32MTtime delay drift | < 1 < 0.05
RM35JA32MTtime delay range | Adjustable 0.1…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35JA32MTtime delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35JA32MTvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM35JA32MTwidth | 22.5 x 90 x 73 ¦ ,Width,
RM35JA32MW | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, 600 ¦ ,Supply,Rated 600 ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, - ¦ ,Over / undercurrent (windows mode), Selectable with memory / without memory ¦ ,Over current, Selectable with memory / without memory ¦ ,Under current, ~/-- 150…15000 0.05 ¦ ,E1-M / B1-C, 0.015 ¦ ,E2-M / B2-C, 0.005 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 150…1500 ¦ ,E1-M / B1-C, ~/-- 500…5000 ¦ ,E2-M / B2-C, ~/-- 1500…15000 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of 1500 ¦ ,E1-M / B1-C, Adjustable 10%...100% of 5000 ¦ ,E2-M / B2-C, Adjustable 10%...100% of 15000 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C, Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C, Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Shunt resistor E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 True RMS MTTFd, B10d,
RM35JA32MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IEC60529,Front Panel,
RM35JA32MWMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM35JA32MW[Ie] rated operational current | IEC61810-1,Rated switching current,
RM35JA32MW[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM35JA32MW[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, 4 ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM35JA32MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM35JA32MW[Us] rated supply voltage | ~/-- 24…240
RM35JA32MWambient air temperature for operation | -20…+50 ¦ ,Operation,
RM35JA32MWambient air temperature for storage | -40…+70 ¦ ,Storage,
RM35JA32MWbump resistance | IEC60068-2-29
RM35JA32MWcable stripping length | Not specified ¦ ,Cable stripping length,
RM35JA32MWcircuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, 600 ¦ ,Output 2,
RM35JA32MWconnections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35JA32MWcontacts material | Cadmium free
RM35JA32MWdepth | Depth,
RM35JA32MWdiagnostic button
RM35JA32MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM35JA32MWdirectives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
RM35JA32MWduty time | Not specified
RM35JA32MWelectrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM35JA32MWelectromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35JA32MWheight | Height,
RM35JA32MWimmunity to microbreaks | 10
RM35JA32MWinsulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM35JA32MWlocal signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM35JA32MWmarking | UL, CSA, GL, C-Tick, GOST, CE, CCC
RM35JA32MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35JA32MWmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, ~ 5 ¦ ,Maximum switching current, 1250 ¦ ,Maximum switching capacity,
RM35JA32MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35JA32MWmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM35JA32MWminimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM35JA32MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35JA32MWmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM35JA32MWnet weight | 130
RM35JA32MWon-load factor
RM35JA32MWoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
RM35JA32MWoutput terminal | 11-12-14, 21-22-24
RM35JA32MWoutput type | 2 x C/O relay contacts
RM35JA32MWovervoltage category | III ¦ IEC60664-1
RM35JA32MWpolarity
RM35JA32MWpollution degree | 3 ¦ IEC60664-1
RM35JA32MWpower consumption | ~ 3.5VA, -- 0.6W
RM35JA32MWpower on delay | 0
RM35JA32MWproduct certifications | UL, CSA, GL, C-Tick, GOST, CCC
RM35JA32MWrelative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM35JA32MWrelease of input voltage
RM35JA32MWrepeat accuracy of time delay | +/- 2%
RM35JA32MWreset time | 0
RM35JA32MWresponse time | Not specified ¦ ,on crossing the threshold,
RM35JA32MWsafety reliability data | MTTF, B10,
RM35JA32MWseismic resistance | IEC60068-3-3
RM35JA32MWsetting accuracy of time delay | +/- 10% of full scales
RM35JA32MWshock resistance | 5 gn ¦ IEC60068-2-27
RM35JA32MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM35JA32MWstandards | EN60255-6, IEC60255-6
RM35JA32MWstatus LED
RM35JA32MWsupply frequency | 50 / 60 45…66
RM35JA32MWsupply terminal | A1-A2
RM35JA32MWsupply voltage limits | ~/-- 20.4…264
RM35JA32MWthermal current | IEC60947-5-1
RM35JA32MWtightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM35JA32MWtime delay drift | Not specified Not specified
RM35JA32MWtime delay range | Adjustable 0.3…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, Adjustable 1…20 ¦ ,Inhibition,
RM35JA32MWtime delay type | · ¦ ,"OFF" delay, - ¦ ,"ON" delay, · ¦ ,Inhibition,
RM35JA32MWvibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM35JA32MWwidth | 35 x 90 x 72 ¦ ,Width,
RM35LM33MW | IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d, Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, 600 ¦ ,Supply,Rated 600 ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d,
RM35LM33MWIP degree of protection | IP 20 ¦ IEC60529,Terminal Block, IP 30 ¦ IEC60529,Housing, IEC60529,Front Panel, IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IEC60529,Front Panel,
RM35LM33MWMaximum length of probes cable | 100 ¦ ,Maximum length of probes cable, 100 ¦ ,Maximum length of probes cable,
RM35LM33MWMaximum probe supplied current | < 1 ¦ ,Maximum probe supplied current, 1 ¦ ,Maximum probe supplied current,
RM35LM33MWMaximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage, 12 ¦ ,Maximum probe supplied voltage,
RM35LM33MWMinimum distance to adjacent devices | Horizontal, Vertical, Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM35LM33MW[Ie] rated operational current | 5 ¦ IEC61810-1,Rated switching current, IEC61810-1,Rated switching current,
RM35LM33MW[Ue] rated operational voltage | 1250 ¦ IEC61810-1,Rated switching voltage, IEC61810-1,Rated switching voltage,
RM35LM33MW[Ui] rated insulation voltage | 250 ¦ IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3, IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, 4 ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM35LM33MW[Uimp] rated impulse withstand voltage | 4 (1.2/50 µs) ¦ IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3, IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM35LM33MW[Us] rated supply voltage | ~/-- 24…240 ~/-- 24…240
RM35LM33MWambient air temperature for operation | - 20…+ 50 ¦ ,Operation, -20…+50 ¦ ,Operation,
RM35LM33MWambient air temperature for storage | - 40…+ 70 ¦ ,Storage, -40…+70 ¦ ,Storage,
RM35LM33MWbump resistance | IEC60068-2-29 IEC60068-2-29
RM35LM33MWcable stripping length | Cable stripping length, Not specified ¦ ,Cable stripping length,
RM35LM33MWcircuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2, Supply,Terminal Input 1, Input 2, Input 3, Output 1, 600 ¦ ,Output 2,
RM35LM33MWconnections - terminals | 1 conductor: 0.5…4 (AWG 20…AWG 11) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 12) ¦ IEC60947-1,Solid cable (spring terminal), 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable (spring terminal), 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35LM33MWcontacts material | Cadmium free Cadmium free
RM35LM33MWdepth | Depth, Depth,
RM35LM33MWdiagnostic button
RM35LM33MWdielectric strength | 2, 1 50 Hz, 1 min. ¦ IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3, Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM35LM33MWdirectives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
RM35LM33MWduty time | Not specified
RM35LM33MWelectrical durability | 1 x 105 operating cycles ¦ IEC60947-4-1,AC-1, AC-12, AC-13, AC-14, AC-15, DC-12, DC-13 ¦ IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13, 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM35LM33MWelectromagnetic compatibility | Immunity NF EN 61000-6-2 2002 / IEC 61000-6-2 ¦ ,Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Emission NF EN 61000-6-4, NF EN 61000-6-3, IEC 61000-6-4, IEC 61000-6-3 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission, IEC61000-6-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35LM33MWheight | Height, Height,
RM35LM33MWhysteresis | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation, 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM35LM33MWimmunity to microbreaks | ~ 90, -- 100 90 (AC), 100 (DC)
RM35LM33MWinput frequency | 1 for LS 2.2 for St 4.7 pour HS ¦ ,Maximum cable capacitance, Maximum cable capacitance,
RM35LM33MWinput terminal | Input terminal, Input terminal,
RM35LM33MWinsulation resistance | > 500 MΩ, 2 500 V ¦ IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3, IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM35LM33MWinternal input resistance | Internal input resistance, Internal input resistance,
RM35LM33MWlocal signalling | Green LED ¦ ,Power supply availability, Power supply not availability, Timing in-progress, Yellow LED ¦ ,Output is energized, Yellow LED ¦ ,Output is de-energized, Range Setting Changes, Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM35LM33MWmarking | 1: 73/23/EEC and EMC 89/336/EEC UL, CSA, GL, C-Tick, GOST, CE
RM35LM33MWmaximum leakage current | IEC62314,Only for solid state output, - ¦ IEC62314,Only for solid state output,
RM35LM33MWmaximum measuring cycle | Maximum measuring cycles, Maximum measuring cycles,
RM35LM33MWmaximum switching capacity | 1/2 250 ¦ ,Maximum switching voltage, 1/2 5 ¦ ,Maximum switching current, Maximum switching capacity, ~ 250 ¦ ,Maximum switching voltage, ~ 5 ¦ ,Maximum switching current, 1250 ¦ ,Maximum switching capacity,
RM35LM33MWmaximum voltage drop | IEC62314,Only for solid state output, - ¦ IEC62314,Only for solid state output,
RM35LM33MWmeasurement method | Measurement method, Liquid level probe ¦ ,Measurement method,
RM35LM33MWmeasurement range | 250 Ω…5 kΩ ¦ ,1 level - Fill operation, 5 kΩ…100 kΩ ¦ ,1 level - Empty operation, 50 kΩ…1 MΩ ¦ ,2 level - Fill operation, 2 level - Empty operation, 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM35LM33MWmechanical durability | 30 x 106 operating cycles ¦ IEC61810-1 30 x 106 switching cycles ¦ IEC61810-1
RM35LM33MWminimum switching capacity | IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, 10/ 2 5 V ¦ IEC60947-5-4,Minimum switching capacity, 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM35LM33MWmonitoring functions | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation, 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM35LM33MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane, Any position ¦ ,In relation to normal vertical mounting plane,
RM35LM33MWmounting support | On 4 rail ¦ IEC/EN 60715,Without socket, IEC/EN 60715,With socket, On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM35LM33MWnet weight | 130
RM35LM33MWon-load factor
RM35LM33MWoutput logic | R1 (11-12-14), R2 (21-22-24), Not specified ¦ ,R1 (11-12-14), R2 (21-22-24),
RM35LM33MWoutput terminal | 11-12-14, 21-22-24
RM35LM33MWoutput type | 2 C/O contacts 2 x C/O relay contacts
RM35LM33MWovervoltage category | III ¦ IEC60664-1 III ¦ IEC60664-1
RM35LM33MWpolarity
RM35LM33MWpollution degree | 3 ¦ IEC60664-1 3 ¦ IEC60664-1
RM35LM33MWpower consumption | 5VA / 1.5W ~ 5VA, -- 1.5W
RM35LM33MWpower on delay | 600 =< 600
RM35LM33MWproduct certifications | UL, CSA, GL, C-Tick, GOST UL, CSA, GL, C-Tick, GOST
RM35LM33MWrelative humidity | 2 x 24 hours…+ 95 % RH at + 55 °C (without condensation) ¦ IEC60068-2-30,Damp heat, 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM35LM33MWrelease of input voltage
RM35LM33MWrepeat accuracy of the switching threshold | Repeat accuracy (constant parameters), Not specified ¦ ,Repeat accuracy (constant parameters),
RM35LM33MWrepeat accuracy of time delay | ± 2 % +/- 2%
RM35LM33MWreset time | 1.75 ¦ ,through Un power reset, through front panel reset, through input control reset, =< 1750 at maximum supply voltage ¦ ,through Un power reset, through front panel reset, through input control reset,
RM35LM33MWresponse time | on crossing the threshold, Not specified ¦ ,on crossing the threshold,
RM35LM33MWsafety reliability data | MTTF, B10, MTTF, B10,
RM35LM33MWseismic resistance | IEC60068-3-3 IEC60068-3-3
RM35LM33MWsetting accuracy of the switching threshold | ± 10 % of the full scale ± 20 % for the HS range ¦ ,Setting accuracy, +/- 10% of full scale value, +/- 20% for HS range ¦ ,Setting accuracy,
RM35LM33MWsetting accuracy of time delay | +/- 10% of full scales
RM35LM33MWshock resistance | 5 gn ¦ IEC60068-2-27 5 gn ¦ IEC60068-2-27
RM35LM33MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse, 8 ¦ IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM35LM33MWstandards | NF EN 60255-6 and IEC 60255-6 EN60255-6, IEC60255-6
RM35LM33MWstatus LED
RM35LM33MWsupply frequency | 50/60 Hz ± 10 % 50 / 60 45…66
RM35LM33MWsupply terminal | A1-A2
RM35LM33MWsupply voltage limits | ~/-- 20.4…264 ~/-- 20.4…264
RM35LM33MWswitching threshold drift | Measurement error with supply voltage variation, 0.5 % / °C ¦ ,Measurement error with temperature variation, Not specified ¦ ,Measurement error with supply voltage variation, 0.5% / oC ¦ ,Measurement error with temperature variation,
RM35LM33MWthermal current | IEC60947-5-1 5 ¦ IEC60947-5-1
RM35LM33MWtightening torque | 0.6…1N.m / 5.3…8.8 Lbf.In ¦ IEC60947-1,Tightening torque, 0.6…1 ¦ IEC60947-1,Tightening torque,
RM35LM33MWtime delay drift | Not specified Not specified
RM35LM33MWtime delay range | 0.1…5, 0 + 10 % ¦ ,"OFF" delay, "ON" delay, Inhibition, Adjustable 0.1…5 ¦ ,"OFF" delay, Adjustable 0.1…5 ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35LM33MWtime delay type | "OFF" delay, "ON" delay, Inhibition, · ¦ ,"OFF" delay, · ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35LM33MWtripping threshold | 5…100 % of the range ¦ ,1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation, 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM35LM33MWvibration resistance | 0.035 mm from 10…150 Hz ¦ IEC60068-2-6 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM35LM33MWwidth | Width, 35 x 90 x 72 ¦ ,Width,
RM35LV14MW | IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d, Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, 600 ¦ ,Supply,Rated 600 ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d,
RM35LV14MWIP degree of protection | IP 20 ¦ IEC60529,Terminal Block, IP 30 ¦ IEC60529,Housing, IEC60529,Front Panel, IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IEC60529,Front Panel,
RM35LV14MWMaximum length of probes cable | 100 ¦ ,Maximum length of probes cable, 100 ¦ ,Maximum length of probes cable,
RM35LV14MWMaximum probe supplied current | 40 ¦ ,Maximum probe supplied current, 40 ¦ ,Maximum probe supplied current,
RM35LV14MWMaximum probe supplied voltage | 12 ¦ ,Maximum probe supplied voltage, 12 ¦ ,Maximum probe supplied voltage,
RM35LV14MWMinimum distance to adjacent devices | Horizontal, Vertical, Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM35LV14MW[Ie] rated operational current | 5 ¦ IEC61810-1,Rated switching current, IEC61810-1,Rated switching current,
RM35LV14MW[Ue] rated operational voltage | 1250 ¦ IEC61810-1,Rated switching voltage, IEC61810-1,Rated switching voltage,
RM35LV14MW[Ui] rated insulation voltage | 250 ¦ IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3, IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, 4 ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM35LV14MW[Uimp] rated impulse withstand voltage | 4 (1.2/50 µs) ¦ IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3, IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM35LV14MW[Us] rated supply voltage | 1/2 24…240 ~/-- 24…240
RM35LV14MWambient air temperature for operation | - 20…+ 50 ¦ ,Operation, -20…+50 ¦ ,Operation,
RM35LV14MWambient air temperature for storage | - 40…+ 70 ¦ ,Storage, -40…+70 ¦ ,Storage,
RM35LV14MWbump resistance | IEC60068-2-29 IEC60068-2-29
RM35LV14MWcable stripping length | Cable stripping length, Not specified ¦ ,Cable stripping length,
RM35LV14MWcircuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2, Supply,Terminal Input 1, Input 2, Input 3, Output 1, 600 ¦ ,Output 2,
RM35LV14MWconnections - terminals | 1 conductor: 0.5…4 (AWG 20…AWG 11) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), 1 conductor: 0.2…2.5 (AWG 24…AWG 12) ¦ IEC60947-1,Solid cable (spring terminal), 2 conductors: 0.2…1.5 (AWG 24…AWG 16) ¦ IEC60947-1,Flexible cable (spring terminal), 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35LV14MWcontacts material | Cadmium free Cadmium free
RM35LV14MWdepth | Depth, Depth,
RM35LV14MWdiagnostic button
RM35LV14MWdielectric strength | 2, 1 50 Hz, 1 min. ¦ IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3, Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM35LV14MWdirectives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
RM35LV14MWduty time | Not specified
RM35LV14MWelectrical durability | 1 x 105 operating cycles ¦ IEC60947-4-1,AC-1, AC-12, AC-13, AC-14, AC-15, DC-12, DC-13 ¦ IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13, 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM35LV14MWelectromagnetic compatibility | Immunity NF EN 61000-6-2 2002 / IEC 61000-6-2 ¦ ,Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Emission NF EN 61000-6-4, NF EN 61000-6-3, IEC 61000-6-4, IEC 61000-6-3 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission, IEC61000-6-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35LV14MWheight | Height, Height,
RM35LV14MWhysteresis | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation, 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM35LV14MWimmunity to microbreaks | ~ 90, -- 100 90 (AC), 100 (DC)
RM35LV14MWinput frequency | 10 ¦ ,Maximum cable capacitance, Maximum cable capacitance,
RM35LV14MWinput terminal | Input terminal, Input terminal,
RM35LV14MWinsulation resistance | > 500 MΩ, 2 500 V ¦ IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3, IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM35LV14MWinternal input resistance | Internal input resistance, Internal input resistance,
RM35LV14MWlocal signalling | Green LED ¦ ,Power supply availability, Power supply not availability, Timing in-progress, Yellow LED ¦ ,Output is energized, Yellow LED ¦ ,Output is de-energized, Range Setting Changes, Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM35LV14MWmarking | 1: 73/23/EEC and EMC 89/336/EEC UL, CSA, GL, C-Tick, GOST, CE
RM35LV14MWmaximum leakage current | IEC62314,Only for solid state output, - ¦ IEC62314,Only for solid state output,
RM35LV14MWmaximum measuring cycle | Maximum measuring cycles, Maximum measuring cycles,
RM35LV14MWmaximum switching capacity | 1/2 250 ¦ ,Maximum switching voltage, 1/2 5 ¦ ,Maximum switching current, Maximum switching capacity, ~ 250 ¦ ,Maximum switching voltage, ~ 5 ¦ ,Maximum switching current, 1250 ¦ ,Maximum switching capacity,
RM35LV14MWmaximum voltage drop | IEC62314,Only for solid state output, - ¦ IEC62314,Only for solid state output,
RM35LV14MWmeasurement method | Measurement method, 12V NPN/PNP ultrasonics sensor ¦ ,Measurement method,
RM35LV14MWmeasurement range | – ¦ ,1 level - Fill operation, – ¦ ,1 level - Empty operation, – ¦ ,2 level - Fill operation, 2 level - Empty operation, 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM35LV14MWmechanical durability | 30 x 106 operating cycles ¦ IEC61810-1 30 x 106 switching cycles ¦ IEC61810-1
RM35LV14MWminimum switching capacity | IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, 10/ 2 5 V ¦ IEC60947-5-4,Minimum switching capacity, 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM35LV14MWmonitoring functions | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation, 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM35LV14MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane, Any position ¦ ,In relation to normal vertical mounting plane,
RM35LV14MWmounting support | On 4 rail ¦ IEC/EN 60715,Without socket, IEC/EN 60715,With socket, On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM35LV14MWnet weight | 130
RM35LV14MWon-load factor
RM35LV14MWoutput logic | R1 (11-12-14), R2 (21-22-24), Not specified ¦ ,R1 (11-12-14), R2 (21-22-24),
RM35LV14MWoutput terminal | 11-12-14
RM35LV14MWoutput type | 1 C/O contact 1 x C/O relay contacts
RM35LV14MWovervoltage category | III ¦ IEC60664-1 III ¦ IEC60664-1
RM35LV14MWpolarity
RM35LV14MWpollution degree | 3 ¦ IEC60664-1 3 ¦ IEC60664-1
RM35LV14MWpower consumption | 5VA / 1.5W ~ 5VA, -- 1.5W
RM35LV14MWpower on delay | 500 =< 600
RM35LV14MWproduct certifications | UL, CSA, GL, C-Tick, GOST UL, CSA, GL, C-Tick, GOST
RM35LV14MWrelative humidity | 2 x 24 hours…+ 95 % RH at + 55 °C (without condensation) ¦ IEC60068-2-30,Damp heat, 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM35LV14MWrelease of input voltage
RM35LV14MWrepeat accuracy of the switching threshold | Repeat accuracy (constant parameters), Not specified ¦ ,Repeat accuracy (constant parameters),
RM35LV14MWrepeat accuracy of time delay | ± 2 % +/- 2%
RM35LV14MWreset time | 4 if 1 line broken / 1 if 2 lines broken ¦ ,through Un power reset, through front panel reset, through input control reset, =< 1000 at maximum supply voltage =< 4000 at maximum supply voltage ¦ ,through Un power reset, through front panel reset, through input control reset,
RM35LV14MWresponse time | on crossing the threshold, Not specified ¦ ,on crossing the threshold,
RM35LV14MWsafety reliability data | MTTF, B10, MTTF, B10,
RM35LV14MWseismic resistance | IEC60068-3-3 IEC60068-3-3
RM35LV14MWsetting accuracy of the switching threshold | ± 10 % of the full scale ± 20 % for the HS range ¦ ,Setting accuracy, +/- 10% of full scale value ¦ ,Setting accuracy,
RM35LV14MWsetting accuracy of time delay | +/- 10% of full scales
RM35LV14MWshock resistance | 5 gn ¦ IEC60068-2-27 5 gn ¦ IEC60068-2-27
RM35LV14MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse, IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM35LV14MWstandards | NF EN 60255-6 and IEC 60255-6 EN60255-6, IEC60255-6
RM35LV14MWstatus LED
RM35LV14MWsupply frequency | 50/60 Hz ± 10 % 50 / 60 45…66
RM35LV14MWsupply terminal | A1-A2
RM35LV14MWsupply voltage limits | 1/2 20.4…264 ~/-- 20.4…264
RM35LV14MWswitching threshold drift | Measurement error with supply voltage variation, 0.5 % / °C ¦ ,Measurement error with temperature variation, Not specified ¦ ,Measurement error with supply voltage variation, 0.5% / oC ¦ ,Measurement error with temperature variation,
RM35LV14MWthermal current | IEC60947-5-1 5 ¦ IEC60947-5-1
RM35LV14MWtightening torque | 0.6…1N.m / 5.3…8.8 Lbf.In ¦ IEC60947-1,Tightening torque, 0.6…1 ¦ IEC60947-1,Tightening torque,
RM35LV14MWtime delay drift | Not specified Not specified
RM35LV14MWtime delay range | 0.1…5, 0 + 10 % ¦ ,"OFF" delay, "ON" delay, Inhibition, Adjustable 0.1…5 ¦ ,"OFF" delay, Adjustable 0.1…5 ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35LV14MWtime delay type | "OFF" delay, "ON" delay, Inhibition, · ¦ ,"OFF" delay, · ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35LV14MWtripping threshold | – ¦ ,1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation, 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM35LV14MWvibration resistance | 0.035 mm from 10…150 Hz ¦ IEC60068-2-6 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM35LV14MWwidth | Width, 35 x 90 x 72 ¦ ,Width,
RM35TF30 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 208..480 AC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, Yes - - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d, Drawing / Diagram
RM35TF30IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, - ¦ IEC60529,Front Panel,
RM35TF30Input nominal voltage selection | 220, 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM35TF30Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM35TF30SP01 | Same as RM35TF30 ¦ IEC60721-3-3,Climatic category, Same as RM35TF30 ¦ Germanisher Lloyd,Environmental category, Same as RM35TF30 ¦ IEC60947-5-1,Cyclic Damp Heat Test, Same as RM35TF30 ¦ ,Supply,Rated Same as RM35TF30 ¦ ,Input 1,Voltage Same as RM35TF30 ¦ ,Input 2,Spec Same as RM35TF30 ¦ ,Input 3, Same as RM35TF30 ¦ ,Output 1, Same as RM35TF30 ¦ ,Output 2, Same as RM35TF30 ¦ ,Measurement mode, Same as RM35TF30 Same as RM35TF30 Same as RM35TF30 Same as RM35TF30 Same as RM35TF30 ¦ ,MTTFd, Same as RM35TF30 ¦ ,B10d, Drawing / Diagram
RM35TF30SP01IP degree of protection | Same as RM35TF30 ¦ IEC60529,Terminal Block, Same as RM35TF30 ¦ IEC60529,Housing, Same as RM35TF30 ¦ IEC60529,Front Panel,
RM35TF30SP01Input nominal voltage selection | Same as RM35TF30 ¦ ,Input nominal voltage selection,
RM35TF30SP01Minimum distance to adjacent devices | Same as RM35TF30 ¦ ,Horizontal, Same as RM35TF30 ¦ ,Vertical,
RM35TF30SP01[Ie] rated operational current | Same as RM35TF30 ¦ IEC61810-1,Rated switching current,
RM35TF30SP01[Ue] rated operational voltage | Same as RM35TF30 ¦ IEC61810-1,Rated switching voltage,
RM35TF30SP01[Ui] rated insulation voltage | Same as RM35TF30 ¦ IEC60664-1,Supply, Same as RM35TF30 ¦ IEC60664-1,Input 1, Same as RM35TF30 ¦ IEC60664-1,Input 2, Same as RM35TF30 ¦ IEC60664-1,Input 3, Same as RM35TF30 ¦ IEC60664-1,Output 1, Same as RM35TF30 ¦ IEC60664-1,Output 2, Same as RM35TF30 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM35TF30 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM35TF30 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM35TF30 ¦ IEC60664-1,Supply / Output 1, Same as RM35TF30 ¦ IEC60664-1,Supply / Output 2, Same as RM35TF30 ¦ IEC60664-1,Output 1 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 2, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Input 3, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 3,
RM35TF30SP01[Uimp] rated impulse withstand voltage | Same as RM35TF30 ¦ IEC60664-1,Supply, Same as RM35TF30 ¦ IEC60664-1,Input 1, Same as RM35TF30 ¦ IEC60664-1,Input 2, Same as RM35TF30 ¦ IEC60664-1,Input 3, Same as RM35TF30 ¦ IEC60664-1,Output 1, Same as RM35TF30 ¦ IEC60664-1,Output 2, Same as RM35TF30 ¦ IEC60664-1,Supply / Input 1,Galvanic Same as RM35TF30 ¦ IEC60664-1,Supply / Input 2,Isolated Same as RM35TF30 ¦ IEC60664-1,Supply / Input 3,Circuit Same as RM35TF30 ¦ IEC60664-1,Supply / Output 1, Same as RM35TF30 ¦ IEC60664-1,Supply / Output 2, Same as RM35TF30 ¦ IEC60664-1,Output 1 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 1, Same as RM35TF30 ¦ IEC60664-1,Input 3 / Output 2, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 2, Same as RM35TF30 ¦ IEC60664-1,Input 2 / Input 3, Same as RM35TF30 ¦ IEC60664-1,Input 1 / Input 3,
RM35TF30SP01[Us] rated supply voltage | Same as RM35TF30
RM35TF30SP01ambient air temperature for operation | Same as RM35TF30 ¦ ,Operation,
RM35TF30SP01ambient air temperature for storage | Same as RM35TF30 ¦ ,Storage,
RM35TF30SP01bump resistance | Same as RM35TF30 ¦ IEC60068-2-29
RM35TF30SP01cable stripping length | Same as RM35TF30 ¦ ,Cable stripping length,
RM35TF30SP01circuit group | Same as RM35TF30 ¦ ,Supply,Terminal Same as RM35TF30 ¦ ,Input 1, Same as RM35TF30 ¦ ,Input 2, Same as RM35TF30 ¦ ,Input 3, Same as RM35TF30 ¦ ,Output 1, Same as RM35TF30 ¦ ,Output 2,
RM35TF30SP01connections - terminals | Same as RM35TF30 ¦ IEC60947-1,Solid cable without cable end (screw terminal), Same as RM35TF30 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), Same as RM35TF30 ¦ IEC60947-1,Solid cable (spring terminal), Same as RM35TF30 ¦ IEC60947-1,Flexible cable (spring terminal),
RM35TF30SP01contacts material | Same as RM35TF30
RM35TF30SP01depth | Same as RM35TF30 ¦ ,Depth,
RM35TF30SP01diagnostic button | Same as RM35TF30
RM35TF30SP01dielectric strength | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 1, Same as RM35TF30 ¦ IEC60255-27,Supply / Input 2, Same as RM35TF30 ¦ IEC60255-27,Supply / Input 3, Same as RM35TF30 ¦ IEC60255-27,Supply / Output 1, Same as RM35TF30 ¦ IEC60255-27,Supply / Output 2, Same as RM35TF30 ¦ IEC60255-27,Output 1 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 2, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Input 3, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 3,
RM35TF30SP01directives | Same as RM35TF30 Same as RM35TF30 Same as RM35TF30
RM35TF30SP01duty time | Same as RM35TF30
RM35TF30SP01electrical durability | Same as RM35TF30 ¦ IEC60947-4-1,AC-1, Same as RM35TF30 ¦ IEC60947-4-1,DC-1, Same as RM35TF30 ¦ IEC60947-5-1,AC-15, Same as RM35TF30 ¦ IEC60947-5-1,DC-13,
RM35TF30SP01electromagnetic compatibility | Same as RM35TF30 ¦ ,Generic immunity standard, Same as RM35TF30 ¦ IEC61000-4-2,Electrostatic discharge, Same as RM35TF30 ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Same as RM35TF30 ¦ IEC61000-4-4,Fast transient / burst, Same as RM35TF30 ¦ IEC61000-4-5,Surge, Same as RM35TF30 ¦ IEC61000-4-6,Conducted RF disturbance, Same as RM35TF30 ¦ IEC61000-4-8,Power frequency magnetic field, Same as RM35TF30 ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Same as RM35TF30 ¦ IEC61000-4-18,1 MHz oscillation wave, Same as RM35TF30 ¦ IEC61000-4-29,DC voltage interruption, Same as RM35TF30 ¦ IEC61000-4-13,Low frequency harmonics, Same as RM35TF30 ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), Same as RM35TF30 ¦ ,Generic emission standard, Same as RM35TF30 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Same as RM35TF30 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Same as RM35TF30 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Same as RM35TF30 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Same as RM35TF30 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Same as RM35TF30 ¦ Germanisher Lloyd,Conducted emission,
RM35TF30SP01height | Same as RM35TF30 ¦ ,Height,
RM35TF30SP01hysteresis | Same as RM35TF30 ¦ ,Phase cut, Same as RM35TF30 ¦ ,Phase sequence, Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode), Fixed 5.35% of selected Un Internal design spec: 5.35% +/- 1.5% ¦ ,Over voltage, Fixed 5.35% of selected Un Internal design spec: 5.35% +/- 1.5% ¦ ,Undervoltage , Same as RM35TF30 ¦ ,Phase asymmetry, Same as RM35TF30 ¦ ,Disconnection of neutral, Same as RM35TF30 ¦ ,Voltage Regeneration, Same as RM35TF30 ¦ ,Extreme undervoltage (Phase loss), Same as RM35TF30 ¦ ,Extreme Overvoltage, Same as RM35TF30 ¦ ,Extreme Asymmetry,
RM35TF30SP01immunity to microbreaks | Same as RM35TF30
RM35TF30SP01input frequency | Same as RM35TF30 ¦ ,Rated frequency, Same as RM35TF30 ¦ ,Frequency operating range,
RM35TF30SP01input terminal | Same as RM35TF30 ¦ ,Input terminal,
RM35TF30SP01insulation resistance | Same as RM35TF30 ¦ IEC60255-27,Supply / Input 1, Same as RM35TF30 ¦ IEC60255-27,Supply / Input 2, Same as RM35TF30 ¦ IEC60255-27,Supply / Input 3, Same as RM35TF30 ¦ IEC60255-27,Supply / Output 1, Same as RM35TF30 ¦ IEC60255-27,Supply / Output 2, Same as RM35TF30 ¦ IEC60255-27,Output 1 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 1, Same as RM35TF30 ¦ IEC60255-27,Input 3 / Output 2, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 2, Same as RM35TF30 ¦ IEC60255-27,Input 2 / Input 3, Same as RM35TF30 ¦ IEC60255-27,Input 1 / Input 3,
RM35TF30SP01internal input resistance | Same as RM35TF30 ¦ ,Internal input resistance,
RM35TF30SP01local signalling | Same as RM35TF30 ¦ ,Power supply availability, Same as RM35TF30 ¦ ,Power supply not availability, Same as RM35TF30 ¦ ,Timing in-progress, Same as RM35TF30 ¦ ,Output is energized, Same as RM35TF30 ¦ ,Output is de-energized, Same as RM35TF30 ¦ ,Range Setting Changes, Same as RM35TF30 ¦ ,Phase Cut, Same as RM35TF30 ¦ ,Phase Sequence Swap, Same as RM35TF30 ¦ ,Undervoltage <U, Same as RM35TF30 ¦ ,Overvoltage >U, Same as RM35TF30 ¦ ,Phase Asymmetry, Same as RM35TF30 ¦ ,Voltage Regeneration, Same as RM35TF30 ¦ ,Extreme Undervoltage <U (Phase loss), Same as RM35TF30 ¦ ,Extreme Overvoltage >U, Same as RM35TF30 ¦ ,Extreme Phase Asymmetry,
RM35TF30SP01marking | Same as RM35TF30
RM35TF30SP01maximum leakage current | Same as RM35TF30 ¦ IEC62314,Only for solid state output,
RM35TF30SP01maximum measuring cycle | Same as RM35TF30 ¦ ,Maximum measuring cycles,
RM35TF30SP01maximum switching capacity | Same as RM35TF30 ¦ ,Maximum switching voltage, Same as RM35TF30 ¦ ,Maximum switching current, Same as RM35TF30 ¦ ,Maximum switching capacity,
RM35TF30SP01maximum voltage drop | Same as RM35TF30 ¦ IEC62314,Only for solid state output,
RM35TF30SP01measurement method | Same as RM35TF30 ¦ ,Measurement method,
RM35TF30SP01measurement range | Same as RM35TF30 ¦ ,Phase lost , Same as RM35TF30 ¦ ,Phase sequence, Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35TF30 ¦ ,Over voltage, Same as RM35TF30 ¦ ,Undervoltage , Same as RM35TF30 ¦ ,Phase asymmetry, Same as RM35TF30 ¦ ,Disconnection of neutral, Same as RM35TF30 ¦ ,Voltage Regeneration, Same as RM35TF30 ¦ ,Extreme undervoltage, Same as RM35TF30 ¦ ,Extreme Overvoltage, Same as RM35TF30 ¦ ,Extreme Asymmetry,
RM35TF30SP01mechanical durability | Same as RM35TF30 ¦ IEC61810-1
RM35TF30SP01minimum switching capacity | Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching voltage, Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching current, Same as RM35TF30 ¦ IEC60947-5-4,Minimum switching capacity,
RM35TF30SP01monitoring functions | Same as RM35TF30 ¦ ,Phase lost , Same as RM35TF30 ¦ ,Phase sequence, Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35TF30 ¦ ,Over voltage, Same as RM35TF30 ¦ ,Undervoltage , Same as RM35TF30 ¦ ,Phase asymmetry, Same as RM35TF30 ¦ ,Disconnection of neutral, Same as RM35TF30 ¦ ,Voltage Regeneration, Same as RM35TF30 ¦ ,Extreme undervoltage, Same as RM35TF30 ¦ ,Extreme overvoltage, Same as RM35TF30 ¦ ,Extreme asymmetry,
RM35TF30SP01mounting position | Same as RM35TF30 ¦ ,In relation to normal vertical mounting plane,
RM35TF30SP01mounting support | Same as RM35TF30 ¦ IEC/EN 60715,Without socket, Same as RM35TF30 ¦ IEC/EN 60715,With socket,
RM35TF30SP01net weight | Same as RM35TF30
RM35TF30SP01on-load factor | Same as RM35TF30
RM35TF30SP01output logic | Same as RM35TF30 ¦ ,R1 (11-12-14), Same as RM35TF30 ¦ ,R2 (21-22-24),
RM35TF30SP01output terminal | Same as RM35TF30
RM35TF30SP01output type | Same as RM35TF30
RM35TF30SP01overvoltage category | Same as RM35TF30 ¦ IEC60664-1
RM35TF30SP01permissible input overload | Same as RM35TF30 ¦ ,permissible input overload,
RM35TF30SP01polarity | Same as RM35TF30
RM35TF30SP01pollution degree | Same as RM35TF30 ¦ IEC60664-1
RM35TF30SP01power consumption | Same as RM35TF30
RM35TF30SP01power on delay | Same as RM35TF30
RM35TF30SP01product certifications | Same as RM35TF30
RM35TF30SP01relative humidity | Same as RM35TF30 ¦ IEC60068-2-30,Damp heat,XX
RM35TF30SP01release of input voltage | Same as RM35TF30
RM35TF30SP01repeat accuracy of the switching threshold | Same as RM35TF30 ¦ ,Repeat accuracy (constant parameters),
RM35TF30SP01repeat accuracy of time delay | Same as RM35TF30
RM35TF30SP01reset time | Same as RM35TF30 ¦ ,through Un power reset, Same as RM35TF30 ¦ ,through front panel reset, Same as RM35TF30 ¦ ,through input control reset,
RM35TF30SP01response time | Same as RM35TF30 ¦ ,on crossing the threshold, Same as RM35TF30 Same as RM35TF30 Same as RM35TF30 Same as RM35TF30
RM35TF30SP01safety reliability data | Same as RM35TF30 ¦ ,MTTF, Same as RM35TF30 ¦ ,B10,
RM35TF30SP01seismic resistance | Same as RM35TF30 ¦ IEC60068-3-3
RM35TF30SP01setting accuracy of the switching threshold | Same as RM35TF30 ¦ ,Setting accuracy,
RM35TF30SP01setting accuracy of time delay | Same as RM35TF30
RM35TF30SP01shock resistance | Same as RM35TF30 ¦ IEC60068-2-27
RM35TF30SP01short circuit protection | Same as RM35TF30 ¦ IEC60947-5-1,Relay Output by external fuse, Same as RM35TF30 ¦ IEC62314,Solid State Output by external fuse,
RM35TF30SP01standards | Same as RM35TF30
RM35TF30SP01status LED | Same as RM35TF30
RM35TF30SP01supply frequency | Same as RM35TF30 Same as RM35TF30
RM35TF30SP01supply terminal | Same as RM35TF30
RM35TF30SP01supply voltage limits | Same as RM35TF30
RM35TF30SP01switching threshold drift | Same as RM35TF30 ¦ ,Measurement error with supply voltage variation, Same as RM35TF30 ¦ ,Measurement error with temperature variation,
RM35TF30SP01thermal current | Same as RM35TF30 ¦ IEC60947-5-1
RM35TF30SP01tightening torque | Same as RM35TF30 ¦ IEC60947-1,Tightening torque,
RM35TF30SP01time delay drift | Same as RM35TF30 Same as RM35TF30
RM35TF30SP01time delay range | Same as RM35TF30 ¦ ,"OFF" delay, Same as RM35TF30 ¦ ,"ON" delay, Same as RM35TF30 ¦ ,Inhibition,
RM35TF30SP01time delay type | Same as RM35TF30 ¦ ,"OFF" delay, Same as RM35TF30 ¦ ,"ON" delay, Same as RM35TF30 ¦ ,Inhibition,
RM35TF30SP01tripping threshold | Same as RM35TF30 ¦ ,Phase cut, Same as RM35TF30 ¦ ,Phase sequence, Same as RM35TF30 ¦ ,Over / undervoltage (symmetry windows mode), Same as RM35TF30 ¦ ,Over voltage, Same as RM35TF30 ¦ ,Undervoltage , Same as RM35TF30 ¦ ,Phase asymmetry, Same as RM35TF30 ¦ ,Disconnection of neutral, Same as RM35TF30 ¦ ,Voltage Regeneration, Same as RM35TF30 ¦ ,Extreme undervoltage (Phase loss), Same as RM35TF30 ¦ ,Extreme Overvoltage, Same as RM35TF30 ¦ ,Extreme Asymmetry,
RM35TF30SP01vibration resistance | Same as RM35TF30 ¦ IEC60068-2-6
RM35TF30SP01width | Same as RM35TF30 ¦ ,Width,
RM35TF30[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM35TF30[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM35TF30[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, 500V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM35TF30[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM35TF30[Us] rated supply voltage | ~ 3 x 220…3 x 480
RM35TF30ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM35TF30ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM35TF30bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM35TF30cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM35TF30circuit group | L1, L2, L3 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM35TF30connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35TF30contacts material | Cadmium free
RM35TF30depth | 72 ¦ ,Depth,
RM35TF30diagnostic button | -
RM35TF30dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM35TF30directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM35TF30duty time | 1
RM35TF30electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM35TF30electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35TF30height | 90 ¦ ,Height,
RM35TF30hysteresis | All phase cut recover ¦ ,Phase cut, Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Over voltage, Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage , Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, All phases > 205V Internal design spec: All phases >190V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: All phases <533V +/- 5% ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM35TF30immunity to microbreaks | 0
RM35TF30input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
RM35TF30input terminal | L1-L2-L3 ¦ ,Input terminal,
RM35TF30insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM35TF30internal input resistance | - ¦ ,Internal input resistance,
RM35TF30local signalling | Un - ON ¦ ,Power supply availability, Un - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R - ON ¦ ,Output is energized, R - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes, Def - Permanent OFF ¦ ,Phase Cut, Def - Permanent OFF ¦ ,Phase Sequence Swap, Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Undervoltage <U, Def - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Overvoltage >U, Def - Permanent ON ¦ ,Phase Asymmetry, - ¦ ,Voltage Regeneration, Def - Permanent OFF ¦ ,Extreme Undervoltage <U (Phase loss), Def - Permanent OFF ¦ ,Extreme Overvoltage >U, Def - Permanent OFF ¦ ,Extreme Phase Asymmetry,
RM35TF30marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35TF30maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35TF30maximum measuring cycle | 140ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM35TF30maximum switching capacity | 250V ¦ ,Maximum switching voltage, 5A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM35TF30maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35TF30measurement method | True RMS ¦ ,Measurement method,
RM35TF30measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), +2…+20 % in the ranges 3 x ~ 220…440 +2…+10 % in the range 3 x ~ 480 ¦ ,Over voltage, -12…-2 % in the range 3 x ~ 220 -20…-2 % in the ranges 3 x ~ 380…480 ¦ ,Undervoltage , +5…+15 % in the ranges 3 x ~ 220…480 ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, - ¦ ,Extreme undervoltage, - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM35TF30mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM35TF30minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM35TF30monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost , governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), governed by time delay, status reflects to both R1 & R2 ¦ ,Over voltage, governed by time delay, status reflects to both R1 & R2 ¦ ,Undervoltage , governed by time delay, status reflects to both R1 & R2 ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM35TF30mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35TF30mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM35TF30net weight | 120
RM35TF30on-load factor | 1
RM35TF30output logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM35TF30output terminal | 11-12-14, 21-22-24
RM35TF30output type | 2 x C/O relay contacts
RM35TF30overvoltage category | 3 ¦ IEC60664-1
RM35TF30permissible input overload | - ¦ ,permissible input overload,
RM35TF30polarity | -
RM35TF30pollution degree | 3 ¦ IEC60664-1
RM35TF30power consumption | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz
RM35TF30power on delay | 0
RM35TF30product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35TF30relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM35TF30release of input voltage | -
RM35TF30repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM35TF30repeat accuracy of time delay | +/- 3%
RM35TF30reset time | 0
RM35TF30response time | 0
RM35TF30safety reliability data | 3,500,000 hours ¦ ,MTTF, 360,000 hours ¦ ,B10,
RM35TF30seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM35TF30setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM35TF30setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM35TF30shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM35TF30short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM35TF30standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM35TF30status LED | Un (Green) R (Amber) Def (Amber)
RM35TF30supply frequency | 50 / 60 45…66
RM35TF30supply terminal | L1-L3
RM35TF30supply voltage limits | ~ 3 x 194…3 x 528
RM35TF30switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation, < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM35TF30thermal current | 5A ¦ IEC60947-5-1
RM35TF30tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM35TF30time delay drift | - -
RM35TF30time delay range | Adjustable 0.1…10 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35TF30time delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35TF30tripping threshold | 1 or more phase cut ¦ ,Phase cut, Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Adjustable 2%...20% of selected Un ¦ ,Over voltage, Adjustable 2%...20% of selected Un ¦ ,Undervoltage , Adjustable 5%...15% of selected Un ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, 1 or more phase < 150V Internal design spec: 1 or more phase <188V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: 543V +/- 5% ¦ ,Extreme Overvoltage, Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM35TF30vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM35TF30width | 35 ¦ ,Width,
RM35TM250MW | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 24…240 AC/DC ¦ ,Supply,Rated PTC probe ¦ ,Input 1,Voltage Push Button Switch ¦ ,Input 2,Spec 208..480 AC/DC ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, 1) When Set to "No Memory" 1a) When motor temperature is normal, - pressing the "Test/Reset" button simulates overheating, R1 is de-energized - R1 will remain energized as long as "Test/Reset" button remains pressed 1b) When motor temperature is abnormal, - pressing the "Test/Reset" button will not change any product status 2) When Set to "Memory" 2a) When motor temperature is normal, - pressing the "Test/Reset" button simulates overheating, R1 is de-energized - R1 will remain energized as long as "Test/Reset" button remains pressed 2b) When motor temperature is abnormal, - pressing the "Test/Reset" button will not change any product status 2c) When motor temperature is abnormal at first and recover to normal - pressing the "Test/Reset" button will reset the fault, R1 is energized 1) Same function as per Test / Reset button 2) Short Y1 to T1 is the same meaning as pressing "Test/Reset" button 3) Open Y1 to T1 is the same meaning as releasing "Test/Reset" button - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM35TM250MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM35TM250MWMaximum resistance of temperature sensor at 20°C | 1500Ω ¦ ,Maximum resistance of temperature sensor at 20°C,
RM35TM250MWMaximum voltage of temperature control circuit | 3.6V when T1-T2 is open ¦ ,Maximum voltage of temperature control circuit,
RM35TM250MWMinimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM35TM250MWTemperature sensing circuit short-circuit current | 7mA when T1-T2 is short-circuited ¦ ,Temperature sensing circuit short-circuit current,
RM35TM250MW[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM35TM250MW[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM35TM250MW[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply, 10V ¦ IEC60664-1,Input 1, 10V ¦ IEC60664-1,Input 2, 500V ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, 500V ¦ IEC60664-1,Supply / Input 1,Galvanic 500V ¦ IEC60664-1,Supply / Input 2,Isolated 500V ¦ IEC60664-1,Supply / Input 3,Circuit 250V ¦ IEC60664-1,Supply / Output 1, 250V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, 500V ¦ IEC60664-1,Input 1 / Output 1, 500V ¦ IEC60664-1,Input 1 / Output 2, 500V ¦ IEC60664-1,Input 2 / Output 1, 500V ¦ IEC60664-1,Input 2 / Output 2, 500V ¦ IEC60664-1,Input 3 / Output 1, 500V ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM35TM250MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, 4kV, OVC3 ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic 4kV, OVC3 ¦ IEC60664-1,Supply / Input 2,Isolated 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 2 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM35TM250MW[Us] rated supply voltage | ~/-- 24…240
RM35TM250MWambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM35TM250MWambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM35TM250MWbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM35TM250MWcable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM35TM250MWcircuit group | A1, A2 ¦ ,Supply,Terminal T1, T2 ¦ ,Input 1, Y1 ¦ ,Input 2, L1, L2, L3 ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM35TM250MWconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35TM250MWcontacts material | Cadmium free
RM35TM250MWdepth | 72 ¦ ,Depth,
RM35TM250MWdiagnostic button | -
RM35TM250MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 2 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM35TM250MWdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM35TM250MWduty time | 1
RM35TM250MWelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM35TM250MWelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35TM250MWheight | 90 ¦ ,Height,
RM35TM250MWhysteresis | 1650 ± 10 % Internal design spec: TBD ¦ ,Motor temperature through PTC sensor, Internal design spec: TBD ¦ ,Short circuit of PTC sensor, All phase cut recover ¦ ,Phase lost , Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence, Internal design spec: TBD ¦ ,Voltage Regeneration, Internal design spec: TBD ¦ ,Extreme undervoltage (Phase loss),
RM35TM250MWimmunity to microbreaks | 20 ms at 20.4 V
RM35TM250MWinput frequency | Resistive Voltage Step Down ¦ ,Measurement mode,3 Phase
RM35TM250MWinput terminal | T1-T2 ¦ ,Input terminal,Motor temperature
RM35TM250MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 2 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM35TM250MWlocal signalling | Un - ON ¦ ,Power supply availability, Un - OFF ¦ ,Power supply not availability, - ¦ ,Timing in-progress, Rx - ON ¦ ,Output is energized, Rx - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes,
RM35TM250MWmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35TM250MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35TM250MWmaximum measuring cycle | 45…66 ¦ ,Frequency operating range,
RM35TM250MWmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM35TM250MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35TM250MWmeasurement method | - ¦ ,Input nominal voltage selection,
RM35TM250MWmeasurement range | Mark A probe characteristics ¦ IEC60034-11,Motor temperature through PTC sensor, ~ 3 x 208…3 x 480 ¦ ,Short circuit of PTC sensor, same as above ¦ ,Phase lost , same as above ¦ ,Phase sequence, same as above ¦ ,Voltage Regeneration,
RM35TM250MWmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM35TM250MWminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM35TM250MWmonitoring functions | - governed by response time only - status reflects to R1 - fault status will be memorized and only resetable through power cycle, Test/Reset button or Y1-T1 volt-free input ¦ ,Motor temperature through PTC sensor, With Memory, - governed by response time only - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis ¦ ,Motor temperature through PTC sensor, Without Memory, - governed by response time only - status reflects to R1 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis ¦ ,Short circuit of PTC sensor, - governed by response time only, - status reflects to R2 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis ¦ ,Phase lost , - governed by response time only, - status reflects to R2 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis ¦ ,Phase sequence, - governed by response time only, - status reflects to R2 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis ¦ ,Voltage Regeneration, - governed by response time only, - status reflects to R2 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis ¦ ,Extreme undervoltage (Phase loss),
RM35TM250MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35TM250MWmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM35TM250MWnet weight | 95
RM35TM250MWon-load factor | 1
RM35TM250MWoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM35TM250MWoutput terminal | 15-16-18, 25-26-28
RM35TM250MWoutput type | 2 x C/O relay contacts
RM35TM250MWovervoltage category | 3 ¦ IEC60664-1
RM35TM250MWpolarity | No
RM35TM250MWpollution degree | 3 ¦ IEC60664-1
RM35TM250MWpower consumption | 1 4 VA / 2 0.5 W
RM35TM250MWpower on delay | 500
RM35TM250MWproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35TM250MWrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM35TM250MWrelease of input voltage | -
RM35TM250MWrepeat accuracy of the switching threshold | L1-L2-L3 ¦ ,Input terminal,
RM35TM250MWrepeat accuracy of time delay | -
RM35TM250MWreset time | 10 000 ¦ ,through Un power reset, >= 50 (press to release) ¦ ,through front panel reset, >= 50 (Y1 short to T1) ¦ ,through input control reset,
RM35TM250MWresponse time | 300 ¦ ,on crossing the threshold (Motor Temperature), 300 ¦ ,on crossing the hysteresis (all 3 Phase functions),
RM35TM250MWsafety reliability data | TBD ¦ ,MTTF, TBD ¦ ,B10,
RM35TM250MWseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM35TM250MWsetting accuracy of the switching threshold | 602/line ¦ ,Internal input resistance,
RM35TM250MWsetting accuracy of time delay | -
RM35TM250MWshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM35TM250MWshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM35TM250MWstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM35TM250MWstatus LED | Un (Green) R1 (Amber) R2 (Amber)
RM35TM250MWsupply frequency | 50 / 60 45…66
RM35TM250MWsupply terminal | A1-A2
RM35TM250MWsupply voltage limits | ~/-- 20.4…264
RM35TM250MWswitching threshold drift | ~ 3 x 176…3 x 528 ¦ ,permissible input overload, 50 / 60 ¦ ,Rated frequency,
RM35TM250MWthermal current | 8A ¦ IEC60947-5-1
RM35TM250MWtightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM35TM250MWtime delay drift | - -
RM35TM250MWtime delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35TM250MWtime delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35TM250MWtripping threshold | 3100 ± 10 % Internal design spec: TBD ¦ ,Motor temperature through PTC sensor, 0…15 ± 5 Internal design spec: TBD ¦ ,Short circuit of PTC sensor, 1 or more phase cut ¦ ,Phase lost , Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence, 1 or more phase =< 30% * [(L21 + L31 + L32) / 3] Internal design spec: TBD ¦ ,Voltage Regeneration, Internal design spec: TBD ¦ ,Extreme undervoltage (Phase loss),
RM35TM250MWvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM35TM250MWwidth | 35 ¦ ,Width,
RM35TM50MW | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 24…240 AC/DC ¦ ,Supply,Rated PTC probe ¦ ,Input 1,Voltage Push Button Switch ¦ ,Input 2,Spec 208..480 AC/DC ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, - - - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d,
RM35TM50MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IP50 (With Transparent Cover) ¦ IEC60529,Front Panel,
RM35TM50MWMaximum resistance of temperature sensor at 20°C | 1500Ω ¦ ,Maximum resistance of temperature sensor at 20°C,
RM35TM50MWMaximum voltage of temperature control circuit | 3.6V when T1-T2 is open ¦ ,Maximum voltage of temperature control circuit,
RM35TM50MWMinimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM35TM50MWTemperature sensing circuit short-circuit current | 7mA when T1-T2 is short-circuited ¦ ,Temperature sensing circuit short-circuit current,
RM35TM50MW[Ie] rated operational current | 8A ¦ IEC61810-1,Rated switching current,
RM35TM50MW[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM35TM50MW[Ui] rated insulation voltage | 250V ¦ IEC60664-1,Supply, 10V ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, 500V ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, 500V ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated 500V ¦ IEC60664-1,Supply / Input 3,Circuit 250V ¦ IEC60664-1,Supply / Output 1, 250V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, 500V ¦ IEC60664-1,Input 1 / Output 1, 500V ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, 500V ¦ IEC60664-1,Input 3 / Output 1, 500V ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM35TM50MW[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, 4kV, OVC3 ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, 4kV, OVC3 ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated 4kV, OVC3 ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 1, 4kV, OVC3 ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM35TM50MW[Us] rated supply voltage | ~/-- 24…240
RM35TM50MWambient air temperature for operation | -20oC..+60oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM35TM50MWambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM35TM50MWbump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM35TM50MWcable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM35TM50MWcircuit group | A1, A2 ¦ ,Supply,Terminal T1, T2 ¦ ,Input 1, - ¦ ,Input 2, L1, L2, L3 ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM35TM50MWconnections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35TM50MWcontacts material | Cadmium free
RM35TM50MWdepth | 72 ¦ ,Depth,
RM35TM50MWdiagnostic button | -
RM35TM50MWdielectric strength | 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM35TM50MWdirectives | 2014/35/EU 2014/30/EU 2011/65/EU
RM35TM50MWduty time | 1
RM35TM50MWelectrical durability | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM35TM50MWelectromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35TM50MWheight | 90 ¦ ,Height,
RM35TM50MWhysteresis | 1650 ± 10 % Internal design spec: TBD ¦ ,Motor temperature through PTC sensor, Internal design spec: TBD ¦ ,Short circuit of PTC sensor, All phase cut recover ¦ ,Phase lost , Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence, Internal design spec: TBD ¦ ,Voltage Regeneration, Internal design spec: TBD ¦ ,Extreme undervoltage (Phase loss),
RM35TM50MWimmunity to microbreaks | 20 ms at 20.4 V
RM35TM50MWinput frequency | Resistive Voltage Step Down ¦ ,Measurement mode,3 Phase
RM35TM50MWinput terminal | T1-T2 ¦ ,Input terminal,Motor temperature
RM35TM50MWinsulation resistance | >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM35TM50MWlocal signalling | Un - ON ¦ ,Power supply availability, Un - OFF ¦ ,Power supply not availability, - ¦ ,Timing in-progress, Rx - ON ¦ ,Output is energized, Rx - OFF ¦ ,Output is de-energized, - ¦ ,Range Setting Changes,
RM35TM50MWmarking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35TM50MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35TM50MWmaximum measuring cycle | 45…66 ¦ ,Frequency operating range,
RM35TM50MWmaximum switching capacity | 250V ¦ ,Maximum switching voltage, 8A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM35TM50MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35TM50MWmeasurement method | - ¦ ,Input nominal voltage selection,
RM35TM50MWmeasurement range | Mark A probe characteristics ¦ IEC60034-11,Motor temperature through PTC sensor, ~ 3 x 208…3 x 480 ¦ ,Short circuit of PTC sensor, same as above ¦ ,Phase lost , same as above ¦ ,Phase sequence, same as above ¦ ,Voltage Regeneration,
RM35TM50MWmechanical durability | 10 x 106 cycles ¦ IEC61810-1
RM35TM50MWminimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM35TM50MWmonitoring functions | - ¦ ,Motor temperature through PTC sensor, With Memory, - governed by response time only - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis ¦ ,Motor temperature through PTC sensor, Without Memory, - governed by response time only - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis ¦ ,Short circuit of PTC sensor, - governed by response time only, - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis ¦ ,Phase lost , - governed by response time only, - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis ¦ ,Phase sequence, - governed by response time only, - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis ¦ ,Voltage Regeneration, - governed by response time only, - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis ¦ ,Extreme undervoltage (Phase loss),
RM35TM50MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35TM50MWmounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM35TM50MWnet weight | 95
RM35TM50MWon-load factor | 1
RM35TM50MWoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM35TM50MWoutput terminal | 15-16-18, 25-26-28
RM35TM50MWoutput type | 2 x C/O relay contacts
RM35TM50MWovervoltage category | 3 ¦ IEC60664-1
RM35TM50MWpolarity | No
RM35TM50MWpollution degree | 3 ¦ IEC60664-1
RM35TM50MWpower consumption | 1 4 VA / 2 0.5 W
RM35TM50MWpower on delay | 500
RM35TM50MWproduct certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35TM50MWrelative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,
RM35TM50MWrelease of input voltage | -
RM35TM50MWrepeat accuracy of the switching threshold | L1-L2-L3 ¦ ,Input terminal,
RM35TM50MWrepeat accuracy of time delay | -
RM35TM50MWreset time | 10 000 ¦ ,through Un power reset, - ¦ ,through front panel reset, - ¦ ,through input control reset,
RM35TM50MWresponse time | 300 ¦ ,on crossing the threshold (Motor Temperature), 300 ¦ ,on crossing the hysteresis (all 3 Phase functions),
RM35TM50MWsafety reliability data | TBD ¦ ,MTTF, TBD ¦ ,B10,
RM35TM50MWseismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM35TM50MWsetting accuracy of the switching threshold | 602/line ¦ ,Internal input resistance,
RM35TM50MWsetting accuracy of time delay | -
RM35TM50MWshock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM35TM50MWshort circuit protection | 8A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM35TM50MWstandards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM35TM50MWstatus LED | Un (Green) R1 (Amber) R2 (Amber)
RM35TM50MWsupply frequency | 50 / 60 45…66
RM35TM50MWsupply terminal | A1-A2
RM35TM50MWsupply voltage limits | ~/-- 20.4…264
RM35TM50MWswitching threshold drift | ~ 3 x 176…3 x 528 ¦ ,permissible input overload, 50 / 60 ¦ ,Rated frequency,
RM35TM50MWthermal current | 8A ¦ IEC60947-5-1
RM35TM50MWtightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM35TM50MWtime delay drift | - -
RM35TM50MWtime delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35TM50MWtime delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35TM50MWtripping threshold | 3100 ± 10 % Internal design spec: TBD ¦ ,Motor temperature through PTC sensor, 0…15 ± 5 Internal design spec: TBD ¦ ,Short circuit of PTC sensor, 1 or more phase cut ¦ ,Phase lost , Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence, 1 or more phase =< 30% * [(L21 + L31 + L32) / 3] Internal design spec: TBD ¦ ,Voltage Regeneration, Internal design spec: TBD ¦ ,Extreme undervoltage (Phase loss),
RM35TM50MWvibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM35TM50MWwidth | 35 ¦ ,Width,
RM35UA11MW | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, 600 ¦ ,Supply,Rated 600 ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, - ¦ ,Over / undervoltage (windows mode), Selectable with memory / without memory ¦ ,Over voltage, Selectable with memory / without memory ¦ ,Undervoltage , ~/-- 0.05…5 5 ¦ ,E1-M / B1-C, 30 ¦ ,E2-M / B2-C, 50 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 0.05…0.5 ¦ ,E1-M / B1-C, ~/-- 0.3…3 ¦ ,E2-M / B2-C, ~/-- 0.5…5 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of 0.5V ¦ ,E1-M / B1-C, Adjustable 10%...100% of 3V ¦ ,E2-M / B2-C, Adjustable 10%...100% of 5V ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C, Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C, Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Resistive Voltage Step Down E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 True RMS MTTFd, B10d,
RM35UA11MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IEC60529,Front Panel,
RM35UA11MWMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM35UA11MW[Ie] rated operational current | IEC61810-1,Rated switching current,
RM35UA11MW[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM35UA11MW[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, 4 ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM35UA11MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM35UA11MW[Us] rated supply voltage | ~/-- 24…240
RM35UA11MWambient air temperature for operation | -20…+50 ¦ ,Operation,
RM35UA11MWambient air temperature for storage | -40…+70 ¦ ,Storage,
RM35UA11MWbump resistance | IEC60068-2-29
RM35UA11MWcable stripping length | Not specified ¦ ,Cable stripping length,
RM35UA11MWcircuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, 600 ¦ ,Output 2,
RM35UA11MWconnections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35UA11MWcontacts material | Cadmium-free
RM35UA11MWdepth | Depth,
RM35UA11MWdiagnostic button
RM35UA11MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM35UA11MWdirectives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
RM35UA11MWduty time | Not specified
RM35UA11MWelectrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM35UA11MWelectromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35UA11MWheight | Height,
RM35UA11MWimmunity to microbreaks | 10
RM35UA11MWinsulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM35UA11MWlocal signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM35UA11MWmarking | UL, CSA, GL, C-Tick, GOST, CE
RM35UA11MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35UA11MWmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 5 ¦ ,Maximum switching current, 1250 ¦ ,Maximum switching capacity,
RM35UA11MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35UA11MWmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM35UA11MWminimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM35UA11MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35UA11MWmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM35UA11MWnet weight | 130
RM35UA11MWon-load factor
RM35UA11MWoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
RM35UA11MWoutput terminal | 11-12-14, 21-22-24
RM35UA11MWoutput type | 2 x C/O relay contacts
RM35UA11MWovervoltage category | III ¦ IEC60664-1
RM35UA11MWpolarity
RM35UA11MWpollution degree | 3 ¦ IEC60664-1
RM35UA11MWpower consumption | ~ 3.5VA, -- 0.6W
RM35UA11MWpower on delay | 0
RM35UA11MWproduct certifications | UL, CSA, GL, C-Tick, GOST
RM35UA11MWrelative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM35UA11MWrelease of input voltage
RM35UA11MWrepeat accuracy of time delay | +/- 2%
RM35UA11MWreset time | 0
RM35UA11MWresponse time | Not specified ¦ ,on crossing the threshold,
RM35UA11MWsafety reliability data | MTTF, B10,
RM35UA11MWseismic resistance | IEC60068-3-3
RM35UA11MWsetting accuracy of time delay | +/- 10% of full scales
RM35UA11MWshock resistance | 5 gn ¦ IEC60068-2-27
RM35UA11MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM35UA11MWstandards | EN60255-6, IEC60255-6
RM35UA11MWstatus LED
RM35UA11MWsupply frequency | 50 / 60 45…66
RM35UA11MWsupply terminal | A1-A2
RM35UA11MWsupply voltage limits | ~/-- 20.4…264
RM35UA11MWthermal current | IEC60947-5-1
RM35UA11MWtightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM35UA11MWtime delay drift | Not specified Not specified
RM35UA11MWtime delay range | Adjustable 0.3…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35UA11MWtime delay type | · ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35UA11MWvibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM35UA11MWwidth | 35 x 90 x 72 ¦ ,Width,
RM35UA12MW | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, 600 ¦ ,Supply,Rated 600 ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, - ¦ ,Over / undervoltage (windows mode), Selectable with memory / without memory ¦ ,Over voltage, Selectable with memory / without memory ¦ ,Undervoltage , ~/-- 1…100 22 ¦ ,E1-M / B1-C, 110 ¦ ,E2-M / B2-C, 220 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 1…10 ¦ ,E1-M / B1-C, ~/-- 5…50 ¦ ,E2-M / B2-C, ~/-- 10…100 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% of 0.5V ¦ ,E1-M / B1-C, Adjustable 10%...100% of 3V ¦ ,E2-M / B2-C, Adjustable 10%...100% of 5V ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C, Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C, Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Resistive Voltage Step Down E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 True RMS MTTFd, B10d,
RM35UA12MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IEC60529,Front Panel,
RM35UA12MWMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM35UA12MW[Ie] rated operational current | IEC61810-1,Rated switching current,
RM35UA12MW[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM35UA12MW[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, 4 ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM35UA12MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM35UA12MW[Us] rated supply voltage | ~/-- 24…240
RM35UA12MWambient air temperature for operation | -20…+50 ¦ ,Operation,
RM35UA12MWambient air temperature for storage | -40…+70 ¦ ,Storage,
RM35UA12MWbump resistance | IEC60068-2-29
RM35UA12MWcable stripping length | Not specified ¦ ,Cable stripping length,
RM35UA12MWcircuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, 600 ¦ ,Output 2,
RM35UA12MWconnections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35UA12MWcontacts material | Cadmium-free
RM35UA12MWdepth | Depth,
RM35UA12MWdiagnostic button
RM35UA12MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM35UA12MWdirectives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
RM35UA12MWduty time | Not specified
RM35UA12MWelectrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM35UA12MWelectromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35UA12MWheight | Height,
RM35UA12MWimmunity to microbreaks | 10
RM35UA12MWinsulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM35UA12MWlocal signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM35UA12MWmarking | UL, CSA, GL, C-Tick, GOST, CE
RM35UA12MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35UA12MWmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 5 ¦ ,Maximum switching current, 1250 ¦ ,Maximum switching capacity,
RM35UA12MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35UA12MWmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM35UA12MWminimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM35UA12MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35UA12MWmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM35UA12MWnet weight | 130
RM35UA12MWon-load factor
RM35UA12MWoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
RM35UA12MWoutput terminal | 11-12-14, 21-22-24
RM35UA12MWoutput type | 2 x C/O relay contacts
RM35UA12MWovervoltage category | III ¦ IEC60664-1
RM35UA12MWpolarity
RM35UA12MWpollution degree | 3 ¦ IEC60664-1
RM35UA12MWpower consumption | ~ 3.5VA, -- 0.6W
RM35UA12MWpower on delay | 0
RM35UA12MWproduct certifications | UL, CSA, GL, C-Tick, GOST
RM35UA12MWrelative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM35UA12MWrelease of input voltage
RM35UA12MWrepeat accuracy of time delay | +/- 2%
RM35UA12MWreset time | 0
RM35UA12MWresponse time | Not specified ¦ ,on crossing the threshold,
RM35UA12MWsafety reliability data | MTTF, B10,
RM35UA12MWseismic resistance | IEC60068-3-3
RM35UA12MWsetting accuracy of time delay | +/- 10% of full scales
RM35UA12MWshock resistance | 5 gn ¦ IEC60068-2-27
RM35UA12MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM35UA12MWstandards | EN60255-6, IEC60255-6
RM35UA12MWstatus LED
RM35UA12MWsupply frequency | 50 / 60 45…66
RM35UA12MWsupply terminal | A1-A2
RM35UA12MWsupply voltage limits | ~/-- 20.4…264
RM35UA12MWthermal current | IEC60947-5-1
RM35UA12MWtightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM35UA12MWtime delay drift | Not specified Not specified
RM35UA12MWtime delay range | Adjustable 0.3…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35UA12MWtime delay type | · ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35UA12MWvibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM35UA12MWwidth | 35 x 90 x 72 ¦ ,Width,
RM35UA13MW | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, 600 ¦ ,Supply,Rated 600 ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, - ¦ ,Over / undervoltage (windows mode), Selectable with memory / without memory ¦ ,Over voltage, Selectable with memory / without memory ¦ ,Undervoltage , ~/-- 15…600 150 ¦ ,E1-M / B1-C, 300 ¦ ,E2-M / B2-C, 600 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 15…150 ¦ ,E1-M / B1-C, ~/-- 30…300 ¦ ,E2-M / B2-C, ~/-- 60…600 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 10%...100% ¦ ,E1-M / B1-C, Adjustable 10%...100% ¦ ,E2-M / B2-C, Adjustable 10%...100% ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 5%...50% of threshold setting ¦ ,E1-M / B1-C, Adjustable 5%...50% of threshold setting ¦ ,E2-M / B2-C, Adjustable 5%...50% of threshold setting ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Resistive Voltage Step Down E1-M, E2-M, E3-M 50 / 60 36…77 +/- 10% of full scale value +/- 0.5% < 1% over whole range 0.05% / oC 30 True RMS MTTFd, B10d,
RM35UA13MWIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, IEC60529,Front Panel,
RM35UA13MWMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM35UA13MW[Ie] rated operational current | IEC61810-1,Rated switching current,
RM35UA13MW[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM35UA13MW[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, 4 ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, 2 @ 50Hz for 1 minutes ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM35UA13MW[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, > 500MOhm @ -- 500V ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM35UA13MW[Us] rated supply voltage | ~/-- 24…240
RM35UA13MWambient air temperature for operation | -20…+50 ¦ ,Operation,
RM35UA13MWambient air temperature for storage | -40…+70 ¦ ,Storage,
RM35UA13MWbump resistance | IEC60068-2-29
RM35UA13MWcable stripping length | Not specified ¦ ,Cable stripping length,
RM35UA13MWcircuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, 600 ¦ ,Output 2,
RM35UA13MWconnections - terminals | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35UA13MWcontacts material | Cadmium-free
RM35UA13MWdepth | Depth,
RM35UA13MWdiagnostic button
RM35UA13MWdielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM35UA13MWdirectives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
RM35UA13MWduty time | Not specified
RM35UA13MWelectrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM35UA13MWelectromagnetic compatibility | IEC61000-6-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, · ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35UA13MWheight | Height,
RM35UA13MWimmunity to microbreaks | 10
RM35UA13MWinsulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM35UA13MWlocal signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM35UA13MWmarking | UL, CSA, GL, C-Tick, GOST, CE
RM35UA13MWmaximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35UA13MWmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 5 ¦ ,Maximum switching current, 1250 ¦ ,Maximum switching capacity,
RM35UA13MWmaximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35UA13MWmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM35UA13MWminimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM35UA13MWmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35UA13MWmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM35UA13MWnet weight | 130
RM35UA13MWon-load factor
RM35UA13MWoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
RM35UA13MWoutput terminal | 11-12-14, 21-22-24
RM35UA13MWoutput type | 2 x C/O relay contacts
RM35UA13MWovervoltage category | III ¦ IEC60664-1
RM35UA13MWpolarity
RM35UA13MWpollution degree | 3 ¦ IEC60664-1
RM35UA13MWpower consumption | ~ 3.5VA, -- 0.6W
RM35UA13MWpower on delay | 0
RM35UA13MWproduct certifications | UL, CSA, GL, C-Tick, GOST
RM35UA13MWrelative humidity | 2 cycles 24h ;+25°C +55°C 95%HR ¦ IEC60068-2-30,Damp heat,
RM35UA13MWrelease of input voltage
RM35UA13MWrepeat accuracy of time delay | +/- 2%
RM35UA13MWreset time | 0
RM35UA13MWresponse time | Not specified ¦ ,on crossing the threshold,
RM35UA13MWsafety reliability data | MTTF, B10,
RM35UA13MWseismic resistance | IEC60068-3-3
RM35UA13MWsetting accuracy of time delay | +/- 10% of full scales
RM35UA13MWshock resistance | 5 gn ¦ IEC60068-2-27
RM35UA13MWshort circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM35UA13MWstandards | EN60255-6, IEC60255-6
RM35UA13MWstatus LED
RM35UA13MWsupply frequency | 50 / 60 45…66
RM35UA13MWsupply terminal | A1-A2
RM35UA13MWsupply voltage limits | 0.85…1.1 Un (~/-- 20.4…264)
RM35UA13MWthermal current | IEC60947-5-1
RM35UA13MWtightening torque | 0.6…1 ¦ IEC60947-1,Tightening torque,
RM35UA13MWtime delay drift | Not specified Not specified
RM35UA13MWtime delay range | Adjustable 0.3…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35UA13MWtime delay type | · ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35UA13MWvibration resistance | 0.035mm from 10Hz…150Hz ¦ IEC60068-2-6
RM35UA13MWwidth | 35 x 90 x 72 ¦ ,Width,
RM35UB330 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 220..480 AC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, Yes - - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d, Drawing / Diagram
RM35UB330IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, - ¦ IEC60529,Front Panel,
RM35UB330Input nominal voltage selection | 220, 380, 400, 415, 440, 480 ¦ ,Input nominal voltage selection,
RM35UB330Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM35UB330[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM35UB330[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM35UB330[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, 500V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM35UB330[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM35UB330[Us] rated supply voltage | ~ 3 x 220…3 x 480
RM35UB330ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM35UB330ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM35UB330bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM35UB330cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM35UB330circuit group | L1, L2, L3 ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM35UB330connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35UB330contacts material | Cadmium free
RM35UB330depth | 72 ¦ ,Depth,
RM35UB330diagnostic button | -
RM35UB330dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM35UB330directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM35UB330duty time | 1
RM35UB330electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM35UB330electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35UB330height | 90 ¦ ,Height,
RM35UB330hysteresis | All phase cut recover ¦ ,Phase cut, Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Over voltage, Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, All phases > 205V Internal design spec: All phases >190V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: All phases > <533V +/- 5% ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM35UB330immunity to microbreaks | 0
RM35UB330input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
RM35UB330input terminal | L1-L2-L3 ¦ ,Input terminal,
RM35UB330insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM35UB330internal input resistance | - ¦ ,Internal input resistance,
RM35UB330local signalling | Un - ON ¦ ,Power supply availability, Un - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R1 / R2 - ON ¦ ,Output is energized, R 1 / R2 - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes, R 1 / R2 - OFF ¦ ,Phase Cut, R 1 / R2 - OFF ¦ ,Phase Sequence Swap, R2 - OFF ¦ ,Undervoltage <U, R 1 - OFF ¦ ,Overvoltage >U, - ¦ ,Phase Asymmetry, - ¦ ,Voltage Regeneration, R 1 / R2 - OFF ¦ ,Extreme Undervoltage <U (Phase loss), R 1 / R2 - OFF ¦ ,Extreme Overvoltage >U, - ¦ ,Extreme Phase Asymmetry,
RM35UB330marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35UB330maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35UB330maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM35UB330maximum switching capacity | 250V ¦ ,Maximum switching voltage, 5A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM35UB330maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35UB330measurement method | True RMS ¦ ,Measurement method,
RM35UB330measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), +2…+20 % in the ranges 3 x ~ 220…440 +2…+10 % in the range 3 x ~ 480 ¦ ,Over voltage, -12…-2 % in the range 3 x ~ 220 -20…-2 % in the ranges 3 x ~ 380…480 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, - ¦ ,Extreme undervoltage, - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM35UB330mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM35UB330minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM35UB330monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost , governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), governed by time delay Tt1, status reflects to R1 ¦ ,Over voltage, governed by time delay Tt2, status reflects to R2 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM35UB330mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35UB330mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM35UB330net weight | 130
RM35UB330on-load factor | 1
RM35UB330output logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM35UB330output terminal | 11-12-14, 21-22-24
RM35UB330output type | 1 x C/O + 1 x C/O relay contacts
RM35UB330overvoltage category | 3 ¦ IEC60664-1
RM35UB330permissible input overload | - ¦ ,permissible input overload,
RM35UB330polarity | -
RM35UB330pollution degree | 3 ¦ IEC60664-1
RM35UB330power consumption | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz
RM35UB330power on delay | 0
RM35UB330product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35UB330relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM35UB330release of input voltage | -
RM35UB330repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM35UB330repeat accuracy of time delay | +/- 3%
RM35UB330reset time | 0
RM35UB330response time | 0
RM35UB330safety reliability data | 2,800,000 hours ¦ ,MTTF, 300,000 hours ¦ ,B10,
RM35UB330seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM35UB330setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM35UB330setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM35UB330shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM35UB330short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM35UB330standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM35UB330status LED | Un (Green) R1 (Amber) R2 (Amber)
RM35UB330supply frequency | 50 / 60 45…66
RM35UB330supply terminal | L1-N
RM35UB330supply voltage limits | ~ 3 x 194…3 x 528
RM35UB330switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation, < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM35UB330thermal current | 5A ¦ IEC60947-5-1
RM35UB330tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM35UB330time delay drift | - -
RM35UB330time delay range | Adjustable Tt1 0.1…30 for overvoltage @ R1 (11-12-14) Adjustable Tt2 0.1…30 for undervoltage @ R2 (21-22-24) ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35UB330time delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35UB330tripping threshold | 1 or more phase cut ¦ ,Phase cut, Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Adjustable 2%...20% of selected Un ¦ ,Over voltage, Adjustable 2%...20% of selected Un ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, 1 or more phase < 150V Internal design spec: 1 or more phase <188V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: 543V +/- 5% ¦ ,Extreme Overvoltage, Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM35UB330vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM35UB330width | 35 ¦ ,Width,
RM35UB3N30 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) ¦ IEC60721-3-3,Climatic category, Class C ¦ Germanisher Lloyd,Environmental category, 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60947-5-1,Cyclic Damp Heat Test, 120..277 AC ¦ ,Supply,Rated - ¦ ,Input 1,Voltage - ¦ ,Input 2,Spec - ¦ ,Input 3, 250V ¦ ,Output 1, 250V ¦ ,Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, Yes - - 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) ¦ ,MTTFd, Cannot declare B10 = B10d (Note: customer confuses as safety product) ¦ ,B10d, Drawing / Diagram
RM35UB3N30IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP30 ¦ IEC60529,Housing, - ¦ IEC60529,Front Panel,
RM35UB3N30Input nominal voltage selection | 120, 127, 220, 230, 240, 260, 277 ¦ ,Input nominal voltage selection,
RM35UB3N30Minimum distance to adjacent devices | 1x product height ¦ ,Horizontal, 1x product width ¦ ,Vertical,
RM35UB3N30[Ie] rated operational current | 5A ¦ IEC61810-1,Rated switching current,
RM35UB3N30[Ue] rated operational voltage | 250V ¦ IEC61810-1,Rated switching voltage,
RM35UB3N30[Ui] rated insulation voltage | 500V ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, 250V ¦ IEC60664-1,Output 1, 250V ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 500V ¦ IEC60664-1,Supply / Output 1, 500V ¦ IEC60664-1,Supply / Output 2, 250V ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM35UB3N30[Uimp] rated impulse withstand voltage | 4kV, OVC3 ¦ IEC60664-1,Supply, - ¦ IEC60664-1,Input 1, - ¦ IEC60664-1,Input 2, - ¦ IEC60664-1,Input 3, - ¦ IEC60664-1,Output 1, - ¦ IEC60664-1,Output 2, - ¦ IEC60664-1,Supply / Input 1,Galvanic - ¦ IEC60664-1,Supply / Input 2,Isolated - ¦ IEC60664-1,Supply / Input 3,Circuit 4kV, OVC3 ¦ IEC60664-1,Supply / Output 1, 4kV, OVC3 ¦ IEC60664-1,Supply / Output 2, 4kV, OVC3 ¦ IEC60664-1,Output 1 / Output 2, - ¦ IEC60664-1,Input 1 / Output 1, - ¦ IEC60664-1,Input 1 / Output 2, - ¦ IEC60664-1,Input 2 / Output 1, - ¦ IEC60664-1,Input 2 / Output 2, - ¦ IEC60664-1,Input 3 / Output 1, - ¦ IEC60664-1,Input 3 / Output 2, - ¦ IEC60664-1,Input 1 / Input 2, - ¦ IEC60664-1,Input 2 / Input 3, - ¦ IEC60664-1,Input 1 / Input 3,
RM35UB3N30[Us] rated supply voltage | ~ 3 x 120…3 x 277
RM35UB3N30ambient air temperature for operation | -20oC..+50oC @50Hz -20oC..+50oC @60Hz ¦ ,Operation,
RM35UB3N30ambient air temperature for storage | -40oC..+70oC ¦ ,Storage,
RM35UB3N30bump resistance | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) ¦ IEC60068-2-29
RM35UB3N30cable stripping length | 6mm (Screw Terminal) ¦ ,Cable stripping length,
RM35UB3N30circuit group | L1, L2, L3, N ¦ ,Supply,Terminal - ¦ ,Input 1, - ¦ ,Input 2, - ¦ ,Input 3, 11,12,14 ¦ ,Output 1, 21,22,24 ¦ ,Output 2,
RM35UB3N30connections - terminals | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) ¦ IEC60947-1,Solid cable without cable end (screw terminal), 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM35UB3N30contacts material | Cadmium free
RM35UB3N30depth | 72 ¦ ,Depth,
RM35UB3N30diagnostic button | -
RM35UB3N30dielectric strength | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 1, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Supply / Output 2, 2.0kV, 50/60Hz for 1 min ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM35UB3N30directives | 2014/35/EU 2014/30/EU 2011/65/EU
RM35UB3N30duty time | 1
RM35UB3N30electrical durability | NO: 250VAC/5A, 100k cycles ¦ IEC60947-4-1,AC-1, NO: 24VDC/5A, 100k cycles ¦ IEC60947-4-1,DC-1, NO: 250VAC/0.15A, 100k cycles ¦ IEC60947-5-1,AC-15, NO: 24VDC/1A, 100k cycles ¦ IEC60947-5-1,DC-13,
RM35UB3N30electromagnetic compatibility | IEC61000-6-1, IEC 61000-6-2 ¦ ,Generic immunity standard, Level III (Contact : 6kV / Air : 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) ¦ IEC61000-4-4,Fast transient / burst, Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) ¦ IEC61000-4-5,Surge, Level III (10Vrms : 0.15MHz to 80MHz) ¦ IEC61000-4-6,Conducted RF disturbance, Level IV (30A/m : continous) (300A/m : 3s) ¦ IEC61000-4-8,Power frequency magnetic field, Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) ¦ IEC61000-4-18,1 MHz oscillation wave, - ¦ IEC61000-4-29,DC voltage interruption, - ¦ IEC61000-4-13,Low frequency harmonics, DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC 61000-6-4 ¦ ,Generic emission standard, Class B ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B, Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM35UB3N30height | 90 ¦ ,Height,
RM35UB3N30hysteresis | All phase cut recover ¦ ,Phase cut, Total phase swap recover Internal design spec: L23 lags L13 < 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Over voltage, Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, All phases > 100V Internal design spec: All phases >88V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: All phases <358V +/- 5% ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM35UB3N30immunity to microbreaks | 5
RM35UB3N30input frequency | 50 / 60 ¦ ,Rated frequency, 45…66 ¦ ,Frequency operating range,
RM35UB3N30input terminal | L1-L2-L3-N ¦ ,Input terminal,
RM35UB3N30insulation resistance | - ¦ IEC60255-27,Supply / Input 1, - ¦ IEC60255-27,Supply / Input 2, - ¦ IEC60255-27,Supply / Input 3, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 1, >100 MOhm at 500 V DC ¦ IEC60255-27,Supply / Output 2, >100 MOhm at 500 V DC ¦ IEC60255-27,Output 1 / Output 2, - ¦ IEC60255-27,Input 1 / Output 1, - ¦ IEC60255-27,Input 1 / Output 2, - ¦ IEC60255-27,Input 2 / Output 1, - ¦ IEC60255-27,Input 2 / Output 2, - ¦ IEC60255-27,Input 3 / Output 1, - ¦ IEC60255-27,Input 3 / Output 2, - ¦ IEC60255-27,Input 1 / Input 2, - ¦ IEC60255-27,Input 2 / Input 3, - ¦ IEC60255-27,Input 1 / Input 3,
RM35UB3N30internal input resistance | - ¦ ,Internal input resistance,
RM35UB3N30local signalling | Un - ON ¦ ,Power supply availability, Un - OFF ¦ ,Power supply not availability, R - Slow Blink (50% ON; 50% OFF) @ 1Hz ¦ ,Timing in-progress, R1 / R2 - ON ¦ ,Output is energized, R 1 / R2 - OFF ¦ ,Output is de-energized, All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz ¦ ,Range Setting Changes, R 1 / R2 - OFF ¦ ,Phase Cut, R 1 / R2 - OFF ¦ ,Phase Sequence Swap, R2 - OFF ¦ ,Undervoltage <U, R 1 - OFF ¦ ,Overvoltage >U, - ¦ ,Phase Asymmetry, - ¦ ,Voltage Regeneration, R 1 / R2 - OFF ¦ ,Extreme Undervoltage <U (Phase loss), R 1 / R2 - OFF ¦ ,Extreme Overvoltage >U, - ¦ ,Extreme Phase Asymmetry,
RM35UB3N30marking | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35UB3N30maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM35UB3N30maximum measuring cycle | 150ms / measurement as true rms value ¦ ,Maximum measuring cycles,
RM35UB3N30maximum switching capacity | 250V ¦ ,Maximum switching voltage, 5A ¦ ,Maximum switching current, - ¦ ,Maximum switching capacity,
RM35UB3N30maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM35UB3N30measurement method | True RMS ¦ ,Measurement method,
RM35UB3N30measurement range | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), +2…+20 % in the ranges 3 x ~ 120…277 ¦ ,Over voltage, -2…-20 % in the ranges 3 x ~ 120…277 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, - ¦ ,Extreme undervoltage, - ¦ ,Extreme Overvoltage, - ¦ ,Extreme Asymmetry,
RM35UB3N30mechanical durability | 30 x 106 cycles ¦ IEC61810-1
RM35UB3N30minimum switching capacity | - ¦ IEC60947-5-4,Minimum switching voltage, - ¦ IEC60947-5-4,Minimum switching current, NO: 12V/10mA, MCTF > 80,000,000 ¦ IEC60947-5-4,Minimum switching capacity,
RM35UB3N30monitoring functions | governed by response time only, status reflects to both R1 & R2 ¦ ,Phase lost , governed by response time only, status reflects to both R1 & R2 ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), governed by time delay Tt1, status reflects to R1 ¦ ,Over voltage, governed by time delay Tt2, status reflects to R2 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, governed by response time only, status reflects to both R1 & R2 ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme undervoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme overvoltage, governed by response time only, status reflects to both R1 & R2 ¦ ,Extreme asymmetry,
RM35UB3N30mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM35UB3N30mounting support | On 35 mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM35UB3N30net weight | 130
RM35UB3N30on-load factor | 1
RM35UB3N30output logic | Energized on fault-free ¦ ,R1 (11-12-14), Energized on fault-free ¦ ,R2 (21-22-24),
RM35UB3N30output terminal | 11-12-14, 21-22-24
RM35UB3N30output type | 1 x C/O + 1 x C/O relay contacts
RM35UB3N30overvoltage category | 3 ¦ IEC60664-1
RM35UB3N30permissible input overload | - ¦ ,permissible input overload,
RM35UB3N30polarity | -
RM35UB3N30pollution degree | 3 ¦ IEC60664-1
RM35UB3N30power consumption | 3.9VA @ 480VAC, 60Hz
RM35UB3N30power on delay | 0
RM35UB3N30product certifications | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
RM35UB3N30relative humidity | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% ¦ IEC60068-2-30,Damp heat,XX
RM35UB3N30release of input voltage | -
RM35UB3N30repeat accuracy of the switching threshold | +/- 0.5% ¦ ,Repeat accuracy (constant parameters),
RM35UB3N30repeat accuracy of time delay | +/- 3%
RM35UB3N30reset time | 0
RM35UB3N30response time | 0
RM35UB3N30safety reliability data | 4,400,000 hours ¦ ,MTTF, 470,000 hours ¦ ,B10,
RM35UB3N30seismic resistance | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz ¦ IEC60068-3-3
RM35UB3N30setting accuracy of the switching threshold | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) ¦ ,Setting accuracy,
RM35UB3N30setting accuracy of time delay | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
RM35UB3N30shock resistance | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) ¦ IEC60068-2-27
RM35UB3N30short circuit protection | 5A ¦ IEC60947-5-1,Relay Output by external fuse, - ¦ IEC62314,Solid State Output by external fuse,
RM35UB3N30standards | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
RM35UB3N30status LED | Un (Green) R1 (Amber) R2 (Amber)
RM35UB3N30supply frequency | 50 / 60 45…66
RM35UB3N30supply terminal | L1-L3
RM35UB3N30supply voltage limits | ~ 3 x 114…3 x 329
RM35UB3N30switching threshold drift | < 1% of selected Un ¦ ,Measurement error with supply voltage variation, < 0.05% / oC ¦ ,Measurement error with temperature variation,
RM35UB3N30thermal current | 5A ¦ IEC60947-5-1
RM35UB3N30tightening torque | 0.6…1 Nm ¦ IEC60947-1,Tightening torque,
RM35UB3N30time delay drift | - -
RM35UB3N30time delay range | Adjustable Tt1 0.1…30 for overvoltage @ R1 (11-12-14) Adjustable Tt2 0.1…30 for undervoltage @ R2 (21-22-24) ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35UB3N30time delay type | Yes ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM35UB3N30tripping threshold | 1 or more phase cut ¦ ,Phase cut, Total swap of phase Internal design spec: L23 lags L13 >= 180o ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Adjustable 2%...20% of selected Un ¦ ,Over voltage, Adjustable 2%...20% of selected Un ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Total cut of N ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, 1 or more phase < 80V Internal design spec: 1 or more phase <86V +/- 5% ¦ ,Extreme undervoltage (Phase loss), Internal design spec: 368V +/- 5% ¦ ,Extreme Overvoltage, Internal design spec: 48% +/- 6% ¦ ,Extreme Asymmetry,
RM35UB3N30vibration resistance | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) ¦ IEC60068-2-6
RM35UB3N30width | 35 ¦ ,Width,
RM4JA01 | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Not specified ¦ ,Supply,Rated Not specified ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, - ¦ ,Over / undercurrent (windows mode), Without memory ¦ ,Over current, Without memory ¦ ,Under current, ~/-- 3…1000 33 ¦ ,E1-M / B1-C, 10 ¦ ,E2-M / B2-C, 1 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, ~/-- 3…30 ¦ ,E1-M / B1-C, ~/-- 10…1000 ¦ ,E2-M / B2-C, ~/-- 100…1000 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, - ¦ ,E1-M / B1-C, Adjustable 10%...100% ¦ ,E2-M / B2-C, Adjustable 10%...100% ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 5%...30% of threshold setting ¦ ,E1-M / B1-C, Adjustable 5%...30% of threshold setting ¦ ,E2-M / B2-C, Adjustable 5%...30% of threshold setting ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Shunt resistor B1-C, B2-C, B3-C 50 / 60 Not specified +/- 10% of full scale value Not specified < 0.5% over whole range 0.06% / oC 80 True RMS MTTFd, B10d,
RM4JA01IP degree of protection | Not specified ¦ IEC60529,Terminal Block, Not specified ¦ IEC60529,Housing, IEC60529,Front Panel,
RM4JA01Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM4JA01[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4JA01[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4JA01[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, Not specified ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4JA01[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4JA01[Us] rated supply voltage | RM4JA01B: ~ 24 RM4JA01F: ~110…130 RM4JA01M: ~220…240
RM4JA01ambient air temperature for operation | Not specified ¦ ,Operation,
RM4JA01ambient air temperature for storage | Not specified ¦ ,Storage,
RM4JA01bump resistance | IEC60068-2-29
RM4JA01cable stripping length | Not specified ¦ ,Cable stripping length,
RM4JA01circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Not specified ¦ ,Output 2,
RM4JA01connections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal), Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4JA01contacts material | Cadmium free
RM4JA01depth | Depth,
RM4JA01diagnostic button
RM4JA01dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4JA01directives
RM4JA01duty time | Not specified
RM4JA01electrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM4JA01electromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B Group1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B Group1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B Group1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B Group1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4JA01height | Height,
RM4JA01immunity to microbreaks | Not specified
RM4JA01insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4JA01local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM4JA01marking | UL, CSA, GL, C-Tick, GOST, CE, CCC
RM4JA01maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM4JA01maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 8 ¦ ,Maximum switching current, 2000 ¦ ,Maximum switching capacity,
RM4JA01maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM4JA01mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM4JA01minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM4JA01mounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
RM4JA01mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM4JA01net weight | Not specified
RM4JA01on-load factor
RM4JA01output logic | De-Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
RM4JA01output terminal | 11-12-14, 21-22-24
RM4JA01output type | 2 x C/O relay contacts
RM4JA01overvoltage category | Not specified ¦ IEC60664-1
RM4JA01polarity
RM4JA01pollution degree | Not specified ¦ IEC60664-1
RM4JA01power consumption | RM4JA01B: ~ 2VA RM4JA01F: ~ 3.3VA RM4JA01M: ~ 3.5VA
RM4JA01power on delay | 0
RM4JA01product certifications | UL, CSA, GL, C-Tick, GOST, CCC
RM4JA01relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
RM4JA01release of input voltage
RM4JA01repeat accuracy of time delay | +/- 0.5%
RM4JA01reset time | 0
RM4JA01response time | Not specified ¦ ,on crossing the threshold,
RM4JA01safety reliability data | MTTF, B10,
RM4JA01seismic resistance | IEC60068-3-3
RM4JA01setting accuracy of time delay | +/- 10% of full scales
RM4JA01shock resistance | Not specified ¦ IEC60068-2-27
RM4JA01short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM4JA01standards | EN60255-6, IEC60255-6
RM4JA01status LED
RM4JA01supply frequency | 50 / 60 Not specified
RM4JA01supply terminal | A1-A2
RM4JA01supply voltage limits | 0.85…1.1 Un
RM4JA01thermal current | IEC60947-5-1
RM4JA01tightening torque | Not specified ¦ IEC60947-1,Tightening torque,
RM4JA01time delay drift | < 0.5% over whole range 0.07% / oC
RM4JA01time delay range | Adjustable 0…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, Adjustable 1…20 ¦ ,Inhibition,
RM4JA01time delay type | · ¦ ,"OFF" delay, - ¦ ,"ON" delay, · ¦ ,Inhibition,
RM4JA01vibration resistance | Not specified ¦ IEC60068-2-6
RM4JA01width | 22.5 x 78 x 80 ¦ ,Width,
RM4JA3 | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Not specified ¦ ,Supply,Rated Not specified ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, - ¦ ,Over / undercurrent (windows mode), Without memory ¦ ,Over current, Without memory ¦ ,Under current, RM4JA31xx: ~/-- 3…1000 RM4JA32xx: ~/-- 300…15000 RM4JA31xx: 33 RM4JA32xx: ~/-- 0.06 ¦ ,E1-M / B1-C, RM4JA31xx: 10 RM4JA32xx: ~/-- 0.02 ¦ ,E2-M / B2-C, RM4JA31xx: 1 RM4JA32xx: ~/-- 0.006 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, RM4JA31xx: ~/-- 3…30 RM4JA32xx: ~/-- 300…1500 ¦ ,E1-M / B1-C, RM4JA31xx: ~/-- 10…1000 RM4JA32xx: ~/-- 1000…5000 ¦ ,E2-M / B2-C, RM4JA31xx: ~/-- 100…1000 RM4JA32xx: ~/-- 3000…15000 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, - ¦ ,E1-M / B1-C, Adjustable 10%...100% ¦ ,E2-M / B2-C, Adjustable 10%...100% ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 5%...30% of threshold setting ¦ ,E1-M / B1-C, Adjustable 5%...30% of threshold setting ¦ ,E2-M / B2-C, Adjustable 5%...30% of threshold setting ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Shunt resistor B1-C, B2-C, B3-C 50 / 60 Not specified +/- 10% of full scale value Not specified < 0.5% over whole range 0.06% / oC 80 True RMS MTTFd, B10d,
RM4JA3IP degree of protection | Not specified ¦ IEC60529,Terminal Block, Not specified ¦ IEC60529,Housing, IEC60529,Front Panel,
RM4JA3Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM4JA3[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4JA3[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4JA3[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, Not specified ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4JA3[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4JA3[Us] rated supply voltage | RM4JA3xMW: ~/-- 24…240 RM4JA3xF: ~110…130 RM4JA3xM: ~220…240 RM4JA3xQ: ~380…415
RM4JA3ambient air temperature for operation | Not specified ¦ ,Operation,
RM4JA3ambient air temperature for storage | Not specified ¦ ,Storage,
RM4JA3bump resistance | IEC60068-2-29
RM4JA3cable stripping length | Not specified ¦ ,Cable stripping length,
RM4JA3circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Not specified ¦ ,Output 2,
RM4JA3connections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal), Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4JA3contacts material | Cadmium free
RM4JA3depth | Depth,
RM4JA3diagnostic button
RM4JA3dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4JA3directives
RM4JA3duty time | Not specified
RM4JA3electrical durability | 1 x 105 switching cycles ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM4JA3electromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B Group1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B Group1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B Group1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B Group1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4JA3height | Height,
RM4JA3immunity to microbreaks | Not specified
RM4JA3insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4JA3local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM4JA3marking | UL, CSA, GL, C-Tick, GOST, CE, CCC
RM4JA3maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM4JA3maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, ~ 5 ¦ ,Maximum switching current, 1250 ¦ ,Maximum switching capacity,
RM4JA3maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM4JA3mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM4JA3minimum switching capacity | 5 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 50 ¦ IEC60947-5-4,Minimum switching capacity,
RM4JA3mounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
RM4JA3mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM4JA3net weight | Not specified
RM4JA3on-load factor
RM4JA3output logic | De-Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
RM4JA3output terminal | 11-12-14, 21-22-24
RM4JA3output type | 2 x C/O relay contacts
RM4JA3overvoltage category | Not specified ¦ IEC60664-1
RM4JA3polarity
RM4JA3pollution degree | Not specified ¦ IEC60664-1
RM4JA3power consumption | RM4JA3xMW: ~ 3.3VA, -- 1.2W RM4JA3xF: ~ 3.3VA RM4JA3xM: ~ 3.4VA RM4JA3xQ: ~ 3VA
RM4JA3power on delay | 0
RM4JA3product certifications | UL, CSA, GL, C-Tick, GOST, CCC
RM4JA3relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
RM4JA3release of input voltage
RM4JA3repeat accuracy of time delay | +/- 0.5%
RM4JA3reset time | 0
RM4JA3response time | Not specified ¦ ,on crossing the threshold,
RM4JA3safety reliability data | MTTF, B10,
RM4JA3seismic resistance | IEC60068-3-3
RM4JA3setting accuracy of time delay | +/- 10% of full scales
RM4JA3shock resistance | Not specified ¦ IEC60068-2-27
RM4JA3short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM4JA3standards | EN60255-6, IEC60255-6
RM4JA3status LED
RM4JA3supply frequency | 50 / 60 Not specified
RM4JA3supply terminal | A1-A2
RM4JA3supply voltage limits | 0.85…1.1 Un
RM4JA3thermal current | IEC60947-5-1
RM4JA3tightening torque | Not specified ¦ IEC60947-1,Tightening torque,
RM4JA3time delay drift | < 0.5% over whole range 0.07% / oC
RM4JA3time delay range | Adjustable 0…30 ¦ ,"OFF" delay, - ¦ ,"ON" delay, Adjustable 1…20 ¦ ,Inhibition,
RM4JA3time delay type | · ¦ ,"OFF" delay, - ¦ ,"ON" delay, · ¦ ,Inhibition,
RM4JA3vibration resistance | Not specified ¦ IEC60068-2-6
RM4JA3width | RM4JA31xx: 22.5 x 78 x 80 RM4JA32xx: 45 x 78 x 80 ¦ ,Width,
RM4LA32 | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Not specified ¦ ,Supply,Rated Not specified ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d,
RM4LA32IP degree of protection | Not specified ¦ IEC60529,Terminal Block, Not specified ¦ IEC60529,Housing, IEC60529,Front Panel,
RM4LA32Maximum length of probes cable | 1000 ¦ ,Maximum length of probes cable,
RM4LA32Maximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
RM4LA32Maximum probe supplied voltage | 24 ¦ ,Maximum probe supplied voltage,
RM4LA32Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM4LA32[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4LA32[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4LA32[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, Not specified ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4LA32[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4LA32[Us] rated supply voltage | RM4LA32B: ~ 24 RM4LA32F: ~110…130 RM4LA32M: ~220…240 RM4LA32MW: ~/-- 24…240 RM4LA32Q: ~380…415
RM4LA32ambient air temperature for operation | Not specified ¦ ,Operation,
RM4LA32ambient air temperature for storage | Not specified ¦ ,Storage,
RM4LA32bump resistance | IEC60068-2-29
RM4LA32cable stripping length | Not specified ¦ ,Cable stripping length,
RM4LA32circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Not specified ¦ ,Output 2,
RM4LA32connections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal), Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4LA32contacts material | Not specified
RM4LA32depth | Depth,
RM4LA32diagnostic button
RM4LA32dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4LA32directives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
RM4LA32duty time | Not specified
RM4LA32electrical durability | Not specified ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM4LA32electromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B Group1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B Group1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B Group1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B Group1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4LA32height | Height,
RM4LA32hysteresis | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM4LA32immunity to microbreaks | Not specified
RM4LA32input frequency | Maximum cable capacitance,
RM4LA32input terminal | Input terminal,
RM4LA32insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4LA32internal input resistance | Internal input resistance,
RM4LA32local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM4LA32marking | UL, CSA, GL, C-Tick, GOST, CE
RM4LA32maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM4LA32maximum measuring cycle | Maximum measuring cycles,
RM4LA32maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 8 ¦ ,Maximum switching current, 2000VA ¦ ,Maximum switching capacity,
RM4LA32maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM4LA32measurement method | Liquid level probe ¦ ,Measurement method,
RM4LA32measurement range | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM4LA32mechanical durability | Not specified ¦ IEC61810-1
RM4LA32minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching voltage, Not specified ¦ IEC60947-5-4,Minimum switching current, Not specified ¦ IEC60947-5-4,Minimum switching capacity,
RM4LA32monitoring functions | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM4LA32mounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
RM4LA32mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM4LA32net weight | 168
RM4LA32on-load factor
RM4LA32output logic | Not specified ¦ ,R1 (11-12-14), R2 (21-22-24),
RM4LA32output terminal | 15-16-18, 25-26-28
RM4LA32output type | 2 x C/O relay contacts
RM4LA32overvoltage category | Not specified ¦ IEC60664-1
RM4LA32polarity
RM4LA32pollution degree | Not specified ¦ IEC60664-1
RM4LA32power consumption | RM4LA32B: 3.1VA RM4LA32F: 2.7VA RM4LA32M: 2.6VA RM4LA32MW: 2.7VA, 2.4W RM4LA32Q: 3.4VA
RM4LA32power on delay | Not specified
RM4LA32product certifications | UL, CSA, GL, C-Tick, GOST
RM4LA32relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
RM4LA32release of input voltage
RM4LA32repeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM4LA32repeat accuracy of time delay | Not specified
RM4LA32reset time | Not specified ¦ ,through Un power reset, through front panel reset, through input control reset,
RM4LA32response time | Not specified ¦ ,on crossing the threshold,
RM4LA32safety reliability data | MTTF, B10,
RM4LA32seismic resistance | IEC60068-3-3
RM4LA32setting accuracy of the switching threshold | Not specified ¦ ,Setting accuracy,
RM4LA32setting accuracy of time delay | Not specified
RM4LA32shock resistance | Not specified ¦ IEC60068-2-27
RM4LA32short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM4LA32standards | EN60255-6, IEC60255-6
RM4LA32status LED
RM4LA32supply frequency | 50 / 60 Not specified
RM4LA32supply terminal | A1-A2
RM4LA32supply voltage limits | Not specified
RM4LA32switching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation, Not specified ¦ ,Measurement error with temperature variation,
RM4LA32thermal current | 8 ¦ IEC60947-5-1
RM4LA32tightening torque | Not specified ¦ IEC60947-1,Tightening torque,
RM4LA32time delay drift | Not specified Not specified
RM4LA32time delay range | Adjustable 0.1…10 ¦ ,"OFF" delay, Adjustable 0.1…10 ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4LA32time delay type | · ¦ ,"OFF" delay, · ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4LA32tripping threshold | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM4LA32vibration resistance | Not specified ¦ IEC60068-2-6
RM4LA32width | 22.5 x 78 x 80 ¦ ,Width,
RM4LG01 | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Not specified ¦ ,Supply,Rated Not specified ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d,
RM4LG01IP degree of protection | Not specified ¦ IEC60529,Terminal Block, Not specified ¦ IEC60529,Housing, IEC60529,Front Panel,
RM4LG01Maximum length of probes cable | 1000 ¦ ,Maximum length of probes cable,
RM4LG01Maximum probe supplied current | 1 ¦ ,Maximum probe supplied current,
RM4LG01Maximum probe supplied voltage | 24 ¦ ,Maximum probe supplied voltage,
RM4LG01Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM4LG01[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4LG01[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4LG01[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, Not specified ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4LG01[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4LG01[Us] rated supply voltage | RM4LA32B: ~ 24 RM4LA32F: ~110…130 RM4LA32M: ~220…240 RM4LA32Q: ~380…415
RM4LG01ambient air temperature for operation | Not specified ¦ ,Operation,
RM4LG01ambient air temperature for storage | Not specified ¦ ,Storage,
RM4LG01bump resistance | IEC60068-2-29
RM4LG01cable stripping length | Not specified ¦ ,Cable stripping length,
RM4LG01circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Not specified ¦ ,Output 2,
RM4LG01connections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal), Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4LG01contacts material | Not specified
RM4LG01depth | Depth,
RM4LG01diagnostic button
RM4LG01dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4LG01directives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
RM4LG01duty time | Not specified
RM4LG01electrical durability | Not specified ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM4LG01electromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B Group1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B Group1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B Group1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B Group1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4LG01height | Height,
RM4LG01hysteresis | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM4LG01immunity to microbreaks | Not specified
RM4LG01input frequency | Maximum cable capacitance,
RM4LG01input terminal | Input terminal,
RM4LG01insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4LG01internal input resistance | Internal input resistance,
RM4LG01local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM4LG01marking | UL, CSA, GL, C-Tick, GOST, CE
RM4LG01maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM4LG01maximum measuring cycle | Maximum measuring cycles,
RM4LG01maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 8 ¦ ,Maximum switching current, 2000VA ¦ ,Maximum switching capacity,
RM4LG01maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM4LG01measurement method | Liquid level probe ¦ ,Measurement method,
RM4LG01measurement range | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM4LG01mechanical durability | Not specified ¦ IEC61810-1
RM4LG01minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching voltage, Not specified ¦ IEC60947-5-4,Minimum switching current, Not specified ¦ IEC60947-5-4,Minimum switching capacity,
RM4LG01monitoring functions | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM4LG01mounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
RM4LG01mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM4LG01net weight | 168
RM4LG01on-load factor
RM4LG01output logic | Not specified ¦ ,R1 (11-12-14), R2 (21-22-24),
RM4LG01output terminal | 15-16-18
RM4LG01output type | 1 x C/O relay contacts
RM4LG01overvoltage category | Not specified ¦ IEC60664-1
RM4LG01polarity
RM4LG01pollution degree | Not specified ¦ IEC60664-1
RM4LG01power consumption | RM4LG01B: 1.9VA RM4LG01F: 2.6VA RM4LG01M: 2.4VA RM4LG01Q: 2.9VA
RM4LG01power on delay | Not specified
RM4LG01product certifications | UL, CSA, GL, C-Tick, GOST
RM4LG01relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
RM4LG01release of input voltage
RM4LG01repeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM4LG01repeat accuracy of time delay | Not specified
RM4LG01reset time | Not specified ¦ ,through Un power reset, through front panel reset, through input control reset,
RM4LG01response time | Not specified ¦ ,on crossing the threshold,
RM4LG01safety reliability data | MTTF, B10,
RM4LG01seismic resistance | IEC60068-3-3
RM4LG01setting accuracy of the switching threshold | Not specified ¦ ,Setting accuracy,
RM4LG01setting accuracy of time delay | Not specified
RM4LG01shock resistance | Not specified ¦ IEC60068-2-27
RM4LG01short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM4LG01standards | EN60255-6, IEC60255-6
RM4LG01status LED
RM4LG01supply frequency | 50 / 60 Not specified
RM4LG01supply terminal | A1-A2
RM4LG01supply voltage limits | Not specified
RM4LG01switching threshold drift | Not specified ¦ ,Measurement error with supply voltage variation, Not specified ¦ ,Measurement error with temperature variation,
RM4LG01thermal current | 8 ¦ IEC60947-5-1
RM4LG01tightening torque | Not specified ¦ IEC60947-1,Tightening torque,
RM4LG01time delay drift | Not specified Not specified
RM4LG01time delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4LG01time delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4LG01tripping threshold | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
RM4LG01vibration resistance | Not specified ¦ IEC60068-2-6
RM4LG01width | 22.5 x 78 x 80 ¦ ,Width,
RM4TA | 3K3 ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, MTTFd, B10d,
RM4TAIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP50 ¦ IEC60529,Housing, Not specified ¦ IEC60529,Front Panel,
RM4TAInput nominal voltage selection | RM4TU0131: ~ 3 x 160…3 x 300 RM4TU02/32: ~ 3 x 290…3 x 580 ¦ ,Input nominal voltage selection,
RM4TAMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM4TA[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4TA[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4TA[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4TA[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4TA[Us] rated supply voltage | RM4TA01/31: ~ 3 x 200…3 x 240 RM4TA02/32: ~ 3 x 380…3 x 500
RM4TAambient air temperature for operation | -20…+65 ¦ ,Operation,
RM4TAambient air temperature for storage | -40…+85 ¦ ,Storage,
RM4TAbump resistance | IEC60068-2-29
RM4TAcable stripping length | Not specified ¦ ,Cable stripping length,
RM4TAcircuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
RM4TAconnections - terminals | 2 conductor: 2.5 ¦ IEC60947-1,Solid cable without cable end (screw terminal), 2 conductor: 1.5 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4TAcontacts material | 90/10 Nickel Silver
RM4TAdepth | Depth,
RM4TAdiagnostic button
RM4TAdielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4TAdirectives | 2006/95/EC 2004/108/EC 2002/95/EC
RM4TAduty time | Not specified
RM4TAelectrical durability | Not specified ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM4TAelectromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC50081-1, IEC50081-2 ¦ ,Generic emission standard, Class B Group 1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B Group 1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4TAheight | Height,
RM4TAhysteresis | - ¦ ,Phase cut, - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Fixed 5% of de-energization threshold ¦ ,Over voltage, Fixed 5% of de-energization threshold ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
RM4TAimmunity to microbreaks | Not specified
RM4TAinput frequency | 50 / 60 ¦ ,Rated frequency, 47.5…63 ¦ ,Frequency operating range,
RM4TAinput terminal | L1-L2-L3 ¦ ,Input terminal,
RM4TAinsulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4TAinternal input resistance | Not specified ¦ ,Internal input resistance,
RM4TAlocal signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Phase Cut, Phase Sequence Swap, Undervoltage <U, Overvoltage >U, Phase Asymmetry, Voltage Regeneration, Extreme Undervoltage <U (Phase loss), Extreme Overvoltage >U, Extreme Phase Asymmetry,
RM4TAmarking | UL, CSA, GL, C-Tick, GOST
RM4TAmaximum leakage current | IEC62314,Only for solid state output,
RM4TAmaximum measuring cycle | 80 ¦ ,Maximum measuring cycles,
RM4TAmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 8 ¦ ,Maximum switching current, 2000 ¦ ,Maximum switching capacity,
RM4TAmaximum voltage drop | IEC62314,Only for solid state output,
RM4TAmeasurement method | Voltage Peak Detection ¦ ,Measurement method,
RM4TAmeasurement range | Fixed value ¦ ,Phase lost , Fixed value ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , Not specified ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme Overvoltage, Extreme Asymmetry,
RM4TAmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM4TAminimum switching capacity | 12 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 120 ¦ IEC60947-5-4,Minimum switching capacity,
RM4TAmonitoring functions | · ¦ ,Phase lost , · ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , · ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry,
RM4TAmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM4TAmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM4TAnet weight | 110
RM4TAon-load factor
RM4TAoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
RM4TAoutput terminal | 15-16-18, 25-26-28
RM4TAoutput type | 2 x C/O relay contacts
RM4TAovervoltage category | IEC60664-1
RM4TApermissible input overload | Not specified ¦ ,permissible input overload,
RM4TApolarity
RM4TApollution degree | IEC60664-1
RM4TApower consumption | Not specified
RM4TApower on delay | Not specified
RM4TAproduct certifications | UL, CSA, GL, C-Tick, GOST
RM4TArelative humidity | 15%...85% ¦ IEC60068-2-30,Damp heat,XX
RM4TArelease of input voltage
RM4TArepeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM4TArepeat accuracy of time delay | Not specified
RM4TAreset time | Not specified ¦ ,through Un power reset, through front panel reset, through input control reset,
RM4TAresponse time | Not specified ¦ ,on crossing the threshold,
RM4TAsafety reliability data | MTTF, B10,
RM4TAseismic resistance | IEC60068-3-3
RM4TAsetting accuracy of the switching threshold | +/- 3% of set value ¦ ,Setting accuracy,
RM4TAsetting accuracy of time delay | +/- 10% of full scales value
RM4TAshock resistance | 15 gn ¦ IEC60068-2-27
RM4TAshort circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM4TAstandards | EN60255-6, IEC60255-6
RM4TAstatus LED
RM4TAsupply frequency | 50 / 60 47.5…63
RM4TAsupply terminal | L1-L2-L3
RM4TAsupply voltage limits | RM4TA01/31: ~ 3 x 160…3 x 300 RM4TA02/32: ~ 3 x 290…3 x 580
RM4TAswitching threshold drift | < 0.5% ¦ ,Measurement error with supply voltage variation, =< 0.06% / oC ¦ ,Measurement error with temperature variation,
RM4TAthermal current | IEC60947-5-1
RM4TAtightening torque | 0.6…1.1 ¦ IEC60947-1,Tightening torque,
RM4TAtime delay drift | < 0.5% =< 0.07% / oC
RM4TAtime delay range | Adjustable 0.1…10 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4TAtime delay type | · ¦ ,"OFF" delay, · ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4TAtripping threshold | Unknown ¦ ,Phase cut, Total swap of phase ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , Adjustable 5%...15% of selected Un ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
RM4TAvibration resistance | a=0.35ms from 10Hz…55Hz ¦ IEC60068-2-6
RM4TAwidth | 22.5 x 78 x 80 ¦ ,Width,
RM4TG20 | 3K3 ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, MTTFd, B10d,
RM4TG20IP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP50 ¦ IEC60529,Housing, Not specified ¦ IEC60529,Front Panel,
RM4TG20Input nominal voltage selection | Fixed @ ~ 3 x 140…3 x 580 ¦ ,Input nominal voltage selection,
RM4TG20Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM4TG20[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4TG20[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4TG20[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4TG20[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4TG20[Us] rated supply voltage | ~ 3 x 200…3 x 500
RM4TG20ambient air temperature for operation | -20…+65 ¦ ,Operation,
RM4TG20ambient air temperature for storage | -40…+85 ¦ ,Storage,
RM4TG20bump resistance | IEC60068-2-29
RM4TG20cable stripping length | Not specified ¦ ,Cable stripping length,
RM4TG20circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
RM4TG20connections - terminals | 2 conductor: 2.5 ¦ IEC60947-1,Solid cable without cable end (screw terminal), 2 conductor: 1.5 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4TG20contacts material | 90/10 Nickel Silver
RM4TG20depth | Depth,
RM4TG20diagnostic button
RM4TG20dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4TG20directives | 2006/95/EC 2004/108/EC 2002/95/EC
RM4TG20duty time | Not specified
RM4TG20electrical durability | Not specified ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM4TG20electromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC50081-1, IEC50081-2 ¦ ,Generic emission standard, Class B Group 1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B Group 1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4TG20height | Height,
RM4TG20hysteresis | - ¦ ,Phase cut, - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Fixed 5% of de-energization threshold ¦ ,Over voltage, Fixed 5% of de-energization threshold ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
RM4TG20immunity to microbreaks | Not specified
RM4TG20input frequency | 50 / 60 ¦ ,Rated frequency, 47.5…63 ¦ ,Frequency operating range,
RM4TG20input terminal | L1-L2-L3 ¦ ,Input terminal,
RM4TG20insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4TG20internal input resistance | Not specified ¦ ,Internal input resistance,
RM4TG20local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Phase Cut, Phase Sequence Swap, Undervoltage <U, Overvoltage >U, Phase Asymmetry, Voltage Regeneration, Extreme Undervoltage <U (Phase loss), Extreme Overvoltage >U, Extreme Phase Asymmetry,
RM4TG20marking | UL, CSA, GL, C-Tick, GOST
RM4TG20maximum leakage current | IEC62314,Only for solid state output,
RM4TG20maximum measuring cycle | 80 ¦ ,Maximum measuring cycles,
RM4TG20maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 8 ¦ ,Maximum switching current, 2000 ¦ ,Maximum switching capacity,
RM4TG20maximum voltage drop | IEC62314,Only for solid state output,
RM4TG20measurement method | Voltage Peak Detection ¦ ,Measurement method,
RM4TG20measurement range | Fixed value ¦ ,Phase lost , Fixed value ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme Overvoltage, Extreme Asymmetry,
RM4TG20mechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM4TG20minimum switching capacity | 12 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 120 ¦ IEC60947-5-4,Minimum switching capacity,
RM4TG20monitoring functions | · ¦ ,Phase lost , · ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry,
RM4TG20mounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM4TG20mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM4TG20net weight | 110
RM4TG20on-load factor
RM4TG20output logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
RM4TG20output terminal | 15-16-18, 25-26-28
RM4TG20output type | 2 x C/O relay contacts
RM4TG20overvoltage category | IEC60664-1
RM4TG20permissible input overload | Not specified ¦ ,permissible input overload,
RM4TG20polarity
RM4TG20pollution degree | IEC60664-1
RM4TG20power consumption | Not specified
RM4TG20power on delay | Not specified
RM4TG20product certifications | UL, CSA, GL, C-Tick, GOST
RM4TG20relative humidity | 15%...85% ¦ IEC60068-2-30,Damp heat,XX
RM4TG20release of input voltage
RM4TG20repeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM4TG20repeat accuracy of time delay | Not specified
RM4TG20reset time | Not specified ¦ ,through Un power reset, through front panel reset, through input control reset,
RM4TG20response time | Not specified ¦ ,on crossing the threshold,
RM4TG20safety reliability data | MTTF, B10,
RM4TG20seismic resistance | IEC60068-3-3
RM4TG20setting accuracy of the switching threshold | +/- 3% of set value ¦ ,Setting accuracy,
RM4TG20setting accuracy of time delay | +/- 10% of full scales value
RM4TG20shock resistance | 15 gn ¦ IEC60068-2-27
RM4TG20short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM4TG20standards | EN60255-6, IEC60255-6
RM4TG20status LED
RM4TG20supply frequency | 50 / 60 47.5…63
RM4TG20supply terminal | L1-L2-L3
RM4TG20supply voltage limits | ~ 3 x 140…3 x 580
RM4TG20switching threshold drift | < 0.5% ¦ ,Measurement error with supply voltage variation, =< 0.06% / oC ¦ ,Measurement error with temperature variation,
RM4TG20thermal current | IEC60947-5-1
RM4TG20tightening torque | 0.6…1.1 ¦ IEC60947-1,Tightening torque,
RM4TG20time delay drift | < 0.5% =< 0.07% / oC
RM4TG20time delay range | Adjustable 0.1…10 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4TG20time delay type | · ¦ ,"OFF" delay, · ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4TG20tripping threshold | Unknown ¦ ,Phase cut, Total swap of phase ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
RM4TG20vibration resistance | a=0.35ms from 10Hz…55Hz ¦ IEC60068-2-6
RM4TG20width | 22.5 x 78 x 80 ¦ ,Width,
RM4TR | 3K3 ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, MTTFd, B10d,
RM4TRIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP50 ¦ IEC60529,Housing, Not specified ¦ IEC60529,Front Panel,
RM4TRInput nominal voltage selection | RM4TR31/33: ~ 3 x 160…3 x 300 RM4TR32/34: ~ 3 x 290…3 x 580 ¦ ,Input nominal voltage selection,
RM4TRMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM4TR[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4TR[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4TR[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4TR[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4TR[Us] rated supply voltage | RM4TR31: ~ 3 x 200…3 x 240 RM4TR32: ~ 3 x 300…3 x 500 RM4TR33: ~ 3 x 220 RM4TR33: ~ 3 x 400
RM4TRambient air temperature for operation | -20…+65 ¦ ,Operation,
RM4TRambient air temperature for storage | -40…+85 ¦ ,Storage,
RM4TRbump resistance | IEC60068-2-29
RM4TRcable stripping length | Not specified ¦ ,Cable stripping length,
RM4TRcircuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
RM4TRconnections - terminals | 2 conductor: 2.5 ¦ IEC60947-1,Solid cable without cable end (screw terminal), 2 conductor: 1.5 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4TRcontacts material | 90/10 Nickel Silver
RM4TRdepth | Depth,
RM4TRdiagnostic button
RM4TRdielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4TRdirectives | 2006/95/EC 2004/108/EC 2002/95/EC
RM4TRduty time | Not specified
RM4TRelectrical durability | Not specified ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM4TRelectromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC50081-1, IEC50081-2 ¦ ,Generic emission standard, Class B Group 1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B Group 1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4TRheight | Height,
RM4TRhysteresis | - ¦ ,Phase cut, - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Fixed 5% of de-energization threshold ¦ ,Over voltage, Fixed 5% of de-energization threshold ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
RM4TRimmunity to microbreaks | Not specified
RM4TRinput frequency | 50 / 60 ¦ ,Rated frequency, 47.5…63 ¦ ,Frequency operating range,
RM4TRinput terminal | L1-L2-L3 ¦ ,Input terminal,
RM4TRinsulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4TRinternal input resistance | Not specified ¦ ,Internal input resistance,
RM4TRlocal signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Phase Cut, Phase Sequence Swap, Undervoltage <U, Overvoltage >U, Phase Asymmetry, Voltage Regeneration, Extreme Undervoltage <U (Phase loss), Extreme Overvoltage >U, Extreme Phase Asymmetry,
RM4TRmarking | UL, CSA, GL, C-Tick, GOST
RM4TRmaximum leakage current | IEC62314,Only for solid state output,
RM4TRmaximum measuring cycle | 80 ¦ ,Maximum measuring cycles,
RM4TRmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 8 ¦ ,Maximum switching current, 2000 ¦ ,Maximum switching capacity,
RM4TRmaximum voltage drop | IEC62314,Only for solid state output,
RM4TRmeasurement method | Voltage Peak Detection ¦ ,Measurement method,
RM4TRmeasurement range | Fixed value ¦ ,Phase lost , Fixed value ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), RM4TR31: ~ 3 x 160…3 x 300 RM4TR32: ~ 3 x 420…3 x 480 RM4TR33: ~ 3 x 198 RM4TR34: ~ 3 x 360 ¦ ,Over voltage, RM4TR31: ~ 3 x 220…3 x 300 RM4TR32: ~ 3 x 300…3 x 430 RM4TR33: ~ 3 x 242 RM4TR34: ~ 3 x 440 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme Overvoltage, Extreme Asymmetry,
RM4TRmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM4TRminimum switching capacity | 12 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 120 ¦ IEC60947-5-4,Minimum switching capacity,
RM4TRmonitoring functions | · ¦ ,Phase lost , · ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), · ¦ ,Over voltage, · ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry,
RM4TRmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM4TRmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM4TRnet weight | 110
RM4TRon-load factor
RM4TRoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
RM4TRoutput terminal | 15-16-18, 25-26-28
RM4TRoutput type | 2 x C/O relay contacts
RM4TRovervoltage category | IEC60664-1
RM4TRpermissible input overload | Not specified ¦ ,permissible input overload,
RM4TRpolarity
RM4TRpollution degree | IEC60664-1
RM4TRpower consumption | Not specified
RM4TRpower on delay | Not specified
RM4TRproduct certifications | UL, CSA, GL, C-Tick, GOST
RM4TRrelative humidity | 15%...85% ¦ IEC60068-2-30,Damp heat,XX
RM4TRrelease of input voltage
RM4TRrepeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM4TRrepeat accuracy of time delay | Not specified
RM4TRreset time | Not specified ¦ ,through Un power reset, through front panel reset, through input control reset,
RM4TRresponse time | Not specified ¦ ,on crossing the threshold,
RM4TRsafety reliability data | MTTF, B10,
RM4TRseismic resistance | IEC60068-3-3
RM4TRsetting accuracy of the switching threshold | +/- 3% of set value ¦ ,Setting accuracy,
RM4TRsetting accuracy of time delay | +/- 10% of full scales value
RM4TRshock resistance | 15 gn ¦ IEC60068-2-27
RM4TRshort circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM4TRstandards | EN60255-6, IEC60255-6
RM4TRstatus LED
RM4TRsupply frequency | 50 / 60 47.5…63
RM4TRsupply terminal | L1-L2-L3
RM4TRsupply voltage limits | RM4TR31/33: ~ 3 x 160…3 x 300 RM4TR32/34: ~ 3 x 290…3 x 580
RM4TRswitching threshold drift | < 0.5% ¦ ,Measurement error with supply voltage variation, =< 0.06% / oC ¦ ,Measurement error with temperature variation,
RM4TRthermal current | IEC60947-5-1
RM4TRtightening torque | 0.6…1.1 ¦ IEC60947-1,Tightening torque,
RM4TRtime delay drift | < 0.5% =< 0.07% / oC
RM4TRtime delay range | Adjustable 0.1…10 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4TRtime delay type | · ¦ ,"OFF" delay, · ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4TRtripping threshold | RM4TR32: (L2-L1) or (L3-L1) or (L2-L3) < 290 or Differences of (L2-L1) / (L3-L1) /(L2-L3) > 105V Other: Unknown ¦ ,Phase cut, Total swap of phase ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Adjustable within measurement range ¦ ,Over voltage, Adjustable within measurement range ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
RM4TRvibration resistance | a=0.35ms from 10Hz…55Hz ¦ IEC60068-2-6
RM4TRwidth | 22.5 x 78 x 80 ¦ ,Width,
RM4TU | 3K3 ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, MTTFd, B10d,
RM4TUIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP50 ¦ IEC60529,Housing, Not specified ¦ IEC60529,Front Panel,
RM4TUInput nominal voltage selection | RM4TU01: ~ 3 x 160…3 x 300 RM4TU01: ~ 3 x 290…3 x 580 ¦ ,Input nominal voltage selection,
RM4TUMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM4TU[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4TU[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4TU[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4TU[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4TU[Us] rated supply voltage | RM4TU01: ~ 3 x 200…3 x 240 RM4TU02: ~ 3 x 380…3 x 500
RM4TUambient air temperature for operation | -20…+65 ¦ ,Operation,
RM4TUambient air temperature for storage | -40…+85 ¦ ,Storage,
RM4TUbump resistance | IEC60068-2-29
RM4TUcable stripping length | Not specified ¦ ,Cable stripping length,
RM4TUcircuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
RM4TUconnections - terminals | 2 conductor: 2.5 ¦ IEC60947-1,Solid cable without cable end (screw terminal), 2 conductor: 1.5 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4TUcontacts material | 90/10 Nickel Silver
RM4TUdepth | Depth,
RM4TUdiagnostic button
RM4TUdielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4TUdirectives | 2006/95/EC 2004/108/EC 2002/95/EC
RM4TUduty time | Not specified
RM4TUelectrical durability | Not specified ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM4TUelectromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC50081-1, IEC50081-2 ¦ ,Generic emission standard, Class B Group 1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B Group 1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4TUheight | Height,
RM4TUhysteresis | - ¦ ,Phase cut, - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Fixed 5% of de-energization threshold ¦ ,Over voltage, Fixed 5% of de-energization threshold ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
RM4TUimmunity to microbreaks | Not specified
RM4TUinput frequency | 50 / 60 ¦ ,Rated frequency, 47.5…63 ¦ ,Frequency operating range,
RM4TUinput terminal | L1-L2-L3 ¦ ,Input terminal,
RM4TUinsulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4TUinternal input resistance | Not specified ¦ ,Internal input resistance,
RM4TUlocal signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Phase Cut, Phase Sequence Swap, Undervoltage <U, Overvoltage >U, Phase Asymmetry, Voltage Regeneration, Extreme Undervoltage <U (Phase loss), Extreme Overvoltage >U, Extreme Phase Asymmetry,
RM4TUmarking | UL, CSA, GL, C-Tick, GOST
RM4TUmaximum leakage current | IEC62314,Only for solid state output,
RM4TUmaximum measuring cycle | 80 ¦ ,Maximum measuring cycles,
RM4TUmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 8 ¦ ,Maximum switching current, 2000 ¦ ,Maximum switching capacity,
RM4TUmaximum voltage drop | IEC62314,Only for solid state output,
RM4TUmeasurement method | Voltage Peak Detection ¦ ,Measurement method,
RM4TUmeasurement range | Fixed value ¦ ,Phase lost , Fixed value ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, RM4TU01: ~ 3 x 160…3 x 220 RM4TU02: ~ 3 x 300…3 x 430 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme Overvoltage, Extreme Asymmetry,
RM4TUmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM4TUminimum switching capacity | 12 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 120 ¦ IEC60947-5-4,Minimum switching capacity,
RM4TUmonitoring functions | · ¦ ,Phase lost , · ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, · ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry,
RM4TUmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM4TUmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM4TUnet weight | 110
RM4TUon-load factor
RM4TUoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
RM4TUoutput terminal | 15-16-18, 25-26-28
RM4TUoutput type | 2 x C/O relay contacts
RM4TUovervoltage category | IEC60664-1
RM4TUpermissible input overload | Not specified ¦ ,permissible input overload,
RM4TUpolarity
RM4TUpollution degree | IEC60664-1
RM4TUpower consumption | Not specified
RM4TUpower on delay | Not specified
RM4TUproduct certifications | UL, CSA, GL, C-Tick, GOST
RM4TUrelative humidity | 15%...85% ¦ IEC60068-2-30,Damp heat,XX
RM4TUrelease of input voltage
RM4TUrepeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM4TUrepeat accuracy of time delay | Not specified
RM4TUreset time | Not specified ¦ ,through Un power reset, through front panel reset, through input control reset,
RM4TUresponse time | Not specified ¦ ,on crossing the threshold,
RM4TUsafety reliability data | MTTF, B10,
RM4TUseismic resistance | IEC60068-3-3
RM4TUsetting accuracy of the switching threshold | +/- 3% of set value ¦ ,Setting accuracy,
RM4TUsetting accuracy of time delay | +/- 10% of full scales value
RM4TUshock resistance | 15 gn ¦ IEC60068-2-27
RM4TUshort circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM4TUstandards | EN60255-6, IEC60255-6
RM4TUstatus LED
RM4TUsupply frequency | 50 / 60 47.5…63
RM4TUsupply terminal | L1-L2-L3
RM4TUsupply voltage limits | RM4TU01: ~ 3 x 160…3 x 300 RM4TU01: ~ 3 x 290…3 x 580
RM4TUswitching threshold drift | < 0.5% ¦ ,Measurement error with supply voltage variation, =< 0.06% / oC ¦ ,Measurement error with temperature variation,
RM4TUthermal current | IEC60947-5-1
RM4TUtightening torque | 0.6…1.1 ¦ IEC60947-1,Tightening torque,
RM4TUtime delay drift | < 0.5% =< 0.07% / oC
RM4TUtime delay range | Adjustable 0.1…10 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4TUtime delay type | · ¦ ,"OFF" delay, · ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4TUtripping threshold | Unknown ¦ ,Phase cut, Total swap of phase ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, Adjustable within measurement range ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
RM4TUvibration resistance | a=0.35ms from 10Hz…55Hz ¦ IEC60068-2-6
RM4TUwidth | 22.5 x 78 x 80 ¦ ,Width,
RM4UA0 | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Not specified ¦ ,Supply,Rated Not specified ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, - ¦ ,Over / undervoltage (windows mode), Without memory ¦ ,Over voltage, - ¦ ,Undervoltage , RM4UA01xx: ~/-- 0.05…5 RM4UA02xx: ~/-- 1…100 RM4UA03xx: ~/-- 30…500 RM4UA31xx: 6.6 RM4UA32xx: ~/-- 23 ¦ ,E1-M / B1-C, RM4UA01xx: 43 RM4UA02xx: ~/-- 112 RM4UA03xx: ~/-- 668 ¦ ,E2-M / B2-C, RM4UA01xx: 71 RM4UA02xx: ~/-- 225 RM4UA03xx: ~/-- 1111 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, RM4UA01xx: ~/-- 0.05…0.5 RM4UA02xx: ~/-- 1…10 ¦ ,E1-M / B1-C, RM4UA01xx: ~/-- 0.3…3 RM4UA02xx: ~/-- 5…50 RM4UA03xx: ~/-- 30…300 ¦ ,E2-M / B2-C, RM4UA01xx: ~/-- 0.5…5 RM4UA02xx: ~/-- 10…100 RM4UA03xx: ~/-- 50…500 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, - ¦ ,E1-M / B1-C, Adjustable 10%...100% ¦ ,E2-M / B2-C, Adjustable 10%...100% ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 5%...30% of threshold setting ¦ ,E1-M / B1-C, Adjustable 5%...30% of threshold setting ¦ ,E2-M / B2-C, Adjustable 5%...30% of threshold setting ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Resistive Voltage Step Down B1-C, B2-C, B3-C 50 / 60 Not specified +/- 5% of full scale value Not specified < 0.5% over whole range 0.06% / oC 80 Voltage Peak Detection MTTFd, B10d,
RM4UA0IP degree of protection | Not specified ¦ IEC60529,Terminal Block, Not specified ¦ IEC60529,Housing, IEC60529,Front Panel,
RM4UA0Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM4UA0[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4UA0[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4UA0[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, Not specified ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4UA0[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4UA0[Us] rated supply voltage | RM4UA0xB: ~24 RM4UA0xF: ~110…130 RM4UA0xM: ~220…240
RM4UA0ambient air temperature for operation | Not specified ¦ ,Operation,
RM4UA0ambient air temperature for storage | Not specified ¦ ,Storage,
RM4UA0bump resistance | IEC60068-2-29
RM4UA0cable stripping length | Not specified ¦ ,Cable stripping length,
RM4UA0circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Not specified ¦ ,Output 2,
RM4UA0connections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal), Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4UA0contacts material | Not specified
RM4UA0depth | Depth,
RM4UA0diagnostic button
RM4UA0dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4UA0directives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
RM4UA0duty time | Not specified
RM4UA0electrical durability | Not specified ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM4UA0electromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B Group1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B Group1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B Group1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B Group1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4UA0height | Height,
RM4UA0immunity to microbreaks | Not specified
RM4UA0insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4UA0local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM4UA0marking | UL, CSA, GL, C-Tick, GOST, CE
RM4UA0maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM4UA0maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 8 ¦ ,Maximum switching current, 2000VA ¦ ,Maximum switching capacity,
RM4UA0maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM4UA0mechanical durability | Not specified ¦ IEC61810-1
RM4UA0minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching voltage, Not specified ¦ IEC60947-5-4,Minimum switching current, Not specified ¦ IEC60947-5-4,Minimum switching capacity,
RM4UA0mounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
RM4UA0mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM4UA0net weight | 168
RM4UA0on-load factor
RM4UA0output logic | Energized on fault ¦ ,R1 (11-12-14), R2 (21-22-24),
RM4UA0output terminal | 15-16-18
RM4UA0output type | 1 x C/O relay contacts
RM4UA0overvoltage category | Not specified ¦ IEC60664-1
RM4UA0polarity
RM4UA0pollution degree | Not specified ¦ IEC60664-1
RM4UA0power consumption | RM4UA0xB: ~ 2VA RM4UA0xF: ~ 3.3VA RM4UA0xM: ~ 3.5VA
RM4UA0power on delay | Not specified
RM4UA0product certifications | UL, CSA, GL, C-Tick, GOST
RM4UA0relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
RM4UA0release of input voltage
RM4UA0repeat accuracy of time delay | Not specified
RM4UA0reset time | Not specified ¦ ,through Un power reset, through front panel reset, through input control reset,
RM4UA0response time | Not specified ¦ ,on crossing the threshold,
RM4UA0safety reliability data | MTTF, B10,
RM4UA0seismic resistance | IEC60068-3-3
RM4UA0setting accuracy of time delay | -
RM4UA0shock resistance | Not specified ¦ IEC60068-2-27
RM4UA0short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM4UA0standards | EN60255-6, IEC60255-6
RM4UA0status LED
RM4UA0supply frequency | 50 / 60 Not specified
RM4UA0supply terminal | A1-A2
RM4UA0supply voltage limits | 0.85…1.1 Un
RM4UA0thermal current | IEC60947-5-1
RM4UA0tightening torque | Not specified ¦ IEC60947-1,Tightening torque,
RM4UA0time delay drift | - -
RM4UA0time delay range | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4UA0time delay type | - ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4UA0vibration resistance | Not specified ¦ IEC60068-2-6
RM4UA0width | 22.5 x 78 x 80 ¦ ,Width,
RM4UA3 | Not specified ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Not specified ¦ ,Supply,Rated Not specified ¦ ,Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, - ¦ ,Over / undervoltage (windows mode), Without memory ¦ ,Over voltage, Without memory ¦ ,Undervoltage , RM4UA31xx: ~/-- 0.05…5 RM4UA32xx: ~/-- 1…100 RM4UA33xx: ~/-- 30…500 RM4UA31xx: 6.6 RM4UA32xx: ~/-- 23 ¦ ,E1-M / B1-C, RM4UA31xx: 43 RM4UA32xx: ~/-- 112 RM4UA33xx: ~/-- 668 ¦ ,E2-M / B2-C, RM4UA31xx: 71 RM4UA32xx: ~/-- 225 RM4UA33xx: ~/-- 1111 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, RM4UA31xx: ~/-- 0.05…0.5 RM4UA32xx: ~/-- 1…10 ¦ ,E1-M / B1-C, RM4UA31xx: ~/-- 0.3…3 RM4UA32xx: ~/-- 5…50 RM4UA33xx: ~/-- 30…300 ¦ ,E2-M / B2-C, RM4UA31xx: ~/-- 0.5…5 RM4UA32xx: ~/-- 10…100 RM4UA33xx: ~/-- 50…500 ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, - ¦ ,E1-M / B1-C, Adjustable 10%...100% ¦ ,E2-M / B2-C, Adjustable 10%...100% ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Adjustable 5%...30% of threshold setting ¦ ,E1-M / B1-C, Adjustable 5%...30% of threshold setting ¦ ,E2-M / B2-C, Adjustable 5%...30% of threshold setting ¦ ,E3-M / B3-C, A1+ / A2-, - ¦ ,Built in current transformer, Resistive Voltage Step Down B1-C, B2-C, B3-C 50 / 60 Not specified +/- 5% of full scale value Not specified < 0.5% over whole range 0.06% / oC 80 Voltage Peak Detection MTTFd, B10d,
RM4UA3IP degree of protection | Not specified ¦ IEC60529,Terminal Block, Not specified ¦ IEC60529,Housing, IEC60529,Front Panel,
RM4UA3Minimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM4UA3[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4UA3[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4UA3[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, Not specified ¦ IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4UA3[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, Not specified ¦ IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4UA3[Us] rated supply voltage | RM4UA3xMW: ~/-- 24…240 RM4UA3xF: ~110…130 RM4UA3xM: ~220…240 RM4UA3xQ: ~380…415
RM4UA3ambient air temperature for operation | Not specified ¦ ,Operation,
RM4UA3ambient air temperature for storage | Not specified ¦ ,Storage,
RM4UA3bump resistance | IEC60068-2-29
RM4UA3cable stripping length | Not specified ¦ ,Cable stripping length,
RM4UA3circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Not specified ¦ ,Output 2,
RM4UA3connections - terminals | Not specified ¦ IEC60947-1,Solid cable without cable end (screw terminal), Not specified ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4UA3contacts material | Not specified
RM4UA3depth | Depth,
RM4UA3diagnostic button
RM4UA3dielectric strength | Yes ¦ IEC60255-27,Supply / Input 1, Yes ¦ IEC60255-27,Supply / Input 2, Yes ¦ IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4UA3directives | No 73/23/EEC + 93/68/EEC No 89/336/EEC + 92/31/EEC + 93/68/EEC 2002/95/EC
RM4UA3duty time | Not specified
RM4UA3electrical durability | Not specified ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM4UA3electromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC61000-6-3, IEC61000-6-4 ¦ ,Generic emission standard, Class B Group1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B Group1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B Group1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B Group1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4UA3height | Height,
RM4UA3immunity to microbreaks | Not specified
RM4UA3insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4UA3local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
RM4UA3marking | UL, CSA, GL, C-Tick, GOST, CE
RM4UA3maximum leakage current | - ¦ IEC62314,Only for solid state output,
RM4UA3maximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 8 ¦ ,Maximum switching current, 2000VA ¦ ,Maximum switching capacity,
RM4UA3maximum voltage drop | - ¦ IEC62314,Only for solid state output,
RM4UA3mechanical durability | Not specified ¦ IEC61810-1
RM4UA3minimum switching capacity | Not specified ¦ IEC60947-5-4,Minimum switching voltage, Not specified ¦ IEC60947-5-4,Minimum switching current, Not specified ¦ IEC60947-5-4,Minimum switching capacity,
RM4UA3mounting position | Not specified ¦ ,In relation to normal vertical mounting plane,
RM4UA3mounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM4UA3net weight | 168
RM4UA3on-load factor
RM4UA3output logic | Energized on fault ¦ ,R1 (11-12-14), R2 (21-22-24),
RM4UA3output terminal | 15-16-18, 25-26-28
RM4UA3output type | 2 x C/O relay contacts
RM4UA3overvoltage category | Not specified ¦ IEC60664-1
RM4UA3polarity
RM4UA3pollution degree | Not specified ¦ IEC60664-1
RM4UA3power consumption | RM4UA3xMW: ~ 3.3VA, -- 1.2W RM4UA3xF: ~ 3.3VA RM4UA3xM: ~ 3.4VA RM4UA3xQ: ~ 3VA
RM4UA3power on delay | Not specified
RM4UA3product certifications | UL, CSA, GL, C-Tick, GOST
RM4UA3relative humidity | Not specified ¦ IEC60068-2-30,Damp heat,
RM4UA3release of input voltage
RM4UA3repeat accuracy of time delay | Not specified
RM4UA3reset time | Not specified ¦ ,through Un power reset, through front panel reset, through input control reset,
RM4UA3response time | Not specified ¦ ,on crossing the threshold,
RM4UA3safety reliability data | MTTF, B10,
RM4UA3seismic resistance | IEC60068-3-3
RM4UA3setting accuracy of time delay | +/- 10% of full scales
RM4UA3shock resistance | Not specified ¦ IEC60068-2-27
RM4UA3short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM4UA3standards | EN60255-6, IEC60255-6
RM4UA3status LED
RM4UA3supply frequency | 50 / 60 Not specified
RM4UA3supply terminal | A1-A2
RM4UA3supply voltage limits | 0.85…1.1 Un
RM4UA3thermal current | IEC60947-5-1
RM4UA3tightening torque | Not specified ¦ IEC60947-1,Tightening torque,
RM4UA3time delay drift | < 0.5% over whole range 0.07% / oC
RM4UA3time delay range | Adjustable (0.5…1),(0.15…3),(0.5…10),(1.5…30) ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4UA3time delay type | · ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4UA3vibration resistance | Not specified ¦ IEC60068-2-6
RM4UA3width | 22.5 x 78 x 80 ¦ ,Width,
RM4UB | 3K3 ¦ IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Resistive Voltage Step Down ¦ ,Measurement mode, MTTFd, B10d,
RM4UBIP degree of protection | IP20 ¦ IEC60529,Terminal Block, IP50 ¦ IEC60529,Housing, Not specified ¦ IEC60529,Front Panel,
RM4UBInput nominal voltage selection | RM4UB34: ~ 160…300 RM4UB35: ~ 160…300 ¦ ,Input nominal voltage selection,
RM4UBMinimum distance to adjacent devices | Not specified ¦ ,Horizontal, Not specified ¦ ,Vertical,
RM4UB[Ie] rated operational current | IEC61810-1,Rated switching current,
RM4UB[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
RM4UB[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4UB[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
RM4UB[Us] rated supply voltage | RM4UB34: ~80…220 RM4UB35: ~160…300
RM4UBambient air temperature for operation | -20…+65 ¦ ,Operation,
RM4UBambient air temperature for storage | -40…+85 ¦ ,Storage,
RM4UBbump resistance | IEC60068-2-29
RM4UBcable stripping length | Not specified ¦ ,Cable stripping length,
RM4UBcircuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
RM4UBconnections - terminals | 2 conductor: 2.5 ¦ IEC60947-1,Solid cable without cable end (screw terminal), 2 conductor: 1.5 ¦ IEC60947-1,Flexible cable with cable end (screw terminal), - ¦ IEC60947-1,Solid cable (spring terminal), - ¦ IEC60947-1,Flexible cable (spring terminal),
RM4UBcontacts material | 90/10 Nickel Silver
RM4UBdepth | Depth,
RM4UBdiagnostic button
RM4UBdielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4UBdirectives | 2006/95/EC 2004/108/EC 2002/95/EC
RM4UBduty time | Not specified
RM4UBelectrical durability | Not specified ¦ IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
RM4UBelectromagnetic compatibility | IEC50082-2 ¦ ,Generic immunity standard, Level 3 (6kV / 8kV) ¦ IEC61000-4-2,Electrostatic discharge, Level 3 (10V/m) ¦ IEC61000-4-3,Radiated RF & electromagnetic field, Level 3 (2kV coupling / 4kV direct) ¦ IEC61000-4-4,Fast transient / burst, Level 3 (1kV phase-phase) ¦ IEC61000-4-5,Surge, Level 3 (10V) ¦ IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, Class 3 (0%, 40%, 70%, 80% of Us) ¦ IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, Not tested ¦ IEC61000-4-13,Low frequency harmonics, ? ¦ Germanisher Lloyd,Conducted low frequency interference (harmonics), IEC50081-1, IEC50081-2 ¦ ,Generic emission standard, Class B Group 1 ¦ EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), Class B Group 1 ¦ EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Radiated emission from enclosure port, Class B Group 1 ¦ EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), Class B Group 1 ¦ EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), EMC 2 ¦ Germanisher Lloyd,Conducted emission,
RM4UBheight | Height,
RM4UBhysteresis | - ¦ ,Phase cut, - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Fixed 5% of de-energization threshold ¦ ,Over voltage, Fixed 5% of de-energization threshold ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
RM4UBimmunity to microbreaks | Not specified
RM4UBinput frequency | 50 / 60 ¦ ,Rated frequency, 47.5…63 ¦ ,Frequency operating range,
RM4UBinput terminal | L1-L3 ¦ ,Input terminal,
RM4UBinsulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
RM4UBinternal input resistance | Not specified ¦ ,Internal input resistance,
RM4UBlocal signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Phase Cut, Phase Sequence Swap, Undervoltage <U, Overvoltage >U, Phase Asymmetry, Voltage Regeneration, Extreme Undervoltage <U (Phase loss), Extreme Overvoltage >U, Extreme Phase Asymmetry,
RM4UBmarking | UL, CSA, GL, C-Tick, GOST
RM4UBmaximum leakage current | IEC62314,Only for solid state output,
RM4UBmaximum measuring cycle | 80 ¦ ,Maximum measuring cycles,
RM4UBmaximum switching capacity | ~ 250 ¦ ,Maximum switching voltage, 8 ¦ ,Maximum switching current, 2000 ¦ ,Maximum switching capacity,
RM4UBmaximum voltage drop | IEC62314,Only for solid state output,
RM4UBmeasurement method | Voltage Peak Detection ¦ ,Measurement method,
RM4UBmeasurement range | Fixed value ¦ ,Phase lost , Fixed value ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), RM4UB34: ~ 160…220 RM4UB34: ~ 220…300 ¦ ,Over voltage, RM4UB34: ~ 80…120 RM4UB34: ~ 160…220 ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme Overvoltage, Extreme Asymmetry,
RM4UBmechanical durability | 30 x 106 switching cycles ¦ IEC61810-1
RM4UBminimum switching capacity | 12 ¦ IEC60947-5-4,Minimum switching voltage, 10 ¦ IEC60947-5-4,Minimum switching current, 120 ¦ IEC60947-5-4,Minimum switching capacity,
RM4UBmonitoring functions | - ¦ ,Phase lost , - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), - ¦ ,Over voltage, - ¦ ,Undervoltage , - ¦ ,Phase asymmetry, - ¦ ,Disconnection of neutral, - ¦ ,Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry,
RM4UBmounting position | Any position ¦ ,In relation to normal vertical mounting plane,
RM4UBmounting support | On Top Hat 35mm DIN rail ¦ IEC/EN 60715,Without socket, - ¦ IEC/EN 60715,With socket,
RM4UBnet weight | 110
RM4UBon-load factor
RM4UBoutput logic | Energized on fault-free ¦ ,R1 (11-12-14), R2 (21-22-24),
RM4UBoutput terminal | 15-16-18, 25-26-28
RM4UBoutput type | 2 x C/O relay contacts
RM4UBovervoltage category | IEC60664-1
RM4UBpermissible input overload | Not specified ¦ ,permissible input overload,
RM4UBpolarity
RM4UBpollution degree | IEC60664-1
RM4UBpower consumption | Not specified
RM4UBpower on delay | Not specified
RM4UBproduct certifications | UL, CSA, GL, C-Tick, GOST
RM4UBrelative humidity | 15%...85% ¦ IEC60068-2-30,Damp heat,XX
RM4UBrelease of input voltage
RM4UBrepeat accuracy of the switching threshold | Not specified ¦ ,Repeat accuracy (constant parameters),
RM4UBrepeat accuracy of time delay | Not specified
RM4UBreset time | Not specified ¦ ,through Un power reset, through front panel reset, through input control reset,
RM4UBresponse time | Not specified ¦ ,on crossing the threshold,
RM4UBsafety reliability data | MTTF, B10,
RM4UBseismic resistance | IEC60068-3-3
RM4UBsetting accuracy of the switching threshold | +/- 3% of set value ¦ ,Setting accuracy,
RM4UBsetting accuracy of time delay | +/- 10% of full scales value
RM4UBshock resistance | 15 gn ¦ IEC60068-2-27
RM4UBshort circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
RM4UBstandards | EN60255-6, IEC60255-6
RM4UBstatus LED
RM4UBsupply frequency | 50 / 60 47.5…63
RM4UBsupply terminal | L1-L3
RM4UBsupply voltage limits | RM4UB34: ~60…300 RM4UB35: ~160…300
RM4UBswitching threshold drift | < 0.5% ¦ ,Measurement error with supply voltage variation, =< 0.06% / oC ¦ ,Measurement error with temperature variation,
RM4UBthermal current | IEC60947-5-1
RM4UBtightening torque | 0.6…1.1 ¦ IEC60947-1,Tightening torque,
RM4UBtime delay drift | < 0.5% =< 0.07% / oC
RM4UBtime delay range | Adjustable 0.1…10 ¦ ,"OFF" delay, - ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4UBtime delay type | · ¦ ,"OFF" delay, · ¦ ,"ON" delay, - ¦ ,Inhibition,
RM4UBtripping threshold | - ¦ ,Phase cut, - ¦ ,Phase sequence, - ¦ ,Over / undervoltage (symmetry windows mode), Adjustable within measurement range ¦ ,Over voltage, Adjustable within measurement range ¦ ,Undervoltage , - ¦ ,Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
RM4UBvibration resistance | a=0.35ms from 10Hz…55Hz ¦ IEC60068-2-6
RM4UBwidth | 22.5 x 78 x 80 ¦ ,Width,
col13 | IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Over / undercurrent (windows mode), Over current, Under current, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, MTTFd, B10d,
col13IP degree of protection | IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel,
col13Minimum distance to adjacent devices | Horizontal, Vertical,
col13[Ie] rated operational current | IEC61810-1,Rated switching current,
col13[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col13[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col13[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col13[Us] rated supply voltage
col13ambient air temperature for operation | Operation,
col13ambient air temperature for storage | Storage,
col13bump resistance | IEC60068-2-29
col13cable stripping length | Cable stripping length,
col13circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
col13connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal),
col13contacts material
col13depth | Depth,
col13diagnostic button
col13dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col13directives
col13duty time
col13electrical durability | IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
col13electromagnetic compatibility | Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission,
col13height | Height,
col13immunity to microbreaks
col13insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col13local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
col13marking
col13maximum leakage current | IEC62314,Only for solid state output,
col13maximum switching capacity | Maximum switching voltage, Maximum switching current, Maximum switching capacity,
col13maximum voltage drop | IEC62314,Only for solid state output,
col13mechanical durability | IEC61810-1
col13minimum switching capacity | IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity,
col13mounting position | In relation to normal vertical mounting plane,
col13mounting support | IEC/EN 60715,Without socket, IEC/EN 60715,With socket,
col13net weight
col13on-load factor
col13output logic | R1 (11-12-14), R2 (21-22-24),
col13output terminal
col13output type
col13overvoltage category | IEC60664-1
col13polarity
col13pollution degree | IEC60664-1
col13power consumption
col13power on delay
col13product certifications
col13relative humidity | IEC60068-2-30,Damp heat,
col13release of input voltage
col13repeat accuracy of time delay
col13reset time | through Un power reset, through front panel reset, through input control reset,
col13response time | on crossing the threshold,
col13safety reliability data | MTTF, B10,
col13seismic resistance | IEC60068-3-3
col13setting accuracy of time delay
col13shock resistance | IEC60068-2-27
col13short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
col13standards
col13status LED
col13supply frequency
col13supply terminal
col13supply voltage limits
col13thermal current | IEC60947-5-1
col13tightening torque | IEC60947-1,Tightening torque,
col13time delay drift
col13time delay range | "OFF" delay, "ON" delay, Inhibition,
col13time delay type | "OFF" delay, "ON" delay, Inhibition,
col13vibration resistance | IEC60068-2-6
col13width | Width,
col14 | IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Over / undercurrent (windows mode), Over current, Under current, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, MTTFd, B10d,
col14IP degree of protection | IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel,
col14Minimum distance to adjacent devices | Horizontal, Vertical,
col14[Ie] rated operational current | IEC61810-1,Rated switching current,
col14[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col14[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col14[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col14[Us] rated supply voltage
col14ambient air temperature for operation | Operation,
col14ambient air temperature for storage | Storage,
col14bump resistance | IEC60068-2-29
col14cable stripping length | Cable stripping length,
col14circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
col14connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal),
col14contacts material
col14depth | Depth,
col14diagnostic button
col14dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col14directives
col14duty time
col14electrical durability | IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
col14electromagnetic compatibility | Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission,
col14height | Height,
col14immunity to microbreaks
col14insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col14local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
col14marking
col14maximum leakage current | IEC62314,Only for solid state output,
col14maximum switching capacity | Maximum switching voltage, Maximum switching current, Maximum switching capacity,
col14maximum voltage drop | IEC62314,Only for solid state output,
col14mechanical durability | IEC61810-1
col14minimum switching capacity | IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity,
col14mounting position | In relation to normal vertical mounting plane,
col14mounting support | IEC/EN 60715,Without socket, IEC/EN 60715,With socket,
col14net weight
col14on-load factor
col14output logic | R1 (11-12-14), R2 (21-22-24),
col14output terminal
col14output type
col14overvoltage category | IEC60664-1
col14polarity
col14pollution degree | IEC60664-1
col14power consumption
col14power on delay
col14product certifications
col14relative humidity | IEC60068-2-30,Damp heat,
col14release of input voltage
col14repeat accuracy of time delay
col14reset time | through Un power reset, through front panel reset, through input control reset,
col14response time | on crossing the threshold,
col14safety reliability data | MTTF, B10,
col14seismic resistance | IEC60068-3-3
col14setting accuracy of time delay
col14shock resistance | IEC60068-2-27
col14short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
col14standards
col14status LED
col14supply frequency
col14supply terminal
col14supply voltage limits
col14thermal current | IEC60947-5-1
col14tightening torque | IEC60947-1,Tightening torque,
col14time delay drift
col14time delay range | "OFF" delay, "ON" delay, Inhibition,
col14time delay type | "OFF" delay, "ON" delay, Inhibition,
col14vibration resistance | IEC60068-2-6
col14width | Width,
col15 | IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d, IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Over / undercurrent (windows mode), Over current, Under current, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, MTTFd, B10d,
col15IP degree of protection | IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel, IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel,
col15Maximum length of probes cable | Maximum length of probes cable,
col15Maximum probe supplied current | Maximum probe supplied current,
col15Maximum probe supplied voltage | Maximum probe supplied voltage,
col15Minimum distance to adjacent devices | Horizontal, Vertical, Horizontal, Vertical,
col15[Ie] rated operational current | IEC61810-1,Rated switching current, IEC61810-1,Rated switching current,
col15[Ue] rated operational voltage | IEC61810-1,Rated switching voltage, IEC61810-1,Rated switching voltage,
col15[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3, IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col15[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3, IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col15[Us] rated supply voltage
col15ambient air temperature for operation | Operation, Operation,
col15ambient air temperature for storage | Storage, Storage,
col15bump resistance | IEC60068-2-29 IEC60068-2-29
col15cable stripping length | Cable stripping length, Cable stripping length,
col15circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2, Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
col15connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal), IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal),
col15contacts material
col15depth | Depth, Depth,
col15diagnostic button
col15dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3, IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col15directives
col15duty time
col15electrical durability | IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13, IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
col15electromagnetic compatibility | Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission, Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission,
col15height | Height, Height,
col15hysteresis | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
col15immunity to microbreaks
col15input frequency | Maximum cable capacitance,
col15input terminal | Input terminal,
col15insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3, IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col15internal input resistance | Internal input resistance,
col15local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
col15marking
col15maximum leakage current | IEC62314,Only for solid state output, IEC62314,Only for solid state output,
col15maximum measuring cycle | Maximum measuring cycles,
col15maximum switching capacity | Maximum switching voltage, Maximum switching current, Maximum switching capacity, Maximum switching voltage, Maximum switching current, Maximum switching capacity,
col15maximum voltage drop | IEC62314,Only for solid state output, IEC62314,Only for solid state output,
col15measurement method | Measurement method,
col15measurement range | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
col15mechanical durability | IEC61810-1 IEC61810-1
col15minimum switching capacity | IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity, IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity,
col15monitoring functions | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
col15mounting position | In relation to normal vertical mounting plane, In relation to normal vertical mounting plane,
col15mounting support | IEC/EN 60715,Without socket, IEC/EN 60715,With socket, IEC/EN 60715,Without socket, IEC/EN 60715,With socket,
col15net weight
col15on-load factor
col15output logic | R1 (11-12-14), R2 (21-22-24), R1 (11-12-14), R2 (21-22-24),
col15output terminal
col15output type
col15overvoltage category | IEC60664-1 IEC60664-1
col15polarity
col15pollution degree | IEC60664-1 IEC60664-1
col15power consumption
col15power on delay
col15product certifications
col15relative humidity | IEC60068-2-30,Damp heat, IEC60068-2-30,Damp heat,
col15release of input voltage
col15repeat accuracy of the switching threshold | Repeat accuracy (constant parameters),
col15repeat accuracy of time delay
col15reset time | through Un power reset, through front panel reset, through input control reset, through Un power reset, through front panel reset, through input control reset,
col15response time | on crossing the threshold, on crossing the threshold,
col15safety reliability data | MTTF, B10, MTTF, B10,
col15seismic resistance | IEC60068-3-3 IEC60068-3-3
col15setting accuracy of the switching threshold | Setting accuracy,
col15setting accuracy of time delay
col15shock resistance | IEC60068-2-27 IEC60068-2-27
col15short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse, IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
col15standards
col15status LED
col15supply frequency
col15supply terminal
col15supply voltage limits
col15switching threshold drift | Measurement error with supply voltage variation, Measurement error with temperature variation,
col15thermal current | IEC60947-5-1 IEC60947-5-1
col15tightening torque | IEC60947-1,Tightening torque, IEC60947-1,Tightening torque,
col15time delay drift
col15time delay range | "OFF" delay, "ON" delay, Inhibition, "OFF" delay, "ON" delay, Inhibition,
col15time delay type | "OFF" delay, "ON" delay, Inhibition, "OFF" delay, "ON" delay, Inhibition,
col15tripping threshold | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
col15vibration resistance | IEC60068-2-6 IEC60068-2-6
col15width | Width, Width,
col16 | IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d, IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Over / undercurrent (windows mode), Over current, Under current, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, MTTFd, B10d,
col16IP degree of protection | IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel, IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel,
col16Maximum length of probes cable | Maximum length of probes cable,
col16Maximum probe supplied current | Maximum probe supplied current,
col16Maximum probe supplied voltage | Maximum probe supplied voltage,
col16Minimum distance to adjacent devices | Horizontal, Vertical, Horizontal, Vertical,
col16[Ie] rated operational current | IEC61810-1,Rated switching current, IEC61810-1,Rated switching current,
col16[Ue] rated operational voltage | IEC61810-1,Rated switching voltage, IEC61810-1,Rated switching voltage,
col16[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3, IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col16[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3, IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col16[Us] rated supply voltage
col16ambient air temperature for operation | Operation, Operation,
col16ambient air temperature for storage | Storage, Storage,
col16bump resistance | IEC60068-2-29 IEC60068-2-29
col16cable stripping length | Cable stripping length, Cable stripping length,
col16circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2, Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
col16connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal), IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal),
col16contacts material
col16depth | Depth, Depth,
col16diagnostic button
col16dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3, IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col16directives
col16duty time
col16electrical durability | IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13, IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
col16electromagnetic compatibility | Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission, Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission,
col16height | Height, Height,
col16hysteresis | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
col16immunity to microbreaks
col16input frequency | Maximum cable capacitance,
col16input terminal | Input terminal,
col16insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3, IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col16internal input resistance | Internal input resistance,
col16local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
col16marking
col16maximum leakage current | IEC62314,Only for solid state output, IEC62314,Only for solid state output,
col16maximum measuring cycle | Maximum measuring cycles,
col16maximum switching capacity | Maximum switching voltage, Maximum switching current, Maximum switching capacity, Maximum switching voltage, Maximum switching current, Maximum switching capacity,
col16maximum voltage drop | IEC62314,Only for solid state output, IEC62314,Only for solid state output,
col16measurement method | Measurement method,
col16measurement range | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
col16mechanical durability | IEC61810-1 IEC61810-1
col16minimum switching capacity | IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity, IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity,
col16monitoring functions | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
col16mounting position | In relation to normal vertical mounting plane, In relation to normal vertical mounting plane,
col16mounting support | IEC/EN 60715,Without socket, IEC/EN 60715,With socket, IEC/EN 60715,Without socket, IEC/EN 60715,With socket,
col16net weight
col16on-load factor
col16output logic | R1 (11-12-14), R2 (21-22-24), R1 (11-12-14), R2 (21-22-24),
col16output terminal
col16output type
col16overvoltage category | IEC60664-1 IEC60664-1
col16polarity
col16pollution degree | IEC60664-1 IEC60664-1
col16power consumption
col16power on delay
col16product certifications
col16relative humidity | IEC60068-2-30,Damp heat, IEC60068-2-30,Damp heat,
col16release of input voltage
col16repeat accuracy of the switching threshold | Repeat accuracy (constant parameters),
col16repeat accuracy of time delay
col16reset time | through Un power reset, through front panel reset, through input control reset, through Un power reset, through front panel reset, through input control reset,
col16response time | on crossing the threshold, on crossing the threshold,
col16safety reliability data | MTTF, B10, MTTF, B10,
col16seismic resistance | IEC60068-3-3 IEC60068-3-3
col16setting accuracy of the switching threshold | Setting accuracy,
col16setting accuracy of time delay
col16shock resistance | IEC60068-2-27 IEC60068-2-27
col16short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse, IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
col16standards
col16status LED
col16supply frequency
col16supply terminal
col16supply voltage limits
col16switching threshold drift | Measurement error with supply voltage variation, Measurement error with temperature variation,
col16thermal current | IEC60947-5-1 IEC60947-5-1
col16tightening torque | IEC60947-1,Tightening torque, IEC60947-1,Tightening torque,
col16time delay drift
col16time delay range | "OFF" delay, "ON" delay, Inhibition, "OFF" delay, "ON" delay, Inhibition,
col16time delay type | "OFF" delay, "ON" delay, Inhibition, "OFF" delay, "ON" delay, Inhibition,
col16tripping threshold | 1 level - Fill operation, 1 level - Empty operation, 2 level - Fill operation, 2 level - Empty operation,
col16vibration resistance | IEC60068-2-6 IEC60068-2-6
col16width | Width, Width,
col17 | IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Over / undervoltage (windows mode), Over voltage, Undervoltage , E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, MTTFd, B10d,
col17IP degree of protection | IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel,
col17Minimum distance to adjacent devices | Horizontal, Vertical,
col17[Ie] rated operational current | IEC61810-1,Rated switching current,
col17[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col17[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col17[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col17[Us] rated supply voltage
col17ambient air temperature for operation | Operation,
col17ambient air temperature for storage | Storage,
col17bump resistance | IEC60068-2-29
col17cable stripping length | Cable stripping length,
col17circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
col17connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal),
col17contacts material
col17depth | Depth,
col17diagnostic button
col17dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col17directives
col17duty time
col17electrical durability | IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
col17electromagnetic compatibility | Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission,
col17height | Height,
col17immunity to microbreaks
col17insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col17local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
col17marking
col17maximum leakage current | IEC62314,Only for solid state output,
col17maximum switching capacity | Maximum switching voltage, Maximum switching current, Maximum switching capacity,
col17maximum voltage drop | IEC62314,Only for solid state output,
col17mechanical durability | IEC61810-1
col17minimum switching capacity | IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity,
col17mounting position | In relation to normal vertical mounting plane,
col17mounting support | IEC/EN 60715,Without socket, IEC/EN 60715,With socket,
col17net weight
col17on-load factor
col17output logic | R1 (11-12-14), R2 (21-22-24),
col17output terminal
col17output type
col17overvoltage category | IEC60664-1
col17polarity
col17pollution degree | IEC60664-1
col17power consumption
col17power on delay
col17product certifications
col17relative humidity | IEC60068-2-30,Damp heat,
col17release of input voltage
col17repeat accuracy of time delay
col17reset time | through Un power reset, through front panel reset, through input control reset,
col17response time | on crossing the threshold,
col17safety reliability data | MTTF, B10,
col17seismic resistance | IEC60068-3-3
col17setting accuracy of time delay
col17shock resistance | IEC60068-2-27
col17short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
col17standards
col17status LED
col17supply frequency
col17supply terminal
col17supply voltage limits
col17thermal current | IEC60947-5-1
col17tightening torque | IEC60947-1,Tightening torque,
col17time delay drift
col17time delay range | "OFF" delay, "ON" delay, Inhibition,
col17time delay type | "OFF" delay, "ON" delay, Inhibition,
col17vibration resistance | IEC60068-2-6
col17width | Width,
col18 | IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Over / undervoltage (windows mode), Over voltage, Undervoltage , E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, MTTFd, B10d,
col18IP degree of protection | IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel,
col18Minimum distance to adjacent devices | Horizontal, Vertical,
col18[Ie] rated operational current | IEC61810-1,Rated switching current,
col18[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col18[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col18[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col18[Us] rated supply voltage
col18ambient air temperature for operation | Operation,
col18ambient air temperature for storage | Storage,
col18bump resistance | IEC60068-2-29
col18cable stripping length | Cable stripping length,
col18circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
col18connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal),
col18contacts material
col18depth | Depth,
col18diagnostic button
col18dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col18directives
col18duty time
col18electrical durability | IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
col18electromagnetic compatibility | Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission,
col18height | Height,
col18immunity to microbreaks
col18insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col18local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
col18marking
col18maximum leakage current | IEC62314,Only for solid state output,
col18maximum switching capacity | Maximum switching voltage, Maximum switching current, Maximum switching capacity,
col18maximum voltage drop | IEC62314,Only for solid state output,
col18mechanical durability | IEC61810-1
col18minimum switching capacity | IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity,
col18mounting position | In relation to normal vertical mounting plane,
col18mounting support | IEC/EN 60715,Without socket, IEC/EN 60715,With socket,
col18net weight
col18on-load factor
col18output logic | R1 (11-12-14), R2 (21-22-24),
col18output terminal
col18output type
col18overvoltage category | IEC60664-1
col18polarity
col18pollution degree | IEC60664-1
col18power consumption
col18power on delay
col18product certifications
col18relative humidity | IEC60068-2-30,Damp heat,
col18release of input voltage
col18repeat accuracy of time delay
col18reset time | through Un power reset, through front panel reset, through input control reset,
col18response time | on crossing the threshold,
col18safety reliability data | MTTF, B10,
col18seismic resistance | IEC60068-3-3
col18setting accuracy of time delay
col18shock resistance | IEC60068-2-27
col18short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
col18standards
col18status LED
col18supply frequency
col18supply terminal
col18supply voltage limits
col18thermal current | IEC60947-5-1
col18tightening torque | IEC60947-1,Tightening torque,
col18time delay drift
col18time delay range | "OFF" delay, "ON" delay, Inhibition,
col18time delay type | "OFF" delay, "ON" delay, Inhibition,
col18vibration resistance | IEC60068-2-6
col18width | Width,
col19 | IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Over / undervoltage (windows mode), Over voltage, Undervoltage , E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, E1-M / B1-C, E2-M / B2-C, E3-M / B3-C, A1+ / A2-, Built in current transformer, MTTFd, B10d,
col19IP degree of protection | IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel,
col19Minimum distance to adjacent devices | Horizontal, Vertical,
col19[Ie] rated operational current | IEC61810-1,Rated switching current,
col19[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col19[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col19[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col19[Us] rated supply voltage
col19ambient air temperature for operation | Operation,
col19ambient air temperature for storage | Storage,
col19bump resistance | IEC60068-2-29
col19cable stripping length | Cable stripping length,
col19circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
col19connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal),
col19contacts material
col19depth | Depth,
col19diagnostic button
col19dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col19directives
col19duty time
col19electrical durability | IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
col19electromagnetic compatibility | Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission,
col19height | Height,
col19immunity to microbreaks
col19insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col19local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes,
col19marking
col19maximum leakage current | IEC62314,Only for solid state output,
col19maximum switching capacity | Maximum switching voltage, Maximum switching current, Maximum switching capacity,
col19maximum voltage drop | IEC62314,Only for solid state output,
col19mechanical durability | IEC61810-1
col19minimum switching capacity | IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity,
col19mounting position | In relation to normal vertical mounting plane,
col19mounting support | IEC/EN 60715,Without socket, IEC/EN 60715,With socket,
col19net weight
col19on-load factor
col19output logic | R1 (11-12-14), R2 (21-22-24),
col19output terminal
col19output type
col19overvoltage category | IEC60664-1
col19polarity
col19pollution degree | IEC60664-1
col19power consumption
col19power on delay
col19product certifications
col19relative humidity | IEC60068-2-30,Damp heat,
col19release of input voltage
col19repeat accuracy of time delay
col19reset time | through Un power reset, through front panel reset, through input control reset,
col19response time | on crossing the threshold,
col19safety reliability data | MTTF, B10,
col19seismic resistance | IEC60068-3-3
col19setting accuracy of time delay
col19shock resistance | IEC60068-2-27
col19short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
col19standards
col19status LED
col19supply frequency
col19supply terminal
col19supply voltage limits
col19thermal current | IEC60947-5-1
col19tightening torque | IEC60947-1,Tightening torque,
col19time delay drift
col19time delay range | "OFF" delay, "ON" delay, Inhibition,
col19time delay type | "OFF" delay, "ON" delay, Inhibition,
col19vibration resistance | IEC60068-2-6
col19width | Width,
col50 | IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d,
col50IP degree of protection | IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel,
col50Input nominal voltage selection | Input nominal voltage selection,
col50Minimum distance to adjacent devices | Horizontal, Vertical,
col50[Ie] rated operational current | IEC61810-1,Rated switching current,
col50[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col50[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col50[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col50[Us] rated supply voltage
col50ambient air temperature for operation | Operation,
col50ambient air temperature for storage | Storage,
col50bump resistance | IEC60068-2-29
col50cable stripping length | Cable stripping length,
col50circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
col50connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal),
col50contacts material
col50depth | Depth,
col50diagnostic button
col50dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col50directives
col50duty time
col50electrical durability | IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
col50electromagnetic compatibility | Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission,
col50height | Height,
col50hysteresis | Phase cut, Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
col50immunity to microbreaks
col50input frequency | Rated frequency, Frequency operating range,
col50input terminal | Input terminal,
col50insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col50internal input resistance | Internal input resistance,
col50local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Phase Cut, Phase Sequence Swap, Undervoltage <U, Overvoltage >U, Phase Asymmetry, Voltage Regeneration, Extreme Undervoltage <U (Phase loss), Extreme Overvoltage >U, Extreme Phase Asymmetry,
col50marking
col50maximum leakage current | IEC62314,Only for solid state output,
col50maximum measuring cycle | Maximum measuring cycles,
col50maximum switching capacity | Maximum switching voltage, Maximum switching current, Maximum switching capacity,
col50maximum voltage drop | IEC62314,Only for solid state output,
col50measurement method | Measurement method,
col50measurement range | Phase lost , Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme Overvoltage, Extreme Asymmetry,
col50mechanical durability | IEC61810-1
col50minimum switching capacity | IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity,
col50monitoring functions | Phase lost , Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry,
col50mounting position | In relation to normal vertical mounting plane,
col50mounting support | IEC/EN 60715,Without socket, IEC/EN 60715,With socket,
col50net weight
col50on-load factor
col50output logic | R1 (11-12-14), R2 (21-22-24),
col50output terminal
col50output type
col50overvoltage category | IEC60664-1
col50permissible input overload | permissible input overload,
col50polarity
col50pollution degree | IEC60664-1
col50power consumption
col50power on delay
col50product certifications
col50relative humidity | IEC60068-2-30,Damp heat,XX
col50release of input voltage
col50repeat accuracy of the switching threshold | Repeat accuracy (constant parameters),
col50repeat accuracy of time delay
col50reset time | through Un power reset, through front panel reset, through input control reset,
col50response time | on crossing the threshold,
col50safety reliability data | MTTF, B10,
col50seismic resistance | IEC60068-3-3
col50setting accuracy of the switching threshold | Setting accuracy,
col50setting accuracy of time delay
col50shock resistance | IEC60068-2-27
col50short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
col50standards
col50status LED
col50supply frequency
col50supply terminal
col50supply voltage limits
col50switching threshold drift | Measurement error with supply voltage variation, Measurement error with temperature variation,
col50thermal current | IEC60947-5-1
col50tightening torque | IEC60947-1,Tightening torque,
col50time delay drift
col50time delay range | "OFF" delay, "ON" delay, Inhibition,
col50time delay type | "OFF" delay, "ON" delay, Inhibition,
col50tripping threshold | Phase cut, Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
col50vibration resistance | IEC60068-2-6
col50width | Width,
col51 | IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d,
col51IP degree of protection | IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel,
col51Input nominal voltage selection | Input nominal voltage selection,
col51Minimum distance to adjacent devices | Horizontal, Vertical,
col51[Ie] rated operational current | IEC61810-1,Rated switching current,
col51[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col51[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col51[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col51[Us] rated supply voltage
col51ambient air temperature for operation | Operation,
col51ambient air temperature for storage | Storage,
col51bump resistance | IEC60068-2-29
col51cable stripping length | Cable stripping length,
col51circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
col51connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal),
col51contacts material
col51depth | Depth,
col51diagnostic button
col51dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col51directives
col51duty time
col51electrical durability | IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
col51electromagnetic compatibility | Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission,
col51height | Height,
col51hysteresis | Phase cut, Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
col51immunity to microbreaks
col51input frequency | Rated frequency, Frequency operating range,
col51input terminal | Input terminal,
col51insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col51internal input resistance | Internal input resistance,
col51local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Phase Cut, Phase Sequence Swap, Undervoltage <U, Overvoltage >U, Phase Asymmetry, Voltage Regeneration, Extreme Undervoltage <U (Phase loss), Extreme Overvoltage >U, Extreme Phase Asymmetry,
col51marking
col51maximum leakage current | IEC62314,Only for solid state output,
col51maximum measuring cycle | Maximum measuring cycles,
col51maximum switching capacity | Maximum switching voltage, Maximum switching current, Maximum switching capacity,
col51maximum voltage drop | IEC62314,Only for solid state output,
col51measurement method | Measurement method,
col51measurement range | Phase lost , Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme Overvoltage, Extreme Asymmetry,
col51mechanical durability | IEC61810-1
col51minimum switching capacity | IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity,
col51monitoring functions | Phase lost , Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry,
col51mounting position | In relation to normal vertical mounting plane,
col51mounting support | IEC/EN 60715,Without socket, IEC/EN 60715,With socket,
col51net weight
col51on-load factor
col51output logic | R1 (11-12-14), R2 (21-22-24),
col51output terminal
col51output type
col51overvoltage category | IEC60664-1
col51permissible input overload | permissible input overload,
col51polarity
col51pollution degree | IEC60664-1
col51power consumption
col51power on delay
col51product certifications
col51relative humidity | IEC60068-2-30,Damp heat,XX
col51release of input voltage
col51repeat accuracy of the switching threshold | Repeat accuracy (constant parameters),
col51repeat accuracy of time delay
col51reset time | through Un power reset, through front panel reset, through input control reset,
col51response time | on crossing the threshold,
col51safety reliability data | MTTF, B10,
col51seismic resistance | IEC60068-3-3
col51setting accuracy of the switching threshold | Setting accuracy,
col51setting accuracy of time delay
col51shock resistance | IEC60068-2-27
col51short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
col51standards
col51status LED
col51supply frequency
col51supply terminal
col51supply voltage limits
col51switching threshold drift | Measurement error with supply voltage variation, Measurement error with temperature variation,
col51thermal current | IEC60947-5-1
col51tightening torque | IEC60947-1,Tightening torque,
col51time delay drift
col51time delay range | "OFF" delay, "ON" delay, Inhibition,
col51time delay type | "OFF" delay, "ON" delay, Inhibition,
col51tripping threshold | Phase cut, Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
col51vibration resistance | IEC60068-2-6
col51width | Width,
col52 | IEC60721-3-3,Climatic category, Germanisher Lloyd,Environmental category, IEC60947-5-1,Cyclic Damp Heat Test, Supply,Rated Input 1,Voltage Input 2,Spec Input 3, Output 1, Output 2, Measurement mode, MTTFd, B10d,
col52IP degree of protection | IEC60529,Terminal Block, IEC60529,Housing, IEC60529,Front Panel,
col52Input nominal voltage selection | Input nominal voltage selection,
col52Minimum distance to adjacent devices | Horizontal, Vertical,
col52[Ie] rated operational current | IEC61810-1,Rated switching current,
col52[Ue] rated operational voltage | IEC61810-1,Rated switching voltage,
col52[Ui] rated insulation voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col52[Uimp] rated impulse withstand voltage | IEC60664-1,Supply, IEC60664-1,Input 1, IEC60664-1,Input 2, IEC60664-1,Input 3, IEC60664-1,Output 1, IEC60664-1,Output 2, IEC60664-1,Supply / Input 1,Galvanic IEC60664-1,Supply / Input 2,Isolated IEC60664-1,Supply / Input 3,Circuit IEC60664-1,Supply / Output 1, IEC60664-1,Supply / Output 2, IEC60664-1,Output 1 / Output 2, IEC60664-1,Input 1 / Output 1, IEC60664-1,Input 1 / Output 2, IEC60664-1,Input 2 / Output 1, IEC60664-1,Input 2 / Output 2, IEC60664-1,Input 3 / Output 1, IEC60664-1,Input 3 / Output 2, IEC60664-1,Input 1 / Input 2, IEC60664-1,Input 2 / Input 3, IEC60664-1,Input 1 / Input 3,
col52[Us] rated supply voltage
col52ambient air temperature for operation | Operation,
col52ambient air temperature for storage | Storage,
col52bump resistance | IEC60068-2-29
col52cable stripping length | Cable stripping length,
col52circuit group | Supply,Terminal Input 1, Input 2, Input 3, Output 1, Output 2,
col52connections - terminals | IEC60947-1,Solid cable without cable end (screw terminal), IEC60947-1,Flexible cable with cable end (screw terminal), IEC60947-1,Solid cable (spring terminal), IEC60947-1,Flexible cable (spring terminal),
col52contacts material
col52depth | Depth,
col52diagnostic button
col52dielectric strength | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col52directives
col52duty time
col52electrical durability | IEC60947-4-1,AC-1, IEC60947-4-1,DC-1, IEC60947-5-1,AC-15, IEC60947-5-1,DC-13,
col52electromagnetic compatibility | Generic immunity standard, IEC61000-4-2,Electrostatic discharge, IEC61000-4-3,Radiated RF & electromagnetic field, IEC61000-4-4,Fast transient / burst, IEC61000-4-5,Surge, IEC61000-4-6,Conducted RF disturbance, IEC61000-4-8,Power frequency magnetic field, IEC61000-4-11,Voltage dips, short interruption & variations on power line, IEC61000-4-18,1 MHz oscillation wave, IEC61000-4-29,DC voltage interruption, IEC61000-4-13,Low frequency harmonics, Germanisher Lloyd,Conducted low frequency interference (harmonics), Generic emission standard, EN55022 / CISPR22,Radiated RF & electromagnetic field (IT equiment), EN55011 / CISPR11,Radiated RF & electromagnetic field (Medical equiment), Germanisher Lloyd,Radiated emission from enclosure port, EN55022 / CISPR22,Conducted RF emission on power line (IT equiment), EN55011 / CISPR11,Conducted RF emission on power line (Medical equiment), Germanisher Lloyd,Conducted emission,
col52height | Height,
col52hysteresis | Phase cut, Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
col52immunity to microbreaks
col52input frequency | Rated frequency, Frequency operating range,
col52input terminal | Input terminal,
col52insulation resistance | IEC60255-27,Supply / Input 1, IEC60255-27,Supply / Input 2, IEC60255-27,Supply / Input 3, IEC60255-27,Supply / Output 1, IEC60255-27,Supply / Output 2, IEC60255-27,Output 1 / Output 2, IEC60255-27,Input 1 / Output 1, IEC60255-27,Input 1 / Output 2, IEC60255-27,Input 2 / Output 1, IEC60255-27,Input 2 / Output 2, IEC60255-27,Input 3 / Output 1, IEC60255-27,Input 3 / Output 2, IEC60255-27,Input 1 / Input 2, IEC60255-27,Input 2 / Input 3, IEC60255-27,Input 1 / Input 3,
col52internal input resistance | Internal input resistance,
col52local signalling | Power supply availability, Power supply not availability, Timing in-progress, Output is energized, Output is de-energized, Range Setting Changes, Phase Cut, Phase Sequence Swap, Undervoltage <U, Overvoltage >U, Phase Asymmetry, Voltage Regeneration, Extreme Undervoltage <U (Phase loss), Extreme Overvoltage >U, Extreme Phase Asymmetry,
col52marking
col52maximum leakage current | IEC62314,Only for solid state output,
col52maximum measuring cycle | Maximum measuring cycles,
col52maximum switching capacity | Maximum switching voltage, Maximum switching current, Maximum switching capacity,
col52maximum voltage drop | IEC62314,Only for solid state output,
col52measurement method | Measurement method,
col52measurement range | Phase lost , Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme Overvoltage, Extreme Asymmetry,
col52mechanical durability | IEC61810-1
col52minimum switching capacity | IEC60947-5-4,Minimum switching voltage, IEC60947-5-4,Minimum switching current, IEC60947-5-4,Minimum switching capacity,
col52monitoring functions | Phase lost , Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry,
col52mounting position | In relation to normal vertical mounting plane,
col52mounting support | IEC/EN 60715,Without socket, IEC/EN 60715,With socket,
col52net weight
col52on-load factor
col52output logic | R1 (11-12-14), R2 (21-22-24),
col52output terminal
col52output type
col52overvoltage category | IEC60664-1
col52permissible input overload | permissible input overload,
col52polarity
col52pollution degree | IEC60664-1
col52power consumption
col52power on delay
col52product certifications
col52relative humidity | IEC60068-2-30,Damp heat,XX
col52release of input voltage
col52repeat accuracy of the switching threshold | Repeat accuracy (constant parameters),
col52repeat accuracy of time delay
col52reset time | through Un power reset, through front panel reset, through input control reset,
col52response time | on crossing the threshold,
col52safety reliability data | MTTF, B10,
col52seismic resistance | IEC60068-3-3
col52setting accuracy of the switching threshold | Setting accuracy,
col52setting accuracy of time delay
col52shock resistance | IEC60068-2-27
col52short circuit protection | IEC60947-5-1,Relay Output by external fuse, IEC62314,Solid State Output by external fuse,
col52standards
col52status LED
col52supply frequency
col52supply terminal
col52supply voltage limits
col52switching threshold drift | Measurement error with supply voltage variation, Measurement error with temperature variation,
col52thermal current | IEC60947-5-1
col52tightening torque | IEC60947-1,Tightening torque,
col52time delay drift
col52time delay range | "OFF" delay, "ON" delay, Inhibition,
col52time delay type | "OFF" delay, "ON" delay, Inhibition,
col52tripping threshold | Phase cut, Phase sequence, Over / undervoltage (symmetry windows mode), Over voltage, Undervoltage , Phase asymmetry, Disconnection of neutral, Voltage Regeneration, Extreme undervoltage (Phase loss), Extreme Overvoltage, Extreme Asymmetry,
col52vibration resistance | IEC60068-2-6
col52width | Width,

## 3P Voltage Control Spec
Main Parameters | Category | Sub Parameters | Conforming to | Remark | Standardized Datasheet Param | Selected for Publication | Old Datasheet | Unit | RM22TG20 | RM22TR33 | RM22TR31 | RM22TU23 | RM22TU21 | RM22TA33 | RM22TA31 | RM17TG20 | 84873021 | 84873891 | RM17TG00 | RM10TG00 | 84873029 | 84873890 | 84873034 | 84873195 | RM17TE00 | RM10TE00 | 84873025 | RM17TU00 | 84873023 | 84873805 | RM17TA00 | 84873024 | 84873892 | 84873804 | RM17TT00 | 84873022 | RM35TF30 | 84873026 | 84873893 | RM35TF30SP01 | RM35UB330 | 84873220 | 84873894 | RM35UB3N30 | 84873221 | 84873895 | RM17UB310 | 84873222 | 84873896 | col50 | col51 | col52 | Competitor Spec Reference | 84873034 (Catch-Up Juret - Actual) | 84873034 (Catch-Up Juret - For Crouzet) | RM4TR | RM4TG20 | RM4TU | RM4TA | RM4UB | 84873004 | 848792299 | 1SVR 630 794 R3300 | K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O) | DPA51CM44
Standard
Product standard |  |  |  | Common C_Rly Spec | standards | Published | Published |  | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM17TE00 | Same as RM17TE00 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM17TU00 | Same as RM17TU00 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM17TT00 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM35UB330 | Same as RM35UB330 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM35UB3N30 | Same as RM35UB3N30 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | EN60255-1, IEC60255-1 | EN60255-1, IEC60255-1 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | Not specified | Not specified | EN60255-6, IEC60255-6, EN50178 | EN60947-5-1 | Not specified
Product certifications |  |  |  | Common C_Rly Spec | product certifications | Published | Published |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | CCC, CE, China ROHS | UL, CSA, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CE, China ROHS | Same as 84873034 | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | Same as RM35TF30 | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS |  |  |  |  | UL, CSA, CE, EAC | UL, CSA, CE, EAC | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | cULus, CE | cULus, CE | cULus, CSA, GL, C-Tick, GOST, CCC, CB |  | UL, CSA
Marking |  |  |  | Common C_Rly Spec | marking | Published |  |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | CCC, CE, China ROHS | UL, CSA, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CE, China ROHS | Same as 84873034 | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | Same as RM35TF30 | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS |  |  |  |  | UL, CSA, CE, EAC | UL, CSA, CE, EAC | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | cULus, CE | cULus, CE | cULus, CSA, GL, C-Tick, GOST, CCC, CB, CE |  | UL, CSA, CE
Low voltage directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 2014/35/EU | Same as RM17TE00 | Same as RM17TE00 | 2014/35/EU | Same as RM17TU00 | Same as RM17TU00 | 2014/35/EU | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 2014/35/EU | Same as RM17TT00 | 2014/35/EU | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 2014/35/EU | Same as RM35UB330 | Same as RM35UB330 | 2014/35/EU | Same as RM35UB3N30 | Same as RM35UB3N30 | 2014/35/EU | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | 2006/95/EC | 2006/95/EC | 2006/95/EC | 2006/95/EC | 2006/95/EC | Not specified | Not specified | 2006/95/EG |  | Not specified
EMC directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 2014/30/EU | Same as RM17TE00 | Same as RM17TE00 | 2014/30/EU | Same as RM17TU00 | Same as RM17TU00 | 2014/30/EU | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 2014/30/EU | Same as RM17TT00 | 2014/30/EU | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 2014/30/EU | Same as RM35UB330 | Same as RM35UB330 | 2014/30/EU | Same as RM35UB3N30 | Same as RM35UB3N30 | 2014/30/EU | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | 2004/108/EC | 2004/108/EC | 2004/108/EC | 2004/108/EC | 2004/108/EC | Not specified | Not specified | 2004/108/EG |  | Not specified
ROHS directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 2011/65/EU | Same as RM17TE00 | Same as RM17TE00 | 2011/65/EU | Same as RM17TU00 | Same as RM17TU00 | 2011/65/EU | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 2011/65/EU | Same as RM17TT00 | 2011/65/EU | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 2011/65/EU | Same as RM35UB330 | Same as RM35UB330 | 2011/65/EU | Same as RM35UB3N30 | Same as RM35UB3N30 | 2011/65/EU | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC | Not specified | Not specified | 2002/95/EC |  | Not specified
Environment Characteristics
Environmental Condition |  | Climatic category | IEC60721-3-3 | Common C_Rly Spec |  |  |  |  | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM17TE00 | Same as RM17TE00 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM17TU00 | Same as RM17TU00 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM17TT00 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM35UB330 | Same as RM35UB330 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM35UB3N30 | Same as RM35UB3N30 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Not specified | Not specified | 3K3 | 3K3 | 3K3 | 3K3 | 3K3 | Not specified | Not specified | 3K3 |  | Not specified
|  | Environmental category | Germanisher Lloyd | Common C_Rly Spec |  |  |  |  | Class C | Class C | Class C | Class C | Class C | Class C | Class C | Class C | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Class C | Same as RM17TE00 | Same as RM17TE00 | Class C | Same as RM17TU00 | Same as RM17TU00 | Class C | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Class C | Same as RM17TT00 | Class C | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Class C | Same as RM35UB330 | Same as RM35UB330 | Class C | Same as RM35UB3N30 | Same as RM35UB3N30 | Class C | Same as RM17UB310 | Same as RM17UB310
Ambient air temperature around the device |  | Storage |  | Common C_Rly Spec | ambient air temperature for storage | Published | Published | oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | -30oC..+70oC | Same as 84873034 | -40oC..+70oC | Same as RM17TE00 | Same as RM17TE00 | -40oC..+70oC | Same as RM17TU00 | Same as RM17TU00 | -40oC..+70oC | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | -40oC..+70oC | Same as RM17TT00 | -40oC..+70oC | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | -40oC..+70oC | Same as RM35UB330 | Same as RM35UB330 | -40oC..+70oC | Same as RM35UB3N30 | Same as RM35UB3N30 | -40oC..+70oC | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | -30…+70 | -30…+70 | -40…+85 | -40…+85 | -40…+85 | -40…+85 | -40…+85 | -30…+70 | -30…+70 | -40…+85 | -25…+65 | -30…+80, R.H. < 95%
|  | Operation |  |  | ambient air temperature for operation | Published | Published | oC | -20oC..+60oC @50Hz -20oC..+50oC @60Hz | -20oC..+60oC @50Hz -20oC..+50oC @60Hz | -20oC..+60oC @50Hz -20oC..+50oC @60Hz | -20oC..+60oC @50Hz -20oC..+50oC @60Hz | -20oC..+60oC @50Hz -20oC..+50oC @60Hz | -20oC..+60oC @50Hz -20oC..+50oC @60Hz | -20oC..+60oC @50Hz -20oC..+50oC @60Hz | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM17TE00 | Same as RM17TE00 | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM17TU00 | Same as RM17TU00 | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM17TT00 | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM35UB330 | Same as RM35UB330 | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM35UB3N30 | Same as RM35UB3N30 | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | -20…+50 | -20…+50 | -20…+65 | -20…+65 | -20…+65 | -20…+65 | -20…+65 | Not specified | Not specified | -25…+60 | -20…+60 | -20…+50, R.H. < 95%
Relative humidity | XX | Damp heat | IEC60068-2-30 | Common C_Rly Spec | relative humidity | Published | Published | XX | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TE00 | Same as RM17TE00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TU00 | Same as RM17TU00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TT00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM35UB330 | Same as RM35UB330 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM35UB3N30 | Same as RM35UB3N30 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 2 cycles 24h ;+25°C +55°C 95%HR | 15%...85% | 15%...85% | 15%...85% | 15%...85% | 15%...85% | Not specified | Not specified | +55°C, 6 cycles |  | Not specified
|  | Cyclic Damp Heat Test | IEC60947-5-1 | Common C_Rly Spec |  |  |  |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | - | Same as 84873034 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TE00 | Same as RM17TE00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TU00 | Same as RM17TU00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TT00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM35UB330 | Same as RM35UB330 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM35UB3N30 | Same as RM35UB3N30 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Not specified | Not specified
Vibration resistance |  |  | IEC60068-2-6 | Common C_Rly Spec | vibration resistance | Published | Published |  | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM17TE00 | Same as RM17TE00 | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM17TU00 | Same as RM17TU00 | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM17TT00 | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM35UB330 | Same as RM35UB330 | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM35UB3N30 | Same as RM35UB3N30 | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | ±0.35mm from 5Hz…57.6Hz 1g from 57.6Hz..150Hz | 0.035mm from 10Hz…150Hz | a=0.35ms from 10Hz…55Hz | a=0.35ms from 10Hz…55Hz | a=0.35ms from 10Hz…55Hz | a=0.35ms from 10Hz…55Hz | a=0.35ms from 10Hz…55Hz | Not specified | Not specified | Class 2 |  | Not specified
Shock resistance |  |  | IEC60068-2-27 | Common C_Rly Spec | shock resistance | Published | Published |  | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM17TE00 | Same as RM17TE00 | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM17TU00 | Same as RM17TU00 | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM17TT00 | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM35UB330 | Same as RM35UB330 | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM35UB3N30 | Same as RM35UB3N30 | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 15gn - 11ms | 5 gn | 15 gn | 15 gn | 15 gn | 15 gn | 15 gn | Not specified | Not specified | Class 2 |  | Not specified
Bump resistance |  |  | IEC60068-2-29 | Common C_Rly Spec | bump resistance |  |  |  | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM17TE00 | Same as RM17TE00 | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM17TU00 | Same as RM17TU00 | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM17TT00 | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM35UB330 | Same as RM35UB330 | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM35UB3N30 | Same as RM35UB3N30 | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM17UB310 | Same as RM17UB310
Seismic resistance |  |  | IEC60068-3-3 | Common C_Rly Spec | seismic resistance |  |  |  | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM17TE00 | Same as RM17TE00 | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM17TU00 | Same as RM17TU00 | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM17TT00 | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM35UB330 | Same as RM35UB330 | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM35UB3N30 | Same as RM35UB3N30 | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM17UB310 | Same as RM17UB310
IP degree of protection |  | Terminal Block | IEC60529 |  | IP degree of protection | Published | Published |  | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | IP20 | Same as RM17TE00 | Same as RM17TE00 | IP20 | Same as RM17TU00 | Same as RM17TU00 | IP20 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | IP20 | Same as RM17TT00 | IP20 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | IP20 | Same as RM35UB330 | Same as RM35UB330 | IP20 | Same as RM35UB3N30 | Same as RM35UB3N30 | IP20 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | IP20 | IP40 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 |  | IP20
|  | Housing | IEC60529 |  | IP degree of protection | Published | Published |  | IP40 | IP40 | IP40 | IP40 | IP40 | IP40 | IP40 | IP30 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | IP30 | Same as RM17TE00 | Same as RM17TE00 | IP30 | Same as RM17TU00 | Same as RM17TU00 | IP30 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | IP30 | Same as RM17TT00 | IP30 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | IP30 | Same as RM35UB330 | Same as RM35UB330 | IP30 | Same as RM35UB3N30 | Same as RM35UB3N30 | IP30 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | IP40 | IP20 | IP50 | IP50 | IP50 | IP50 | IP50 | IP40 | IP40 | IP50 |  | Not specified
|  | Front Panel | IEC60529 |  | IP degree of protection |  |  |  | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | - | Same as RM17TG20 | - | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | IP40 | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified |  | Not specified
Installation Data
Dimension (nominal) |  | Width |  |  | width | Published |  | mm | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 17.5 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | 22.5 | Same as 84873034 | 17.5 | Same as RM17TE00 | Same as RM17TE00 | 17.5 | Same as RM17TU00 | Same as RM17TU00 | 17.5 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 17.5 | Same as RM17TT00 | 35 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 35 | Same as RM35UB330 | Same as RM35UB330 | 35 | Same as RM35UB3N30 | Same as RM35UB3N30 | 17.5 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 78 x 80 | 22.5 x 78 x 80 | 22.5 x 78 x 80 | 22.5 x 78 x 80 | 22.5 x 78 x 80 | 22.5 x 78.5 x 100 | 22.5 x 78.5 x 100 | 22.5 x 78 x 100 |  | 17.5 x 81 x 67.2
|  | Height |  |  | height | Published |  | mm | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | 90 | Same as 84873034 | 90 | Same as RM17TE00 | Same as RM17TE00 | 90 | Same as RM17TU00 | Same as RM17TU00 | 90 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 90 | Same as RM17TT00 | 90 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 90 | Same as RM35UB330 | Same as RM35UB330 | 90 | Same as RM35UB3N30 | Same as RM35UB3N30 | 90 | Same as RM17UB310 | Same as RM17UB310
|  | Depth |  |  | depth | Published |  | mm | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 72 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | 73 | Same as 84873034 | 72 | Same as RM17TE00 | Same as RM17TE00 | 72 | Same as RM17TU00 | Same as RM17TU00 | 72 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 72 | Same as RM17TT00 | 72 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 72 | Same as RM35UB330 | Same as RM35UB330 | 72 | Same as RM35UB3N30 | Same as RM35UB3N30 | 72 | Same as RM17UB310 | Same as RM17UB310
Weight (without packaging) |  |  |  |  | net weight | Published |  | g | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 85 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 80 | Same as RM17TE00 | Same as RM17TE00 | 80 | Same as RM17TU00 | Same as RM17TU00 | 80 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 80 | Same as RM17TT00 | 120 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 130 | Same as RM35UB330 | Same as RM35UB330 | 130 | Same as RM35UB3N30 | Same as RM35UB3N30 | 80 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | ? | To be updated | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 130 |  | 75
Mounting |  | Without socket | IEC/EN 60715 |  | mounting support | Published | Published |  | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | On 35 mm DIN rail | Same as RM17TE00 | Same as RM17TE00 | On 35 mm DIN rail | Same as RM17TU00 | Same as RM17TU00 | On 35 mm DIN rail | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | On 35 mm DIN rail | Same as RM17TT00 | On 35 mm DIN rail | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | On 35 mm DIN rail | Same as RM35UB330 | Same as RM35UB330 | On 35 mm DIN rail | Same as RM35UB3N30 | Same as RM35UB3N30 | On 35 mm DIN rail | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | On 35 mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail |  |  | DIN rail snap-on mounting without any tool |  | Mounting in DIN rail according EN50022
|  | With socket | IEC/EN 60715 |  | mounting support |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | - | - | - | - | - | - | - | - |  | -
Mounting position |  | In relation to normal vertical mounting plane |  | Common C_Rly Spec | mounting position | Published | Published |  | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Any position | Same as RM17TE00 | Same as RM17TE00 | Any position | Same as RM17TU00 | Same as RM17TU00 | Any position | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Any position | Same as RM17TT00 | Any position | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Any position | Same as RM35UB330 | Same as RM35UB330 | Any position | Same as RM35UB3N30 | Same as RM35UB3N30 | Any position | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Any position | Any position | Any position | Any position | Any position | Any position | Any position |  |  | Any position |  | Not specified
Minimum distance to adjacent devices |  | Horizontal |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | 1x product height | 1x product height | 1x product height | 1x product height | 1x product height | 1x product height | 1x product height | 1x product height | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1x product height | Same as RM17TE00 | Same as RM17TE00 | 1x product height | Same as RM17TU00 | Same as RM17TU00 | 1x product height | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1x product height | Same as RM17TT00 | 1x product height | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1x product height | Same as RM35UB330 | Same as RM35UB330 | 1x product height | Same as RM35UB3N30 | Same as RM35UB3N30 | 1x product height | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | None |  | Not specified
|  | Vertical |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | 1x product width | 1x product width | 1x product width | 1x product width | 1x product width | 1x product width | 1x product width | 1x product width | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1x product width | Same as RM17TE00 | Same as RM17TE00 | 1x product width | Same as RM17TU00 | Same as RM17TU00 | 1x product width | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1x product width | Same as RM17TT00 | 1x product width | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1x product width | Same as RM35UB330 | Same as RM35UB330 | 1x product width | Same as RM35UB3N30 | Same as RM35UB3N30 | 1x product width | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | None |  | Not specified
Wiring connection (Clamping Capacity) |  | Solid cable without cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM17TE00 | Same as RM17TE00 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM17TU00 | Same as RM17TU00 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1 conductor: 0.5…4 (AWG 20…AWG 11) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM17TT00 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM35UB330 | Same as RM35UB330 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM35UB3N30 | Same as RM35UB3N30 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | 1 conductor:0.5…4 2 conductor:0.5…2.5 | 2 conductor: 2.5 | 2 conductor: 2.5 | 2 conductor: 2.5 | 2 conductor: 2.5 | 2 conductor: 2.5 | 1 conductor: 4 (AWG11) 2 conductor:2.5 (AWG14) | 1 conductor: 4 (AWG11) 2 conductor:2.5 (AWG14) | 2 conductor:0.75…2.5 (AWG18…AWG14) |  | Not specified
|  | Flexible cable with cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | Same as RM17TE00 | Same as RM17TE00 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | Same as RM17TU00 | Same as RM17TU00 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | Same as RM17TT00 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | Same as RM35UB330 | Same as RM35UB330 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | Same as RM35UB3N30 | Same as RM35UB3N30 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | 1 conductor:0.2…2.5 2 conductor:0.2…1.5 | 2 conductor: 1.5 | 2 conductor: 1.5 | 2 conductor: 1.5 | 2 conductor: 1.5 | 2 conductor: 1.5 | 2 conductor: 1.5 (AWG16) | 2 conductor: 1.5 (AWG16) | 2 conductor:0.5…4 (AWG20…AWG12) |  | Not specified
|  | Solid cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Flexible cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Tightening torque | IEC60947-1 | Common C_Rly Spec | tightening torque | Published | Published | Nm | 0.6…1 Nm | 0.6…1 Nm | 0.6…1 Nm | 0.6…1 Nm | 0.6…1 Nm | 0.6…1 Nm | 0.6…1 Nm | 0.6…1 Nm | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 0.6…1 Nm | Same as RM17TE00 | Same as RM17TE00 | 0.6…1 Nm | Same as RM17TU00 | Same as RM17TU00 | 0.6…1 Nm | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 0.6…1 Nm | Same as RM17TT00 | 0.6…1 Nm | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 0.6…1 Nm | Same as RM35UB330 | Same as RM35UB330 | 0.6…1 Nm | Same as RM35UB3N30 | Same as RM35UB3N30 | 0.6…1 Nm | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 0.6…1.0 | 0.6…1 | 0.6…1.1 | 0.6…1.1 | 0.6…1.1 | 0.6…1.1 | 0.6…1.1 | Max 1 | Max 1 | 0.6…0.8 | 0.54Nm (Rec) 0.59Nm (Max) | 0.5Nm (Max)
|  | Cable stripping length |  | Common C_Rly Spec | cable stripping length |  |  | mm | 6mm (Screw Terminal) | 6mm (Screw Terminal) | 6mm (Screw Terminal) | 6mm (Screw Terminal) | 6mm (Screw Terminal) | 6mm (Screw Terminal) | 6mm (Screw Terminal) | 6mm (Screw Terminal) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 6mm (Screw Terminal) | Same as RM17TE00 | Same as RM17TE00 | 6mm (Screw Terminal) | Same as RM17TU00 | Same as RM17TU00 | 6mm (Screw Terminal) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 6mm (Screw Terminal) | Same as RM17TT00 | 6mm (Screw Terminal) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 6mm (Screw Terminal) | Same as RM35UB330 | Same as RM35UB330 | 6mm (Screw Terminal) | Same as RM35UB3N30 | Same as RM35UB3N30 | 6mm (Screw Terminal) | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified |  |  | 7 |  | Not specified
Duty time |  |  |  | Common C_Rly Spec | duty time |  |  | % | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1 | Same as RM17TE00 | Same as RM17TE00 | 1 | Same as RM17TU00 | Same as RM17TU00 | 1 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1 | Same as RM17TT00 | 1 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1 | Same as RM35UB330 | Same as RM35UB330 | 1 | Same as RM35UB3N30 | Same as RM35UB3N30 | 1 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified |  |  | 100 |  | Not specified
Electromagnetic Compatibility
Immunity |  | Generic immunity standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | IEC61000-6-1, IEC 61000-6-2 | Same as RM17TE00 | Same as RM17TE00 | IEC61000-6-1, IEC 61000-6-2 | Same as RM17TU00 | Same as RM17TU00 | IEC61000-6-1, IEC 61000-6-2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | IEC61000-6-1, IEC 61000-6-2 | Same as RM17TT00 | IEC61000-6-1, IEC 61000-6-2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | IEC61000-6-1, IEC 61000-6-2 | Same as RM35UB330 | Same as RM35UB330 | IEC61000-6-1, IEC 61000-6-2 | Same as RM35UB3N30 | Same as RM35UB3N30 | IEC61000-6-1, IEC 61000-6-2 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-2 | IEC50082-2 | IEC50082-2 | IEC50082-2 | IEC50082-2 | IEC50082-2 | Not specified | Not specified | IEC61000-6-1, IEC61000-6-2 |  | IEC61000-6-2
|  | Electrostatic discharge | IEC61000-4-2 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Level III (Contact : 6kV / Air : 8kV) | Same as RM17TE00 | Same as RM17TE00 | Level III (Contact : 6kV / Air : 8kV) | Same as RM17TU00 | Same as RM17TU00 | Level III (Contact : 6kV / Air : 8kV) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Level III (Contact : 6kV / Air : 8kV) | Same as RM17TT00 | Level III (Contact : 6kV / Air : 8kV) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Level III (Contact : 6kV / Air : 8kV) | Same as RM35UB330 | Same as RM35UB330 | Level III (Contact : 6kV / Air : 8kV) | Same as RM35UB3N30 | Same as RM35UB3N30 | Level III (Contact : 6kV / Air : 8kV) | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Level III (Contact : 6kV / Air : 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Not specified | Not specified | Level 3 (6kV / 8kV) |  | Not specified
|  | Radiated RF & electromagnetic field | IEC61000-4-3 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM17TE00 | Same as RM17TE00 | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM17TU00 | Same as RM17TU00 | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM17TT00 | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM35UB330 | Same as RM35UB330 | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM35UB3N30 | Same as RM35UB3N30 | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Not specified | Not specified | Level 3 (10V/m) |  | Not specified
|  | Fast transient / burst | IEC61000-4-4 |  | electromagnetic compatibility | Published |  |  | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM17TE00 | Same as RM17TE00 | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM17TU00 | Same as RM17TU00 | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM17TT00 | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM35UB330 | Same as RM35UB330 | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM35UB3N30 | Same as RM35UB3N30 | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Level III (Supply: 2kV, 5kHx / 100kHz) (I/O: 2kV, 5kHx / 100kHz) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Not specified | Not specified | Level 3 (2kV / 2kHz) |  | Not specified
|  | Surge | IEC61000-4-5 |  | electromagnetic compatibility | Published |  |  | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM17TE00 | Same as RM17TE00 | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM17TU00 | Same as RM17TU00 | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM17TT00 | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM35UB330 | Same as RM35UB330 | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM35UB3N30 | Same as RM35UB3N30 | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Not specified | Not specified | Level 3 (2kV phase-phase) |  | Not specified
|  | Conducted RF disturbance | IEC61000-4-6 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (10Vrms : 0.15MHz to 80MHz) | Level III (10Vrms : 0.15MHz to 80MHz) | Level III (10Vrms : 0.15MHz to 80MHz) | Level III (10Vrms : 0.15MHz to 80MHz) | Level III (10Vrms : 0.15MHz to 80MHz) | Level III (10Vrms : 0.15MHz to 80MHz) | Level III (10Vrms : 0.15MHz to 80MHz) | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM17TE00 | Same as RM17TE00 | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM17TU00 | Same as RM17TU00 | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM17TT00 | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM35UB330 | Same as RM35UB330 | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM35UB3N30 | Same as RM35UB3N30 | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Not specified | Not specified | Level 3 (10V) |  | Not specified
|  | Power frequency magnetic field | IEC61000-4-8 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM17TE00 | Same as RM17TE00 | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM17TU00 | Same as RM17TU00 | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM17TT00 | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM35UB330 | Same as RM35UB330 | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM35UB3N30 | Same as RM35UB3N30 | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | -
|  | Voltage dips, short interruption & variations on power line | IEC61000-4-11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM17TE00 | Same as RM17TE00 | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM17TU00 | Same as RM17TU00 | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM17TT00 | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM35UB330 | Same as RM35UB330 | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM35UB3N30 | Same as RM35UB3N30 | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Not specified | Not specified | Not specified |  | Not specified
|  | 1 MHz oscillation wave | IEC61000-4-18 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM17TE00 | Same as RM17TE00 | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM17TU00 | Same as RM17TU00 | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM17TT00 | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM35UB330 | Same as RM35UB330 | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM35UB3N30 | Same as RM35UB3N30 | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | -
|  | DC voltage interruption | IEC61000-4-29 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | -
|  | Low frequency harmonics | IEC61000-4-13 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | Not tested | Not tested | Not tested | Not tested | Not tested | Not specified | Not specified | Class 3 |  | Not specified
|  | Conducted low frequency interference (harmonics) | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM17TE00 | Same as RM17TE00 | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM17TU00 | Same as RM17TU00 | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM17TT00 | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM35UB330 | Same as RM35UB330 | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM35UB3N30 | Same as RM35UB3N30 | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | · | ? | ? | ? | ? | ? | Not specified | Not specified
Emission |  | Generic emission standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | IEC61000-6-3, IEC 61000-6-4 | Same as RM17TE00 | Same as RM17TE00 | IEC61000-6-3, IEC 61000-6-4 | Same as RM17TU00 | Same as RM17TU00 | IEC61000-6-3, IEC 61000-6-4 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | IEC61000-6-3, IEC 61000-6-4 | Same as RM17TT00 | IEC61000-6-3, IEC 61000-6-4 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | IEC61000-6-3, IEC 61000-6-4 | Same as RM35UB330 | Same as RM35UB330 | IEC61000-6-3, IEC 61000-6-4 | Same as RM35UB3N30 | Same as RM35UB3N30 | IEC61000-6-3, IEC 61000-6-4 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC50081-1, IEC50081-2 | IEC50081-1, IEC50081-2 | IEC50081-1, IEC50081-2 | IEC50081-1, IEC50081-2 | IEC50081-1, IEC50081-2 | Not specified | Not specified | IEC61000-6-3, IEC61000-6-4 |  | IEC50081-1
|  | Radiated RF & electromagnetic field (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B | Class B | Class B | Class B | Class B | Class B | Class B | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Class B | Same as RM17TE00 | Same as RM17TE00 | Class B | Same as RM17TU00 | Same as RM17TU00 | Class B | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Class B | Same as RM17TT00 | Class B | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Class B | Same as RM35UB330 | Same as RM35UB330 | Class B | Same as RM35UB3N30 | Same as RM35UB3N30 | Class B | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | Class B | Class B Group 1 | Class B Group 1 | Class B Group 1 | Class B Group 1 | Class B Group 1 | Not specified | Not specified | Class B |  | Not specified
|  | Radiated RF & electromagnetic field (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Class B, Group 1 | Same as RM17TE00 | Same as RM17TE00 | Class B, Group 1 | Same as RM17TU00 | Same as RM17TU00 | Class B, Group 1 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Class B, Group 1 | Same as RM17TT00 | Class B, Group 1 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Class B, Group 1 | Same as RM35UB330 | Same as RM35UB330 | Class B, Group 1 | Same as RM35UB3N30 | Same as RM35UB3N30 | Class B, Group 1 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Class B, Group 2 | Class B | Class B Group 1 | Class B Group 1 | Class B Group 1 | Class B Group 1 | Class B Group 1 | Not specified | Not specified | - |  | Not specified
|  | Radiated emission from enclosure port | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | EMC 2 | Same as RM17TE00 | Same as RM17TE00 | EMC 2 | Same as RM17TU00 | Same as RM17TU00 | EMC 2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | EMC 2 | Same as RM17TT00 | EMC 2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | EMC 2 | Same as RM35UB330 | Same as RM35UB330 | EMC 2 | Same as RM35UB3N30 | Same as RM35UB3N30 | EMC 2 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | Not specified | Not specified | Not specified |  | -
|  | Conducted RF emission on power line (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B | Class B | Class B | Class B | Class B | Class B | Class B | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Class B | Same as RM17TE00 | Same as RM17TE00 | Class B | Same as RM17TU00 | Same as RM17TU00 | Class B | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Class B | Same as RM17TT00 | Class B | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Class B | Same as RM35UB330 | Same as RM35UB330 | Class B | Same as RM35UB3N30 | Same as RM35UB3N30 | Class B | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | Class B | Class B Group 1 | Class B Group 1 | Class B Group 1 | Class B Group 1 | Class B Group 1 | Not specified | Not specified | Class B |  | Not specified
|  | Conducted RF emission on power line (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Class B, Group 1 | Same as RM17TE00 | Same as RM17TE00 | Class B, Group 1 | Same as RM17TU00 | Same as RM17TU00 | Class B, Group 1 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Class B, Group 1 | Same as RM17TT00 | Class B, Group 1 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Class B, Group 1 | Same as RM35UB330 | Same as RM35UB330 | Class B, Group 1 | Same as RM35UB3N30 | Same as RM35UB3N30 | Class B, Group 1 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Class B, Group 2 | Class B | Class B Group 1 | Class B Group 1 | Class B Group 1 | Class B Group 1 | Class B Group 1 | Not specified | Not specified | - |  | Not specified
|  | Conducted emission | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | EMC 2 | Same as RM17TE00 | Same as RM17TE00 | EMC 2 | Same as RM17TU00 | Same as RM17TU00 | EMC 2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | EMC 2 | Same as RM17TT00 | EMC 2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | EMC 2 | Same as RM35UB330 | Same as RM35UB330 | EMC 2 | Same as RM35UB3N30 | Same as RM35UB3N30 | EMC 2 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | Not specified | Not specified | Not specified |  | -
Electrical Isolation
Degree of pollution |  |  | IEC60664-1 | Common C_Rly Spec | pollution degree | Published | Published |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 3 | Same as RM17TE00 | Same as RM17TE00 | 3 | Same as RM17TU00 | Same as RM17TU00 | 3 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 3 | Same as RM17TT00 | 3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 3 | Same as RM35UB330 | Same as RM35UB330 | 3 | Same as RM35UB3N30 | Same as RM35UB3N30 | 3 | Same as RM17UB310 | Same as RM17UB310
Overvoltage category |  |  | IEC60664-1 | Common C_Rly Spec | overvoltage category | Published | Published |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 3 | Same as RM17TE00 | Same as RM17TE00 | 3 | Same as RM17TU00 | Same as RM17TU00 | 3 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 3 | Same as RM17TT00 | 3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 3 | Same as RM35UB330 | Same as RM35UB330 | 3 | Same as RM35UB3N30 | Same as RM35UB3N30 | 3 | Same as RM17UB310 | Same as RM17UB310
Circuit Group | Terminal | Supply |  |  | circuit group | Published |  |  | L1, L2, L3 | L1, L2, L3 | L1, L2, L3 | L1, L2, L3 | L1, L2, L3 | L1, L2, L3 | L1, L2, L3 | L1, L2, L3 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | L1, L2, L3 | Same as RM17TE00 | Same as RM17TE00 | L1, L2, L3 | Same as RM17TU00 | Same as RM17TU00 | L1, L2, L3 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | L1, L2, L3 | Same as RM17TT00 | L1, L2, L3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | L1, L2, L3 | Same as RM35UB330 | Same as RM35UB330 | L1, L2, L3, N | Same as RM35UB3N30 | Same as RM35UB3N30 | L1, L2, L3 | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 |  |  | circuit group | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 |  |  | circuit group | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 |  |  | circuit group | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 1 |  |  | circuit group | Published |  |  | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 11,12,14 | Same as RM17TE00 | Same as RM17TE00 | 11,12,14 | Same as RM17TU00 | Same as RM17TU00 | 11,12,14 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 11,12,14 | Same as RM17TT00 | 11,12,14 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 11,12,14 | Same as RM35UB330 | Same as RM35UB330 | 11,12,14 | Same as RM35UB3N30 | Same as RM35UB3N30 | 11,12,14 | Same as RM17UB310 | Same as RM17UB310
|  | Output 2 |  |  | circuit group | Published |  |  | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 21,22,24 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 21,22,24 | Same as RM35UB330 | Same as RM35UB330 | 21,22,24 | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
| Rated | Supply | [6 empty] | 208..480 AC | 380..480 AC | 208..240 AC | 380..480 AC | 208..240 AC | 380..480 AC | 208..240 AC | 208..440 AC | Same as RM17TG20 | Same as RM17TG20 | 208..480 AC | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 208..480 AC | Same as RM17TE00 | Same as RM17TE00 | 208..480 AC | Same as RM17TU00 | Same as RM17TU00 | 208..480 AC | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 208..480 AC | Same as RM17TT00 | 208..480 AC | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 220..480 AC | Same as RM35UB330 | Same as RM35UB330 | 120..277 AC | Same as RM35UB3N30 | Same as RM35UB3N30 | 208..480 AC | Same as RM17UB310 | Same as RM17UB310
| Voltage | Input 1 | [6 empty] | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
| Spec | Input 2 | [6 empty] | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 | [6 empty] | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 1 | [6 empty] | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | Same as RM17TG20 | Same as RM17TG20 | 250V | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 250V | Same as RM17TE00 | Same as RM17TE00 | 250V | Same as RM17TU00 | Same as RM17TU00 | 250V | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 250V | Same as RM17TT00 | 250V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 250V | Same as RM35UB330 | Same as RM35UB330 | 250V | Same as RM35UB3N30 | Same as RM35UB3N30 | 250V | Same as RM17UB310 | Same as RM17UB310
|  | Output 2 | [6 empty] | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 250V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 250V | Same as RM35UB330 | Same as RM35UB330 | 250V | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Rated Insulation Voltage |  | Supply | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | 500V | 500V | 500V | 500V | 500V | 500V | 500V | Same as RM17TG20 | Same as RM17TG20 | 500V | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 500V | Same as RM17TE00 | Same as RM17TE00 | 500V | Same as RM17TU00 | Same as RM17TU00 | 500V | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 500V | Same as RM17TT00 | 500V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 500V | Same as RM35UB330 | Same as RM35UB330 | 500V | Same as RM35UB3N30 | Same as RM35UB3N30 | 500V | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | Same as RM17TG20 | Same as RM17TG20 | 250V | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 250V | Same as RM17TE00 | Same as RM17TE00 | 250V | Same as RM17TU00 | Same as RM17TU00 | 250V | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 250V | Same as RM17TT00 | 250V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 250V | Same as RM35UB330 | Same as RM35UB330 | 250V | Same as RM35UB3N30 | Same as RM35UB3N30 | 250V | Same as RM17UB310 | Same as RM17UB310
|  | Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 250V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 250V | Same as RM35UB330 | Same as RM35UB330 | 250V | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 500V | 500V | 500V | 500V | 500V | 500V | 500V | 500V | Same as RM17TG20 | Same as RM17TG20 | 500V | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 500V | Same as RM17TE00 | Same as RM17TE00 | 500V | Same as RM17TU00 | Same as RM17TU00 | 500V | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 500V | Same as RM17TT00 | 500V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 500V | Same as RM35UB330 | Same as RM35UB330 | 500V | Same as RM35UB3N30 | Same as RM35UB3N30 | 500V | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 500V | 500V | 500V | 500V | 500V | 500V | 500V | 500V | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 500V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 500V | Same as RM35UB330 | Same as RM35UB330 | 500V | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 250V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 250V | Same as RM35UB330 | Same as RM35UB330 | 250V | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Rated Impulse Voltage |  | Supply | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | Same as RM17TG20 | Same as RM17TG20 | 4kV, OVC3 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 4kV, OVC3 | Same as RM17TE00 | Same as RM17TE00 | 4kV, OVC3 | Same as RM17TU00 | Same as RM17TU00 | 4kV, OVC3 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 4kV, OVC3 | Same as RM17TT00 | 4kV, OVC3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 4kV, OVC3 | Same as RM35UB330 | Same as RM35UB330 | 4kV, OVC3 | Same as RM35UB3N30 | Same as RM35UB3N30 | 4kV, OVC3 | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | Same as RM17TG20 | Same as RM17TG20 | 4kV, OVC3 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 4kV, OVC3 | Same as RM17TE00 | Same as RM17TE00 | 4kV, OVC3 | Same as RM17TU00 | Same as RM17TU00 | 4kV, OVC3 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 4kV, OVC3 | Same as RM17TT00 | 4kV, OVC3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 4kV, OVC3 | Same as RM35UB330 | Same as RM35UB330 | 4kV, OVC3 | Same as RM35UB3N30 | Same as RM35UB3N30 | 4kV, OVC3 | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 4kV, OVC3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 4kV, OVC3 | Same as RM35UB330 | Same as RM35UB330 | 4kV, OVC3 | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 4kV, OVC3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 4kV, OVC3 | Same as RM35UB330 | Same as RM35UB330 | 4kV, OVC3 | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Dielectric test voltage |  | Supply / Input 1 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Output 1 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | Same as RM17TG20 | Same as RM17TG20 | 2.0kV, 50/60Hz for 1 min | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 2.0kV, 50/60Hz for 1 min | Same as RM17TE00 | Same as RM17TE00 | 2.0kV, 50/60Hz for 1 min | Same as RM17TU00 | Same as RM17TU00 | 2.0kV, 50/60Hz for 1 min | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 2.0kV, 50/60Hz for 1 min | Same as RM17TT00 | 2.0kV, 50/60Hz for 1 min | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 2.0kV, 50/60Hz for 1 min | Same as RM35UB330 | Same as RM35UB330 | 2.0kV, 50/60Hz for 1 min | Same as RM35UB3N30 | Same as RM35UB3N30 | 2.0kV, 50/60Hz for 1 min | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 2.0kV, 50/60Hz for 1 min | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 2.0kV, 50/60Hz for 1 min | Same as RM35UB330 | Same as RM35UB330 | 2.0kV, 50/60Hz for 1 min | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 1 / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 2.0kV, 50/60Hz for 1 min | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 2.0kV, 50/60Hz for 1 min | Same as RM35UB330 | Same as RM35UB330 | 2.0kV, 50/60Hz for 1 min | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Insulation resistance |  | Supply / Input 1 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Output 1 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | Same as RM17TG20 | Same as RM17TG20 | >100 MOhm at 500 V DC | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | >100 MOhm at 500 V DC | Same as RM17TE00 | Same as RM17TE00 | >100 MOhm at 500 V DC | Same as RM17TU00 | Same as RM17TU00 | >100 MOhm at 500 V DC | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | >100 MOhm at 500 V DC | Same as RM17TT00 | >100 MOhm at 500 V DC | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | >100 MOhm at 500 V DC | Same as RM35UB330 | Same as RM35UB330 | >100 MOhm at 500 V DC | Same as RM35UB3N30 | Same as RM35UB3N30 | >100 MOhm at 500 V DC | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | >100 MOhm at 500 V DC | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | >100 MOhm at 500 V DC | Same as RM35UB330 | Same as RM35UB330 | >100 MOhm at 500 V DC | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 1 / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | >100 MOhm at 500 V DC | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | >100 MOhm at 500 V DC | Same as RM35UB330 | Same as RM35UB330 | >100 MOhm at 500 V DC | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Power Supply Characteristics
Rated supply voltage, Us |  |  |  |  | [Us] rated supply voltage | Published | Published | V | ~ 3 x 208…3 x 480 | ~ 3 x 380… 3 x 480 | ~ 3 x 200…3 x 240 | ~ 3 x 380… 3 x 480 | ~ 3 x 200…3 x 240 | ~ 3 x 380… 3 x 480 | ~ 3 x 200…3 x 240 | ~ 3 x 208…3 x 440 | Same as RM17TG20 | Same as RM17TG20 | ~ 3 x 208…3 x 480 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | ~ 3 x 230…3 x 440 | Same as 84873034 | ~ 3 x 208…3 x 480 | Same as RM17TE00 | Same as RM17TE00 | ~ 3 x 208…3 x 480 | Same as RM17TU00 | Same as RM17TU00 | ~ 3 x 208…3 x 480 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | ~ 3 x 208…3 x 480 | Same as RM17TT00 | ~ 3 x 220…3 x 480 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | ~ 3 x 220…3 x 480 | Same as RM35UB330 | Same as RM35UB330 | ~ 3 x 120…3 x 277 | Same as RM35UB3N30 | Same as RM35UB3N30 | ~ 3 x 208…3 x 480 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | ~ 3 x 208…3 x 480 | ~ 3 x 230…3 x 440 | RM4TR31: ~ 3 x 200…3 x 240 RM4TR32: ~ 3 x 300…3 x 500 RM4TR33: ~ 3 x 220 RM4TR33: ~ 3 x 400 | ~ 3 x 200…3 x 500 | RM4TU01: ~ 3 x 200…3 x 240 RM4TU02: ~ 3 x 380…3 x 500 | RM4TA01/31: ~ 3 x 200…3 x 240 RM4TA02/32: ~ 3 x 380…3 x 500 | RM4UB34: ~80…220 RM4UB35: ~160…300 | ~ 3 x 230…3 x 440 | ~ 3 x 230…3 x 440 | ~ 3 x 300…3 x 500 |  | ~ 3 x 208…3 x 480
Supply voltage operating range |  |  |  |  | supply voltage limits | Published | Published | V | ~ 3 x 183…3 x 528 | ~ 3 x 304…3 x 576 | ~ 3 x 160…3 x 288 | ~ 3 x 304…3 x 576 | ~ 3 x 160…3 x 288 | ~ 3 x 304…3 x 576 | ~ 3 x 160…3 x 288 | ~ 3 x 183…3 x 484 | Same as RM17TG20 | Same as RM17TG20 | ~ 3 x 183…3 x 528 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | ~ 3 x 200…3 x 460 | Same as 84873034 | ~ 3 x 183…3 x 528 | Same as RM17TE00 | Same as RM17TE00 | ~ 3 x 183…3 x 528 | Same as RM17TU00 | Same as RM17TU00 | ~ 3 x 183…3 x 528 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | ~ 3 x 183…3 x 528 | Same as RM17TT00 | ~ 3 x 194…3 x 528 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | ~ 3 x 194…3 x 528 | Same as RM35UB330 | Same as RM35UB330 | ~ 3 x 114…3 x 329 | Same as RM35UB3N30 | Same as RM35UB3N30 | ~ 3 x 183…3 x 528 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | ~ 3 x 183…3 x 528 | ~ 3 x 207…3 x 484 | RM4TR31/33: ~ 3 x 160…3 x 300 RM4TR32/34: ~ 3 x 290…3 x 580 | ~ 3 x 140…3 x 580 | RM4TU01: ~ 3 x 160…3 x 300 RM4TU01: ~ 3 x 290…3 x 580 | RM4TA01/31: ~ 3 x 160…3 x 300 RM4TA02/32: ~ 3 x 290…3 x 580 | RM4UB34: ~60…300 RM4UB35: ~160…300 | Not specified | Not specified | ~ 3 x 255…3 x 550 |  | ~ 3 x 177…3 x 550
Polarity on d.c. supply |  |  |  |  | polarity |  | Published |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | - | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Rated frequency |  |  |  |  | supply frequency | Published | Published | Hz | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 50 / 60 | Same as RM17TE00 | Same as RM17TE00 | 50 / 60 | Same as RM17TU00 | Same as RM17TU00 | 50 / 60 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 50 / 60 | Same as RM17TT00 | 50 / 60 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 50 / 60 | Same as RM35UB330 | Same as RM35UB330 | 50 / 60 | Same as RM35UB3N30 | Same as RM35UB3N30 | 50 / 60 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 |  | 50 / 60
Frequency operating range |  |  |  |  | supply frequency | Published | Published | Hz | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 45…66 | Same as RM17TE00 | Same as RM17TE00 | 45…66 | Same as RM17TU00 | Same as RM17TU00 | 45…66 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 45…66 | Same as RM17TT00 | 45…66 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 45…66 | Same as RM35UB330 | Same as RM35UB330 | 45…66 | Same as RM35UB3N30 | Same as RM35UB3N30 | 45…66 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 45…66 | 49…61 | 47.5…63 | 47.5…63 | 47.5…63 | 47.5…63 | 47.5…63 | 49…61 | 49…61 | 45…66 |  | 45…66
Maximum power consumption |  |  |  |  | power consumption | Published | Published |  | 18VA @ 480VAC, 60Hz 12VA @ 400VAC, 50Hz | 18VA @ 480VAC, 60Hz 12VA @ 400VAC, 50Hz | 10VA @ 240VAC, 60Hz | 15VA | 10VA | 15VA | 10VA | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | 28VA @ 480VAC, 60Hz 18VA @ 415VAC, 50Hz | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz | Same as RM17TE00 | Same as RM17TE00 | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz | Same as RM17TU00 | Same as RM17TU00 | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz | Same as RM17TT00 | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz | Same as RM35UB330 | Same as RM35UB330 | 3.9VA @ 480VAC, 60Hz | Same as RM35UB3N30 | Same as RM35UB3N30 | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 25 | 25 | Not specified | Not specified | Not specified | Not specified | Not specified | 25 | 25 | 25mA / 18VA (400VAC) |  | 13VA (400VAC, 50Hz) by L2, L3
Immunity to micro-breakage |  |  |  |  | immunity to microbreaks | Published | Published | ms | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 0 | Same as RM17TE00 | Same as RM17TE00 | 0 | Same as RM17TU00 | Same as RM17TU00 | 0 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 0 | Same as RM17TT00 | 0 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 0 | Same as RM35UB330 | Same as RM35UB330 | 5 | Same as RM35UB3N30 | Same as RM35UB3N30 | 0 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 10 |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | - |  | -
Supply terminal |  |  |  |  | supply terminal |  |  |  | L1-L3 | L1-L3 | L1-L3 | L1-L3 | L1-L3 | L1-L3 | L1-L3 | L1-L3 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | L1-L3 | Same as RM17TE00 | Same as RM17TE00 | L1-L3 | Same as RM17TU00 | Same as RM17TU00 | L1-L3 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | L1-L3 | Same as RM17TT00 | L1-L3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | L1-N | Same as RM35UB330 | Same as RM35UB330 | L1-L3 | Same as RM35UB3N30 | Same as RM35UB3N30 | L1-L3 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | L1-L3 | L1-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L3 | Not specified | Not specified | L1-L2-L3 |  | L1-L2-L3
On Load Factor |  |  |  | Common C_Rly Spec | on-load factor |  |  | % | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1 | Same as RM17TE00 | Same as RM17TE00 | 1 | Same as RM17TU00 | Same as RM17TU00 | 1 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1 | Same as RM17TT00 | 1 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1 | Same as RM35UB330 | Same as RM35UB330 | 1 | Same as RM35UB3N30 | Same as RM35UB3N30 | 1 | Same as RM17UB310 | Same as RM17UB310 | [5 empty] | Not specified
Release of input voltage |  |  |  |  | release of input voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 | [5 empty] | Not specified
Input Circuit Characteristics
Monitoring functions |  | Phase lost |  |  | monitoring functions | Published |  |  | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TE00 | Same as RM17TE00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TU00 | Same as RM17TU00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TT00 | governed by response time only, status reflects to both R1 & R2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB330 | Same as RM35UB330 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB3N30 | Same as RM35UB3N30 | governed by response time only, status reflects to both R1 & R2 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | · | · | · | · | · | · | - | · | · | · |  | ·
|  | Phase sequence |  |  | monitoring functions | Published |  |  | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TE00 | Same as RM17TE00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TU00 | Same as RM17TU00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TT00 | governed by response time only, status reflects to both R1 & R2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB330 | Same as RM35UB330 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB3N30 | Same as RM35UB3N30 | governed by response time only, status reflects to both R1 & R2 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | · | · | · | · | · | · | - | · | · | can be switched off |  | ·
|  | Over / undervoltage (symmetry windows mode) |  |  | monitoring functions | Published |  |  | - | governed by time delay, status reflects to both R1 & R2 | governed by time delay, status reflects to both R1 & R2 | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | governed by time delay, status reflects to both R1 & R2 | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Over voltage |  |  | monitoring functions | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | governed by time delay, status reflects to both R1 & R2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | governed by time delay Tt1, status reflects to R1 | Same as RM35UB330 | Same as RM35UB330 | governed by time delay Tt1, status reflects to R1 | Same as RM35UB3N30 | Same as RM35UB3N30 | governed by time delay, status reflects to both R1 & R2 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | · | - | - | - | - | - | - | · |  | -
|  | Undervoltage |  |  | monitoring functions | Published |  |  | - | - | - | governed by time delay, status reflects to both R1 & R2 | governed by time delay, status reflects to both R1 & R2 | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | governed by time delay, status reflects to both R1 & R2 | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | governed by time delay, status reflects to both R1 & R2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | governed by time delay Tt2, status reflects to R2 | Same as RM35UB330 | Same as RM35UB330 | governed by time delay Tt2, status reflects to R2 | Same as RM35UB3N30 | Same as RM35UB3N30 | governed by time delay, status reflects to both R1 & R2 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | · | - | · | - | - | - | - | · |  | -
|  | Phase asymmetry |  |  | monitoring functions | Published |  |  | - | - | - | - | - | governed by time delay, status reflects to both R1 & R2 | governed by time delay, status reflects to both R1 & R2 | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | governed by time delay, status reflects to both R1 & R2 | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | governed by time delay, status reflects to both R1 & R2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | governed by time delay, status reflects to both R1 & R2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | - | - | - | · | - | - | - | - |  | -
|  | Disconnection of neutral |  |  | monitoring functions | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Voltage Regeneration |  |  | monitoring functions | Published |  |  | - | - | - | - | - | governed by time delay, status reflects to both R1 & R2 | governed by time delay, status reflects to both R1 & R2 | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Extreme undervoltage |  |  | monitoring functions | Published |  |  | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TE00 | Same as RM17TE00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TU00 | Same as RM17TU00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TT00 | governed by response time only, status reflects to both R1 & R2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB330 | Same as RM35UB330 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB3N30 | Same as RM35UB3N30 | governed by response time only, status reflects to both R1 & R2 | Same as RM17UB310 | Same as RM17UB310
|  | Extreme overvoltage |  |  | monitoring functions |  |  |  | - | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TE00 | Same as RM17TE00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TU00 | Same as RM17TU00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TT00 | governed by response time only, status reflects to both R1 & R2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB330 | Same as RM35UB330 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB3N30 | Same as RM35UB3N30 | governed by response time only, status reflects to both R1 & R2 | Same as RM17UB310 | Same as RM17UB310
|  | Extreme asymmetry |  |  | monitoring functions |  |  |  | - | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TT00 | governed by response time only, status reflects to both R1 & R2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB330 | Same as RM35UB330 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB3N30 | Same as RM35UB3N30 | governed by response time only, status reflects to both R1 & R2 | Same as RM17UB310 | Same as RM17UB310
Monitoring function characteristics |  | Measurement mode | [6 empty] | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Resistive Voltage Step Down | Same as RM17TE00 | Same as RM17TE00 | Resistive Voltage Step Down | Same as RM17TU00 | Same as RM17TU00 | Resistive Voltage Step Down | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Resistive Voltage Step Down | Same as RM17TT00 | Resistive Voltage Step Down | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Resistive Voltage Step Down | Same as RM35UB330 | Same as RM35UB330 | Resistive Voltage Step Down | Same as RM35UB3N30 | Same as RM35UB3N30 | Resistive Voltage Step Down | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down |  |  | Resistive Voltage Step Down |  | Resistive Voltage Step Down
|  | Internal input resistance |  |  | internal input resistance |  |  | W | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Not specified | - | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified |  | Not specified
|  | Input terminal |  |  | input terminal |  |  |  | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | L1-L2-L3 | Same as RM17TE00 | Same as RM17TE00 | L1-L2-L3 | Same as RM17TU00 | Same as RM17TU00 | L1-L2-L3 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | L1-L2-L3 | Same as RM17TT00 | L1-L2-L3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | L1-L2-L3 | Same as RM35UB330 | Same as RM35UB330 | L1-L2-L3-N | Same as RM35UB3N30 | Same as RM35UB3N30 | L1-L2-L3 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 |  | L1-L2-L3
|  | Input nominal voltage selection |  |  | Input nominal voltage selection |  |  | V | - | 380, 400, 415, 440, 480 | 200, 208, 220, 240 | 380, 400, 415, 440, 480 | 200, 208, 220, 240 | 380, 400, 415, 440, 480 | 200, 208, 220, 240 | - | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG21 | Same as 84873034 | 208, 220, 380, 400, 415, 440, 480 | Same as RM17TE00 | Same as RM17TE00 | 208, 220, 380, 400, 415, 440, 480 | Same as RM17TU00 | - | 208, 220, 380, 400, 415, 440, 480 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 208, 220, 380, 400, 415, 440, 480 | Same as RM17TT00 | 220, 380, 400, 415, 440, 480 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 220, 380, 400, 415, 440, 480 | Same as RM35UB330 | Same as RM35UB330 | 120, 127, 220, 230, 240, 260, 277 | Same as RM35UB3N30 | Same as RM35UB3N30 | 208, 220, 380, 400, 415, 440, 480 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Fixed @ ~ 3 x 183…3 x 528 | Fixed @ ~ 3 x 230…3 x 440 | RM4TR31/33: ~ 3 x 160…3 x 300 RM4TR32/34: ~ 3 x 290…3 x 580 | Fixed @ ~ 3 x 140…3 x 580 | RM4TU01: ~ 3 x 160…3 x 300 RM4TU01: ~ 3 x 290…3 x 580 | RM4TU0131: ~ 3 x 160…3 x 300 RM4TU02/32: ~ 3 x 290…3 x 580 | RM4UB34: ~ 160…300 RM4UB35: ~ 160…300 | Fixed @ ~ 3 x 230…3 x 440 | Fixed @ ~ 3 x 230…3 x 440 | Fixed @ ~ 3 x 255…3 x 550 |  | Fixed @ ~ 3 x 177…3 x 550
|  | permissible input overload |  |  | permissible input overload |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG22 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified |  | Not specified
|  | Rated frequency |  |  | input frequency | Published | Published | Hz | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 50 / 60 | Same as RM17TE00 | Same as RM17TE00 | 50 / 60 | Same as RM17TU00 | Same as RM17TU00 | 50 / 60 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 50 / 60 | Same as RM17TT00 | 50 / 60 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 50 / 60 | Same as RM35UB330 | Same as RM35UB330 | 50 / 60 | Same as RM35UB3N30 | Same as RM35UB3N30 | 50 / 60 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 |  | 50 / 60
|  | Frequency operating range |  |  | input frequency | Published | Published | Hz | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 45…66 | Same as RM17TE00 | Same as RM17TE00 | 45…66 | Same as RM17TU00 | Same as RM17TU00 | 45…66 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 45…66 | Same as RM17TT00 | 45…66 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 45…66 | Same as RM35UB330 | Same as RM35UB330 | 45…66 | Same as RM35UB3N30 | Same as RM35UB3N30 | 45…66 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 45…66 | 49…61 | 47.5…63 | 47.5…63 | 47.5…63 | 47.5…63 | 47.5…63 | 49…61 | 49…61 | 45…66 |  | 45…66
|  | Setting accuracy |  |  | setting accuracy of the switching threshold | Published | Published |  | - | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | Same as RM17TE00 | Same as RM17TE00 | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | Same as RM17TU00 | Same as RM17TU00 | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | Same as RM35UB330 | Same as RM35UB330 | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | Same as RM35UB3N30 | Same as RM35UB3N30 | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | +/- 3% of set value | +/- 3% of set value | +/- 3% of set value | +/- 3% of set value | +/- 3% of set value | - | - | Not specified |  | -
|  | Repeat accuracy (constant parameters) |  |  | repeat accuracy of the switching threshold | Published | Published | % | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | +/- 0.5% | Same as RM17TE00 | Same as RM17TE00 | +/- 0.5% | Same as RM17TU00 | Same as RM17TU00 | +/- 0.5% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | +/- 0.5% | Same as RM17TT00 | +/- 0.5% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | +/- 0.5% | Same as RM35UB330 | Same as RM35UB330 | +/- 0.5% | Same as RM35UB3N30 | Same as RM35UB3N30 | +/- 0.5% | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | +/- 0.5% | +/- 0.5% | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | < +/- 0.2% |  | +/- 0.5% on full scale
|  | Measurement method |  |  | measurement method | Published | Published |  | Non True RMS | True RMS | True RMS | True RMS | True RMS | True RMS | True RMS | Non True RMS | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | True RMS | Same as RM17TE00 | Same as RM17TE00 | True RMS | Same as RM17TU00 | Same as RM17TU00 | True RMS | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | True RMS | Same as RM17TT00 | True RMS | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | True RMS | Same as RM35UB330 | Same as RM35UB330 | True RMS | Same as RM35UB3N30 | Same as RM35UB3N30 | True RMS | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Not specified | Not specified | Voltage Peak Detection | Voltage Peak Detection | Voltage Peak Detection | Voltage Peak Detection | Voltage Peak Detection | Not specified | Not specified | True RMS |  | Not specified
|  | Measurement error with supply voltage variation |  |  | switching threshold drift | Published | Published | %/V | - | < 1% of selected Un | < 1% of selected Un | < 1% of selected Un | < 1% of selected Un | < 1% of selected Un | < 1% of selected Un | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | < 1% of selected Un | Same as RM17TE00 | Same as RM17TE00 | < 1% of selected Un | Same as RM17TU00 | Same as RM17TU00 | < 1% of selected Un | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | < 1% of selected Un | Same as RM17TT00 | < 1% of selected Un | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | < 1% of selected Un | Same as RM35UB330 | Same as RM35UB330 | < 1% of selected Un | Same as RM35UB3N30 | Same as RM35UB3N30 | < 1% of selected Un | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | < 1% over whole range | < 1% over whole range | < 0.5% | < 0.5% | < 0.5% | < 0.5% | < 0.5% | Not specified | Not specified | < 0.5% |  | -
|  | Measurement error with temperature variation |  |  | switching threshold drift | Published | Published | %/oC | - | < 0.05% / oC | < 0.05% / oC | < 0.05% / oC | < 0.05% / oC | < 0.05% / oC | < 0.05% / oC | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | < 0.05% / oC | Same as RM17TE00 | Same as RM17TE00 | < 0.05% / oC | Same as RM17TU00 | Same as RM17TU00 | < 0.05% / oC | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | < 0.05% / oC | Same as RM17TT00 | < 0.05% / oC | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | < 0.05% / oC | Same as RM35UB330 | Same as RM35UB330 | < 0.05% / oC | Same as RM35UB3N30 | Same as RM35UB3N30 | < 0.05% / oC | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 0.05% / oC | 0.05% / oC | =< 0.06% / oC | =< 0.06% / oC | =< 0.06% / oC | =< 0.06% / oC | =< 0.06% / oC | Not specified | Not specified | =< 0.06% / oC |  | 0.1% / oC
|  | Maximum measuring cycles |  |  | maximum measuring cycle | Published | Published | ms | - | 170ms / measurement as true rms value | 150ms / measurement as true rms value | 150ms / measurement as true rms value | 150ms / measurement as true rms value | 150ms / measurement as true rms value | 150ms / measurement as true rms value | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 150ms / measurement as true rms value | Same as RM17TE00 | Same as RM17TE00 | 150ms / measurement as true rms value | Same as RM17TU00 | Same as RM17TU00 | 150ms / measurement as true rms value | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 150ms / measurement as true rms value | Same as RM17TT00 | 140ms / measurement as true rms value | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 150ms / measurement as true rms value | Same as RM35UB330 | Same as RM35UB330 | 150ms / measurement as true rms value | Same as RM35UB3N30 | Same as RM35UB3N30 | 150ms / measurement as true rms value | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Not specified | Not specified | 80 | 80 | 80 | 80 | 80 | Not specified | Not specified | 100 |  | -
Measurement range |  | Phase lost |  |  | measurement range | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Fixed value | - | Fixed value | Fixed value | Fixed value | Fixed value | Fixed value | Not specified | Not specified | Not specified |  | Not specified
|  | Phase sequence |  |  | measurement range | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Fixed value | - | Fixed value | Fixed value | Fixed value | Fixed value | Fixed value | Not specified | Not specified | Not specified |  | Not specified
|  | Over / undervoltage (symmetry windows mode) |  |  | measurement range | Published | Published |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | -2…-20 % in the ranges 3 x ~ 380…480 -2…-12 % in the range 3 x ~ 208 -2…-17 % in the range 3 x ~ 220 +2…+20 % in the ranges 3 x ~ 208…440 +2…+10 % in the range 3 x ~ 480 | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Over voltage |  |  | measurement range | Published | Published |  | - | +2…+20 % in the ranges 3 x 380…480 | +2…+20 % in the ranges 3 x ~200…240 | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | +2…+20 % in the ranges 3 x ~ 220…440 +2…+10 % in the range 3 x ~ 480 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | +2…+20 % in the ranges 3 x ~ 220…440 +2…+10 % in the range 3 x ~ 480 | Same as RM35UB330 | Same as RM35UB330 | +2…+20 % in the ranges 3 x ~ 120…277 | Same as RM35UB3N30 | Same as RM35UB3N30 | +2…+20 % in the ranges 3 x ~ 208…440 +2…+10 % in the range 3 x ~ 480 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | RM4TR31: ~ 3 x 160…3 x 300 RM4TR32: ~ 3 x 420…3 x 480 RM4TR33: ~ 3 x 198 RM4TR34: ~ 3 x 360 | - | - | - | RM4UB34: ~ 160…220 RM4UB34: ~ 220…300 | - | - | ~ 3 x 420…3 x 500 |  | -
|  | Undervoltage |  |  | measurement range | Published | Published |  | - | -2…-20 % in the ranges 3 x 380…480 | -2…-20 % in the ranges 3 x ~ 200…240 | -2…-20 % in the ranges 3 x 380…480 | -2…-20 % in the ranges 3 x ~ 200…240 | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | -2…-20 % in the ranges 3 x ~ 380…480 -2…-12 % in the range 3 x ~ 208 -2…-17 % in the range 3 x ~ 220 | Same as RM17TU00 | Fixed 400 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | -12…-2 % in the range 3 x ~ 220 -20…-2 % in the ranges 3 x ~ 380…480 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | -12…-2 % in the range 3 x ~ 220 -20…-2 % in the ranges 3 x ~ 380…480 | Same as RM35UB330 | Same as RM35UB330 | -2…-20 % in the ranges 3 x ~ 120…277 | Same as RM35UB3N30 | Same as RM35UB3N30 | -2…-20 % in the ranges 3 x ~ 380…480 -2…-12 % in the range 3 x ~ 208 -2…-17 % in the range 3 x ~ 220 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | RM4TR31: ~ 3 x 220…3 x 300 RM4TR32: ~ 3 x 300…3 x 430 RM4TR33: ~ 3 x 242 RM4TR34: ~ 3 x 440 | - | RM4TU01: ~ 3 x 160…3 x 220 RM4TU02: ~ 3 x 300…3 x 430 | - | RM4UB34: ~ 80…120 RM4UB34: ~ 160…220 | - | - | ~ 3 x 300…3 x 380 |  | -
|  | Phase asymmetry |  |  | measurement range | Published | Published |  | - | - | - | - | - | +5…+15 % in the ranges 3 x ~ 380…480 | +5…+15 % in the ranges 3 x ~ 200…240 | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | +5…+15 % in the ranges 3 x ~ 208…480 | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | +5…+15 % in the ranges 3 x ~ 208…480 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | +5…+15 % in the ranges 3 x ~ 220…480 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | - | - | - | Not specified | - | - | - | - |  | -
|  | Disconnection of neutral |  |  | measurement range | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Voltage Regeneration |  |  | measurement range | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Extreme undervoltage |  |  | measurement range | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Overvoltage |  |  | measurement range |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Asymmetry |  |  | measurement range |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Tripping threshold |  | Phase cut |  |  | tripping threshold | Published | Published |  | 1 or more phase cut | 1 or more phase cut | 1 or more phase cut | 1 or more phase cut | 1 or more phase cut | 1 or more phase cut | 1 or more phase cut | 1 or more phase cut | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1 or more phase cut | Same as RM17TE00 | Same as RM17TE00 | 1 or more phase cut | Same as RM17TU00 | Same as RM17TU00 | 1 or more phase cut | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1 or more phase cut | Same as RM17TT00 | 1 or more phase cut | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1 or more phase cut | Same as RM35UB330 | Same as RM35UB330 | 1 or more phase cut | Same as RM35UB3N30 | Same as RM35UB3N30 | 1 or more phase cut | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | (L2-L1) or (L3-L1) or (L2-L3) < 100 | (L2-L1) or (L3-L1) or (L2-L3) < 100 | RM4TR32: (L2-L1) or (L3-L1) or (L2-L3) < 290 or Differences of (L2-L1) / (L3-L1) /(L2-L3) > 105V Other: Unknown | Unknown | Unknown | Unknown | - | Not specified | Not specified | - |  | 1 phase below 85% of other phase
|  | Phase sequence |  |  | tripping threshold | Published | Published |  | Total swap of phase Internal design spec: L31 lag L21 =< 10o or L31 lag L21 >= 150o | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Total swap of phase Internal design spec: L31 lag L21 =< 10o or L31 lag L21 >= 150o | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Same as RM17TE00 | Same as RM17TE00 | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Same as RM17TU00 | Same as RM17TU00 | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Same as RM17TT00 | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Same as RM35UB330 | Same as RM35UB330 | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Same as RM35UB3N30 | Same as RM35UB3N30 | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | (L2-L1) leads (L3-L1) < 10o or (L2-L1) leads (L3-L1) > 150o | (L2-L1) leads (L3-L1) < 10o or (L2-L1) leads (L3-L1) > 150o | Total swap of phase | Total swap of phase | Total swap of phase | Total swap of phase | - | Not specified | Not specified | - |  | -
|  | Over / undervoltage (symmetry windows mode) |  |  | tripping threshold | Published | Published |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Adjustable 2%...20% of selected Un | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Over voltage |  |  | tripping threshold | Published | Published |  | - | Adjustable 2%...20% of selected Un | Adjustable 2%...20% of selected Un | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Adjustable 2%...20% of selected Un | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Adjustable 2%...20% of selected Un | Same as RM35UB330 | Same as RM35UB330 | Adjustable 2%...20% of selected Un | Same as RM35UB3N30 | Same as RM35UB3N30 | Adjustable 2%...20% of selected Un | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | Adjustable within measurement range | - | - | - | Adjustable within measurement range | - | - | Adjustable within measurement range |  | -
|  | Undervoltage |  |  | tripping threshold | Published | Published |  | - | Adjustable 2%...20% of selected Un | Adjustable 2%...20% of selected Un | Adjustable 2%...20% of selected Un | Adjustable 2%...20% of selected Un | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | Adjustable 2%...20% of selected Un | Same as RM17TU00 | Fixed -10% of Un | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Adjustable 2%...20% of selected Un | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Adjustable 2%...20% of selected Un | Same as RM35UB330 | Same as RM35UB330 | Adjustable 2%...20% of selected Un | Same as RM35UB3N30 | Same as RM35UB3N30 | Adjustable 2%...20% of selected Un | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | Adjustable within measurement range | - | Adjustable within measurement range | - | Adjustable within measurement range | - | - | Adjustable within measurement range |  | -
|  | Phase asymmetry |  |  | tripping threshold | Published | Published |  | - | - | - | - | - | Adjustable 5%...15% of selected Un | Adjustable 5%...15% of selected Un | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Adjustable 5%...15% of selected Un | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | Adjustable 5%...15% of selected Un | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Adjustable 5%...15% of selected Un | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | - | - | - | Adjustable 5%...15% of selected Un | - | - | - | - |  | -
|  | Disconnection of neutral |  |  | tripping threshold | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | Total cut of N | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Voltage Regeneration |  |  | tripping threshold | Published |  |  | - | - | - | - | - | 1 or more phase < 70% of selected Un Internal design spec: 30% +/- 5% | 1 or more phase < 70% of selected Un Internal design spec: 30% +/- 5% | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1 or more phase < 70% of selected Un Internal design spec: 30% +/- 5% | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Extreme undervoltage (Phase loss) |  |  | tripping threshold | Published |  | V | 2 or more phase < 100V Internal design spec: 2 or more phase <150V +/- 10% | 1 or more phase < 250V Internal design spec: 1 or more phase <290V +/- 5% | 1 or more phase < 150V Internal design spec: 1 or more phase <160V +/- 5% | 1 or more phase < 250V Internal design spec: 1 or more phase <290V +/- 5% | 1 or more phase < 150V Internal design spec: 1 or more phase <160V +/- 5% | 1 or more phase < 250V Internal design spec: 1 or more phase <290V +/- 5% | 1 or more phase < 150V Internal design spec: 1 or more phase <160V +/- 5% | 2 or more phase < 100V Internal design spec: 2 or more phase <150V +/- 10% | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% | Same as RM17TE00 | Same as RM17TE00 | 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% | Same as RM17TU00 | Same as RM17TU00 | 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% | Same as RM17TT00 | 1 or more phase < 150V Internal design spec: 1 or more phase <188V +/- 5% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1 or more phase < 150V Internal design spec: 1 or more phase <188V +/- 5% | Same as RM35UB330 | Same as RM35UB330 | 1 or more phase < 80V Internal design spec: 1 or more phase <86V +/- 5% | Same as RM35UB3N30 | Same as RM35UB3N30 | 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Overvoltage |  |  | tripping threshold |  |  | V | - | Internal design spec: 593V +/- 5% | Internal design spec: 297V +/- 5% | Internal design spec: 593V +/- 5% | Internal design spec: 297V +/- 5% | Internal design spec: 593V +/- 5% | Internal design spec: 297V +/- 5% | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Internal design spec: 543V +/- 5% | Same as RM17TE00 | Same as RM17TE00 | Internal design spec: 543V +/- 5% | Same as RM17TU00 | Same as RM17TU00 | Internal design spec: 543V +/- 5% | Same as RM17TA00 | Same as RM17TA00 | When > 543V +/- 5% last longer than 2s +/- 10% , output de-energized When > 543V +/- 5% last shorter than 2s +/- 10% , output energized | Internal design spec: 543V +/- 5% | Same as RM17TT00 | Internal design spec: 543V +/- 5% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Internal design spec: 543V +/- 5% | Same as RM35UB330 | Same as RM35UB330 | Internal design spec: 368V +/- 5% | Same as RM35UB3N30 | Same as RM35UB3N30 | Internal design spec: 543V +/- 5% | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Asymmetry |  |  | tripping threshold |  |  | % | - | Internal design spec: 48% +/- 6% | Internal design spec: 48% +/- 6% | Internal design spec: 48% +/- 6% | Internal design spec: 48% +/- 6% | Internal design spec: 48% +/- 6% | Internal design spec: 48% +/- 6% | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Internal design spec: 48% +/- 6% | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | Internal design spec: 48% +/- 6% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Internal design spec: 48% +/- 6% | Same as RM17TT00 | Internal design spec: 48% +/- 6% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Internal design spec: 48% +/- 6% | Same as RM35UB330 | Same as RM35UB330 | Internal design spec: 48% +/- 6% | Same as RM35UB3N30 | Same as RM35UB3N30 | Internal design spec: 48% +/- 6% | Same as RM17UB310 | Same as RM17UB310
Hysteresis |  | Phase cut |  |  | hysteresis | Published | Published |  | All phase cut recover | All phase cut recover | All phase cut recover | All phase cut recover | All phase cut recover | All phase cut recover | All phase cut recover | All phase cut recover | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | All phase cut recover | Same as RM17TE00 | Same as RM17TE00 | All phase cut recover | Same as RM17TU00 | Same as RM17TU00 | All phase cut recover | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | All phase cut recover | Same as RM17TT00 | All phase cut recover | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | All phase cut recover | Same as RM35UB330 | Same as RM35UB330 | All phase cut recover | Same as RM35UB3N30 | Same as RM35UB3N30 | All phase cut recover | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | Not specified | - | - | - | - | - | Not specified | Not specified | - |  | -
|  | Phase sequence |  |  | hysteresis | Published | Published |  | Total phase swap recover Internal design spec: L31 lag L21 >= 15o or L31 lag L21 <= 135o | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Total phase swap recover Internal design spec: L31 lag L21 >= 15o or L31 lag L21 <= 135o | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Same as RM17TE00 | Same as RM17TE00 | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Same as RM17TU00 | Same as RM17TU00 | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Same as RM17TT00 | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Same as RM35UB330 | Same as RM35UB330 | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Same as RM35UB3N30 | Same as RM35UB3N30 | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | (L2-L1) leads (L3-L1) >=15o or (L2-L1) leads (L3-L1) =< 135o | (L2-L1) leads (L3-L1) >=15o or (L2-L1) leads (L3-L1) =< 135o | - | - | - | - | - | Not specified | Not specified | - |  | -
|  | Over / undervoltage (symmetry windows mode) |  |  | hysteresis | Published | Published |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Over voltage |  |  | hysteresis | Published | Published |  | - | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM35TF30 | Same as RM35TF30 | Fixed 5.35% of selected Un Internal design spec: 5.35% +/- 1.5% | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM35UB330 | Same as RM35UB330 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM35UB3N30 | Same as RM35UB3N30 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | Fixed 5% of de-energization threshold | Fixed 5% of de-energization threshold | Fixed 5% of de-energization threshold | Fixed 5% of de-energization threshold | Fixed 5% of de-energization threshold | - | - | Fixed 5% |  | -
|  | Undervoltage |  |  | hysteresis | Published | Published |  | - | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM17TU00 | Fixed 5% of selected Un Internal design spec: 5% +/- 1.5% | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM35TF30 | Same as RM35TF30 | Fixed 5.35% of selected Un Internal design spec: 5.35% +/- 1.5% | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM35UB330 | Same as RM35UB330 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM35UB3N30 | Same as RM35UB3N30 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | Fixed 5% of de-energization threshold | Fixed 5% of de-energization threshold | Fixed 5% of de-energization threshold | Fixed 5% of de-energization threshold | Fixed 5% of de-energization threshold | - | - | Fixed 5% |  | -
|  | Phase asymmetry |  |  | hysteresis | Published | Published |  | - | - | - | - | - | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Disconnection of neutral |  |  | hysteresis | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Voltage Regeneration |  |  | hysteresis | Published |  |  | - | - | - | - | - | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 0.3 | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Extreme undervoltage (Phase loss) |  |  | hysteresis | Published |  |  | All phases > 183V Internal design spec: All phases >153V +/- 10% | All phases > 315V Internal design spec: All phases >296V +/- 5% | All phases > 175V Internal design spec: All phases >163V +/- 5% | All phases > 315V Internal design spec: All phases >296V +/- 5% | All phases > 175V Internal design spec: All phases >163V +/- 5% | All phases > 315V Internal design spec: All phases >296V +/- 5% | All phases > 175V Internal design spec: All phases >163V +/- 5% | All phases > 183V Internal design spec: All phases >153V +/- 10% | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | All phases > 195V Internal design spec: All phases >180V +/- 5% | Same as RM17TE00 | Same as RM17TE00 | All phases > 195V Internal design spec: All phases >180V +/- 5% | Same as RM17TU00 | Same as RM17TU00 | All phases >195V Internal design spec: All phases >180V +/- 5% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | All phases > 195V Internal design spec: All phases >180V +/- 5% | Same as RM17TT00 | All phases > 205V Internal design spec: All phases >190V +/- 5% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | All phases > 205V Internal design spec: All phases >190V +/- 5% | Same as RM35UB330 | Same as RM35UB330 | All phases > 100V Internal design spec: All phases >88V +/- 5% | Same as RM35UB3N30 | Same as RM35UB3N30 | All phases > 195V Internal design spec: All phases >180V +/- 5% | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Overvoltage |  |  | hysteresis |  |  |  | - | Internal design spec: All phases <583V +/- 5% | Internal design spec: All phases <287V +/- 5% | Internal design spec: All phases <583V +/- 5% | Internal design spec: All phases <287V +/- 5% | Internal design spec: All phases <583V +/- 5% | Internal design spec: All phases <287V +/- 5% | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Internal design spec: All phases <533V +/- 5% | Same as RM17TE00 | Same as RM17TE00 | Internal design spec: All phases <533V +/- 5% | Same as RM17TU00 | Same as RM17TU00 | Internal design spec: All phases <533V +/- 5% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Internal design spec: All phases <533V +/- 5% | Same as RM17TT00 | Internal design spec: All phases <533V +/- 5% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Internal design spec: All phases > <533V +/- 5% | Same as RM35UB330 | Same as RM35UB330 | Internal design spec: All phases <358V +/- 5% | Same as RM35UB3N30 | Same as RM35UB3N30 | Internal design spec: All phases <533V +/- 5% | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Asymmetry |  |  | hysteresis |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Output Circuit Characteristics | [44 empty] | Same as RM35UB3N30 | Same as RM35UB3N30
Type of output |  |  |  |  | output type | Published | Published |  | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | Same as RM17TG20 | Same as RM17TG20 | 1 x C/O relay contacts | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1 x C/O relay contacts | Same as RM17TE00 | Same as RM17TE00 | 1 x C/O relay contacts | Same as RM17TU00 | Same as RM17TU00 | 1 x C/O relay contacts | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1 x C/O relay contacts | Same as RM17TT00 | 2 x C/O relay contacts | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1 x C/O + 1 x C/O relay contacts | Same as RM35UB330 | Same as RM35UB330 | 1 x C/O + 1 x C/O relay contacts | Same as RM35UB3N30 | Same as RM35UB3N30 | 1 x C/O relay contacts | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 1 x C/O relay contacts | 2 x C/O relay contacts |  | 1 x C/O relay contact
Output terminal |  |  |  |  | output terminal |  |  |  | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 11-12-14, 21-22-24 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 11-12-14 | Same as RM17TE00 | Same as RM17TE00 | 11-12-14 | Same as RM17TU00 | Same as RM17TU00 | 11-12-14 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 11-12-14 | Same as RM17TT00 | 11-12-14, 21-22-24 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 11-12-14, 21-22-24 | Same as RM35UB330 | Same as RM35UB330 | 11-12-14, 21-22-24 | Same as RM35UB3N30 | Same as RM35UB3N30 | 11-12-14 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 11-12-14, 21-22-24 | 2014-11-12
Operation principle |  | R1 (11-12-14) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Energized on fault-free | Same as RM17TE00 | Same as RM17TE00 | Energized on fault-free | Same as RM17TU00 | Same as RM17TU00 | Energized on fault-free | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Energized on fault-free | Same as RM17TT00 | Energized on fault-free | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Energized on fault-free | Same as RM35UB330 | Same as RM35UB330 | Energized on fault-free | Same as RM35UB3N30 | Same as RM35UB3N30 | Energized on fault-free | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free |  | -
|  | R2 (21-22-24) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Energized on fault-free | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Energized on fault-free | Same as RM35UB330 | Same as RM35UB330 | Energized on fault-free | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 | [5 empty] | -
Contact material |  |  |  | Common C_Rly Spec | contacts material | Published | Published |  | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Cadmium free | Same as RM17TE00 | Same as RM17TE00 | Cadmium free | Same as RM17TU00 | Same as RM17TU00 | Cadmium free | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Cadmium free | Same as RM17TT00 | Cadmium free | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Cadmium free | Same as RM35UB330 | Same as RM35UB330 | Cadmium free | Same as RM35UB3N30 | Same as RM35UB3N30 | Cadmium free | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | Cadmium free | Cadmium free | 90/10 Nickel Silver | 90/10 Nickel Silver | 90/10 Nickel Silver | 90/10 Nickel Silver | 90/10 Nickel Silver | Cadmium free | Cadmium free | AgNi alloy, Cadmium free |  | AgSnO2
Mechanical durability |  |  | IEC61810-1 | Common C_Rly Spec | mechanical durability | Published | Published | Cyc | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 30 x 106 cycles | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 30 x 106 cycles | Same as RM17TE00 | Same as RM17TE00 | 30 x 106 cycles | Same as RM17TU00 | Same as RM17TU00 | 30 x 106 cycles | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 30 x 106 cycles | Same as RM17TT00 | 30 x 106 cycles | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 30 x 106 cycles | Same as RM35UB330 | Same as RM35UB330 | 30 x 106 cycles | Same as RM35UB3N30 | Same as RM35UB3N30 | 30 x 106 cycles | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 30 x 106 switching cycles | 20 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 20 x 106 switching cycles | 20 x 106 switching cycles | 30 x 106 switching cycles |  | >= 30 x 106 switching cycles
Electrical durability |  | AC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/5A, 100k cycles | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | NO: 250VAC/5A, 100k cycles | Same as RM17TE00 | Same as RM17TE00 | NO: 250VAC/5A, 100k cycles | Same as RM17TU00 | Same as RM17TU00 | NO: 250VAC/5A, 100k cycles | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | NO: 250VAC/5A, 100k cycles | Same as RM17TT00 | NO: 250VAC/5A, 100k cycles | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | NO: 250VAC/5A, 100k cycles | Same as RM35UB330 | Same as RM35UB330 | NO: 250VAC/5A, 100k cycles | Same as RM35UB3N30 | Same as RM35UB3N30 | NO: 250VAC/5A, 100k cycles | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 1 x 104 switching cycles | 1 x 104 switching cycles | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | 1 x 105 switching cycles | - | >= 1 x 105 switching cycles @ 5A, 250VAC
|  | DC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | NO: 24VDC/5A, 100k cycles | Same as RM17TE00 | Same as RM17TE00 | NO: 24VDC/5A, 100k cycles | Same as RM17TU00 | Same as RM17TU00 | NO: 24VDC/5A, 100k cycles | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | NO: 24VDC/5A, 100k cycles | Same as RM17TT00 | NO: 24VDC/5A, 100k cycles | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | NO: 24VDC/5A, 100k cycles | Same as RM35UB330 | Same as RM35UB330 | NO: 24VDC/5A, 100k cycles | Same as RM35UB3N30 | Same as RM35UB3N30 | NO: 24VDC/5A, 100k cycles | Same as RM17UB310 | Same as RM17UB310 | [14 empty] | -
|  | AC-15 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | NO: 250VAC/0.15A, 100k cycles | Same as RM17TE00 | Same as RM17TE00 | NO: 250VAC/0.15A, 100k cycles | Same as RM17TU00 | Same as RM17TU00 | NO: 250VAC/0.15A, 100k cycles | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | NO: 250VAC/0.15A, 100k cycles | Same as RM17TT00 | NO: 250VAC/0.15A, 100k cycles | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | NO: 250VAC/0.15A, 100k cycles | Same as RM35UB330 | Same as RM35UB330 | NO: 250VAC/0.15A, 100k cycles | Same as RM35UB3N30 | Same as RM35UB3N30 | NO: 250VAC/0.15A, 100k cycles | Same as RM17UB310 | Same as RM17UB310 | [14 empty] | -
|  | DC-13 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | NO: 24VDC/1A, 100k cycles | Same as RM17TE00 | Same as RM17TE00 | NO: 24VDC/1A, 100k cycles | Same as RM17TU00 | Same as RM17TU00 | NO: 24VDC/1A, 100k cycles | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | NO: 24VDC/1A, 100k cycles | Same as RM17TT00 | NO: 24VDC/1A, 100k cycles | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | NO: 24VDC/1A, 100k cycles | Same as RM35UB330 | Same as RM35UB330 | NO: 24VDC/1A, 100k cycles | Same as RM35UB3N30 | Same as RM35UB3N30 | NO: 24VDC/1A, 100k cycles | Same as RM17UB310 | Same as RM17UB310 | [14 empty] | -
Rated capacity |  | Rated switching voltage | IEC61810-1 | Common C_Rly Spec | [Ue] rated operational voltage | Published |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 250V | Same as RM17TE00 | Same as RM17TE00 | 250V | Same as RM17TU00 | Same as RM17TU00 | 250V | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 250V | Same as RM17TT00 | 250V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 250V | Same as RM35UB330 | Same as RM35UB330 | 250V | Same as RM35UB3N30 | Same as RM35UB3N30 | 250V | Same as RM17UB310 | Same as RM17UB310
|  | Rated switching current | IEC61810-1 | Common C_Rly Spec | [Ie] rated operational current | Published | Published | A | 8A | 8A | 8A | 8A | 8A | 8A | 8A | 5A | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | 8A | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 5A | Same as RM17TE00 | Same as RM17TE00 | 5A | Same as RM17TU00 | Same as RM17TU00 | 5A | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 5A | Same as RM17TT00 | 5A | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 5A | Same as RM35UB330 | Same as RM35UB330 | 5A | Same as RM35UB3N30 | Same as RM35UB3N30 | 5A | Same as RM17UB310 | Same as RM17UB310
Maximum switching capacity |  | Maximum switching voltage |  | Common C_Rly Spec | maximum switching capacity | Published | Published | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 250V | Same as RM17TE00 | Same as RM17TE00 | 250V | Same as RM17TU00 | Same as RM17TU00 | 250V | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 250V | Same as RM17TT00 | 250V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 250V | Same as RM35UB330 | Same as RM35UB330 | 250V | Same as RM35UB3N30 | Same as RM35UB3N30 | 250V | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~/-- 250 |  | -
|  | Maximum switching current |  | Common C_Rly Spec | maximum switching capacity | Published | Published | A | 8A | 8A | 8A | 8A | 8A | 8A | 8A | 5A | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | 8A | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 5A | Same as RM17TE00 | Same as RM17TE00 | 5A | Same as RM17TU00 | Same as RM17TU00 | 5A | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 5A | Same as RM17TT00 | 5A | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 5A | Same as RM35UB330 | Same as RM35UB330 | 5A | Same as RM35UB3N30 | Same as RM35UB3N30 | 5A | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | - |  | -
|  | Maximum switching capacity |  | Common C_Rly Spec | maximum switching capacity | Published | Published | VA | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
Minimum switching capacity |  | Minimum switching voltage | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 5 | 5 | 12 | 12 | 12 | 12 | 12 | 5 | 5 | 24
|  | Minimum switching current | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | mA | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | Minimum switching capacity | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published | Published | mW | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM17TE00 | Same as RM17TE00 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM17TU00 | Same as RM17TU00 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM17TT00 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM35UB330 | Same as RM35UB330 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM35UB3N30 | Same as RM35UB3N30 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 50 | 50 | 120 | 120 | 120 | 120 | 120 | 50 | 50 | 240
Maximum voltage drop at terminals |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum voltage drop |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 | [5 empty] | -
Leakage current |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum leakage current |  |  | mA | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 | [5 empty] | -
Thermal Current |  |  | IEC60947-5-1 | Common C_Rly Spec | thermal current |  |  | A | 8A | 8A | 8A | 8A | 8A | 8A | 8A | 5A | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | 8A | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 5A | Same as RM17TE00 | Same as RM17TE00 | 5A | Same as RM17TU00 | Same as RM17TU00 | 5A | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 5A | Same as RM17TT00 | 5A | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 5A | Same as RM35UB330 | Same as RM35UB330 | 5A | Same as RM35UB3N30 | Same as RM35UB3N30 | 5A | Same as RM17UB310 | Same as RM17UB310 | [5 empty] | -
Short circuit protection |  | Relay Output by external fuse | IEC60947-5-1 | Common C_Rly Spec | short circuit protection |  |  | gG | 8A | 8A | 8A | 8A | 8A | 8A | 8A | 5A | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | 8A | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 5A | Same as RM17TE00 | Same as RM17TE00 | 5A | Same as RM17TU00 | Same as RM17TU00 | 5A | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 5A | Same as RM17TT00 | 5A | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 5A | Same as RM35UB330 | Same as RM35UB330 | 5A | Same as RM35UB3N30 | Same as RM35UB3N30 | 5A | Same as RM17UB310 | Same as RM17UB310 | [5 empty] | -
|  | Solid State Output by external fuse | IEC62314 | Common C_Rly Spec | short circuit protection |  |  | gG | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 | [5 empty] | -
Time Delay Characteristics
Time delay functions |  | "OFF" delay |  |  | time delay type | Published |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Yes | Same as RM17TE00 | Same as RM17TE00 | Yes | Same as RM17TU00 | Same as RM17TU00 | Yes | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Yes | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Yes | Same as RM35UB330 | Same as RM35UB330 | Yes | Same as RM35UB3N30 | Same as RM35UB3N30 | Yes | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | · | · | · | · | · | - | - | · |  | -
|  | "ON" delay |  |  | time delay type | Published |  |  | - | Yes | Yes | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | · | · | · | · | · | - | - | · |  | -
|  | Inhibition |  |  | time delay type | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | - | - | - | - | - | - | - | - |  | -
Timing range |  | "OFF" delay |  |  | time delay range | Published | Published | s | - | Adjustable 0.1…30 | Adjustable 0.1…30 | - | - | Adjustable 0.1…30 | Adjustable 0.1…30 | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Adjustable 0.1…10 | Same as RM17TE00 | Same as RM17TE00 | Adjustable 0.1…10 | Same as RM17TU00 | Fixed 3.5s +/- 5% | Adjustable 0.1…10 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Adjustable 0.1…10 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Adjustable Tt1 0.1…30 for overvoltage @ R1 (11-12-14) Adjustable Tt2 0.1…30 for undervoltage @ R2 (21-22-24) | Same as RM35UB330 | Same as RM35UB330 | Adjustable Tt1 0.1…30 for overvoltage @ R1 (11-12-14) Adjustable Tt2 0.1…30 for undervoltage @ R2 (21-22-24) | Same as RM35UB3N30 | Same as RM35UB3N30 | Adjustable 0.1…30 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | Adjustable 0.1…10 | Adjustable 0.1…10 | Adjustable 0.1…10 | Adjustable 0.1…10 | Adjustable 0.1…10 | - | - | Adjustable 0.1…30 |  | -
|  | "ON" delay |  |  | time delay range | Published |  | s | - | Adjustable 0.1…30 | Adjustable 0.1…30 | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Inhibition |  |  | time delay range | Published | Published | s | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | - | - | - | - | - | - | - | - |  | -
Response time |  | on crossing the threshold |  |  | response time | Published | Published | ms | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 0 | Same as RM17TE00 | Same as RM17TE00 | 0 | Same as RM17TU00 | Same as RM17TU00 | 0 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 0 | Same as RM17TT00 | 0 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 0 | Same as RM35UB330 | Same as RM35UB330 | 0 | Same as RM35UB3N30 | Same as RM35UB3N30 | 0 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 0 | 0 | Not specified | Not specified | Not specified | Not specified | Not specified | 0 | 0 | - |  | < 100 for ON delay ; < 300 for OFF delay
|  |  |  | Reserved for other products | response time | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  |  |  | Reserved for other products | response time | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  |  |  | Reserved for other products | response time | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  |  |  | Reserved for other products | response time | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Time delay of pick-up |  |  |  |  | power on delay | Published | Published | ms | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 0 | Same as RM17TE00 | Same as RM17TE00 | 0 | Same as RM17TU00 | Same as RM17TU00 | 0 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 0 | Same as RM17TT00 | 0 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 0 | Same as RM35UB330 | Same as RM35UB330 | 0 | Same as RM35UB3N30 | Same as RM35UB3N30 | 0 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | 0 | 0 | Not specified | Not specified | Not specified | Not specified | Not specified | 0 | 0 | Fixed 200 |  | -
Reset time |  | through Un power reset |  |  | reset time | Published | Published | ms | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 0 | Same as RM17TE00 | Same as RM17TE00 | 0 | Same as RM17TU00 | Same as RM17TU00 | 0 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 0 | Same as RM17TT00 | 0 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 0 | Same as RM35UB330 | Same as RM35UB330 | 0 | Same as RM35UB3N30 | Same as RM35UB3N30 | 0 | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | Not specified | Not specified | Not specified | Not specified | Not specified | - | - | - |  | -
|  | through front panel reset |  | Reserved for other products | reset time | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | through input control reset |  | Reserved for other products | reset time | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Setting accuracy |  |  |  | Common C_Rly Spec | setting accuracy of time delay | Published | Published | % | - | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | - | - | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | Same as RM17TE00 | Same as RM17TE00 | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | Same as RM17TU00 | Same as RM17TU00 | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | Same as RM35UB330 | Same as RM35UB330 | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | Same as RM35UB3N30 | Same as RM35UB3N30 | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | +/- 10% of full scales value | +/- 10% of full scales value | +/- 10% of full scales value | +/- 10% of full scales value | +/- 10% of full scales value | - | - | - |  | -
Repeat accuracy (constant parameters) |  |  |  | Common C_Rly Spec | repeat accuracy of time delay | Published |  | % | - | +/- 3% | +/- 3% | - | - | +/- 3% | +/- 3% | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | +/- 3% | Same as RM17TE00 | Same as RM17TE00 | +/- 3% | Same as RM17TU00 | Same as RM17TU00 | +/- 3% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | +/- 3% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | +/- 3% | Same as RM35UB330 | Same as RM35UB330 | +/- 3% | Same as RM35UB3N30 | Same as RM35UB3N30 | +/- 3% | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | Not specified | Not specified | Not specified | Not specified | Not specified | - | - | < +/- 0.2% |  | -
Timing error with supply voltage variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/V | - | < 1 | < 1 | - | - | < 1 | < 1 | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | < 0.5% | < 0.5% | < 0.5% | < 0.5% | < 0.5% | - | - | < 0.5% |  | -
Timing error with temperature variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/oC | - | < 0.05 | < 0.05 | - | - | < 0.05 | < 0.05 | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  |  |  | - | - | =< 0.07% / oC | =< 0.07% / oC | =< 0.07% / oC | =< 0.07% / oC | =< 0.07% / oC | - | - | =< 0.06% / oC |  | -
LED Indication
status LED |  |  |  |  | status LED |  |  |  | Un (Green) R (Amber) | Dial pointer (Green) R (Amber) Def (Red) | Dial pointer (Green) R (Amber) Def (Red) | Dial pointer (Green) R (Amber) Def (Red) | Dial pointer (Green) R (Amber) Def (Red) | Dial pointer (Green) R (Amber) Def (Red) | Dial pointer (Green) R (Amber) Def (Red) | R (Amber) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | R (Amber) | Rel (Amber) | Un (Green) R (Amber) | Same as RM17TE00 | Same as RM17TE00 | Un (Green) R (Amber) | Same as RM17TU00 | R (Amber) | Un (Green) R (Amber) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Un (Green) R (Amber) | Same as RM17TT00 | Un (Green) R (Amber) Def (Amber) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Un (Green) R1 (Amber) R2 (Amber) | Same as RM35UB330 | Same as RM35UB330 | Un (Green) R1 (Amber) R2 (Amber) | Same as RM35UB3N30 | Same as RM35UB3N30 | Un (Green) R (Amber) | Same as RM17UB310 | Same as RM17UB310
local signalling |  | Power supply availability |  |  | local signalling |  |  |  | Un - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | - | - | Un - ON | Same as RM17TE00 | Same as RM17TE00 | Un - ON | Same as RM17TU00 | - | Un - ON | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Un - ON | Same as RM17TT00 | Un - ON | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Un - ON | Same as RM35UB330 | Same as RM35UB330 | Un - ON | Same as RM35UB3N30 | Same as RM35UB3N30 | Un - ON | Same as RM17UB310 | Same as RM17UB310
|  | Power supply not availability |  |  | local signalling |  |  |  | Un - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | - | - | Un - OFF | Same as RM17TE00 | Same as RM17TE00 | Un - OFF | Same as RM17TU00 | - | Un - OFF | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Un - OFF | Same as RM17TT00 | Un - OFF | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Un - OFF | Same as RM35UB330 | Same as RM35UB330 | Un - OFF | Same as RM35UB3N30 | Same as RM35UB3N30 | Un - OFF | Same as RM17UB310 | Same as RM17UB310
|  | Timing in-progress |  |  | local signalling |  |  |  | - | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | - | - | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM17TE00 | Same as RM17TE00 | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM17TU00 | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM17TT00 | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM35UB330 | Same as RM35UB330 | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM35UB3N30 | Same as RM35UB3N30 | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM17UB310 | Same as RM17UB310
|  | Output is energized |  |  | local signalling |  |  |  | R - ON | R - ON | R - ON | R - ON | R - ON | R - ON | R - ON | R - ON | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | R - ON | R - ON | R - ON | Same as RM17TE00 | Same as RM17TE00 | R - ON | Same as RM17TU00 | R - ON | R - ON | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | R - ON | Same as RM17TT00 | R - ON | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R1 / R2 - ON | Same as RM35UB330 | Same as RM35UB330 | R1 / R2 - ON | Same as RM35UB3N30 | Same as RM35UB3N30 | R - ON | Same as RM17UB310 | Same as RM17UB310
|  | Output is de-energized |  |  | local signalling |  |  |  | R - OFF | R - OFF | R - OFF | R - OFF | R - OFF | R - OFF | R - OFF | R - OFF | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | R - OFF | R - OFF | R - OFF | Same as RM17TE00 | Same as RM17TE00 | R - OFF | Same as RM17TU00 | R - OFF | R - OFF | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | R - OFF | Same as RM17TT00 | R - OFF | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R 1 / R2 - OFF | Same as RM35UB330 | Same as RM35UB330 | R 1 / R2 - OFF | Same as RM35UB3N30 | Same as RM35UB3N30 | R - OFF | Same as RM17UB310 | Same as RM17UB310
|  | Range Setting Changes |  |  | local signalling |  |  |  | - | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | - | - | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | Same as RM17TE00 | Same as RM17TE00 | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | Same as RM17TU00 | - | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | Same as RM17TT00 | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | Same as RM35UB330 | Same as RM35UB330 | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | Same as RM35UB3N30 | Same as RM35UB3N30 | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | Same as RM17UB310 | Same as RM17UB310
|  | Phase Cut |  |  | local signalling |  |  |  | - | Def - Permanent OFF | Def - Permanent OFF | Def - Permanent OFF | Def - Permanent OFF | Def - Permanent OFF | Def - Permanent OFF | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Def - Permanent OFF | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R 1 / R2 - OFF | Same as RM35UB330 | Same as RM35UB330 | R 1 / R2 - OFF | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Phase Sequence Swap |  |  | local signalling |  |  |  | - | Def - Permanent ON | Def - Permanent ON | Def - Permanent ON | Def - Permanent ON | Def - Permanent ON | Def - Permanent ON | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Def - Permanent OFF | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R 1 / R2 - OFF | Same as RM35UB330 | Same as RM35UB330 | R 1 / R2 - OFF | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Undervoltage <U |  |  | local signalling |  |  |  | - | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R2 - OFF | Same as RM35UB330 | Same as RM35UB330 | R2 - OFF | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Overvoltage >U |  |  | local signalling |  |  |  | - | Def - Fast Blink (5% ON; 95% OFF) @ 1Hz | Def - Fast Blink (5% ON; 95% OFF) @ 1Hz | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R 1 - OFF | Same as RM35UB330 | Same as RM35UB330 | R 1 - OFF | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Phase Asymmetry |  |  | local signalling |  |  |  | - | - | - | - | - | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Def - Permanent ON | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Voltage Regeneration |  |  | local signalling | Published |  |  | - | - | - | - | - | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Undervoltage <U (Phase loss) |  |  | local signalling |  |  |  | - | Def - Permanent OFF | Def - Permanent OFF | Def - Permanent OFF | Def - Permanent OFF | Def - Permanent OFF | Def - Permanent OFF | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Def - Permanent OFF | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R 1 / R2 - OFF | Same as RM35UB330 | Same as RM35UB330 | R 1 / R2 - OFF | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Overvoltage >U |  |  | local signalling |  |  |  | - | Def - Permanent ON | Def - Permanent ON | Def - Permanent ON | Def - Permanent ON | Def - Permanent ON | Def - Permanent ON | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Def - Permanent OFF | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R 1 / R2 - OFF | Same as RM35UB330 | Same as RM35UB330 | R 1 / R2 - OFF | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Phase Asymmetry |  |  | local signalling |  |  |  | - | - | - | - | - | Def - Permanent OFF | Def - Permanent OFF | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Def - Permanent OFF | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Special Features
True RMS | [8 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Yes | Same as RM17TE00 | Same as RM17TE00 | Yes | Same as RM17TU00 | Same as RM17TU00 | Yes | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Yes | Same as RM17TT00 | Yes | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Yes | Same as RM35UB330 | Same as RM35UB330 | Yes | Same as RM35UB3N30 | Same as RM35UB3N30 | Yes | Same as RM17UB310 | Same as RM17UB310
Backlight Indicator | [8 empty] | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Diagnostic Button |  |  |  |  | diagnostic button | Published |  |  | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Pre-Alarm Output | [8 empty] | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Output | [8 empty] | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM17TE00 | Same as RM17TE00 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM17TU00 | Same as RM17TU00 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM17TT00 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM35UB330 | Same as RM35UB330 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM35UB3N30 | Same as RM35UB3N30 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM17UB310 | Same as RM17UB310
Reliability Data
Reliability Data |  | MTTF |  |  | safety reliability data | Published |  | hrs | 8,100,000 hours | 3,400,000 hours | 3,400,000 hours | 3,400,000 hours | 3,400,000 hours | 3,400,000 hours | 3,400,000 hours | 8,100,000 hours | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 4,400,000 hours | Same as RM17TE00 | Same as RM17TE00 | 4,400,000 hours | Same as RM17TU00 | Same as RM17TU00 | 4,400,000 hours | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 4,400,000 hours | Same as RM17TT00 | 3,500,000 hours | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 2,800,000 hours | Same as RM35UB330 | Same as RM35UB330 | 4,400,000 hours | Same as RM35UB3N30 | Same as RM35UB3N30 | 4,400,000 hours | Same as RM17UB310 | Same as RM17UB310
|  | B10 |  |  | safety reliability data | Published |  | hrs | 850,000 hours | 350,000 hours | 350,000 hours | 350,000 hours | 350,000 hours | 350,000 hours | 350,000 hours | 850,000 hours | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 470,000 hours | Same as RM17TE00 | Same as RM17TE00 | 470,000 hours | Same as RM17TU00 | Same as RM17TU00 | 470,000 hours | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 470,000 hours | Same as RM17TT00 | 360,000 hours | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 300,000 hours | Same as RM35UB330 | Same as RM35UB330 | 470,000 hours | Same as RM35UB3N30 | Same as RM35UB3N30 | 470,000 hours | Same as RM17UB310 | Same as RM17UB310
|  | MTTFd | [5 empty] | hrs | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM17TE00 | Same as RM17TE00 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM17TU00 | Same as RM17TU00 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM17TT00 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM35UB330 | Same as RM35UB330 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM35UB3N30 | Same as RM35UB3N30 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM17UB310 | Same as RM17UB310
|  | B10d | [5 empty] | hrs | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM17TE00 | Same as RM17TE00 | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM17TU00 | Same as RM17TU00 | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM17TT00 | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM35UB330 | Same as RM35UB330 | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM35UB3N30 | Same as RM35UB3N30 | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM17UB310 | Same as RM17UB310
Drawing / Diagram
[9 empty] | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram

## Level Control Spec
Main Parameters | Category | Sub Parameters | Conforming to | Remark | Standardized Datasheet Param | Selected for Publication | Old Datasheet | Unit | RM22LG11MR | RM22LG11MT | RM22LA32MR | RM22LA32MT | RM35LM33MW | RM35LV14MW | col15 | col16 | Competitor Spec Reference | RM35LM33MW | RM35LV14MW | RM4LA32 | RM4LG01 | RM22 (Catch Up) | 8487020x | RM22 (Catch Up) | 8487021x
Standard
Product standard |  |  |  | Common C_Rly Spec | standards | Published | Published |  | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | NF EN 60255-6 and IEC 60255-6 | NF EN 60255-6 and IEC 60255-6 |  |  |  | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | Not specified | EN60255-6, IEC60255-6 | Not specified
Product certifications |  |  |  | Common C_Rly Spec | product certifications | Published | Published |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST |  |  |  | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | cULus, CE, CSA | UL, CSA, GL, C-Tick, GOST | cULus, CE, CSA
Marking |  |  |  | Common C_Rly Spec | marking | Published |  |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | 1: 73/23/EEC and EMC 89/336/EEC | 1: 73/23/EEC and EMC 89/336/EEC |  |  |  | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE | cULus, CE, CSA | UL, CSA, GL, C-Tick, GOST, CE | cULus, CE, CSA
Low voltage directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | [5 empty] | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | Not specified | No 73/23/EEC + 93/68/EEC | Not specified
EMC directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | [5 empty] | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | Not specified | No 89/336/EEC + 92/31/EEC + 93/68/EEC | Not specified
ROHS directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | [5 empty] | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC | Not specified | 2002/95/EC | Not specified
Environment Characteristics
Environmental Condition |  | Climatic category | IEC60721-3-3 | Common C_Rly Spec |  |  |  |  | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | [5 empty] | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | Environmental category | Germanisher Lloyd | Common C_Rly Spec |  |  |  |  | Class C | Class C | Class C | Class C
Ambient air temperature around the device |  | Storage |  | Common C_Rly Spec | ambient air temperature for storage | Published | Published | oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | - 40…+ 70 | - 40…+ 70 |  |  |  | -40…+70 | -40…+70 | Not specified | Not specified | -40…+70 | -40…+70 | -40…+70 | -40…+70
|  | Operation |  |  | ambient air temperature for operation | Published | Published | oC | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | - 20…+ 50 | - 20…+ 50 |  |  |  | -20…+50 | -20…+50 | Not specified | Not specified | -20…+50 | -20…+50 | -20…+50 | -20…+50
Relative humidity |  | Damp heat | IEC60068-2-30 | Common C_Rly Spec | relative humidity | Published | Published |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 2 x 24 hours…+ 95 % RH at + 55 °C (without condensation) | 2 x 24 hours…+ 95 % RH at + 55 °C (without condensation) |  |  |  | 2 cycles 24h ;+25°C +55°C 95%HR | 2 cycles 24h ;+25°C +55°C 95%HR | Not specified | Not specified | 2 cycles 24h ;+25°C +55°C 95%HR | Not specified | 2 cycles 24h ;+25°C +55°C 95%HR | Not specified
|  | Cyclic Damp Heat Test | IEC60947-5-1 | Common C_Rly Spec |  |  |  |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97%
Vibration resistance |  |  | IEC60068-2-6 | Common C_Rly Spec | vibration resistance | Published | Published |  | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.035 mm from 10…150 Hz | 0.035 mm from 10…150 Hz |  |  |  | 0.035mm from 10Hz…150Hz | 0.035mm from 10Hz…150Hz | Not specified | Not specified | 0.035mm from 10Hz…150Hz | Not specified | 0.035mm from 10Hz…150Hz | Not specified
Shock resistance |  |  | IEC60068-2-27 | Common C_Rly Spec | shock resistance | Published | Published |  | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 5 gn | 5 gn |  |  |  | 5 gn | 5 gn | Not specified | Not specified | 5 gn | Not specified | 5 gn | Not specified
Bump resistance |  |  | IEC60068-2-29 | Common C_Rly Spec | bump resistance |  |  |  | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating)
Seismic resistance |  |  | IEC60068-3-3 | Common C_Rly Spec | seismic resistance |  |  |  | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz
IP degree of protection |  | Terminal Block | IEC60529 |  | IP degree of protection | Published | Published |  | IP20 | IP20 | IP20 | IP20 | IP 20 | IP 20 |  |  |  | IP20 | IP20 | Not specified | Not specified | IP20 | Not specified | IP20 | Not specified
|  | Housing | IEC60529 |  | IP degree of protection | Published | Published |  | IP40 | IP40 | IP40 | IP40 | IP 30 | IP 30 |  |  |  | IP30 | IP30 | Not specified | Not specified | IP30 | Not specified | IP30 | Not specified
|  | Front Panel | IEC60529 |  | IP degree of protection |  |  |  | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover)
Installation Data
Dimension (nominal) |  | Width |  |  | width | Published |  | mm | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 | [5 empty] | 35 x 90 x 72 | 35 x 90 x 72 | 22.5 x 78 x 80 | 22.5 x 78 x 80 | 22.5 x ? x ? | 22.5 x 78.5 x 100 | 22.5 x ? x ? | 22.5 x 78.5 x 100
|  | Height |  |  | height | Published |  | mm
|  | Depth |  |  | depth | Published |  | mm
Weight (without packaging) |  |  |  |  | net weight | Published |  | g | 100 | 100 | 110 | 110 | [5 empty] | 130 | 130 | 168 | 168 | ? | 150 | ? | 150
Mounting |  | Without socket | IEC/EN 60715 |  | mounting support | Published | Published |  | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 4 rail | On 4 rail |  |  |  | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail
|  | With socket | IEC/EN 60715 |  | mounting support |  |  |  | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | -
Mounting position |  | In relation to normal vertical mounting plane |  | Common C_Rly Spec | mounting position | Published | Published |  | Any position | Any position | Any position | Any position | Any position | Any position |  |  |  | Any position | Any position | Not specified | Not specified | Any position | Not specified | Any position | Not specified
Minimum distance to adjacent devices |  | Horizontal |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | Not specified | Not specified | Not specified | Not specified | [5 empty] | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | Vertical |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | Not specified | Not specified | Not specified | Not specified | [5 empty] | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Wiring connection (Clamping Capacity) |  | Solid cable without cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…4 (AWG 20…AWG 11) | 1 conductor: 0.5…4 (AWG 20…AWG 11) |  |  |  | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | Not specified | Not specified | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | Not specified | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | Not specified
|  | Flexible cable with cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 2 conductors: 0.5…2.5 (AWG 20…AWG 14) |  |  |  | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | Not specified | Not specified | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | Not specified | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | Not specified
|  | Solid cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | - | - | - | 1 conductor: 0.2…2.5 (AWG 24…AWG 12) | 1 conductor: 0.2…2.5 (AWG 24…AWG 12) |  |  |  | - | - | - | - | - | - | - | -
|  | Flexible cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | - | - | - | 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 2 conductors: 0.2…1.5 (AWG 24…AWG 16) |  |  |  | - | - | - | - | - | - | - | -
|  | Tightening torque | IEC60947-1 | Common C_Rly Spec | tightening torque | Published | Published | Nm | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | 0.6…1N.m / 5.3…8.8 Lbf.In | 0.6…1N.m / 5.3…8.8 Lbf.In |  |  |  | 0.6…1 | 0.6…1 | Not specified | Not specified | 0.6…1 | Not specified | 0.6…1 | Not specified
|  | Cable stripping length |  | Common C_Rly Spec | cable stripping length |  |  | mm | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | [5 empty] | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Duty time |  |  |  | Common C_Rly Spec | duty time |  |  | % | 1 | 1 | 1 | 1 | [5 empty] | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Electromagnetic Compatibility
Immunity |  | Generic immunity standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | Immunity NF EN 61000-6-2 2002 / IEC 61000-6-2 | Immunity NF EN 61000-6-2 2002 / IEC 61000-6-2 |  |  |  | IEC61000-6-2 | IEC61000-6-2 | IEC50082-2 | IEC50082-2 | IEC61000-6-2 | Not specified | IEC61000-6-2 | Not specified
|  | Electrostatic discharge | IEC61000-4-2 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | [5 empty] | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Not specified | Level 3 (6kV / 8kV) | Not specified
|  | Radiated RF & electromagnetic field | IEC61000-4-3 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | [5 empty] | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Not specified | Level 3 (10V/m) | Not specified
|  | Fast transient / burst | IEC61000-4-4 |  | electromagnetic compatibility | Published |  |  | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | [5 empty] | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Not specified | Level 3 (2kV coupling / 4kV direct) | Not specified
|  | Surge | IEC61000-4-5 |  | electromagnetic compatibility | Published |  |  | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | [5 empty] | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Not specified | Level 3 (1kV phase-phase) | Not specified
|  | Conducted RF disturbance | IEC61000-4-6 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | [5 empty] | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Not specified | Level 3 (10V) | Not specified
|  | Power frequency magnetic field | IEC61000-4-8 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s)
|  | Voltage dips, short interruption & variations on power line | IEC61000-4-11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | - | - | - | [5 empty] | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Not specified | Class 3 (0%, 40%, 70%, 80% of Us) | Not specified
|  | 1 MHz oscillation wave | IEC61000-4-18 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV)
|  | DC voltage interruption | IEC61000-4-29 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms
|  | Low frequency harmonics | IEC61000-4-13 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | - | - | - | [5 empty] | Not tested | Not tested | Not tested | Not tested | Not tested | Not specified | Not tested | Not specified
|  | Conducted low frequency interference (harmonics) | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | Emission NF EN 61000-6-4, NF EN 61000-6-3, IEC 61000-6-4, IEC 61000-6-3 | Emission NF EN 61000-6-4, NF EN 61000-6-3, IEC 61000-6-4, IEC 61000-6-3 |  |  |  | · | · | ? | ? | · | Not specified | · | Not specified
Emission |  | Generic emission standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | [5 empty] | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | Not specified | IEC61000-6-3, IEC61000-6-4 | Not specified
|  | Radiated RF & electromagnetic field (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B | Class B | Class B | [5 empty] | Class B | Class B | Class B Group1 | Class B Group1 | Class B | Not specified | Class B | Not specified
|  | Radiated RF & electromagnetic field (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | [5 empty] | Class B | Class B | Class B Group1 | Class B Group1 | Class B | Not specified | Class B | Not specified
|  | Radiated emission from enclosure port | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | [5 empty] | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | Not specified | EMC 2 | Not specified
|  | Conducted RF emission on power line (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B | Class B | Class B | [5 empty] | Class B | Class B | Class B Group1 | Class B Group1 | Class B | Not specified | Class B | Not specified
|  | Conducted RF emission on power line (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | [5 empty] | Class B | Class B | Class B Group1 | Class B Group1 | Class B | Not specified | Class B | Not specified
|  | Conducted emission | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | [5 empty] | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | Not specified | EMC 2 | Not specified
Electrical Isolation
Degree of pollution |  |  | IEC60664-1 | Common C_Rly Spec | pollution degree | Published | Published |  | 3 | 3 | 3 | 3 | 3 | 3 |  |  |  | 3 | 3 | Not specified | Not specified | 3 | Not specified | 3 | Not specified
Overvoltage category |  |  | IEC60664-1 | Common C_Rly Spec | overvoltage category | Published | Published |  | 3 | 3 | 3 | 3 | III | III |  |  |  | III | III | Not specified | Not specified | III | Not specified | III | Not specified
Circuit Group | Terminal | Supply |  |  | circuit group | Published |  |  | A1, A2 | A1, A2 | A1, A2 | A1, A2
|  | Input 1 |  |  | circuit group | Published |  |  | Min, Max, C | Min, Max, C | Min, Max, C | Min, Max, C
|  | Input 2 |  |  | circuit group | Published |  |  | - | - | - | -
|  | Input 3 |  |  | circuit group | Published |  |  | - | - | - | -
|  | Output 1 |  |  | circuit group | Published |  |  | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14
|  | Output 2 |  |  | circuit group | Published |  |  | - | - | 21,22,24 | 21,22,24 | [5 empty] | 600 | 600 | Not specified | Not specified | 600 | Not specified | 600 | Not specified
| Rated | Supply | [6 empty] | 24…240 AC/DC | 380…415 AC | 24…240 AC/DC | 380…415 AC | [5 empty] | 600 | 600 | Not specified | Not specified | 600 | Not specified | 600 | Not specified
| Voltage | Input 1 | [6 empty] | Level probe | Level probe | Level probe | Level probe | [5 empty] | 600 | 600 | Not specified | Not specified | 600 | Not specified | 600 | Not specified
| Spec | Input 2 | [6 empty] | - | - | - | -
|  | Input 3 | [6 empty] | - | - | - | -
|  | Output 1 | [6 empty] | 250V | 250V | 250V | 250V
|  | Output 2 | [6 empty] | - | - | 250V | 250V
Rated Insulation Voltage |  | Supply | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 400V | 250V | 400V | 250 | 250
|  | Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 10V | 10V | 10V | 10V
|  | Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | [5 empty] | 4 | 4 | Not specified | Not specified | 4 | Not specified | 4 | Not specified
|  | Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | 250V | 250V
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 400V | 250V | 400V
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Supply / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 400V | 250V | 400V
|  | Supply / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | - | - | 250V | 400V
|  | Output 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | - | - | 250V | 250V
|  | Input 1 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V
|  | Input 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | 250V | 250V
|  | Input 2 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Input 2 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | [5 empty] | 2 @ 50Hz for 1 minutes | 2 @ 50Hz for 1 minutes | Not specified | Not specified | 2 @ 50Hz for 1 minutes | Not specified | 2 @ 50Hz for 1 minutes | Not specified
|  | Input 3 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Input 3 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Input 1 / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
Rated Impulse Voltage |  | Supply | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4 (1.2/50 µs) | 4 (1.2/50 µs)
|  | Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Supply / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Supply / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | - | - | 4kV, OVC3 | 4kV, OVC3
|  | Output 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | - | - | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | 4kV, OVC3 | 4kV, OVC3
|  | Input 2 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 2 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | [5 empty] | > 500MOhm @ -- 500V | > 500MOhm @ -- 500V | Not specified | Not specified | > 500MOhm @ -- 500V | Not specified | > 500MOhm @ -- 500V | Not specified
|  | Input 3 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 3 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 1 / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
Dielectric test voltage |  | Supply / Input 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2, 1 50 Hz, 1 min. | 2, 1 50 Hz, 1 min. |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
|  | Supply / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | [5 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
|  | Supply / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | [5 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
|  | Supply / Output 1 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Supply / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | - | - | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Output 1 / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | - | - | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 2 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
|  | Input 2 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
|  | Input 3 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
|  | Input 3 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
|  | Input 1 / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
|  | Input 2 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
|  | Input 1 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
Insulation resistance |  | Supply / Input 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | > 500 MΩ, 2 500 V | > 500 MΩ, 2 500 V
|  | Supply / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Supply / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Supply / Output 1 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | - | - | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Output 1 / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | - | - | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 2 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Input 2 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Input 3 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Input 3 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Input 1 / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Input 2 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Input 1 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
Power Supply Characteristics
Rated supply voltage, Us |  |  |  |  | [Us] rated supply voltage | Published | Published | V | ~/-- 24…240 | ~380…415 | ~/-- 24…240 | ~380…415 | ~/-- 24…240 | 1/2 24…240 |  |  |  | ~/-- 24…240 | ~/-- 24…240 | RM4LA32B: ~ 24 RM4LA32F: ~110…130 RM4LA32M: ~220…240 RM4LA32MW: ~/-- 24…240 RM4LA32Q: ~380…415 | RM4LA32B: ~ 24 RM4LA32F: ~110…130 RM4LA32M: ~220…240 RM4LA32Q: ~380…415 | ~/-- 24…240 | 84870201: ~ 24 84870203: ~120 84870204: ~230 | ~/-- 24…240 | 84870211: ~ 24 84870213: ~120 84870214: ~230
Supply voltage operating range |  |  |  |  | supply voltage limits | Published | Published | V | ~/-- 20.4…264 | ~323…456.5 | ~/-- 20.4…264 | ~323…456.5 | ~/-- 20.4…264 | 1/2 20.4…264 |  |  |  | ~/-- 20.4…264 | ~/-- 20.4…264 | Not specified | Not specified | ~/-- 20.4…264 | Not specified | ~/-- 20.4…264 | Not specified
Polarity on d.c. supply |  |  |  |  | polarity |  | Published
Rated frequency |  |  |  |  | supply frequency | Published | Published | Hz | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50/60 Hz ± 10 % | 50/60 Hz ± 10 % |  |  |  | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60
Frequency operating range |  |  |  |  | supply frequency | Published | Published | Hz | 45…66 | 45…66 | 45…66 | 45…66 | [5 empty] | 45…66 | 45…66 | Not specified | Not specified | 45…66 | Not specified | 45…66 | Not specified
Maximum power consumption |  |  |  |  | power consumption | Published | Published |  | ~ 3.5VA, ~5VA, 1.5W | ~ 10VA ~ 8VA | ~ 3.5VA, ~5VA, 1.5W | ~ 10VA ~ 8VA | 5VA / 1.5W | 5VA / 1.5W |  |  |  | ~ 5VA, -- 1.5W | ~ 5VA, -- 1.5W | RM4LA32B: 3.1VA RM4LA32F: 2.7VA RM4LA32M: 2.6VA RM4LA32MW: 2.7VA, 2.4W RM4LA32Q: 3.4VA | RM4LG01B: 1.9VA RM4LG01F: 2.6VA RM4LG01M: 2.4VA RM4LG01Q: 2.9VA | ~ 5VA, -- 1.5W | 3VA | ~ 5VA, -- 1.5W | 3VA
Immunity to micro-breakage |  |  |  |  | immunity to microbreaks | Published | Published | ms | ~ 90, -- 100 | ~ 90, -- 100 | ~ 90, -- 100 | ~ 90, -- 100 | ~ 90, -- 100 | ~ 90, -- 100 |  |  |  | 90 (AC), 100 (DC) | 90 (AC), 100 (DC) | Not specified | Not specified | 90 (AC), 100 (DC) | Not specified | 90 (AC), 100 (DC) | Not specified
Supply terminal |  |  |  |  | supply terminal |  |  |  | A1-A2 | A1-A2 | A1-A2 | A1-A2 | [5 empty] | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2
On Load Factor |  |  |  | Common C_Rly Spec | on-load factor |  |  | % | 1 | 1 | 1 | 1
Release of input voltage |  |  |  |  | release of input voltage |  |  | V | - | - | - | -
Input Circuit Characteristics
Monitoring functions |  | 1 level - Fill operation |  |  | monitoring functions |  |  |  | - governed by response time - status reflects to both R1 & R2 | - governed by response time - status reflects to both R1 & R2 | - governed by time delay - status reflects to both R1 & R2 | - governed by time delay - status reflects to both R1 & R2
|  | 1 level - Empty operation |  |  | monitoring functions |  |  |  | - governed by response time - status reflects to both R1 & R2 | - governed by response time - status reflects to both R1 & R2 | - governed by time delay - status reflects to both R1 & R2 | - governed by time delay - status reflects to both R1 & R2
|  | 2 level - Fill operation |  |  | monitoring functions |  |  |  | - governed by response time - status reflects to both R1 & R2 | - governed by response time - status reflects to both R1 & R2 | - governed by time delay - status reflects to both R1 & R2 | - governed by time delay - status reflects to both R1 & R2
|  | 2 level - Empty operation |  |  | monitoring functions |  |  |  | - governed by response time - status reflects to both R1 & R2 | - governed by response time - status reflects to both R1 & R2 | - governed by time delay - status reflects to both R1 & R2 | - governed by time delay - status reflects to both R1 & R2
Monitoring function characteristics |  | Measurement mode
|  | Internal input resistance |  |  | internal input resistance |  |  |  | - | - | - | -
|  | Input terminal |  |  | input terminal |  |  |  | Min-Max-C | Min-Max-C | Min-Max-C | Min-Max-C
|  | Maximum probe supplied voltage |  |  | Maximum probe supplied voltage |  |  | V | 12 | 12 | 12 | 12 | 12 | 12 |  |  |  | 12 | 12 | 24 | 24 | 12 | 24 | 12 | 24
|  | Maximum probe supplied current |  |  | Maximum probe supplied current |  |  | mA | 1 | 1 | 1 | 1 | < 1 | 40 |  |  |  | 1 | 40 | 1 | 1 | 1 | 1 | 1 | 1
|  | Maximum length of probes cable |  |  | Maximum length of probes cable |  |  | m | 100 | 100 | 100 | 100 | 100 | 100 |  |  |  | 100 | 100 | 1000 | 1000 | 100 | Not specified | 100 | Not specified
|  | Maximum cable capacitance |  |  | input frequency |  |  | nF | 1 for LS 2.2 for St 4.7 for HS | 1 for LS 2.2 for St 4.7 for HS | 1 for LS 2.2 for St 4.7 for HS | 1 for LS 2.2 for St 4.7 for HS | 1 for LS 2.2 for St 4.7 pour HS | 10 | [8 empty] | 10 |  | 10
|  | Setting accuracy |  |  | setting accuracy of the switching threshold |  |  | % | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value for LS '+/- 10% of full scale value for St '+/- 35% of full scale value for HS | +/- 10% of full scale value for LS '+/- 10% of full scale value for St '+/- 35% of full scale value for HS | ± 10 % of the full scale ± 20 % for the HS range | ± 10 % of the full scale ± 20 % for the HS range |  |  |  | +/- 10% of full scale value, +/- 20% for HS range | +/- 10% of full scale value | Not specified | Not specified | +/- 10% of full scale value, +/- 20% for HS range | +/- 30% at max sensitivity | +/- 10% of full scale value, +/- 20% for HS range | +/- 30% at max sensitivity
|  | Repeat accuracy (constant parameters) |  |  | repeat accuracy of the switching threshold |  |  | % | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | [5 empty] | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | Measurement method |  |  | measurement method |  |  |  | Liquid level resistive probe | Liquid level resistive probe | Liquid level resistive probe | Liquid level resistive probe | [5 empty] | Liquid level probe | 12V NPN/PNP ultrasonics sensor | Liquid level probe | Liquid level probe | Liquid level probe | Liquid level probe | Liquid level probe | Liquid level probe
|  | Measurement error with supply voltage variation |  |  | switching threshold drift |  |  | %/V | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range | [5 empty] | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | Measurement error with temperature variation |  |  | switching threshold drift |  |  | %/oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.5 % / °C | 0.5 % / °C |  |  |  | 0.5% / oC | 0.5% / oC | Not specified | Not specified | 0.5% / oC | Not specified | 0.5% / oC | Not specified
|  | Maximum measuring cycles |  |  | maximum measuring cycle
Measurement range |  | 1 level - Fill operation |  |  | measurement range |  |  | kW | 5kW…100kW | 5kW…100kW | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS | 250 Ω…5 kΩ | –
|  | 1 level - Empty operation |  |  | measurement range |  |  | kW | 5kW…100kW | 5kW…100kW | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS | 5 kΩ…100 kΩ | –
|  | 2 level - Fill operation |  |  | measurement range |  |  | kW | 5kW…100kW | 5kW…100kW | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS | 50 kΩ…1 MΩ | –
|  | 2 level - Empty operation |  |  | measurement range |  |  | kW | 5kW…100kW | 5kW…100kW | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS
Tripping threshold |  | 1 level - Fill operation |  |  | tripping threshold |  |  | % | Adjustable 5%...100% of 100kW | Adjustable 5%...100% of 100kW | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS | 5…100 % of the range | –
|  | 1 level - Empty operation |  |  | tripping threshold |  |  | % | Adjustable 5%...100% of 100kW | Adjustable 5%...100% of 100kW | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS
|  | 2 level - Fill operation |  |  | tripping threshold |  |  | % | Adjustable 5%...100% of 100kW | Adjustable 5%...100% of 100kW | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS
|  | 2 level - Empty operation |  |  | tripping threshold |  |  | % | Adjustable 5%...100% of 100kW | Adjustable 5%...100% of 100kW | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS
Hysteresis |  | 1 level - Fill operation |  |  | hysteresis |  |  |  | - | - | - | -
|  | 1 level - Empty operation |  |  | hysteresis |  |  |  | - | - | - | -
|  | 2 level - Fill operation |  |  | hysteresis |  |  |  | - | - | - | -
|  | 2 level - Empty operation |  |  | hysteresis |  |  |  | - | - | - | -
Output Circuit Characteristics
Type of output |  |  |  |  | output type | Published | Published |  | 1 x C/O relay contacts | 1 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 C/O contacts | 1 C/O contact |  |  |  | 2 x C/O relay contacts | 1 x C/O relay contacts | 2 x C/O relay contacts | 1 x C/O relay contacts | 1 x C/O relay contacts | 1 x C/O relay contacts | 2 x C/O relay contacts | 1 x C/O relay contacts
Output terminal |  |  |  |  | output terminal |  |  |  | 11/12/14, | 11/12/14, | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | [5 empty] | 11-12-14, 21-22-24 | 11-12-14 | 15-16-18, 25-26-28 | 15-16-18 | 11-12-14 | 11-12-14 | 11-12-14, 21-22-24 | 11-12-14
Operation principle |  | R1 (11-12-14) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | [5 empty] | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | R2 (21-22-24) |  |  | output logic |  |  |  | - | - | Energized on fault-free | Energized on fault-free
Contact material |  |  |  | Common C_Rly Spec | contacts material | Published | Published |  | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free |  |  |  | Cadmium free | Cadmium free | Not specified | Not specified | Cadmium free | Cadmium free | Cadmium free | Cadmium free
Mechanical durability |  |  | IEC61810-1 | Common C_Rly Spec | mechanical durability | Published | Published | Cyc | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 30 x 106 operating cycles | 30 x 106 operating cycles |  |  |  | 30 x 106 switching cycles | 30 x 106 switching cycles | Not specified | Not specified | 30 x 106 switching cycles | Not specified | 30 x 106 switching cycles | Not specified
Electrical durability |  | AC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | 1 x 105 operating cycles | 1 x 105 operating cycles |  |  |  | 1 x 105 switching cycles | 1 x 105 switching cycles | Not specified | Not specified | 1 x 105 switching cycles | Not specified | 1 x 105 switching cycles | Not specified
|  | DC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | AC-12, AC-13, AC-14, AC-15, DC-12, DC-13 | AC-12, AC-13, AC-14, AC-15, DC-12, DC-13
|  | AC-15 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles
|  | DC-13 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles
Rated capacity |  | Rated switching voltage | IEC61810-1 | Common C_Rly Spec | [Ue] rated operational voltage | Published |  | V | 250V | 250V | 250V | 250V | 1250 | 1250
|  | Rated switching current | IEC61810-1 | Common C_Rly Spec | [Ie] rated operational current | Published | Published | A | 8A | 8A | 8A | 8A | 5 | 5
Maximum switching capacity |  | Maximum switching voltage |  | Common C_Rly Spec | maximum switching capacity | Published | Published | V | 250V | 250V | 250V | 250V | 1/2 250 | 1/2 250 |  |  |  | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | Not specified | ~ 250 | Not specified
|  | Maximum switching current |  | Common C_Rly Spec | maximum switching capacity | Published | Published | A | 8A | 8A | 8A | 8A | 1/2 5 | 1/2 5 |  |  |  | ~ 5 | ~ 5 | 8 | 8 | ~ 8 | Not specified | ~ 5 | Not specified
|  | Maximum switching capacity |  | Common C_Rly Spec | maximum switching capacity | Published | Published | VA | - | - | - | - | [5 empty] | 1250 | 1250 | 2000VA | 2000VA | 2000 | Not specified | 1250 | Not specified
Minimum switching capacity |  | Minimum switching voltage | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | V | - | - | - | - | [5 empty] | 5 | 5 | Not specified | Not specified | 5 | Not specified | 5 | Not specified
|  | Minimum switching current | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | mA | - | - | - | - | [5 empty] | 10 | 10 | Not specified | Not specified | 10 | Not specified | 10 | Not specified
|  | Minimum switching capacity | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published | Published | mW | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | 10/ 2 5 V | 10/ 2 5 V |  |  |  | 50 | 50 | Not specified | Not specified | 50 | Not specified | 50 | Not specified
Maximum voltage drop at terminals |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum voltage drop |  |  | V | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | -
Leakage current |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum leakage current |  |  | mA | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | -
Thermal Current |  |  | IEC60947-5-1 | Common C_Rly Spec | thermal current |  |  | A | 8A | 8A | 8A | 8A | [5 empty] | 5 | 5 | 8 | 8 | 8
Short circuit protection |  | Relay Output by external fuse | IEC60947-5-1 | Common C_Rly Spec | short circuit protection |  |  | gG | 8A | 8A | 8A | 8A | [5 empty] | 8 |  |  |  | 8
|  | Solid State Output by external fuse | IEC62314 | Common C_Rly Spec | short circuit protection |  |  | gG | - | - | - | -
Time Delay Characteristics
Time delay functions |  | "OFF" delay |  |  | time delay type | Published |  |  | - | - | Yes | Yes | [5 empty] | · | · | · | - | - | - | · | ·
|  | "ON" delay |  |  | time delay type | Published |  |  | Yes | Yes | Yes | Yes | [5 empty] | · | · | · | - | - | - | · | ·
|  | Inhibition |  |  | time delay type | Published |  |  | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | -
Timing range |  | "OFF" delay |  |  | time delay range | Published | Published | s | - | - | Adjustable 0.1…30 | Adjustable 0.1…30 | 0.1…5, 0 + 10 % | 0.1…5, 0 + 10 % |  |  |  | Adjustable 0.1…5 | Adjustable 0.1…5 | Adjustable 0.1…10 | - | - | - | Adjustable 0.1…5 | Adjustable 0.1…5
|  | "ON" delay |  |  | time delay range | Published |  | s | - | - | Adjustable 0.1…30 | Adjustable 0.1…30 | [5 empty] | Adjustable 0.1…5 | Adjustable 0.1…5 | Adjustable 0.1…10 | - | - | - | Adjustable 0.1…5 | Adjustable 0.1…5
|  | Inhibition |  |  | time delay range | Published | Published | s | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | -
Response time |  | on crossing the threshold |  |  | response time | Published | Published | ms | 0 | 0 | 0 | 0 | [5 empty] | Not specified | Not specified | Not specified | Not specified | Not specified | 300 high level; 500 low level | Not specified | 300 high level; 500 low level
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
Time delay of pick-up |  |  |  |  | power on delay | Published | Published | ms | 0 | 0 | 0 | 0 | 600 | 500 |  |  |  | 0 | 0 | Not specified | Not specified | 0 | Not specified | 0 | Not specified
Reset time |  | through Un power reset |  |  | reset time | Published | Published | ms | 0 | 0 | 0 | 0 | 1.75 | 4 if 1 line broken / 1 if 2 lines broken |  |  |  | 0 | 0 | Not specified | Not specified | 0 | Not specified | 0 | Not specified
|  | through front panel reset |  | Reserved for other products | reset time | Published
|  | through input control reset |  | Reserved for other products | reset time | Published
Setting accuracy |  |  |  | Common C_Rly Spec | setting accuracy of time delay | Published | Published | % | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | [5 empty] | +/- 10% of full scales | +/- 10% of full scales | Not specified | Not specified | +/- 10% of full scales | Not specified | +/- 10% of full scales | Not specified
Repeat accuracy (constant parameters) |  |  |  | Common C_Rly Spec | repeat accuracy of time delay | Published |  | % | +/- 2% | +/- 2% | +/- 2% | +/- 2% | ± 2 % | ± 2 % |  |  |  | +/- 2% | +/- 2% | Not specified | Not specified | +/- 2% | Not specified | +/- 2% | Not specified
Timing error with supply voltage variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/V | < 1 | < 1 | < 1 | < 1 | [5 empty] | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Timing error with temperature variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/oC | < 0.05 | < 0.05 | < 0.05 | < 0.05 | [5 empty] | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
LED Indication
status LED |  |  |  |  | status LED |  |  |  | R (Amber) | R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber)
local signalling |  | Power supply availability |  |  | local signalling |  |  |  | - | - | Dial pointer - ON | Dial pointer - ON | Green LED | Green LED
|  | Power supply not availability |  |  | local signalling |  |  |  | - | - | Dial pointer - OFF | Dial pointer - OFF
|  | Timing in-progress |  |  | local signalling |  |  |  | - | - | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz
|  | Output is energized |  |  | local signalling |  |  |  | R - ON | R - ON | R - ON | R - ON | Yellow LED | Yellow LED
|  | Output is de-energized |  |  | local signalling |  |  |  | R - OFF | R - OFF | R - OFF | R - OFF | Yellow LED | Yellow LED
|  | Range Setting Changes |  |  | local signalling |  |  |  | - | - | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
Special Features
True RMS | [8 empty] | - | - | - | -
Backlight Indicator | [8 empty] | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product
Diagnostic Button |  |  |  |  | diagnostic button | Published |  |  | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated
Pre-Alarm Output | [8 empty] | - | - | - | -
Output | [8 empty] | 1) Output is energized/ de-energized according to function diagram 2) When input monitored @ fault condition, output is always de-energized | 1) Output is energized/ de-energized according to function diagram 2) When input monitored @ fault condition, output is always de-energized | 1) Output is energized/ de-energized according to function diagram 2) When input monitored @ fault condition, output is always de-energized | 1) Output is energized/ de-energized according to function diagram 2) When input monitored @ fault condition, output is always de-energized
Reliability Data
Reliability Data |  | MTTF |  |  | safety reliability data | Published |  |  | 1,100,000 hours | 1,100,000 hours | 1,600,000 hours | 1,600,000 hours
|  | B10 |  |  | safety reliability data | Published |  |  | 120,000 hours | 120,000 hours | 170,000 hours | 170,000 hours
|  | MTTFd | [6 empty] | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product)
|  | B10d | [6 empty] | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product)
Drawing / Diagram

## RM35HZ Spec
Main Parameters | Category | Sub Parameters | Conforming to | Remark | Standardized Datasheet Param | Selected for Publication | Old Datasheet | Unit | RM35HZ21FM
Standard
Product standard |  |  |  | Common C_Rly Spec | standards | Published | Published |  | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
Product certifications |  |  |  | Common C_Rly Spec | product certifications | Published | Published |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
Marking |  |  |  | Common C_Rly Spec | marking | Published |  |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
Low voltage directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/35/EU
EMC directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/30/EU
ROHS directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2011/65/EU
Environment Characteristics
Environmental Condition |  | Climatic category | IEC60721-3-3 | Common C_Rly Spec |  |  |  |  | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation)
|  | Environmental category | Germanisher Lloyd | Common C_Rly Spec |  |  |  |  | Class C
Ambient air temperature around the device |  | Storage |  | Common C_Rly Spec | ambient air temperature for storage | Published | Published | oC | -40oC..+70oC
|  | Operation |  |  | ambient air temperature for operation | Published | Published | oC | -20oC..+60oC @50Hz -20oC..+50oC @60Hz
Relative humidity |  | Damp heat | IEC60068-2-30 | Common C_Rly Spec | relative humidity | Published | Published |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97%
|  | Cyclic Damp Heat Test | IEC60947-5-1 | Common C_Rly Spec |  |  |  |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97%
Vibration resistance |  |  | IEC60068-2-6 | Common C_Rly Spec | vibration resistance | Published | Published |  | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating)
Shock resistance |  |  | IEC60068-2-27 | Common C_Rly Spec | shock resistance | Published | Published |  | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating)
Bump resistance |  |  | IEC60068-2-29 | Common C_Rly Spec | bump resistance |  |  |  | 10gn - 16ms ; 1000 X 6 axis (Non-Operating)
Seismic resistance |  |  | IEC60068-3-3 | Common C_Rly Spec | seismic resistance |  |  |  | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz
IP degree of protection |  | Terminal Block | IEC60529 |  | IP degree of protection | Published | Published |  | IP20
|  | Housing | IEC60529 |  | IP degree of protection | Published | Published |  | IP30
|  | Front Panel | IEC60529 |  | IP degree of protection |  |  |  | IP50 (With Transparent Cover)
Installation Data
Dimension (nominal) |  | Width |  |  | width | Published |  | mm | 35
|  | Height |  |  | height | Published |  | mm | 90
|  | Depth |  |  | depth | Published |  | mm | 72
Weight (without packaging) |  |  |  |  | net weight | Published |  | g | 95
Mounting |  | Without socket | IEC/EN 60715 |  | mounting support | Published | Published |  | On 35 mm DIN rail
|  | With socket | IEC/EN 60715 |  | mounting support |  |  |  | -
Mounting position |  | In relation to normal vertical mounting plane |  | Common C_Rly Spec | mounting position | Published | Published |  | Any position
Minimum distance to adjacent devices |  | Horizontal |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | 1x product height
|  | Vertical |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | 1x product width
Wiring connection (Clamping Capacity) |  | Solid cable without cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14)
|  | Flexible cable with cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16)
|  | Solid cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | -
|  | Flexible cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | -
|  | Tightening torque | IEC60947-1 | Common C_Rly Spec | tightening torque | Published | Published | Nm | 0.6…1 Nm
|  | Cable stripping length |  | Common C_Rly Spec | cable stripping length |  |  | mm | 6mm (Screw Terminal)
Duty time |  |  |  | Common C_Rly Spec | duty time |  |  | % | 1
Electromagnetic Compatibility
Immunity |  | Generic immunity standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-1, IEC 61000-6-2
|  | Electrostatic discharge | IEC61000-4-2 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Contact : 6kV / Air : 8kV)
|  | Radiated RF & electromagnetic field | IEC61000-4-3 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz)
|  | Fast transient / burst | IEC61000-4-4 |  | electromagnetic compatibility | Published |  |  | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz)
|  | Surge | IEC61000-4-5 |  | electromagnetic compatibility | Published |  |  | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV)
|  | Conducted RF disturbance | IEC61000-4-6 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (10Vrms : 0.15MHz to 80MHz)
|  | Power frequency magnetic field | IEC61000-4-8 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level IV (30A/m : continous) (300A/m : 3s)
|  | Voltage dips, short interruption & variations on power line | IEC61000-4-11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz)
|  | 1 MHz oscillation wave | IEC61000-4-18 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV)
|  | DC voltage interruption | IEC61000-4-29 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | -
|  | Low frequency harmonics | IEC61000-4-13 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | -
|  | Conducted low frequency interference (harmonics) | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W
Emission |  | Generic emission standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-3, IEC 61000-6-4
|  | Radiated RF & electromagnetic field (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B
|  | Radiated RF & electromagnetic field (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1
|  | Radiated emission from enclosure port | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2
|  | Conducted RF emission on power line (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B
|  | Conducted RF emission on power line (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1
|  | Conducted emission | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2
Electrical Isolation
Degree of pollution |  |  | IEC60664-1 | Common C_Rly Spec | pollution degree | Published | Published |  | 3
Overvoltage category |  |  | IEC60664-1 | Common C_Rly Spec | overvoltage category | Published | Published |  | 3
Circuit Group | Terminal | Supply |  |  | circuit group | Published |  |  | A1, A2
|  | Input 1 |  |  | circuit group | Published |  |  | -
|  | Input 2 |  |  | circuit group | Published |  |  | -
|  | Input 3 |  |  | circuit group | Published |  |  | -
|  | Output 1 |  |  | circuit group | Published |  |  | 11,12,14
|  | Output 2 |  |  | circuit group | Published |  |  | 21,22,24
| Rated | Supply | [6 empty] | 120…277 AC/DC
| Voltage | Input 1 | [6 empty] | -
| Spec | Input 2 | [6 empty] | -
|  | Input 3 | [6 empty] | -
|  | Output 1 | [6 empty] | 250V
|  | Output 2 | [6 empty] | 250V
Rated Insulation Voltage |  | Supply | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V
|  | Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V
|  | Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Supply / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V
|  | Supply / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V
|  | Output 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V
|  | Input 1 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 2 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 2 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 3 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 3 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 1 / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
Rated Impulse Voltage |  | Supply | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3
|  | Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Supply / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3
|  | Supply / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3
|  | Output 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3
|  | Input 1 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 2 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 2 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 3 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 3 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 1 / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
Dielectric test voltage |  | Supply / Input 1 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Supply / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Supply / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Supply / Output 1 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min
|  | Supply / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min
|  | Output 1 / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Input 1 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Input 2 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Input 2 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Input 3 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Input 3 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Input 1 / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Input 2 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Input 1 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | -
Insulation resistance |  | Supply / Input 1 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Supply / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Supply / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Supply / Output 1 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC
|  | Supply / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC
|  | Output 1 / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC
|  | Input 1 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Input 1 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Input 2 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Input 2 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Input 3 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Input 3 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Input 1 / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Input 2 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Input 1 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | -
Power Supply Characteristics
Rated supply voltage, Us |  |  |  |  | [Us] rated supply voltage | Published | Published | V | ~ 120…277
Supply voltage operating range |  |  |  |  | supply voltage limits | Published | Published | V | ~ 102…308
Polarity on d.c. supply |  |  |  |  | polarity |  | Published |  | -
Rated frequency |  |  |  |  | supply frequency | Published | Published | Hz | 50 / 60
Frequency operating range |  |  |  |  | supply frequency | Published | Published | Hz | 45…66
Maximum power consumption |  |  |  |  | power consumption | Published | Published |  | 6
Immunity to micro-breakage |  |  |  |  | immunity to microbreaks | Published | Published | ms | 10
Supply terminal |  |  |  |  | supply terminal |  |  |  | A1-A2
On Load Factor |  |  |  | Common C_Rly Spec | on-load factor |  |  | % | 1
Release of input voltage |  |  |  |  | release of input voltage |  |  | V | -
Input Circuit Characteristics
Monitoring functions |  | Over frequency @ 50Hz, With Memory |  |  | monitoring functions |  |  |  | - governed by time delay - status reflects to R1 - fault status will be memorized and only resetable through power cycle
|  | Over frequency @ 50Hz, Without Memory |  |  | monitoring functions |  |  |  | - governed by time delay - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis
|  | Over frequency @ 60Hz, With Memory |  |  | monitoring functions |  |  |  | - governed by time delay - status reflects to R1 - fault status will be memorized and only resetable through power cycle
|  | Over frequency @ 60Hz, Without Memory |  |  | monitoring functions |  |  |  | - governed by time delay - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis
|  | Under frequency @ 50Hz, With Memory |  |  | monitoring functions |  |  |  | - governed by time delay - status reflects to R2 - fault status will be memorized and only resetable through power cycle
|  | Under frequency @ 50Hz, Without Memory |  |  | monitoring functions |  |  |  | - governed by time delay - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis
|  | Under frequency @ 60Hz, With Memory |  |  | monitoring functions |  |  |  | - governed by time delay - status reflects to R2 - fault status will be memorized and only resetable through power cycle
|  | Under frequency @ 60Hz, Without Memory |  |  | monitoring functions |  |  |  | - governed by time delay - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis
Monitoring function characteristics |  | Measurement mode | [6 empty] | Resistive Voltage Step Down
|  | Internal input resistance |  |  | internal input resistance |  |  | W | -
|  | Input terminal |  |  | input terminal |  |  |  | A1-A2
|  | Input nominal frequency selection |  |  | Input nominal frequency selection |  |  | Hz | 50, 60
|  | permissible input overload |  |  | permissible input overload |  |  | Hz | 70
|  | Rated frequency |  |  | input frequency |  |  | Hz | 50 / 60
|  | Frequency operating range |  |  | input frequency |  |  | Hz | 40…70
|  | Setting accuracy |  |  | setting accuracy of the switching threshold |  |  | % | ± 10 % of the full scale value
|  | Repeat accuracy (constant parameters) |  |  | repeat accuracy of the switching threshold |  |  | % | +/- 0.5%
|  | Measurement method |  |  | measurement method |  |  |  | -
|  | Measurement error with supply voltage variation |  |  | switching threshold drift |  |  | %/V | < 1% of selected Un
|  | Measurement error with temperature variation |  |  | switching threshold drift |  |  | %/oC | < 0.05% / oC
|  | Maximum measuring cycles |  |  | maximum measuring cycle |  |  |  | 200ms / measurement as true rms value
Measurement range |  | Over frequency @ 50Hz, With Memory |  |  | measurement range |  |  | Hz | 40...70
|  | Over frequency @ 50Hz, Without Memory |  |  | measurement range |  |  | Hz | same as above
|  | Over frequency @ 60Hz, With Memory |  |  | measurement range |  |  | Hz | same as above
|  | Over frequency @ 60Hz, Without Memory |  |  | measurement range |  |  | Hz | same as above
|  | Under frequency @ 50Hz, With Memory |  |  | measurement range |  |  | Hz | same as above
|  | Under frequency @ 50Hz, Without Memory |  |  | measurement range |  |  | Hz | same as above
|  | Under frequency @ 60Hz, With Memory |  |  | measurement range |  |  | Hz | same as above
|  | Under frequency @ 60Hz, Without Memory |  |  | measurement range |  |  | Hz | same as above
Tripping threshold |  | Over frequency @ 50Hz, With Memory |  |  | tripping threshold |  |  | Hz | Adjustable -1 Hz…5 Hz for x1 scale Adjustable -2 Hz…10 Hz for x2 scale
|  | Over frequency @ 50Hz, Without Memory |  |  | tripping threshold |  |  | Hz | same as above
|  | Over frequency @ 60Hz, With Memory |  |  | tripping threshold |  |  | Hz | same as above
|  | Over frequency @ 60Hz, Without Memory |  |  | tripping threshold |  |  | Hz | same as above
|  | Under frequency @ 50Hz, With Memory |  |  | tripping threshold |  |  | Hz | Adjustable -5 Hz…1 Hz for x1 scale Adjustable -10 Hz…2 Hz for x2 scale
|  | Under frequency @ 50Hz, Without Memory |  |  | tripping threshold |  |  | Hz | same as above
|  | Under frequency @ 60Hz, With Memory |  |  | tripping threshold |  |  | Hz | same as above
|  | Under frequency @ 60Hz, Without Memory |  |  | tripping threshold |  |  | Hz | same as above
Hysteresis |  | Over frequency @ 50Hz, With Memory |  |  | hysteresis |  |  | Hz | Fixed +/- 0.3Hz Internal design spec: Fixed +/- 0.2Hz
|  | Over frequency @ 50Hz, Without Memory |  |  | hysteresis |  |  | Hz | same as above
|  | Over frequency @ 60Hz, With Memory |  |  | hysteresis |  |  | Hz | same as above
|  | Over frequency @ 60Hz, Without Memory |  |  | hysteresis |  |  | Hz | same as above
|  | Under frequency @ 50Hz, With Memory |  |  | hysteresis |  |  | Hz | same as above
|  | Under frequency @ 50Hz, Without Memory |  |  | hysteresis |  |  | Hz | same as above
|  | Under frequency @ 60Hz, With Memory |  |  | hysteresis |  |  | Hz | same as above
|  | Under frequency @ 60Hz, Without Memory |  |  | hysteresis |  |  | Hz | same as above
Output Circuit Characteristics
Type of output |  |  |  |  | output type | Published | Published |  | 2 x C/O relay contacts
Output terminal |  |  |  |  | output terminal |  |  |  | 15-16-18, 25-26-28
Operation principle |  | R1 (11-12-14) |  |  | output logic |  |  |  | Energized on fault-free
|  | R2 (21-22-24) |  |  | output logic |  |  |  | Energized on fault-free
Contact material |  |  |  | Common C_Rly Spec | contacts material | Published | Published |  | Cadmium free
Mechanical durability |  |  | IEC61810-1 | Common C_Rly Spec | mechanical durability | Published | Published | Cyc | 10 x 106 cycles
Electrical durability |  | AC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles
|  | DC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/5A, 100k cycles
|  | AC-15 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/0.15A, 100k cycles
|  | DC-13 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/1A, 100k cycles
Rated capacity |  | Rated switching voltage | IEC61810-1 | Common C_Rly Spec | [Ue] rated operational voltage | Published |  | V | 250V
|  | Rated switching current | IEC61810-1 | Common C_Rly Spec | [Ie] rated operational current | Published | Published | A | 8A
Maximum switching capacity |  | Maximum switching voltage |  | Common C_Rly Spec | maximum switching capacity | Published | Published | V | 250V
|  | Maximum switching current |  | Common C_Rly Spec | maximum switching capacity | Published | Published | A | 8A
|  | Maximum switching capacity |  | Common C_Rly Spec | maximum switching capacity | Published | Published | VA | -
Minimum switching capacity |  | Minimum switching voltage | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | V | -
|  | Minimum switching current | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | mA | -
|  | Minimum switching capacity | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published | Published | mW | NO: 12V/10mA, MCTF > 80,000,000
Maximum voltage drop at terminals |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum voltage drop |  |  | V | -
Leakage current |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum leakage current |  |  | mA | -
Thermal Current |  |  | IEC60947-5-1 | Common C_Rly Spec | thermal current |  |  | A | 8A
Short circuit protection |  | Relay Output by external fuse | IEC60947-5-1 | Common C_Rly Spec | short circuit protection |  |  | gG | 8A
|  | Solid State Output by external fuse | IEC62314 | Common C_Rly Spec | short circuit protection |  |  | gG | -
Time Delay Characteristics
Time delay functions |  | "OFF" delay |  |  | time delay type | Published |  |  | Yes
|  | "ON" delay |  |  | time delay type | Published |  |  | -
|  | Inhibition |  |  | time delay type | Published |  |  | -
Timing delay range |  | "OFF" delay |  |  | time delay range | Published | Published | s | Adjustable 0.1…10
|  | "ON" delay |  |  | time delay range | Published |  | s | -
|  | Inhibition |  |  | time delay range | Published | Published | s | -
Response time |  | on crossing the threshold (all monitoring functions) |  |  | response time | Published | Published | ms | TBD
|  | on crossing the hysteresis (all monitoring functions) |  | Reserved for other products | response time | Published |  |  | -
|  | on crossing the threshold (specific monitoring functions 1) |  | Reserved for other products | response time | Published |  |  | -
|  | on crossing the threshold (specific monitoring functions 2) |  | Reserved for other products | response time | Published |  |  | -
|  | on crossing the threshold (specific monitoring functions 3) |  | Reserved for other products | response time | Published |  |  | -
Time delay of pick-up |  |  |  |  | power on delay | Published | Published | ms | 0
Reset time |  | through Un power reset |  |  | reset time | Published | Published | ms | 0
|  | through front panel reset |  | Reserved for other products | reset time | Published |  |  | -
|  | through input control reset |  | Reserved for other products | reset time | Published |  |  | -
Setting accuracy |  |  |  | Common C_Rly Spec | setting accuracy of time delay | Published | Published | % | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
Repeat accuracy (constant parameters) |  |  |  | Common C_Rly Spec | repeat accuracy of time delay | Published |  | % | +/- 0.5%
Timing error with supply voltage variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/V | -
Timing error with temperature variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/oC | -
LED Indication
status LED |  |  |  |  | status LED |  |  |  | Un (Green) R1 (Amber) R2 (Amber)
local signalling |  | Power supply availability |  |  | local signalling |  |  |  | Un - ON
|  | Power supply not availability |  |  | local signalling |  |  |  | Un - OFF
|  | Timing in-progress |  |  | local signalling |  |  |  | Rx - Slow Blink (50% ON; 50% OFF) @ 1Hz
|  | Output is energized |  |  | local signalling |  |  |  | Rx - ON
|  | Output is de-energized |  |  | local signalling |  |  |  | Rx - OFF
|  | Range Setting Changes |  |  | local signalling |  |  |  | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
Special Features
True RMS | [8 empty] | -
Backlight Indicator | [8 empty] | -
Diagnostic Button |  |  |  |  | diagnostic button | Published |  |  | -
Pre-Alarm Output | [8 empty] | -
Output | [8 empty] | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
Reliability Data
Reliability Data |  | MTTF |  |  | safety reliability data | Published |  |  | TBD
|  | B10 |  |  | safety reliability data | Published |  |  | TBD
|  | MTTFd | [6 empty] | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product)
|  | B10d | [6 empty] | Cannot declare B10 = B10d (Note: customer confuses as safety product)
Drawing / Diagram

## RM35TM Spec
Main Parameters | Category | Sub Parameters | Conforming to | Remark | Standardized Datasheet Param | Selected for Publication | Old Datasheet | Unit | RM35TM250MW | RM35TM50MW
Standard
Product standard |  |  |  | Common C_Rly Spec | standards | Published | Published |  | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
Product certifications |  |  |  | Common C_Rly Spec | product certifications | Published | Published |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
Marking |  |  |  | Common C_Rly Spec | marking | Published |  |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
Low voltage directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/35/EU | 2014/35/EU
EMC directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/30/EU | 2014/30/EU
ROHS directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2011/65/EU | 2011/65/EU
Environment Characteristics
Environmental Condition |  | Climatic category | IEC60721-3-3 | Common C_Rly Spec |  |  |  |  | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation)
|  | Environmental category | Germanisher Lloyd | Common C_Rly Spec |  |  |  |  | Class C | Class C
Ambient air temperature around the device |  | Storage |  | Common C_Rly Spec | ambient air temperature for storage | Published | Published | oC | -40oC..+70oC | -40oC..+70oC
|  | Operation |  |  | ambient air temperature for operation | Published | Published | oC | -20oC..+60oC @50Hz -20oC..+50oC @60Hz | -20oC..+60oC @50Hz -20oC..+50oC @60Hz
Relative humidity |  | Damp heat | IEC60068-2-30 | Common C_Rly Spec | relative humidity | Published | Published |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97%
|  | Cyclic Damp Heat Test | IEC60947-5-1 | Common C_Rly Spec |  |  |  |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97%
Vibration resistance |  |  | IEC60068-2-6 | Common C_Rly Spec | vibration resistance | Published | Published |  | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating)
Shock resistance |  |  | IEC60068-2-27 | Common C_Rly Spec | shock resistance | Published | Published |  | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating)
Bump resistance |  |  | IEC60068-2-29 | Common C_Rly Spec | bump resistance |  |  |  | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating)
Seismic resistance |  |  | IEC60068-3-3 | Common C_Rly Spec | seismic resistance |  |  |  | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz
IP degree of protection |  | Terminal Block | IEC60529 |  | IP degree of protection | Published | Published |  | IP20 | IP20
|  | Housing | IEC60529 |  | IP degree of protection | Published | Published |  | IP30 | IP30
|  | Front Panel | IEC60529 |  | IP degree of protection |  |  |  | IP50 (With Transparent Cover) | IP50 (With Transparent Cover)
Installation Data
Dimension (nominal) |  | Width |  |  | width | Published |  | mm | 35 | 35
|  | Height |  |  | height | Published |  | mm | 90 | 90
|  | Depth |  |  | depth | Published |  | mm | 72 | 72
Weight (without packaging) |  |  |  |  | net weight | Published |  | g | 95 | 95
Mounting |  | Without socket | IEC/EN 60715 |  | mounting support | Published | Published |  | On 35 mm DIN rail | On 35 mm DIN rail
|  | With socket | IEC/EN 60715 |  | mounting support |  |  |  | - | -
Mounting position |  | In relation to normal vertical mounting plane |  | Common C_Rly Spec | mounting position | Published | Published |  | Any position | Any position
Minimum distance to adjacent devices |  | Horizontal |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | 1x product height | 1x product height
|  | Vertical |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | 1x product width | 1x product width
Wiring connection (Clamping Capacity) |  | Solid cable without cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14)
|  | Flexible cable with cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16)
|  | Solid cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | -
|  | Flexible cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | -
|  | Tightening torque | IEC60947-1 | Common C_Rly Spec | tightening torque | Published | Published | Nm | 0.6…1 Nm | 0.6…1 Nm
|  | Cable stripping length |  | Common C_Rly Spec | cable stripping length |  |  | mm | 6mm (Screw Terminal) | 6mm (Screw Terminal)
Duty time |  |  |  | Common C_Rly Spec | duty time |  |  | % | 1 | 1
Electromagnetic Compatibility
Immunity |  | Generic immunity standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2
|  | Electrostatic discharge | IEC61000-4-2 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV)
|  | Radiated RF & electromagnetic field | IEC61000-4-3 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz)
|  | Fast transient / burst | IEC61000-4-4 |  | electromagnetic compatibility | Published |  |  | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz)
|  | Surge | IEC61000-4-5 |  | electromagnetic compatibility | Published |  |  | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV)
|  | Conducted RF disturbance | IEC61000-4-6 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (10Vrms : 0.15MHz to 80MHz) | Level III (10Vrms : 0.15MHz to 80MHz)
|  | Power frequency magnetic field | IEC61000-4-8 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s)
|  | Voltage dips, short interruption & variations on power line | IEC61000-4-11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz)
|  | 1 MHz oscillation wave | IEC61000-4-18 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV)
|  | DC voltage interruption | IEC61000-4-29 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | -
|  | Low frequency harmonics | IEC61000-4-13 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | -
|  | Conducted low frequency interference (harmonics) | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W
Emission |  | Generic emission standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4
|  | Radiated RF & electromagnetic field (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B
|  | Radiated RF & electromagnetic field (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1
|  | Radiated emission from enclosure port | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2
|  | Conducted RF emission on power line (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B
|  | Conducted RF emission on power line (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1
|  | Conducted emission | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2
Electrical Isolation
Degree of pollution |  |  | IEC60664-1 | Common C_Rly Spec | pollution degree | Published | Published |  | 3 | 3
Overvoltage category |  |  | IEC60664-1 | Common C_Rly Spec | overvoltage category | Published | Published |  | 3 | 3
Circuit Group | Terminal | Supply |  |  | circuit group | Published |  |  | A1, A2 | A1, A2
|  | Input 1 |  |  | circuit group | Published |  |  | T1, T2 | T1, T2
|  | Input 2 |  |  | circuit group | Published |  |  | Y1 | -
|  | Input 3 |  |  | circuit group | Published |  |  | L1, L2, L3 | L1, L2, L3
|  | Output 1 |  |  | circuit group | Published |  |  | 11,12,14 | 11,12,14
|  | Output 2 |  |  | circuit group | Published |  |  | 21,22,24 | 21,22,24
| Rated | Supply | [6 empty] | 24…240 AC/DC | 24…240 AC/DC
| Voltage | Input 1 | [6 empty] | PTC probe | PTC probe
| Spec | Input 2 | [6 empty] | Push Button Switch | Push Button Switch
|  | Input 3 | [6 empty] | 208..480 AC/DC | 208..480 AC/DC
|  | Output 1 | [6 empty] | 250V | 250V
|  | Output 2 | [6 empty] | 250V | 250V
Rated Insulation Voltage |  | Supply | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V
|  | Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 10V | 10V
|  | Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 10V | -
|  | Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | 500V
|  | Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V
|  | Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | 500V
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | -
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | 500V
|  | Supply / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V
|  | Supply / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V
|  | Output 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V
|  | Input 1 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | 500V
|  | Input 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | 500V
|  | Input 2 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | -
|  | Input 2 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | -
|  | Input 3 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | 500V
|  | Input 3 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | 500V
|  | Input 1 / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | -
Rated Impulse Voltage |  | Supply | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | -
|  | Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | -
|  | Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | -
|  | Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | -
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | -
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Supply / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Supply / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Output 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Input 2 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | -
|  | Input 2 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | -
|  | Input 3 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Input 3 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | -
Dielectric test voltage |  | Supply / Input 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Supply / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | -
|  | Supply / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Supply / Output 1 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Supply / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Output 1 / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 2 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | -
|  | Input 2 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | -
|  | Input 3 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 3 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | -
|  | Input 2 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | -
|  | Input 1 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | -
Insulation resistance |  | Supply / Input 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | -
|  | Supply / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Output 1 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Output 1 / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 2 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | -
|  | Input 2 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | -
|  | Input 3 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 3 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | -
|  | Input 2 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | -
|  | Input 1 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | -
Power Supply Characteristics
Rated supply voltage, Us |  |  |  |  | [Us] rated supply voltage | Published | Published | V | ~/-- 24…240 | ~/-- 24…240
Supply voltage operating range |  |  |  |  | supply voltage limits | Published | Published | V | ~/-- 20.4…264 | ~/-- 20.4…264
Polarity on d.c. supply |  |  |  |  | polarity |  | Published |  | No | No
Rated frequency |  |  |  |  | supply frequency | Published | Published | Hz | 50 / 60 | 50 / 60
Frequency operating range |  |  |  |  | supply frequency | Published | Published | Hz | 45…66 | 45…66
Maximum power consumption |  |  |  |  | power consumption | Published | Published |  | 1 4 VA / 2 0.5 W | 1 4 VA / 2 0.5 W
Immunity to micro-breakage |  |  |  |  | immunity to microbreaks | Published | Published | ms | 20 ms at 20.4 V | 20 ms at 20.4 V
Supply terminal |  |  |  |  | supply terminal |  |  |  | A1-A2 | A1-A2
On Load Factor |  |  |  | Common C_Rly Spec | on-load factor |  |  | % | 1 | 1
Release of input voltage |  |  |  |  | release of input voltage |  |  | V | - | -
Input Circuit Characteristics
Monitoring functions |  | Motor temperature through PTC sensor, With Memory |  |  | monitoring functions |  |  |  | - governed by response time only - status reflects to R1 - fault status will be memorized and only resetable through power cycle, Test/Reset button or Y1-T1 volt-free input | -
|  | Motor temperature through PTC sensor, Without Memory |  |  | monitoring functions |  |  |  | - governed by response time only - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis | - governed by response time only - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis
|  | Short circuit of PTC sensor |  |  | monitoring functions |  |  |  | - governed by response time only - status reflects to R1 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis | - governed by response time only - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis
|  | Phase lost |  |  | monitoring functions |  |  |  | - governed by response time only, - status reflects to R2 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis | - governed by response time only, - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis
|  | Phase sequence |  |  | monitoring functions |  |  |  | - governed by response time only, - status reflects to R2 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis | - governed by response time only, - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis
|  | Voltage Regeneration |  |  | monitoring functions |  |  |  | - governed by response time only, - status reflects to R2 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis | - governed by response time only, - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis
|  | Extreme undervoltage (Phase loss) |  |  | monitoring functions |  |  |  | - governed by response time only, - status reflects to R2 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis | - governed by response time only, - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis
Monitoring function characteristics | Motor temperature | Input terminal |  |  | input terminal |  |  |  | T1-T2 | T1-T2
|  | Maximum voltage of temperature control circuit |  |  | Maximum voltage of temperature control circuit |  |  | V | 3.6V when T1-T2 is open | 3.6V when T1-T2 is open
|  | Temperature sensing circuit short-circuit current |  |  | Temperature sensing circuit short-circuit current |  |  | mA | 7mA when T1-T2 is short-circuited | 7mA when T1-T2 is short-circuited
|  | Maximum resistance of temperature sensor at 20°C |  |  | Maximum resistance of temperature sensor at 20°C |  |  | W | 1500Ω | 1500Ω
| 3 Phase | Measurement mode |  |  | input frequency |  |  |  | Resistive Voltage Step Down | Resistive Voltage Step Down
|  | Internal input resistance |  |  | setting accuracy of the switching threshold |  |  | kW | 602/line | 602/line
|  | Input terminal |  |  | repeat accuracy of the switching threshold |  |  |  | L1-L2-L3 | L1-L2-L3
|  | Input nominal voltage selection |  |  | measurement method |  |  |  | - | -
|  | permissible input overload |  |  | switching threshold drift |  |  | V | ~ 3 x 176…3 x 528 | ~ 3 x 176…3 x 528
|  | Rated frequency |  |  | switching threshold drift |  |  | Hz | 50 / 60 | 50 / 60
|  | Frequency operating range |  |  | maximum measuring cycle |  |  | Hz | 45…66 | 45…66
Measurement range |  | Motor temperature through PTC sensor | IEC60034-11 |  | measurement range |  |  |  | Mark A probe characteristics | Mark A probe characteristics
|  | Short circuit of PTC sensor |  |  | measurement range |  |  | V | ~ 3 x 208…3 x 480 | ~ 3 x 208…3 x 480
|  | Phase lost |  |  | measurement range |  |  |  | same as above | same as above
|  | Phase sequence |  |  | measurement range |  |  |  | same as above | same as above
|  | Voltage Regeneration |  |  | measurement range |  |  |  | same as above | same as above
Tripping threshold |  | Motor temperature through PTC sensor |  |  | tripping threshold |  |  | W | 3100 ± 10 % Internal design spec: TBD | 3100 ± 10 % Internal design spec: TBD
|  | Short circuit of PTC sensor |  |  | tripping threshold |  |  | W | 0…15 ± 5 Internal design spec: TBD | 0…15 ± 5 Internal design spec: TBD
|  | Phase lost |  |  | tripping threshold |  |  |  | 1 or more phase cut | 1 or more phase cut
|  | Phase sequence |  |  | tripping threshold |  |  |  | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Total swap of phase Internal design spec: L23 lags L13 >= 180o
|  | Voltage Regeneration |  |  | tripping threshold |  |  | % | 1 or more phase =< 30% * [(L21 + L31 + L32) / 3] Internal design spec: TBD | 1 or more phase =< 30% * [(L21 + L31 + L32) / 3] Internal design spec: TBD
|  | Extreme undervoltage (Phase loss) |  |  | tripping threshold |  |  |  | Internal design spec: TBD | Internal design spec: TBD
Hysteresis |  | Motor temperature through PTC sensor |  |  | hysteresis |  |  | W | 1650 ± 10 % Internal design spec: TBD | 1650 ± 10 % Internal design spec: TBD
|  | Short circuit of PTC sensor |  |  | hysteresis |  |  | W | Internal design spec: TBD | Internal design spec: TBD
|  | Phase lost |  |  | hysteresis |  |  |  | All phase cut recover | All phase cut recover
|  | Phase sequence |  |  | hysteresis |  |  |  | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Total phase swap recover Internal design spec: L23 lags L13 < 180o
|  | Voltage Regeneration |  |  | hysteresis |  |  | % | Internal design spec: TBD | Internal design spec: TBD
|  | Extreme undervoltage (Phase loss) |  |  | hysteresis |  |  |  | Internal design spec: TBD | Internal design spec: TBD
Output Circuit Characteristics
Type of output |  |  |  |  | output type | Published | Published |  | 2 x C/O relay contacts | 2 x C/O relay contacts
Output terminal |  |  |  |  | output terminal |  |  |  | 15-16-18, 25-26-28 | 15-16-18, 25-26-28
Operation principle |  | R1 (11-12-14) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free
|  | R2 (21-22-24) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free
Contact material |  |  |  | Common C_Rly Spec | contacts material | Published | Published |  | Cadmium free | Cadmium free
Mechanical durability |  |  | IEC61810-1 | Common C_Rly Spec | mechanical durability | Published | Published | Cyc | 10 x 106 cycles | 10 x 106 cycles
Electrical durability |  | AC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles
|  | DC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles
|  | AC-15 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles
|  | DC-13 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles
Rated capacity |  | Rated switching voltage | IEC61810-1 | Common C_Rly Spec | [Ue] rated operational voltage | Published |  | V | 250V | 250V
|  | Rated switching current | IEC61810-1 | Common C_Rly Spec | [Ie] rated operational current | Published | Published | A | 8A | 8A
Maximum switching capacity |  | Maximum switching voltage |  | Common C_Rly Spec | maximum switching capacity | Published | Published | V | 250V | 250V
|  | Maximum switching current |  | Common C_Rly Spec | maximum switching capacity | Published | Published | A | 8A | 8A
|  | Maximum switching capacity |  | Common C_Rly Spec | maximum switching capacity | Published | Published | VA | - | -
Minimum switching capacity |  | Minimum switching voltage | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | V | - | -
|  | Minimum switching current | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | mA | - | -
|  | Minimum switching capacity | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published | Published | mW | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000
Maximum voltage drop at terminals |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum voltage drop |  |  | V | - | -
Leakage current |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum leakage current |  |  | mA | - | -
Thermal Current |  |  | IEC60947-5-1 | Common C_Rly Spec | thermal current |  |  | A | 8A | 8A
Short circuit protection |  | Relay Output by external fuse | IEC60947-5-1 | Common C_Rly Spec | short circuit protection |  |  | gG | 8A | 8A
|  | Solid State Output by external fuse | IEC62314 | Common C_Rly Spec | short circuit protection |  |  | gG | - | -
Time Delay Characteristics
Time delay functions |  | "OFF" delay |  |  | time delay type | Published |  |  | - | -
|  | "ON" delay |  |  | time delay type | Published |  |  | - | -
|  | Inhibition |  |  | time delay type | Published |  |  | - | -
Timing delay range |  | "OFF" delay |  |  | time delay range | Published | Published | s | - | -
|  | "ON" delay |  |  | time delay range | Published |  | s | - | -
|  | Inhibition |  |  | time delay range | Published | Published | s | - | -
Response time |  | on crossing the threshold (Motor Temperature) |  |  | response time | Published | Published | ms | 300 | 300
|  | on crossing the hysteresis (all 3 Phase functions) |  | Reserved for other products | response time | Published |  | ms | 300 | 300
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
Time delay of pick-up |  |  |  |  | power on delay | Published | Published | ms | 500 | 500
Reset time |  | through Un power reset |  |  | reset time | Published | Published | ms | 10 000 | 10 000
|  | through front panel reset |  | Reserved for other products | reset time | Published |  | ms | >= 50 (press to release) | -
|  | through input control reset |  | Reserved for other products | reset time | Published |  | ms | >= 50 (Y1 short to T1) | -
Setting accuracy |  |  |  | Common C_Rly Spec | setting accuracy of time delay | Published | Published | % | - | -
Repeat accuracy (constant parameters) |  |  |  | Common C_Rly Spec | repeat accuracy of time delay | Published |  | % | - | -
Timing error with supply voltage variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/V | - | -
Timing error with temperature variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/oC | - | -
LED Indication
status LED |  |  |  |  | status LED |  |  |  | Un (Green) R1 (Amber) R2 (Amber) | Un (Green) R1 (Amber) R2 (Amber)
local signalling |  | Power supply availability |  |  | local signalling |  |  |  | Un - ON | Un - ON
|  | Power supply not availability |  |  | local signalling |  |  |  | Un - OFF | Un - OFF
|  | Timing in-progress |  |  | local signalling |  |  |  | - | -
|  | Output is energized |  |  | local signalling |  |  |  | Rx - ON | Rx - ON
|  | Output is de-energized |  |  | local signalling |  |  |  | Rx - OFF | Rx - OFF
|  | Range Setting Changes |  |  | local signalling |  |  |  | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | -
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
Special Features
Test / Reset button | [8 empty] | 1) When Set to "No Memory" 1a) When motor temperature is normal, - pressing the "Test/Reset" button simulates overheating, R1 is de-energized - R1 will remain energized as long as "Test/Reset" button remains pressed 1b) When motor temperature is abnormal, - pressing the "Test/Reset" button will not change any product status 2) When Set to "Memory" 2a) When motor temperature is normal, - pressing the "Test/Reset" button simulates overheating, R1 is de-energized - R1 will remain energized as long as "Test/Reset" button remains pressed 2b) When motor temperature is abnormal, - pressing the "Test/Reset" button will not change any product status 2c) When motor temperature is abnormal at first and recover to normal - pressing the "Test/Reset" button will reset the fault, R1 is energized | -
Y1-T1 voltage free contact | [8 empty] | 1) Same function as per Test / Reset button 2) Short Y1 to T1 is the same meaning as pressing "Test/Reset" button 3) Open Y1 to T1 is the same meaning as releasing "Test/Reset" button | -
Diagnostic Button |  |  |  |  | diagnostic button | Published |  |  | - | -
Pre-Alarm Output | [8 empty] | - | -
Output | [8 empty] | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
Reliability Data
Reliability Data |  | MTTF |  |  | safety reliability data | Published |  |  | TBD | TBD
|  | B10 |  |  | safety reliability data | Published |  |  | TBD | TBD
|  | MTTFd | [6 empty] | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product)
|  | B10d | [6 empty] | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product)
Drawing / Diagram

## 1P Voltage Control Spec
Main Parameters | Category | Sub Parameters | Conforming to | Remark | Standardized Datasheet Param | Selected for Publication | Old Datasheet | Unit | RM22UA21MR | RM22UA22MR | RM22UA23MR | RM22UA31MR | RM22UA32MR | RM22UA33MR | RM22UA33MT | RM22UB34 | col17 | col18 | col19 | Competitor Spec Reference | RM35UA11MW | RM35UA12MW | RM35UA13MW | RM22UA3 (Catch Up) | RM4UA3 | RM4UA0
Standard
Product standard |  |  |  | Common C_Rly Spec | standards | Published | Published |  | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 |  |  |  |  | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6
Product certifications |  |  |  | Common C_Rly Spec | product certifications | Published | Published |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS |  |  |  |  | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST
Marking |  |  |  | Common C_Rly Spec | marking | Published |  |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS |  |  |  |  | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE
Low voltage directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU |  |  |  |  | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC
EMC directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU |  |  |  |  | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC
ROHS directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU |  |  |  |  | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC
Environment Characteristics
Environmental Condition |  | Climatic category | IEC60721-3-3 | Common C_Rly Spec |  |  |  |  | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) |  |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | Environmental category | Germanisher Lloyd | Common C_Rly Spec |  |  |  |  | Class C | Class C | Class C | Class C | Class C | Class C | Class C | Class C
Ambient air temperature around the device |  | Storage |  | Common C_Rly Spec | ambient air temperature for storage | Published | Published | oC | -40oC..+80oC | -40oC..+80oC | -40oC..+80oC | -40oC..+80oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC |  |  |  |  | -40…+70 | -40…+70 | -40…+70 | -40…+70 | Not specified | Not specified
|  | Operation |  |  | ambient air temperature for operation | Published | Published | oC | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) |  |  |  |  | -20…+50 | -20…+50 | -20…+50 | -20…+50 | Not specified | Not specified
Relative humidity |  | Damp heat | IEC60068-2-30 | Common C_Rly Spec | relative humidity | Published | Published |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% |  |  |  |  | 2 cycles 24h ;+25°C +55°C 95%HR | 2 cycles 24h ;+25°C +55°C 95%HR | 2 cycles 24h ;+25°C +55°C 95%HR | 2 cycles 24h ;+25°C +55°C 95%HR | Not specified | Not specified
|  | Cyclic Damp Heat Test | IEC60947-5-1 | Common C_Rly Spec |  |  |  |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97%
Vibration resistance |  |  | IEC60068-2-6 | Common C_Rly Spec | vibration resistance | Published | Published |  | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) |  |  |  |  | 0.035mm from 10Hz…150Hz | 0.035mm from 10Hz…150Hz | 0.035mm from 10Hz…150Hz | 0.035mm from 10Hz…150Hz | Not specified | Not specified
Shock resistance |  |  | IEC60068-2-27 | Common C_Rly Spec | shock resistance | Published | Published |  | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) |  |  |  |  | 5 gn | 5 gn | 5 gn | 5 gn | Not specified | Not specified
Bump resistance |  |  | IEC60068-2-29 | Common C_Rly Spec | bump resistance |  |  |  | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating)
Seismic resistance |  |  | IEC60068-3-3 | Common C_Rly Spec | seismic resistance |  |  |  | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz
IP degree of protection |  | Terminal Block | IEC60529 |  | IP degree of protection | Published | Published |  | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 |  |  |  |  | IP20 | IP20 | IP20 | IP20 | Not specified | Not specified
|  | Housing | IEC60529 |  | IP degree of protection | Published | Published |  | IP40 | IP40 | IP40 | IP40 | IP40 | IP40 | IP40 | IP40 |  |  |  |  | IP30 | IP30 | IP30 | IP30 | Not specified | Not specified
|  | Front Panel | IEC60529 |  | IP degree of protection |  |  |  | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover)
Installation Data
Dimension (nominal) |  | Width |  |  | width | Published |  | mm | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 |  |  |  |  | 35 x 90 x 72 | 35 x 90 x 72 | 35 x 90 x 72 | 22.5 x ? x ? | 22.5 x 78 x 80 | 22.5 x 78 x 80
|  | Height |  |  | height | Published |  | mm
|  | Depth |  |  | depth | Published |  | mm
Weight (without packaging) |  |  |  |  | net weight | Published |  | g | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 90 |  |  |  |  | 130 | 130 | 130 | ? | 168 | 168
Mounting |  | Without socket | IEC/EN 60715 |  | mounting support | Published | Published |  | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail |  |  |  |  | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail
|  | With socket | IEC/EN 60715 |  | mounting support |  |  |  | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | -
Mounting position |  | In relation to normal vertical mounting plane |  | Common C_Rly Spec | mounting position | Published | Published |  | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position |  |  |  |  | Any position | Any position | Any position | Any position | Not specified | Not specified
Minimum distance to adjacent devices |  | Horizontal |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified |  |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | Vertical |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified |  |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Wiring connection (Clamping Capacity) |  | Solid cable without cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) |  |  |  |  | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | Not specified | Not specified
|  | Flexible cable with cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) |  |  |  |  | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | Not specified | Not specified
|  | Solid cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | -
|  | Flexible cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | -
|  | Tightening torque | IEC60947-1 | Common C_Rly Spec | tightening torque | Published | Published | Nm | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 |  |  |  |  | 0.6…1 | 0.6…1 | 0.6…1 | 0.6…1 | Not specified | Not specified
|  | Cable stripping length |  | Common C_Rly Spec | cable stripping length |  |  | mm | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) |  |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Duty time |  |  |  | Common C_Rly Spec | duty time |  |  | % | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Electromagnetic Compatibility
Immunity |  | Generic immunity standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 |  |  |  |  | IEC61000-6-2 | IEC61000-6-2 | IEC61000-6-2 | IEC61000-6-2 | IEC50082-2 | IEC50082-2
|  | Electrostatic discharge | IEC61000-4-2 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) |  |  |  |  | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV)
|  | Radiated RF & electromagnetic field | IEC61000-4-3 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) |  |  |  |  | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m)
|  | Fast transient / burst | IEC61000-4-4 |  | electromagnetic compatibility | Published |  |  | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) |  |  |  |  | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct)
|  | Surge | IEC61000-4-5 |  | electromagnetic compatibility | Published |  |  | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) |  |  |  |  | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase)
|  | Conducted RF disturbance | IEC61000-4-6 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) |  |  |  |  | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V)
|  | Power frequency magnetic field | IEC61000-4-8 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s)
|  | Voltage dips, short interruption & variations on power line | IEC61000-4-11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | - | - | - | - | - | - | - |  |  |  |  | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us)
|  | 1 MHz oscillation wave | IEC61000-4-18 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV)
|  | DC voltage interruption | IEC61000-4-29 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms
|  | Low frequency harmonics | IEC61000-4-13 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | - | - | - | - | - | - | - |  |  |  |  | Not tested | Not tested | Not tested | Not tested | Not tested | Not tested
|  | Conducted low frequency interference (harmonics) | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W |  |  |  |  | · | · | · | · | ? | ?
Emission |  | Generic emission standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 (Except Radiared RF IEC 61000-6-4 only) | IEC61000-6-3, IEC 61000-6-4 |  |  |  |  | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4
|  | Radiated RF & electromagnetic field (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B | Class B | Class B | Class B | Class B | Class A | Class B |  |  |  |  | Class B | Class B | Class B | Class B | Class B Group1 | Class B Group1
|  | Radiated RF & electromagnetic field (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class A, Group 1 | Class B, Group 1 |  |  |  |  | Class B | Class B | Class B | Class B | Class B Group1 | Class B Group1
|  | Radiated emission from enclosure port | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 |  |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2
|  | Conducted RF emission on power line (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B | Class B | Class B | Class B | Class B | Class B | Class B |  |  |  |  | Class B | Class B | Class B | Class B | Class B Group1 | Class B Group1
|  | Conducted RF emission on power line (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 |  |  |  |  | Class B | Class B | Class B | Class B | Class B Group1 | Class B Group1
|  | Conducted emission | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 |  |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2
Electrical Isolation
Degree of pollution |  |  | IEC60664-1 | Common C_Rly Spec | pollution degree | Published | Published |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  |  |  | 3 | 3 | 3 | 3 | Not specified | Not specified
Overvoltage category |  |  | IEC60664-1 | Common C_Rly Spec | overvoltage category | Published | Published |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  |  |  |  | III | III | III | III | Not specified | Not specified
Circuit Group | Terminal | Supply |  |  | circuit group | Published |  |  | A1, A2 | A1, A2 | A1, A2 | A1, A2 | A1, A2 | A1, A2 | A1, A2 | A1, A2
|  | Input 1 |  |  | circuit group | Published |  |  | E1, M | E1, M | E1, M | E1, M | E1, M | E1, M | E1, M | -
|  | Input 2 |  |  | circuit group | Published |  |  | E2, M | E2, M | E2, M | E2, M | E2, M | E2, M | E2, M | -
|  | Input 3 |  |  | circuit group | Published |  |  | E3, M | E3, M | E3, M | E3, M | E3, M | E3, M | E3, M | -
|  | Output 1 |  |  | circuit group | Published |  |  | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14
|  | Output 2 |  |  | circuit group | Published |  |  | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 |  |  |  |  | 600 | 600 | 600 | 600 | Not specified | Not specified
| Rated | Supply | [6 empty] | 24…240 AC/DC | 24…240 AC/DC | 24…240 AC/DC | 24…240 AC/DC | 24…240 AC/DC | 24…240 AC/DC | 380…415 AC | 110…240 AC/DC |  |  |  |  | 600 | 600 | 600 | 600 | Not specified | Not specified
| Voltage | Input 1 | [6 empty] | 0.05..0.5 AC/DC [full: 0.05..0.5 AC/DC] | 1..10 AC/DC [full: 1..10 AC/DC] | 18..125 AC/DC [full: 15..150 AC/DC] | 0.05..0.5 AC/DC [full: 0.05..0.5 AC/DC] | 1..10 AC/DC [full: 1..10 AC/DC] | 18..125 AC/DC [full: 15..150 AC/DC] | 18..125 AC/DC [full: 15..150 AC/DC] | - |  |  |  |  | 600 | 600 | 600 | 600 | Not specified | Not specified
| Spec | Input 2 | [6 empty] | 0.3..3 AC/DC [full: 0.3..3 AC/DC] | 5..50 AC/DC [full: 5..50 AC/DC] | 37..250 AC/DC [full: 30..300 AC/DC] | 0.3..3 AC/DC [full: 0.3..3 AC/DC] | 5..50 AC/DC [full: 5..50 AC/DC] | 37..250 AC/DC [full: 30..300 AC/DC] | 37..250 AC/DC [full: 30..300 AC/DC] | -
|  | Input 3 | [6 empty] | 0.5..5 AC/DC [full: 0.5..5 AC/DC] | 10..100 AC/DC [full: 10..100 AC/DC] | 75..440 AC/DC [full: 50..500 AC/DC] | 0.5..5 AC/DC [full: 0.5..5 AC/DC] | 10..100 AC/DC [full: 10..100 AC/DC] | 75..440 AC/DC [full: 50..500 AC/DC] | 75..440 AC/DC [full: 50..500 AC/DC] | -
|  | Output 1 | [6 empty] | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V
|  | Output 2 | [6 empty] | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V
Rated Insulation Voltage |  | Supply | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 400V | 250V
|  | Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 12.5 | 12.5 | 125V | 12.5 | 12.5 | 125V | 125V | -
|  | Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 12.5 | 50 | 250V | 12.5 | 50 | 250V | 250V | -
|  | Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 12.5 | 100 | 500V | 12.5 | 100 | 500V | 500V | -
|  | Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V |  |  |  |  | 4 | 4 | 4 | 4 | Not specified | Not specified
|  | Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 400V | -
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 400V | -
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 500V | 250V | 250V | 500V | 500V | -
|  | Supply / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 400V | 250V
|  | Supply / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 400V | 250V
|  | Output 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V
|  | Input 1 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | -
|  | Input 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | -
|  | Input 2 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | -
|  | Input 2 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | - |  |  |  |  | 2 @ 50Hz for 1 minutes | 2 @ 50Hz for 1 minutes | 2 @ 50Hz for 1 minutes | 2 @ 50Hz for 1 minutes | Not specified | Not specified
|  | Input 3 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 500V | 250V | 250V | 500V | 500V | -
|  | Input 3 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 500V | 250V | 250V | 500V | 500V | -
|  | Input 1 / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | -
Rated Impulse Voltage |  | Supply | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 0.8kV, OVC3 | 0.8kV, OVC3 | 2.5kV, OVC3 | 0.8kV, OVC3 | 0.8kV, OVC3 | 2.5kV, OVC3 | 2.5kV, OVC3 | -
|  | Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 0.8kV, OVC3 | 0.8kV, OVC3 | 4kV, OVC3 | 0.8kV, OVC3 | 0.8kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
|  | Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 0.8kV, OVC3 | 1.5kV, OVC3 | 4kV, OVC3 | 0.8kV, OVC3 | 1.5kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
|  | Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | -
|  | Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | -
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
|  | Supply / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Supply / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Output 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
|  | Input 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
|  | Input 2 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
|  | Input 2 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | - |  |  |  |  | > 500MOhm @ -- 500V | > 500MOhm @ -- 500V | > 500MOhm @ -- 500V | > 500MOhm @ -- 500V | Not specified | Not specified
|  | Input 3 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
|  | Input 3 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
|  | Input 1 / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | -
Dielectric test voltage |  | Supply / Input 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | - |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes
|  | Supply / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | - |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes
|  | Supply / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | - |  |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes
|  | Supply / Output 1 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Supply / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Output 1 / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | -
|  | Input 1 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | -
|  | Input 2 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | -
|  | Input 2 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | -
|  | Input 3 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | -
|  | Input 3 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | -
|  | Input 1 / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | -
|  | Input 2 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | -
|  | Input 1 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | -
Insulation resistance |  | Supply / Input 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Supply / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Supply / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Supply / Output 1 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Output 1 / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Input 1 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Input 2 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Input 2 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Input 3 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Input 3 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Input 1 / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | -
|  | Input 2 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | -
|  | Input 1 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | -
Power Supply Characteristics
Rated supply voltage, Us |  |  |  |  | [Us] rated supply voltage | Published | Published | V | ~/-- 24…240 | ~/-- 24…240 | ~/-- 24…240 | ~/-- 24…240 | ~/-- 24…240 | ~/-- 24…240 | ~380…415 | ~/--110…240 |  |  |  |  | ~/-- 24…240 | ~/-- 24…240 | ~/-- 24…240 | ~/-- 24…240 | RM4UA3xMW: ~/-- 24…240 RM4UA3xF: ~110…130 RM4UA3xM: ~220…240 RM4UA3xQ: ~380…415 | RM4UA0xB: ~24 RM4UA0xF: ~110…130 RM4UA0xM: ~220…240
Supply voltage operating range |  |  |  |  | supply voltage limits | Published | Published | V | ~/-- 20.4…264 | ~/-- 20.4…264 | ~/-- 20.4…264 | ~/-- 20.4…264 | ~/-- 20.4…264 | ~/-- 20.4…264 | ~323…456.5 | ~60…280 (F0) ~80…300 (F1) |  |  |  |  | ~/-- 20.4…264 | ~/-- 20.4…264 | 0.85…1.1 Un (~/-- 20.4…264) | ~/-- 20.4…264 | 0.85…1.1 Un | 0.85…1.1 Un
Polarity on d.c. supply |  |  |  |  | polarity |  | Published
Rated frequency |  |  |  |  | supply frequency | Published | Published | Hz | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 |  |  |  |  | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60
Frequency operating range |  |  |  |  | supply frequency | Published | Published | Hz | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 |  |  |  |  | 45…66 | 45…66 | 45…66 | 45…66 | Not specified | Not specified
Maximum power consumption |  |  |  |  | power consumption | Published | Published |  | ~ 3.5VA, -- 0.6W 1.5W | ~ 3.5VA, -- 0.6W 1.5W | ~ 3.5VA, -- 0.6W 1.5W | ~ 3.5VA, -- 0.6W 1.5W | ~ 3.5VA, -- 0.6W 1.5W | ~ 3.5VA, -- 0.6W 1.5W | ~ 10VA ~ 8VA | ~ 3.5VA, -- 1.5W ~ 5VA, -- 2W |  |  |  |  | ~ 3.5VA, -- 0.6W | ~ 3.5VA, -- 0.6W | ~ 3.5VA, -- 0.6W | ~ 3.5VA, -- 0.6W | RM4UA3xMW: ~ 3.3VA, -- 1.2W RM4UA3xF: ~ 3.3VA RM4UA3xM: ~ 3.4VA RM4UA3xQ: ~ 3VA | RM4UA0xB: ~ 2VA RM4UA0xF: ~ 3.3VA RM4UA0xM: ~ 3.5VA
Immunity to micro-breakage |  |  |  |  | immunity to microbreaks | Published | Published | ms | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 |  |  |  |  | 10 | 10 | 10 | 10 | Not specified | Not specified
Supply terminal |  |  |  |  | supply terminal |  |  |  | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1+ - A2- |  |  |  |  | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2
On Load Factor |  |  |  | Common C_Rly Spec | on-load factor |  |  | % | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Release of input voltage |  |  |  |  | release of input voltage |  |  | V | - | - | - | - | - | - | - | -
Input Circuit Characteristics
Monitoring functions |  | Over / undervoltage (windows mode) | [6 empty] | - | - | - | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Selectable threshold |  |  |  |  | - | - | - | - | - | -
|  | Over voltage | [6 empty] | Without memory | Without memory | Without memory | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | - |  |  |  |  | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Without memory | Without memory
|  | Undervoltage | [6 empty] | - | - | - | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | - |  |  |  |  | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Without memory | -
Full Measurement range | [7 empty] | V | ~/-- 0.05…5 | ~/-- 1…100 | ~/-- 15…500 | ~/-- 0.05…5 | ~/-- 1…100 | ~/-- 15…500 | ~/-- 15…500 | ~60…280 (F0) ~60…300 (F1) ~/--80…300 (F1) |  |  |  |  | ~/-- 0.05…5 | ~/-- 1…100 | ~/-- 15…600 | ~/-- 0.05…5 | RM4UA31xx: ~/-- 0.05…5 RM4UA32xx: ~/-- 1…100 RM4UA33xx: ~/-- 30…500 | RM4UA01xx: ~/-- 0.05…5 RM4UA02xx: ~/-- 1…100 RM4UA03xx: ~/-- 30…500
Input Resistance |  | E1-M / B1-C | [5 empty] | kW | 5 | 22 | 150 | 5 | 22 | 150 | 150 | - |  |  |  |  | 5 | 22 | 150 | RM22UA31MW: 5 RM22UA32MW: 22 RM22UA33MW: 150 | RM4UA31xx: 6.6 RM4UA32xx: ~/-- 23 | RM4UA31xx: 6.6 RM4UA32xx: ~/-- 23
|  | E2-M / B2-C | [5 empty] | kW | 30 | 110 | 300 | 30 | 110 | 300 | 300 | - |  |  |  |  | 30 | 110 | 300 | RM22UA31MW: 30 RM22UA32MW: 110 RM22UA33MW: 300 | RM4UA31xx: 43 RM4UA32xx: ~/-- 112 RM4UA33xx: ~/-- 668 | RM4UA01xx: 43 RM4UA02xx: ~/-- 112 RM4UA03xx: ~/-- 668
|  | E3-M / B3-C | [5 empty] | kW | 50 | 220 | 500 | 50 | 220 | 500 | 500 | - |  |  |  |  | 50 | 220 | 600 | RM22UA31MW: 50 RM22UA32MW: 220 RM22UA33MW: 600 | RM4UA31xx: 71 RM4UA32xx: ~/-- 225 RM4UA33xx: ~/-- 1111 | RM4UA01xx: 71 RM4UA02xx: ~/-- 225 RM4UA03xx: ~/-- 1111
|  | A1+ / A2- | [5 empty] | kW | - | - | - | - | - | - | - | Not specified
|  | Built in current transformer | [5 empty] | kW | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | -
Sub measurement range |  | E1-M / B1-C | [5 empty] | V | ~/-- 0.05…0.5 | ~/-- 1…10 | ~/-- 15…150 | ~/-- 0.05…0.5 | ~/-- 1…10 | ~/-- 15…150 | ~/-- 15…150 | - |  |  |  |  | ~/-- 0.05…0.5 | ~/-- 1…10 | ~/-- 15…150 | RM22UA31MW: ~/-- 0.05…0.5 RM22UA32MW: ~/-- 1…10 RM22UA33MW: ~/-- 15…150 | RM4UA31xx: ~/-- 0.05…0.5 RM4UA32xx: ~/-- 1…10 | RM4UA01xx: ~/-- 0.05…0.5 RM4UA02xx: ~/-- 1…10
|  | E2-M / B2-C | [5 empty] | V | ~/-- 0.3…3 | ~/-- 5…50 | ~/-- 30…300 | ~/-- 0.3…3 | ~/-- 5…50 | ~/-- 30…300 | ~/-- 30…300 | - |  |  |  |  | ~/-- 0.3…3 | ~/-- 5…50 | ~/-- 30…300 | RM22UA31MW: ~/-- 0.5…3 RM22UA32MW: ~/-- 5…50 RM22UA33MW: ~/-- 30…300 | RM4UA31xx: ~/-- 0.3…3 RM4UA32xx: ~/-- 5…50 RM4UA33xx: ~/-- 30…300 | RM4UA01xx: ~/-- 0.3…3 RM4UA02xx: ~/-- 5…50 RM4UA03xx: ~/-- 30…300
|  | E3-M / B3-C | [5 empty] | V | ~/-- 0.5…5 | ~/-- 10…100 | ~/-- 50…500 | ~/-- 0.5…5 | ~/-- 10…100 | ~/-- 50…500 | ~/-- 50…500 | - |  |  |  |  | ~/-- 0.5…5 | ~/-- 10…100 | ~/-- 60…600 | RM22UA31MW: ~/-- 0.5…5 RM22UA32MW: ~/-- 10…100 RM22UA33MW: ~/-- 60…600 | RM4UA31xx: ~/-- 0.5…5 RM4UA32xx: ~/-- 10…100 RM4UA33xx: ~/-- 50…500 | RM4UA01xx: ~/-- 0.5…5 RM4UA02xx: ~/-- 10…100 RM4UA03xx: ~/-- 50…500
|  | A1+ / A2- | [5 empty] | V | - | - | - | - | - | - | - | -
|  | Built in current transformer | [6 empty] | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | -
Threshold |  | E1-M / B1-C | [5 empty] | V | Adjustable 10%...100% of 0.5V | Adjustable 10%...100% of 10V | Adjustable 10%...100% of 150V | Adjustable 10%...100% of 0.5V | Adjustable 10%...100% of 10V | Adjustable 10%...100% of 150V | Adjustable 10%...100% of 150V | - |  |  |  |  | Adjustable 10%...100% of 0.5V | Adjustable 10%...100% of 0.5V | Adjustable 10%...100% | Adjustable 10%...100% of full range | - | -
|  | E2-M / B2-C | [5 empty] | V | Adjustable 10%...100% of 3V | Adjustable 10%...100% of 50V | Adjustable 10%...100% of 300V | Adjustable 10%...100% of 3V | Adjustable 10%...100% of 50V | Adjustable 10%...100% of 300V | Adjustable 10%...100% of 300V | - |  |  |  |  | Adjustable 10%...100% of 3V | Adjustable 10%...100% of 3V | Adjustable 10%...100% | Adjustable 10%...100% of full range | Adjustable 10%...100% | Adjustable 10%...100%
|  | E3-M / B3-C | [5 empty] | V | Adjustable 10%...100% of 5V | Adjustable 10%...100% of 100V | Adjustable 10%...100% of 500V | Adjustable 10%...100% of 5V | Adjustable 10%...100% of 100V | Adjustable 10%...100% of 500V | Adjustable 10%...100% of 500V | - |  |  |  |  | Adjustable 10%...100% of 5V | Adjustable 10%...100% of 5V | Adjustable 10%...100% | Adjustable 10%...100% of full range | Adjustable 10%...100% | Adjustable 10%...100%
|  | A1+ / A2- | [5 empty] | V | - | - | - | - | - | - | - | Adjustable <U : 80…300 Adjustable >U : 80…300
|  | Built in current transformer | [6 empty] | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | -
Hysteresis |  | E1-M / B1-C | [5 empty] | V | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | - |  |  |  |  | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...30% of threshold setting | Adjustable 5%...30% of threshold setting
|  | E2-M / B2-C | [5 empty] | V | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | - |  |  |  |  | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...30% of threshold setting | Adjustable 5%...30% of threshold setting
|  | E3-M / B3-C | [5 empty] | V | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | - |  |  |  |  | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...30% of threshold setting | Adjustable 5%...30% of threshold setting
|  | A1+ / A2- | [5 empty] | V | - | - | - | - | - | - | - | Fixed 3% of threshold setting
|  | Built in current transformer | [6 empty] | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | -
Measurement mode | [8 empty] | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down |  |  |  |  | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down
Connection terminals | [8 empty] | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | A1+ / A2- |  |  |  |  | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | B1-C, B2-C, B3-C | B1-C, B2-C, B3-C
Rated frequency | [7 empty] | Hz | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 |  |  |  |  | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60
Frequency operating range | [7 empty] | Hz | 36…77 | 36…77 | 36…77 | 36…77 | 36…77 | 36…77 | 36…77 | 45…66 |  |  |  |  | 36…77 | 36…77 | 36…77 | 36…77 | Not specified | Not specified
Setting accuracy | [8 empty] | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value |  |  |  |  | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 5% of full scale value | +/- 5% of full scale value
Repeat accuracy (constant parameters) | [8 empty] | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% |  |  |  |  | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | Not specified | Not specified
Measurement error with supply voltage variation | [7 empty] | %/V | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range |  |  |  |  | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 0.5% over whole range | < 0.5% over whole range
Measurement error with temperature variation | [7 empty] | %/oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.2% / oC |  |  |  |  | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.06% / oC | 0.06% / oC
Maximum measuring cycles | [7 empty] | ms | 30 100 | 30 100 | 30 100 | 30 100 | 30 100 | 30 100 | 30 100 | 250 |  |  |  |  | 30 | 30 | 30 | 30 | 80 | 80
Measurement method | [8 empty] | True RMS | True RMS | True RMS | True RMS | True RMS | True RMS | True RMS | True RMS |  |  |  |  | True RMS | True RMS | True RMS | True RMS | Voltage Peak Detection | Voltage Peak Detection
Output Circuit Characteristics
Type of output |  |  |  |  | output type | Published | Published |  | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts |  |  |  |  | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 1 x C/O relay contacts
Output terminal |  |  |  |  | output terminal |  |  |  | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 |  |  |  |  | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 15-16-18, 25-26-28 | 15-16-18
Operation principle |  | R1 (11-12-14) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free |  |  |  |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault | Energized on fault
|  | R2 (21-22-24) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free
Contact material |  |  |  | Common C_Rly Spec | contacts material | Published | Published |  | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free |  |  |  |  | Cadmium-free | Cadmium-free | Cadmium-free | Cadmium-free | Not specified | Not specified
Mechanical durability |  |  | IEC61810-1 | Common C_Rly Spec | mechanical durability | Published | Published | Cyc | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles |  |  |  |  | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | Not specified | Not specified
Electrical durability |  | AC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles |  |  |  |  | 1 x 105 switching cycles | 1 x 105 switching cycles | 1 x 105 switching cycles | 1 x 105 switching cycles | Not specified | Not specified
|  | DC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles
|  | AC-15 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles
|  | DC-13 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles
Rated capacity |  | Rated switching voltage | IEC61810-1 | Common C_Rly Spec | [Ue] rated operational voltage | Published |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V
|  | Rated switching current | IEC61810-1 | Common C_Rly Spec | [Ie] rated operational current | Published | Published | A | 8A | 8A | 8A | 8A | 8A | 8A | 8A | 8A
Maximum switching capacity |  | Maximum switching voltage |  | Common C_Rly Spec | maximum switching capacity | Published | Published | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V |  |  |  |  | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250
|  | Maximum switching current |  | Common C_Rly Spec | maximum switching capacity | Published | Published | A | 8A | 8A | 8A | 8A | 8A | 8A | 8A | 8A |  |  |  |  | 5 | 5 | 5 | ~ 8 | 8 | 8
|  | Maximum switching capacity |  | Common C_Rly Spec | maximum switching capacity | Published | Published | VA | - | - | - | - | - | - | - | - |  |  |  |  | 1250 | 1250 | 1250 | 2000 | 2000VA | 2000VA
Minimum switching capacity |  | Minimum switching voltage | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | V | - | - | - | - | - | - | - | - |  |  |  |  | 5 | 5 | 5 | 5 | Not specified | Not specified
|  | Minimum switching current | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | mA | - | - | - | - | - | - | - | - |  |  |  |  | 10 | 10 | 10 | 10 | Not specified | Not specified
|  | Minimum switching capacity | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published | Published | mW | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 |  |  |  |  | 50 | 50 | 50 | 50 | Not specified | Not specified
Maximum voltage drop at terminals |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum voltage drop |  |  | V | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | -
Leakage current |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum leakage current |  |  | mA | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | -
Thermal Current |  |  | IEC60947-5-1 | Common C_Rly Spec | thermal current |  |  | A | 8A | 8A | 8A | 8A | 8A | 8A | 8A | 8A
Short circuit protection |  | Relay Output by external fuse | IEC60947-5-1 | Common C_Rly Spec | short circuit protection |  |  | gG | 8A | 8A | 8A | 8A | 8A | 8A | 8A | 8A
|  | Solid State Output by external fuse | IEC62314 | Common C_Rly Spec | short circuit protection |  |  | gG | - | - | - | - | - | - | - | -
Time Delay Characteristics
Time delay functions |  | "OFF" delay |  |  | time delay type | Published |  |  | - | - | - | Yes | Yes | Yes | Yes | Yes |  |  |  |  | · | · | · | · | · | -
|  | "ON" delay |  |  | time delay type | Published |  |  | - | - | - | - | - | - | - | Yes |  |  |  |  | - | - | - | - | - | -
|  | Inhibition |  |  | time delay type | Published |  |  | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | -
Timing range |  | "OFF" delay |  |  | time delay range | Published | Published | s | - | - | - | Adjustable 0.1…30 | Adjustable 0.1…30 | Adjustable 0.1…30 | Adjustable 0.1…30 | Adjustable 0.1…30 |  |  |  |  | Adjustable 0.3…30 | Adjustable 0.3…30 | Adjustable 0.3…30 | Adjustable 0.3…30 | Adjustable (0.5…1),(0.15…3),(0.5…10),(1.5…30) | -
|  | "ON" delay |  |  | time delay range | Published |  | s | - | - | - | - | - | - | - | Adjustable 0.1…30 |  |  |  |  | - | - | - | - | - | -
|  | Inhibition |  |  | time delay range | Published | Published | s | - | - | - | - | - | - | - | - |  |  |  |  | - | - | - | - | - | -
Response time |  | on crossing the threshold |  |  | response time | Published | Published | ms | Not specified =< 300ms | Not specified =< 300ms | Not specified =< 300ms | Not specified =< 300ms | Not specified =< 300ms | Not specified =< 300ms | Not specified =< 300ms | Not specified =< 300ms |  |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
Time delay of pick-up |  |  |  |  | power on delay | Published | Published | ms | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | Not specified | Not specified
Reset time |  | through Un power reset |  |  | reset time | Published | Published | ms | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | Not specified | Not specified
|  | through front panel reset |  | Reserved for other products | reset time | Published
|  | through input control reset |  | Reserved for other products | reset time | Published
Setting accuracy |  |  |  | Common C_Rly Spec | setting accuracy of time delay | Published | Published | % | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales |  |  |  |  | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | -
Repeat accuracy (constant parameters) |  |  |  | Common C_Rly Spec | repeat accuracy of time delay | Published |  | % | +/- 2% | +/- 2% | +/- 2% | +/- 2% | +/- 2% | +/- 2% | +/- 2% | +/- 2% |  |  |  |  | +/- 2% | +/- 2% | +/- 2% | +/- 2% | Not specified | Not specified
Timing error with supply voltage variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/V | < 1 | < 1 | < 1 | < 1 | < 1 | < 1 | < 1 | < 1 |  |  |  |  | Not specified | Not specified | Not specified | Not specified | < 0.5% over whole range | -
Timing error with temperature variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/oC | < 0.05 | < 0.05 | < 0.05 | < 0.05 | < 0.05 | < 0.05 | < 0.05 | < 0.05 |  |  |  |  | Not specified | Not specified | Not specified | Not specified | 0.07% / oC | -
LED Indication
status LED |  |  |  |  | status LED |  |  |  | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber)
local signalling |  | Power supply availability |  |  | local signalling |  |  |  | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON
|  | Power supply not availability |  |  | local signalling |  |  |  | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF
|  | Timing in-progress |  |  | local signalling |  |  |  | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz
|  | Output is energized |  |  | local signalling |  |  |  | R - ON | R - ON | R - ON | R - ON | R - ON | R - ON | R - ON | R - ON
|  | Output is de-energized |  |  | local signalling |  |  |  | R - OFF | R - OFF | R - OFF | R - OFF | R - OFF | R - OFF | R - OFF | R - OFF
|  | Range Setting Changes |  |  | local signalling |  |  |  | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
Special Features
True RMS | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Backlight Indicator | [8 empty] | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product
Diagnostic Button |  |  |  |  | diagnostic button | Published |  |  | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated
Pre-Alarm Output | [8 empty] | - | - | - | - | - | - | - | -
Output | [8 empty] | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
Reliability Data
Reliability Data |  | MTTF |  |  | safety reliability data | Published |  |  | 2,700,000 hours | 2,700,000 hours | 2,700,000 hours | 2,700,000 hours | 2,700,000 hours | 2,700,000 hours | 2,700,000 hours | 3,800,000 hours
|  | B10 |  |  | safety reliability data | Published |  |  | 290,000 hours | 290,000 hours | 290,000 hours | 290,000 hours | 290,000 hours | 290,000 hours | 290,000 hours | 400,000 hours
|  | MTTFd | [6 empty] | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product)
|  | B10d | [6 empty] | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product)
Drawing / Diagram

## 1P Current Control Spec
Main Parameters | Category | Sub Parameters | Conforming to | Remark | Standardized Datasheet Param | Selected for Publication | Old Datasheet | Unit | RM22JA21MR | RM22JA31MR | RM35JA32MR | RM35JA32MT | col13 | col14 | col15 | col16 | Competitor Spec Reference | RM35JA31MW | RM35JA32MW | RM4JA3 | RM4JA01 | RM17JC00MW | RM22JA31MW (Catch Up) | 84893852 (Catch Up) | 84893852 (Autelec Distribution)
Standard
Product standard |  |  |  | Common C_Rly Spec | standards | Published | Published |  | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | [5 empty] | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | Not specified
Product certifications |  |  |  | Common C_Rly Spec | product certifications | Published | Published |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | [5 empty] | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST, CCC | UL, CSA, GL, C-Tick, GOST, CCC | UL, CSA, GL, C-Tick, GOST, CCC | UL, CSA, GL, C-Tick, GOST, CCC | UL, CSA, GL, C-Tick, GOST, CCC | UL, CSA, GL, C-Tick, GOST, CCC | Not specified
Marking |  |  |  | Common C_Rly Spec | marking | Published |  |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | [5 empty] | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE, CCC | UL, CSA, GL, C-Tick, GOST, CE, CCC | UL, CSA, GL, C-Tick, GOST, CE, CCC | UL, CSA, GL, C-Tick, GOST, CE, CCC | UL, CSA, GL, C-Tick, GOST, CE, CCC | UL, CSA, GL, C-Tick, GOST, CE, CCC | CE
Low voltage directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | [5 empty] | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC |  |  | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | Not specified
EMC directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | [5 empty] | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC |  |  | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | Not specified
ROHS directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | [5 empty] | 2002/95/EC | 2002/95/EC |  |  | 2002/95/EC | 2002/95/EC | 2002/95/EC | Not specified
Environment Characteristics
Environmental Condition |  | Climatic category | IEC60721-3-3 | Common C_Rly Spec |  |  |  |  | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | [5 empty] | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | Environmental category | Germanisher Lloyd | Common C_Rly Spec |  |  |  |  | Class C | Class C | Class C | Class C
Ambient air temperature around the device |  | Storage |  | Common C_Rly Spec | ambient air temperature for storage | Published | Published | oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | [5 empty] | -40…+70 | -40…+70 | Not specified | Not specified | -40…+70 | -40…+70 | -40…+70 | Not specified
|  | Operation |  |  | ambient air temperature for operation | Published | Published | oC | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | [5 empty] | -20…+50 | -20…+50 | Not specified | Not specified | -20…+50 | -20…+50 | -20…+50 | Not specified
Relative humidity |  | Damp heat | IEC60068-2-30 | Common C_Rly Spec | relative humidity | Published | Published |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | [5 empty] | 2 cycles 24h ;+25°C +55°C 95%HR | 2 cycles 24h ;+25°C +55°C 95%HR | Not specified | Not specified | 2 cycles 24h ;+25°C +55°C 95%HR | 2 cycles 24h ;+25°C +55°C 95%HR | 2 cycles 24h ;+25°C +55°C 95%HR | Not specified
|  | Cyclic Damp Heat Test | IEC60947-5-1 | Common C_Rly Spec |  |  |  |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97%
Vibration resistance |  |  | IEC60068-2-6 | Common C_Rly Spec | vibration resistance | Published | Published |  | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | [5 empty] | 0.035mm from 10Hz…150Hz | 0.035mm from 10Hz…150Hz | Not specified | Not specified | 0.035mm from 10Hz…150Hz | 0.035mm from 10Hz…150Hz | 0.035mm from 10Hz…150Hz | Not specified
Shock resistance |  |  | IEC60068-2-27 | Common C_Rly Spec | shock resistance | Published | Published |  | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | [5 empty] | 5 gn | 5 gn | Not specified | Not specified | 5 gn | 5 gn | 5 gn | Not specified
Bump resistance |  |  | IEC60068-2-29 | Common C_Rly Spec | bump resistance |  |  |  | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating)
Seismic resistance |  |  | IEC60068-3-3 | Common C_Rly Spec | seismic resistance |  |  |  | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz
IP degree of protection |  | Terminal Block | IEC60529 |  | IP degree of protection | Published | Published |  | IP20 | IP20 | IP20 | IP20 | [5 empty] | IP20 | IP20 | Not specified | Not specified | IP20 | IP20 | IP20 | Not specified
|  | Housing | IEC60529 |  | IP degree of protection | Published | Published |  | IP40 | IP40 | IP30 | IP30 | [5 empty] | IP30 | IP30 | Not specified | Not specified | IP30 | IP30 | IP30 | Not specified
|  | Front Panel | IEC60529 |  | IP degree of protection |  |  |  | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover)
Installation Data
Dimension (nominal) |  | Width |  |  | width | Published |  | mm | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 | [5 empty] | 35 x 90 x 72 | 35 x 90 x 72 | RM4JA31xx: 22.5 x 78 x 80 RM4JA32xx: 45 x 78 x 80 | 22.5 x 78 x 80 | 17.5 x 90 x 72 | 22.5 x ? x ? | 22.5 x ? x ? | 22.5 x 78.5 x 100
|  | Height |  |  | height | Published |  | mm
|  | Depth |  |  | depth | Published |  | mm
Weight (without packaging) |  |  |  |  | net weight | Published |  | g | 110 | 110 | 120 | 120 | [5 empty] | 130 | 130 | Not specified | Not specified | 110 | ? | ? | Not specified
Mounting |  | Without socket | IEC/EN 60715 |  | mounting support | Published | Published |  | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | [5 empty] | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | Not specified
|  | With socket | IEC/EN 60715 |  | mounting support |  |  |  | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | -
Mounting position |  | In relation to normal vertical mounting plane |  | Common C_Rly Spec | mounting position | Published | Published |  | Any position | Any position | Any position | Any position | [5 empty] | Any position | Any position | Not specified | Not specified | Any position | Any position | Any position | Not specified
Minimum distance to adjacent devices |  | Horizontal |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | Not specified | Not specified | Not specified | Not specified | [5 empty] | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | Vertical |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | Not specified | Not specified | Not specified | Not specified | [5 empty] | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Wiring connection (Clamping Capacity) |  | Solid cable without cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | [5 empty] | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | Not specified | Not specified | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | Not specified
|  | Flexible cable with cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | [5 empty] | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | Not specified | Not specified | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | Not specified
|  | Solid cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | -
|  | Flexible cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | -
|  | Tightening torque | IEC60947-1 | Common C_Rly Spec | tightening torque | Published | Published | Nm | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | [5 empty] | 0.6…1 | 0.6…1 | Not specified | Not specified | 0.6…1 | 0.6…1 | 0.6…1 | Not specified
|  | Cable stripping length |  | Common C_Rly Spec | cable stripping length |  |  | mm | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | [5 empty] | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Duty time |  |  |  | Common C_Rly Spec | duty time |  |  | % | 1 | 1 | 1 | 1 | [5 empty] | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Electromagnetic Compatibility
Immunity |  | Generic immunity standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | [5 empty] | IEC61000-6-2 | IEC61000-6-2 | IEC50082-2 | IEC50082-2 | IEC61000-6-2 | IEC61000-6-2 | IEC61000-6-2 | Not specified
|  | Electrostatic discharge | IEC61000-4-2 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | [5 empty] | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Not specified
|  | Radiated RF & electromagnetic field | IEC61000-4-3 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | [5 empty] | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Not specified
|  | Fast transient / burst | IEC61000-4-4 |  | electromagnetic compatibility | Published |  |  | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | [5 empty] | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Not specified
|  | Surge | IEC61000-4-5 |  | electromagnetic compatibility | Published |  |  | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | [5 empty] | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Not specified
|  | Conducted RF disturbance | IEC61000-4-6 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | [5 empty] | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Not specified
|  | Power frequency magnetic field | IEC61000-4-8 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s)
|  | Voltage dips, short interruption & variations on power line | IEC61000-4-11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | - | - | - | [5 empty] | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Not specified
|  | 1 MHz oscillation wave | IEC61000-4-18 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV)
|  | DC voltage interruption | IEC61000-4-29 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms
|  | Low frequency harmonics | IEC61000-4-13 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | - | - | - | [5 empty] | Not tested | Not tested | Not tested | Not tested | Not tested | Not tested | Not tested | Not specified
|  | Conducted low frequency interference (harmonics) | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | [5 empty] | · | · | ? | ? | · | · | · | Not specified
Emission |  | Generic emission standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | [5 empty] | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | Not specified
|  | Radiated RF & electromagnetic field (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B | Class B | Class B | [5 empty] | Class B | Class B | Class B Group1 | Class B Group1 | Class B | Class B | Class B | Not specified
|  | Radiated RF & electromagnetic field (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | [5 empty] | Class B | Class B | Class B Group1 | Class B Group1 | Class B | Class B | Class B | Not specified
|  | Radiated emission from enclosure port | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | [5 empty] | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | Not specified
|  | Conducted RF emission on power line (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B | Class B | Class B | [5 empty] | Class B | Class B | Class B Group1 | Class B Group1 | Class B | Class B | Class B | Not specified
|  | Conducted RF emission on power line (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | [5 empty] | Class B | Class B | Class B Group1 | Class B Group1 | Class B | Class B | Class B | Not specified
|  | Conducted emission | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | [5 empty] | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | Not specified
Electrical Isolation
Degree of pollution |  |  | IEC60664-1 | Common C_Rly Spec | pollution degree | Published | Published |  | 3 | 3 | 3 | 3 | [5 empty] | 3 | 3 | Not specified | Not specified | 3 | 3 | 3 | Not specified
Overvoltage category |  |  | IEC60664-1 | Common C_Rly Spec | overvoltage category | Published | Published |  | 3 | 3 | 3 | 3 | [5 empty] | III | III | Not specified | Not specified | III | III | III | Not specified
Circuit Group | Terminal | Supply |  |  | circuit group | Published |  |  | A1, A2 | A1, A2 | A1, A2 | A1, A2
|  | Input 1 |  |  | circuit group | Published |  |  | E1, M | E1, M | E1, M | E1, M
|  | Input 2 |  |  | circuit group | Published |  |  | E2, M | E2, M | E2, M | E2, M
|  | Input 3 |  |  | circuit group | Published |  |  | E3, M | E3, M | E3, M | E3, M
|  | Output 1 |  |  | circuit group | Published |  |  | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14
|  | Output 2 |  |  | circuit group | Published |  |  | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | [5 empty] | 600 | 600 | Not specified | Not specified | 600 | 600 | 600 | Not specified
| Rated | Supply | [6 empty] | 24…240 AC/DC | 24…240 AC/DC | 24…240 AC/DC | 380…415 AC | [5 empty] | 600 | 600 | Not specified | Not specified | 600 | 600 | 600 | Not specified
| Voltage | Input 1 | [6 empty] | 4..40mA AC/DC [full: 4..40mA AC/DC ] | 4..40mA AC/DC [full: 4..40mA AC/DC ] | 0.15..1.5A AC/DC [full: 0.18..1.2A AC/DC] | 0.15..1.5A AC/DC [full: 0.18..1.2A AC/DC] | [5 empty] | 600 | 600 | Not specified | Not specified | 600 | 600 | 600 | Not specified
| Spec | Input 2 | [6 empty] | 20..200mA AC/DC [full: 20..200mA AC/DC] | 20..200mA AC/DC [full: 20..200mA AC/DC] | 0.5..5A AC/DC [full: 6..4A AC/DC] | 0.5..5A AC/DC [full: 6..4A AC/DC]
|  | Input 3 | [6 empty] | 100..1000mA AC/DC [full: 100..1000mA AC/DC] | 100..1000mA AC/DC [full: 100..1000mA AC/DC] | 1.8..12A AC/DC [full: 1.5..15A AC/DC] | 1.8..12A AC/DC [full: 1.5..15A AC/DC]
|  | Output 1 | [6 empty] | 250V | 250V | 250V | 250V
|  | Output 2 | [6 empty] | 250V | 250V | 250V | 250V
Rated Insulation Voltage |  | Supply | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 400V
|  | Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 10V | 10V | 10V | 10V
|  | Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 10V | 10V | 10V | 10V
|  | Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 10V | 10V | 10V | 10V
|  | Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | [5 empty] | 4 | 4 | Not specified | Not specified | 4 | 4 | 4 | Not specified
|  | Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 400V
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 400V
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V
|  | Supply / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V | 250V | 400V
|  | Supply / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V | 250V | 400V
|  | Output 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V | 250V | 250V
|  | Input 1 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V
|  | Input 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V
|  | Input 2 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V
|  | Input 2 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | [5 empty] | 2 @ 50Hz for 1 minutes | 2 @ 50Hz for 1 minutes | Not specified | Not specified | 2 @ 50Hz for 1 minutes | 2 @ 50Hz for 1 minutes | 2 @ 50Hz for 1 minutes | Not specified
|  | Input 3 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V
|  | Input 3 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V
|  | Input 1 / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
Rated Impulse Voltage |  | Supply | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Supply / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Supply / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Output 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 2 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 2 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | [5 empty] | > 500MOhm @ -- 500V | > 500MOhm @ -- 500V | Not specified | Not specified | > 500MOhm @ -- 500V | > 500MOhm @ -- 500V | > 500MOhm @ -- 500V | Not specified
|  | Input 3 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 3 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
Dielectric test voltage |  | Supply / Input 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | [5 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Not specified
|  | Supply / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | [5 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Not specified
|  | Supply / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | [5 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Not specified
|  | Supply / Output 1 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Supply / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Output 1 / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 2 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 2 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 3 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 3 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
|  | Input 2 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
|  | Input 1 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
Insulation resistance |  | Supply / Input 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Output 1 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Output 1 / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 2 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 2 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 3 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 3 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Input 2 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Input 1 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
Power Supply Characteristics
Rated supply voltage, Us |  |  |  |  | [Us] rated supply voltage | Published | Published | V | ~/-- 24…240 | ~/-- 24…240 | ~/-- 24…240 | ~380…415 | [5 empty] | ~/-- 24…240 | ~/-- 24…240 | RM4JA3xMW: ~/-- 24…240 RM4JA3xF: ~110…130 RM4JA3xM: ~220…240 RM4JA3xQ: ~380…415 | RM4JA01B: ~ 24 RM4JA01F: ~110…130 RM4JA01M: ~220…240 | ~/-- 24…240 | ~/-- 24…240 | ~/-- 24…240 | ~ 24…240
Supply voltage operating range |  |  |  |  | supply voltage limits | Published | Published | V | ~/-- 20.4…264 | ~/-- 20.4…264 | ~/-- 20.4…264 | ~323…456.5 | [5 empty] | ~/-- 20.4…264 | ~/-- 20.4…264 | 0.85…1.1 Un | 0.85…1.1 Un | ~/-- 20.4…264 | ~/-- 20.4…264 | ~/-- 20.4…264 | Not specified
Polarity on d.c. supply |  |  |  |  | polarity |  | Published
Rated frequency |  |  |  |  | supply frequency | Published | Published | Hz | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | [5 empty] | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | Not specified
Frequency operating range |  |  |  |  | supply frequency | Published | Published | Hz | 45…66 | 45…66 | 45…66 | 45…66 | [5 empty] | 45…66 | 45…66 | Not specified | Not specified | 45…66 | 45…66 | 45…66 | Not specified
Maximum power consumption |  |  |  |  | power consumption | Published | Published |  | ~ 3.5VA, -- 0.6W 1.5W | ~ 3.5VA, -- 0.6W 1.5W | ~ 3.5VA, -- 0.6W 1.5W | ~ 10VA ~ 8VA | [5 empty] | ~ 3.5VA, -- 0.6W | ~ 3.5VA, -- 0.6W | RM4JA3xMW: ~ 3.3VA, -- 1.2W RM4JA3xF: ~ 3.3VA RM4JA3xM: ~ 3.4VA RM4JA3xQ: ~ 3VA | RM4JA01B: ~ 2VA RM4JA01F: ~ 3.3VA RM4JA01M: ~ 3.5VA | ~ 3VA, -- 1W | ~ 3.5VA, -- 0.6W | ~ 3.5VA, -- 0.6W | Not specified
Immunity to micro-breakage |  |  |  |  | immunity to microbreaks | Published | Published | ms | 50 | 50 | 50 | 50 | [5 empty] | 50 | 10 | Not specified | Not specified | 10 | 10 | 10 | Not specified
Supply terminal |  |  |  |  | supply terminal |  |  |  | A1-A2 | A1-A2 | A1-A2 | A1-A2 | [5 empty] | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2
On Load Factor |  |  |  | Common C_Rly Spec | on-load factor |  |  | % | 1 | 1 | 1 | 1
Release of input voltage |  |  |  |  | release of input voltage |  |  | V | - | - | - | -
Input Circuit Characteristics
Monitoring functions |  | Over / undercurrent (windows mode) | [6 empty] | - | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | [5 empty] | - | - | - | - | - | - | - | -
|  | Over current | [6 empty] | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | [5 empty] | Selectable with memory / without memory | Selectable with memory / without memory | Without memory | Without memory | · | Selectable with memory / without memory | - | -
|  | Under current | [6 empty] | - | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | [5 empty] | Selectable with memory / without memory | Selectable with memory / without memory | Without memory | Without memory | - | Selectable with memory / without memory | · | ·
Full Measurement range | [7 empty] | mA | ~/-- 4…1000 | ~/-- 4…1000 | ~/-- 150…15000 | ~/-- 150…15000 | [5 empty] | ~/-- 2…500 | ~/-- 150…15000 | RM4JA31xx: ~/-- 3…1000 RM4JA32xx: ~/-- 300…15000 | ~/-- 3…1000 | ~ 2000…20000 | ~/-- 2…500 | Fix 0.7A | Fix 0.7A
Input Resistance |  | E1-M / B1-C | [5 empty] | W | 2.5 | 2.5 | 0.05 | 0.05 | [5 empty] | 5 | 0.05 | RM4JA31xx: 33 RM4JA32xx: ~/-- 0.06 | 33 | - | 5 | - | Not specified
|  | E2-M / B2-C | [5 empty] | W | 0.5 | 0.5 | 0.015 | 0.015 | [5 empty] | 1 | 0.015 | RM4JA31xx: 10 RM4JA32xx: ~/-- 0.02 | 10 | - | 1 | 0.015 | Not specified
|  | E3-M / B3-C | [5 empty] | W | 0.1 | 0.1 | 0.005 | 0.005 | [5 empty] | 0.2 | 0.005 | RM4JA31xx: 1 RM4JA32xx: ~/-- 0.006 | 1 | - | 0.2 | - | Not specified
|  | A1+ / A2- | [5 empty] | W | - | - | - | -
|  | Built in current transformer | [5 empty] | W | - | - |  | - | [5 empty] | - | - | - | - | · | - | - | Not specified
Sub measurement range |  | E1-M / B1-C | [5 empty] | mA | ~/-- 4…40 | ~/-- 4…40 | ~/-- 150…1500 | ~/-- 150…1500 | [5 empty] | ~/-- 2…20 | ~/-- 150…1500 | RM4JA31xx: ~/-- 3…30 RM4JA32xx: ~/-- 300…1500 | ~/-- 3…30 | - | ~/-- 2…20 | - | Not specified
|  | E2-M / B2-C | [5 empty] | mA | ~/-- 20…200 | ~/-- 20…200 | ~/-- 500…5000 | ~/-- 500…5000 | [5 empty] | ~/-- 10…100 | ~/-- 500…5000 | RM4JA31xx: ~/-- 10…1000 RM4JA32xx: ~/-- 1000…5000 | ~/-- 10…1000 | - | ~/-- 10…100 | Max 12A | Max 12A
|  | E3-M / B3-C | [5 empty] | mA | ~/-- 100…1000 | ~/-- 100…1000 | ~/-- 1500…15000 | ~/-- 1500…15000 | [5 empty] | ~/-- 50…500 | ~/-- 1500…15000 | RM4JA31xx: ~/-- 100…1000 RM4JA32xx: ~/-- 3000…15000 | ~/-- 100…1000 | - | ~/-- 50…500 | - | Not specified
|  | A1+ / A2- | [5 empty] | mA | - | - | - | -
|  | Built in current transformer | [5 empty] | mA | - | - | - | - | [5 empty] | - | - | - | - | ~ 2000…20000 | - | - | Not specified
Threshold |  | E1-M / B1-C | [5 empty] | mA | Adjustable 10%...100% of 40 | Adjustable 10%...100% of 40 | Adjustable 10%...100% of 1500 | Adjustable 10%...100% of 1500 | [5 empty] | Adjustable 10%...100% of 20 | Adjustable 10%...100% of 1500 | - | - | - | Adjustable 10%...100% of 20 | - | Not specified
|  | E2-M / B2-C | [5 empty] | mA | Adjustable 10%...100% of 200 | Adjustable 10%...100% of 200 | Adjustable 10%...100% of 5000 | Adjustable 10%...100% of 5000 | [5 empty] | Adjustable 10%...100% of 100 | Adjustable 10%...100% of 5000 | Adjustable 10%...100% | Adjustable 10%...100% | - | Adjustable 10%...100% of 100 | - | Not specified
|  | E3-M / B3-C | [5 empty] | mA | Adjustable 10%...100% of 1000 | Adjustable 10%...100% of 1000 | Adjustable 10%...100% of 15000 | Adjustable 10%...100% of 15000 | [5 empty] | Adjustable 10%...100% of 500 | Adjustable 10%...100% of 15000 | Adjustable 10%...100% | Adjustable 10%...100% | - | Adjustable 10%...100% of 500 | - | Not specified
|  | A1+ / A2- | [5 empty] | mA | - | - | - | -
|  | Built in current transformer | [5 empty] | mA | - | - | - | - | [5 empty] | - | - | - | - | Adjustable 10%...100% of 20000 | - | - | Not specified
Hysteresis |  | E1-M / B1-C | [5 empty] | mA | Adjustable 5%...50% of threshold setting | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | [5 empty] | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...30% of threshold setting | Adjustable 5%...30% of threshold setting | - | Adjustable 5%...50% of threshold setting | - | Not specified
|  | E2-M / B2-C | [5 empty] | mA | Adjustable 5%...50% of threshold setting | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | [5 empty] | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...30% of threshold setting | Adjustable 5%...30% of threshold setting | - | Adjustable 5%...50% of threshold setting | - | Not specified
|  | E3-M / B3-C | [5 empty] | mA | Adjustable 5%...50% of threshold setting | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | [5 empty] | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...30% of threshold setting | Adjustable 5%...30% of threshold setting | - | Adjustable 5%...50% of threshold setting | - | Not specified
|  | A1+ / A2- | [5 empty] | mA | - | - | - | -
|  | Built in current transformer | [5 empty] | mA | - | - | - | - | [5 empty] | - | - | - | - | Fixed 15% of threshold setting | - | - | Not specified
Measurement mode | [8 empty] | Shunt resistor | Shunt resistor | Shunt resistor | Shunt resistor | [5 empty] | Shunt resistor | Shunt resistor | Shunt resistor | Shunt resistor | Current transformer | Shunt resistor | Shunt resistor | Not specified
Connection terminals | [8 empty] | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | [5 empty] | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | B1-C, B2-C, B3-C | B1-C, B2-C, B3-C | Turning conductor around current transformer | E1-M, E2-M, E3-M | E2-M | Not specified
Rated frequency | [7 empty] | Hz | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | [5 empty] | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | Not specified
Frequency operating range | [7 empty] | Hz | 36…77 | 36…77 | 36…77 | 36…77 | [5 empty] | 36…77 | 36…77 | Not specified | Not specified | 40…70 | 36…77 | 36…77 | Not specified
Setting accuracy | [8 empty] | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value (For 1.5A and 5A) +/- 20% of full scale value (For 15A) | [5 empty] | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | Not specified
Repeat accuracy (constant parameters) | [8 empty] | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | [5 empty] | +/- 0.5% | +/- 0.5% | Not specified | Not specified | +/- 0.5% | +/- 0.5% | +/- 0.5% | Not specified
Measurement error with supply voltage variation | [7 empty] | %/V | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range | [5 empty] | < 1% over whole range | < 1% over whole range | < 0.5% over whole range | < 0.5% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range | Not specified
Measurement error with temperature variation | [7 empty] | %/oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | [5 empty] | 0.05% / oC | 0.05% / oC | 0.06% / oC | 0.06% / oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | Not specified
Maximum measuring cycles | [7 empty] | ms | 30 100 | 30 100 | 30 100 | 30 100 | [5 empty] | 30 | 30 | 80 | 80 | 30 | 30 | 30 | Not specified
Measurement method | [8 empty] | True RMS | True RMS | True RMS | True RMS | [5 empty] | True RMS | True RMS | True RMS | True RMS | True RMS | True RMS | True RMS | Not specified
Output Circuit Characteristics
Type of output |  |  |  |  | output type | Published | Published |  | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | [5 empty] | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 1 x C/O relay contacts | 2 x C/O relay contacts | 21x C/O relay contacts | 1 x C/O relay contacts
Output terminal |  |  |  |  | output terminal |  |  |  | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | [5 empty] | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14 | 11-12-14, 21-22-24 | 2014-11-12 | 11-12-14
Operation principle |  | R1 (11-12-14) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | [5 empty] | Energized on fault-free | Energized on fault-free | De-Energized on fault-free | De-Energized on fault-free | Selectable energized/de-energized on fault-free | Energized on fault-free | Energized on fault-free | De-Energized on fault-free
|  | R2 (21-22-24) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free
Contact material |  |  |  | Common C_Rly Spec | contacts material | Published | Published |  | Cadmium free | Cadmium free | Cadmium free | Cadmium free | [5 empty] | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Not specified
Mechanical durability |  |  | IEC61810-1 | Common C_Rly Spec | mechanical durability | Published | Published | Cyc | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | [5 empty] | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | Not specified
Electrical durability |  | AC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | [5 empty] | 1 x 105 switching cycles | 1 x 105 switching cycles | 1 x 105 switching cycles | 1 x 105 switching cycles | 1 x 105 switching cycles | 1 x 105 switching cycles | 1 x 105 switching cycles | Not specified
|  | DC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles
|  | AC-15 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles
|  | DC-13 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles
Rated capacity |  | Rated switching voltage | IEC61810-1 | Common C_Rly Spec | [Ue] rated operational voltage | Published |  | V | 250V | 250V | 250V | 250V
|  | Rated switching current | IEC61810-1 | Common C_Rly Spec | [Ie] rated operational current | Published | Published | A | 8A | 8A | 8A | 8A
Maximum switching capacity |  | Maximum switching voltage |  | Common C_Rly Spec | maximum switching capacity | Published | Published | V | 250V | 250V | 250V | 250V | [5 empty] | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250
|  | Maximum switching current |  | Common C_Rly Spec | maximum switching capacity | Published | Published | A | 8A | 8A | 8A | 8A | [5 empty] | 5 | ~ 5 | ~ 5 | 8 | 8 | ~ 8 | ~ 5 | ~ 5
|  | Maximum switching capacity |  | Common C_Rly Spec | maximum switching capacity | Published | Published | VA | - | - | - | - | [5 empty] | 1250 | 1250 | 1250 | 2000 | 2000 | 2000 | 1250 | 1250
Minimum switching capacity |  | Minimum switching voltage | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | V | - | - | - | - | [5 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | Not specified
|  | Minimum switching current | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | mA | - | - | - | - | [5 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | Not specified
|  | Minimum switching capacity | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published | Published | mW | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | [5 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | Not specified
Maximum voltage drop at terminals |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum voltage drop |  |  | V | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | -
Leakage current |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum leakage current |  |  | mA | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | -
Thermal Current |  |  | IEC60947-5-1 | Common C_Rly Spec | thermal current |  |  | A | 8A | 8A | 8A | 8A
Short circuit protection |  | Relay Output by external fuse | IEC60947-5-1 | Common C_Rly Spec | short circuit protection |  |  | gG | 8A | 8A | 8A | 8A
|  | Solid State Output by external fuse | IEC62314 | Common C_Rly Spec | short circuit protection |  |  | gG | - | - | - | -
Time Delay Characteristics
Time delay functions |  | "OFF" delay |  |  | time delay type | Published |  |  | Yes | Yes | Yes | Yes | [5 empty] | · | · | · | · | - | · | - | -
|  | "ON" delay |  |  | time delay type | Published |  |  | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | -
|  | Inhibition |  |  | time delay type | Published |  |  | - | - | - | - | [5 empty] | · | · | · | · | - | · | - | -
Timing range |  | "OFF" delay |  |  | time delay range | Published | Published | s | - | Adjustable 0.1…30 | Adjustable 0.1…30 | Adjustable 0.1…30 | [5 empty] | Adjustable 0.3…30 | Adjustable 0.3…30 | Adjustable 0…30 | Adjustable 0…30 | - | Adjustable 0.3…30 | - | -
|  | "ON" delay |  |  | time delay range | Published |  | s | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | -
|  | Inhibition |  |  | time delay range | Published | Published | s | - | - | - | - | [5 empty] | Adjustable 1…20 | Adjustable 1…20 | Adjustable 1…20 | Adjustable 1…20 | - | Adjustable 1…20 | - | -
Response time |  | on crossing the threshold |  |  | response time | Published | Published | ms | Not specified =< 500ms | Not specified =< 500ms | Not specified =< 500ms | Not specified =< 500ms | [5 empty] | Not specified | Not specified | Not specified | Not specified | 0 | Not specified | Not specified | Not specified
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
Time delay of pick-up |  |  |  |  | power on delay | Published | Published | ms | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Not specified
Reset time |  | through Un power reset |  |  | reset time | Published | Published | ms | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | - | 0 | 0 | Not specified
|  | through front panel reset |  | Reserved for other products | reset time | Published
|  | through input control reset |  | Reserved for other products | reset time | Published
Setting accuracy |  |  |  | Common C_Rly Spec | setting accuracy of time delay | Published | Published | % | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | [5 empty] | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | - | +/- 10% of full scales | +/- 10% of full scales | Not specified
Repeat accuracy (constant parameters) |  |  |  | Common C_Rly Spec | repeat accuracy of time delay | Published |  | % | +/- 2% | +/- 2% | +/- 2% | +/- 2% | [5 empty] | +/- 2% | +/- 2% | +/- 0.5% | +/- 0.5% | - | +/- 2% | +/- 2% | Not specified
Timing error with supply voltage variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/V | < 1 | < 1 | < 1 | < 1 | [5 empty] | Not specified | Not specified | < 0.5% over whole range | < 0.5% over whole range | - | Not specified | Not specified | Not specified
Timing error with temperature variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/oC | < 0.05 | < 0.05 | < 0.05 | < 0.05 | [5 empty] | Not specified | Not specified | 0.07% / oC | 0.07% / oC | - | Not specified | Not specified | Not specified
LED Indication
status LED |  |  |  |  | status LED |  |  |  | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber)
local signalling |  | Power supply availability |  |  | local signalling |  |  |  | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON
|  | Power supply not availability |  |  | local signalling |  |  |  | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF
|  | Timing in-progress |  |  | local signalling |  |  |  | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz
|  | Output is energized |  |  | local signalling |  |  |  | R - ON | R - ON | R - ON | R - ON
|  | Output is de-energized |  |  | local signalling |  |  |  | R - OFF | R - OFF | R - OFF | R - OFF
|  | Range Setting Changes |  |  | local signalling |  |  |  | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
Special Features
True RMS | [8 empty] | Yes | Yes | Yes | Yes
Backlight Indicator | [8 empty] | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product
Diagnostic Button |  |  |  |  | diagnostic button | Published |  |  | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated
Pre-Alarm Output | [8 empty] | - | - | - | -
Output | [8 empty] | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
Reliability Data
Reliability Data |  | MTTF |  |  | safety reliability data | Published |  |  | 2,600,000 hours | 2,600,000 hours | 2,600,000 hours | 2,600,000 hours
|  | B10 |  |  | safety reliability data | Published |  |  | 270,000 hours | 270,000 hours | 270,000 hours | 270,000 hours
|  | MTTFd | [6 empty] | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product)
|  | B10d | [6 empty] | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product)
Drawing / Diagram