## status
0 | RM17JC00MW | https://www.se.com/ww/en/product/RM17JC00MW/ | Found
1 | RM17TA00 | https://www.se.com/ww/en/product/RM17TA00/ | Found
2 | RM17TE00 | https://www.se.com/ww/en/product/RM17TE00/ | Found
3 | RM10TE00 | https://www.se.com/ww/en/product/RM10TE00/ | Not Found
4 | RM10TE00 | https://www.se.com/us/en/product/RM10TE00/ | Not Found
5 | RM10TE00 | https://www.se.com/in/en/product/RM10TE00/ | Found
6 | RE22R2AMR | https://www.se.com/ww/en/product/RE22R2AMR/ | Found
7 | RE22R2CMR | https://www.se.com/ww/en/product/RE22R2CMR/ | Found
8 | RMTJ60BD | https://www.se.com/ww/en/product/RMTJ60BD/ | Found
9 | XVDLS37 | https://www.se.com/ww/en/product/XVDLS37/ | Found
10 | XVDLS38 | https://www.se.com/ww/en/product/XVDLS38/ | Found
11 | RHT428B | https://www.se.com/ww/en/product/RHT428B/ | Found
12 | RHT418BE | https://www.se.com/ww/en/product/RHT418BE/ | Found
13 | RSB1A160M7S | https://www.se.com/ww/en/product/RSB1A160M7S/ | Found
14 | RSB1A160NDS | https://www.se.com/ww/en/product/RSB1A160NDS/ | Found
15 | RSB2A080P7S | https://www.se.com/ww/en/product/RSB2A080P7S/ | Found
16 | RSB2A080RDS | https://www.se.com/ww/en/product/RSB2A080RDS/ | Found
17 | RSB2A080U7S | https://www.se.com/ww/en/product/RSB2A080U7S/ | Found
18 | RSB2A080M7S | https://www.se.com/ww/en/product/RSB2A080M7S/ | Found
19 | RXG11RD | https://www.se.com/ww/en/product/RXG11RD/ | Found
20 | RXM2AB1B7 | https://www.se.com/ww/en/product/RXM2AB1B7/ | Found
21 | RXM4AB1B7 | https://www.se.com/ww/en/product/RXM4AB1B7/ | Found

## raw_datasheet
| Reference | Section | Parameters | Value | Param_ID
0 | RM17JC00MW | Main | range of product | Zelio Control | RM17JC00MWrange of product
1 | RM17JC00MW | Main | product or component type | Modular measurement and control relays | RM17JC00MWproduct or component type
2 | RM17JC00MW | Main | relay type | Current control relay | RM17JC00MWrelay type
3 | RM17JC00MW | Main | relay name | RM17JC | RM17JC00MWrelay name
4 | RM17JC00MW | Main | relay monitored parameters | Overcurrent detection | RM17JC00MWrelay monitored parameters
5 | RM17JC00MW | Main | time delay | Without | RM17JC00MWtime delay
6 | RM17JC00MW | Main | switching capacity in VA | 1250 VA | RM17JC00MWswitching capacity in VA
7 | RM17JC00MW | Main | minimum switching current | 10 mA at 5 V DC | RM17JC00MWminimum switching current
8 | RM17JC00MW | Main | maximum power consumption in VA | 3 VA | RM17JC00MWmaximum power consumption in VA
9 | RM17JC00MW | Main | measurement range | 2...20 A current | RM17JC00MWmeasurement range
10 | RM17JC00MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1 | RM17JC00MWutilisation category
11 | RM17JC00MW | Complementary | maximum switching voltage | 250 V AC/DC | RM17JC00MWmaximum switching voltage
12 | RM17JC00MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 % | RM17JC00MW[Us] rated supply voltage
13 | RM17JC00MW | Complementary | supply voltage limits | 20.4…264 V AC/DC | RM17JC00MWsupply voltage limits
14 | RM17JC00MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un | RM17JC00MWoperating voltage tolerance
15 | RM17JC00MW | Complementary | maximum power consumption in W | 1 W | RM17JC00MWmaximum power consumption in W
16 | RM17JC00MW | Complementary | control circuit frequency | 40...70 Hz sinusoidal | RM17JC00MWcontrol circuit frequency
17 | RM17JC00MW | Complementary | output contacts | 1 C/O | RM17JC00MWoutput contacts
18 | RM17JC00MW | Complementary | nominal output current | 5 A | RM17JC00MWnominal output current
19 | RM17JC00MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value | RM17JC00MWmaximum measuring cycle
20 | RM17JC00MW | Complementary | hysteresis | 15 % fixed of threshold setting | RM17JC00MWhysteresis
21 | RM17JC00MW | Complementary | delay at power up | 0.5 s | RM17JC00MWdelay at power up
22 | RM17JC00MW | Complementary | measurement accuracy | +/- 10 % of the full scale value | RM17JC00MWmeasurement accuracy
23 | RM17JC00MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit | RM17JC00MWrepeat accuracy
24 | RM17JC00MW | Complementary | measurement error | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | RM17JC00MWmeasurement error
25 | RM17JC00MW | Complementary | response time | < 200 ms (in the event of a fault) | RM17JC00MWresponse time
26 | RM17JC00MW | Complementary | polarity | Yes DC | RM17JC00MWpolarity
27 | RM17JC00MW | Complementary | threshold setting | 10...100 % | RM17JC00MWthreshold setting
28 | RM17JC00MW | Complementary | input current | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C | RM17JC00MWinput current
29 | RM17JC00MW | Complementary | marking | CE : 73/23/EEC CE : EMC 89/336/EEC | RM17JC00MWmarking
30 | RM17JC00MW | Complementary | overvoltage category | III conforming to IEC 60664-1 | RM17JC00MWovervoltage category
31 | RM17JC00MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | RM17JC00MWinsulation resistance
32 | RM17JC00MW | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1 | RM17JC00MW[Ui] rated insulation voltage
33 | RM17JC00MW | Complementary | insulation | Between supply and measurement | RM17JC00MWinsulation
34 | RM17JC00MW | Complementary | operating position | Any position without derating | RM17JC00MWoperating position
35 | RM17JC00MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | RM17JC00MWconnections - terminals
36 | RM17JC00MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | RM17JC00MWtightening torque
37 | RM17JC00MW | Complementary | housing material | Self-extinguishing plastic | RM17JC00MWhousing material
38 | RM17JC00MW | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON | RM17JC00MWlocal signalling
39 | RM17JC00MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | RM17JC00MWmounting support
40 | RM17JC00MW | Complementary | electrical durability | 100000 cycles | RM17JC00MWelectrical durability
41 | RM17JC00MW | Complementary | mechanical durability | 30000000 cycles | RM17JC00MWmechanical durability
42 | RM17JC00MW | Complementary | operating rate | <= 360 operations/hour full load | RM17JC00MWoperating rate
43 | RM17JC00MW | Complementary | contacts material | Cadmium free | RM17JC00MWcontacts material
44 | RM17JC00MW | Complementary | width | 17.5 mm | RM17JC00MWwidth
45 | RM17JC00MW | Complementary | net weight | 0.13 kg | RM17JC00MWnet weight
46 | RM17JC00MW | Environment | immunity to microbreaks | 10 ms | RM17JC00MWimmunity to microbreaks
47 | RM17JC00MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | RM17JC00MWelectromagnetic compatibility
48 | RM17JC00MW | Environment | standards | EN/IEC 60255-6 | RM17JC00MWstandards
49 | RM17JC00MW | Environment | product certifications | GL C-Tick GOST UL CSA | RM17JC00MWproduct certifications
50 | RM17JC00MW | Environment | ambient air temperature for storage | -40…70 °C | RM17JC00MWambient air temperature for storage
51 | RM17JC00MW | Environment | ambient air temperature for operation | -20…50 °C | RM17JC00MWambient air temperature for operation
52 | RM17JC00MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30 | RM17JC00MWrelative humidity
53 | RM17JC00MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | RM17JC00MWvibration resistance
54 | RM17JC00MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1 | RM17JC00MWshock resistance
55 | RM17JC00MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | RM17JC00MWIP degree of protection
56 | RM17JC00MW | Environment | pollution degree | 3 conforming to IEC 60664-1 | RM17JC00MWpollution degree
57 | RM17JC00MW | Environment | dielectric test voltage | 2 kV AC 50 Hz | RM17JC00MWdielectric test voltage
58 | RM17JC00MW | Environment | non-dissipating shock wave | 4 kV | RM17JC00MWnon-dissipating shock wave
59 | RM17JC00MW | Packing Units | Package 1 Weight | 120 g | RM17JC00MWPackage 1 Weight
60 | RM17JC00MW | Packing Units | Package 2 Weight | 4.295 kg | RM17JC00MWPackage 2 Weight
61 | RM17JC00MW | Offer Sustainability | Sustainable offer status | Green Premium product | RM17JC00MWSustainable offer status
62 | RM17JC00MW | Offer Sustainability | REACh Regulation | REACh Declaration | RM17JC00MWREACh Regulation
63 | RM17JC00MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RM17JC00MWEU RoHS Directive
64 | RM17JC00MW | Offer Sustainability | Mercury free | Yes | RM17JC00MWMercury free
65 | RM17JC00MW | Offer Sustainability | RoHS exemption information | Yes | RM17JC00MWRoHS exemption information
66 | RM17JC00MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RM17JC00MWChina RoHS Regulation
67 | RM17JC00MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RM17JC00MWEnvironmental Disclosure
68 | RM17JC00MW | Offer Sustainability | Circularity Profile | End of Life Information | RM17JC00MWCircularity Profile
69 | RM17JC00MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RM17JC00MWWEEE
70 | RM17JC00MW | Contractual warranty | Warranty | 18 months | RM17JC00MWWarranty
71 | RM17TA00 | Main | range of product | Zelio Control | RM17TA00range of product
72 | RM17TA00 | Main | product or component type | Modular measurement and control relays | RM17TA00product or component type
73 | RM17TA00 | Main | relay type | Multifunction control relay | RM17TA00relay type
74 | RM17TA00 | Main | product specific application | For 3-phase supply | RM17TA00product specific application
75 | RM17TA00 | Main | relay name | RM17TA | RM17TA00relay name
76 | RM17TA00 | Main | relay monitored parameters | Asymmetry Phase sequence Phase failure detection | RM17TA00relay monitored parameters
77 | RM17TA00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value | RM17TA00time delay
78 | RM17TA00 | Main | switching capacity in VA | 1250 VA | RM17TA00switching capacity in VA
79 | RM17TA00 | Main | measurement range | 208...480 V voltage AC | RM17TA00measurement range
80 | RM17TA00 | Complementary | reset time | 1500 ms time delay | RM17TA00reset time
81 | RM17TA00 | Complementary | maximum switching voltage | 250 V AC 250 V DC | RM17TA00maximum switching voltage
82 | RM17TA00 | Complementary | minimum switching current | 10 mA at 5 V DC | RM17TA00minimum switching current
83 | RM17TA00 | Complementary | maximum switching current | 5 A AC 5 A DC | RM17TA00maximum switching current
84 | RM17TA00 | Complementary | supply voltage limits | 183…528 V AC | RM17TA00supply voltage limits
85 | RM17TA00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un | RM17TA00control circuit voltage limits
86 | RM17TA00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz | RM17TA00power consumption in VA
87 | RM17TA00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 % | RM17TA00control circuit frequency
88 | RM17TA00 | Complementary | output contacts | 1 C/O | RM17TA00output contacts
89 | RM17TA00 | Complementary | nominal output current | 5 A | RM17TA00nominal output current
90 | RM17TA00 | Complementary | measurement voltage limits | 183…528 V AC | RM17TA00measurement voltage limits
91 | RM17TA00 | Complementary | hysteresis | 2 % | RM17TA00hysteresis
92 | RM17TA00 | Complementary | delay at power up | 650 ms | RM17TA00delay at power up
93 | RM17TA00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value | RM17TA00maximum measuring cycle
94 | RM17TA00 | Complementary | threshold adjustment voltage | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC | RM17TA00threshold adjustment voltage
95 | RM17TA00 | Complementary | voltage range | 208...480 V phase to phase | RM17TA00voltage range
96 | RM17TA00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected | RM17TA00adjustment of asymmetry threshold
97 | RM17TA00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit 3 % for time delay | RM17TA00repeat accuracy
98 | RM17TA00 | Complementary | measurement error | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | RM17TA00measurement error
99 | RM17TA00 | Complementary | phase failure sensitivity | 0.7 Un | RM17TA00phase failure sensitivity
100 | RM17TA00 | Complementary | response time | < 200 ms (in the event of a fault) | RM17TA00response time
101 | RM17TA00 | Complementary | marking | CE | RM17TA00marking
102 | RM17TA00 | Complementary | overvoltage category | III conforming to IEC 60664-1 | RM17TA00overvoltage category
103 | RM17TA00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | RM17TA00insulation resistance
104 | RM17TA00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1 | RM17TA00[Ui] rated insulation voltage
105 | RM17TA00 | Complementary | supply frequency | 50/60 Hz +/- 10 % | RM17TA00supply frequency
106 | RM17TA00 | Complementary | operating position | Any position without derating | RM17TA00operating position
107 | RM17TA00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | RM17TA00connections - terminals
108 | RM17TA00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | RM17TA00tightening torque
109 | RM17TA00 | Complementary | housing material | Self-extinguishing plastic | RM17TA00housing material
110 | RM17TA00 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON | RM17TA00local signalling
111 | RM17TA00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | RM17TA00mounting support
112 | RM17TA00 | Complementary | electrical durability | 100000 cycles | RM17TA00electrical durability
113 | RM17TA00 | Complementary | mechanical durability | 30000000 cycles | RM17TA00mechanical durability
114 | RM17TA00 | Complementary | operating rate | <= 360 operations/hour full load | RM17TA00operating rate
115 | RM17TA00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | RM17TA00utilisation category
116 | RM17TA00 | Complementary | safety reliability data | MTTFd = 502.2 years B10d = 470000 | RM17TA00safety reliability data
117 | RM17TA00 | Complementary | width | 17.5 mm | RM17TA00width
118 | RM17TA00 | Complementary | net weight | 0.13 kg | RM17TA00net weight
119 | RM17TA00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | RM17TA00electromagnetic compatibility
120 | RM17TA00 | Environment | standards | EN/IEC 60255-1 | RM17TA00standards
121 | RM17TA00 | Environment | product certifications | GOST CSA GL C-Tick UL | RM17TA00product certifications
122 | RM17TA00 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | RM17TA00directives
123 | RM17TA00 | Environment | ambient air temperature for storage | -40…70 °C | RM17TA00ambient air temperature for storage
124 | RM17TA00 | Environment | ambient air temperature for operation | -20…50 °C | RM17TA00ambient air temperature for operation
125 | RM17TA00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30 | RM17TA00relative humidity
126 | RM17TA00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | RM17TA00vibration resistance
127 | RM17TA00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1 | RM17TA00shock resistance
128 | RM17TA00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | RM17TA00IP degree of protection
129 | RM17TA00 | Environment | pollution degree | 3 conforming to IEC 60664-1 | RM17TA00pollution degree
130 | RM17TA00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | RM17TA00dielectric test voltage
131 | RM17TA00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | RM17TA00non-dissipating shock wave
132 | RM17TA00 | Packing Units | Package 1 Weight | 89 g | RM17TA00Package 1 Weight
133 | RM17TA00 | Packing Units | Package 2 Weight | 4.685 kg | RM17TA00Package 2 Weight
134 | RM17TA00 | Offer Sustainability | Sustainable offer status | Green Premium product | RM17TA00Sustainable offer status
135 | RM17TA00 | Offer Sustainability | REACh Regulation | REACh Declaration | RM17TA00REACh Regulation
136 | RM17TA00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RM17TA00EU RoHS Directive
137 | RM17TA00 | Offer Sustainability | Mercury free | Yes | RM17TA00Mercury free
138 | RM17TA00 | Offer Sustainability | RoHS exemption information | Yes | RM17TA00RoHS exemption information
139 | RM17TA00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RM17TA00China RoHS Regulation
140 | RM17TA00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RM17TA00Environmental Disclosure
141 | RM17TA00 | Offer Sustainability | Circularity Profile | End of Life Information | RM17TA00Circularity Profile
142 | RM17TA00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RM17TA00WEEE
143 | RM17TA00 | Contractual warranty | Warranty | 18 months | RM17TA00Warranty
144 | RM17TE00 | Main | range of product | Zelio Control | RM17TE00range of product
145 | RM17TE00 | Main | product or component type | Modular measurement and control relays | RM17TE00product or component type
146 | RM17TE00 | Main | relay type | Multifunction control relay | RM17TE00relay type
147 | RM17TE00 | Main | product specific application | For 3-phase supply | RM17TE00product specific application
148 | RM17TE00 | Main | relay name | RM17TE | RM17TE00relay name
149 | RM17TE00 | Main | relay monitored parameters | Undervoltage and overvoltage in window mode Asymmetry Phase sequence Phase failure detection | RM17TE00relay monitored parameters
150 | RM17TE00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value | RM17TE00time delay
151 | RM17TE00 | Main | switching capacity in VA | 1250 VA | RM17TE00switching capacity in VA
152 | RM17TE00 | Main | measurement range | 208...480 V voltage AC | RM17TE00measurement range
153 | RM17TE00 | Complementary | reset time | 1500 ms time delay | RM17TE00reset time
154 | RM17TE00 | Complementary | maximum switching voltage | 250 V AC 250 V DC | RM17TE00maximum switching voltage
155 | RM17TE00 | Complementary | minimum switching current | 10 mA at 5 V DC | RM17TE00minimum switching current
156 | RM17TE00 | Complementary | maximum switching current | 5 A AC 5 A DC | RM17TE00maximum switching current
157 | RM17TE00 | Complementary | supply voltage limits | 183…528 V AC | RM17TE00supply voltage limits
158 | RM17TE00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un | RM17TE00control circuit voltage limits
159 | RM17TE00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz | RM17TE00power consumption in VA
160 | RM17TE00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 % | RM17TE00control circuit frequency
161 | RM17TE00 | Complementary | output contacts | 1 C/O | RM17TE00output contacts
162 | RM17TE00 | Complementary | nominal output current | 5 A | RM17TE00nominal output current
163 | RM17TE00 | Complementary | measurement voltage limits | 183…528 V AC | RM17TE00measurement voltage limits
164 | RM17TE00 | Complementary | hysteresis | 2 % | RM17TE00hysteresis
165 | RM17TE00 | Complementary | delay at power up | 650 ms | RM17TE00delay at power up
166 | RM17TE00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value | RM17TE00maximum measuring cycle
167 | RM17TE00 | Complementary | threshold adjustment voltage | -2...-17 % in the range 220 V AC +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC 2...20 % of Un selected | RM17TE00threshold adjustment voltage
168 | RM17TE00 | Complementary | voltage range | 208...480 V phase to phase | RM17TE00voltage range
169 | RM17TE00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected | RM17TE00adjustment of asymmetry threshold
170 | RM17TE00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit 3 % for time delay | RM17TE00repeat accuracy
171 | RM17TE00 | Complementary | measurement error | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | RM17TE00measurement error
172 | RM17TE00 | Complementary | phase failure sensitivity | 0.7 Un | RM17TE00phase failure sensitivity
173 | RM17TE00 | Complementary | response time | < 200 ms (in the event of a fault) | RM17TE00response time
174 | RM17TE00 | Complementary | marking | CE | RM17TE00marking
175 | RM17TE00 | Complementary | overvoltage category | III conforming to IEC 60664-1 | RM17TE00overvoltage category
176 | RM17TE00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | RM17TE00insulation resistance
177 | RM17TE00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1 | RM17TE00[Ui] rated insulation voltage
178 | RM17TE00 | Complementary | supply frequency | 50/60 Hz +/- 10 % | RM17TE00supply frequency
179 | RM17TE00 | Complementary | operating position | Any position without derating | RM17TE00operating position
180 | RM17TE00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | RM17TE00connections - terminals
181 | RM17TE00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | RM17TE00tightening torque
182 | RM17TE00 | Complementary | housing material | Self-extinguishing plastic | RM17TE00housing material
183 | RM17TE00 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON | RM17TE00local signalling
184 | RM17TE00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | RM17TE00mounting support
185 | RM17TE00 | Complementary | electrical durability | 100000 cycles | RM17TE00electrical durability
186 | RM17TE00 | Complementary | mechanical durability | 30000000 cycles | RM17TE00mechanical durability
187 | RM17TE00 | Complementary | operating rate | <= 360 operations/hour full load | RM17TE00operating rate
188 | RM17TE00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | RM17TE00utilisation category
189 | RM17TE00 | Complementary | safety reliability data | MTTFd = 502.2 years B10d = 470000 | RM17TE00safety reliability data
190 | RM17TE00 | Complementary | width | 17.5 mm | RM17TE00width
191 | RM17TE00 | Complementary | net weight | 0.13 kg | RM17TE00net weight
192 | RM17TE00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | RM17TE00electromagnetic compatibility
193 | RM17TE00 | Environment | standards | EN/IEC 60255-1 | RM17TE00standards
194 | RM17TE00 | Environment | product certifications | GOST C-Tick CSA UL GL | RM17TE00product certifications
195 | RM17TE00 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | RM17TE00directives
196 | RM17TE00 | Environment | ambient air temperature for storage | -40…70 °C | RM17TE00ambient air temperature for storage
197 | RM17TE00 | Environment | ambient air temperature for operation | -20…50 °C | RM17TE00ambient air temperature for operation
198 | RM17TE00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30 | RM17TE00relative humidity
199 | RM17TE00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | RM17TE00vibration resistance
200 | RM17TE00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1 | RM17TE00shock resistance
201 | RM17TE00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | RM17TE00IP degree of protection
202 | RM17TE00 | Environment | pollution degree | 3 conforming to IEC 60664-1 | RM17TE00pollution degree
203 | RM17TE00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | RM17TE00dielectric test voltage
204 | RM17TE00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | RM17TE00non-dissipating shock wave
205 | RM17TE00 | Packing Units | Package 1 Weight | 89 g | RM17TE00Package 1 Weight
206 | RM17TE00 | Packing Units | Package 2 Weight | 5.017 kg | RM17TE00Package 2 Weight
207 | RM17TE00 | Offer Sustainability | Sustainable offer status | Green Premium product | RM17TE00Sustainable offer status
208 | RM17TE00 | Offer Sustainability | REACh Regulation | REACh Declaration | RM17TE00REACh Regulation
209 | RM17TE00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RM17TE00EU RoHS Directive
210 | RM17TE00 | Offer Sustainability | Mercury free | Yes | RM17TE00Mercury free
211 | RM17TE00 | Offer Sustainability | RoHS exemption information | Yes | RM17TE00RoHS exemption information
212 | RM17TE00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RM17TE00China RoHS Regulation
213 | RM17TE00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RM17TE00Environmental Disclosure
214 | RM17TE00 | Offer Sustainability | Circularity Profile | End of Life Information | RM17TE00Circularity Profile
215 | RM17TE00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RM17TE00WEEE
216 | RM17TE00 | Contractual warranty | Warranty | 18 months | RM17TE00Warranty
217 | RM10TE00 | Main | range of product | Zelio Control | RM10TE00range of product
218 | RM10TE00 | Main | product or component type | Modular measurement and control relays | RM10TE00product or component type
219 | RM10TE00 | Main | relay type | Multifunction control relay | RM10TE00relay type
220 | RM10TE00 | Main | product specific application | For 3-phase supply | RM10TE00product specific application
221 | RM10TE00 | Main | relay name | RM10TE | RM10TE00relay name
222 | RM10TE00 | Main | relay monitored parameters | Phase sequence Asymmetry Undervoltage and overvoltage in window mode Phase failure detection | RM10TE00relay monitored parameters
223 | RM10TE00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value | RM10TE00time delay
224 | RM10TE00 | Main | switching capacity in VA | 1250 VA | RM10TE00switching capacity in VA
225 | RM10TE00 | Main | measurement range | 183...528 V AC | RM10TE00measurement range
226 | RM10TE00 | Complementary | reset time | 1500 ms time delay | RM10TE00reset time
227 | RM10TE00 | Complementary | maximum switching voltage | 250 V AC 250 V DC | RM10TE00maximum switching voltage
228 | RM10TE00 | Complementary | minimum switching current | 10 mA at 5 V DC | RM10TE00minimum switching current
229 | RM10TE00 | Complementary | maximum switching current | 5 A AC 5 A DC | RM10TE00maximum switching current
230 | RM10TE00 | Complementary | supply voltage limits | 183…528 V AC | RM10TE00supply voltage limits
231 | RM10TE00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un | RM10TE00control circuit voltage limits
232 | RM10TE00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz | RM10TE00power consumption in VA
233 | RM10TE00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 % | RM10TE00control circuit frequency
234 | RM10TE00 | Complementary | output contacts | 1 C/O | RM10TE00output contacts
235 | RM10TE00 | Complementary | nominal output current | 5 A | RM10TE00nominal output current
236 | RM10TE00 | Complementary | hysteresis | 2 % | RM10TE00hysteresis
237 | RM10TE00 | Complementary | delay at power up | 650 ms | RM10TE00delay at power up
238 | RM10TE00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value | RM10TE00maximum measuring cycle
239 | RM10TE00 | Complementary | threshold adjustment voltage | -2...-12 % in the range 208 V AC 2...20 % of Un selected +2...+17 % in the range 480 V AC -2...-17 % in the range 220 V AC | RM10TE00threshold adjustment voltage
240 | RM10TE00 | Complementary | voltage range | 208...480 V phase to phase | RM10TE00voltage range
241 | RM10TE00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected | RM10TE00adjustment of asymmetry threshold
242 | RM10TE00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit 3 % for time delay | RM10TE00repeat accuracy
243 | RM10TE00 | Complementary | measurement error | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | RM10TE00measurement error
244 | RM10TE00 | Complementary | phase failure sensitivity | 0.7 Un | RM10TE00phase failure sensitivity
245 | RM10TE00 | Complementary | response time | < 200 ms (in the event of a fault) | RM10TE00response time
246 | RM10TE00 | Complementary | marking | CE | RM10TE00marking
247 | RM10TE00 | Complementary | overvoltage category | III conforming to IEC 60664-1 | RM10TE00overvoltage category
248 | RM10TE00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | RM10TE00insulation resistance
249 | RM10TE00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1 | RM10TE00[Ui] rated insulation voltage
250 | RM10TE00 | Complementary | supply frequency | 50/60 Hz +/- 10 % | RM10TE00supply frequency
251 | RM10TE00 | Complementary | operating position | Any position without derating | RM10TE00operating position
252 | RM10TE00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | RM10TE00connections - terminals
253 | RM10TE00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | RM10TE00tightening torque
254 | RM10TE00 | Complementary | housing material | Self-extinguishing plastic | RM10TE00housing material
255 | RM10TE00 | Complementary | local signalling | LED (green)power ON: LED (yellow)relay ON: | RM10TE00local signalling
256 | RM10TE00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | RM10TE00mounting support
257 | RM10TE00 | Complementary | electrical durability | 100000 cycles | RM10TE00electrical durability
258 | RM10TE00 | Complementary | mechanical durability | 30000000 cycles | RM10TE00mechanical durability
259 | RM10TE00 | Complementary | operating rate | <= 360 operations/hour full load | RM10TE00operating rate
260 | RM10TE00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | RM10TE00utilisation category
261 | RM10TE00 | Complementary | safety reliability data | B10d = 470000 MTTFd = 502.2 years | RM10TE00safety reliability data
262 | RM10TE00 | Complementary | width | 17.5 mm | RM10TE00width
263 | RM10TE00 | Complementary | net weight | 0.13 kg | RM10TE00net weight
264 | RM10TE00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | RM10TE00electromagnetic compatibility
265 | RM10TE00 | Environment | standards | EN/IEC 60255-1 | RM10TE00standards
266 | RM10TE00 | Environment | product certifications | C-Tick UL GOST CSA GL | RM10TE00product certifications
267 | RM10TE00 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | RM10TE00directives
268 | RM10TE00 | Environment | ambient air temperature for storage | -40…70 °C | RM10TE00ambient air temperature for storage
269 | RM10TE00 | Environment | ambient air temperature for operation | -20…50 °C | RM10TE00ambient air temperature for operation
270 | RM10TE00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30 | RM10TE00relative humidity
271 | RM10TE00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | RM10TE00vibration resistance
272 | RM10TE00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1 | RM10TE00shock resistance
273 | RM10TE00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | RM10TE00IP degree of protection
274 | RM10TE00 | Environment | pollution degree | 3 conforming to IEC 60664-1 | RM10TE00pollution degree
275 | RM10TE00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | RM10TE00dielectric test voltage
276 | RM10TE00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | RM10TE00non-dissipating shock wave
277 | RM10TE00 | Offer Sustainability | Sustainable offer status | Green Premium product | RM10TE00Sustainable offer status
278 | RM10TE00 | Offer Sustainability | REACh Regulation | REACh Declaration | RM10TE00REACh Regulation
279 | RM10TE00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RM10TE00EU RoHS Directive
280 | RM10TE00 | Offer Sustainability | Mercury free | Yes | RM10TE00Mercury free
281 | RM10TE00 | Offer Sustainability | RoHS exemption information | Yes | RM10TE00RoHS exemption information
282 | RM10TE00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RM10TE00China RoHS Regulation
283 | RM10TE00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RM10TE00Environmental Disclosure
284 | RM10TE00 | Offer Sustainability | Circularity Profile | End of Life Information | RM10TE00Circularity Profile
285 | RM10TE00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RM10TE00WEEE
286 | RE22R2AMR | Main | range of product | Zelio Time | RE22R2AMRrange of product
287 | RE22R2AMR | Main | product or component type | Modular timing relay | RE22R2AMRproduct or component type
288 | RE22R2AMR | Main | discrete output type | Relay | RE22R2AMRdiscrete output type
289 | RE22R2AMR | Main | device short name | RE22 | RE22R2AMRdevice short name
290 | RE22R2AMR | Main | nominal output current | 8 A | RE22R2AMRnominal output current
291 | RE22R2AMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free | RE22R2AMRcontacts type and composition
292 | RE22R2AMR | Complementary | time delay type | Aw A | RE22R2AMRtime delay type
293 | RE22R2AMR | Complementary | time delay range | 0.05...1 s 0.3...3 s 3...30 h 30...300 min 10...100 s 30...300 s 3...30 s 30...300 h 1...10 s 3...30 min | RE22R2AMRtime delay range
294 | RE22R2AMR | Complementary | control type | Rotary knob Diagnostic button Potentiometer external | RE22R2AMRcontrol type
295 | RE22R2AMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz | RE22R2AMR[Us] rated supply voltage
296 | RE22R2AMR | Complementary | Release input voltage | <= 2.4 V | RE22R2AMRRelease input voltage
297 | RE22R2AMR | Complementary | voltage range | 0.85...1.1 Us | RE22R2AMRvoltage range
298 | RE22R2AMR | Complementary | supply frequency | 50...60 Hz +/- 5 % | RE22R2AMRsupply frequency
299 | RE22R2AMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | RE22R2AMRconnections - terminals
300 | RE22R2AMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | RE22R2AMRtightening torque
301 | RE22R2AMR | Complementary | housing material | Self-extinguishing | RE22R2AMRhousing material
302 | RE22R2AMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1 | RE22R2AMRrepeat accuracy
303 | RE22R2AMR | Complementary | temperature drift | +/- 0.05 %/°C | RE22R2AMRtemperature drift
304 | RE22R2AMR | Complementary | voltage drift | +/- 0.2 %/V | RE22R2AMRvoltage drift
305 | RE22R2AMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | RE22R2AMRsetting accuracy of time delay
306 | RE22R2AMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms | RE22R2AMRControl signal pulse width
307 | RE22R2AMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1 | RE22R2AMRinsulation resistance
308 | RE22R2AMR | Complementary | Recovery time | 120 ms on de-energisation | RE22R2AMRRecovery time
309 | RE22R2AMR | Complementary | immunity to microbreaks | 10 ms | RE22R2AMRimmunity to microbreaks
310 | RE22R2AMR | Complementary | power consumption in VA | 3 VA at 240 V AC | RE22R2AMRpower consumption in VA
311 | RE22R2AMR | Complementary | power consumption in W | 1.5 W at 240 V DC | RE22R2AMRpower consumption in W
312 | RE22R2AMR | Complementary | switching capacity in VA | 2000 VA | RE22R2AMRswitching capacity in VA
313 | RE22R2AMR | Complementary | minimum switching current | 10 mA at 5 V DC | RE22R2AMRminimum switching current
314 | RE22R2AMR | Complementary | maximum switching current | 8 A | RE22R2AMRmaximum switching current
315 | RE22R2AMR | Complementary | maximum switching voltage | 250 V AC | RE22R2AMRmaximum switching voltage
316 | RE22R2AMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | RE22R2AMRelectrical durability
317 | RE22R2AMR | Complementary | mechanical durability | 10000000 cycles | RE22R2AMRmechanical durability
318 | RE22R2AMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | RE22R2AMRRated impulse withstand voltage
319 | RE22R2AMR | Complementary | Power on delay | 100 ms | RE22R2AMRPower on delay
320 | RE22R2AMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1 | RE22R2AMRcreepage distance
321 | RE22R2AMR | Complementary | overvoltage category | III conforming to IEC 60664-1 | RE22R2AMRovervoltage category
322 | RE22R2AMR | Complementary | safety reliability data | B10d = 200000 MTTFd = 216.8 years | RE22R2AMRsafety reliability data
323 | RE22R2AMR | Complementary | mounting position | Any position | RE22R2AMRmounting position
324 | RE22R2AMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715 | RE22R2AMRmounting support
325 | RE22R2AMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | RE22R2AMRstatus LED
326 | RE22R2AMR | Complementary | width | 22.5 mm | RE22R2AMRwidth
327 | RE22R2AMR | Complementary | net weight | 0.105 kg | RE22R2AMRnet weight
328 | RE22R2AMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | RE22R2AMRdielectric strength
329 | RE22R2AMR | Environment | standards | UL 508 IEC 61812-1 | RE22R2AMRstandards
330 | RE22R2AMR | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | RE22R2AMRdirectives
331 | RE22R2AMR | Environment | product certifications | CE CCC GL China RoHS UL RCM EAC CSA | RE22R2AMRproduct certifications
332 | RE22R2AMR | Environment | ambient air temperature for operation | -20…60 °C | RE22R2AMRambient air temperature for operation
333 | RE22R2AMR | Environment | ambient air temperature for storage | -40…70 °C | RE22R2AMRambient air temperature for storage
334 | RE22R2AMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | RE22R2AMRIP degree of protection
335 | RE22R2AMR | Environment | pollution degree | 3 conforming to IEC 60664-1 | RE22R2AMRpollution degree
336 | RE22R2AMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | RE22R2AMRvibration resistance
337 | RE22R2AMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | RE22R2AMRshock resistance
338 | RE22R2AMR | Environment | relative humidity | 95 % at 25…55 °C | RE22R2AMRrelative humidity
339 | RE22R2AMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | RE22R2AMRelectromagnetic compatibility
340 | RE22R2AMR | Packing Units | Package 1 Weight | 0.114 kg | RE22R2AMRPackage 1 Weight
341 | RE22R2AMR | Offer Sustainability | Sustainable offer status | Green Premium product | RE22R2AMRSustainable offer status
342 | RE22R2AMR | Offer Sustainability | REACh Regulation | REACh Declaration | RE22R2AMRREACh Regulation
343 | RE22R2AMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RE22R2AMREU RoHS Directive
344 | RE22R2AMR | Offer Sustainability | Mercury free | Yes | RE22R2AMRMercury free
345 | RE22R2AMR | Offer Sustainability | RoHS exemption information | Yes | RE22R2AMRRoHS exemption information
346 | RE22R2AMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RE22R2AMRChina RoHS Regulation
347 | RE22R2AMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RE22R2AMREnvironmental Disclosure
348 | RE22R2AMR | Offer Sustainability | Circularity Profile | End of Life Information | RE22R2AMRCircularity Profile
349 | RE22R2CMR | Main | range of product | Zelio Time | RE22R2CMRrange of product
350 | RE22R2CMR | Main | product or component type | Modular timing relay | RE22R2CMRproduct or component type
351 | RE22R2CMR | Main | discrete output type | Relay | RE22R2CMRdiscrete output type
352 | RE22R2CMR | Main | device short name | RE22 | RE22R2CMRdevice short name
353 | RE22R2CMR | Main | nominal output current | 8 A | RE22R2CMRnominal output current
354 | RE22R2CMR | Complementary | contacts type and composition | 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free | RE22R2CMRcontacts type and composition
355 | RE22R2CMR | Complementary | time delay type | C | RE22R2CMRtime delay type
356 | RE22R2CMR | Complementary | time delay range | 10...100 s 3...30 h 1...10 s 3...30 s 30...300 h 0.3...3 s 0.05...1 s 30...300 min 30...300 s 3...30 min | RE22R2CMRtime delay range
357 | RE22R2CMR | Complementary | control type | Rotary knob Diagnostic button | RE22R2CMRcontrol type
358 | RE22R2CMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz | RE22R2CMR[Us] rated supply voltage
359 | RE22R2CMR | Complementary | Release input voltage | <= 2.4 V | RE22R2CMRRelease input voltage
360 | RE22R2CMR | Complementary | voltage range | 0.85...1.1 Us | RE22R2CMRvoltage range
361 | RE22R2CMR | Complementary | supply frequency | 50...60 Hz +/- 5 % | RE22R2CMRsupply frequency
362 | RE22R2CMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | RE22R2CMRconnections - terminals
363 | RE22R2CMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | RE22R2CMRtightening torque
364 | RE22R2CMR | Complementary | housing material | Self-extinguishing | RE22R2CMRhousing material
365 | RE22R2CMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1 | RE22R2CMRrepeat accuracy
366 | RE22R2CMR | Complementary | temperature drift | +/- 0.05 %/°C | RE22R2CMRtemperature drift
367 | RE22R2CMR | Complementary | voltage drift | +/- 0.2 %/V | RE22R2CMRvoltage drift
368 | RE22R2CMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | RE22R2CMRsetting accuracy of time delay
369 | RE22R2CMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms | RE22R2CMRControl signal pulse width
370 | RE22R2CMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1 | RE22R2CMRinsulation resistance
371 | RE22R2CMR | Complementary | Recovery time | 120 ms on de-energisation | RE22R2CMRRecovery time
372 | RE22R2CMR | Complementary | immunity to microbreaks | 10 ms | RE22R2CMRimmunity to microbreaks
373 | RE22R2CMR | Complementary | power consumption in VA | 3 VA at 240 V AC | RE22R2CMRpower consumption in VA
374 | RE22R2CMR | Complementary | power consumption in W | 1.5 W at 240 V DC | RE22R2CMRpower consumption in W
375 | RE22R2CMR | Complementary | switching capacity in VA | 2000 VA | RE22R2CMRswitching capacity in VA
376 | RE22R2CMR | Complementary | minimum switching current | 10 mA at 5 V DC | RE22R2CMRminimum switching current
377 | RE22R2CMR | Complementary | maximum switching current | 8 A | RE22R2CMRmaximum switching current
378 | RE22R2CMR | Complementary | maximum switching voltage | 250 V AC | RE22R2CMRmaximum switching voltage
379 | RE22R2CMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | RE22R2CMRelectrical durability
380 | RE22R2CMR | Complementary | mechanical durability | 10000000 cycles | RE22R2CMRmechanical durability
381 | RE22R2CMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | RE22R2CMRRated impulse withstand voltage
382 | RE22R2CMR | Complementary | Power on delay | 100 ms | RE22R2CMRPower on delay
383 | RE22R2CMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1 | RE22R2CMRcreepage distance
384 | RE22R2CMR | Complementary | overvoltage category | III conforming to IEC 60664-1 | RE22R2CMRovervoltage category
385 | RE22R2CMR | Complementary | safety reliability data | MTTFd = 251.1 years B10d = 230000 | RE22R2CMRsafety reliability data
386 | RE22R2CMR | Complementary | mounting position | Any position | RE22R2CMRmounting position
387 | RE22R2CMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715 | RE22R2CMRmounting support
388 | RE22R2CMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | RE22R2CMRstatus LED
389 | RE22R2CMR | Complementary | width | 22.5 mm | RE22R2CMRwidth
390 | RE22R2CMR | Complementary | net weight | 0.105 kg | RE22R2CMRnet weight
391 | RE22R2CMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | RE22R2CMRdielectric strength
392 | RE22R2CMR | Environment | standards | UL 508 IEC 61812-1 | RE22R2CMRstandards
393 | RE22R2CMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | RE22R2CMRdirectives
394 | RE22R2CMR | Environment | product certifications | CSA CCC RCM China RoHS CE GL UL EAC | RE22R2CMRproduct certifications
395 | RE22R2CMR | Environment | ambient air temperature for operation | -20…60 °C | RE22R2CMRambient air temperature for operation
396 | RE22R2CMR | Environment | ambient air temperature for storage | -40…70 °C | RE22R2CMRambient air temperature for storage
397 | RE22R2CMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | RE22R2CMRIP degree of protection
398 | RE22R2CMR | Environment | pollution degree | 3 conforming to IEC 60664-1 | RE22R2CMRpollution degree
399 | RE22R2CMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | RE22R2CMRvibration resistance
400 | RE22R2CMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | RE22R2CMRshock resistance
401 | RE22R2CMR | Environment | relative humidity | 95 % at 25…55 °C | RE22R2CMRrelative humidity
402 | RE22R2CMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | RE22R2CMRelectromagnetic compatibility
403 | RE22R2CMR | Packing Units | Package 1 Weight | 0.108 kg | RE22R2CMRPackage 1 Weight
404 | RE22R2CMR | Offer Sustainability | Sustainable offer status | Green Premium product | RE22R2CMRSustainable offer status
405 | RE22R2CMR | Offer Sustainability | REACh Regulation | REACh Declaration | RE22R2CMRREACh Regulation
406 | RE22R2CMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RE22R2CMREU RoHS Directive
407 | RE22R2CMR | Offer Sustainability | Mercury free | Yes | RE22R2CMRMercury free
408 | RE22R2CMR | Offer Sustainability | RoHS exemption information | Yes | RE22R2CMRRoHS exemption information
409 | RE22R2CMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RE22R2CMRChina RoHS Regulation
410 | RE22R2CMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RE22R2CMREnvironmental Disclosure
411 | RE22R2CMR | Offer Sustainability | Circularity Profile | End of Life Information | RE22R2CMRCircularity Profile
412 | RMTJ60BD | Main | range of product | Zelio Analog | RMTJ60BDrange of product
413 | RMTJ60BD | Main | product or component type | Converter for thermocouples | RMTJ60BDproduct or component type
414 | RMTJ60BD | Main | analogue input type | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584 | RMTJ60BDanalogue input type
415 | RMTJ60BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | RMTJ60BDanalogue output type
416 | RMTJ60BD | Complementary | protection type | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output | RMTJ60BDprotection type
417 | RMTJ60BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | RMTJ60BDabnormal analogue output voltage
418 | RMTJ60BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken | RMTJ60BDabnormal analogue output current
419 | RMTJ60BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, non isolated | RMTJ60BD[Us] rated supply voltage
420 | RMTJ60BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output | RMTJ60BDcurrent consumption
421 | RMTJ60BD | Complementary | local signalling | LED (green) for power ON | RMTJ60BDlocal signalling
422 | RMTJ60BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C | RMTJ60BDmeasurement error
423 | RMTJ60BD | Complementary | repeat accuracy | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C | RMTJ60BDrepeat accuracy
424 | RMTJ60BD | Complementary | temperature coefficient | 200 ppm/°C | RMTJ60BDtemperature coefficient
425 | RMTJ60BD | Complementary | cold junction compensation | Built-in, measurement: between 0 and 60 °C | RMTJ60BDcold junction compensation
426 | RMTJ60BD | Complementary | clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm² | RMTJ60BDclamping connection capacity
427 | RMTJ60BD | Complementary | tightening torque | 0.6…1.1 N.m | RMTJ60BDtightening torque
428 | RMTJ60BD | Complementary | marking | CE | RMTJ60BDmarking
429 | RMTJ60BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | RMTJ60BDsurge withstand
430 | RMTJ60BD | Complementary | [Ui] rated insulation voltage | 2 kV | RMTJ60BD[Ui] rated insulation voltage
431 | RMTJ60BD | Complementary | fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail) | RMTJ60BDfixing mode
432 | RMTJ60BD | Complementary | safety reliability data | B10d = 45447 MTTFd = 49.2 years | RMTJ60BDsafety reliability data
433 | RMTJ60BD | Complementary | net weight | 0.12 kg | RMTJ60BDnet weight
434 | RMTJ60BD | Environment | standards | IEC 60584-1 IEC 60947-1 | RMTJ60BDstandards
435 | RMTJ60BD | Environment | product certifications | CSA GL UL | RMTJ60BDproduct certifications
436 | RMTJ60BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing) | RMTJ60BDIP degree of protection
437 | RMTJ60BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | RMTJ60BDfire resistance
438 | RMTJ60BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27 | RMTJ60BDshock resistance
439 | RMTJ60BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | RMTJ60BDvibration resistance
440 | RMTJ60BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3 | RMTJ60BDresistance to electrostatic discharge
441 | RMTJ60BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | RMTJ60BDresistance to fast transients
442 | RMTJ60BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B CISPR 11 | RMTJ60BDdisturbance radiated/conducted
443 | RMTJ60BD | Environment | ambient air temperature for storage | -40…85 °C | RMTJ60BDambient air temperature for storage
444 | RMTJ60BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | RMTJ60BDambient air temperature for operation
445 | RMTJ60BD | Environment | pollution degree | 2 conforming to IEC 60664-1 | RMTJ60BDpollution degree
446 | RMTJ60BD | Packing Units | Package 1 Weight | 0.101 kg | RMTJ60BDPackage 1 Weight
447 | RMTJ60BD | Offer Sustainability | Sustainable offer status | Green Premium product | RMTJ60BDSustainable offer status
448 | RMTJ60BD | Offer Sustainability | REACh Regulation | REACh Declaration | RMTJ60BDREACh Regulation
449 | RMTJ60BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RMTJ60BDEU RoHS Directive
450 | RMTJ60BD | Offer Sustainability | Mercury free | Yes | RMTJ60BDMercury free
451 | RMTJ60BD | Offer Sustainability | RoHS exemption information | Yes | RMTJ60BDRoHS exemption information
452 | RMTJ60BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RMTJ60BDChina RoHS Regulation
453 | RMTJ60BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RMTJ60BDEnvironmental Disclosure
454 | RMTJ60BD | Offer Sustainability | Circularity Profile | End of Life Information | RMTJ60BDCircularity Profile
455 | RMTJ60BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RMTJ60BDWEEE
456 | RMTJ60BD | Contractual warranty | Warranty | 18 months | RMTJ60BDWarranty
457 | XVDLS37 | Main | range of product | Harmony XVD Optimum | XVDLS37range of product
458 | XVDLS37 | Main | product or component type | Complete miniature beacon | XVDLS37product or component type
459 | XVDLS37 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit | XVDLS37beacon or indicator bank unit type
460 | XVDLS37 | Main | signalling type | Steady | XVDLS37signalling type
461 | XVDLS37 | Main | mounting diameter | 45 mm | XVDLS37mounting diameter
462 | XVDLS37 | Main | component name | XVDLS | XVDLS37component name
463 | XVDLS37 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | XVDLS37material
464 | XVDLS37 | Main | light source | Bulb not included, clear | XVDLS37light source
465 | XVDLS37 | Main | bulb type | Incandescent with BA 15d base | XVDLS37bulb type
466 | XVDLS37 | Main | [Us] rated supply voltage | <= 230 V | XVDLS37[Us] rated supply voltage
467 | XVDLS37 | Main | maximum power dissipation in W | 5 W | XVDLS37maximum power dissipation in W
468 | XVDLS37 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | XVDLS37connections - terminals
469 | XVDLS37 | Complementary | cable entry | 1 entry tapped for Pg 7 | XVDLS37cable entry
470 | XVDLS37 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1 | XVDLS37[Ui] rated insulation voltage
471 | XVDLS37 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1 | XVDLS37[Uimp] rated impulse withstand voltage
472 | XVDLS37 | Complementary | CAD overall width | 45 mm | XVDLS37CAD overall width
473 | XVDLS37 | Complementary | CAD overall height | 104 mm | XVDLS37CAD overall height
474 | XVDLS37 | Complementary | CAD overall depth | 45 mm | XVDLS37CAD overall depth
475 | XVDLS37 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW | XVDLS37terminals description ISO n°1
476 | XVDLS37 | Complementary | net weight | 0.08 kg | XVDLS37net weight
477 | XVDLS37 | Environment | product certifications | CSA UL | XVDLS37product certifications
478 | XVDLS37 | Environment | standards | EN/IEC 60947-5-1 | XVDLS37standards
479 | XVDLS37 | Environment | protective treatment | TC | XVDLS37protective treatment
480 | XVDLS37 | Environment | ambient air temperature for operation | -25…70 °C | XVDLS37ambient air temperature for operation
481 | XVDLS37 | Environment | ambient air temperature for storage | -40…70 °C | XVDLS37ambient air temperature for storage
482 | XVDLS37 | Environment | electrical shock protection class | Class II conforming to IEC 60536 | XVDLS37electrical shock protection class
483 | XVDLS37 | Environment | IP degree of protection | IP40 conforming to IEC 60529 | XVDLS37IP degree of protection
484 | XVDLS37 | Packing Units | Package 1 Weight | 0.101 kg | XVDLS37Package 1 Weight
485 | XVDLS37 | Offer Sustainability | Sustainable offer status | Green Premium product | XVDLS37Sustainable offer status
486 | XVDLS37 | Offer Sustainability | REACh Regulation | REACh Declaration | XVDLS37REACh Regulation
487 | XVDLS37 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | XVDLS37EU RoHS Directive
488 | XVDLS37 | Offer Sustainability | Mercury free | Yes | XVDLS37Mercury free
489 | XVDLS37 | Offer Sustainability | RoHS exemption information | Yes | XVDLS37RoHS exemption information
490 | XVDLS37 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | XVDLS37China RoHS Regulation
491 | XVDLS37 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | XVDLS37Environmental Disclosure
492 | XVDLS37 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | XVDLS37WEEE
493 | XVDLS37 | Contractual warranty | Warranty | 18 months | XVDLS37Warranty
494 | XVDLS38 | Main | range of product | Harmony XVD Optimum | XVDLS38range of product
495 | XVDLS38 | Main | product or component type | Complete miniature beacon | XVDLS38product or component type
496 | XVDLS38 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit | XVDLS38beacon or indicator bank unit type
497 | XVDLS38 | Main | signalling type | Steady | XVDLS38signalling type
498 | XVDLS38 | Main | mounting diameter | 45 mm | XVDLS38mounting diameter
499 | XVDLS38 | Main | component name | XVDLS | XVDLS38component name
500 | XVDLS38 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | XVDLS38material
501 | XVDLS38 | Main | light source | Bulb not included, yellow | XVDLS38light source
502 | XVDLS38 | Main | bulb type | Incandescent with BA 15d base | XVDLS38bulb type
503 | XVDLS38 | Main | [Us] rated supply voltage | <= 230 V | XVDLS38[Us] rated supply voltage
504 | XVDLS38 | Main | maximum power dissipation in W | 5 W | XVDLS38maximum power dissipation in W
505 | XVDLS38 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | XVDLS38connections - terminals
506 | XVDLS38 | Complementary | cable entry | 1 entry tapped for Pg 7 | XVDLS38cable entry
507 | XVDLS38 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1 | XVDLS38[Ui] rated insulation voltage
508 | XVDLS38 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1 | XVDLS38[Uimp] rated impulse withstand voltage
509 | XVDLS38 | Complementary | CAD overall width | 45 mm | XVDLS38CAD overall width
510 | XVDLS38 | Complementary | CAD overall height | 104 mm | XVDLS38CAD overall height
511 | XVDLS38 | Complementary | CAD overall depth | 45 mm | XVDLS38CAD overall depth
512 | XVDLS38 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND | XVDLS38terminals description ISO n°1
513 | XVDLS38 | Complementary | net weight | 0.08 kg | XVDLS38net weight
514 | XVDLS38 | Environment | product certifications | CSA UL | XVDLS38product certifications
515 | XVDLS38 | Environment | standards | EN/IEC 60947-5-1 | XVDLS38standards
516 | XVDLS38 | Environment | protective treatment | TC | XVDLS38protective treatment
517 | XVDLS38 | Environment | ambient air temperature for operation | -25…70 °C | XVDLS38ambient air temperature for operation
518 | XVDLS38 | Environment | ambient air temperature for storage | -40…70 °C | XVDLS38ambient air temperature for storage
519 | XVDLS38 | Environment | electrical shock protection class | Class II conforming to IEC 60536 | XVDLS38electrical shock protection class
520 | XVDLS38 | Environment | IP degree of protection | IP40 conforming to IEC 60529 | XVDLS38IP degree of protection
521 | XVDLS38 | Packing Units | Package 1 Weight | 0.100 kg | XVDLS38Package 1 Weight
522 | XVDLS38 | Offer Sustainability | Sustainable offer status | Green Premium product | XVDLS38Sustainable offer status
523 | XVDLS38 | Offer Sustainability | REACh Regulation | REACh Declaration | XVDLS38REACh Regulation
524 | XVDLS38 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | XVDLS38EU RoHS Directive
525 | XVDLS38 | Offer Sustainability | Mercury free | Yes | XVDLS38Mercury free
526 | XVDLS38 | Offer Sustainability | RoHS exemption information | Yes | XVDLS38RoHS exemption information
527 | XVDLS38 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | XVDLS38China RoHS Regulation
528 | XVDLS38 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | XVDLS38Environmental Disclosure
529 | XVDLS38 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | XVDLS38WEEE
530 | XVDLS38 | Contractual warranty | Warranty | 18 months | XVDLS38Warranty
531 | RHT428B | Main | range of product | Zelio Relay | RHT428Brange of product
532 | RHT428B | Main | product or component type | Plug-in relay Timing relay | RHT428Bproduct or component type
533 | RHT428B | Main | device short name | RHT | RHT428Bdevice short name
534 | RHT428B | Main | contacts type and composition | 4 C/O | RHT428Bcontacts type and composition
535 | RHT428B | Main | contact operation | Low level | RHT428Bcontact operation
536 | RHT428B | Main | [Uc] control circuit voltage | 24 V AC/DC 50/60 Hz | RHT428B[Uc] control circuit voltage
537 | RHT428B | Main | time delay type | On-delay | RHT428Btime delay type
538 | RHT428B | Main | time delay range | 15...300 s 0.2...3 s 1.5...30 s | RHT428Btime delay range
539 | RHT428B | Main | [Ithe] conventional enclosed thermal current | 1 A 40 °C | RHT428B[Ithe] conventional enclosed thermal current
540 | RHT428B | Main | status LED | With | RHT428Bstatus LED
541 | RHT428B | Main | control type | Selector switch | RHT428Bcontrol type
542 | RHT428B | Main | coil interference suppression | With | RHT428Bcoil interference suppression
543 | RHT428B | Complementary | [Ui] rated insulation voltage | 250 V | RHT428B[Ui] rated insulation voltage
544 | RHT428B | Complementary | operating position | Any position | RHT428Boperating position
545 | RHT428B | Complementary | minimum switching capacity | 50 mVA at 1 mA, 1 V | RHT428Bminimum switching capacity
546 | RHT428B | Complementary | contact bounce time | <= 10 ms | RHT428Bcontact bounce time
547 | RHT428B | Complementary | maximum voltage drop | <100 V for 3 A at 24 V | RHT428Bmaximum voltage drop
548 | RHT428B | Complementary | average resistance | 30 mOhm at 20 °C | RHT428Baverage resistance
549 | RHT428B | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | RHT428Bswitching time
550 | RHT428B | Complementary | average coil consumption | 2.5 W at 20 °C | RHT428Baverage coil consumption
551 | RHT428B | Complementary | average coil consumption in VA | 2.9 at 20 °C | RHT428Baverage coil consumption in VA
552 | RHT428B | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255 | RHT428Bcontrol circuit voltage limits
553 | RHT428B | Complementary | mechanical durability | 20000000 cycles | RHT428Bmechanical durability
554 | RHT428B | Complementary | repeat accuracy | +/- 1 % | RHT428Brepeat accuracy
555 | RHT428B | Complementary | setting accuracy of time delay | +/- 15 % of full scale | RHT428Bsetting accuracy of time delay
556 | RHT428B | Complementary | reset time | 100 ms | RHT428Breset time
557 | RHT428B | Complementary | CAD overall width | 33 mm | RHT428BCAD overall width
558 | RHT428B | Complementary | CAD overall height | 43 mm | RHT428BCAD overall height
559 | RHT428B | Complementary | CAD overall depth | 108 mm | RHT428BCAD overall depth
560 | RHT428B | Complementary | terminals description ISO n°1 | (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC | RHT428Bterminals description ISO n°1
561 | RHT428B | Complementary | net weight | 0.13 kg | RHT428Bnet weight
562 | RHT428B | Environment | standards | IEC 60255 NF C 45-250 VDE 0435 | RHT428Bstandards
563 | RHT428B | Environment | product certifications | USSR EDF ASE BV CSA | RHT428Bproduct certifications
564 | RHT428B | Environment | protective treatment | TC | RHT428Bprotective treatment
565 | RHT428B | Environment | dielectric strength | 2500 V | RHT428Bdielectric strength
566 | RHT428B | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255 | RHT428Bambient air temperature for operation
567 | RHT428B | Environment | ambient air temperature for storage | -40…70 °C | RHT428Bambient air temperature for storage
568 | RHT428B | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | RHT428Bvibration resistance
569 | RHT428B | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608 | RHT428Bshock resistance
570 | RHT428B | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay | RHT428Bimmunity to microbreaks
571 | RHT428B | Packing Units | Package 1 Weight | 0.135 kg | RHT428BPackage 1 Weight
572 | RHT428B | Contractual warranty | Warranty | 18 months | RHT428BWarranty
573 | RHT418BE | Main | range of product | Zelio Relay | RHT418BErange of product
574 | RHT418BE | Main | product or component type | Timing relay Plug-in relay | RHT418BEproduct or component type
575 | RHT418BE | Main | device short name | RHT | RHT418BEdevice short name
576 | RHT418BE | Main | contacts type and composition | 4 C/O | RHT418BEcontacts type and composition
577 | RHT418BE | Main | contact operation | Standard | RHT418BEcontact operation
578 | RHT418BE | Main | [Uc] control circuit voltage | 27 V AC/DC 50/60 Hz | RHT418BE[Uc] control circuit voltage
579 | RHT418BE | Main | time delay type | On-delay | RHT418BEtime delay type
580 | RHT418BE | Main | time delay range | 0.2...3 s 15...300 s 1.5...30 s | RHT418BEtime delay range
581 | RHT418BE | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C | RHT418BE[Ithe] conventional enclosed thermal current
582 | RHT418BE | Main | status LED | With | RHT418BEstatus LED
583 | RHT418BE | Main | control type | Selector switch | RHT418BEcontrol type
584 | RHT418BE | Main | coil interference suppression | With | RHT418BEcoil interference suppression
585 | RHT418BE | Complementary | [Ui] rated insulation voltage | 250 V | RHT418BE[Ui] rated insulation voltage
586 | RHT418BE | Complementary | operating position | Any position | RHT418BEoperating position
587 | RHT418BE | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V | RHT418BEminimum switching capacity
588 | RHT418BE | Complementary | contact bounce time | <= 10 ms | RHT418BEcontact bounce time
589 | RHT418BE | Complementary | maximum voltage drop | <100 V for 3 A at 24 V | RHT418BEmaximum voltage drop
590 | RHT418BE | Complementary | average resistance | 30 mOhm at 20 °C | RHT418BEaverage resistance
591 | RHT418BE | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | RHT418BEswitching time
592 | RHT418BE | Complementary | average coil consumption | 2.5 W at 20 °C | RHT418BEaverage coil consumption
593 | RHT418BE | Complementary | average coil consumption in VA | 2.9 at 20 °C | RHT418BEaverage coil consumption in VA
594 | RHT418BE | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255 | RHT418BEcontrol circuit voltage limits
595 | RHT418BE | Complementary | mechanical durability | 20000000 cycles | RHT418BEmechanical durability
596 | RHT418BE | Complementary | repeat accuracy | +/- 1 % | RHT418BErepeat accuracy
597 | RHT418BE | Complementary | setting accuracy of time delay | +/- 15 % of full scale | RHT418BEsetting accuracy of time delay
598 | RHT418BE | Complementary | reset time | 100 ms | RHT418BEreset time
599 | RHT418BE | Complementary | CAD overall width | 33 mm | RHT418BECAD overall width
600 | RHT418BE | Complementary | CAD overall height | 43 mm | RHT418BECAD overall height
601 | RHT418BE | Complementary | CAD overall depth | 108 mm | RHT418BECAD overall depth
602 | RHT418BE | Complementary | terminals description ISO n°1 | (31-32-34)OC (41-42-44)OC (11-12-14)OC (21-22-24)OC (A1-A2)CO | RHT418BEterminals description ISO n°1
603 | RHT418BE | Complementary | net weight | 0.13 kg | RHT418BEnet weight
604 | RHT418BE | Environment | standards | IEC 60255 NF C 45-250 VDE 0435 | RHT418BEstandards
605 | RHT418BE | Environment | product certifications | ASE EDF USSR BV CSA | RHT418BEproduct certifications
606 | RHT418BE | Environment | protective treatment | TC | RHT418BEprotective treatment
607 | RHT418BE | Environment | dielectric strength | 2500 V | RHT418BEdielectric strength
608 | RHT418BE | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255 | RHT418BEambient air temperature for operation
609 | RHT418BE | Environment | ambient air temperature for storage | -40…70 °C | RHT418BEambient air temperature for storage
610 | RHT418BE | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | RHT418BEvibration resistance
611 | RHT418BE | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608 | RHT418BEshock resistance
612 | RHT418BE | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay | RHT418BEimmunity to microbreaks
613 | RHT418BE | Packing Units | Package 1 Weight | 0.136 kg | RHT418BEPackage 1 Weight
614 | RHT418BE | Contractual warranty | Warranty | 18 months | RHT418BEWarranty
615 | RSB1A160M7S | Main | range of product | Zelio Relay | RSB1A160M7Srange of product
616 | RSB1A160M7S | Main | series name | Interface relay | RSB1A160M7Sseries name
617 | RSB1A160M7S | Main | product or component type | Plug-in relay | RSB1A160M7Sproduct or component type
618 | RSB1A160M7S | Main | device short name | RSB | RSB1A160M7Sdevice short name
619 | RSB1A160M7S | Main | contacts type and composition | 1 C/O | RSB1A160M7Scontacts type and composition
620 | RSB1A160M7S | Main | contact operation | Standard | RSB1A160M7Scontact operation
621 | RSB1A160M7S | Main | [Uc] control circuit voltage | 220 V AC | RSB1A160M7S[Uc] control circuit voltage
622 | RSB1A160M7S | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C | RSB1A160M7S[Ithe] conventional enclosed thermal current
623 | RSB1A160M7S | Main | status LED | Without | RSB1A160M7Sstatus LED
624 | RSB1A160M7S | Complementary | shape of pin | Flat | RSB1A160M7Sshape of pin
625 | RSB1A160M7S | Complementary | average coil resistance | 35500 Ohm network: AC at 20 °C +/- 15 % | RSB1A160M7Saverage coil resistance
626 | RSB1A160M7S | Complementary | [Ue] rated operational voltage | 176...264 V AC 50 Hz 187...264 V AC 60 Hz | RSB1A160M7S[Ue] rated operational voltage
627 | RSB1A160M7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | RSB1A160M7S[Ui] rated insulation voltage
628 | RSB1A160M7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV | RSB1A160M7S[Uimp] rated impulse withstand voltage
629 | RSB1A160M7S | Complementary | contacts material | Silver alloy (Ag/Ni) | RSB1A160M7Scontacts material
630 | RSB1A160M7S | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | RSB1A160M7S[Ie] rated operational current
631 | RSB1A160M7S | Complementary | minimum switching current | 5 mA | RSB1A160M7Sminimum switching current
632 | RSB1A160M7S | Complementary | maximum switching voltage | 300 V DC 400 V AC | RSB1A160M7Smaximum switching voltage
633 | RSB1A160M7S | Complementary | minimum switching voltage | 5 V | RSB1A160M7Sminimum switching voltage
634 | RSB1A160M7S | Complementary | maximum switching capacity | 4000 VA AC 448 W DC | RSB1A160M7Smaximum switching capacity
635 | RSB1A160M7S | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC | RSB1A160M7Sresistive rated load
636 | RSB1A160M7S | Complementary | minimum switching capacity | 300 mW at 5 mA | RSB1A160M7Sminimum switching capacity
637 | RSB1A160M7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | RSB1A160M7Soperating rate
638 | RSB1A160M7S | Complementary | mechanical durability | 30000000 cycles | RSB1A160M7Smechanical durability
639 | RSB1A160M7S | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | RSB1A160M7Selectrical durability
640 | RSB1A160M7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | RSB1A160M7Soperating time
641 | RSB1A160M7S | Complementary | marking | CE | RSB1A160M7Smarking
642 | RSB1A160M7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz | RSB1A160M7Saverage coil consumption
643 | RSB1A160M7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC | RSB1A160M7Sdrop-out voltage threshold
644 | RSB1A160M7S | Complementary | safety reliability data | B10d = 100000 | RSB1A160M7Ssafety reliability data
645 | RSB1A160M7S | Complementary | protection category | RT I | RSB1A160M7Sprotection category
646 | RSB1A160M7S | Complementary | operating position | Any position | RSB1A160M7Soperating position
647 | RSB1A160M7S | Complementary | sale per indivisible quantity | 10 | RSB1A160M7Ssale per indivisible quantity
648 | RSB1A160M7S | Complementary | device presentation | Complete product | RSB1A160M7Sdevice presentation
649 | RSB1A160M7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | RSB1A160M7Sdielectric strength
650 | RSB1A160M7S | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | RSB1A160M7Sstandards
651 | RSB1A160M7S | Environment | product certifications | CSA UL GOST | RSB1A160M7Sproduct certifications
652 | RSB1A160M7S | Environment | ambient air temperature for storage | -40…85 °C | RSB1A160M7Sambient air temperature for storage
653 | RSB1A160M7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | RSB1A160M7Svibration resistance
654 | RSB1A160M7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | RSB1A160M7SIP degree of protection
655 | RSB1A160M7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | RSB1A160M7Sshock resistance
656 | RSB1A160M7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | RSB1A160M7Sambient air temperature for operation
657 | RSB1A160M7S | Packing Units | Package 1 Weight | 0.001 kg | RSB1A160M7SPackage 1 Weight
658 | RSB1A160M7S | Offer Sustainability | Sustainable offer status | Green Premium product | RSB1A160M7SSustainable offer status
659 | RSB1A160M7S | Offer Sustainability | REACh free of SVHC | Yes | RSB1A160M7SREACh free of SVHC
660 | RSB1A160M7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RSB1A160M7SEU RoHS Directive
661 | RSB1A160M7S | Offer Sustainability | Toxic heavy metal free | Yes | RSB1A160M7SToxic heavy metal free
662 | RSB1A160M7S | Offer Sustainability | Mercury free | Yes | RSB1A160M7SMercury free
663 | RSB1A160M7S | Offer Sustainability | RoHS exemption information | Yes | RSB1A160M7SRoHS exemption information
664 | RSB1A160M7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RSB1A160M7SChina RoHS Regulation
665 | RSB1A160M7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RSB1A160M7SEnvironmental Disclosure
666 | RSB1A160M7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RSB1A160M7SWEEE
667 | RSB1A160M7S | Contractual warranty | Warranty | 18 months | RSB1A160M7SWarranty
668 | RSB1A160NDS | Main | range of product | Zelio Relay | RSB1A160NDSrange of product
669 | RSB1A160NDS | Main | series name | Interface relay | RSB1A160NDSseries name
670 | RSB1A160NDS | Main | product or component type | Plug-in relay | RSB1A160NDSproduct or component type
671 | RSB1A160NDS | Main | device short name | RSB | RSB1A160NDSdevice short name
672 | RSB1A160NDS | Main | contacts type and composition | 1 C/O | RSB1A160NDScontacts type and composition
673 | RSB1A160NDS | Main | contact operation | Standard | RSB1A160NDScontact operation
674 | RSB1A160NDS | Main | [Uc] control circuit voltage | 60 V DC | RSB1A160NDS[Uc] control circuit voltage
675 | RSB1A160NDS | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C | RSB1A160NDS[Ithe] conventional enclosed thermal current
676 | RSB1A160NDS | Main | status LED | Without | RSB1A160NDSstatus LED
677 | RSB1A160NDS | Complementary | shape of pin | Flat | RSB1A160NDSshape of pin
678 | RSB1A160NDS | Complementary | average coil resistance | 7500 Ohm network: DC at 20 °C +/- 10 % | RSB1A160NDSaverage coil resistance
679 | RSB1A160NDS | Complementary | [Ue] rated operational voltage | 48...66 V DC | RSB1A160NDS[Ue] rated operational voltage
680 | RSB1A160NDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | RSB1A160NDS[Ui] rated insulation voltage
681 | RSB1A160NDS | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5 | RSB1A160NDS[Uimp] rated impulse withstand voltage
682 | RSB1A160NDS | Complementary | contacts material | Silver alloy (Ag/Ni) | RSB1A160NDScontacts material
683 | RSB1A160NDS | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | RSB1A160NDS[Ie] rated operational current
684 | RSB1A160NDS | Complementary | minimum switching current | 5 mA | RSB1A160NDSminimum switching current
685 | RSB1A160NDS | Complementary | maximum switching voltage | 300 V DC 400 V AC | RSB1A160NDSmaximum switching voltage
686 | RSB1A160NDS | Complementary | minimum switching voltage | 5 V | RSB1A160NDSminimum switching voltage
687 | RSB1A160NDS | Complementary | maximum switching capacity | 4000 VA AC 448 W DC | RSB1A160NDSmaximum switching capacity
688 | RSB1A160NDS | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC | RSB1A160NDSresistive rated load
689 | RSB1A160NDS | Complementary | minimum switching capacity | 300 mW at 5 mA | RSB1A160NDSminimum switching capacity
690 | RSB1A160NDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | RSB1A160NDSoperating rate
691 | RSB1A160NDS | Complementary | mechanical durability | 30000000 cycles | RSB1A160NDSmechanical durability
692 | RSB1A160NDS | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | RSB1A160NDSelectrical durability
693 | RSB1A160NDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | RSB1A160NDSoperating time
694 | RSB1A160NDS | Complementary | marking | CE | RSB1A160NDSmarking
695 | RSB1A160NDS | Complementary | average coil consumption | 0.45 W DC | RSB1A160NDSaverage coil consumption
696 | RSB1A160NDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC | RSB1A160NDSdrop-out voltage threshold
697 | RSB1A160NDS | Complementary | safety reliability data | B10d = 100000 | RSB1A160NDSsafety reliability data
698 | RSB1A160NDS | Complementary | protection category | RT I | RSB1A160NDSprotection category
699 | RSB1A160NDS | Complementary | operating position | Any position | RSB1A160NDSoperating position
700 | RSB1A160NDS | Complementary | sale per indivisible quantity | 10 | RSB1A160NDSsale per indivisible quantity
701 | RSB1A160NDS | Complementary | device presentation | Complete product | RSB1A160NDSdevice presentation
702 | RSB1A160NDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | RSB1A160NDSdielectric strength
703 | RSB1A160NDS | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | RSB1A160NDSstandards
704 | RSB1A160NDS | Environment | product certifications | CSA UL GOST | RSB1A160NDSproduct certifications
705 | RSB1A160NDS | Environment | ambient air temperature for storage | -40…85 °C | RSB1A160NDSambient air temperature for storage
706 | RSB1A160NDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | RSB1A160NDSvibration resistance
707 | RSB1A160NDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | RSB1A160NDSIP degree of protection
708 | RSB1A160NDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | RSB1A160NDSshock resistance
709 | RSB1A160NDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | RSB1A160NDSambient air temperature for operation
710 | RSB1A160NDS | Packing Units | Package 1 Weight | 0.001 kg | RSB1A160NDSPackage 1 Weight
711 | RSB1A160NDS | Contractual warranty | Warranty | 18 months | RSB1A160NDSWarranty
712 | RSB2A080P7S | Main | range of product | Zelio Relay | RSB2A080P7Srange of product
713 | RSB2A080P7S | Main | series name | Interface relay | RSB2A080P7Sseries name
714 | RSB2A080P7S | Main | product or component type | Plug-in relay | RSB2A080P7Sproduct or component type
715 | RSB2A080P7S | Main | device short name | RSB | RSB2A080P7Sdevice short name
716 | RSB2A080P7S | Main | contacts type and composition | 2 C/O | RSB2A080P7Scontacts type and composition
717 | RSB2A080P7S | Main | contact operation | Standard | RSB2A080P7Scontact operation
718 | RSB2A080P7S | Main | [Uc] control circuit voltage | 230 V AC | RSB2A080P7S[Uc] control circuit voltage
719 | RSB2A080P7S | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C | RSB2A080P7S[Ithe] conventional enclosed thermal current
720 | RSB2A080P7S | Main | status LED | Without | RSB2A080P7Sstatus LED
721 | RSB2A080P7S | Main | control type | Without push-button | RSB2A080P7Scontrol type
722 | RSB2A080P7S | Complementary | shape of pin | Flat | RSB2A080P7Sshape of pin
723 | RSB2A080P7S | Complementary | average coil resistance | 38500 Ohm network: AC at 20 °C +/- 15 % | RSB2A080P7Saverage coil resistance
724 | RSB2A080P7S | Complementary | [Ue] rated operational voltage | 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz | RSB2A080P7S[Ue] rated operational voltage
725 | RSB2A080P7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | RSB2A080P7S[Ui] rated insulation voltage
726 | RSB2A080P7S | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5 | RSB2A080P7S[Uimp] rated impulse withstand voltage
727 | RSB2A080P7S | Complementary | contacts material | Silver alloy (Ag/Ni) | RSB2A080P7Scontacts material
728 | RSB2A080P7S | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | RSB2A080P7S[Ie] rated operational current
729 | RSB2A080P7S | Complementary | minimum switching current | 5 mA | RSB2A080P7Sminimum switching current
730 | RSB2A080P7S | Complementary | maximum switching voltage | 300 V DC 400 V AC | RSB2A080P7Smaximum switching voltage
731 | RSB2A080P7S | Complementary | minimum switching voltage | 5 V | RSB2A080P7Sminimum switching voltage
732 | RSB2A080P7S | Complementary | maximum switching capacity | 2000 VA AC 224 W DC | RSB2A080P7Smaximum switching capacity
733 | RSB2A080P7S | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC | RSB2A080P7Sresistive rated load
734 | RSB2A080P7S | Complementary | minimum switching capacity | 300 mW at 5 mA | RSB2A080P7Sminimum switching capacity
735 | RSB2A080P7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | RSB2A080P7Soperating rate
736 | RSB2A080P7S | Complementary | mechanical durability | 30000000 cycles | RSB2A080P7Smechanical durability
737 | RSB2A080P7S | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | RSB2A080P7Selectrical durability
738 | RSB2A080P7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | RSB2A080P7Soperating time
739 | RSB2A080P7S | Complementary | marking | CE | RSB2A080P7Smarking
740 | RSB2A080P7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz | RSB2A080P7Saverage coil consumption
741 | RSB2A080P7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC | RSB2A080P7Sdrop-out voltage threshold
742 | RSB2A080P7S | Complementary | safety reliability data | B10d = 100000 | RSB2A080P7Ssafety reliability data
743 | RSB2A080P7S | Complementary | protection category | RT I | RSB2A080P7Sprotection category
744 | RSB2A080P7S | Complementary | operating position | Any position | RSB2A080P7Soperating position
745 | RSB2A080P7S | Complementary | sale per indivisible quantity | 10 | RSB2A080P7Ssale per indivisible quantity
746 | RSB2A080P7S | Complementary | device presentation | Complete product | RSB2A080P7Sdevice presentation
747 | RSB2A080P7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | RSB2A080P7Sdielectric strength
748 | RSB2A080P7S | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | RSB2A080P7Sstandards
749 | RSB2A080P7S | Environment | product certifications | GOST CSA UL | RSB2A080P7Sproduct certifications
750 | RSB2A080P7S | Environment | ambient air temperature for storage | -40…85 °C | RSB2A080P7Sambient air temperature for storage
751 | RSB2A080P7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | RSB2A080P7Svibration resistance
752 | RSB2A080P7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | RSB2A080P7SIP degree of protection
753 | RSB2A080P7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | RSB2A080P7Sshock resistance
754 | RSB2A080P7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | RSB2A080P7Sambient air temperature for operation
755 | RSB2A080P7S | Packing Units | Package 1 Weight | 61 g | RSB2A080P7SPackage 1 Weight
756 | RSB2A080P7S | Packing Units | Package 2 Weight | 1.23 kg | RSB2A080P7SPackage 2 Weight
757 | RSB2A080P7S | Packing Units | Package 3 Weight | 7.876 kg | RSB2A080P7SPackage 3 Weight
758 | RSB2A080P7S | Offer Sustainability | Sustainable offer status | Green Premium product | RSB2A080P7SSustainable offer status
759 | RSB2A080P7S | Offer Sustainability | REACh free of SVHC | Yes | RSB2A080P7SREACh free of SVHC
760 | RSB2A080P7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RSB2A080P7SEU RoHS Directive
761 | RSB2A080P7S | Offer Sustainability | Toxic heavy metal free | Yes | RSB2A080P7SToxic heavy metal free
762 | RSB2A080P7S | Offer Sustainability | Mercury free | Yes | RSB2A080P7SMercury free
763 | RSB2A080P7S | Offer Sustainability | RoHS exemption information | Yes | RSB2A080P7SRoHS exemption information
764 | RSB2A080P7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RSB2A080P7SChina RoHS Regulation
765 | RSB2A080P7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RSB2A080P7SEnvironmental Disclosure
766 | RSB2A080P7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RSB2A080P7SWEEE
767 | RSB2A080P7S | Contractual warranty | Warranty | 18 months | RSB2A080P7SWarranty
768 | RSB2A080RDS | Main | range of product | Zelio Relay | RSB2A080RDSrange of product
769 | RSB2A080RDS | Main | series name | Interface relay | RSB2A080RDSseries name
770 | RSB2A080RDS | Main | product or component type | Plug-in relay | RSB2A080RDSproduct or component type
771 | RSB2A080RDS | Main | device short name | RSB | RSB2A080RDSdevice short name
772 | RSB2A080RDS | Main | contacts type and composition | 2 C/O | RSB2A080RDScontacts type and composition
773 | RSB2A080RDS | Main | contact operation | Standard | RSB2A080RDScontact operation
774 | RSB2A080RDS | Main | [Uc] control circuit voltage | 6 V DC | RSB2A080RDS[Uc] control circuit voltage
775 | RSB2A080RDS | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C | RSB2A080RDS[Ithe] conventional enclosed thermal current
776 | RSB2A080RDS | Main | status LED | Without | RSB2A080RDSstatus LED
777 | RSB2A080RDS | Complementary | shape of pin | Flat | RSB2A080RDSshape of pin
778 | RSB2A080RDS | Complementary | average coil resistance | 90 Ohm network: DC at 20 °C +/- 10 % | RSB2A080RDSaverage coil resistance
779 | RSB2A080RDS | Complementary | [Ue] rated operational voltage | 4.8...6.6 V DC | RSB2A080RDS[Ue] rated operational voltage
780 | RSB2A080RDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | RSB2A080RDS[Ui] rated insulation voltage
781 | RSB2A080RDS | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV | RSB2A080RDS[Uimp] rated impulse withstand voltage
782 | RSB2A080RDS | Complementary | contacts material | Silver alloy (Ag/Ni) | RSB2A080RDScontacts material
783 | RSB2A080RDS | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | RSB2A080RDS[Ie] rated operational current
784 | RSB2A080RDS | Complementary | minimum switching current | 5 mA | RSB2A080RDSminimum switching current
785 | RSB2A080RDS | Complementary | maximum switching voltage | 300 V DC 400 V AC | RSB2A080RDSmaximum switching voltage
786 | RSB2A080RDS | Complementary | minimum switching voltage | 5 V | RSB2A080RDSminimum switching voltage
787 | RSB2A080RDS | Complementary | maximum switching capacity | 2000 VA AC 224 W DC | RSB2A080RDSmaximum switching capacity
788 | RSB2A080RDS | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC | RSB2A080RDSresistive rated load
789 | RSB2A080RDS | Complementary | minimum switching capacity | 300 mW at 5 mA | RSB2A080RDSminimum switching capacity
790 | RSB2A080RDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | RSB2A080RDSoperating rate
791 | RSB2A080RDS | Complementary | mechanical durability | 30000000 cycles | RSB2A080RDSmechanical durability
792 | RSB2A080RDS | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | RSB2A080RDSelectrical durability
793 | RSB2A080RDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | RSB2A080RDSoperating time
794 | RSB2A080RDS | Complementary | marking | CE | RSB2A080RDSmarking
795 | RSB2A080RDS | Complementary | average coil consumption | 0.45 W DC | RSB2A080RDSaverage coil consumption
796 | RSB2A080RDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC | RSB2A080RDSdrop-out voltage threshold
797 | RSB2A080RDS | Complementary | safety reliability data | B10d = 100000 | RSB2A080RDSsafety reliability data
798 | RSB2A080RDS | Complementary | protection category | RT I | RSB2A080RDSprotection category
799 | RSB2A080RDS | Complementary | operating position | Any position | RSB2A080RDSoperating position
800 | RSB2A080RDS | Complementary | sale per indivisible quantity | 10 | RSB2A080RDSsale per indivisible quantity
801 | RSB2A080RDS | Complementary | device presentation | Complete product | RSB2A080RDSdevice presentation
802 | RSB2A080RDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | RSB2A080RDSdielectric strength
803 | RSB2A080RDS | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | RSB2A080RDSstandards
804 | RSB2A080RDS | Environment | product certifications | CSA GOST UL | RSB2A080RDSproduct certifications
805 | RSB2A080RDS | Environment | ambient air temperature for storage | -40…85 °C | RSB2A080RDSambient air temperature for storage
806 | RSB2A080RDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | RSB2A080RDSvibration resistance
807 | RSB2A080RDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | RSB2A080RDSIP degree of protection
808 | RSB2A080RDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | RSB2A080RDSshock resistance
809 | RSB2A080RDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | RSB2A080RDSambient air temperature for operation
810 | RSB2A080RDS | Packing Units | Package 1 Weight | 0.001 kg | RSB2A080RDSPackage 1 Weight
811 | RSB2A080RDS | Contractual warranty | Warranty | 18 months | RSB2A080RDSWarranty
812 | RSB2A080U7S | Main | range of product | Zelio Relay | RSB2A080U7Srange of product
813 | RSB2A080U7S | Main | series name | Interface relay | RSB2A080U7Sseries name
814 | RSB2A080U7S | Main | product or component type | Plug-in relay | RSB2A080U7Sproduct or component type
815 | RSB2A080U7S | Main | device short name | RSB | RSB2A080U7Sdevice short name
816 | RSB2A080U7S | Main | contacts type and composition | 2 C/O | RSB2A080U7Scontacts type and composition
817 | RSB2A080U7S | Main | contact operation | Standard | RSB2A080U7Scontact operation
818 | RSB2A080U7S | Main | [Uc] control circuit voltage | 240 V AC | RSB2A080U7S[Uc] control circuit voltage
819 | RSB2A080U7S | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C | RSB2A080U7S[Ithe] conventional enclosed thermal current
820 | RSB2A080U7S | Main | status LED | Without | RSB2A080U7Sstatus LED
821 | RSB2A080U7S | Complementary | shape of pin | Flat | RSB2A080U7Sshape of pin
822 | RSB2A080U7S | Complementary | average coil resistance | 42500 Ohm network: AC at 20 °C +/- 15 % | RSB2A080U7Saverage coil resistance
823 | RSB2A080U7S | Complementary | [Ue] rated operational voltage | 192...288 V AC 50 Hz 204...288 V AC 60 Hz | RSB2A080U7S[Ue] rated operational voltage
824 | RSB2A080U7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | RSB2A080U7S[Ui] rated insulation voltage
825 | RSB2A080U7S | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5 | RSB2A080U7S[Uimp] rated impulse withstand voltage
826 | RSB2A080U7S | Complementary | contacts material | Silver alloy (Ag/Ni) | RSB2A080U7Scontacts material
827 | RSB2A080U7S | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | RSB2A080U7S[Ie] rated operational current
828 | RSB2A080U7S | Complementary | minimum switching current | 5 mA | RSB2A080U7Sminimum switching current
829 | RSB2A080U7S | Complementary | maximum switching voltage | 300 V DC 400 V AC | RSB2A080U7Smaximum switching voltage
830 | RSB2A080U7S | Complementary | minimum switching voltage | 5 V | RSB2A080U7Sminimum switching voltage
831 | RSB2A080U7S | Complementary | maximum switching capacity | 2000 VA AC 224 W DC | RSB2A080U7Smaximum switching capacity
832 | RSB2A080U7S | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC | RSB2A080U7Sresistive rated load
833 | RSB2A080U7S | Complementary | minimum switching capacity | 300 mW at 5 mA | RSB2A080U7Sminimum switching capacity
834 | RSB2A080U7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | RSB2A080U7Soperating rate
835 | RSB2A080U7S | Complementary | mechanical durability | 30000000 cycles | RSB2A080U7Smechanical durability
836 | RSB2A080U7S | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | RSB2A080U7Selectrical durability
837 | RSB2A080U7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | RSB2A080U7Soperating time
838 | RSB2A080U7S | Complementary | marking | CE | RSB2A080U7Smarking
839 | RSB2A080U7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz | RSB2A080U7Saverage coil consumption
840 | RSB2A080U7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC | RSB2A080U7Sdrop-out voltage threshold
841 | RSB2A080U7S | Complementary | safety reliability data | B10d = 100000 | RSB2A080U7Ssafety reliability data
842 | RSB2A080U7S | Complementary | protection category | RT I | RSB2A080U7Sprotection category
843 | RSB2A080U7S | Complementary | operating position | Any position | RSB2A080U7Soperating position
844 | RSB2A080U7S | Complementary | sale per indivisible quantity | 10 | RSB2A080U7Ssale per indivisible quantity
845 | RSB2A080U7S | Complementary | device presentation | Complete product | RSB2A080U7Sdevice presentation
846 | RSB2A080U7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | RSB2A080U7Sdielectric strength
847 | RSB2A080U7S | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | RSB2A080U7Sstandards
848 | RSB2A080U7S | Environment | product certifications | UL CSA GOST | RSB2A080U7Sproduct certifications
849 | RSB2A080U7S | Environment | ambient air temperature for storage | -40…85 °C | RSB2A080U7Sambient air temperature for storage
850 | RSB2A080U7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | RSB2A080U7Svibration resistance
851 | RSB2A080U7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | RSB2A080U7SIP degree of protection
852 | RSB2A080U7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | RSB2A080U7Sshock resistance
853 | RSB2A080U7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | RSB2A080U7Sambient air temperature for operation
854 | RSB2A080U7S | Packing Units | Package 1 Weight | 0.001 kg | RSB2A080U7SPackage 1 Weight
855 | RSB2A080U7S | Offer Sustainability | Sustainable offer status | Green Premium product | RSB2A080U7SSustainable offer status
856 | RSB2A080U7S | Offer Sustainability | REACh free of SVHC | Yes | RSB2A080U7SREACh free of SVHC
857 | RSB2A080U7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RSB2A080U7SEU RoHS Directive
858 | RSB2A080U7S | Offer Sustainability | Toxic heavy metal free | Yes | RSB2A080U7SToxic heavy metal free
859 | RSB2A080U7S | Offer Sustainability | Mercury free | Yes | RSB2A080U7SMercury free
860 | RSB2A080U7S | Offer Sustainability | RoHS exemption information | Yes | RSB2A080U7SRoHS exemption information
861 | RSB2A080U7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RSB2A080U7SChina RoHS Regulation
862 | RSB2A080U7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RSB2A080U7SEnvironmental Disclosure
863 | RSB2A080U7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RSB2A080U7SWEEE
864 | RSB2A080U7S | Contractual warranty | Warranty | 18 months | RSB2A080U7SWarranty
865 | RSB2A080M7S | Main | range of product | Zelio Relay | RSB2A080M7Srange of product
866 | RSB2A080M7S | Main | series name | Interface relay | RSB2A080M7Sseries name
867 | RSB2A080M7S | Main | product or component type | Plug-in relay | RSB2A080M7Sproduct or component type
868 | RSB2A080M7S | Main | device short name | RSB | RSB2A080M7Sdevice short name
869 | RSB2A080M7S | Main | contacts type and composition | 2 C/O | RSB2A080M7Scontacts type and composition
870 | RSB2A080M7S | Main | contact operation | Standard | RSB2A080M7Scontact operation
871 | RSB2A080M7S | Main | [Uc] control circuit voltage | 220 V AC | RSB2A080M7S[Uc] control circuit voltage
872 | RSB2A080M7S | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C | RSB2A080M7S[Ithe] conventional enclosed thermal current
873 | RSB2A080M7S | Main | status LED | Without | RSB2A080M7Sstatus LED
874 | RSB2A080M7S | Complementary | shape of pin | Flat | RSB2A080M7Sshape of pin
875 | RSB2A080M7S | Complementary | average coil resistance | 35500 Ohm network: AC at 20 °C +/- 15 % | RSB2A080M7Saverage coil resistance
876 | RSB2A080M7S | Complementary | [Ue] rated operational voltage | 176...264 V AC 50 Hz 187...264 V AC 60 Hz | RSB2A080M7S[Ue] rated operational voltage
877 | RSB2A080M7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | RSB2A080M7S[Ui] rated insulation voltage
878 | RSB2A080M7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV | RSB2A080M7S[Uimp] rated impulse withstand voltage
879 | RSB2A080M7S | Complementary | contacts material | Silver alloy (Ag/Ni) | RSB2A080M7Scontacts material
880 | RSB2A080M7S | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | RSB2A080M7S[Ie] rated operational current
881 | RSB2A080M7S | Complementary | minimum switching current | 5 mA | RSB2A080M7Sminimum switching current
882 | RSB2A080M7S | Complementary | maximum switching voltage | 300 V DC 400 V AC | RSB2A080M7Smaximum switching voltage
883 | RSB2A080M7S | Complementary | minimum switching voltage | 5 V | RSB2A080M7Sminimum switching voltage
884 | RSB2A080M7S | Complementary | maximum switching capacity | 2000 VA AC 224 W DC | RSB2A080M7Smaximum switching capacity
885 | RSB2A080M7S | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC | RSB2A080M7Sresistive rated load
886 | RSB2A080M7S | Complementary | minimum switching capacity | 300 mW at 5 mA | RSB2A080M7Sminimum switching capacity
887 | RSB2A080M7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | RSB2A080M7Soperating rate
888 | RSB2A080M7S | Complementary | mechanical durability | 30000000 cycles | RSB2A080M7Smechanical durability
889 | RSB2A080M7S | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | RSB2A080M7Selectrical durability
890 | RSB2A080M7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | RSB2A080M7Soperating time
891 | RSB2A080M7S | Complementary | marking | CE | RSB2A080M7Smarking
892 | RSB2A080M7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz | RSB2A080M7Saverage coil consumption
893 | RSB2A080M7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC | RSB2A080M7Sdrop-out voltage threshold
894 | RSB2A080M7S | Complementary | safety reliability data | B10d = 100000 | RSB2A080M7Ssafety reliability data
895 | RSB2A080M7S | Complementary | protection category | RT I | RSB2A080M7Sprotection category
896 | RSB2A080M7S | Complementary | operating position | Any position | RSB2A080M7Soperating position
897 | RSB2A080M7S | Complementary | sale per indivisible quantity | 10 | RSB2A080M7Ssale per indivisible quantity
898 | RSB2A080M7S | Complementary | device presentation | Complete product | RSB2A080M7Sdevice presentation
899 | RSB2A080M7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | RSB2A080M7Sdielectric strength
900 | RSB2A080M7S | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | RSB2A080M7Sstandards
901 | RSB2A080M7S | Environment | product certifications | GOST UL CSA | RSB2A080M7Sproduct certifications
902 | RSB2A080M7S | Environment | ambient air temperature for storage | -40…85 °C | RSB2A080M7Sambient air temperature for storage
903 | RSB2A080M7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | RSB2A080M7Svibration resistance
904 | RSB2A080M7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | RSB2A080M7SIP degree of protection
905 | RSB2A080M7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | RSB2A080M7Sshock resistance
906 | RSB2A080M7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | RSB2A080M7Sambient air temperature for operation
907 | RSB2A080M7S | Packing Units | Package 1 Weight | 0.001 kg | RSB2A080M7SPackage 1 Weight
908 | RSB2A080M7S | Offer Sustainability | Sustainable offer status | Green Premium product | RSB2A080M7SSustainable offer status
909 | RSB2A080M7S | Offer Sustainability | REACh free of SVHC | Yes | RSB2A080M7SREACh free of SVHC
910 | RSB2A080M7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RSB2A080M7SEU RoHS Directive
911 | RSB2A080M7S | Offer Sustainability | Toxic heavy metal free | Yes | RSB2A080M7SToxic heavy metal free
912 | RSB2A080M7S | Offer Sustainability | Mercury free | Yes | RSB2A080M7SMercury free
913 | RSB2A080M7S | Offer Sustainability | RoHS exemption information | Yes | RSB2A080M7SRoHS exemption information
914 | RSB2A080M7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RSB2A080M7SChina RoHS Regulation
915 | RSB2A080M7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RSB2A080M7SEnvironmental Disclosure
916 | RSB2A080M7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RSB2A080M7SWEEE
917 | RSB2A080M7S | Contractual warranty | Warranty | 18 months | RSB2A080M7SWarranty
918 | RXG11RD | Main | range of product | Harmony Relay | RXG11RDrange of product
919 | RXG11RD | Main | series name | Interface relay | RXG11RDseries name
920 | RXG11RD | Main | product or component type | Plug-in relay | RXG11RDproduct or component type
921 | RXG11RD | Main | device short name | RXG | RXG11RDdevice short name
922 | RXG11RD | Main | contacts type and composition | 1 C/O | RXG11RDcontacts type and composition
923 | RXG11RD | Complementary | status LED | Without | RXG11RDstatus LED
924 | RXG11RD | Complementary | contacts material | Silver alloy (AgSnO2In2O3) | RXG11RDcontacts material
925 | RXG11RD | Complementary | Maximum contact resistance | 100 mOhm | RXG11RDMaximum contact resistance
926 | RXG11RD | Complementary | [Ithe] conventional enclosed thermal current | 10 A at -40…55 °C | RXG11RD[Ithe] conventional enclosed thermal current
927 | RXG11RD | Complementary | [Ie] rated operational current | 10 A at 30 V (DC) conforming to UL 10 A at 30 V (DC) conforming to IEC 10 A at 250 V (AC) conforming to IEC 10 A at 250 V (AC) conforming to UL | RXG11RD[Ie] rated operational current
928 | RXG11RD | Complementary | maximum switching voltage | 250 V AC 30 V DC | RXG11RDmaximum switching voltage
929 | RXG11RD | Complementary | load current | 10 A at 250 V AC | RXG11RDload current
930 | RXG11RD | Complementary | maximum switching capacity | 2500 VA | RXG11RDmaximum switching capacity
931 | RXG11RD | Complementary | minimum switching capacity | 500 mW at 100 mA, 5 V DC | RXG11RDminimum switching capacity
932 | RXG11RD | Complementary | operating rate | <= 1800 cycles/hour under load <= 18000 cycles/hour no-load | RXG11RDoperating rate
933 | RXG11RD | Complementary | utilisation coefficient | 20 % | RXG11RDutilisation coefficient
934 | RXG11RD | Complementary | mechanical durability | 10000000 cycles | RXG11RDmechanical durability
935 | RXG11RD | Complementary | electrical durability | 100000 cycles for NO resistive load at 55 °C 100000 cycles for NC resistive load at 55 °C | RXG11RDelectrical durability
936 | RXG11RD | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL | RXG11RD[Ui] rated insulation voltage
937 | RXG11RD | Complementary | [Uimp] rated impulse withstand voltage | 6 kV 1.2/50 µs | RXG11RD[Uimp] rated impulse withstand voltage
938 | RXG11RD | Complementary | dielectric strength | 1000 V AC between contacts with micro disconnection 5000 V AC between coil and contact with reinforced insulation | RXG11RDdielectric strength
939 | RXG11RD | Complementary | Coil resistance | 68 Ohm +/- 10 % | RXG11RDCoil resistance
940 | RXG11RD | Complementary | insulation resistance | 1000 MOhm at 500 V DC | RXG11RDinsulation resistance
941 | RXG11RD | Complementary | test levels | Level A group mounting | RXG11RDtest levels
942 | RXG11RD | Complementary | mounting position | Any position | RXG11RDmounting position
943 | RXG11RD | Complementary | drop-out voltage threshold | >= 0.1 Uc DC | RXG11RDdrop-out voltage threshold
944 | RXG11RD | Complementary | Coil insulation class | Class F | RXG11RDCoil insulation class
945 | RXG11RD | Complementary | Operate time | 20 ms | RXG11RDOperate time
946 | RXG11RD | Complementary | Release time | 20 ms | RXG11RDRelease time
947 | RXG11RD | Complementary | [Uc] control circuit voltage | 6 V DC | RXG11RD[Uc] control circuit voltage
948 | RXG11RD | Complementary | safety reliability data | B10d = 100000 | RXG11RDsafety reliability data
949 | RXG11RD | Complementary | colour of cover | Standard | RXG11RDcolour of cover
950 | RXG11RD | Complementary | control type | Lockable test button | RXG11RDcontrol type
951 | RXG11RD | Complementary | local signalling | Flag | RXG11RDlocal signalling
952 | RXG11RD | Complementary | torque value | 0.8 N.m | RXG11RDtorque value
953 | RXG11RD | Complementary | net weight | 0.02 kg | RXG11RDnet weight
954 | RXG11RD | Complementary | device presentation | Complete product | RXG11RDdevice presentation
955 | RXG11RD | Environment | vibration resistance | 3 gn, amplitude = +/- 0.75 mm (f = 10…150 Hz)in operation 5 gn, amplitude = +/- 0.75 mm (f = 10…150 Hz)not in operation | RXG11RDvibration resistance
956 | RXG11RD | Environment | IP degree of protection | IP40 | RXG11RDIP degree of protection
957 | RXG11RD | Environment | shock resistance | 20 gn in operation 100 gn not in operation | RXG11RDshock resistance
958 | RXG11RD | Environment | protection category | RT I | RXG11RDprotection category
959 | RXG11RD | Environment | standards | UL 508 IEC 61810-1 CSA C22.2 No 14 | RXG11RDstandards
960 | RXG11RD | Environment | product certifications | UL China RoHS CSA EAC REACH CE RoHS | RXG11RDproduct certifications
961 | RXG11RD | Environment | pollution degree | 2 | RXG11RDpollution degree
962 | RXG11RD | Environment | overvoltage category | III | RXG11RDovervoltage category
963 | RXG11RD | Environment | ambient air temperature for storage | -40…85 °C | RXG11RDambient air temperature for storage
964 | RXG11RD | Environment | ambient air temperature for operation | -40…70 °C | RXG11RDambient air temperature for operation
965 | RXG11RD | Environment | relative humidity | 10…85 % | RXG11RDrelative humidity
966 | RXG11RD | Packing Units | Package 1 Weight | 20.200 g | RXG11RDPackage 1 Weight
967 | RXG11RD | Offer Sustainability | Sustainable offer status | Green Premium product | RXG11RDSustainable offer status
968 | RXG11RD | Offer Sustainability | REACh Regulation | REACh Declaration | RXG11RDREACh Regulation
969 | RXG11RD | Offer Sustainability | REACh free of SVHC | Yes | RXG11RDREACh free of SVHC
970 | RXG11RD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RXG11RDEU RoHS Directive
971 | RXG11RD | Offer Sustainability | Toxic heavy metal free | Yes | RXG11RDToxic heavy metal free
972 | RXG11RD | Offer Sustainability | Mercury free | Yes | RXG11RDMercury free
973 | RXG11RD | Offer Sustainability | RoHS exemption information | Yes | RXG11RDRoHS exemption information
974 | RXG11RD | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RXG11RDChina RoHS Regulation
975 | RXG11RD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RXG11RDEnvironmental Disclosure
976 | RXM2AB1B7 | Main | range of product | Zelio Relay | RXM2AB1B7range of product
977 | RXM2AB1B7 | Main | series name | Miniature | RXM2AB1B7series name
978 | RXM2AB1B7 | Main | product or component type | Plug-in relay | RXM2AB1B7product or component type
979 | RXM2AB1B7 | Main | device short name | RXM | RXM2AB1B7device short name
980 | RXM2AB1B7 | Main | contacts type and composition | 2 C/O | RXM2AB1B7contacts type and composition
981 | RXM2AB1B7 | Main | [Uc] control circuit voltage | 24 V AC 50/60 Hz | RXM2AB1B7[Uc] control circuit voltage
982 | RXM2AB1B7 | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…55 °C | RXM2AB1B7[Ithe] conventional enclosed thermal current
983 | RXM2AB1B7 | Main | status LED | Without | RXM2AB1B7status LED
984 | RXM2AB1B7 | Main | control type | Lockable test button | RXM2AB1B7control type
985 | RXM2AB1B7 | Main | utilisation coefficient | 20 % | RXM2AB1B7utilisation coefficient
986 | RXM2AB1B7 | Complementary | shape of pin | Flat | RXM2AB1B7shape of pin
987 | RXM2AB1B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL | RXM2AB1B7[Ui] rated insulation voltage
988 | RXM2AB1B7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV during 1.2/50 µs | RXM2AB1B7[Uimp] rated impulse withstand voltage
989 | RXM2AB1B7 | Complementary | contacts material | AgNi | RXM2AB1B7contacts material
990 | RXM2AB1B7 | Complementary | [Ie] rated operational current | 12 A at 28 V (DC) NO conforming to IEC 12 A at 250 V (AC) NO conforming to IEC 6 A at 28 V (DC) NC conforming to IEC 6 A at 250 V (AC) NC conforming to IEC 12 A at 28 V (DC) conforming to UL 12 A at 277 V (AC) conforming to UL | RXM2AB1B7[Ie] rated operational current
991 | RXM2AB1B7 | Complementary | maximum switching voltage | 250 V conforming to IEC | RXM2AB1B7maximum switching voltage
992 | RXM2AB1B7 | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC | RXM2AB1B7resistive rated load
993 | RXM2AB1B7 | Complementary | maximum switching capacity | 3000 VA/336 W | RXM2AB1B7maximum switching capacity
994 | RXM2AB1B7 | Complementary | minimum switching capacity | 170 mW at 10 mA, 17 V | RXM2AB1B7minimum switching capacity
995 | RXM2AB1B7 | Complementary | operating rate | <= 1200 cycles/hour under load <= 18000 cycles/hour no-load | RXM2AB1B7operating rate
996 | RXM2AB1B7 | Complementary | mechanical durability | 10000000 cycles | RXM2AB1B7mechanical durability
997 | RXM2AB1B7 | Complementary | electrical durability | 100000 cycles for resistive load | RXM2AB1B7electrical durability
998 | RXM2AB1B7 | Complementary | average coil consumption in VA | 1.2 at 60 Hz | RXM2AB1B7average coil consumption in VA
999 | RXM2AB1B7 | Complementary | average consumption | 1.2 VA at 60 Hz | RXM2AB1B7average consumption
1000 | RXM2AB1B7 | Complementary | drop-out voltage threshold | >= 0.15 Uc | RXM2AB1B7drop-out voltage threshold
1001 | RXM2AB1B7 | Complementary | operate time | 20 ms | RXM2AB1B7operate time
1002 | RXM2AB1B7 | Complementary | release time | 20 ms | RXM2AB1B7release time
1003 | RXM2AB1B7 | Complementary | average coil resistance | 180 Ohm at 20 °C +/- 15 % | RXM2AB1B7average coil resistance
1004 | RXM2AB1B7 | Complementary | rated operational voltage limits | 19.2...26.4 V AC | RXM2AB1B7rated operational voltage limits
1005 | RXM2AB1B7 | Complementary | safety reliability data | B10d = 100000 | RXM2AB1B7safety reliability data
1006 | RXM2AB1B7 | Complementary | protection category | RT I | RXM2AB1B7protection category
1007 | RXM2AB1B7 | Complementary | test levels | Level A group mounting | RXM2AB1B7test levels
1008 | RXM2AB1B7 | Complementary | operating position | Any position | RXM2AB1B7operating position
1009 | RXM2AB1B7 | Complementary | net weight | 0.037 kg | RXM2AB1B7net weight
1010 | RXM2AB1B7 | Complementary | device presentation | Complete product | RXM2AB1B7device presentation
1011 | RXM2AB1B7 | Environment | dielectric strength | 1300 V AC between contacts with micro disconnection 2000 V AC between coil and contact 2000 V AC between poles | RXM2AB1B7dielectric strength
1012 | RXM2AB1B7 | Environment | product certifications | UL Lloyd's RoHS CE CSA GOST REACH | RXM2AB1B7product certifications
1013 | RXM2AB1B7 | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | RXM2AB1B7standards
1014 | RXM2AB1B7 | Environment | ambient air temperature for storage | -40…85 °C | RXM2AB1B7ambient air temperature for storage
1015 | RXM2AB1B7 | Environment | ambient air temperature for operation | -40…55 °C | RXM2AB1B7ambient air temperature for operation
1016 | RXM2AB1B7 | Environment | vibration resistance | 3 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles in operation 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles not operating | RXM2AB1B7vibration resistance
1017 | RXM2AB1B7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | RXM2AB1B7IP degree of protection
1018 | RXM2AB1B7 | Environment | shock resistance | 10 gn for in operation 30 gn for not operating | RXM2AB1B7shock resistance
1019 | RXM2AB1B7 | Environment | pollution degree | 3 | RXM2AB1B7pollution degree
1020 | RXM2AB1B7 | Packing Units | Package 1 Weight | 0.035 kg | RXM2AB1B7Package 1 Weight
1021 | RXM2AB1B7 | Offer Sustainability | Sustainable offer status | Green Premium product | RXM2AB1B7Sustainable offer status
1022 | RXM2AB1B7 | Offer Sustainability | REACh Regulation | REACh Declaration | RXM2AB1B7REACh Regulation
1023 | RXM2AB1B7 | Offer Sustainability | REACh free of SVHC | Yes | RXM2AB1B7REACh free of SVHC
1024 | RXM2AB1B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RXM2AB1B7EU RoHS Directive
1025 | RXM2AB1B7 | Offer Sustainability | Toxic heavy metal free | Yes | RXM2AB1B7Toxic heavy metal free
1026 | RXM2AB1B7 | Offer Sustainability | Mercury free | Yes | RXM2AB1B7Mercury free
1027 | RXM2AB1B7 | Offer Sustainability | RoHS exemption information | Yes | RXM2AB1B7RoHS exemption information
1028 | RXM2AB1B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RXM2AB1B7China RoHS Regulation
1029 | RXM2AB1B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RXM2AB1B7Environmental Disclosure
1030 | RXM2AB1B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RXM2AB1B7WEEE
1031 | RXM2AB1B7 | Contractual warranty | Warranty | 18 months | RXM2AB1B7Warranty
1032 | RXM4AB1B7 | Main | range of product | Zelio Relay | RXM4AB1B7range of product
1033 | RXM4AB1B7 | Main | series name | Miniature | RXM4AB1B7series name
1034 | RXM4AB1B7 | Main | product or component type | Plug-in relay | RXM4AB1B7product or component type
1035 | RXM4AB1B7 | Main | device short name | RXM | RXM4AB1B7device short name
1036 | RXM4AB1B7 | Main | contacts type and composition | 4 C/O | RXM4AB1B7contacts type and composition
1037 | RXM4AB1B7 | Main | [Uc] control circuit voltage | 24 V AC 50/60 Hz | RXM4AB1B7[Uc] control circuit voltage
1038 | RXM4AB1B7 | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C | RXM4AB1B7[Ithe] conventional enclosed thermal current
1039 | RXM4AB1B7 | Main | status LED | Without | RXM4AB1B7status LED
1040 | RXM4AB1B7 | Main | control type | Lockable test button | RXM4AB1B7control type
1041 | RXM4AB1B7 | Main | utilisation coefficient | 20 % | RXM4AB1B7utilisation coefficient
1042 | RXM4AB1B7 | Complementary | shape of pin | Flat | RXM4AB1B7shape of pin
1043 | RXM4AB1B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL | RXM4AB1B7[Ui] rated insulation voltage
1044 | RXM4AB1B7 | Complementary | [Uimp] rated impulse withstand voltage | 2.5 kV during 1.2/50 µs | RXM4AB1B7[Uimp] rated impulse withstand voltage
1045 | RXM4AB1B7 | Complementary | contacts material | AgNi | RXM4AB1B7contacts material
1046 | RXM4AB1B7 | Complementary | [Ie] rated operational current | 3 A at 28 V (DC) NC conforming to IEC 3 A at 250 V (AC) NC conforming to IEC 6 A at 28 V (DC) NO conforming to IEC 6 A at 250 V (AC) NO conforming to IEC 6 A at 277 V (AC) conforming to UL 8 A at 30 V (DC) conforming to UL | RXM4AB1B7[Ie] rated operational current
1047 | RXM4AB1B7 | Complementary | maximum switching voltage | 250 V conforming to IEC | RXM4AB1B7maximum switching voltage
1048 | RXM4AB1B7 | Complementary | resistive rated load | 6 A at 250 V AC 6 A at 28 V DC | RXM4AB1B7resistive rated load
1049 | RXM4AB1B7 | Complementary | maximum switching capacity | 1500 VA/168 W | RXM4AB1B7maximum switching capacity
1050 | RXM4AB1B7 | Complementary | minimum switching capacity | 170 mW at 10 mA, 17 V | RXM4AB1B7minimum switching capacity
1051 | RXM4AB1B7 | Complementary | operating rate | <= 1200 cycles/hour under load <= 18000 cycles/hour no-load | RXM4AB1B7operating rate
1052 | RXM4AB1B7 | Complementary | mechanical durability | 10000000 cycles | RXM4AB1B7mechanical durability
1053 | RXM4AB1B7 | Complementary | electrical durability | 100000 cycles for resistive load | RXM4AB1B7electrical durability
1054 | RXM4AB1B7 | Complementary | average coil consumption in VA | 1.2 at 60 Hz | RXM4AB1B7average coil consumption in VA
1055 | RXM4AB1B7 | Complementary | average consumption | 1.2 VA at 60 Hz | RXM4AB1B7average consumption
1056 | RXM4AB1B7 | Complementary | drop-out voltage threshold | >= 0.15 Uc | RXM4AB1B7drop-out voltage threshold
1057 | RXM4AB1B7 | Complementary | operate time | 20 ms | RXM4AB1B7operate time
1058 | RXM4AB1B7 | Complementary | release time | 20 ms | RXM4AB1B7release time
1059 | RXM4AB1B7 | Complementary | average coil resistance | 180 Ohm at 20 °C +/- 15 % | RXM4AB1B7average coil resistance
1060 | RXM4AB1B7 | Complementary | rated operational voltage limits | 19.2...26.4 V AC | RXM4AB1B7rated operational voltage limits
1061 | RXM4AB1B7 | Complementary | safety reliability data | B10d = 100000 | RXM4AB1B7safety reliability data
1062 | RXM4AB1B7 | Complementary | protection category | RT I | RXM4AB1B7protection category
1063 | RXM4AB1B7 | Complementary | test levels | Level A group mounting | RXM4AB1B7test levels
1064 | RXM4AB1B7 | Complementary | operating position | Any position | RXM4AB1B7operating position
1065 | RXM4AB1B7 | Complementary | CAD overall height | 79 mm | RXM4AB1B7CAD overall height
1066 | RXM4AB1B7 | Complementary | CAD overall depth | 78.45 mm | RXM4AB1B7CAD overall depth
1067 | RXM4AB1B7 | Complementary | net weight | 0.037 kg | RXM4AB1B7net weight
1068 | RXM4AB1B7 | Complementary | device presentation | Complete product | RXM4AB1B7device presentation
1069 | RXM4AB1B7 | Environment | dielectric strength | 1300 V AC between contacts with micro disconnection 2000 V AC between coil and contact 2000 V AC between poles | RXM4AB1B7dielectric strength
1070 | RXM4AB1B7 | Environment | product certifications | RoHS CSA Lloyd's CE UL REACH GOST | RXM4AB1B7product certifications
1071 | RXM4AB1B7 | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | RXM4AB1B7standards
1072 | RXM4AB1B7 | Environment | ambient air temperature for storage | -40…85 °C | RXM4AB1B7ambient air temperature for storage
1073 | RXM4AB1B7 | Environment | ambient air temperature for operation | -40…55 °C | RXM4AB1B7ambient air temperature for operation
1074 | RXM4AB1B7 | Environment | vibration resistance | 3 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles in operation 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles not operating | RXM4AB1B7vibration resistance
1075 | RXM4AB1B7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | RXM4AB1B7IP degree of protection
1076 | RXM4AB1B7 | Environment | shock resistance | 10 gn for in operation 30 gn for not operating | RXM4AB1B7shock resistance
1077 | RXM4AB1B7 | Environment | pollution degree | 2 | RXM4AB1B7pollution degree
1078 | RXM4AB1B7 | Packing Units | Package 1 Weight | 0.036 kg | RXM4AB1B7Package 1 Weight
1079 | RXM4AB1B7 | Offer Sustainability | Sustainable offer status | Green Premium product | RXM4AB1B7Sustainable offer status
1080 | RXM4AB1B7 | Offer Sustainability | REACh Regulation | REACh Declaration | RXM4AB1B7REACh Regulation
1081 | RXM4AB1B7 | Offer Sustainability | REACh free of SVHC | Yes | RXM4AB1B7REACh free of SVHC
1082 | RXM4AB1B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RXM4AB1B7EU RoHS Directive
1083 | RXM4AB1B7 | Offer Sustainability | Toxic heavy metal free | Yes | RXM4AB1B7Toxic heavy metal free
1084 | RXM4AB1B7 | Offer Sustainability | Mercury free | Yes | RXM4AB1B7Mercury free
1085 | RXM4AB1B7 | Offer Sustainability | RoHS exemption information | Yes | RXM4AB1B7RoHS exemption information
1086 | RXM4AB1B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RXM4AB1B7China RoHS Regulation
1087 | RXM4AB1B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RXM4AB1B7Environmental Disclosure
1088 | RXM4AB1B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RXM4AB1B7WEEE
1089 | RXM4AB1B7 | Contractual warranty | Warranty | 18 months | RXM4AB1B7Warranty

## pivot_datasheet
| Reference | RE22R2AMR | RE22R2CMR | RHT418BE | RHT428B | RM10TE00 | RM17JC00MW | RM17TA00 | RM17TE00 | RMTJ60BD | RSB1A160M7S | RSB1A160NDS | RSB2A080M7S | RSB2A080P7S | RSB2A080RDS | RSB2A080U7S | RXG11RD | RXM2AB1B7 | RXM4AB1B7 | XVDLS37 | XVDLS38
|  | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value
Section | Parameters
Complementary | CAD overall depth |  |  | 108 mm | 108 mm | [13 empty] | 78.45 mm | 45 mm | 45 mm
| CAD overall height |  |  | 43 mm | 43 mm | [13 empty] | 79 mm | 104 mm | 104 mm
| CAD overall width |  |  | 33 mm | 33 mm | [14 empty] | 45 mm | 45 mm
| Coil insulation class | [15 empty] | Class F
| Coil resistance | [15 empty] | 68 Ohm +/- 10 %
| Control signal pulse width | 100 ms with load in parallel 30 ms | 100 ms with load in parallel 30 ms
| Maximum contact resistance | [15 empty] | 100 mOhm
| Operate time | [15 empty] | 20 ms
| Power on delay | 100 ms | 100 ms
| Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1
| Recovery time | 120 ms on de-energisation | 120 ms on de-energisation
| Release input voltage | <= 2.4 V | <= 2.4 V
| Release time | [15 empty] | 20 ms
| [Ie] rated operational current | [9 empty] | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 10 A at 30 V (DC) conforming to UL 10 A at 30 V (DC) conforming to IEC 10 A at 250 V (AC) conforming to IEC 10 A at 250 V (AC) conforming to UL | 12 A at 28 V (DC) NO conforming to IEC 12 A at 250 V (AC) NO conforming to IEC 6 A at 28 V (DC) NC conforming to IEC 6 A at 250 V (AC) NC conforming to IEC 12 A at 28 V (DC) conforming to UL 12 A at 277 V (AC) conforming to UL | 3 A at 28 V (DC) NC conforming to IEC 3 A at 250 V (AC) NC conforming to IEC 6 A at 28 V (DC) NO conforming to IEC 6 A at 250 V (AC) NO conforming to IEC 6 A at 277 V (AC) conforming to UL 8 A at 30 V (DC) conforming to UL
| [Ithe] conventional enclosed thermal current | [15 empty] | 10 A at -40…55 °C
| [Uc] control circuit voltage | [15 empty] | 6 V DC
| [Ue] rated operational voltage | [9 empty] | 176...264 V AC 50 Hz 187...264 V AC 60 Hz | 48...66 V DC | 176...264 V AC 50 Hz 187...264 V AC 60 Hz | 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz | 4.8...6.6 V DC | 192...288 V AC 50 Hz 204...288 V AC 60 Hz
| [Ui] rated insulation voltage |  |  | 250 V | 250 V | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 2 kV | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL | 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL | 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1
| [Uimp] rated impulse withstand voltage | [9 empty] | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | 6 kV 1.2/50 µs | 4 kV during 1.2/50 µs | 2.5 kV during 1.2/50 µs | 4 kV IEC 60947-1 | 4 kV IEC 60947-1
| [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz |  |  |  | 24...240 V AC/DC 50/60 Hz +/- 10 % |  |  | 24 V DC +/- 20 %, non isolated
| abnormal analogue output current | [8 empty] | -30…0 mA when no input or input wire broken
| abnormal analogue output voltage | [8 empty] | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
| adjustment of asymmetry threshold |  |  |  |  | 5...15 % of Un selected |  | 5...15 % of Un selected | 5...15 % of Un selected
| average coil consumption |  |  | 2.5 W at 20 °C | 2.5 W at 20 °C | [5 empty] | 0.75 VA AC 60 Hz | 0.45 W DC | 0.75 VA AC 60 Hz | 0.75 VA AC 60 Hz | 0.45 W DC | 0.75 VA AC 60 Hz
| average coil consumption in VA |  |  | 2.9 at 20 °C | 2.9 at 20 °C | [12 empty] | 1.2 at 60 Hz | 1.2 at 60 Hz
| average coil resistance | [9 empty] | 35500 Ohm network: AC at 20 °C +/- 15 % | 7500 Ohm network: DC at 20 °C +/- 10 % | 35500 Ohm network: AC at 20 °C +/- 15 % | 38500 Ohm network: AC at 20 °C +/- 15 % | 90 Ohm network: DC at 20 °C +/- 10 % | 42500 Ohm network: AC at 20 °C +/- 15 % |  | 180 Ohm at 20 °C +/- 15 % | 180 Ohm at 20 °C +/- 15 %
| average consumption | [16 empty] | 1.2 VA at 60 Hz | 1.2 VA at 60 Hz
| average resistance |  |  | 30 mOhm at 20 °C | 30 mOhm at 20 °C
| cable entry | [18 empty] | 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7
| clamping connection capacity | [8 empty] | 2 x 1.5 mm² 1 x 2.5 mm²
| cold junction compensation | [8 empty] | Built-in, measurement: between 0 and 60 °C
| colour of cover | [15 empty] | Standard
| connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end |  |  | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | [10 empty] | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
| contact bounce time |  |  | <= 10 ms | <= 10 ms
| contacts material | [5 empty] | Cadmium free |  |  |  | Silver alloy (Ag/Ni) | Silver alloy (Ag/Ni) | Silver alloy (Ag/Ni) | Silver alloy (Ag/Ni) | Silver alloy (Ag/Ni) | Silver alloy (Ag/Ni) | Silver alloy (AgSnO2In2O3) | AgNi | AgNi
| contacts type and composition | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free | 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free
| control circuit frequency |  |  |  |  | 50...60 Hz +/- 10 % | 40...70 Hz sinusoidal | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 %
| control circuit voltage limits |  |  | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | - 12 % + 10 % Un |  | - 12 % + 10 % Un | - 12 % + 10 % Un
| control type | Rotary knob Diagnostic button Potentiometer external | Rotary knob Diagnostic button | [13 empty] | Lockable test button
| creepage distance | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1
| current consumption | [8 empty] | <= 40 mA for voltage output <= 60 mA for current output
| delay at power up |  |  |  |  | 650 ms | 0.5 s | 650 ms | 650 ms
| device presentation | [9 empty] | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product
| dielectric strength | [15 empty] | 1000 V AC between contacts with micro disconnection 5000 V AC between coil and contact with reinforced insulation
| drop-out voltage threshold | [9 empty] | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.15 Uc | >= 0.15 Uc
| electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 |  |  | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles |  | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles for NO resistive load at 55 °C 100000 cycles for NC resistive load at 55 °C | 100000 cycles for resistive load | 100000 cycles for resistive load
| fixing mode | [8 empty] | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
| housing material | Self-extinguishing | Self-extinguishing |  |  | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic
| hysteresis |  |  |  |  | 2 % | 15 % fixed of threshold setting | 2 % | 2 %
| immunity to microbreaks | 10 ms | 10 ms
| input current | [5 empty] | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C
| insulation | [5 empty] | Between supply and measurement
| insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 |  |  | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | [7 empty] | 1000 MOhm at 500 V DC
| load current | [15 empty] | 10 A at 250 V AC
| local signalling |  |  |  |  | LED (green)power ON: LED (yellow)relay ON: | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON | [6 empty] | Flag
| marking |  |  |  |  | CE | CE : 73/23/EEC CE : EMC 89/336/EEC | CE | CE | CE | CE | CE | CE | CE | CE | CE
| maximum measuring cycle |  |  |  |  | 150 ms measurement cycle as true rms value | 30 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value
| maximum power consumption in W | [5 empty] | 1 W
| maximum switching capacity | [9 empty] | 4000 VA AC 448 W DC | 4000 VA AC 448 W DC | 2000 VA AC 224 W DC | 2000 VA AC 224 W DC | 2000 VA AC 224 W DC | 2000 VA AC 224 W DC | 2500 VA | 3000 VA/336 W | 1500 VA/168 W
| maximum switching current | 8 A | 8 A |  |  | 5 A AC 5 A DC |  | 5 A AC 5 A DC | 5 A AC 5 A DC
| maximum switching voltage | 250 V AC | 250 V AC |  |  | 250 V AC 250 V DC | 250 V AC/DC | 250 V AC 250 V DC | 250 V AC 250 V DC |  | 300 V DC 400 V AC | 300 V DC 400 V AC | 300 V DC 400 V AC | 300 V DC 400 V AC | 300 V DC 400 V AC | 300 V DC 400 V AC | 250 V AC 30 V DC | 250 V conforming to IEC | 250 V conforming to IEC
| maximum voltage drop |  |  | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V
| measurement accuracy | [5 empty] | +/- 10 % of the full scale value
| measurement error |  |  |  |  | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C
| measurement voltage limits | [6 empty] | 183…528 V AC | 183…528 V AC
| mechanical durability | 10000000 cycles | 10000000 cycles | 20000000 cycles | 20000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles |  | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles
| minimum switching capacity |  |  | 150 mVA at 10 mA, 1 V | 50 mVA at 1 mA, 1 V | [5 empty] | 300 mW at 5 mA | 300 mW at 5 mA | 300 mW at 5 mA | 300 mW at 5 mA | 300 mW at 5 mA | 300 mW at 5 mA | 500 mW at 100 mA, 5 V DC | 170 mW at 10 mA, 17 V | 170 mW at 10 mA, 17 V
| minimum switching current | 10 mA at 5 V DC | 10 mA at 5 V DC |  |  | 10 mA at 5 V DC |  | 10 mA at 5 V DC | 10 mA at 5 V DC |  | 5 mA | 5 mA | 5 mA | 5 mA | 5 mA | 5 mA
| minimum switching voltage | [9 empty] | 5 V | 5 V | 5 V | 5 V | 5 V | 5 V
| mounting position | Any position | Any position | [13 empty] | Any position
| mounting support | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 |  |  | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
| net weight | 0.105 kg | 0.105 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.12 kg | [6 empty] | 0.02 kg | 0.037 kg | 0.037 kg | 0.08 kg | 0.08 kg
| nominal output current |  |  |  |  | 5 A | 5 A | 5 A | 5 A
| operate time | [16 empty] | 20 ms | 20 ms
| operating position |  |  | Any position | Any position | Any position without derating | Any position without derating | Any position without derating | Any position without derating |  | Any position | Any position | Any position | Any position | Any position | Any position |  | Any position | Any position
| operating rate |  |  |  |  | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load |  | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 1800 cycles/hour under load <= 18000 cycles/hour no-load | <= 1200 cycles/hour under load <= 18000 cycles/hour no-load | <= 1200 cycles/hour under load <= 18000 cycles/hour no-load
| operating time | [9 empty] | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
| operating voltage tolerance | [5 empty] | - 15 % + 10 % Un
| output contacts |  |  |  |  | 1 C/O | 1 C/O | 1 C/O | 1 C/O
| overvoltage category | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 |  |  | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1
| phase failure sensitivity |  |  |  |  | 0.7 Un |  | 0.7 Un | 0.7 Un
| polarity | [5 empty] | Yes DC
| power consumption in VA | 3 VA at 240 V AC | 3 VA at 240 V AC |  |  | 0…22 VA at 400 V AC 50 Hz |  | 0…22 VA at 400 V AC 50 Hz | 0…22 VA at 400 V AC 50 Hz
| power consumption in W | 1.5 W at 240 V DC | 1.5 W at 240 V DC
| protection category | [9 empty] | RT I | RT I | RT I | RT I | RT I | RT I |  | RT I | RT I
| protection type | [8 empty] | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output
| rated operational voltage limits | [16 empty] | 19.2...26.4 V AC | 19.2...26.4 V AC
| release time | [16 empty] | 20 ms | 20 ms
| repeat accuracy | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 1 % | +/- 1 % | 0.5 % for input and measurement circuit 3 % for time delay | +/- 0.5 % for input and measurement circuit | 0.5 % for input and measurement circuit 3 % for time delay | 0.5 % for input and measurement circuit 3 % for time delay | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C
| reset time |  |  | 100 ms | 100 ms | 1500 ms time delay |  | 1500 ms time delay | 1500 ms time delay
| resistive rated load | [9 empty] | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC |  | 12 A at 250 V AC 12 A at 28 V DC | 6 A at 250 V AC 6 A at 28 V DC
| response time |  |  |  |  | < 200 ms (in the event of a fault) | < 200 ms (in the event of a fault) | < 200 ms (in the event of a fault) | < 200 ms (in the event of a fault)
| safety reliability data | B10d = 200000 MTTFd = 216.8 years | MTTFd = 251.1 years B10d = 230000 |  |  | B10d = 470000 MTTFd = 502.2 years |  | MTTFd = 502.2 years B10d = 470000 | MTTFd = 502.2 years B10d = 470000 | B10d = 45447 MTTFd = 49.2 years | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000
| sale per indivisible quantity | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10
| setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 15 % of full scale | +/- 15 % of full scale
| shape of pin | [9 empty] | Flat | Flat | Flat | Flat | Flat | Flat |  | Flat | Flat
| status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | [13 empty] | Without
| supply frequency | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % |  |  | 50/60 Hz +/- 10 % |  | 50/60 Hz +/- 10 % | 50/60 Hz +/- 10 %
| supply voltage limits |  |  |  |  | 183…528 V AC | 20.4…264 V AC/DC | 183…528 V AC | 183…528 V AC
| surge withstand | [8 empty] | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
| switching capacity in VA | 2000 VA | 2000 VA
| switching time |  |  | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
| temperature coefficient | [8 empty] | 200 ppm/°C
| temperature drift | +/- 0.05 %/°C | +/- 0.05 %/°C
| terminals description ISO n°1 |  |  | (31-32-34)OC (41-42-44)OC (11-12-14)OC (21-22-24)OC (A1-A2)CO | (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC | [14 empty] | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND
| test levels | [15 empty] | Level A group mounting | Level A group mounting | Level A group mounting
| threshold adjustment voltage |  |  |  |  | -2...-12 % in the range 208 V AC 2...20 % of Un selected +2...+17 % in the range 480 V AC -2...-17 % in the range 220 V AC |  | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC | -2...-17 % in the range 220 V AC +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC 2...20 % of Un selected
| threshold setting | [5 empty] | 10...100 %
| tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 |  |  | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1.1 N.m
| time delay range | 0.05...1 s 0.3...3 s 3...30 h 30...300 min 10...100 s 30...300 s 3...30 s 30...300 h 1...10 s 3...30 min | 10...100 s 3...30 h 1...10 s 3...30 s 30...300 h 0.3...3 s 0.05...1 s 30...300 min 30...300 s 3...30 min
| time delay type | Aw A | C
| torque value | [15 empty] | 0.8 N.m
| utilisation category |  |  |  |  | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 |  | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
| utilisation coefficient | [15 empty] | 20 %
| voltage drift | +/- 0.2 %/V | +/- 0.2 %/V
| voltage range | 0.85...1.1 Us | 0.85...1.1 Us |  |  | 208...480 V phase to phase |  | 208...480 V phase to phase | 208...480 V phase to phase
| width | 22.5 mm | 22.5 mm |  |  | 17.5 mm | 17.5 mm | 17.5 mm | 17.5 mm
Contractual warranty | Warranty |  |  | 18 months | 18 months |  | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months |  | 18 months | 18 months | 18 months | 18 months
Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 |  |  | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminal block) IP50 (housing) | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529
| ambient air temperature for operation | -20…60 °C | -20…60 °C | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C | -40…55 °C | -40…55 °C | -25…70 °C | -25…70 °C
| ambient air temperature for storage | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…70 °C | -40…70 °C
| dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2500 V | 2500 V | [5 empty] | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact |  | 1300 V AC between contacts with micro disconnection 2000 V AC between coil and contact 2000 V AC between poles | 1300 V AC between contacts with micro disconnection 2000 V AC between coil and contact 2000 V AC between poles
| dielectric test voltage |  |  |  |  | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV AC 50 Hz | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
| directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility |  |  | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive |  | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
| disturbance radiated/conducted | [8 empty] | CISPR 22 group 1 - class B CISPR 11
| electrical shock protection class | [18 empty] | Class II conforming to IEC 60536 | Class II conforming to IEC 60536
| electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 |  |  | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2
| fire resistance | [8 empty] | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
| immunity to microbreaks |  |  | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay |  | 10 ms
| non-dissipating shock wave |  |  |  |  | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
| overvoltage category | [15 empty] | III
| pollution degree | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 |  |  | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | [6 empty] | 2 | 3 | 2
| product certifications | CE CCC GL China RoHS UL RCM EAC CSA | CSA CCC RCM China RoHS CE GL UL EAC | ASE EDF USSR BV CSA | USSR EDF ASE BV CSA | C-Tick UL GOST CSA GL | GL C-Tick GOST UL CSA | GOST CSA GL C-Tick UL | GOST C-Tick CSA UL GL | CSA GL UL | CSA UL GOST | CSA UL GOST | GOST UL CSA | GOST CSA UL | CSA GOST UL | UL CSA GOST | UL China RoHS CSA EAC REACH CE RoHS | UL Lloyd's RoHS CE CSA GOST REACH | RoHS CSA Lloyd's CE UL REACH GOST | CSA UL | CSA UL
| protection category | [15 empty] | RT I
| protective treatment |  |  | TC | TC | [14 empty] | TC | TC
| relative humidity | 95 % at 25…55 °C | 95 % at 25…55 °C |  |  | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | [7 empty] | 10…85 %
| resistance to electrostatic discharge | [8 empty] | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
| resistance to fast transients | [8 empty] | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
| shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 20 gn in operation 100 gn not in operation | 10 gn for in operation 30 gn for not operating | 10 gn for in operation 30 gn for not operating
| standards | UL 508 IEC 61812-1 | UL 508 IEC 61812-1 | IEC 60255 NF C 45-250 VDE 0435 | IEC 60255 NF C 45-250 VDE 0435 | EN/IEC 60255-1 | EN/IEC 60255-6 | EN/IEC 60255-1 | EN/IEC 60255-1 | IEC 60584-1 IEC 60947-1 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | UL 508 IEC 61810-1 CSA C22.2 No 14 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1
| vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | 3 gn, amplitude = +/- 0.75 mm (f = 10…150 Hz)in operation 5 gn, amplitude = +/- 0.75 mm (f = 10…150 Hz)not in operation | 3 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles in operation 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles not operating | 3 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles in operation 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles not operating
Main | [Ithe] conventional enclosed thermal current |  |  | 5 A 40 °C | 1 A 40 °C | [5 empty] | 16 A at -40…40 °C | 16 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C |  | 12 A at -40…55 °C | 6 A at -40…55 °C
| [Uc] control circuit voltage |  |  | 27 V AC/DC 50/60 Hz | 24 V AC/DC 50/60 Hz | [5 empty] | 220 V AC | 60 V DC | 220 V AC | 230 V AC | 6 V DC | 240 V AC |  | 24 V AC 50/60 Hz | 24 V AC 50/60 Hz
| [Us] rated supply voltage | [18 empty] | <= 230 V | <= 230 V
| analogue input type | [8 empty] | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584
| analogue output type | [8 empty] | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
| beacon or indicator bank unit type | [18 empty] | Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit
| bulb type | [18 empty] | Incandescent with BA 15d base | Incandescent with BA 15d base
| coil interference suppression |  |  | With | With
| component name | [18 empty] | XVDLS | XVDLS
| contact operation |  |  | Standard | Low level | [5 empty] | Standard | Standard | Standard | Standard | Standard | Standard
| contacts type and composition |  |  | 4 C/O | 4 C/O | [5 empty] | 1 C/O | 1 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 1 C/O | 2 C/O | 4 C/O
| control type |  |  | Selector switch | Selector switch | [8 empty] | Without push-button |  |  |  | Lockable test button | Lockable test button
| device short name | RE22 | RE22 | RHT | RHT | [5 empty] | RSB | RSB | RSB | RSB | RSB | RSB | RXG | RXM | RXM
| discrete output type | Relay | Relay
| light source | [18 empty] | Bulb not included, clear | Bulb not included, yellow
| material | [18 empty] | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
| maximum power consumption in VA | [5 empty] | 3 VA
| maximum power dissipation in W | [18 empty] | 5 W | 5 W
| measurement range |  |  |  |  | 183...528 V AC | 2...20 A current | 208...480 V voltage AC | 208...480 V voltage AC
| minimum switching current | [5 empty] | 10 mA at 5 V DC
| mounting diameter | [18 empty] | 45 mm | 45 mm
| nominal output current | 8 A | 8 A
| product or component type | Modular timing relay | Modular timing relay | Timing relay Plug-in relay | Plug-in relay Timing relay | Modular measurement and control relays | Modular measurement and control relays | Modular measurement and control relays | Modular measurement and control relays | Converter for thermocouples | Plug-in relay | Plug-in relay | Plug-in relay | Plug-in relay | Plug-in relay | Plug-in relay | Plug-in relay | Plug-in relay | Plug-in relay | Complete miniature beacon | Complete miniature beacon
| product specific application |  |  |  |  | For 3-phase supply |  | For 3-phase supply | For 3-phase supply
| range of product | Zelio Time | Zelio Time | Zelio Relay | Zelio Relay | Zelio Control | Zelio Control | Zelio Control | Zelio Control | Zelio Analog | Zelio Relay | Zelio Relay | Zelio Relay | Zelio Relay | Zelio Relay | Zelio Relay | Harmony Relay | Zelio Relay | Zelio Relay | Harmony XVD Optimum | Harmony XVD Optimum
| relay monitored parameters |  |  |  |  | Phase sequence Asymmetry Undervoltage and overvoltage in window mode Phase failure detection | Overcurrent detection | Asymmetry Phase sequence Phase failure detection | Undervoltage and overvoltage in window mode Asymmetry Phase sequence Phase failure detection
| relay name |  |  |  |  | RM10TE | RM17JC | RM17TA | RM17TE
| relay type |  |  |  |  | Multifunction control relay | Current control relay | Multifunction control relay | Multifunction control relay
| series name | [9 empty] | Interface relay | Interface relay | Interface relay | Interface relay | Interface relay | Interface relay | Interface relay | Miniature | Miniature
| signalling type | [18 empty] | Steady | Steady
| status LED |  |  | With | With | [5 empty] | Without | Without | Without | Without | Without | Without |  | Without | Without
| switching capacity in VA |  |  |  |  | 1250 VA | 1250 VA | 1250 VA | 1250 VA
| time delay |  |  |  |  | Adjustable 0.1...10 s, +/- 10 % of the full scale value | Without | Adjustable 0.1...10 s, +/- 10 % of the full scale value | Adjustable 0.1...10 s, +/- 10 % of the full scale value
| time delay range |  |  | 0.2...3 s 15...300 s 1.5...30 s | 15...300 s 0.2...3 s 1.5...30 s
| time delay type |  |  | On-delay | On-delay
| utilisation category | [5 empty] | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
| utilisation coefficient | [16 empty] | 20 % | 20 %
Offer Sustainability | China RoHS Regulation | China RoHS declaration | China RoHS declaration |  |  | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration |  | China RoHS declaration | China RoHS declaration |  | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration
| Circularity Profile | End of Life Information | End of Life Information |  |  | End of Life Information | End of Life Information | End of Life Information | End of Life Information | End of Life Information
| EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration |  |  | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration |  | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration |  | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
| Environmental Disclosure | Product Environmental Profile | Product Environmental Profile |  |  | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile |  | Product Environmental Profile | Product Environmental Profile |  | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile
| Mercury free | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes
| REACh Regulation | REACh Declaration | REACh Declaration |  |  | REACh Declaration | REACh Declaration | REACh Declaration | REACh Declaration | REACh Declaration | [6 empty] | REACh Declaration | REACh Declaration | REACh Declaration | REACh Declaration | REACh Declaration
| REACh free of SVHC | [9 empty] | Yes |  | Yes | Yes |  | Yes | Yes | Yes | Yes
| RoHS exemption information | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes
| Sustainable offer status | Green Premium product | Green Premium product |  |  | Green Premium product | Green Premium product | Green Premium product | Green Premium product | Green Premium product | Green Premium product |  | Green Premium product | Green Premium product |  | Green Premium product | Green Premium product | Green Premium product | Green Premium product | Green Premium product | Green Premium product
| Toxic heavy metal free | [9 empty] | Yes |  | Yes | Yes |  | Yes | Yes | Yes | Yes
| WEEE |  |  |  |  | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins |  | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins |  | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins |  | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
Packing Units | Package 1 Weight | 0.114 kg | 0.108 kg | 0.136 kg | 0.135 kg |  | 120 g | 89 g | 89 g | 0.101 kg | 0.001 kg | 0.001 kg | 0.001 kg | 61 g | 0.001 kg | 0.001 kg | 20.200 g | 0.035 kg | 0.036 kg | 0.101 kg | 0.100 kg
| Package 2 Weight | [5 empty] | 4.295 kg | 4.685 kg | 5.017 kg |  |  |  |  | 1.23 kg
| Package 3 Weight | [12 empty] | 7.876 kg

## pivot1_datasheet
Section | Parameters | Value
Complementary | CAD overall depth | 45 mm 45 mm 108 mm 108 mm 78.45 mm
| CAD overall height | 104 mm 104 mm 43 mm 43 mm 79 mm
| CAD overall width | 45 mm 45 mm 33 mm 33 mm
| Coil insulation class | Class F
| Coil resistance | 68 Ohm +/- 10 %
| Control signal pulse width | 100 ms with load in parallel 30 ms 100 ms with load in parallel 30 ms
| Maximum contact resistance | 100 mOhm
| Operate time | 20 ms
| Power on delay | 100 ms 100 ms
| Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV for 1.2…50 µs conforming to IEC 60664-1
| Recovery time | 120 ms on de-energisation 120 ms on de-energisation
| Release input voltage | <= 2.4 V <= 2.4 V
| Release time | 20 ms
| [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC 10 A at 30 V (DC) conforming to UL 10 A at 30 V (DC) conforming to IEC 10 A at 250 V (AC) conforming to IEC 10 A at 250 V (AC) conforming to UL 12 A at 28 V (DC) NO conforming to IEC 12 A at 250 V (AC) NO conforming to IEC 6 A at 28 V (DC) NC conforming to IEC 6 A at 250 V (AC) NC conforming to IEC 12 A at 28 V (DC) conforming to UL 12 A at 277 V (AC) conforming to UL 3 A at 28 V (DC) NC conforming to IEC 3 A at 250 V (AC) NC conforming to IEC 6 A at 28 V (DC) NO conforming to IEC 6 A at 250 V (AC) NO conforming to IEC 6 A at 277 V (AC) conforming to UL 8 A at 30 V (DC) conforming to UL
| [Ithe] conventional enclosed thermal current | 10 A at -40…55 °C
| [Uc] control circuit voltage | 6 V DC
| [Ue] rated operational voltage | 176...264 V AC 50 Hz 187...264 V AC 60 Hz 48...66 V DC 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz 4.8...6.6 V DC 192...288 V AC 50 Hz 204...288 V AC 60 Hz 176...264 V AC 50 Hz 187...264 V AC 60 Hz
| [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1 2 kV 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 250 V 250 V 400 V conforming to EN/IEC 60947 400 V conforming to EN/IEC 60947 400 V conforming to EN/IEC 60947 400 V conforming to EN/IEC 60947 400 V conforming to EN/IEC 60947 400 V conforming to EN/IEC 60947 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL
| [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1 4 kV IEC 60947-1 IEC 61000-4-5 3.6 kV 3.6 kV IEC 61000-4-5 3.6 kV IEC 61000-4-5 IEC 61000-4-5 3.6 kV 3.6 kV IEC 61000-4-5 IEC 61000-4-5 3.6 kV 6 kV 1.2/50 µs 4 kV during 1.2/50 µs 2.5 kV during 1.2/50 µs
| [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 % 24...240 V AC/DC 50/60 Hz 24...240 V AC/DC 50/60 Hz 24 V DC +/- 20 %, non isolated
| abnormal analogue output current | -30…0 mA when no input or input wire broken
| abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
| adjustment of asymmetry threshold | 5...15 % of Un selected 5...15 % of Un selected 5...15 % of Un selected
| average coil consumption | 2.5 W at 20 °C 2.5 W at 20 °C 0.75 VA AC 60 Hz 0.45 W DC 0.75 VA AC 60 Hz 0.45 W DC 0.75 VA AC 60 Hz 0.75 VA AC 60 Hz
| average coil consumption in VA | 2.9 at 20 °C 2.9 at 20 °C 1.2 at 60 Hz 1.2 at 60 Hz
| average coil resistance | 35500 Ohm network: AC at 20 °C +/- 15 % 7500 Ohm network: DC at 20 °C +/- 10 % 38500 Ohm network: AC at 20 °C +/- 15 % 90 Ohm network: DC at 20 °C +/- 10 % 42500 Ohm network: AC at 20 °C +/- 15 % 35500 Ohm network: AC at 20 °C +/- 15 % 180 Ohm at 20 °C +/- 15 % 180 Ohm at 20 °C +/- 15 %
| average consumption | 1.2 VA at 60 Hz 1.2 VA at 60 Hz
| average resistance | 30 mOhm at 20 °C 30 mOhm at 20 °C
| cable entry | 1 entry tapped for Pg 7 1 entry tapped for Pg 7
| clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm²
| cold junction compensation | Built-in, measurement: between 0 and 60 °C
| colour of cover | Standard
| connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end
| contact bounce time | <= 10 ms <= 10 ms
| contacts material | Cadmium free Silver alloy (Ag/Ni) Silver alloy (Ag/Ni) Silver alloy (Ag/Ni) Silver alloy (Ag/Ni) Silver alloy (Ag/Ni) Silver alloy (Ag/Ni) Silver alloy (AgSnO2In2O3) AgNi AgNi
| contacts type and composition | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free
| control circuit frequency | 40...70 Hz sinusoidal 50...60 Hz +/- 10 % 50...60 Hz +/- 10 % 50...60 Hz +/- 10 %
| control circuit voltage limits | - 12 % + 10 % Un - 12 % + 10 % Un - 12 % + 10 % Un 0.8...1.1 Uc conforming to IEC 60255 0.8...1.1 Uc conforming to IEC 60255
| control type | Rotary knob Diagnostic button Potentiometer external Rotary knob Diagnostic button Lockable test button
| creepage distance | 4 kV/3 conforming to IEC 60664-1 4 kV/3 conforming to IEC 60664-1
| current consumption | <= 40 mA for voltage output <= 60 mA for current output
| delay at power up | 0.5 s 650 ms 650 ms 650 ms
| device presentation | Complete product Complete product Complete product Complete product Complete product Complete product Complete product Complete product Complete product
| dielectric strength | 1000 V AC between contacts with micro disconnection 5000 V AC between coil and contact with reinforced insulation
| drop-out voltage threshold | >= 0.15 Uc AC >= 0.1 Uc DC >= 0.15 Uc AC >= 0.1 Uc DC >= 0.15 Uc AC >= 0.15 Uc AC >= 0.1 Uc DC >= 0.15 Uc >= 0.15 Uc
| electrical durability | 100000 cycles 100000 cycles 100000 cycles 100000 cycles 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC 100000 cycles for NO resistive load at 55 °C 100000 cycles for NC resistive load at 55 °C 100000 cycles for resistive load 100000 cycles for resistive load
| fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
| housing material | Self-extinguishing plastic Self-extinguishing plastic Self-extinguishing plastic Self-extinguishing plastic Self-extinguishing Self-extinguishing
| hysteresis | 15 % fixed of threshold setting 2 % 2 % 2 %
| immunity to microbreaks | 10 ms 10 ms
| input current | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C
| insulation | Between supply and measurement
| insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 100 MOhm at 500 V DC conforming to IEC 60664-1 100 MOhm at 500 V DC conforming to IEC 60664-1 1000 MOhm at 500 V DC
| load current | 10 A at 250 V AC
| local signalling | LED (green) for power ON LED (yellow) for relay ON LED (green) for power ON LED (yellow) for relay ON LED (green) for power ON LED (yellow) for relay ON LED (green)power ON: LED (yellow)relay ON: LED (green) for power ON Flag
| marking | CE : 73/23/EEC CE : EMC 89/336/EEC CE CE CE CE CE CE CE CE CE CE
| maximum measuring cycle | 30 ms measurement cycle as true rms value 150 ms measurement cycle as true rms value 150 ms measurement cycle as true rms value 150 ms measurement cycle as true rms value
| maximum power consumption in W | 1 W
| maximum switching capacity | 4000 VA AC 448 W DC 4000 VA AC 448 W DC 2000 VA AC 224 W DC 2000 VA AC 224 W DC 2000 VA AC 224 W DC 2000 VA AC 224 W DC 2500 VA 3000 VA/336 W 1500 VA/168 W
| maximum switching current | 5 A AC 5 A DC 5 A AC 5 A DC 5 A AC 5 A DC 8 A 8 A
| maximum switching voltage | 250 V AC/DC 250 V AC 250 V DC 250 V AC 250 V DC 250 V AC 250 V DC 250 V AC 250 V AC 300 V DC 400 V AC 300 V DC 400 V AC 300 V DC 400 V AC 300 V DC 400 V AC 300 V DC 400 V AC 300 V DC 400 V AC 250 V AC 30 V DC 250 V conforming to IEC 250 V conforming to IEC
| maximum voltage drop | <100 V for 3 A at 24 V <100 V for 3 A at 24 V
| measurement accuracy | +/- 10 % of the full scale value
| measurement error | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C
| measurement voltage limits | 183…528 V AC 183…528 V AC
| mechanical durability | 30000000 cycles 30000000 cycles 30000000 cycles 30000000 cycles 10000000 cycles 10000000 cycles 20000000 cycles 20000000 cycles 30000000 cycles 30000000 cycles 30000000 cycles 30000000 cycles 30000000 cycles 30000000 cycles 10000000 cycles 10000000 cycles 10000000 cycles
| minimum switching capacity | 50 mVA at 1 mA, 1 V 150 mVA at 10 mA, 1 V 300 mW at 5 mA 300 mW at 5 mA 300 mW at 5 mA 300 mW at 5 mA 300 mW at 5 mA 300 mW at 5 mA 500 mW at 100 mA, 5 V DC 170 mW at 10 mA, 17 V 170 mW at 10 mA, 17 V
| minimum switching current | 10 mA at 5 V DC 10 mA at 5 V DC 10 mA at 5 V DC 10 mA at 5 V DC 10 mA at 5 V DC 5 mA 5 mA 5 mA 5 mA 5 mA 5 mA
| minimum switching voltage | 5 V 5 V 5 V 5 V 5 V 5 V
| mounting position | Any position Any position Any position
| mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 35 mm symmetrical DIN rail conforming to EN/IEC 60715 35 mm symmetrical DIN rail conforming to EN/IEC 60715 35 mm symmetrical DIN rail conforming to EN/IEC 60715 35 mm DIN rail conforming to EN/IEC 60715 35 mm DIN rail conforming to EN/IEC 60715
| net weight | 0.13 kg 0.13 kg 0.13 kg 0.13 kg 0.105 kg 0.105 kg 0.12 kg 0.08 kg 0.08 kg 0.13 kg 0.13 kg 0.02 kg 0.037 kg 0.037 kg
| nominal output current | 5 A 5 A 5 A 5 A
| operate time | 20 ms 20 ms
| operating position | Any position without derating Any position without derating Any position without derating Any position without derating Any position Any position Any position Any position Any position Any position Any position Any position Any position Any position
| operating rate | <= 360 operations/hour full load <= 360 operations/hour full load <= 360 operations/hour full load <= 360 operations/hour full load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 1800 cycles/hour under load <= 18000 cycles/hour no-load <= 1200 cycles/hour under load <= 18000 cycles/hour no-load <= 1200 cycles/hour under load <= 18000 cycles/hour no-load
| operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
| operating voltage tolerance | - 15 % + 10 % Un
| output contacts | 1 C/O 1 C/O 1 C/O 1 C/O
| overvoltage category | III conforming to IEC 60664-1 III conforming to IEC 60664-1 III conforming to IEC 60664-1 III conforming to IEC 60664-1 III conforming to IEC 60664-1 III conforming to IEC 60664-1
| phase failure sensitivity | 0.7 Un 0.7 Un 0.7 Un
| polarity | Yes DC
| power consumption in VA | 0…22 VA at 400 V AC 50 Hz 0…22 VA at 400 V AC 50 Hz 0…22 VA at 400 V AC 50 Hz 3 VA at 240 V AC 3 VA at 240 V AC
| power consumption in W | 1.5 W at 240 V DC 1.5 W at 240 V DC
| protection category | RT I RT I RT I RT I RT I RT I RT I RT I
| protection type | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output
| rated operational voltage limits | 19.2...26.4 V AC 19.2...26.4 V AC
| release time | 20 ms 20 ms
| repeat accuracy | +/- 0.5 % for input and measurement circuit 0.5 % for input and measurement circuit 3 % for time delay 0.5 % for input and measurement circuit 3 % for time delay 0.5 % for input and measurement circuit 3 % for time delay +/- 0.5 % conforming to IEC 61812-1 +/- 0.5 % conforming to IEC 61812-1 +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C +/- 1 % +/- 1 %
| reset time | 1500 ms time delay 1500 ms time delay 1500 ms time delay 100 ms 100 ms
| resistive rated load | 16 A at 250 V AC 16 A at 28 V DC 16 A at 250 V AC 16 A at 28 V DC 8 A at 250 V AC 8 A at 28 V DC 8 A at 250 V AC 8 A at 28 V DC 8 A at 250 V AC 8 A at 28 V DC 8 A at 250 V AC 8 A at 28 V DC 12 A at 250 V AC 12 A at 28 V DC 6 A at 250 V AC 6 A at 28 V DC
| response time | < 200 ms (in the event of a fault) < 200 ms (in the event of a fault) < 200 ms (in the event of a fault) < 200 ms (in the event of a fault)
| safety reliability data | MTTFd = 502.2 years B10d = 470000 MTTFd = 502.2 years B10d = 470000 B10d = 470000 MTTFd = 502.2 years B10d = 200000 MTTFd = 216.8 years MTTFd = 251.1 years B10d = 230000 B10d = 45447 MTTFd = 49.2 years B10d = 100000 B10d = 100000 B10d = 100000 B10d = 100000 B10d = 100000 B10d = 100000 B10d = 100000 B10d = 100000 B10d = 100000
| sale per indivisible quantity | 10 10 10 10 10 10
| setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 +/- 15 % of full scale +/- 15 % of full scale
| shape of pin | Flat Flat Flat Flat Flat Flat Flat Flat
| status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised Without
| supply frequency | 50/60 Hz +/- 10 % 50/60 Hz +/- 10 % 50/60 Hz +/- 10 % 50...60 Hz +/- 5 % 50...60 Hz +/- 5 %
| supply voltage limits | 20.4…264 V AC/DC 183…528 V AC 183…528 V AC 183…528 V AC
| surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
| switching capacity in VA | 2000 VA 2000 VA
| switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
| temperature coefficient | 200 ppm/°C
| temperature drift | +/- 0.05 %/°C +/- 0.05 %/°C
| terminals description ISO n°1 | (GND)GROUND (COM-1)PW (COM-1)PW (GND)GROUND (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC (31-32-34)OC (41-42-44)OC (11-12-14)OC (21-22-24)OC (A1-A2)CO
| test levels | Level A group mounting Level A group mounting Level A group mounting
| threshold adjustment voltage | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC -2...-17 % in the range 220 V AC +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC 2...20 % of Un selected -2...-12 % in the range 208 V AC 2...20 % of Un selected +2...+17 % in the range 480 V AC -2...-17 % in the range 220 V AC
| threshold setting | 10...100 %
| tightening torque | 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1.1 N.m
| time delay range | 0.05...1 s 0.3...3 s 3...30 h 30...300 min 10...100 s 30...300 s 3...30 s 30...300 h 1...10 s 3...30 min 10...100 s 3...30 h 1...10 s 3...30 s 30...300 h 0.3...3 s 0.05...1 s 30...300 min 30...300 s 3...30 min
| time delay type | Aw A C
| torque value | 0.8 N.m
| utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
| utilisation coefficient | 20 %
| voltage drift | +/- 0.2 %/V +/- 0.2 %/V
| voltage range | 208...480 V phase to phase 208...480 V phase to phase 208...480 V phase to phase 0.85...1.1 Us 0.85...1.1 Us
| width | 17.5 mm 17.5 mm 17.5 mm 17.5 mm 22.5 mm 22.5 mm
Contractual warranty | Warranty | 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months
Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 IP20 (terminal block) IP50 (housing) IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529 IP40 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529
| ambient air temperature for operation | -20…50 °C -20…50 °C -20…50 °C -20…50 °C -20…60 °C -20…60 °C 0…50 °C mounting side by side 0…60 °C 2 cm spacing -25…70 °C -25…70 °C -5…40 °C conforming to IEC 60255 -5…40 °C conforming to IEC 60255 -40…70 °C (AC) -40…85 °C (DC) -40…70 °C (AC) -40…85 °C (DC) -40…70 °C (AC) -40…85 °C (DC) -40…70 °C (AC) -40…85 °C (DC) -40…70 °C (AC) -40…85 °C (DC) -40…70 °C (AC) -40…85 °C (DC) -40…70 °C -40…55 °C -40…55 °C
| ambient air temperature for storage | -40…70 °C -40…70 °C -40…70 °C -40…70 °C -40…70 °C -40…70 °C -40…85 °C -40…70 °C -40…70 °C -40…70 °C -40…70 °C -40…85 °C -40…85 °C -40…85 °C -40…85 °C -40…85 °C -40…85 °C -40…85 °C -40…85 °C -40…85 °C
| dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 2500 V 2500 V 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1300 V AC between contacts with micro disconnection 2000 V AC between coil and contact 2000 V AC between poles 1300 V AC between contacts with micro disconnection 2000 V AC between coil and contact 2000 V AC between poles
| dielectric test voltage | 2 kV AC 50 Hz 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
| directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
| disturbance radiated/conducted | CISPR 22 group 1 - class B CISPR 11
| electrical shock protection class | Class II conforming to IEC 60536 Class II conforming to IEC 60536
| electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
| fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
| immunity to microbreaks | 10 ms 10 ms during time delay 2 ms after time delay 10 ms during time delay 2 ms after time delay
| non-dissipating shock wave | 4 kV 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
| overvoltage category | III
| pollution degree | 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 2 conforming to IEC 60664-1 2 3 2
| product certifications | GL C-Tick GOST UL CSA GOST CSA GL C-Tick UL GOST C-Tick CSA UL GL C-Tick UL GOST CSA GL CE CCC GL China RoHS UL RCM EAC CSA CSA CCC RCM China RoHS CE GL UL EAC CSA GL UL CSA UL CSA UL USSR EDF ASE BV CSA ASE EDF USSR BV CSA CSA UL GOST CSA UL GOST GOST CSA UL CSA GOST UL UL CSA GOST GOST UL CSA UL China RoHS CSA EAC REACH CE RoHS UL Lloyd's RoHS CE CSA GOST REACH RoHS CSA Lloyd's CE UL REACH GOST
| protection category | RT I
| protective treatment | TC TC TC TC
| relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30 95 % at 55 °C conforming to IEC 60068-2-30 95 % at 55 °C conforming to IEC 60068-2-30 95 % at 55 °C conforming to IEC 60068-2-30 95 % at 25…55 °C 95 % at 25…55 °C 10…85 %
| resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
| resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
| shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1 15 gn for 11 ms conforming to IEC 60255-21-1 15 gn for 11 ms conforming to IEC 60255-21-1 15 gn for 11 ms conforming to IEC 60255-21-1 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 50 gn for 11 ms conforming to IEC 60068-2-27 50 gn for 11 ms conforming to NF C 20-608 50 gn for 11 ms conforming to NF C 20-608 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 20 gn in operation 100 gn not in operation 10 gn for in operation 30 gn for not operating 10 gn for in operation 30 gn for not operating
| standards | EN/IEC 60255-6 EN/IEC 60255-1 EN/IEC 60255-1 EN/IEC 60255-1 UL 508 IEC 61812-1 UL 508 IEC 61812-1 IEC 60584-1 IEC 60947-1 EN/IEC 60947-5-1 EN/IEC 60947-5-1 IEC 60255 NF C 45-250 VDE 0435 IEC 60255 NF C 45-250 VDE 0435 CSA C22.2 No 14 UL 508 EN/IEC 61810-1 CSA C22.2 No 14 EN/IEC 61810-1 UL 508 UL 508 CSA C22.2 No 14 EN/IEC 61810-1 CSA C22.2 No 14 UL 508 EN/IEC 61810-1 CSA C22.2 No 14 EN/IEC 61810-1 UL 508 EN/IEC 61810-1 CSA C22.2 No 14 UL 508 UL 508 IEC 61810-1 CSA C22.2 No 14 EN/IEC 61810-1 CSA C22.2 No 14 UL 508 CSA C22.2 No 14 UL 508 EN/IEC 61810-1
| vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 3 gn, amplitude = +/- 0.75 mm (f = 10…150 Hz)in operation 5 gn, amplitude = +/- 0.75 mm (f = 10…150 Hz)not in operation 3 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles in operation 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles not operating 3 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles in operation 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles not operating
Main | [Ithe] conventional enclosed thermal current | 1 A 40 °C 5 A 40 °C 16 A at -40…40 °C 16 A at -40…40 °C 8 A at -40…40 °C 8 A at -40…40 °C 8 A at -40…40 °C 8 A at -40…40 °C 12 A at -40…55 °C 6 A at -40…55 °C
| [Uc] control circuit voltage | 24 V AC/DC 50/60 Hz 27 V AC/DC 50/60 Hz 220 V AC 60 V DC 230 V AC 6 V DC 240 V AC 220 V AC 24 V AC 50/60 Hz 24 V AC 50/60 Hz
| [Us] rated supply voltage | <= 230 V <= 230 V
| analogue input type | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584
| analogue output type | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
| beacon or indicator bank unit type | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit
| bulb type | Incandescent with BA 15d base Incandescent with BA 15d base
| coil interference suppression | With With
| component name | XVDLS XVDLS
| contact operation | Low level Standard Standard Standard Standard Standard Standard Standard
| contacts type and composition | 4 C/O 4 C/O 1 C/O 1 C/O 2 C/O 2 C/O 2 C/O 2 C/O 1 C/O 2 C/O 4 C/O
| control type | Selector switch Selector switch Without push-button Lockable test button Lockable test button
| device short name | RE22 RE22 RHT RHT RSB RSB RSB RSB RSB RSB RXG RXM RXM
| discrete output type | Relay Relay
| light source | Bulb not included, clear Bulb not included, yellow
| material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
| maximum power consumption in VA | 3 VA
| maximum power dissipation in W | 5 W 5 W
| measurement range | 2...20 A current 208...480 V voltage AC 208...480 V voltage AC 183...528 V AC
| minimum switching current | 10 mA at 5 V DC
| mounting diameter | 45 mm 45 mm
| nominal output current | 8 A 8 A
| product or component type | Modular measurement and control relays Modular measurement and control relays Modular measurement and control relays Modular measurement and control relays Modular timing relay Modular timing relay Converter for thermocouples Complete miniature beacon Complete miniature beacon Plug-in relay Timing relay Timing relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay
| product specific application | For 3-phase supply For 3-phase supply For 3-phase supply
| range of product | Zelio Control Zelio Control Zelio Control Zelio Control Zelio Time Zelio Time Zelio Analog Harmony XVD Optimum Harmony XVD Optimum Zelio Relay Zelio Relay Zelio Relay Zelio Relay Zelio Relay Zelio Relay Zelio Relay Zelio Relay Harmony Relay Zelio Relay Zelio Relay
| relay monitored parameters | Overcurrent detection Asymmetry Phase sequence Phase failure detection Undervoltage and overvoltage in window mode Asymmetry Phase sequence Phase failure detection Phase sequence Asymmetry Undervoltage and overvoltage in window mode Phase failure detection
| relay name | RM17JC RM17TA RM17TE RM10TE
| relay type | Current control relay Multifunction control relay Multifunction control relay Multifunction control relay
| series name | Interface relay Interface relay Interface relay Interface relay Interface relay Interface relay Interface relay Miniature Miniature
| signalling type | Steady Steady
| status LED | With With Without Without Without Without Without Without Without Without
| switching capacity in VA | 1250 VA 1250 VA 1250 VA 1250 VA
| time delay | Without Adjustable 0.1...10 s, +/- 10 % of the full scale value Adjustable 0.1...10 s, +/- 10 % of the full scale value Adjustable 0.1...10 s, +/- 10 % of the full scale value
| time delay range | 15...300 s 0.2...3 s 1.5...30 s 0.2...3 s 15...300 s 1.5...30 s
| time delay type | On-delay On-delay
| utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
| utilisation coefficient | 20 % 20 %
Offer Sustainability | China RoHS Regulation | China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration
| Circularity Profile | End of Life Information End of Life Information End of Life Information End of Life Information End of Life Information End of Life Information End of Life Information
| EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
| Environmental Disclosure | Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile
| Mercury free | Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes
| REACh Regulation | REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration
| REACh free of SVHC | Yes Yes Yes Yes Yes Yes Yes
| RoHS exemption information | Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes
| Sustainable offer status | Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product
| Toxic heavy metal free | Yes Yes Yes Yes Yes Yes Yes
| WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
Packing Units | Package 1 Weight | 120 g 89 g 89 g 0.114 kg 0.108 kg 0.101 kg 0.101 kg 0.100 kg 0.135 kg 0.136 kg 0.001 kg 0.001 kg 61 g 0.001 kg 0.001 kg 0.001 kg 20.200 g 0.035 kg 0.036 kg
| Package 2 Weight | 4.295 kg 4.685 kg 5.017 kg 1.23 kg
| Package 3 Weight | 7.876 kg