## status
0 | RM17JC00MW | https://www.se.com/ww/en/product/RM17JC00MW/ | Found
1 | RM17TA00 | https://www.se.com/ww/en/product/RM17TA00/ | Found
2 | RM17TE00 | https://www.se.com/ww/en/product/RM17TE00/ | Found
3 | RM10TE00 | https://www.se.com/ww/en/product/RM10TE00/ | Not Found
4 | RM17TG00 | https://www.se.com/ww/en/product/RM17TG00/ | Found
5 | RM17TG20 | https://www.se.com/ww/en/product/RM17TG20/ | Found
6 | RM17TT00 | https://www.se.com/ww/en/product/RM17TT00/ | Found
7 | RM17TU00 | https://www.se.com/ww/en/product/RM17TU00/ | Found
8 | RM17UAS14 | https://www.se.com/ww/en/product/RM17UAS14/ | Found
9 | RM17UAS15 | https://www.se.com/ww/en/product/RM17UAS15/ | Found
10 | RM17UAS15315M | https://www.se.com/ww/en/product/RM17UAS15315M/ | Found
11 | RM17UAS16 | https://www.se.com/ww/en/product/RM17UAS16/ | Found
12 | RM17UB310 | https://www.se.com/ww/en/product/RM17UB310/ | Found
13 | RM17UBE15 | https://www.se.com/ww/en/product/RM17UBE15/ | Found
14 | RM17UBE16 | https://www.se.com/ww/en/product/RM17UBE16/ | Found
15 | RM35ATL0MW | https://www.se.com/ww/en/product/RM35ATL0MW/ | Found
16 | RM35ATR5MW | https://www.se.com/ww/en/product/RM35ATR5MW/ | Found
17 | RM35ATW5MW | https://www.se.com/ww/en/product/RM35ATW5MW/ | Found
18 | RM35BA10 | https://www.se.com/ww/en/product/RM35BA10/ | Found
19 | RM35HZ21FM | https://www.se.com/ww/en/product/RM35HZ21FM/ | Found
20 | RM35JA31MW | https://www.se.com/ww/en/product/RM35JA31MW/ | Found
21 | RM35JA32MW | https://www.se.com/ww/en/product/RM35JA32MW/ | Found
22 | RM35LM33MW | https://www.se.com/ww/en/product/RM35LM33MW/ | Found
23 | RM35LV14MW | https://www.se.com/ww/en/product/RM35LV14MW/ | Found
24 | RM35S0MW | https://www.se.com/ww/en/product/RM35S0MW/ | Found
25 | RM35TF30 | https://www.se.com/ww/en/product/RM35TF30/ | Found
26 | RM35TF30SP01 | https://www.se.com/ww/en/product/RM35TF30SP01/ | Not Found
27 | RM35TM250MW | https://www.se.com/ww/en/product/RM35TM250MW/ | Found
28 | RM35TM50MW | https://www.se.com/ww/en/product/RM35TM50MW/ | Found
29 | RM35UA11MW | https://www.se.com/ww/en/product/RM35UA11MW/ | Found
30 | RM35UA12MW | https://www.se.com/ww/en/product/RM35UA12MW/ | Found
31 | RM35UA13MW | https://www.se.com/ww/en/product/RM35UA13MW/ | Found
32 | RM35UB330 | https://www.se.com/ww/en/product/RM35UB330/ | Found
33 | RM35UB3N30 | https://www.se.com/ww/en/product/RM35UB3N30/ | Found
34 | RM22JA21MR | https://www.se.com/ww/en/product/RM22JA21MR/ | Found
35 | RM22JA31MR | https://www.se.com/ww/en/product/RM22JA31MR/ | Found
36 | RM22JA31MRSP01 | https://www.se.com/ww/en/product/RM22JA31MRSP01/ | Not Found
37 | RM22LA32MR | https://www.se.com/ww/en/product/RM22LA32MR/ | Found
38 | RM22LA32MRSP01 | https://www.se.com/ww/en/product/RM22LA32MRSP01/ | Not Found
39 | RM22LA32MT | https://www.se.com/ww/en/product/RM22LA32MT/ | Found
40 | RM22LG11MR | https://www.se.com/ww/en/product/RM22LG11MR/ | Found
41 | RM22LG11MT | https://www.se.com/ww/en/product/RM22LG11MT/ | Found
42 | RM22TA31 | https://www.se.com/ww/en/product/RM22TA31/ | Found
43 | RM22TA33 | https://www.se.com/ww/en/product/RM22TA33/ | Found
44 | RM22TG20 | https://www.se.com/ww/en/product/RM22TG20/ | Found
45 | RM22TR31 | https://www.se.com/ww/en/product/RM22TR31/ | Found
46 | RM22TR33 | https://www.se.com/ww/en/product/RM22TR33/ | Found
47 | RM22TU21 | https://www.se.com/ww/en/product/RM22TU21/ | Found
48 | RM22TU23 | https://www.se.com/ww/en/product/RM22TU23/ | Found
49 | RM22UA21MR | https://www.se.com/ww/en/product/RM22UA21MR/ | Found
50 | RM22UA22MR | https://www.se.com/ww/en/product/RM22UA22MR/ | Found
51 | RM22UA23MR | https://www.se.com/ww/en/product/RM22UA23MR/ | Found
52 | RM22UA31MR | https://www.se.com/ww/en/product/RM22UA31MR/ | Found
53 | RM22UA32MR | https://www.se.com/ww/en/product/RM22UA32MR/ | Found
54 | RM22UA33MR | https://www.se.com/ww/en/product/RM22UA33MR/ | Found
55 | RM22UA33MT | https://www.se.com/ww/en/product/RM22UA33MT / | Not Found
56 | RM22UB34 | https://www.se.com/ww/en/product/RM22UB34/ | Found
57 | RM35JA32MR | https://www.se.com/ww/en/product/RM35JA32MR/ | Found
58 | RM35JA32MRSP01 | https://www.se.com/ww/en/product/RM35JA32MRSP01/ | Not Found
59 | RM35JA32MT | https://www.se.com/ww/en/product/RM35JA32MT/ | Found
60 | RMNF22TB30 | https://www.se.com/ww/en/product/RMNF22TB30/ | Found
61 | RE10RMMU | https://www.se.com/ww/en/product/RE10RMMU/ | Not Found
62 | RE17LAMW | https://www.se.com/ww/en/product/RE17LAMW/ | Found
63 | RE17LCBM | https://www.se.com/ww/en/product/RE17LCBM/ | Found
64 | RE17LHBM | https://www.se.com/ww/en/product/RE17LHBM/ | Found
65 | RE17LLBM | https://www.se.com/ww/en/product/RE17LLBM/ | Found
66 | RE17LMBM | https://www.se.com/ww/en/product/RE17LMBM/ | Found
67 | RE17RAMU | https://www.se.com/ww/en/product/RE17RAMU/ | Found
68 | RE17RBMU | https://www.se.com/ww/en/product/RE17RBMU/ | Found
69 | RE17RCMU | https://www.se.com/ww/en/product/RE17RCMU/ | Found
70 | RE17RHMU | https://www.se.com/ww/en/product/RE17RHMU/ | Found
71 | RE17RLJU | https://www.se.com/ww/en/product/RE17RLJU/ | Found
72 | RE17RLMU | https://www.se.com/ww/en/product/RE17RLMU/ | Found
73 | RE17RMEMU | https://www.se.com/ww/en/product/RE17RMEMU/ | Found
74 | RE17RMJU | https://www.se.com/ww/en/product/RE17RMJU/ | Found
75 | RE17RMMU | https://www.se.com/ww/en/product/RE17RMMU/ | Found
76 | RE17RMMW | https://www.se.com/ww/en/product/RE17RMMW/ | Found
77 | RE17RMMWS | https://www.se.com/ww/en/product/RE17RMMWS/ | Found
78 | RE17RMXMU | https://www.se.com/ww/en/product/RE17RMXMU/ | Found
79 | RE22R1QMU | https://www.se.com/ww/en/product/RE22R1QMU/ | Found
80 | RE22R1QMQ | https://www.se.com/ww/en/product/RE22R1QMQ/ | Found
81 | RE22R2AMU | https://www.se.com/ww/en/product/RE22R2AMU/ | Found
82 | RE22R2MJU | https://www.se.com/ww/en/product/RE22R2MJU/ | Found
83 | RE22R2MMW | https://www.se.com/ww/en/product/RE22R2MMW/ | Found
84 | RE22R2MMU | https://www.se.com/ww/en/product/RE22R2MMU/ | Found
85 | RE22R2MXMU | https://www.se.com/ww/en/product/RE22R2MXMU/ | Found
86 | RE22R1ACMR | https://www.se.com/ww/en/product/RE22R1ACMR/ | Found
87 | RE22R1AKMR | https://www.se.com/ww/en/product/RE22R1AKMR/ | Found
88 | RE22R1AMR | https://www.se.com/ww/en/product/RE22R1AMR/ | Found
89 | RE22R1CMR | https://www.se.com/ww/en/product/RE22R1CMR/ | Found
90 | RE22R1CMR | https://www.se.com/ww/en/product/RE22R1CMR/ | Found
91 | RE22R1DMR | https://www.se.com/ww/en/product/RE22R1DMR/ | Found
92 | RE22R1HMR | https://www.se.com/ww/en/product/RE22R1HMR/ | Found
93 | RE22R1KMR | https://www.se.com/ww/en/product/RE22R1KMR/ | Found
94 | RE22R1MAMR | https://www.se.com/ww/en/product/RE22R1MAMR/ | Found
95 | RE22R1MKMR | https://www.se.com/ww/en/product/RE22R1MKMR/ | Found
96 | RE22R1MLMR | https://www.se.com/ww/en/product/RE22R1MLMR/ | Found
97 | RE22R1MYMR | https://www.se.com/ww/en/product/RE22R1MYMR/ | Found
98 | RE22R1QCMU | https://www.se.com/ww/en/product/RE22R1QCMU/ | Found
99 | RE22R2ACMR | https://www.se.com/ww/en/product/RE22R2ACMR/ | Found
100 | RE22R2AMR | https://www.se.com/ww/en/product/RE22R2AMR/ | Found
101 | RE22R2CMR | https://www.se.com/ww/en/product/RE22R2CMR/ | Found
102 | RE22R2DMR | https://www.se.com/ww/en/product/RE22R2DMR/ | Found
103 | RE22R2HMR | https://www.se.com/ww/en/product/RE22R2HMR/ | Found
104 | RE22R2KMR | https://www.se.com/ww/en/product/RE22R2KMR/ | Found
105 | RE22R2MWMR | https://www.se.com/ww/en/product/RE22R2MWMR/ | Found
106 | RE22R2MYMR | https://www.se.com/ww/en/product/RE22R2MYMR/ | Found
107 | RE22R2QEMR | https://www.se.com/ww/en/product/RE22R2QEMR/ | Found
108 | RE22R2QEMT | https://www.se.com/ww/en/product/RE22R2QEMT/ | Found
109 | RE22R2QGMR | https://www.se.com/ww/en/product/RE22R2QGMR/ | Found
110 | RE22R2QTMR | https://www.se.com/ww/en/product/RE22R2QTMR/ | Found
111 | RENF22R2MMW | https://www.se.com/ww/en/product/RENF22R2MMW/ | Found
112 | RE48AML12MW | https://www.se.com/ww/en/product/RE48AML12MW/ | Found
113 | RE48ATM12MW | https://www.se.com/ww/en/product/RE48ATM12MW/ | Found
114 | RE48AMH13MW | https://www.se.com/ww/en/product/RE48AMH13MW/ | Found
115 | RE48ACV12MW | https://www.se.com/ww/en/product/RE48ACV12MW/ | Found
116 | REXL2TMJD | https://www.se.com/ww/en/product/REXL2TMJD/ | Found
117 | REXL2TMBD | https://www.se.com/ww/en/product/REXL2TMBD/ | Found
118 | REXL2TMB7 | https://www.se.com/ww/en/product/REXL2TMB7/ | Found
119 | REXL2TMF7 | https://www.se.com/ww/en/product/REXL2TMF7/ | Found
120 | REXL2TMP7 | https://www.se.com/ww/en/product/REXL2TMP7/ | Found
121 | REXL4TMJD | https://www.se.com/ww/en/product/REXL4TMJD/ | Found
122 | REXL4TMBD | https://www.se.com/ww/en/product/REXL4TMBD/ | Found
123 | REXL4TMB7 | https://www.se.com/ww/en/product/REXL4TMB7/ | Found
124 | REXL4TMF7 | https://www.se.com/ww/en/product/REXL4TMF7/ | Found
125 | REXL4TMP7 | https://www.se.com/ww/en/product/REXL4TMP7/ | Found
126 | RMPT10BD | https://www.se.com/ww/en/product/RMPT10BD/ | Found
127 | RMPT20BD | https://www.se.com/ww/en/product/RMPT20BD/ | Found
128 | RMPT30BD | https://www.se.com/ww/en/product/RMPT30BD/ | Found
129 | RMPT50BD | https://www.se.com/ww/en/product/RMPT50BD/ | Found
130 | RMPT70BD | https://www.se.com/ww/en/product/RMPT70BD/ | Not Found
131 | RMPT13BD | https://www.se.com/ww/en/product/RMPT13BD/ | Found
132 | RMPT23BD | https://www.se.com/ww/en/product/RMPT23BD/ | Found
133 | RMPT33BD | https://www.se.com/ww/en/product/RMPT33BD/ | Found
134 | RMPT53BD | https://www.se.com/ww/en/product/RMPT53BD/ | Found
135 | RMPT73BD | https://www.se.com/ww/en/product/RMPT73BD/ | Found
136 | RMTJ40BD | https://www.se.com/ww/en/product/RMTJ40BD/ | Found
137 | RMTJ60BD | https://www.se.com/ww/en/product/RMTJ60BD/ | Found
138 | RMTJ80BD | https://www.se.com/ww/en/product/RMTJ80BD/ | Found
139 | RMTK80BD | https://www.se.com/ww/en/product/RMTK80BD/ | Found
140 | RMTK90BD | https://www.se.com/ww/en/product/RMTK90BD/ | Found
141 | RMCN22BD | https://www.se.com/ww/en/product/RMCN22BD/ | Found
142 | RMCL55BD | https://www.se.com/ww/en/product/RMCL55BD/ | Found
143 | RMCV60BD | https://www.se.com/ww/en/product/RMCV60BD/ | Found
144 | RMCA61BD | https://www.se.com/ww/en/product/RMCA61BD/ | Found
145 | XVR3M04S | https://www.se.com/ww/en/product/XVR3M04S/ | Found
146 | XVR3M05S | https://www.se.com/ww/en/product/XVR3M05S/ | Found
147 | XVR3M06S | https://www.se.com/ww/en/product/XVR3M06S/ | Found
148 | XVR3E03 | https://www.se.com/ww/en/product/XVR3E03/ | Found
149 | XVR3E04 | https://www.se.com/ww/en/product/XVR3E04/ | Found
150 | XVR3E05 | https://www.se.com/ww/en/product/XVR3E05/ | Found
151 | XVR3E06 | https://www.se.com/ww/en/product/XVR3E06/ | Found
152 | XVDLS33 | https://www.se.com/ww/en/product/XVDLS33/ | Found
153 | XVDLS34 | https://www.se.com/ww/en/product/XVDLS34/ | Found
154 | XVDLS35 | https://www.se.com/ww/en/product/XVDLS35/ | Found
155 | XVDLS36 | https://www.se.com/ww/en/product/XVDLS36/ | Found
156 | XVDLS37 | https://www.se.com/ww/en/product/XVDLS37/ | Found
157 | XVDLS38 | https://www.se.com/ww/en/product/XVDLS38/ | Found
158 | DL1BEBS | https://www.se.com/ww/en/product/DL1BEBS/ | Found
159 | DL1BEGS | https://www.se.com/ww/en/product/DL1BEGS/ | Found
160 | DL1BEMS | https://www.se.com/ww/en/product/DL1BEMS/ | Found
161 | XVDLS6B3 | https://www.se.com/ww/en/product/XVDLS6B3/ | Found
162 | XVDLS6B4 | https://www.se.com/ww/en/product/XVDLS6B4/ | Found
163 | XVDLS6B5 | https://www.se.com/ww/en/product/XVDLS6B5/ | Found
164 | XVDLS6B6 | https://www.se.com/ww/en/product/XVDLS6B6/ | Found
165 | XVDLS6B7 | https://www.se.com/ww/en/product/XVDLS6B7/ | Found
166 | XVDLS6B8 | https://www.se.com/ww/en/product/XVDLS6B8/ | Found
167 | XVDLS6G3 | https://www.se.com/ww/en/product/XVDLS6G3/ | Found
168 | XVDLS6G4 | https://www.se.com/ww/en/product/XVDLS6G4/ | Found
169 | XVDLS6G5 | https://www.se.com/ww/en/product/XVDLS6G5/ | Found
170 | XVDLS6G6 | https://www.se.com/ww/en/product/XVDLS6G6/ | Found
171 | XVDLS6G7 | https://www.se.com/ww/en/product/XVDLS6G7/ | Found
172 | XVDLS6G8 | https://www.se.com/ww/en/product/XVDLS6G8/ | Found
173 | XVDLS6M3 | https://www.se.com/ww/en/product/XVDLS6M3/ | Found
174 | XVDLS6M4 | https://www.se.com/ww/en/product/XVDLS6M4/ | Found
175 | XVDLS6M5 | https://www.se.com/ww/en/product/XVDLS6M5/ | Found
176 | XVDLS6M6 | https://www.se.com/ww/en/product/XVDLS6M6/ | Found
177 | XVDLS6M7 | https://www.se.com/ww/en/product/XVDLS6M7/ | Found
178 | XVDLS6M8 | https://www.se.com/ww/en/product/XVDLS6M8/ | Found
179 | XVSV7BBN | https://www.se.com/ww/en/product/XVSV7BBN/ | Found
180 | XVSV7BWN | https://www.se.com/ww/en/product/XVSV7BWN/ | Found
181 | XVSV7BBP | https://www.se.com/ww/en/product/XVSV7BBP/ | Found
182 | XVSV9BBN | https://www.se.com/ww/en/product/XVSV9BBN/ | Found
183 | XVSV9BWN | https://www.se.com/ww/en/product/XVSV9BWN/ | Found
184 | XVSV9BBP | https://www.se.com/ww/en/product/XVSV9BBP/ | Found
185 | XVSV9MBN | https://www.se.com/ww/en/product/XVSV9MBN/ | Found
186 | XVSV9MWN | https://www.se.com/ww/en/product/XVSV9MWN/ | Found
187 | XVSA7BBN | https://www.se.com/ww/en/product/XVSA7BBN/ | Not Found
188 | XVSA7BBP | https://www.se.com/ww/en/product/XVSA7BBP/ | Not Found
189 | XVSA7BWN | https://www.se.com/ww/en/product/XVSA7BWN/ | Not Found
190 | XVSA9BBN | https://www.se.com/ww/en/product/XVSA9BBN/ | Not Found
191 | XVSA9BBP | https://www.se.com/ww/en/product/XVSA9BBP/ | Not Found
192 | XVSA9BWN | https://www.se.com/ww/en/product/XVSA9BWN/ | Not Found
193 | XVSA9MBN | https://www.se.com/ww/en/product/XVSA9MBN/ | Not Found
194 | XVSA9MWN | https://www.se.com/ww/en/product/XVSA9MWN/ | Not Found
195 | XVS10BMW | https://www.se.com/ww/en/product/XVS10BMW/ | Found
196 | XVS10GMW | https://www.se.com/ww/en/product/XVS10GMW/ | Found
197 | XVS10MMW | https://www.se.com/ww/en/product/XVS10MMW/ | Found
198 | XVS14BMW | https://www.se.com/ww/en/product/XVS14BMW/ | Found
199 | XVS14GMW | https://www.se.com/ww/en/product/XVS14GMW/ | Found
200 | XVS14MMW | https://www.se.com/ww/en/product/XVS14MMW/ | Found
201 | XVS72BMBP | https://www.se.com/ww/en/product/XVS72BMBP/ | Found
202 | XVS72BMWP | https://www.se.com/ww/en/product/XVS72BMWP/ | Found
203 | XVS72BMBN | https://www.se.com/ww/en/product/XVS72BMBN/ | Found
204 | XVS72BMWN | https://www.se.com/ww/en/product/XVS72BMWN/ | Found
205 | XVS96BMBP | https://www.se.com/ww/en/product/XVS96BMBP/ | Found
206 | XVS96BMWP | https://www.se.com/ww/en/product/XVS96BMWP/ | Found
207 | XVS96BMBN | https://www.se.com/ww/en/product/XVS96BMBN/ | Found
208 | XVS96BMWN | https://www.se.com/ww/en/product/XVS96BMWN/ | Found
209 | DL1EDBS | https://www.se.com/ww/en/product/DL1EDBS/ | Found
210 | DL1EDGS | https://www.se.com/ww/en/product/DL1EDGS/ | Found
211 | DL1EDMS | https://www.se.com/ww/en/product/DL1EDMS/ | Found
212 | DL2EDB1SB | https://www.se.com/ww/en/product/DL2EDB1SB/ | Found
213 | DL2EDB3SB | https://www.se.com/ww/en/product/DL2EDB3SB/ | Found
214 | DL2EDB4SB | https://www.se.com/ww/en/product/DL2EDB4SB/ | Found
215 | DL2EDB6SB | https://www.se.com/ww/en/product/DL2EDB6SB/ | Found
216 | DL2EDB8SB | https://www.se.com/ww/en/product/DL2EDB8SB/ | Found
217 | DL2EDG1SB | https://www.se.com/ww/en/product/DL2EDG1SB/ | Found
218 | DL2EDG3SB | https://www.se.com/ww/en/product/DL2EDG3SB/ | Found
219 | DL2EDG4SB | https://www.se.com/ww/en/product/DL2EDG4SB/ | Found
220 | DL2EDG6SB | https://www.se.com/ww/en/product/DL2EDG6SB/ | Found
221 | DL2EDG8SB | https://www.se.com/ww/en/product/DL2EDG8SB/ | Found
222 | DL2EDM1SB | https://www.se.com/ww/en/product/DL2EDM1SB/ | Found
223 | DL2EDM3SB | https://www.se.com/ww/en/product/DL2EDM3SB/ | Found
224 | DL2EDM4SB | https://www.se.com/ww/en/product/DL2EDM4SB/ | Found
225 | DL2EDM6SB | https://www.se.com/ww/en/product/DL2EDM6SB/ | Found
226 | DL2EDM8SB | https://www.se.com/ww/en/product/DL2EDM8SB/ | Found
227 | DL2EKB1SB | https://www.se.com/ww/en/product/DL2EKB1SB/ | Found
228 | DL2EKB3SB | https://www.se.com/ww/en/product/DL2EKB3SB/ | Found
229 | DL2EKB4SB | https://www.se.com/ww/en/product/DL2EKB4SB/ | Found
230 | DL2EKB6SB | https://www.se.com/ww/en/product/DL2EKB6SB/ | Found
231 | DL2EKB8SB | https://www.se.com/ww/en/product/DL2EKB8SB/ | Found
232 | DL2EKG1SB | https://www.se.com/ww/en/product/DL2EKG1SB/ | Found
233 | DL2EKG3SB | https://www.se.com/ww/en/product/DL2EKG3SB/ | Found
234 | DL2EKG4SB | https://www.se.com/ww/en/product/DL2EKG4SB/ | Found
235 | DL2EKG6SB | https://www.se.com/ww/en/product/DL2EKG6SB/ | Found
236 | DL2EKG8SB | https://www.se.com/ww/en/product/DL2EKG8SB/ | Found
237 | DL2EKM1SB | https://www.se.com/ww/en/product/DL2EKM1SB/ | Found
238 | DL2EKM3SB | https://www.se.com/ww/en/product/DL2EKM3SB/ | Found
239 | DL2EKM4SB | https://www.se.com/ww/en/product/DL2EKM4SB/ | Found
240 | DL2EKM6SB | https://www.se.com/ww/en/product/DL2EKM6SB/ | Found
241 | DL2EKM8SB | https://www.se.com/ww/en/product/DL2EKM8SB/ | Found
242 | DL6BB | https://www.se.com/ww/en/product/DL6BB/ | Found
243 | DL6BG | https://www.se.com/ww/en/product/DL6BG/ | Found
244 | DL6BM | https://www.se.com/ww/en/product/DL6BM/ | Found
245 | XVMC21 | https://www.se.com/ww/en/product/XVMC21/ | Found
246 | XVMC29B | https://www.se.com/ww/en/product/XVMC29B/ | Found
247 | XVMC29G | https://www.se.com/ww/en/product/XVMC29G/ | Found
248 | XVMC29M | https://www.se.com/ww/en/product/XVMC29M/ | Found
249 | DL1BEJ | https://www.se.com/ww/en/product/DL1BEJ/ | Found
250 | DL1BEB | https://www.se.com/ww/en/product/DL1BEB/ | Found
251 | DL1BEE | https://www.se.com/ww/en/product/DL1BEE/ | Found
252 | DL1BEG | https://www.se.com/ww/en/product/DL1BEG/ | Found
253 | DL1BEM | https://www.se.com/ww/en/product/DL1BEM/ | Found
254 | DL1BDB1 | https://www.se.com/ww/en/product/DL1BDB1/ | Found
255 | DL1BDB3 | https://www.se.com/ww/en/product/DL1BDB3/ | Found
256 | DL1BDB4 | https://www.se.com/ww/en/product/DL1BDB4/ | Found
257 | DL1BDB5 | https://www.se.com/ww/en/product/DL1BDB5/ | Found
258 | DL1BDB6 | https://www.se.com/ww/en/product/DL1BDB6/ | Found
259 | DL1BDB8 | https://www.se.com/ww/en/product/DL1BDB8/ | Found
260 | DL1BDG1 | https://www.se.com/ww/en/product/DL1BDG1/ | Found
261 | DL1BDG3 | https://www.se.com/ww/en/product/DL1BDG3/ | Found
262 | DL1BDG4 | https://www.se.com/ww/en/product/DL1BDG4/ | Found
263 | DL1BDG5 | https://www.se.com/ww/en/product/DL1BDG5/ | Found
264 | DL1BDG6 | https://www.se.com/ww/en/product/DL1BDG6/ | Found
265 | DL1BDG8 | https://www.se.com/ww/en/product/DL1BDG8/ | Found
266 | DL1BDM1 | https://www.se.com/ww/en/product/DL1BDM1/ | Found
267 | DL1BDM3 | https://www.se.com/ww/en/product/DL1BDM3/ | Found
268 | DL1BDM4 | https://www.se.com/ww/en/product/DL1BDM4/ | Found
269 | DL1BDM5 | https://www.se.com/ww/en/product/DL1BDM5/ | Found
270 | DL1BDM6 | https://www.se.com/ww/en/product/DL1BDM6/ | Found
271 | DL1BDM8 | https://www.se.com/ww/en/product/DL1BDM8/ | Found
272 | DL1BKB1 | https://www.se.com/ww/en/product/DL1BKB1/ | Found
273 | DL1BKB3 | https://www.se.com/ww/en/product/DL1BKB3/ | Found
274 | DL1BKB4 | https://www.se.com/ww/en/product/DL1BKB4/ | Found
275 | DL1BKB5 | https://www.se.com/ww/en/product/DL1BKB5/ | Found
276 | DL1BKB6 | https://www.se.com/ww/en/product/DL1BKB6/ | Found
277 | DL1BKB8 | https://www.se.com/ww/en/product/DL1BKB8/ | Found
278 | DL1BKG1 | https://www.se.com/ww/en/product/DL1BKG1/ | Found
279 | DL1BKG3 | https://www.se.com/ww/en/product/DL1BKG3/ | Found
280 | DL1BKG4 | https://www.se.com/ww/en/product/DL1BKG4/ | Found
281 | DL1BKG5 | https://www.se.com/ww/en/product/DL1BKG5/ | Found
282 | DL1BKG6 | https://www.se.com/ww/en/product/DL1BKG6/ | Found
283 | DL1BKG8 | https://www.se.com/ww/en/product/DL1BKG8/ | Found
284 | DL1BKM1 | https://www.se.com/ww/en/product/DL1BKM1/ | Found
285 | DL1BKM3 | https://www.se.com/ww/en/product/DL1BKM3/ | Found
286 | DL1BKM4 | https://www.se.com/ww/en/product/DL1BKM4/ | Found
287 | DL1BKM5 | https://www.se.com/ww/en/product/DL1BKM5/ | Found
288 | DL1BKM6 | https://www.se.com/ww/en/product/DL1BKM6/ | Found
289 | DL1BKM8 | https://www.se.com/ww/en/product/DL1BKM8/ | Found
290 | XVBC9B | https://www.se.com/ww/en/product/XVBC9B/ | Found
291 | XVBC9M | https://www.se.com/ww/en/product/XVBC9M/ | Found
292 | XVBC07 | https://www.se.com/ww/en/product/XVBC07/ | Found
293 | XVBC21 | https://www.se.com/ww/en/product/XVBC21/ | Found
294 | XVBC21A | https://www.se.com/ww/en/product/XVBC21A/ | Found
295 | XVBC21B | https://www.se.com/ww/en/product/XVBC21B/ | Found
296 | XVDLS33 | https://www.se.com/ww/en/product/XVDLS33/ | Found
297 | XVDLS34 | https://www.se.com/ww/en/product/XVDLS34/ | Found
298 | XVDLS35 | https://www.se.com/ww/en/product/XVDLS35/ | Found
299 | XVDLS36 | https://www.se.com/ww/en/product/XVDLS36/ | Found
300 | XVDLS37 | https://www.se.com/ww/en/product/XVDLS37/ | Found
301 | XVDLS38 | https://www.se.com/ww/en/product/XVDLS38/ | Found
302 | XVDLS6B3 | https://www.se.com/ww/en/product/XVDLS6B3/ | Found
303 | XVDLS6B4 | https://www.se.com/ww/en/product/XVDLS6B4/ | Found
304 | XVDLS6B5 | https://www.se.com/ww/en/product/XVDLS6B5/ | Found
305 | XVDLS6B6 | https://www.se.com/ww/en/product/XVDLS6B6/ | Found
306 | XVDLS6B7 | https://www.se.com/ww/en/product/XVDLS6B7/ | Found
307 | XVDLS6B8 | https://www.se.com/ww/en/product/XVDLS6B8/ | Found
308 | XVDLS6G3 | https://www.se.com/ww/en/product/XVDLS6G3/ | Found
309 | XVDLS6G4 | https://www.se.com/ww/en/product/XVDLS6G4/ | Found
310 | XVDLS6G5 | https://www.se.com/ww/en/product/XVDLS6G5/ | Found
311 | XVDLS6G6 | https://www.se.com/ww/en/product/XVDLS6G6/ | Found
312 | XVDLS6G7 | https://www.se.com/ww/en/product/XVDLS6G7/ | Found
313 | XVDLS6G8 | https://www.se.com/ww/en/product/XVDLS6G8/ | Found
314 | XVDLS6M3 | https://www.se.com/ww/en/product/XVDLS6M3/ | Found
315 | XVDLS6M4 | https://www.se.com/ww/en/product/XVDLS6M4/ | Found
316 | XVDLS6M5 | https://www.se.com/ww/en/product/XVDLS6M5/ | Found
317 | XVDLS6M6 | https://www.se.com/ww/en/product/XVDLS6M6/ | Found
318 | XVDLS6M7 | https://www.se.com/ww/en/product/XVDLS6M7/ | Found
319 | XVDLS6M8 | https://www.se.com/ww/en/product/XVDLS6M8/ | Found
320 | XVD | https://www.se.com/ww/en/product/XVD/ | Not Found
321 | XVDBR6 | https://www.se.com/ww/en/product/XVDBR6/ | Found
322 | XVDBA6 | https://www.se.com/ww/en/product/XVDBA6/ | Found
323 | XVDMR6 | https://www.se.com/ww/en/product/XVDMR6/ | Found
324 | XVDMA6 | https://www.se.com/ww/en/product/XVDMA6/ | Found
325 | XVDB2GR | https://www.se.com/ww/en/product/XVDB2GR/ | Found
326 | XVDB2AR | https://www.se.com/ww/en/product/XVDB2AR/ | Found
327 | XVDB2GR6 | https://www.se.com/ww/en/product/XVDB2GR6/ | Found
328 | XVDBSA6 | https://www.se.com/ww/en/product/XVDBSA6/ | Found
329 | XVDB1GAR | https://www.se.com/ww/en/product/XVDB1GAR/ | Found
330 | XVDM1GAR | https://www.se.com/ww/en/product/XVDM1GAR/ | Found
331 | XVDB2GAR | https://www.se.com/ww/en/product/XVDB2GAR/ | Found
332 | XVDM2GAR | https://www.se.com/ww/en/product/XVDM2GAR/ | Found
333 | XVDB2GAR6 | https://www.se.com/ww/en/product/XVDB2GAR6/ | Found
334 | XVDB2SGR | https://www.se.com/ww/en/product/XVDB2SGR/ | Found
335 | XVDB2SAR | https://www.se.com/ww/en/product/XVDB2SAR/ | Found
336 | XVDM2SGR | https://www.se.com/ww/en/product/XVDM2SGR/ | Found
337 | XVDB2CGAR | https://www.se.com/ww/en/product/XVDB2CGAR/ | Found
338 | XVDB1SGAR | https://www.se.com/ww/en/product/XVDB1SGAR/ | Found
339 | XVDB2SGAR | https://www.se.com/ww/en/product/XVDB2SGAR/ | Found
340 | XVDM2SGAR | https://www.se.com/ww/en/product/XVDM2SGAR/ | Found
341 | XVDL33 | https://www.se.com/ww/en/product/XVDL33/ | Found
342 | XVDL34 | https://www.se.com/ww/en/product/XVDL34/ | Found
343 | XVDL35 | https://www.se.com/ww/en/product/XVDL35/ | Found
344 | XVDL36 | https://www.se.com/ww/en/product/XVDL36/ | Not Found
345 | XVDL37 | https://www.se.com/ww/en/product/XVDL37/ | Not Found
346 | XVDL38 | https://www.se.com/ww/en/product/XVDL38/ | Found
347 | XVDL4B3 | https://www.se.com/ww/en/product/XVDL4B3/ | Found
348 | XVDL4B4 | https://www.se.com/ww/en/product/XVDL4B4/ | Found
349 | XVDL4B5 | https://www.se.com/ww/en/product/XVDL4B5/ | Found
350 | XVDL4B6 | https://www.se.com/ww/en/product/XVDL4B6/ | Found
351 | XVDL4B7 | https://www.se.com/ww/en/product/XVDL4B7/ | Found
352 | XVDL4B8 | https://www.se.com/ww/en/product/XVDL4B8/ | Found
353 | XVDL4M3 | https://www.se.com/ww/en/product/XVDL4M3/ | Found
354 | XVDL4M4 | https://www.se.com/ww/en/product/XVDL4M4/ | Found
355 | XVDL4M5 | https://www.se.com/ww/en/product/XVDL4M5/ | Found
356 | XVDL4M6 | https://www.se.com/ww/en/product/XVDL4M6/ | Found
357 | XVDL4M7 | https://www.se.com/ww/en/product/XVDL4M7/ | Found
358 | XVDL4M8 | https://www.se.com/ww/en/product/XVDL4M8/ | Found
359 | XVDL6B3 | https://www.se.com/ww/en/product/XVDL6B3/ | Found
360 | XVDL6B4 | https://www.se.com/ww/en/product/XVDL6B4/ | Found
361 | XVDL6B5 | https://www.se.com/ww/en/product/XVDL6B5/ | Found
362 | XVDL6B6 | https://www.se.com/ww/en/product/XVDL6B6/ | Found
363 | XVDL6B7 | https://www.se.com/ww/en/product/XVDL6B7/ | Found
364 | XVDL6B8 | https://www.se.com/ww/en/product/XVDL6B8/ | Found
365 | XVDL6M3 | https://www.se.com/ww/en/product/XVDL6M3/ | Found
366 | XVDL6M4 | https://www.se.com/ww/en/product/XVDL6M4/ | Found
367 | XVDL6M5 | https://www.se.com/ww/en/product/XVDL6M5/ | Found
368 | XVDL6M6 | https://www.se.com/ww/en/product/XVDL6M6/ | Found
369 | XVDL6M7 | https://www.se.com/ww/en/product/XVDL6M7/ | Found
370 | XVDL6M8 | https://www.se.com/ww/en/product/XVDL6M8/ | Found
371 | XVM | https://www.se.com/ww/en/product/XVM/ | Not Found
372 | XVMB1RF | https://www.se.com/ww/en/product/XVMB1RF/ | Not Found
373 | XVMB1AF | https://www.se.com/ww/en/product/XVMB1AF/ | Not Found
374 | XVMG1RF | https://www.se.com/ww/en/product/XVMG1RF/ | Not Found
375 | XVMG1AF | https://www.se.com/ww/en/product/XVMG1AF/ | Not Found
376 | XVMM1RF | https://www.se.com/ww/en/product/XVMM1RF/ | Not Found
377 | XVMM1AF | https://www.se.com/ww/en/product/XVMM1AF/ | Not Found
378 | XVMB2RF | https://www.se.com/ww/en/product/XVMB2RF/ | Not Found
379 | XVMB2A5F | https://www.se.com/ww/en/product/XVMB2A5F/ | Not Found
380 | XVMG2RF | https://www.se.com/ww/en/product/XVMG2RF/ | Not Found
381 | XVMG2A5F | https://www.se.com/ww/en/product/XVMG2A5F/ | Not Found
382 | XVMM2RF | https://www.se.com/ww/en/product/XVMM2RF/ | Not Found
383 | XVMM2A5F | https://www.se.com/ww/en/product/XVMM2A5F/ | Not Found
384 | XVMBR6F | https://www.se.com/ww/en/product/XVMBR6F/ | Not Found
385 | XVMBA6F | https://www.se.com/ww/en/product/XVMBA6F/ | Not Found
386 | XVMGR6F | https://www.se.com/ww/en/product/XVMGR6F/ | Not Found
387 | XVMGA6F | https://www.se.com/ww/en/product/XVMGA6F/ | Not Found
388 | XVMMR6F | https://www.se.com/ww/en/product/XVMMR6F/ | Not Found
389 | XVMMA6F | https://www.se.com/ww/en/product/XVMMA6F/ | Not Found
390 | XVMB1RSF | https://www.se.com/ww/en/product/XVMB1RSF/ | Not Found
391 | XVMB1ASF | https://www.se.com/ww/en/product/XVMB1ASF/ | Not Found
392 | XVMG1RSF | https://www.se.com/ww/en/product/XVMG1RSF/ | Not Found
393 | XVMG1ASF | https://www.se.com/ww/en/product/XVMG1ASF/ | Not Found
394 | XVMM1RSF | https://www.se.com/ww/en/product/XVMM1RSF/ | Not Found
395 | XVMM1ASF | https://www.se.com/ww/en/product/XVMM1ASF/ | Not Found
396 | XVMB2RSF | https://www.se.com/ww/en/product/XVMB2RSF/ | Not Found
397 | XVMB2A5SF | https://www.se.com/ww/en/product/XVMB2A5SF/ | Not Found
398 | XVMG2RSF | https://www.se.com/ww/en/product/XVMG2RSF/ | Not Found
399 | XVMG2A5SF | https://www.se.com/ww/en/product/XVMG2A5SF/ | Not Found
400 | XVMM2RSF | https://www.se.com/ww/en/product/XVMM2RSF/ | Not Found
401 | XVMM2A5SF | https://www.se.com/ww/en/product/XVMM2A5SF/ | Not Found
402 | XVMBR6SF | https://www.se.com/ww/en/product/XVMBR6SF/ | Not Found
403 | XVMBA6SF | https://www.se.com/ww/en/product/XVMBA6SF/ | Not Found
404 | XVMGR6SF | https://www.se.com/ww/en/product/XVMGR6SF/ | Not Found
405 | XVMGA6SF | https://www.se.com/ww/en/product/XVMGA6SF/ | Not Found
406 | XVMMR6SF | https://www.se.com/ww/en/product/XVMMR6SF/ | Not Found
407 | XVMMA6SF | https://www.se.com/ww/en/product/XVMMA6SF/ | Not Found
408 | XVMB1RA | https://www.se.com/ww/en/product/XVMB1RA/ | Found
409 | XVMB1RG | https://www.se.com/ww/en/product/XVMB1RG/ | Found
410 | XVMG1RA | https://www.se.com/ww/en/product/XVMG1RA/ | Found
411 | XVMG1RG | https://www.se.com/ww/en/product/XVMG1RG/ | Found
412 | XVMM1RA | https://www.se.com/ww/en/product/XVMM1RA/ | Found
413 | XVMM1RG | https://www.se.com/ww/en/product/XVMM1RG/ | Found
414 | XVMB2RA | https://www.se.com/ww/en/product/XVMB2RA/ | Not Found
415 | XVMB2RG | https://www.se.com/ww/en/product/XVMB2RG/ | Not Found
416 | XVMB2R5G | https://www.se.com/ww/en/product/XVMB2R5G/ | Not Found
417 | XVMB2RA5 | https://www.se.com/ww/en/product/XVMB2RA5/ | Not Found
418 | XVMB2R5A5 | https://www.se.com/ww/en/product/XVMB2R5A5/ | Not Found
419 | XVMG2RA | https://www.se.com/ww/en/product/XVMG2RA/ | Not Found
420 | XVMG2RG | https://www.se.com/ww/en/product/XVMG2RG/ | Not Found
421 | XVMG2R5G | https://www.se.com/ww/en/product/XVMG2R5G/ | Not Found
422 | XVMG2RA5 | https://www.se.com/ww/en/product/XVMG2RA5/ | Not Found
423 | XVMG2R5A5 | https://www.se.com/ww/en/product/XVMG2R5A5/ | Not Found
424 | XVMM2RA | https://www.se.com/ww/en/product/XVMM2RA/ | Not Found
425 | XVMM2RG | https://www.se.com/ww/en/product/XVMM2RG/ | Not Found
426 | XVMM2R5G | https://www.se.com/ww/en/product/XVMM2R5G/ | Not Found
427 | XVMM2RA5 | https://www.se.com/ww/en/product/XVMM2RA5/ | Not Found
428 | XVMM2R5A5 | https://www.se.com/ww/en/product/XVMM2R5A5/ | Not Found
429 | XVMB1RAS | https://www.se.com/ww/en/product/XVMB1RAS/ | Found
430 | XVMB1RGS | https://www.se.com/ww/en/product/XVMB1RGS/ | Found
431 | XVMG1RAS | https://www.se.com/ww/en/product/XVMG1RAS/ | Found
432 | XVMM1RAS | https://www.se.com/ww/en/product/XVMM1RAS/ | Found
433 | XVMM1RGS | https://www.se.com/ww/en/product/XVMM1RGS/ | Found
434 | XVMB2RAS | https://www.se.com/ww/en/product/XVMB2RAS/ | Not Found
435 | XVMB2RGS | https://www.se.com/ww/en/product/XVMB2RGS/ | Not Found
436 | XVMB2R5GS | https://www.se.com/ww/en/product/XVMB2R5GS/ | Not Found
437 | XVMB2RA5S | https://www.se.com/ww/en/product/XVMB2RA5S/ | Not Found
438 | XVMB2R5A5S | https://www.se.com/ww/en/product/XVMB2R5A5S/ | Not Found
439 | XVMG2RAS | https://www.se.com/ww/en/product/XVMG2RAS/ | Not Found
440 | XVMG2RGS | https://www.se.com/ww/en/product/XVMG2RGS/ | Not Found
441 | XVMG2R5GS | https://www.se.com/ww/en/product/XVMG2R5GS/ | Not Found
442 | XVMG2RA5S | https://www.se.com/ww/en/product/XVMG2RA5S/ | Not Found
443 | XVMG2R5A5S | https://www.se.com/ww/en/product/XVMG2R5A5S/ | Not Found
444 | XVMM2RAS | https://www.se.com/ww/en/product/XVMM2RAS/ | Not Found
445 | XVMM2RGS | https://www.se.com/ww/en/product/XVMM2RGS/ | Not Found
446 | XVMM2R5GS | https://www.se.com/ww/en/product/XVMM2R5GS/ | Not Found
447 | XVMM2RA5S | https://www.se.com/ww/en/product/XVMM2RA5S/ | Not Found
448 | XVMM2R5A5S | https://www.se.com/ww/en/product/XVMM2R5A5S/ | Not Found
449 | XVMB1RAG | https://www.se.com/ww/en/product/XVMB1RAG/ | Found
450 | XVMB1R6AG | https://www.se.com/ww/en/product/XVMB1R6AG/ | Found
451 | XVMG1RAG | https://www.se.com/ww/en/product/XVMG1RAG/ | Found
452 | XVMG1R6AG | https://www.se.com/ww/en/product/XVMG1R6AG/ | Found
453 | XVMM1RAG | https://www.se.com/ww/en/product/XVMM1RAG/ | Found
454 | XVMM1R6AG | https://www.se.com/ww/en/product/XVMM1R6AG/ | Found
455 | XVMB2RAG | https://www.se.com/ww/en/product/XVMB2RAG/ | Not Found
456 | XVMB2R6AG | https://www.se.com/ww/en/product/XVMB2R6AG/ | Not Found
457 | XVMB2RA5G | https://www.se.com/ww/en/product/XVMB2RA5G/ | Not Found
458 | XVMB2R5A5G | https://www.se.com/ww/en/product/XVMB2R5A5G/ | Not Found
459 | XVMB2R6A5G | https://www.se.com/ww/en/product/XVMB2R6A5G/ | Not Found
460 | XVMG2RAG | https://www.se.com/ww/en/product/XVMG2RAG/ | Not Found
461 | XVMG2R6AG | https://www.se.com/ww/en/product/XVMG2R6AG/ | Not Found
462 | XVMG2RA5G | https://www.se.com/ww/en/product/XVMG2RA5G/ | Not Found
463 | XVMG2R5A5G | https://www.se.com/ww/en/product/XVMG2R5A5G/ | Not Found
464 | XVMG2R6A5G | https://www.se.com/ww/en/product/XVMG2R6A5G/ | Not Found
465 | XVMM2RAG | https://www.se.com/ww/en/product/XVMM2RAG/ | Not Found
466 | XVMM2R6AG | https://www.se.com/ww/en/product/XVMM2R6AG/ | Not Found
467 | XVMM2RA5G | https://www.se.com/ww/en/product/XVMM2RA5G/ | Not Found
468 | XVMM2R5A5G | https://www.se.com/ww/en/product/XVMM2R5A5G/ | Not Found
469 | XVMM2R6A5G | https://www.se.com/ww/en/product/XVMM2R6A5G/ | Not Found
470 | XVMB1RAGS | https://www.se.com/ww/en/product/XVMB1RAGS/ | Found
471 | XVMB1R6AGS | https://www.se.com/ww/en/product/XVMB1R6AGS/ | Found
472 | XVMG1RAGS | https://www.se.com/ww/en/product/XVMG1RAGS/ | Found
473 | XVMG1R6AGS | https://www.se.com/ww/en/product/XVMG1R6AGS/ | Found
474 | XVMM1RAGS | https://www.se.com/ww/en/product/XVMM1RAGS/ | Found
475 | XVMB2RAGS | https://www.se.com/ww/en/product/XVMB2RAGS/ | Not Found
476 | XVMB2R6AGS | https://www.se.com/ww/en/product/XVMB2R6AGS/ | Not Found
477 | XVMB2RA5GS | https://www.se.com/ww/en/product/XVMB2RA5GS/ | Not Found
478 | XVMB2R5A5GS | https://www.se.com/ww/en/product/XVMB2R5A5GS/ | Not Found
479 | XVMB2R6A5GS | https://www.se.com/ww/en/product/XVMB2R6A5GS/ | Not Found
480 | XVMG2RAGS | https://www.se.com/ww/en/product/XVMG2RAGS/ | Not Found
481 | XVMG2R6AGS | https://www.se.com/ww/en/product/XVMG2R6AGS/ | Not Found
482 | XVMG2RA5GS | https://www.se.com/ww/en/product/XVMG2RA5GS/ | Not Found
483 | XVMG2R5A5GS | https://www.se.com/ww/en/product/XVMG2R5A5GS/ | Not Found
484 | XVMG2R6A5GS | https://www.se.com/ww/en/product/XVMG2R6A5GS/ | Not Found
485 | XVMM2RAGS | https://www.se.com/ww/en/product/XVMM2RAGS/ | Not Found
486 | XVMM2R6AGS | https://www.se.com/ww/en/product/XVMM2R6AGS/ | Not Found
487 | XVMM2RA5GS | https://www.se.com/ww/en/product/XVMM2RA5GS/ | Not Found
488 | XVMM2R6A5GS | https://www.se.com/ww/en/product/XVMM2R6A5GS/ | Not Found
489 | XVMB1RAGB | https://www.se.com/ww/en/product/XVMB1RAGB/ | Found
490 | XVMG1RAGB | https://www.se.com/ww/en/product/XVMG1RAGB/ | Found
491 | XVMM1RAGB | https://www.se.com/ww/en/product/XVMM1RAGB/ | Found
492 | XVMB2RAGB | https://www.se.com/ww/en/product/XVMB2RAGB/ | Not Found
493 | XVMG2RAGB | https://www.se.com/ww/en/product/XVMG2RAGB/ | Not Found
494 | XVMM2RAGB | https://www.se.com/ww/en/product/XVMM2RAGB/ | Not Found
495 | XVMB1RAGBS | https://www.se.com/ww/en/product/XVMB1RAGBS/ | Found
496 | XVMG1RAGBS | https://www.se.com/ww/en/product/XVMG1RAGBS/ | Found
497 | XVMM1RAGBS | https://www.se.com/ww/en/product/XVMM1RAGBS/ | Found
498 | XVMB2RAGBS | https://www.se.com/ww/en/product/XVMB2RAGBS/ | Not Found
499 | XVMG2RAGBS | https://www.se.com/ww/en/product/XVMG2RAGBS/ | Not Found
500 | XVMM2RAGBS | https://www.se.com/ww/en/product/XVMM2RAGBS/ | Not Found
501 | XVE | https://www.se.com/ww/en/product/XVE/ | Not Found
502 | XVEL33 | https://www.se.com/ww/en/product/XVEL33/ | Found
503 | XVEL34 | https://www.se.com/ww/en/product/XVEL34/ | Found
504 | XVEL35 | https://www.se.com/ww/en/product/XVEL35/ | Found
505 | XVEL36 | https://www.se.com/ww/en/product/XVEL36/ | Found
506 | XVEL37 | https://www.se.com/ww/en/product/XVEL37/ | Found
507 | XVEL2B3 | https://www.se.com/ww/en/product/XVEL2B3/ | Found
508 | XVEL2B4 | https://www.se.com/ww/en/product/XVEL2B4/ | Found
509 | XVEL2B5 | https://www.se.com/ww/en/product/XVEL2B5/ | Found
510 | XVEL2B6 | https://www.se.com/ww/en/product/XVEL2B6/ | Found
511 | XVEL2B7 | https://www.se.com/ww/en/product/XVEL2B7/ | Found
512 | XVEL2G3 | https://www.se.com/ww/en/product/XVEL2G3/ | Found
513 | XVEL2G4 | https://www.se.com/ww/en/product/XVEL2G4/ | Found
514 | XVEL2G5 | https://www.se.com/ww/en/product/XVEL2G5/ | Found
515 | XVEL2G6 | https://www.se.com/ww/en/product/XVEL2G6/ | Found
516 | XVEL2G7 | https://www.se.com/ww/en/product/XVEL2G7/ | Found
517 | XVEL2M3 | https://www.se.com/ww/en/product/XVEL2M3/ | Found
518 | XVEL2M4 | https://www.se.com/ww/en/product/XVEL2M4/ | Found
519 | XVEL2M5 | https://www.se.com/ww/en/product/XVEL2M5/ | Found
520 | XVEL2M6 | https://www.se.com/ww/en/product/XVEL2M6/ | Found
521 | XVEL2M7 | https://www.se.com/ww/en/product/XVEL2M7/ | Found
522 | XVEL6B3 | https://www.se.com/ww/en/product/XVEL6B3/ | Found
523 | XVEL6B4 | https://www.se.com/ww/en/product/XVEL6B4/ | Found
524 | XVEL6B5 | https://www.se.com/ww/en/product/XVEL6B5/ | Found
525 | XVEL6B6 | https://www.se.com/ww/en/product/XVEL6B6/ | Found
526 | XVEL6B7 | https://www.se.com/ww/en/product/XVEL6B7/ | Found
527 | XVEL6G3 | https://www.se.com/ww/en/product/XVEL6G3/ | Found
528 | XVEL6G4 | https://www.se.com/ww/en/product/XVEL6G4/ | Found
529 | XVEL6G5 | https://www.se.com/ww/en/product/XVEL6G5/ | Found
530 | XVEL6G6 | https://www.se.com/ww/en/product/XVEL6G6/ | Found
531 | XVEL6G7 | https://www.se.com/ww/en/product/XVEL6G7/ | Found
532 | XVEL6M3 | https://www.se.com/ww/en/product/XVEL6M3/ | Found
533 | XVEL6M4 | https://www.se.com/ww/en/product/XVEL6M4/ | Found
534 | XVEL6M5 | https://www.se.com/ww/en/product/XVEL6M5/ | Found
535 | XVEL6M6 | https://www.se.com/ww/en/product/XVEL6M6/ | Found
536 | XVEL6M7 | https://www.se.com/ww/en/product/XVEL6M7/ | Found
537 | XVBL | https://www.se.com/ww/en/product/XVBL/ | Not Found
538 | XVBL33 | https://www.se.com/ww/en/product/XVBL33/ | Found
539 | XVBL34 | https://www.se.com/ww/en/product/XVBL34/ | Found
540 | XVBL35 | https://www.se.com/ww/en/product/XVBL35/ | Found
541 | XVBL36 | https://www.se.com/ww/en/product/XVBL36/ | Found
542 | XVBL37 | https://www.se.com/ww/en/product/XVBL37/ | Found
543 | XVBL38 | https://www.se.com/ww/en/product/XVBL38/ | Found
544 | XVBL4B3 | https://www.se.com/ww/en/product/XVBL4B3/ | Found
545 | XVBL4B4 | https://www.se.com/ww/en/product/XVBL4B4/ | Found
546 | XVBL4B5 | https://www.se.com/ww/en/product/XVBL4B5/ | Found
547 | XVBL4B6 | https://www.se.com/ww/en/product/XVBL4B6/ | Found
548 | XVBL4B7 | https://www.se.com/ww/en/product/XVBL4B7/ | Found
549 | XVBL4B8 | https://www.se.com/ww/en/product/XVBL4B8/ | Found
550 | XVBL4M3 | https://www.se.com/ww/en/product/XVBL4M3/ | Found
551 | XVBL4M4 | https://www.se.com/ww/en/product/XVBL4M4/ | Found
552 | XVBL4M5 | https://www.se.com/ww/en/product/XVBL4M5/ | Found
553 | XVBL4M6 | https://www.se.com/ww/en/product/XVBL4M6/ | Found
554 | XVBL4M7 | https://www.se.com/ww/en/product/XVBL4M7/ | Found
555 | XVBL4M8 | https://www.se.com/ww/en/product/XVBL4M8/ | Found
556 | XVBL0B3 | https://www.se.com/ww/en/product/XVBL0B3/ | Found
557 | XVBL0B4 | https://www.se.com/ww/en/product/XVBL0B4/ | Found
558 | XVBL0B5 | https://www.se.com/ww/en/product/XVBL0B5/ | Found
559 | XVBL0B6 | https://www.se.com/ww/en/product/XVBL0B6/ | Found
560 | XVBL0B7 | https://www.se.com/ww/en/product/XVBL0B7/ | Found
561 | XVBL0B8 | https://www.se.com/ww/en/product/XVBL0B8/ | Found
562 | XVBL0G3 | https://www.se.com/ww/en/product/XVBL0G3/ | Found
563 | XVBL0G4 | https://www.se.com/ww/en/product/XVBL0G4/ | Found
564 | XVBL0G5 | https://www.se.com/ww/en/product/XVBL0G5/ | Found
565 | XVBL0G6 | https://www.se.com/ww/en/product/XVBL0G6/ | Found
566 | XVBL0G7 | https://www.se.com/ww/en/product/XVBL0G7/ | Found
567 | XVBL0G8 | https://www.se.com/ww/en/product/XVBL0G8/ | Found
568 | XVBL0M3 | https://www.se.com/ww/en/product/XVBL0M3/ | Found
569 | XVBL0M4 | https://www.se.com/ww/en/product/XVBL0M4/ | Found
570 | XVBL0M5 | https://www.se.com/ww/en/product/XVBL0M5/ | Found
571 | XVBL0M6 | https://www.se.com/ww/en/product/XVBL0M6/ | Found
572 | XVBL0M7 | https://www.se.com/ww/en/product/XVBL0M7/ | Found
573 | XVBL0M8 | https://www.se.com/ww/en/product/XVBL0M8/ | Found
574 | XVBL1B3 | https://www.se.com/ww/en/product/XVBL1B3/ | Found
575 | XVBL1B4 | https://www.se.com/ww/en/product/XVBL1B4/ | Found
576 | XVBL1B5 | https://www.se.com/ww/en/product/XVBL1B5/ | Found
577 | XVBL1B6 | https://www.se.com/ww/en/product/XVBL1B6/ | Found
578 | XVBL1B7 | https://www.se.com/ww/en/product/XVBL1B7/ | Found
579 | XVBL1B8 | https://www.se.com/ww/en/product/XVBL1B8/ | Found
580 | XVBL1G3 | https://www.se.com/ww/en/product/XVBL1G3/ | Found
581 | XVBL1G4 | https://www.se.com/ww/en/product/XVBL1G4/ | Found
582 | XVBL1G5 | https://www.se.com/ww/en/product/XVBL1G5/ | Found
583 | XVBL1G6 | https://www.se.com/ww/en/product/XVBL1G6/ | Found
584 | XVBL1G7 | https://www.se.com/ww/en/product/XVBL1G7/ | Found
585 | XVBL1G8 | https://www.se.com/ww/en/product/XVBL1G8/ | Found
586 | XVBL1M3 | https://www.se.com/ww/en/product/XVBL1M3/ | Found
587 | XVBL1M4 | https://www.se.com/ww/en/product/XVBL1M4/ | Found
588 | XVBL1M5 | https://www.se.com/ww/en/product/XVBL1M5/ | Found
589 | XVBL1M6 | https://www.se.com/ww/en/product/XVBL1M6/ | Found
590 | XVBL1M7 | https://www.se.com/ww/en/product/XVBL1M7/ | Found
591 | XVBL1M8 | https://www.se.com/ww/en/product/XVBL1M8/ | Found
592 | XVBL6B3 | https://www.se.com/ww/en/product/XVBL6B3/ | Found
593 | XVBL6B4 | https://www.se.com/ww/en/product/XVBL6B4/ | Found
594 | XVBL6B5 | https://www.se.com/ww/en/product/XVBL6B5/ | Found
595 | XVBL6B6 | https://www.se.com/ww/en/product/XVBL6B6/ | Found
596 | XVBL6B7 | https://www.se.com/ww/en/product/XVBL6B7/ | Found
597 | XVBL6B8 | https://www.se.com/ww/en/product/XVBL6B8/ | Found
598 | XVBL6G3 | https://www.se.com/ww/en/product/XVBL6G3/ | Found
599 | XVBL6G4 | https://www.se.com/ww/en/product/XVBL6G4/ | Found
600 | XVBL6G5 | https://www.se.com/ww/en/product/XVBL6G5/ | Found
601 | XVBL6G6 | https://www.se.com/ww/en/product/XVBL6G6/ | Found
602 | XVBL6G7 | https://www.se.com/ww/en/product/XVBL6G7/ | Found
603 | XVBL6G8 | https://www.se.com/ww/en/product/XVBL6G8/ | Found
604 | XVBL6M3 | https://www.se.com/ww/en/product/XVBL6M3/ | Found
605 | XVBL6M4 | https://www.se.com/ww/en/product/XVBL6M4/ | Found
606 | XVBL6M5 | https://www.se.com/ww/en/product/XVBL6M5/ | Found
607 | XVBL6M6 | https://www.se.com/ww/en/product/XVBL6M6/ | Found
608 | XVBL6M7 | https://www.se.com/ww/en/product/XVBL6M7/ | Found
609 | XVBL6M8 | https://www.se.com/ww/en/product/XVBL6M8/ | Found
610 | XVBL8B3 | https://www.se.com/ww/en/product/XVBL8B3/ | Found
611 | XVBL8B4 | https://www.se.com/ww/en/product/XVBL8B4/ | Found
612 | XVBL8B5 | https://www.se.com/ww/en/product/XVBL8B5/ | Found
613 | XVBL8B6 | https://www.se.com/ww/en/product/XVBL8B6/ | Found
614 | XVBL8B7 | https://www.se.com/ww/en/product/XVBL8B7/ | Found
615 | XVBL8B8 | https://www.se.com/ww/en/product/XVBL8B8/ | Found
616 | XVBL8G3 | https://www.se.com/ww/en/product/XVBL8G3/ | Found
617 | XVBL8G4 | https://www.se.com/ww/en/product/XVBL8G4/ | Found
618 | XVBL8G5 | https://www.se.com/ww/en/product/XVBL8G5/ | Found
619 | XVBL8G6 | https://www.se.com/ww/en/product/XVBL8G6/ | Found
620 | XVBL8G7 | https://www.se.com/ww/en/product/XVBL8G7/ | Found
621 | XVBL8G8 | https://www.se.com/ww/en/product/XVBL8G8/ | Found
622 | XVBL8M3 | https://www.se.com/ww/en/product/XVBL8M3/ | Found
623 | XVBL8M4 | https://www.se.com/ww/en/product/XVBL8M4/ | Found
624 | XVBL8M5 | https://www.se.com/ww/en/product/XVBL8M5/ | Found
625 | XVBL8M6 | https://www.se.com/ww/en/product/XVBL8M6/ | Found
626 | XVBL8M7 | https://www.se.com/ww/en/product/XVBL8M7/ | Found
627 | XVBL8M8 | https://www.se.com/ww/en/product/XVBL8M8/ | Found
628 | XVBC6B3 | https://www.se.com/ww/en/product/XVBC6B3/ | Found
629 | XVBC6B4 | https://www.se.com/ww/en/product/XVBC6B4/ | Found
630 | XVBC6B5 | https://www.se.com/ww/en/product/XVBC6B5/ | Found
631 | XVBC6B6 | https://www.se.com/ww/en/product/XVBC6B6/ | Found
632 | XVBC6B7 | https://www.se.com/ww/en/product/XVBC6B7/ | Found
633 | XVBC6B8 | https://www.se.com/ww/en/product/XVBC6B8/ | Found
634 | XVBC6G3 | https://www.se.com/ww/en/product/XVBC6G3/ | Found
635 | XVBC6G4 | https://www.se.com/ww/en/product/XVBC6G4/ | Found
636 | XVBC6G5 | https://www.se.com/ww/en/product/XVBC6G5/ | Found
637 | XVBC6G6 | https://www.se.com/ww/en/product/XVBC6G6/ | Found
638 | XVBC6G7 | https://www.se.com/ww/en/product/XVBC6G7/ | Found
639 | XVBC6G8 | https://www.se.com/ww/en/product/XVBC6G8/ | Found
640 | XVBC6M3 | https://www.se.com/ww/en/product/XVBC6M3/ | Found
641 | XVBC6M4 | https://www.se.com/ww/en/product/XVBC6M4/ | Found
642 | XVBC6M5 | https://www.se.com/ww/en/product/XVBC6M5/ | Found
643 | XVBC6M6 | https://www.se.com/ww/en/product/XVBC6M6/ | Found
644 | XVBC6M7 | https://www.se.com/ww/en/product/XVBC6M7/ | Found
645 | XVBC6M8 | https://www.se.com/ww/en/product/XVBC6M8/ | Found
646 | XVBC8B3 | https://www.se.com/ww/en/product/XVBC8B3/ | Found
647 | XVBC8B4 | https://www.se.com/ww/en/product/XVBC8B4/ | Found
648 | XVBC8B5 | https://www.se.com/ww/en/product/XVBC8B5/ | Found
649 | XVBC8B6 | https://www.se.com/ww/en/product/XVBC8B6/ | Found
650 | XVBC8B7 | https://www.se.com/ww/en/product/XVBC8B7/ | Found
651 | XVBC8B8 | https://www.se.com/ww/en/product/XVBC8B8/ | Found
652 | XVBC8E5 | https://www.se.com/ww/en/product/XVBC8E5/ | Found
653 | XVBC8G3 | https://www.se.com/ww/en/product/XVBC8G3/ | Found
654 | XVBC8G4 | https://www.se.com/ww/en/product/XVBC8G4/ | Found
655 | XVBC8G5 | https://www.se.com/ww/en/product/XVBC8G5/ | Found
656 | XVBC8G6 | https://www.se.com/ww/en/product/XVBC8G6/ | Found
657 | XVBC8G7 | https://www.se.com/ww/en/product/XVBC8G7/ | Found
658 | XVBC8G8 | https://www.se.com/ww/en/product/XVBC8G8/ | Found
659 | XVBC8M3 | https://www.se.com/ww/en/product/XVBC8M3/ | Found
660 | XVBC8M4 | https://www.se.com/ww/en/product/XVBC8M4/ | Found
661 | XVBC8M5 | https://www.se.com/ww/en/product/XVBC8M5/ | Found
662 | XVBC8M6 | https://www.se.com/ww/en/product/XVBC8M6/ | Found
663 | XVBC8M7 | https://www.se.com/ww/en/product/XVBC8M7/ | Found
664 | XVBC8M8 | https://www.se.com/ww/en/product/XVBC8M8/ | Found
665 | RHR4138J | https://www.se.com/ww/en/product/RHR4138J/ | Found
666 | RHR418J | https://www.se.com/ww/en/product/RHR418J/ | Found
667 | RHT4138J | https://www.se.com/ww/en/product/RHT4138J/ | Found
668 | RHT418J | https://www.se.com/ww/en/product/RHT418J/ | Found
669 | RHR4138F | https://www.se.com/ww/en/product/RHR4138F/ | Found
670 | RHR4138G | https://www.se.com/ww/en/product/RHR4138G/ | Found
671 | RHR4131M | https://www.se.com/ww/en/product/RHR4131M/ | Found
672 | RHR4138B | https://www.se.com/ww/en/product/RHR4138B/ | Found
673 | RHR4138BE | https://www.se.com/ww/en/product/RHR4138BE/ | Found
674 | RHR428F | https://www.se.com/ww/en/product/RHR428F/ | Found
675 | RHR421M | https://www.se.com/ww/en/product/RHR421M/ | Found
676 | RHR428B | https://www.se.com/ww/en/product/RHR428B/ | Found
677 | RHR428E | https://www.se.com/ww/en/product/RHR428E/ | Found
678 | RHR418F | https://www.se.com/ww/en/product/RHR418F/ | Found
679 | RHR418G | https://www.se.com/ww/en/product/RHR418G/ | Found
680 | RHR411M | https://www.se.com/ww/en/product/RHR411M/ | Found
681 | RHR411U | https://www.se.com/ww/en/product/RHR411U/ | Found
682 | RHR418B | https://www.se.com/ww/en/product/RHR418B/ | Found
683 | RHR418BE | https://www.se.com/ww/en/product/RHR418BE/ | Found
684 | RHR418E | https://www.se.com/ww/en/product/RHR418E/ | Found
685 | RHR418P | https://www.se.com/ww/en/product/RHR418P/ | Found
686 | RHR418EN | https://www.se.com/ww/en/product/RHR418EN/ | Found
687 | RHT4138F | https://www.se.com/ww/en/product/RHT4138F/ | Found
688 | RHT4138G | https://www.se.com/ww/en/product/RHT4138G/ | Found
689 | RHT4131M | https://www.se.com/ww/en/product/RHT4131M/ | Found
690 | RHT4138B | https://www.se.com/ww/en/product/RHT4138B/ | Found
691 | RHT4138E | https://www.se.com/ww/en/product/RHT4138E/ | Found
692 | RHT428F | https://www.se.com/ww/en/product/RHT428F/ | Found
693 | RHT428G | https://www.se.com/ww/en/product/RHT428G/ | Found
694 | RHT421M | https://www.se.com/ww/en/product/RHT421M/ | Found
695 | RHT428B | https://www.se.com/ww/en/product/RHT428B/ | Found
696 | RHT418F | https://www.se.com/ww/en/product/RHT418F/ | Found
697 | RHT418G | https://www.se.com/ww/en/product/RHT418G/ | Found
698 | RHT411M | https://www.se.com/ww/en/product/RHT411M/ | Found
699 | RHT411U | https://www.se.com/ww/en/product/RHT411U/ | Found
700 | RHT418B | https://www.se.com/ww/en/product/RHT418B/ | Found
701 | RHT418BE | https://www.se.com/ww/en/product/RHT418BE/ | Found
702 | RHT418E | https://www.se.com/ww/en/product/RHT418E/ | Found
703 | RM4JA01B | https://www.se.com/ww/en/product/RM4JA01B/ | Found
704 | RM4JA01F | https://www.se.com/ww/en/product/RM4JA01F/ | Found
705 | RM4JA01M | https://www.se.com/ww/en/product/RM4JA01M/ | Found
706 | RM4JA31F | https://www.se.com/ww/en/product/RM4JA31F/ | Found
707 | RM4JA31M | https://www.se.com/ww/en/product/RM4JA31M/ | Found
708 | RM4JA31MW | https://www.se.com/ww/en/product/RM4JA31MW/ | Found
709 | RM4JA31Q | https://www.se.com/ww/en/product/RM4JA31Q/ | Found
710 | RM4JA32F | https://www.se.com/ww/en/product/RM4JA32F/ | Found
711 | RM4JA32M | https://www.se.com/ww/en/product/RM4JA32M/ | Found
712 | RM4JA32MW | https://www.se.com/ww/en/product/RM4JA32MW/ | Found
713 | RM4JA32Q | https://www.se.com/ww/en/product/RM4JA32Q/ | Found
714 | RM4UA01B | https://www.se.com/ww/en/product/RM4UA01B/ | Found
715 | RM4UA01F | https://www.se.com/ww/en/product/RM4UA01F/ | Found
716 | RM4UA01M | https://www.se.com/ww/en/product/RM4UA01M/ | Found
717 | RM4UA02B | https://www.se.com/ww/en/product/RM4UA02B/ | Found
718 | RM4UA02F | https://www.se.com/ww/en/product/RM4UA02F/ | Found
719 | RM4UA02M | https://www.se.com/ww/en/product/RM4UA02M/ | Found
720 | RM4UA03B | https://www.se.com/ww/en/product/RM4UA03B/ | Found
721 | RM4UA03F | https://www.se.com/ww/en/product/RM4UA03F/ | Found
722 | RM4UA03M | https://www.se.com/ww/en/product/RM4UA03M/ | Found
723 | RM4UA31F | https://www.se.com/ww/en/product/RM4UA31F/ | Found
724 | RM4UA31M | https://www.se.com/ww/en/product/RM4UA31M/ | Found
725 | RM4UA31MW | https://www.se.com/ww/en/product/RM4UA31MW/ | Found
726 | RM4UA31Q | https://www.se.com/ww/en/product/RM4UA31Q/ | Found
727 | RM4UA32F | https://www.se.com/ww/en/product/RM4UA32F/ | Found
728 | RM4UA32M | https://www.se.com/ww/en/product/RM4UA32M/ | Found
729 | RM4UA32MW | https://www.se.com/ww/en/product/RM4UA32MW/ | Found
730 | RM4UA32Q | https://www.se.com/ww/en/product/RM4UA32Q/ | Found
731 | RM4UA33F | https://www.se.com/ww/en/product/RM4UA33F/ | Found
732 | RM4UA33M | https://www.se.com/ww/en/product/RM4UA33M/ | Found
733 | RM4UA33MW | https://www.se.com/ww/en/product/RM4UA33MW/ | Found
734 | RM4UA33Q | https://www.se.com/ww/en/product/RM4UA33Q/ | Found
735 | RM4UB34 | https://www.se.com/ww/en/product/RM4UB34/ | Found
736 | RM4UB35 | https://www.se.com/ww/en/product/RM4UB35/ | Found
737 | RM4TA02 | https://www.se.com/ww/en/product/RM4TA02/ | Found
738 | RM4TA32 | https://www.se.com/ww/en/product/RM4TA32/ | Found
739 | RM4TA01 | https://www.se.com/ww/en/product/RM4TA01/ | Found
740 | RM4TA31 | https://www.se.com/ww/en/product/RM4TA31/ | Found
741 | RM4TG20 | https://www.se.com/ww/en/product/RM4TG20/ | Found
742 | RM4TR31 | https://www.se.com/ww/en/product/RM4TR31/ | Found
743 | RM4TR33 | https://www.se.com/ww/en/product/RM4TR33/ | Found
744 | RM4TR32 | https://www.se.com/ww/en/product/RM4TR32/ | Found
745 | RM4TR34 | https://www.se.com/ww/en/product/RM4TR34/ | Found
746 | RM4TR35 | https://www.se.com/ww/en/product/RM4TR35/ | Found
747 | RM4TU01 | https://www.se.com/ww/en/product/RM4TU01/ | Found
748 | RM4TU02 | https://www.se.com/ww/en/product/RM4TU02/ | Found
749 | RM4LA32B | https://www.se.com/ww/en/product/RM4LA32B/ | Found
750 | RM4LA32F | https://www.se.com/ww/en/product/RM4LA32F/ | Found
751 | RM4LA32M | https://www.se.com/ww/en/product/RM4LA32M/ | Found
752 | RM4LA32MW | https://www.se.com/ww/en/product/RM4LA32MW/ | Found
753 | RM4LA32Q | https://www.se.com/ww/en/product/RM4LA32Q/ | Found
754 | RM4LG01B | https://www.se.com/ww/en/product/RM4LG01B/ | Found
755 | RM4LG01F | https://www.se.com/ww/en/product/RM4LG01F/ | Found
756 | RM4LG01M | https://www.se.com/ww/en/product/RM4LG01M/ | Found
757 | RM4LG01Q | https://www.se.com/ww/en/product/RM4LG01Q/ | Found
758 | RE7TL11BU | https://www.se.com/ww/en/product/RE7TL11BU/ | Found
759 | RE7TP13BU | https://www.se.com/ww/en/product/RE7TP13BU/ | Found
760 | RE7PE11BU | https://www.se.com/ww/en/product/RE7PE11BU/ | Not Found
761 | RE7PP13BU | https://www.se.com/ww/en/product/RE7PP13BU/ | Not Found
762 | RE7CL11BU | https://www.se.com/ww/en/product/RE7CL11BU/ | Not Found
763 | RE7CP13BU | https://www.se.com/ww/en/product/RE7CP13BU/ | Not Found
764 | RE7RB11MW | https://www.se.com/ww/en/product/RE7RB11MW/ | Found
765 | RE7RB13MW | https://www.se.com/ww/en/product/RE7RB13MW/ | Found
766 | RE7RM11BU | https://www.se.com/ww/en/product/RE7RM11BU/ | Not Found
767 | RE7RA11BU | https://www.se.com/ww/en/product/RE7RA11BU/ | Not Found
768 | RE7RL13BU | https://www.se.com/ww/en/product/RE7RL13BU/ | Not Found
769 | RE7MA11BU | https://www.se.com/ww/en/product/RE7MA11BU/ | Not Found
770 | RE7MA13BU | https://www.se.com/ww/en/product/RE7MA13BU/ | Not Found
771 | RE7PD13BU | https://www.se.com/ww/en/product/RE7PD13BU/ | Not Found
772 | RE7MV11BU | https://www.se.com/ww/en/product/RE7MV11BU/ | Not Found
773 | RE7TM11BU | https://www.se.com/ww/en/product/RE7TM11BU/ | Not Found
774 | RE7MY13BU | https://www.se.com/ww/en/product/RE7MY13BU/ | Not Found
775 | RE7MY13MW | https://www.se.com/ww/en/product/RE7MY13MW/ | Found
776 | RE7ML11BU | https://www.se.com/ww/en/product/RE7ML11BU/ | Found
777 | RE7PM11BU | https://www.se.com/ww/en/product/RE7PM11BU/ | Not Found
778 | RE7CV11BU | https://www.se.com/ww/en/product/RE7CV11BU/ | Found
779 | RE7YA12BU | https://www.se.com/ww/en/product/RE7YA12BU/ | Found
780 | RE7YR12BU | https://www.se.com/ww/en/product/RE7YR12BU/ | Not Found
781 | RE8YG11BU | https://www.se.com/ww/en/product/RE8YG11BU/ | Not Found
782 | RE8YG21BU | https://www.se.com/ww/en/product/RE8YG21BU/ | Not Found
783 | RE8YG31BU | https://www.se.com/ww/en/product/RE8YG31BU/ | Not Found
784 | RE8PT01BU | https://www.se.com/ww/en/product/RE8PT01BU/ | Not Found
785 | RE8RB11BU | https://www.se.com/ww/en/product/RE8RB11BU/ | Not Found
786 | RE8RB31BU | https://www.se.com/ww/en/product/RE8RB31BU/ | Not Found
787 | RE8RB51BU | https://www.se.com/ww/en/product/RE8RB51BU/ | Not Found
788 | RE8YA32B | https://www.se.com/ww/en/product/RE8YA32B/ | Not Found
789 | RE8YA32FU | https://www.se.com/ww/en/product/RE8YA32FU/ | Not Found
790 | RE8YA32Q | https://www.se.com/ww/en/product/RE8YA32Q/ | Not Found
791 | RE8TA11BU | https://www.se.com/ww/en/product/RE8TA11BU/ | Found
792 | RE8TA21BU | https://www.se.com/ww/en/product/RE8TA21BU/ | Found
793 | RE8TA31BU | https://www.se.com/ww/en/product/RE8TA31BU/ | Found
794 | RE8TA41BU | https://www.se.com/ww/en/product/RE8TA41BU/ | Not Found
795 | RE8TA61BU | https://www.se.com/ww/en/product/RE8TA61BU/ | Not Found
796 | RE8PE11BU | https://www.se.com/ww/en/product/RE8PE11BU/ | Not Found
797 | RE8PE21BU | https://www.se.com/ww/en/product/RE8PE21BU/ | Not Found
798 | RE8PE31BU | https://www.se.com/ww/en/product/RE8PE31BU/ | Not Found
799 | RE8PE71BU | https://www.se.com/ww/en/product/RE8PE71BU/ | Not Found
800 | RE8RA11B | https://www.se.com/ww/en/product/RE8RA11B/ | Not Found
801 | RE8RA11FU | https://www.se.com/ww/en/product/RE8RA11FU/ | Not Found
802 | RE8RA21B | https://www.se.com/ww/en/product/RE8RA21B/ | Not Found
803 | RE8RA21FU | https://www.se.com/ww/en/product/RE8RA21FU/ | Not Found
804 | RE8RA31B | https://www.se.com/ww/en/product/RE8RA31B/ | Not Found
805 | RE8RA31FU | https://www.se.com/ww/en/product/RE8RA31FU/ | Not Found
806 | RE8RA41FU | https://www.se.com/ww/en/product/RE8RA41FU/ | Not Found
807 | RE8PD11B | https://www.se.com/ww/en/product/RE8PD11B/ | Not Found
808 | RE8PD11FU | https://www.se.com/ww/en/product/RE8PD11FU/ | Not Found
809 | RE8PD21B | https://www.se.com/ww/en/product/RE8PD21B/ | Not Found
810 | RE8PD21FU | https://www.se.com/ww/en/product/RE8PD21FU/ | Not Found
811 | RE8PD31B | https://www.se.com/ww/en/product/RE8PD31B/ | Not Found
812 | RE8PD31FU | https://www.se.com/ww/en/product/RE8PD31FU/ | Not Found
813 | RE8CL11BU | https://www.se.com/ww/en/product/RE8CL11BU/ | Not Found
814 | RE9TA11MW | https://www.se.com/ww/en/product/RE9TA11MW/ | Not Found
815 | RE9TA21MW | https://www.se.com/ww/en/product/RE9TA21MW/ | Not Found
816 | RE9TA31MW | https://www.se.com/ww/en/product/RE9TA31MW/ | Not Found
817 | RE9TA51MW | https://www.se.com/ww/en/product/RE9TA51MW/ | Not Found
818 | RE9RA11MW7 | https://www.se.com/ww/en/product/RE9RA11MW7/ | Not Found
819 | RE9RA21MW7 | https://www.se.com/ww/en/product/RE9RA21MW7/ | Not Found
820 | RE9RA31MW7 | https://www.se.com/ww/en/product/RE9RA31MW7/ | Not Found
821 | RE9RA51MW7 | https://www.se.com/ww/en/product/RE9RA51MW7/ | Not Found
822 | RE9MS21MW | https://www.se.com/ww/en/product/RE9MS21MW/ | Not Found
823 | RSL1AB4BD | https://www.se.com/ww/en/product/RSL1AB4BD/ | Found
824 | RSL1AB4ED | https://www.se.com/ww/en/product/RSL1AB4ED/ | Found
825 | RSL1AB4JD | https://www.se.com/ww/en/product/RSL1AB4JD/ | Found
826 | RSL1AB4ND | https://www.se.com/ww/en/product/RSL1AB4ND/ | Found
827 | RSL1GB4BD | https://www.se.com/ww/en/product/RSL1GB4BD/ | Found
828 | RSL1GB4ED | https://www.se.com/ww/en/product/RSL1GB4ED/ | Found
829 | RSL1GB4JD | https://www.se.com/ww/en/product/RSL1GB4JD/ | Found
830 | RSL1GB4ND | https://www.se.com/ww/en/product/RSL1GB4ND/ | Found
831 | RSB1A120B7 | https://www.se.com/ww/en/product/RSB1A120B7/ | Found
832 | RSB1A120BD | https://www.se.com/ww/en/product/RSB1A120BD/ | Found
833 | RSB1A120E7 | https://www.se.com/ww/en/product/RSB1A120E7/ | Found
834 | RSB1A120ED | https://www.se.com/ww/en/product/RSB1A120ED/ | Found
835 | RSB1A120F7 | https://www.se.com/ww/en/product/RSB1A120F7/ | Found
836 | RSB1A120FD | https://www.se.com/ww/en/product/RSB1A120FD/ | Found
837 | RSB1A120JD | https://www.se.com/ww/en/product/RSB1A120JD/ | Found
838 | RSB1A120P7 | https://www.se.com/ww/en/product/RSB1A120P7/ | Found
839 | RSB1A120U7 | https://www.se.com/ww/en/product/RSB1A120U7/ | Found
840 | RSB1A120M7 | https://www.se.com/ww/en/product/RSB1A120M7/ | Found
841 | RSB1A120ND | https://www.se.com/ww/en/product/RSB1A120ND/ | Found
842 | RSB1A120RD | https://www.se.com/ww/en/product/RSB1A120RD/ | Found
843 | RSB1A160B7 | https://www.se.com/ww/en/product/RSB1A160B7/ | Found
844 | RSB1A160BD | https://www.se.com/ww/en/product/RSB1A160BD/ | Found
845 | RSB1A160E7 | https://www.se.com/ww/en/product/RSB1A160E7/ | Found
846 | RSB1A160ED | https://www.se.com/ww/en/product/RSB1A160ED/ | Found
847 | RSB1A160F7 | https://www.se.com/ww/en/product/RSB1A160F7/ | Found
848 | RSB1A160FD | https://www.se.com/ww/en/product/RSB1A160FD/ | Found
849 | RSB1A160JD | https://www.se.com/ww/en/product/RSB1A160JD/ | Found
850 | RSB1A160P7 | https://www.se.com/ww/en/product/RSB1A160P7/ | Found
851 | RSB1A160U7 | https://www.se.com/ww/en/product/RSB1A160U7/ | Found
852 | RSB1A160M7 | https://www.se.com/ww/en/product/RSB1A160M7/ | Found
853 | RSB1A160ND | https://www.se.com/ww/en/product/RSB1A160ND/ | Found
854 | RSB1A160RD | https://www.se.com/ww/en/product/RSB1A160RD/ | Found
855 | RSB2A080B7 | https://www.se.com/ww/en/product/RSB2A080B7/ | Found
856 | RSB2A080BD | https://www.se.com/ww/en/product/RSB2A080BD/ | Found
857 | RSB2A080E7 | https://www.se.com/ww/en/product/RSB2A080E7/ | Found
858 | RSB2A080ED | https://www.se.com/ww/en/product/RSB2A080ED/ | Found
859 | RSB2A080F7 | https://www.se.com/ww/en/product/RSB2A080F7/ | Found
860 | RSB2A080FD | https://www.se.com/ww/en/product/RSB2A080FD/ | Found
861 | RSB2A080JD | https://www.se.com/ww/en/product/RSB2A080JD/ | Found
862 | RSB2A080ND | https://www.se.com/ww/en/product/RSB2A080ND/ | Found
863 | RSB2A080P7 | https://www.se.com/ww/en/product/RSB2A080P7/ | Found
864 | RSB2A080RD | https://www.se.com/ww/en/product/RSB2A080RD/ | Found
865 | RSB2A080U7 | https://www.se.com/ww/en/product/RSB2A080U7/ | Found
866 | RSB2A080M7 | https://www.se.com/ww/en/product/RSB2A080M7/ | Found
867 | RSL1PVJU | https://www.se.com/ww/en/product/RSL1PVJU/ | Found
868 | RSL1PVBU | https://www.se.com/ww/en/product/RSL1PVBU/ | Found
869 | RSL1PVEU | https://www.se.com/ww/en/product/RSL1PVEU/ | Found
870 | RSL1PVFU | https://www.se.com/ww/en/product/RSL1PVFU/ | Found
871 | RSL1PVPU | https://www.se.com/ww/en/product/RSL1PVPU/ | Found
872 | RSL1PRJU | https://www.se.com/ww/en/product/RSL1PRJU/ | Found
873 | RSL1PRBU | https://www.se.com/ww/en/product/RSL1PRBU/ | Found
874 | RSL1PREU | https://www.se.com/ww/en/product/RSL1PREU/ | Found
875 | RSL1PRFU | https://www.se.com/ww/en/product/RSL1PRFU/ | Found
876 | RSL1PRPU | https://www.se.com/ww/en/product/RSL1PRPU/ | Found
877 | RSB1A120B7S | https://www.se.com/ww/en/product/RSB1A120B7S/ | Found
878 | RSB1A120BDS | https://www.se.com/ww/en/product/RSB1A120BDS/ | Found
879 | RSB1A120E7S | https://www.se.com/ww/en/product/RSB1A120E7S/ | Found
880 | RSB1A120EDS | https://www.se.com/ww/en/product/RSB1A120EDS/ | Found
881 | RSB1A120F7S | https://www.se.com/ww/en/product/RSB1A120F7S/ | Found
882 | RSB1A120FDS | https://www.se.com/ww/en/product/RSB1A120FDS/ | Found
883 | RSB1A120JDS | https://www.se.com/ww/en/product/RSB1A120JDS/ | Found
884 | RSB1A120P7S | https://www.se.com/ww/en/product/RSB1A120P7S/ | Found
885 | RSB1A120U7S | https://www.se.com/ww/en/product/RSB1A120U7S/ | Found
886 | RSB1A120M7S | https://www.se.com/ww/en/product/RSB1A120M7S/ | Found
887 | RSB1A120NDS | https://www.se.com/ww/en/product/RSB1A120NDS/ | Found
888 | RSB1A120RDS | https://www.se.com/ww/en/product/RSB1A120RDS/ | Found
889 | RSB1A160B7S | https://www.se.com/ww/en/product/RSB1A160B7S/ | Found
890 | RSB1A160BDS | https://www.se.com/ww/en/product/RSB1A160BDS/ | Found
891 | RSB1A160E7S | https://www.se.com/ww/en/product/RSB1A160E7S/ | Found
892 | RSB1A160EDS | https://www.se.com/ww/en/product/RSB1A160EDS/ | Found
893 | RSB1A160F7S | https://www.se.com/ww/en/product/RSB1A160F7S/ | Found
894 | RSB1A160FDS | https://www.se.com/ww/en/product/RSB1A160FDS/ | Found
895 | RSB1A160JDS | https://www.se.com/ww/en/product/RSB1A160JDS/ | Found
896 | RSB1A160P7S | https://www.se.com/ww/en/product/RSB1A160P7S/ | Found
897 | RSB1A160U7S | https://www.se.com/ww/en/product/RSB1A160U7S/ | Found
898 | RSB1A160M7S | https://www.se.com/ww/en/product/RSB1A160M7S/ | Found
899 | RSB1A160NDS | https://www.se.com/ww/en/product/RSB1A160NDS/ | Found
900 | RSB1A160RDS | https://www.se.com/ww/en/product/RSB1A160RDS/ | Found
901 | RSB2A080B7S | https://www.se.com/ww/en/product/RSB2A080B7S/ | Found
902 | RSB2A080BDS | https://www.se.com/ww/en/product/RSB2A080BDS/ | Found
903 | RSB2A080E7S | https://www.se.com/ww/en/product/RSB2A080E7S/ | Found
904 | RSB2A080EDS | https://www.se.com/ww/en/product/RSB2A080EDS/ | Found
905 | RSB2A080F7S | https://www.se.com/ww/en/product/RSB2A080F7S/ | Found
906 | RSB2A080FDS | https://www.se.com/ww/en/product/RSB2A080FDS/ | Found
907 | RSB2A080JDS | https://www.se.com/ww/en/product/RSB2A080JDS/ | Found
908 | RSB2A080NDS | https://www.se.com/ww/en/product/RSB2A080NDS/ | Found
909 | RSB2A080P7S | https://www.se.com/ww/en/product/RSB2A080P7S/ | Found
910 | RSB2A080RDS | https://www.se.com/ww/en/product/RSB2A080RDS/ | Found
911 | RSB2A080U7S | https://www.se.com/ww/en/product/RSB2A080U7S/ | Found
912 | RSB2A080M7S | https://www.se.com/ww/en/product/RSB2A080M7S/ | Found

## raw_datasheet
| Reference | Section | Parameters | Value
0 | RM17JC00MW | Main | range of product | Zelio Control
1 | RM17JC00MW | Main | product or component type | Modular measurement and control relays
2 | RM17JC00MW | Main | relay type | Current control relay
3 | RM17JC00MW | Main | relay name | RM17JC
4 | RM17JC00MW | Main | relay monitored parameters | Overcurrent detection
5 | RM17JC00MW | Main | time delay | Without
6 | RM17JC00MW | Main | switching capacity in VA | 1250 VA
7 | RM17JC00MW | Main | minimum switching current | 10 mA at 5 V DC
8 | RM17JC00MW | Main | maximum power consumption in VA | 3 VA
9 | RM17JC00MW | Main | measurement range | 2...20 A current
10 | RM17JC00MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
11 | RM17JC00MW | Complementary | maximum switching voltage | 250 V AC/DC
12 | RM17JC00MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
13 | RM17JC00MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
14 | RM17JC00MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
15 | RM17JC00MW | Complementary | maximum power consumption in W | 1 W
16 | RM17JC00MW | Complementary | control circuit frequency | 40...70 Hz sinusoidal
17 | RM17JC00MW | Complementary | output contacts | 1 C/O
18 | RM17JC00MW | Complementary | nominal output current | 5 A
19 | RM17JC00MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value
20 | RM17JC00MW | Complementary | hysteresis | 15 % fixed of threshold setting
21 | RM17JC00MW | Complementary | delay at power up | 0.5 s
22 | RM17JC00MW | Complementary | measurement accuracy | +/- 10 % of the full scale value
23 | RM17JC00MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit
24 | RM17JC00MW | Complementary | measurement error | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation
25 | RM17JC00MW | Complementary | response time | < 200 ms (in the event of a fault)
26 | RM17JC00MW | Complementary | polarity | Yes DC
27 | RM17JC00MW | Complementary | threshold setting | 10...100 %
28 | RM17JC00MW | Complementary | input current | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C
29 | RM17JC00MW | Complementary | marking | CE : 73/23/EEC CE : EMC 89/336/EEC
30 | RM17JC00MW | Complementary | overvoltage category | III conforming to IEC 60664-1
31 | RM17JC00MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
32 | RM17JC00MW | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
33 | RM17JC00MW | Complementary | insulation | Between supply and measurement
34 | RM17JC00MW | Complementary | operating position | Any position without derating
35 | RM17JC00MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
36 | RM17JC00MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
37 | RM17JC00MW | Complementary | housing material | Self-extinguishing plastic
38 | RM17JC00MW | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
39 | RM17JC00MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
40 | RM17JC00MW | Complementary | electrical durability | 100000 cycles
41 | RM17JC00MW | Complementary | mechanical durability | 30000000 cycles
42 | RM17JC00MW | Complementary | operating rate | <= 360 operations/hour full load
43 | RM17JC00MW | Complementary | contacts material | Cadmium free
44 | RM17JC00MW | Complementary | width | 17.5 mm
45 | RM17JC00MW | Complementary | net weight | 0.13 kg
46 | RM17JC00MW | Environment | immunity to microbreaks | 10 ms
47 | RM17JC00MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
48 | RM17JC00MW | Environment | standards | EN/IEC 60255-6
49 | RM17JC00MW | Environment | product certifications | GL C-Tick GOST UL CSA
50 | RM17JC00MW | Environment | ambient air temperature for storage | -40…70 °C
51 | RM17JC00MW | Environment | ambient air temperature for operation | -20…50 °C
52 | RM17JC00MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
53 | RM17JC00MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
54 | RM17JC00MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
55 | RM17JC00MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
56 | RM17JC00MW | Environment | pollution degree | 3 conforming to IEC 60664-1
57 | RM17JC00MW | Environment | dielectric test voltage | 2 kV AC 50 Hz
58 | RM17JC00MW | Environment | non-dissipating shock wave | 4 kV
59 | RM17JC00MW | Offer Sustainability | Sustainable offer status | Green Premium product
60 | RM17JC00MW | Offer Sustainability | REACh Regulation | REACh Declaration
61 | RM17JC00MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
62 | RM17JC00MW | Offer Sustainability | Mercury free | Yes
63 | RM17JC00MW | Offer Sustainability | RoHS exemption information | Yes
64 | RM17JC00MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
65 | RM17JC00MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
66 | RM17JC00MW | Offer Sustainability | Circularity Profile | End of Life Information
67 | RM17JC00MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
68 | RM17JC00MW | Contractual warranty | Warranty | 18 months
69 | RM17TA00 | Main | range of product | Zelio Control
70 | RM17TA00 | Main | product or component type | Modular measurement and control relays
71 | RM17TA00 | Main | relay type | Multifunction control relay
72 | RM17TA00 | Main | product specific application | For 3-phase supply
73 | RM17TA00 | Main | relay name | RM17TA
74 | RM17TA00 | Main | relay monitored parameters | Asymmetry Phase sequence Phase failure detection
75 | RM17TA00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value
76 | RM17TA00 | Main | switching capacity in VA | 1250 VA
77 | RM17TA00 | Main | measurement range | 208...480 V voltage AC
78 | RM17TA00 | Complementary | reset time | 1500 ms time delay
79 | RM17TA00 | Complementary | maximum switching voltage | 250 V AC 250 V DC
80 | RM17TA00 | Complementary | minimum switching current | 10 mA at 5 V DC
81 | RM17TA00 | Complementary | maximum switching current | 5 A AC 5 A DC
82 | RM17TA00 | Complementary | supply voltage limits | 183…528 V AC
83 | RM17TA00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
84 | RM17TA00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
85 | RM17TA00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
86 | RM17TA00 | Complementary | output contacts | 1 C/O
87 | RM17TA00 | Complementary | nominal output current | 5 A
88 | RM17TA00 | Complementary | measurement voltage limits | 183…528 V AC
89 | RM17TA00 | Complementary | hysteresis | 2 %
90 | RM17TA00 | Complementary | delay at power up | 650 ms
91 | RM17TA00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
92 | RM17TA00 | Complementary | threshold adjustment voltage | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC
93 | RM17TA00 | Complementary | voltage range | 208...480 V phase to phase
94 | RM17TA00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
95 | RM17TA00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit 3 % for time delay
96 | RM17TA00 | Complementary | measurement error | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation
97 | RM17TA00 | Complementary | phase failure sensitivity | 0.7 Un
98 | RM17TA00 | Complementary | response time | < 200 ms (in the event of a fault)
99 | RM17TA00 | Complementary | marking | CE
100 | RM17TA00 | Complementary | overvoltage category | III conforming to IEC 60664-1
101 | RM17TA00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
102 | RM17TA00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
103 | RM17TA00 | Complementary | supply frequency | 50/60 Hz +/- 10 %
104 | RM17TA00 | Complementary | operating position | Any position without derating
105 | RM17TA00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
106 | RM17TA00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
107 | RM17TA00 | Complementary | housing material | Self-extinguishing plastic
108 | RM17TA00 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
109 | RM17TA00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
110 | RM17TA00 | Complementary | electrical durability | 100000 cycles
111 | RM17TA00 | Complementary | mechanical durability | 30000000 cycles
112 | RM17TA00 | Complementary | operating rate | <= 360 operations/hour full load
113 | RM17TA00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
114 | RM17TA00 | Complementary | safety reliability data | MTTFd = 502.2 years B10d = 470000
115 | RM17TA00 | Complementary | width | 17.5 mm
116 | RM17TA00 | Complementary | net weight | 0.13 kg
117 | RM17TA00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2
118 | RM17TA00 | Environment | standards | EN/IEC 60255-1
119 | RM17TA00 | Environment | product certifications | GOST CSA GL C-Tick UL
120 | RM17TA00 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
121 | RM17TA00 | Environment | ambient air temperature for storage | -40…70 °C
122 | RM17TA00 | Environment | ambient air temperature for operation | -20…50 °C
123 | RM17TA00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
124 | RM17TA00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
125 | RM17TA00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
126 | RM17TA00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
127 | RM17TA00 | Environment | pollution degree | 3 conforming to IEC 60664-1
128 | RM17TA00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
129 | RM17TA00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
130 | RM17TA00 | Offer Sustainability | Sustainable offer status | Green Premium product
131 | RM17TA00 | Offer Sustainability | REACh Regulation | REACh Declaration
132 | RM17TA00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
133 | RM17TA00 | Offer Sustainability | Mercury free | Yes
134 | RM17TA00 | Offer Sustainability | RoHS exemption information | Yes
135 | RM17TA00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
136 | RM17TA00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
137 | RM17TA00 | Offer Sustainability | Circularity Profile | End of Life Information
138 | RM17TA00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
139 | RM17TA00 | Contractual warranty | Warranty | 18 months
140 | RM17TE00 | Main | range of product | Zelio Control
141 | RM17TE00 | Main | product or component type | Modular measurement and control relays
142 | RM17TE00 | Main | relay type | Multifunction control relay
143 | RM17TE00 | Main | product specific application | For 3-phase supply
144 | RM17TE00 | Main | relay name | RM17TE
145 | RM17TE00 | Main | relay monitored parameters | Undervoltage and overvoltage in window mode Asymmetry Phase sequence Phase failure detection
146 | RM17TE00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value
147 | RM17TE00 | Main | switching capacity in VA | 1250 VA
148 | RM17TE00 | Main | measurement range | 208...480 V voltage AC
149 | RM17TE00 | Complementary | reset time | 1500 ms time delay
150 | RM17TE00 | Complementary | maximum switching voltage | 250 V AC 250 V DC
151 | RM17TE00 | Complementary | minimum switching current | 10 mA at 5 V DC
152 | RM17TE00 | Complementary | maximum switching current | 5 A AC 5 A DC
153 | RM17TE00 | Complementary | supply voltage limits | 183…528 V AC
154 | RM17TE00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
155 | RM17TE00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
156 | RM17TE00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
157 | RM17TE00 | Complementary | output contacts | 1 C/O
158 | RM17TE00 | Complementary | nominal output current | 5 A
159 | RM17TE00 | Complementary | measurement voltage limits | 183…528 V AC
160 | RM17TE00 | Complementary | hysteresis | 2 %
161 | RM17TE00 | Complementary | delay at power up | 650 ms
162 | RM17TE00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
163 | RM17TE00 | Complementary | threshold adjustment voltage | -2...-17 % in the range 220 V AC +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC 2...20 % of Un selected
164 | RM17TE00 | Complementary | voltage range | 208...480 V phase to phase
165 | RM17TE00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
166 | RM17TE00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit 3 % for time delay
167 | RM17TE00 | Complementary | measurement error | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation
168 | RM17TE00 | Complementary | phase failure sensitivity | 0.7 Un
169 | RM17TE00 | Complementary | response time | < 200 ms (in the event of a fault)
170 | RM17TE00 | Complementary | marking | CE
171 | RM17TE00 | Complementary | overvoltage category | III conforming to IEC 60664-1
172 | RM17TE00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
173 | RM17TE00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
174 | RM17TE00 | Complementary | supply frequency | 50/60 Hz +/- 10 %
175 | RM17TE00 | Complementary | operating position | Any position without derating
176 | RM17TE00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
177 | RM17TE00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
178 | RM17TE00 | Complementary | housing material | Self-extinguishing plastic
179 | RM17TE00 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
180 | RM17TE00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
181 | RM17TE00 | Complementary | electrical durability | 100000 cycles
182 | RM17TE00 | Complementary | mechanical durability | 30000000 cycles
183 | RM17TE00 | Complementary | operating rate | <= 360 operations/hour full load
184 | RM17TE00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
185 | RM17TE00 | Complementary | safety reliability data | MTTFd = 502.2 years B10d = 470000
186 | RM17TE00 | Complementary | width | 17.5 mm
187 | RM17TE00 | Complementary | net weight | 0.13 kg
188 | RM17TE00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2
189 | RM17TE00 | Environment | standards | EN/IEC 60255-1
190 | RM17TE00 | Environment | product certifications | GOST C-Tick CSA UL GL
191 | RM17TE00 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
192 | RM17TE00 | Environment | ambient air temperature for storage | -40…70 °C
193 | RM17TE00 | Environment | ambient air temperature for operation | -20…50 °C
194 | RM17TE00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
195 | RM17TE00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
196 | RM17TE00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
197 | RM17TE00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
198 | RM17TE00 | Environment | pollution degree | 3 conforming to IEC 60664-1
199 | RM17TE00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
200 | RM17TE00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
201 | RM17TE00 | Offer Sustainability | Sustainable offer status | Green Premium product
202 | RM17TE00 | Offer Sustainability | REACh Regulation | REACh Declaration
203 | RM17TE00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
204 | RM17TE00 | Offer Sustainability | Mercury free | Yes
205 | RM17TE00 | Offer Sustainability | RoHS exemption information | Yes
206 | RM17TE00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
207 | RM17TE00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
208 | RM17TE00 | Offer Sustainability | Circularity Profile | End of Life Information
209 | RM17TE00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
210 | RM17TE00 | Contractual warranty | Warranty | 18 months
211 | RM17TG00 | Main | range of product | Zelio Control
212 | RM17TG00 | Main | product or component type | Modular measurement and control relays
213 | RM17TG00 | Main | relay type | Control relay
214 | RM17TG00 | Main | product specific application | For 3-phase supply
215 | RM17TG00 | Main | relay name | RM17TG
216 | RM17TG00 | Main | relay monitored parameters | Phase sequence Phase failure detection (2 or more phase cut)
217 | RM17TG00 | Main | time delay | Without
218 | RM17TG00 | Main | switching capacity in VA | 1250 VA
219 | RM17TG00 | Main | measurement range | 208...480 V voltage AC
220 | RM17TG00 | Complementary | maximum switching voltage | 250 V AC 250 V DC
221 | RM17TG00 | Complementary | minimum switching current | 10 mA at 5 V DC
222 | RM17TG00 | Complementary | supply voltage limits | 183…528 V AC
223 | RM17TG00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
224 | RM17TG00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
225 | RM17TG00 | Complementary | voltage detection threshold | < 100 V AC
226 | RM17TG00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
227 | RM17TG00 | Complementary | output contacts | 1 C/O
228 | RM17TG00 | Complementary | nominal output current | 5 A
229 | RM17TG00 | Complementary | measurement voltage limits | 183…528 V AC
230 | RM17TG00 | Complementary | delay at power up | 650 ms
231 | RM17TG00 | Complementary | voltage range | 183...528 V
232 | RM17TG00 | Complementary | response time | <= 130 ms (in the event of a fault)
233 | RM17TG00 | Complementary | marking | CE
234 | RM17TG00 | Complementary | overvoltage category | III conforming to IEC 60664-1
235 | RM17TG00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
236 | RM17TG00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
237 | RM17TG00 | Complementary | supply frequency | 50/60 Hz +/- 10 %
238 | RM17TG00 | Complementary | operating position | Any position without derating
239 | RM17TG00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
240 | RM17TG00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
241 | RM17TG00 | Complementary | housing material | Self-extinguishing plastic
242 | RM17TG00 | Complementary | local signalling | LED (yellow) for relay ON
243 | RM17TG00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
244 | RM17TG00 | Complementary | electrical durability | 100000 cycles
245 | RM17TG00 | Complementary | mechanical durability | 30000000 cycles
246 | RM17TG00 | Complementary | operating rate | <= 360 operations/hour full load
247 | RM17TG00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
248 | RM17TG00 | Complementary | safety reliability data | MTTFd = 924.6 years B10d = 850000
249 | RM17TG00 | Complementary | width | 17.5 mm
250 | RM17TG00 | Complementary | net weight | 0.13 kg
251 | RM17TG00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2
252 | RM17TG00 | Environment | standards | EN/IEC 60255-1
253 | RM17TG00 | Environment | product certifications | C-Tick GL CSA UL GOST
254 | RM17TG00 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
255 | RM17TG00 | Environment | ambient air temperature for storage | -40…70 °C
256 | RM17TG00 | Environment | ambient air temperature for operation | -20…50 °C
257 | RM17TG00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
258 | RM17TG00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
259 | RM17TG00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
260 | RM17TG00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
261 | RM17TG00 | Environment | pollution degree | 3 conforming to IEC 60664-1
262 | RM17TG00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
263 | RM17TG00 | Environment | non-dissipating shock wave | 4 kV
264 | RM17TG00 | Offer Sustainability | Sustainable offer status | Green Premium product
265 | RM17TG00 | Offer Sustainability | REACh Regulation | REACh Declaration
266 | RM17TG00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
267 | RM17TG00 | Offer Sustainability | Mercury free | Yes
268 | RM17TG00 | Offer Sustainability | RoHS exemption information | Yes
269 | RM17TG00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
270 | RM17TG00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
271 | RM17TG00 | Offer Sustainability | Circularity Profile | End of Life Information
272 | RM17TG00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
273 | RM17TG00 | Contractual warranty | Warranty | 18 months
274 | RM17TG20 | Main | range of product | Zelio Control
275 | RM17TG20 | Main | product or component type | Modular measurement and control relays
276 | RM17TG20 | Main | relay type | Control relay
277 | RM17TG20 | Main | product specific application | For 3-phase supply
278 | RM17TG20 | Main | relay name | RM17TG
279 | RM17TG20 | Main | relay monitored parameters | Phase sequence Phase failure detection (2 or more phase cut)
280 | RM17TG20 | Main | time delay | Without
281 | RM17TG20 | Main | switching capacity in VA | 1250 VA
282 | RM17TG20 | Main | measurement range | 208...480 V voltage AC
283 | RM17TG20 | Complementary | maximum switching voltage | 250 V AC 250 V DC
284 | RM17TG20 | Complementary | minimum switching current | 10 mA at 5 V DC
285 | RM17TG20 | Complementary | supply voltage limits | 183…484 V AC
286 | RM17TG20 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
287 | RM17TG20 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
288 | RM17TG20 | Complementary | voltage detection threshold | < 100 V AC
289 | RM17TG20 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
290 | RM17TG20 | Complementary | output contacts | 2 C/O
291 | RM17TG20 | Complementary | nominal output current | 5 A
292 | RM17TG20 | Complementary | measurement voltage limits | 183…528 V AC
293 | RM17TG20 | Complementary | delay at power up | 650 ms
294 | RM17TG20 | Complementary | voltage range | 183...484 V
295 | RM17TG20 | Complementary | response time | <= 130 ms (in the event of a fault)
296 | RM17TG20 | Complementary | marking | CE
297 | RM17TG20 | Complementary | overvoltage category | III conforming to IEC 60664-1
298 | RM17TG20 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
299 | RM17TG20 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
300 | RM17TG20 | Complementary | supply frequency | 50/60 Hz +/- 10 %
301 | RM17TG20 | Complementary | operating position | Any position without derating
302 | RM17TG20 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
303 | RM17TG20 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
304 | RM17TG20 | Complementary | housing material | Self-extinguishing plastic
305 | RM17TG20 | Complementary | local signalling | LED (yellow) for relay ON
306 | RM17TG20 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
307 | RM17TG20 | Complementary | electrical durability | 10000 cycles
308 | RM17TG20 | Complementary | mechanical durability | 30000000 cycles
309 | RM17TG20 | Complementary | operating rate | <= 360 operations/hour full load
310 | RM17TG20 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
311 | RM17TG20 | Complementary | safety reliability data | B10d = 850000 MTTFd = 924.6 years
312 | RM17TG20 | Complementary | width | 17.5 mm
313 | RM17TG20 | Complementary | net weight | 0.13 kg
314 | RM17TG20 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2
315 | RM17TG20 | Environment | standards | EN/IEC 60255-1
316 | RM17TG20 | Environment | product certifications | GOST C-Tick UL CSA GL
317 | RM17TG20 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
318 | RM17TG20 | Environment | ambient air temperature for storage | -40…70 °C
319 | RM17TG20 | Environment | ambient air temperature for operation | -20…50 °C
320 | RM17TG20 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
321 | RM17TG20 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
322 | RM17TG20 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
323 | RM17TG20 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
324 | RM17TG20 | Environment | pollution degree | 3 conforming to IEC 60664-1
325 | RM17TG20 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
326 | RM17TG20 | Environment | non-dissipating shock wave | 4 kV
327 | RM17TG20 | Offer Sustainability | Sustainable offer status | Green Premium product
328 | RM17TG20 | Offer Sustainability | REACh Regulation | REACh Declaration
329 | RM17TG20 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
330 | RM17TG20 | Offer Sustainability | Mercury free | Yes
331 | RM17TG20 | Offer Sustainability | RoHS exemption information | Yes
332 | RM17TG20 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
333 | RM17TG20 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
334 | RM17TG20 | Offer Sustainability | Circularity Profile | End of Life Information
335 | RM17TG20 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
336 | RM17TG20 | Contractual warranty | Warranty | 18 months
337 | RM17TT00 | Main | range of product | Zelio Control
338 | RM17TT00 | Main | product or component type | Modular measurement and control relays
339 | RM17TT00 | Main | relay type | Multifunction control relay
340 | RM17TT00 | Main | product specific application | For 3-phase supply
341 | RM17TT00 | Main | relay name | RM17TT
342 | RM17TT00 | Main | relay monitored parameters | Phase failure detection Phase sequence
343 | RM17TT00 | Main | time delay | Without
344 | RM17TT00 | Main | switching capacity in VA | 1250 VA
345 | RM17TT00 | Main | measurement range | 208...480 V voltage AC
346 | RM17TT00 | Complementary | reset time | 1500 ms time delay
347 | RM17TT00 | Complementary | maximum switching voltage | 250 V AC 250 V DC
348 | RM17TT00 | Complementary | minimum switching current | 10 mA at 5 V DC
349 | RM17TT00 | Complementary | maximum switching current | 5 A AC 5 A DC
350 | RM17TT00 | Complementary | supply voltage limits | 183…528 V AC
351 | RM17TT00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
352 | RM17TT00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
353 | RM17TT00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
354 | RM17TT00 | Complementary | output contacts | 1 C/O
355 | RM17TT00 | Complementary | nominal output current | 5 A
356 | RM17TT00 | Complementary | measurement voltage limits | 183…528 V AC
357 | RM17TT00 | Complementary | hysteresis | 2 %
358 | RM17TT00 | Complementary | delay at power up | 650 ms
359 | RM17TT00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
360 | RM17TT00 | Complementary | threshold adjustment voltage | -2...-17 % in the range 220 V AC 2...20 % of Un selected +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC
361 | RM17TT00 | Complementary | voltage range | 208...480 V phase to phase
362 | RM17TT00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
363 | RM17TT00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit 3 % for time delay
364 | RM17TT00 | Complementary | measurement error | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation
365 | RM17TT00 | Complementary | phase failure sensitivity | 0.7 Un
366 | RM17TT00 | Complementary | response time | < 200 ms (in the event of a fault)
367 | RM17TT00 | Complementary | marking | CE
368 | RM17TT00 | Complementary | overvoltage category | III conforming to IEC 60664-1
369 | RM17TT00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
370 | RM17TT00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
371 | RM17TT00 | Complementary | supply frequency | 50/60 Hz +/- 10 %
372 | RM17TT00 | Complementary | operating position | Any position without derating
373 | RM17TT00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
374 | RM17TT00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
375 | RM17TT00 | Complementary | housing material | Self-extinguishing plastic
376 | RM17TT00 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
377 | RM17TT00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
378 | RM17TT00 | Complementary | electrical durability | 100000 cycles
379 | RM17TT00 | Complementary | mechanical durability | 30000000 cycles
380 | RM17TT00 | Complementary | operating rate | <= 360 operations/hour full load
381 | RM17TT00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
382 | RM17TT00 | Complementary | safety reliability data | MTTFd = 502.2 years B10d = 470000
383 | RM17TT00 | Complementary | width | 17.5 mm
384 | RM17TT00 | Complementary | net weight | 0.13 kg
385 | RM17TT00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2
386 | RM17TT00 | Environment | standards | EN/IEC 60255-1
387 | RM17TT00 | Environment | product certifications | UL GL C-Tick GOST CSA
388 | RM17TT00 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
389 | RM17TT00 | Environment | ambient air temperature for storage | -40…70 °C
390 | RM17TT00 | Environment | ambient air temperature for operation | -20…50 °C
391 | RM17TT00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
392 | RM17TT00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
393 | RM17TT00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
394 | RM17TT00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
395 | RM17TT00 | Environment | pollution degree | 3 conforming to IEC 60664-1
396 | RM17TT00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
397 | RM17TT00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
398 | RM17TT00 | Offer Sustainability | Sustainable offer status | Green Premium product
399 | RM17TT00 | Offer Sustainability | REACh Regulation | REACh Declaration
400 | RM17TT00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
401 | RM17TT00 | Offer Sustainability | Mercury free | Yes
402 | RM17TT00 | Offer Sustainability | RoHS exemption information | Yes
403 | RM17TT00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
404 | RM17TT00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
405 | RM17TT00 | Offer Sustainability | Circularity Profile | End of Life Information
406 | RM17TT00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
407 | RM17TT00 | Contractual warranty | Warranty | 18 months
408 | RM17TU00 | Main | range of product | Zelio Control
409 | RM17TU00 | Main | product or component type | Modular measurement and control relays
410 | RM17TU00 | Main | relay type | Multifunction control relay
411 | RM17TU00 | Main | product specific application | For 3-phase supply
412 | RM17TU00 | Main | relay name | RM17TU
413 | RM17TU00 | Main | relay monitored parameters | Undervoltage detection Phase sequence Phase failure detection
414 | RM17TU00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value
415 | RM17TU00 | Main | switching capacity in VA | 1250 VA
416 | RM17TU00 | Main | measurement range | 208...480 V voltage AC
417 | RM17TU00 | Complementary | reset time | 1500 ms time delay
418 | RM17TU00 | Complementary | maximum switching voltage | 250 V AC 250 V DC
419 | RM17TU00 | Complementary | minimum switching current | 10 mA at 5 V DC
420 | RM17TU00 | Complementary | maximum switching current | 5 A AC 5 A DC
421 | RM17TU00 | Complementary | supply voltage limits | 183…528 V AC
422 | RM17TU00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
423 | RM17TU00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
424 | RM17TU00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
425 | RM17TU00 | Complementary | output contacts | 1 C/O
426 | RM17TU00 | Complementary | nominal output current | 5 A
427 | RM17TU00 | Complementary | measurement voltage limits | 183…528 V AC
428 | RM17TU00 | Complementary | hysteresis | 2 %
429 | RM17TU00 | Complementary | delay at power up | 650 ms
430 | RM17TU00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
431 | RM17TU00 | Complementary | threshold adjustment voltage | -2...-12 % in the range 208 V AC -2...-17 % in the range 220 V AC 2...20 % of Un selected +2...+17 % in the range 480 V AC
432 | RM17TU00 | Complementary | voltage range | 208...480 V phase to phase
433 | RM17TU00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
434 | RM17TU00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit 3 % for time delay
435 | RM17TU00 | Complementary | measurement error | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation
436 | RM17TU00 | Complementary | phase failure sensitivity | 0.7 Un
437 | RM17TU00 | Complementary | response time | < 200 ms (in the event of a fault)
438 | RM17TU00 | Complementary | marking | CE
439 | RM17TU00 | Complementary | overvoltage category | III conforming to IEC 60664-1
440 | RM17TU00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
441 | RM17TU00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
442 | RM17TU00 | Complementary | supply frequency | 50/60 Hz +/- 10 %
443 | RM17TU00 | Complementary | operating position | Any position without derating
444 | RM17TU00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
445 | RM17TU00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
446 | RM17TU00 | Complementary | housing material | Self-extinguishing plastic
447 | RM17TU00 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
448 | RM17TU00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
449 | RM17TU00 | Complementary | electrical durability | 100000 cycles
450 | RM17TU00 | Complementary | mechanical durability | 30000000 cycles
451 | RM17TU00 | Complementary | operating rate | <= 360 operations/hour full load
452 | RM17TU00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
453 | RM17TU00 | Complementary | safety reliability data | MTTFd = 502.2 years B10d = 470000
454 | RM17TU00 | Complementary | width | 17.5 mm
455 | RM17TU00 | Complementary | net weight | 0.13 kg
456 | RM17TU00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2
457 | RM17TU00 | Environment | standards | EN/IEC 60255-1
458 | RM17TU00 | Environment | product certifications | GL GOST UL C-Tick CSA
459 | RM17TU00 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
460 | RM17TU00 | Environment | ambient air temperature for storage | -40…70 °C
461 | RM17TU00 | Environment | ambient air temperature for operation | -20…50 °C
462 | RM17TU00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
463 | RM17TU00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
464 | RM17TU00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
465 | RM17TU00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
466 | RM17TU00 | Environment | pollution degree | 3 conforming to IEC 60664-1
467 | RM17TU00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
468 | RM17TU00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
469 | RM17TU00 | Offer Sustainability | Sustainable offer status | Green Premium product
470 | RM17TU00 | Offer Sustainability | REACh Regulation | REACh Declaration
471 | RM17TU00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
472 | RM17TU00 | Offer Sustainability | Mercury free | Yes
473 | RM17TU00 | Offer Sustainability | RoHS exemption information | Yes
474 | RM17TU00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
475 | RM17TU00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
476 | RM17TU00 | Offer Sustainability | Circularity Profile | End of Life Information
477 | RM17TU00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
478 | RM17TU00 | Contractual warranty | Warranty | 18 months
479 | RM17UAS14 | Main | range of product | Zelio Control
480 | RM17UAS14 | Main | product or component type | Modular measurement and control relays
481 | RM17UAS14 | Main | relay type | Voltage control relay
482 | RM17UAS14 | Main | product specific application | For single-phase and DC supply
483 | RM17UAS14 | Main | relay name | RM17UAS
484 | RM17UAS14 | Main | relay monitored parameters | Overvoltage or undervoltage detection Self-powered
485 | RM17UAS14 | Main | time delay | Adjustable 0.1...10 s, 0 + 10 % on crossing the threshold
486 | RM17UAS14 | Main | switching capacity in VA | 1250 VA
487 | RM17UAS14 | Main | minimum switching current | 10 mA at 5 V DC
488 | RM17UAS14 | Main | maximum switching current | 5 A AC/DC
489 | RM17UAS14 | Main | measurement range | 9...15 V voltage DC
490 | RM17UAS14 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
491 | RM17UAS14 | Complementary | reset time | 1500 ms time delay
492 | RM17UAS14 | Complementary | maximum switching voltage | 250 V AC/DC
493 | RM17UAS14 | Complementary | [Us] rated supply voltage | 12 V DC +/- 10 %
494 | RM17UAS14 | Complementary | supply voltage limits | 7…20 V DC
495 | RM17UAS14 | Complementary | maximum power consumption in W | 1 W DC
496 | RM17UAS14 | Complementary | immunity to microbreaks | 20 ms at 12 V
497 | RM17UAS14 | Complementary | output contacts | 1 C/O
498 | RM17UAS14 | Complementary | nominal output current | 5 A
499 | RM17UAS14 | Complementary | hysteresis | 5…20 % of threshold setting
500 | RM17UAS14 | Complementary | delay at power up | 1000 ms DC
501 | RM17UAS14 | Complementary | measurement accuracy | +/- 10 % of the full scale value
502 | RM17UAS14 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay
503 | RM17UAS14 | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.2 %/°C with temperature variation
504 | RM17UAS14 | Complementary | polarity | Non reversible polarity on DC supply
505 | RM17UAS14 | Complementary | quality labels | CE
506 | RM17UAS14 | Complementary | overvoltage category | III conforming to IEC 60664-1
507 | RM17UAS14 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
508 | RM17UAS14 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1
509 | RM17UAS14 | Complementary | operating position | Any position without derating
510 | RM17UAS14 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
511 | RM17UAS14 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
512 | RM17UAS14 | Complementary | housing material | Self-extinguishing plastic
513 | RM17UAS14 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
514 | RM17UAS14 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
515 | RM17UAS14 | Complementary | electrical durability | 100000 cycles
516 | RM17UAS14 | Complementary | mechanical durability | 30000000 cycles
517 | RM17UAS14 | Complementary | operating rate | <= 360 operations/hour full load
518 | RM17UAS14 | Complementary | width | 17.5 mm
519 | RM17UAS14 | Complementary | net weight | 0.08 kg
520 | RM17UAS14 | Complementary | compatibility code | RM17
521 | RM17UAS14 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
522 | RM17UAS14 | Environment | standards | EN/IEC 60255-6
523 | RM17UAS14 | Environment | product certifications | CSA C-Tick GL UL GOST
524 | RM17UAS14 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
525 | RM17UAS14 | Environment | ambient air temperature for storage | -40…70 °C
526 | RM17UAS14 | Environment | ambient air temperature for operation | -20…50 °C
527 | RM17UAS14 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
528 | RM17UAS14 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
529 | RM17UAS14 | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
530 | RM17UAS14 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
531 | RM17UAS14 | Environment | pollution degree | 3 conforming to IEC 60664-1
532 | RM17UAS14 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
533 | RM17UAS14 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
534 | RM17UAS14 | Offer Sustainability | Sustainable offer status | Green Premium product
535 | RM17UAS14 | Offer Sustainability | REACh Regulation | REACh Declaration
536 | RM17UAS14 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
537 | RM17UAS14 | Offer Sustainability | Mercury free | Yes
538 | RM17UAS14 | Offer Sustainability | RoHS exemption information | Yes
539 | RM17UAS14 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
540 | RM17UAS14 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
541 | RM17UAS14 | Offer Sustainability | Circularity Profile | End of Life Information
542 | RM17UAS14 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
543 | RM17UAS14 | Contractual warranty | Warranty | 18 months
544 | RM17UAS15 | Main | range of product | Zelio Control
545 | RM17UAS15 | Main | product or component type | Modular measurement and control relays
546 | RM17UAS15 | Main | relay type | Voltage control relay
547 | RM17UAS15 | Main | product specific application | For single-phase and DC supply
548 | RM17UAS15 | Main | relay name | RM17UAS
549 | RM17UAS15 | Main | relay monitored parameters | Overvoltage or undervoltage detection Self-powered
550 | RM17UAS15 | Main | time delay | Adjustable 0.1...10 s, 0 + 10 % on crossing the threshold
551 | RM17UAS15 | Main | switching capacity in VA | 1250 VA
552 | RM17UAS15 | Main | minimum switching current | 10 mA at 5 V DC
553 | RM17UAS15 | Main | maximum switching current | 5 A AC/DC
554 | RM17UAS15 | Main | power consumption in VA | 0…3 VA AC
555 | RM17UAS15 | Main | measurement range | 65...260 V voltage AC 50/60 Hz 65...260 V voltage DC
556 | RM17UAS15 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
557 | RM17UAS15 | Complementary | reset time | 1500 ms time delay
558 | RM17UAS15 | Complementary | maximum switching voltage | 250 V AC/DC
559 | RM17UAS15 | Complementary | [Us] rated supply voltage | 110...240 V AC/DC 50/60 Hz +/- 10 %
560 | RM17UAS15 | Complementary | supply voltage limits | 50…270 V AC/DC
561 | RM17UAS15 | Complementary | maximum power consumption in W | 1 W DC
562 | RM17UAS15 | Complementary | immunity to microbreaks | 20 ms
563 | RM17UAS15 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
564 | RM17UAS15 | Complementary | output contacts | 1 C/O
565 | RM17UAS15 | Complementary | nominal output current | 5 A
566 | RM17UAS15 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
567 | RM17UAS15 | Complementary | hysteresis | 5…20 % of threshold setting
568 | RM17UAS15 | Complementary | delay at power up | 1000 ms DC 500 ms AC
569 | RM17UAS15 | Complementary | measurement accuracy | +/- 10 % of the full scale value
570 | RM17UAS15 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay
571 | RM17UAS15 | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.2 %/°C with temperature variation
572 | RM17UAS15 | Complementary | polarity | Non reversible polarity on DC supply
573 | RM17UAS15 | Complementary | quality labels | CE
574 | RM17UAS15 | Complementary | overvoltage category | III conforming to IEC 60664-1
575 | RM17UAS15 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
576 | RM17UAS15 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1
577 | RM17UAS15 | Complementary | operating position | Any position without derating
578 | RM17UAS15 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
579 | RM17UAS15 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
580 | RM17UAS15 | Complementary | housing material | Self-extinguishing plastic
581 | RM17UAS15 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
582 | RM17UAS15 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
583 | RM17UAS15 | Complementary | electrical durability | 100000 cycles
584 | RM17UAS15 | Complementary | mechanical durability | 30000000 cycles
585 | RM17UAS15 | Complementary | operating rate | <= 360 operations/hour full load
586 | RM17UAS15 | Complementary | width | 17.5 mm
587 | RM17UAS15 | Complementary | net weight | 0.08 kg
588 | RM17UAS15 | Complementary | compatibility code | RM17
589 | RM17UAS15 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
590 | RM17UAS15 | Environment | standards | EN/IEC 60255-6
591 | RM17UAS15 | Environment | product certifications | GL UL GOST CSA C-Tick
592 | RM17UAS15 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
593 | RM17UAS15 | Environment | ambient air temperature for storage | -40…70 °C
594 | RM17UAS15 | Environment | ambient air temperature for operation | -20…50 °C
595 | RM17UAS15 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
596 | RM17UAS15 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
597 | RM17UAS15 | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
598 | RM17UAS15 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
599 | RM17UAS15 | Environment | pollution degree | 3 conforming to IEC 60664-1
600 | RM17UAS15 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
601 | RM17UAS15 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
602 | RM17UAS15 | Offer Sustainability | Sustainable offer status | Green Premium product
603 | RM17UAS15 | Offer Sustainability | REACh Regulation | REACh Declaration
604 | RM17UAS15 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
605 | RM17UAS15 | Offer Sustainability | Mercury free | Yes
606 | RM17UAS15 | Offer Sustainability | RoHS exemption information | Yes
607 | RM17UAS15 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
608 | RM17UAS15 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
609 | RM17UAS15 | Offer Sustainability | Circularity Profile | End of Life Information
610 | RM17UAS15 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
611 | RM17UAS15 | Contractual warranty | Warranty | 18 months
612 | RM17UAS15315M | Main | range of product | Zelio Control
613 | RM17UAS15315M | Main | product or component type | Modular measurement and control relays
614 | RM17UAS15315M | Main | relay type | Voltage control relay
615 | RM17UAS15315M | Main | product specific application | For single-phase
616 | RM17UAS15315M | Main | relay name | RM17UAS
617 | RM17UAS15315M | Main | relay monitored parameters | Undervoltage detection Self-powered
618 | RM17UAS15315M | Main | time delay | Adjustable 3...15 min on recovery and start up time
619 | RM17UAS15315M | Main | switching capacity in VA | 1250 VA
620 | RM17UAS15315M | Main | minimum switching current | 10 mA at 5 V DC
621 | RM17UAS15315M | Main | maximum switching current | 5 A AC/DC
622 | RM17UAS15315M | Main | power consumption in VA | 0…3 VA AC
623 | RM17UAS15315M | Main | measurement range | 165 V voltage AC
624 | RM17UAS15315M | Main | utilisation category | AC-1 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-1 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
625 | RM17UAS15315M | Complementary | reset time | 1500 ms time delay
626 | RM17UAS15315M | Complementary | maximum switching voltage | 250 V AC/DC
627 | RM17UAS15315M | Complementary | [Us] rated supply voltage | 220 V AC 50 Hz +/- 10 %
628 | RM17UAS15315M | Complementary | supply voltage limits | 165…270 V AC
629 | RM17UAS15315M | Complementary | maximum power consumption in W | 1 W
630 | RM17UAS15315M | Complementary | immunity to microbreaks | 20 ms
631 | RM17UAS15315M | Complementary | control circuit frequency | 50 Hz +/- 10 %
632 | RM17UAS15315M | Complementary | output contacts | 1 C/O
633 | RM17UAS15315M | Complementary | nominal output current | 5 A
634 | RM17UAS15315M | Complementary | response time | <= 200 ms
635 | RM17UAS15315M | Complementary | hysteresis | 5 % fixed of threshold setting
636 | RM17UAS15315M | Complementary | delay at power up | 3 min minimum
637 | RM17UAS15315M | Complementary | measurement accuracy | +/- 3 %
638 | RM17UAS15315M | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay
639 | RM17UAS15315M | Complementary | measurement error | 0.2 %/°C with temperature variation
640 | RM17UAS15315M | Complementary | quality labels | CE
641 | RM17UAS15315M | Complementary | overvoltage category | III conforming to IEC 60664-1
642 | RM17UAS15315M | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
643 | RM17UAS15315M | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1
644 | RM17UAS15315M | Complementary | operating position | Any position without derating
645 | RM17UAS15315M | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
646 | RM17UAS15315M | Complementary | tightening torque | 0.60…0.99 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1
647 | RM17UAS15315M | Complementary | housing material | Self-extinguishing plastic
648 | RM17UAS15315M | Complementary | local signalling | LED (green)power ON: LED (yellow)relay ON:
649 | RM17UAS15315M | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
650 | RM17UAS15315M | Complementary | electrical durability | 100000 cycles
651 | RM17UAS15315M | Complementary | mechanical durability | 30000000 cycles
652 | RM17UAS15315M | Complementary | operating rate | <= 360 operations/hour full load
653 | RM17UAS15315M | Complementary | width | 17.5 mm
654 | RM17UAS15315M | Complementary | net weight | 0.08 kg
655 | RM17UAS15315M | Complementary | compatibility code | RM17
656 | RM17UAS15315M | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
657 | RM17UAS15315M | Environment | standards | EN/IEC 60255-1
658 | RM17UAS15315M | Environment | product certifications | UL
659 | RM17UAS15315M | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
660 | RM17UAS15315M | Environment | ambient air temperature for storage | -40…70 °C
661 | RM17UAS15315M | Environment | ambient air temperature for operation | -20…50 °C
662 | RM17UAS15315M | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
663 | RM17UAS15315M | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
664 | RM17UAS15315M | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
665 | RM17UAS15315M | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
666 | RM17UAS15315M | Environment | pollution degree | 3 conforming to IEC 60664-1
667 | RM17UAS15315M | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
668 | RM17UAS15315M | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
669 | RM17UAS15315M | Offer Sustainability | REACh Regulation | REACh Declaration
670 | RM17UAS15315M | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
671 | RM17UAS15315M | Offer Sustainability | Mercury free | Yes
672 | RM17UAS15315M | Offer Sustainability | RoHS exemption information | Yes
673 | RM17UAS15315M | Offer Sustainability | China RoHS Regulation | China RoHS declaration
674 | RM17UAS15315M | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
675 | RM17UAS16 | Main | range of product | Zelio Control
676 | RM17UAS16 | Main | product or component type | Modular measurement and control relays
677 | RM17UAS16 | Main | relay type | Voltage control relay
678 | RM17UAS16 | Main | product specific application | For single-phase and DC supply
679 | RM17UAS16 | Main | relay name | RM17UAS
680 | RM17UAS16 | Main | relay monitored parameters | Overvoltage or undervoltage detection Self-powered
681 | RM17UAS16 | Main | time delay | Adjustable 0.1...10 s, 0 + 10 % on crossing the threshold
682 | RM17UAS16 | Main | switching capacity in VA | 1250 VA
683 | RM17UAS16 | Main | minimum switching current | 10 mA at 5 V DC
684 | RM17UAS16 | Main | maximum switching current | 5 A AC/DC
685 | RM17UAS16 | Main | power consumption in VA | 0…3.9 VA AC
686 | RM17UAS16 | Main | measurement range | 20...80 V voltage AC 50/60 Hz 20...80 V voltage DC
687 | RM17UAS16 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
688 | RM17UAS16 | Complementary | reset time | 1500 ms time delay
689 | RM17UAS16 | Complementary | maximum switching voltage | 250 V AC/DC
690 | RM17UAS16 | Complementary | [Us] rated supply voltage | 24...48 V AC/DC 50/60 Hz +/- 10 %
691 | RM17UAS16 | Complementary | supply voltage limits | 15…100 V AC/DC
692 | RM17UAS16 | Complementary | maximum power consumption in W | 1.6 W DC
693 | RM17UAS16 | Complementary | immunity to microbreaks | 20 ms
694 | RM17UAS16 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
695 | RM17UAS16 | Complementary | output contacts | 1 C/O
696 | RM17UAS16 | Complementary | nominal output current | 5 A
697 | RM17UAS16 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
698 | RM17UAS16 | Complementary | hysteresis | 5…20 % of threshold setting
699 | RM17UAS16 | Complementary | delay at power up | 1000 ms DC 500 ms AC
700 | RM17UAS16 | Complementary | measurement accuracy | +/- 10 % of the full scale value
701 | RM17UAS16 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay
702 | RM17UAS16 | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.2 %/°C with temperature variation
703 | RM17UAS16 | Complementary | polarity | Non reversible polarity on DC supply
704 | RM17UAS16 | Complementary | quality labels | CE
705 | RM17UAS16 | Complementary | overvoltage category | III conforming to IEC 60664-1
706 | RM17UAS16 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
707 | RM17UAS16 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1
708 | RM17UAS16 | Complementary | operating position | Any position without derating
709 | RM17UAS16 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
710 | RM17UAS16 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
711 | RM17UAS16 | Complementary | housing material | Self-extinguishing plastic
712 | RM17UAS16 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
713 | RM17UAS16 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
714 | RM17UAS16 | Complementary | electrical durability | 100000 cycles
715 | RM17UAS16 | Complementary | mechanical durability | 30000000 cycles
716 | RM17UAS16 | Complementary | operating rate | <= 360 operations/hour full load
717 | RM17UAS16 | Complementary | width | 17.5 mm
718 | RM17UAS16 | Complementary | net weight | 0.08 kg
719 | RM17UAS16 | Complementary | compatibility code | RM17
720 | RM17UAS16 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
721 | RM17UAS16 | Environment | standards | EN/IEC 60255-6
722 | RM17UAS16 | Environment | product certifications | CSA GL UL GOST C-Tick
723 | RM17UAS16 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
724 | RM17UAS16 | Environment | ambient air temperature for storage | -40…70 °C
725 | RM17UAS16 | Environment | ambient air temperature for operation | -20…50 °C
726 | RM17UAS16 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
727 | RM17UAS16 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
728 | RM17UAS16 | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
729 | RM17UAS16 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
730 | RM17UAS16 | Environment | pollution degree | 3 conforming to IEC 60664-1
731 | RM17UAS16 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
732 | RM17UAS16 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
733 | RM17UAS16 | Offer Sustainability | Sustainable offer status | Green Premium product
734 | RM17UAS16 | Offer Sustainability | REACh Regulation | REACh Declaration
735 | RM17UAS16 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
736 | RM17UAS16 | Offer Sustainability | Mercury free | Yes
737 | RM17UAS16 | Offer Sustainability | RoHS exemption information | Yes
738 | RM17UAS16 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
739 | RM17UAS16 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
740 | RM17UAS16 | Offer Sustainability | Circularity Profile | End of Life Information
741 | RM17UAS16 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
742 | RM17UAS16 | Contractual warranty | Warranty | 18 months
743 | RM17UB310 | Main | range of product | Zelio Control
744 | RM17UB310 | Main | product or component type | Modular measurement and control relays
745 | RM17UB310 | Main | relay type | Voltage control relay
746 | RM17UB310 | Main | product specific application | For 3-phase supply
747 | RM17UB310 | Main | relay name | RM17UB3
748 | RM17UB310 | Main | relay monitored parameters | Overvoltage and undervoltage between phases
749 | RM17UB310 | Main | time delay | Adjustable 0.3...30 s, 0 + 10 % on crossing the threshold
750 | RM17UB310 | Main | switching capacity in VA | 1250 VA
751 | RM17UB310 | Main | minimum switching current | 10 mA at 5 V DC
752 | RM17UB310 | Main | maximum switching current | 5 A AC/DC
753 | RM17UB310 | Main | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
754 | RM17UB310 | Main | measurement range | 183...528 V voltage AC
755 | RM17UB310 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
756 | RM17UB310 | Complementary | reset time | 1500 ms time delay
757 | RM17UB310 | Complementary | maximum switching voltage | 250 V AC/DC
758 | RM17UB310 | Complementary | [Us] rated supply voltage | 208...480 V AC 50/60 Hz +/- 10 %
759 | RM17UB310 | Complementary | supply voltage limits | 183…528 V AC
760 | RM17UB310 | Complementary | voltage detection threshold | 183 V
761 | RM17UB310 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
762 | RM17UB310 | Complementary | output contacts | 1 C/O
763 | RM17UB310 | Complementary | nominal output current | 5 A
764 | RM17UB310 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
765 | RM17UB310 | Complementary | hysteresis | 2 %
766 | RM17UB310 | Complementary | delay at power up | 650 ms
767 | RM17UB310 | Complementary | measurement accuracy | +/- 10 % of the full scale value
768 | RM17UB310 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay
769 | RM17UB310 | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
770 | RM17UB310 | Complementary | response time | < 200 ms (in the event of a fault)
771 | RM17UB310 | Complementary | quality labels | CE
772 | RM17UB310 | Complementary | overvoltage category | III conforming to IEC 60664-1
773 | RM17UB310 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
774 | RM17UB310 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
775 | RM17UB310 | Complementary | operating position | Any position without derating
776 | RM17UB310 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
777 | RM17UB310 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
778 | RM17UB310 | Complementary | housing material | Self-extinguishing plastic
779 | RM17UB310 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
780 | RM17UB310 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
781 | RM17UB310 | Complementary | electrical durability | 100000 cycles
782 | RM17UB310 | Complementary | mechanical durability | 30000000 cycles
783 | RM17UB310 | Complementary | operating rate | <= 360 operations/hour full load
784 | RM17UB310 | Complementary | safety reliability data | B10d = 470000 MTTFd = 502.2 years
785 | RM17UB310 | Complementary | width | 17.5 mm
786 | RM17UB310 | Complementary | net weight | 0.08 kg
787 | RM17UB310 | Complementary | functionality | Overvoltage and undervoltage detection
788 | RM17UB310 | Complementary | compatibility code | RM17
789 | RM17UB310 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
790 | RM17UB310 | Environment | standards | EN/IEC 60255-1
791 | RM17UB310 | Environment | product certifications | GOST UL GL C-Tick CSA
792 | RM17UB310 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
793 | RM17UB310 | Environment | ambient air temperature for storage | -40…70 °C
794 | RM17UB310 | Environment | ambient air temperature for operation | -20…50 °C
795 | RM17UB310 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
796 | RM17UB310 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
797 | RM17UB310 | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
798 | RM17UB310 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
799 | RM17UB310 | Environment | pollution degree | 3 conforming to IEC 60664-1
800 | RM17UB310 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
801 | RM17UB310 | Environment | non-dissipating shock wave | 4 kV
802 | RM17UB310 | Offer Sustainability | Sustainable offer status | Green Premium product
803 | RM17UB310 | Offer Sustainability | REACh Regulation | REACh Declaration
804 | RM17UB310 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
805 | RM17UB310 | Offer Sustainability | Mercury free | Yes
806 | RM17UB310 | Offer Sustainability | RoHS exemption information | Yes
807 | RM17UB310 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
808 | RM17UB310 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
809 | RM17UB310 | Offer Sustainability | Circularity Profile | End of Life Information
810 | RM17UB310 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
811 | RM17UB310 | Contractual warranty | Warranty | 18 months
812 | RM17UBE15 | Main | range of product | Zelio Control
813 | RM17UBE15 | Main | product or component type | Modular measurement and control relays
814 | RM17UBE15 | Main | relay type | Voltage control relay
815 | RM17UBE15 | Main | product specific application | For single-phase and DC supply
816 | RM17UBE15 | Main | relay name | RM17UBE
817 | RM17UBE15 | Main | relay monitored parameters | Self-powered Overvoltage and undervoltage detection
818 | RM17UBE15 | Main | time delay | Adjustable 0.1...10 s, 0 + 10 % on crossing the threshold
819 | RM17UBE15 | Main | switching capacity in VA | 1250 VA
820 | RM17UBE15 | Main | minimum switching current | 10 mA at 5 V DC
821 | RM17UBE15 | Main | maximum switching current | 5 A AC/DC
822 | RM17UBE15 | Main | power consumption in VA | 0…3 VA AC
823 | RM17UBE15 | Main | measurement range | 65...260 V voltage AC/DC
824 | RM17UBE15 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
825 | RM17UBE15 | Complementary | reset time | 1500 ms time delay
826 | RM17UBE15 | Complementary | maximum switching voltage | 250 V AC/DC
827 | RM17UBE15 | Complementary | [Us] rated supply voltage | 110...240 V AC/DC 50/60 Hz +/- 10 %
828 | RM17UBE15 | Complementary | supply voltage limits | 50…270 V AC/DC
829 | RM17UBE15 | Complementary | maximum power consumption in W | 1 W DC
830 | RM17UBE15 | Complementary | immunity to microbreaks | 20 ms
831 | RM17UBE15 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
832 | RM17UBE15 | Complementary | output contacts | 1 C/O
833 | RM17UBE15 | Complementary | nominal output current | 5 A
834 | RM17UBE15 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
835 | RM17UBE15 | Complementary | hysteresis | 3 % fixed of threshold setting
836 | RM17UBE15 | Complementary | delay at power up | 1000 ms DC 500 ms AC
837 | RM17UBE15 | Complementary | measurement accuracy | +/- 10 % of the full scale value
838 | RM17UBE15 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay
839 | RM17UBE15 | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.2 %/°C with temperature variation
840 | RM17UBE15 | Complementary | polarity | Non reversible polarity on DC supply
841 | RM17UBE15 | Complementary | quality labels | CE
842 | RM17UBE15 | Complementary | overvoltage category | III conforming to IEC 60664-1
843 | RM17UBE15 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
844 | RM17UBE15 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1
845 | RM17UBE15 | Complementary | operating position | Any position without derating
846 | RM17UBE15 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
847 | RM17UBE15 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
848 | RM17UBE15 | Complementary | housing material | Self-extinguishing plastic
849 | RM17UBE15 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
850 | RM17UBE15 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
851 | RM17UBE15 | Complementary | electrical durability | 100000 cycles
852 | RM17UBE15 | Complementary | mechanical durability | 30000000 cycles
853 | RM17UBE15 | Complementary | operating rate | <= 360 operations/hour full load
854 | RM17UBE15 | Complementary | safety reliability data | B10d = 470000 MTTFd = 502.2 years
855 | RM17UBE15 | Complementary | width | 17.5 mm
856 | RM17UBE15 | Complementary | net weight | 0.08 kg
857 | RM17UBE15 | Complementary | functionality | Overvoltage and undervoltage detection
858 | RM17UBE15 | Complementary | compatibility code | RM17
859 | RM17UBE15 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
860 | RM17UBE15 | Environment | standards | EN/IEC 60255-6
861 | RM17UBE15 | Environment | product certifications | UL GL GOST C-Tick CSA
862 | RM17UBE15 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
863 | RM17UBE15 | Environment | ambient air temperature for storage | -40…70 °C
864 | RM17UBE15 | Environment | ambient air temperature for operation | -20…50 °C
865 | RM17UBE15 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
866 | RM17UBE15 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
867 | RM17UBE15 | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
868 | RM17UBE15 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
869 | RM17UBE15 | Environment | pollution degree | 3 conforming to IEC 60664-1
870 | RM17UBE15 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
871 | RM17UBE15 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
872 | RM17UBE15 | Offer Sustainability | Sustainable offer status | Green Premium product
873 | RM17UBE15 | Offer Sustainability | REACh Regulation | REACh Declaration
874 | RM17UBE15 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
875 | RM17UBE15 | Offer Sustainability | Mercury free | Yes
876 | RM17UBE15 | Offer Sustainability | RoHS exemption information | Yes
877 | RM17UBE15 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
878 | RM17UBE15 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
879 | RM17UBE15 | Offer Sustainability | Circularity Profile | End of Life Information
880 | RM17UBE15 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
881 | RM17UBE15 | Contractual warranty | Warranty | 18 months
882 | RM17UBE16 | Main | range of product | Zelio Control
883 | RM17UBE16 | Main | product or component type | Modular measurement and control relays
884 | RM17UBE16 | Main | relay type | Voltage control relay
885 | RM17UBE16 | Main | product specific application | For single-phase and DC supply
886 | RM17UBE16 | Main | relay name | RM17UBE
887 | RM17UBE16 | Main | relay monitored parameters | Self-powered Overvoltage and undervoltage detection
888 | RM17UBE16 | Main | time delay | Adjustable 0.1...10 s, 0 + 10 % on crossing the threshold
889 | RM17UBE16 | Main | switching capacity in VA | 1250 VA
890 | RM17UBE16 | Main | minimum switching current | 10 mA at 5 V DC
891 | RM17UBE16 | Main | maximum switching current | 5 A AC/DC
892 | RM17UBE16 | Main | power consumption in VA | 0…3.9 VA AC
893 | RM17UBE16 | Main | measurement range | 20...80 V voltage AC 50/60 Hz 20...80 V voltage DC
894 | RM17UBE16 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
895 | RM17UBE16 | Complementary | reset time | 1500 ms time delay
896 | RM17UBE16 | Complementary | maximum switching voltage | 250 V AC/DC
897 | RM17UBE16 | Complementary | [Us] rated supply voltage | 24...48 V AC/DC 50/60 Hz +/- 10 %
898 | RM17UBE16 | Complementary | supply voltage limits | 15…100 V AC/DC
899 | RM17UBE16 | Complementary | maximum power consumption in W | 1.6 W DC
900 | RM17UBE16 | Complementary | immunity to microbreaks | 20 ms
901 | RM17UBE16 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
902 | RM17UBE16 | Complementary | output contacts | 1 C/O
903 | RM17UBE16 | Complementary | nominal output current | 5 A
904 | RM17UBE16 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
905 | RM17UBE16 | Complementary | hysteresis | 3 % fixed of threshold setting
906 | RM17UBE16 | Complementary | delay at power up | 1000 ms DC 500 ms AC
907 | RM17UBE16 | Complementary | measurement accuracy | +/- 10 % of the full scale value
908 | RM17UBE16 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay
909 | RM17UBE16 | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.2 %/°C with temperature variation
910 | RM17UBE16 | Complementary | polarity | Non reversible polarity on DC supply
911 | RM17UBE16 | Complementary | quality labels | CE
912 | RM17UBE16 | Complementary | overvoltage category | III conforming to IEC 60664-1
913 | RM17UBE16 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
914 | RM17UBE16 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1
915 | RM17UBE16 | Complementary | operating position | Any position without derating
916 | RM17UBE16 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
917 | RM17UBE16 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
918 | RM17UBE16 | Complementary | housing material | Self-extinguishing plastic
919 | RM17UBE16 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
920 | RM17UBE16 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
921 | RM17UBE16 | Complementary | electrical durability | 100000 cycles
922 | RM17UBE16 | Complementary | mechanical durability | 30000000 cycles
923 | RM17UBE16 | Complementary | operating rate | <= 360 operations/hour full load
924 | RM17UBE16 | Complementary | safety reliability data | MTTFd = 502.2 years B10d = 470000
925 | RM17UBE16 | Complementary | width | 17.5 mm
926 | RM17UBE16 | Complementary | net weight | 0.08 kg
927 | RM17UBE16 | Complementary | functionality | Overvoltage and undervoltage detection
928 | RM17UBE16 | Complementary | compatibility code | RM17
929 | RM17UBE16 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
930 | RM17UBE16 | Environment | standards | EN/IEC 60255-6
931 | RM17UBE16 | Environment | product certifications | C-Tick GOST GL CSA UL
932 | RM17UBE16 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
933 | RM17UBE16 | Environment | ambient air temperature for storage | -40…70 °C
934 | RM17UBE16 | Environment | ambient air temperature for operation | -20…50 °C
935 | RM17UBE16 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
936 | RM17UBE16 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
937 | RM17UBE16 | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
938 | RM17UBE16 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
939 | RM17UBE16 | Environment | pollution degree | 3 conforming to IEC 60664-1
940 | RM17UBE16 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
941 | RM17UBE16 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
942 | RM17UBE16 | Offer Sustainability | Sustainable offer status | Green Premium product
943 | RM17UBE16 | Offer Sustainability | REACh Regulation | REACh Declaration
944 | RM17UBE16 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
945 | RM17UBE16 | Offer Sustainability | Mercury free | Yes
946 | RM17UBE16 | Offer Sustainability | RoHS exemption information | Yes
947 | RM17UBE16 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
948 | RM17UBE16 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
949 | RM17UBE16 | Offer Sustainability | Circularity Profile | End of Life Information
950 | RM17UBE16 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
951 | RM17UBE16 | Contractual warranty | Warranty | 18 months
952 | RM35ATL0MW | Main | range of product | Zelio Control
953 | RM35ATL0MW | Main | product or component type | Modular measurement and control relays
954 | RM35ATL0MW | Main | relay type | Temperature control relays
955 | RM35ATL0MW | Main | product specific application | For elevator machine rooms and 3-phase supplies
956 | RM35ATL0MW | Main | relay name | RM35AT
957 | RM35ATL0MW | Main | relay monitored parameters | Undertemperature: -1...11°C Overtemperature: 34...46°C
958 | RM35ATL0MW | Main | time delay range | 0.1...10 s adjustable delay (tolerance: 0...10 % of the full scale value)
959 | RM35ATL0MW | Main | switching capacity in VA | 1250 VA
960 | RM35ATL0MW | Main | minimum switching current | 10 mA at 5 V DC
961 | RM35ATL0MW | Main | maximum power consumption in VA | 3.5 VA AC
962 | RM35ATL0MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
963 | RM35ATL0MW | Complementary | reset time | 8 s
964 | RM35ATL0MW | Complementary | maximum switching voltage | 250 V AC/DC
965 | RM35ATL0MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC
966 | RM35ATL0MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC
967 | RM35ATL0MW | Complementary | supply voltage limits | 20.4…264 V AC 21.6…264 V DC
968 | RM35ATL0MW | Complementary | maximum power consumption in W | 0.6 W DC
969 | RM35ATL0MW | Complementary | resistance across terminals | 1.33 kOhm at temperature
970 | RM35ATL0MW | Complementary | width | 35 mm
971 | RM35ATL0MW | Complementary | output contacts | 1 C/O
972 | RM35ATL0MW | Complementary | contacts material | Cadmium free
973 | RM35ATL0MW | Complementary | nominal output current | 5 A
974 | RM35ATL0MW | Complementary | delay at power up | 0.2 s
975 | RM35ATL0MW | Complementary | measurement accuracy | +/- 2 °C
976 | RM35ATL0MW | Complementary | response time | <= 3.5 s + Tt (in case of temperature fault) <= 3.5 s (on disappearance of fault)
977 | RM35ATL0MW | Complementary | temperature probe type | Pt 100 - 3-wire
978 | RM35ATL0MW | Complementary | installed device | Pt 100 probe cable length <= 10 m
979 | RM35ATL0MW | Complementary | marking | CE : EMC 89/336/EEC CE : 73/23/EEC
980 | RM35ATL0MW | Complementary | overvoltage category | III conforming to IEC 60664-1
981 | RM35ATL0MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
982 | RM35ATL0MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1
983 | RM35ATL0MW | Complementary | operating voltage tolerance | - 10 % + 10 % Un DC - 15 % + 10 % Un AC
984 | RM35ATL0MW | Complementary | supply frequency | 50/60 Hz +/- 10 %
985 | RM35ATL0MW | Complementary | insulation | Galvanic insulation between supply and measurement
986 | RM35ATL0MW | Complementary | operating position | Any position without derating
987 | RM35ATL0MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
988 | RM35ATL0MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
989 | RM35ATL0MW | Complementary | housing material | Self-extinguishing plastic
990 | RM35ATL0MW | Complementary | local signalling | 1 LED green for power ON 1 LED yellow for correct temperature (high R1) 1 LED yellow for correct temperature (low R2)
991 | RM35ATL0MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
992 | RM35ATL0MW | Complementary | electrical durability | 100000 cycles
993 | RM35ATL0MW | Complementary | mechanical durability | 30000000 cycles
994 | RM35ATL0MW | Complementary | operating rate | <= 360 operations/hour full load
995 | RM35ATL0MW | Environment | immunity to microbreaks | 10 ms
996 | RM35ATL0MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
997 | RM35ATL0MW | Environment | standards | IEC 60255-6 NF EN 60255-6
998 | RM35ATL0MW | Environment | product certifications | GOST GL C-Tick UL CSA
999 | RM35ATL0MW | Environment | ambient air temperature for storage | -40…70 °C
1000 | RM35ATL0MW | Environment | ambient air temperature for operation | -20…50 °C
1001 | RM35ATL0MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1
1002 | RM35ATL0MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
1003 | RM35ATL0MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
1004 | RM35ATL0MW | Environment | pollution degree | 3 conforming to IEC 60664-1
1005 | RM35ATL0MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
1006 | RM35ATL0MW | Environment | non-dissipating shock wave | 4 kV
1007 | RM35ATL0MW | Offer Sustainability | Sustainable offer status | Green Premium product
1008 | RM35ATL0MW | Offer Sustainability | REACh Regulation | REACh Declaration
1009 | RM35ATL0MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
1010 | RM35ATL0MW | Offer Sustainability | Mercury free | Yes
1011 | RM35ATL0MW | Offer Sustainability | RoHS exemption information | Yes
1012 | RM35ATL0MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
1013 | RM35ATL0MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
1014 | RM35ATL0MW | Offer Sustainability | Circularity Profile | End of Life Information
1015 | RM35ATL0MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
1016 | RM35ATL0MW | Contractual warranty | Warranty | 18 months
1017 | RM35ATR5MW | Main | range of product | Zelio Control
1018 | RM35ATR5MW | Main | product or component type | Modular measurement and control relays
1019 | RM35ATR5MW | Main | relay type | Temperature control relays
1020 | RM35ATR5MW | Main | product specific application | For elevator machine rooms and 3-phase supplies
1021 | RM35ATR5MW | Main | relay name | RM35AT
1022 | RM35ATR5MW | Main | relay monitored parameters | Overtemperature: 34...46°C Undertemperature: -1...11°C
1023 | RM35ATR5MW | Main | time delay range | 0.1...10 s adjustable delay (tolerance: 0...10 % of the full scale value)
1024 | RM35ATR5MW | Main | switching capacity in VA | 1250 VA
1025 | RM35ATR5MW | Main | minimum switching current | 10 mA at 5 V DC
1026 | RM35ATR5MW | Main | maximum power consumption in VA | 3.5 VA AC
1027 | RM35ATR5MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
1028 | RM35ATR5MW | Complementary | reset time | 8 s
1029 | RM35ATR5MW | Complementary | maximum switching voltage | 250 V AC/DC
1030 | RM35ATR5MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC
1031 | RM35ATR5MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC
1032 | RM35ATR5MW | Complementary | supply voltage limits | 20.4…264 V AC 21.6…264 V DC
1033 | RM35ATR5MW | Complementary | maximum power consumption in W | 0.6 W DC
1034 | RM35ATR5MW | Complementary | resistance across terminals | 1.33 kOhm at temperature
1035 | RM35ATR5MW | Complementary | width | 35 mm
1036 | RM35ATR5MW | Complementary | output contacts | 2 NO
1037 | RM35ATR5MW | Complementary | contacts material | Cadmium free
1038 | RM35ATR5MW | Complementary | nominal output current | 5 A
1039 | RM35ATR5MW | Complementary | delay at power up | 0.2 s
1040 | RM35ATR5MW | Complementary | measurement accuracy | +/- 2 °C
1041 | RM35ATR5MW | Complementary | response time | <= 3.5 s + Tt (in case of temperature fault) <= 3.5 s (on disappearance of fault)
1042 | RM35ATR5MW | Complementary | temperature probe type | Pt 100 - 3-wire
1043 | RM35ATR5MW | Complementary | installed device | Pt 100 probe cable length <= 10 m
1044 | RM35ATR5MW | Complementary | marking | CE : EMC 89/336/EEC CE : 73/23/EEC
1045 | RM35ATR5MW | Complementary | overvoltage category | III conforming to IEC 60664-1
1046 | RM35ATR5MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
1047 | RM35ATR5MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1
1048 | RM35ATR5MW | Complementary | operating voltage tolerance | - 10 % + 10 % Un DC - 15 % + 10 % Un AC
1049 | RM35ATR5MW | Complementary | supply frequency | 50/60 Hz +/- 10 %
1050 | RM35ATR5MW | Complementary | insulation | Galvanic insulation between supply and measurement
1051 | RM35ATR5MW | Complementary | operating position | Any position without derating
1052 | RM35ATR5MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
1053 | RM35ATR5MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
1054 | RM35ATR5MW | Complementary | housing material | Self-extinguishing plastic
1055 | RM35ATR5MW | Complementary | local signalling | 1 LED green for power ON 1 LED yellow for correct temperature (high R1) 1 LED yellow for correct temperature (low R2)
1056 | RM35ATR5MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
1057 | RM35ATR5MW | Complementary | electrical durability | 100000 cycles
1058 | RM35ATR5MW | Complementary | mechanical durability | 30000000 cycles
1059 | RM35ATR5MW | Complementary | operating rate | <= 360 operations/hour full load
1060 | RM35ATR5MW | Environment | immunity to microbreaks | 10 ms
1061 | RM35ATR5MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
1062 | RM35ATR5MW | Environment | standards | IEC 60255-6 NF EN 60255-6
1063 | RM35ATR5MW | Environment | product certifications | GL GOST C-Tick CSA UL
1064 | RM35ATR5MW | Environment | ambient air temperature for storage | -40…70 °C
1065 | RM35ATR5MW | Environment | ambient air temperature for operation | -20…50 °C
1066 | RM35ATR5MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1
1067 | RM35ATR5MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
1068 | RM35ATR5MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
1069 | RM35ATR5MW | Environment | pollution degree | 3 conforming to IEC 60664-1
1070 | RM35ATR5MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
1071 | RM35ATR5MW | Environment | non-dissipating shock wave | 4 kV
1072 | RM35ATR5MW | Offer Sustainability | Sustainable offer status | Green Premium product
1073 | RM35ATR5MW | Offer Sustainability | REACh Regulation | REACh Declaration
1074 | RM35ATR5MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
1075 | RM35ATR5MW | Offer Sustainability | Mercury free | Yes
1076 | RM35ATR5MW | Offer Sustainability | RoHS exemption information | Yes
1077 | RM35ATR5MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
1078 | RM35ATR5MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
1079 | RM35ATR5MW | Offer Sustainability | Circularity Profile | End of Life Information
1080 | RM35ATR5MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
1081 | RM35ATR5MW | Contractual warranty | Warranty | 18 months
1082 | RM35ATW5MW | Main | range of product | Zelio Control
1083 | RM35ATW5MW | Main | product or component type | Modular measurement and control relays
1084 | RM35ATW5MW | Main | relay type | Temperature control relays
1085 | RM35ATW5MW | Main | product specific application | For elevator machine rooms and 3-phase supplies
1086 | RM35ATW5MW | Main | relay name | RM35AT
1087 | RM35ATW5MW | Main | relay monitored parameters | Phase sequence Phase failure detection Undertemperature: -1...11°C Overtemperature: 34...46°C
1088 | RM35ATW5MW | Main | time delay range | 0.1...10 s adjustable delay (tolerance: 0...10 % of the full scale value)
1089 | RM35ATW5MW | Main | switching capacity in VA | 1250 VA
1090 | RM35ATW5MW | Main | minimum switching current | 10 mA at 5 V DC
1091 | RM35ATW5MW | Main | maximum power consumption in VA | 3.5 VA AC
1092 | RM35ATW5MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
1093 | RM35ATW5MW | Complementary | reset time | 8 s
1094 | RM35ATW5MW | Complementary | maximum switching voltage | 250 V AC/DC
1095 | RM35ATW5MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC
1096 | RM35ATW5MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC
1097 | RM35ATW5MW | Complementary | supply voltage limits | 20.4…264 V AC 21.6…264 V DC
1098 | RM35ATW5MW | Complementary | maximum power consumption in W | 0.6 W DC
1099 | RM35ATW5MW | Complementary | resistance across terminals | 600 kOhm at 3-phase 1.33 kOhm at temperature
1100 | RM35ATW5MW | Complementary | width | 35 mm
1101 | RM35ATW5MW | Complementary | output contacts | 2 NO
1102 | RM35ATW5MW | Complementary | contacts material | Cadmium free
1103 | RM35ATW5MW | Complementary | nominal output current | 5 A
1104 | RM35ATW5MW | Complementary | delay at power up | 0.2 s
1105 | RM35ATW5MW | Complementary | measurement accuracy | +/- 2 °C
1106 | RM35ATW5MW | Complementary | response time | <= 3.5 s + Tt (in case of temperature fault) 500 ms (in case of 3-phase fault) 500 ms (on disappearance of fault)
1107 | RM35ATW5MW | Complementary | temperature probe type | Pt 100 - 3-wire
1108 | RM35ATW5MW | Complementary | installed device | Pt 100 probe cable length <= 10 m
1109 | RM35ATW5MW | Complementary | marking | CE : EMC 89/336/EEC CE : 73/23/EEC
1110 | RM35ATW5MW | Complementary | overvoltage category | III conforming to IEC 60664-1
1111 | RM35ATW5MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
1112 | RM35ATW5MW | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
1113 | RM35ATW5MW | Complementary | operating voltage tolerance | - 10 % + 10 % Un DC - 15 % + 10 % Un AC
1114 | RM35ATW5MW | Complementary | supply frequency | 50/60 Hz +/- 10 %
1115 | RM35ATW5MW | Complementary | operating position | Any position without derating
1116 | RM35ATW5MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
1117 | RM35ATW5MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
1118 | RM35ATW5MW | Complementary | housing material | Self-extinguishing plastic
1119 | RM35ATW5MW | Complementary | local signalling | 1 LED green for power ON 1 LED yellow for correct temperature (high R1)/(low R2) 1 LED yellow for phases of relay
1120 | RM35ATW5MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
1121 | RM35ATW5MW | Complementary | electrical durability | 100000 cycles
1122 | RM35ATW5MW | Complementary | mechanical durability | 30000000 cycles
1123 | RM35ATW5MW | Complementary | operating rate | <= 360 operations/hour full load
1124 | RM35ATW5MW | Environment | immunity to microbreaks | 10 ms
1125 | RM35ATW5MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
1126 | RM35ATW5MW | Environment | standards | NF EN 60255-6 IEC 60255-6
1127 | RM35ATW5MW | Environment | product certifications | GL UL C-Tick CSA GOST
1128 | RM35ATW5MW | Environment | ambient air temperature for storage | -40…70 °C
1129 | RM35ATW5MW | Environment | ambient air temperature for operation | -20…50 °C
1130 | RM35ATW5MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1
1131 | RM35ATW5MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
1132 | RM35ATW5MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
1133 | RM35ATW5MW | Environment | pollution degree | 3 conforming to IEC 60664-1
1134 | RM35ATW5MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
1135 | RM35ATW5MW | Environment | non-dissipating shock wave | 4 kV
1136 | RM35ATW5MW | Offer Sustainability | Sustainable offer status | Green Premium product
1137 | RM35ATW5MW | Offer Sustainability | REACh Regulation | REACh Declaration
1138 | RM35ATW5MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
1139 | RM35ATW5MW | Offer Sustainability | Mercury free | Yes
1140 | RM35ATW5MW | Offer Sustainability | RoHS exemption information | Yes
1141 | RM35ATW5MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
1142 | RM35ATW5MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
1143 | RM35ATW5MW | Offer Sustainability | Circularity Profile | End of Life Information
1144 | RM35ATW5MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
1145 | RM35ATW5MW | Contractual warranty | Warranty | 18 months
1146 | RM35BA10 | Main | range of product | Zelio Control
1147 | RM35BA10 | Main | product or component type | Modular measurement and control relays
1148 | RM35BA10 | Main | relay type | Pump control relays
1149 | RM35BA10 | Main | product specific application | For 3-phase and single-phase pump
1150 | RM35BA10 | Main | relay name | RM35BA
1151 | RM35BA10 | Main | relay monitored parameters | Overcurrent and undercurrent control Phase sequence on 3-phase supply Phase failure on 3-phase supply
1152 | RM35BA10 | Main | time delay type | Adjustable 1...60 s, +/- 10 % Ti on energisation Fixed 0.3 s reset on terminal Y2 Adjustable 0.1...10 s, +/- 10 % Tt on crossing the threshold
1153 | RM35BA10 | Main | switching capacity in VA | 1250 VA
1154 | RM35BA10 | Main | minimum switching current | 10 mA at 5 V DC
1155 | RM35BA10 | Main | maximum switching current | 5 A AC/DC
1156 | RM35BA10 | Main | maximum power consumption in VA | 5 VA AC
1157 | RM35BA10 | Main | measurement range | 1...10 A AC
1158 | RM35BA10 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
1159 | RM35BA10 | Complementary | reset time | 2000 ms
1160 | RM35BA10 | Complementary | maximum switching voltage | 250 V AC/DC
1161 | RM35BA10 | Complementary | [Un] rated nominal voltage | 208...480 V AC 3 phases 230 V AC single phase
1162 | RM35BA10 | Complementary | [Un] rated nominal voltage | 208...480 V AC 3 phases 230 V AC 1 phase
1163 | RM35BA10 | Complementary | supply voltage limits | 183…528 V AC
1164 | RM35BA10 | Complementary | operating voltage tolerance | - 15 % + 10 % Un
1165 | RM35BA10 | Complementary | resistance across terminals | 0.01 Ohm at E1-L2 terminals
1166 | RM35BA10 | Complementary | width | 35 mm
1167 | RM35BA10 | Complementary | output contacts | 1 C/O
1168 | RM35BA10 | Complementary | nominal output current | 5 A
1169 | RM35BA10 | Complementary | maximum measuring cycle | 140 ms as true rms value
1170 | RM35BA10 | Complementary | delay at power up | 0.5 s
1171 | RM35BA10 | Complementary | hysteresis | 5 % of threshold
1172 | RM35BA10 | Complementary | measurement accuracy | +/- 10 % of the full scale value
1173 | RM35BA10 | Complementary | repeat accuracy | +/- 1 % for input and measurement circuit +/- 1 % for time delay
1174 | RM35BA10 | Complementary | measurement error | 1 % by volt over the whole range +/- 0.05 %/°C
1175 | RM35BA10 | Complementary | response time | < 300 ms (in the event of a fault)
1176 | RM35BA10 | Complementary | overload input current | 11 A permanent at 25 °C E1-L2 terminals 50 A non repetitive < 1 s at 25 °C E1-L2 terminals
1177 | RM35BA10 | Complementary | marking | CE : EMC 89/336/EEC CE : 73/23/EEC
1178 | RM35BA10 | Complementary | overvoltage category | III conforming to IEC 60664-1
1179 | RM35BA10 | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to 60664-1
1180 | RM35BA10 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
1181 | RM35BA10 | Complementary | supply frequency | 50/60 Hz +/- 10 %
1182 | RM35BA10 | Complementary | operating position | Any position
1183 | RM35BA10 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
1184 | RM35BA10 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
1185 | RM35BA10 | Complementary | housing material | Self-extinguishing plastic
1186 | RM35BA10 | Complementary | status LED | 1 LED green for power ON 1 LED yellow for fault 1 LED yellow for relay ON
1187 | RM35BA10 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
1188 | RM35BA10 | Complementary | electrical durability | 100000 cycles
1189 | RM35BA10 | Complementary | mechanical durability | 30000000 cycles
1190 | RM35BA10 | Complementary | operating rate | <= 360 operations/hour full load
1191 | RM35BA10 | Environment | immunity to microbreaks | 500 ms
1192 | RM35BA10 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
1193 | RM35BA10 | Environment | standards | EN/IEC 60255-6
1194 | RM35BA10 | Environment | product certifications | C-Tick CSA GOST UL GL
1195 | RM35BA10 | Environment | ambient air temperature for storage | -40…70 °C
1196 | RM35BA10 | Environment | ambient air temperature for operation | -20…50 °C
1197 | RM35BA10 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
1198 | RM35BA10 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1
1199 | RM35BA10 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
1200 | RM35BA10 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
1201 | RM35BA10 | Environment | pollution degree | 3 conforming to IEC 60664-1
1202 | RM35BA10 | Environment | dielectric strength | 2 kV AC 50 Hz (shock wave 4 kV)
1203 | RM35BA10 | Offer Sustainability | Sustainable offer status | Green Premium product
1204 | RM35BA10 | Offer Sustainability | REACh Regulation | REACh Declaration
1205 | RM35BA10 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
1206 | RM35BA10 | Offer Sustainability | Mercury free | Yes
1207 | RM35BA10 | Offer Sustainability | RoHS exemption information | Yes
1208 | RM35BA10 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
1209 | RM35BA10 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
1210 | RM35BA10 | Offer Sustainability | Circularity Profile | End of Life Information
1211 | RM35BA10 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
1212 | RM35BA10 | Contractual warranty | Warranty | 18 months
1213 | RM35HZ21FM | Main | range of product | Zelio Control
1214 | RM35HZ21FM | Main | product or component type | Modular measurement and control relays
1215 | RM35HZ21FM | Main | relay type | Frequency control relays
1216 | RM35HZ21FM | Main | relay name | RM35HZ21FM
1217 | RM35HZ21FM | Main | relay monitored parameters | Overfrequency and underfrequency 50 or 60 Hz
1218 | RM35HZ21FM | Main | time delay type | Adjustable 0.1...10 s, +/- 10 % on crossing the threshold
1219 | RM35HZ21FM | Main | switching capacity in VA | 1250 VA
1220 | RM35HZ21FM | Main | minimum switching current | 10 mA at 5 V DC
1221 | RM35HZ21FM | Main | maximum power consumption in VA | 6 VA AC
1222 | RM35HZ21FM | Main | measurement range | 40...70 Hz frequency
1223 | RM35HZ21FM | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
1224 | RM35HZ21FM | Complementary | reset time | 2000 ms time delay
1225 | RM35HZ21FM | Complementary | maximum switching voltage | 250 V AC/DC
1226 | RM35HZ21FM | Complementary | [Us] rated supply voltage | 120...277 V AC
1227 | RM35HZ21FM | Complementary | [Us] rated supply voltage | 120...277 V AC
1228 | RM35HZ21FM | Complementary | supply voltage limits | 102…308 V AC
1229 | RM35HZ21FM | Complementary | control circuit frequency | 40...70 Hz
1230 | RM35HZ21FM | Complementary | width | 35 mm
1231 | RM35HZ21FM | Complementary | output contacts | 1 C/O + 1 C/O
1232 | RM35HZ21FM | Complementary | contacts material | Cadmium free
1233 | RM35HZ21FM | Complementary | nominal output current | 5 A
1234 | RM35HZ21FM | Complementary | maximum input frequency | 70 Hz
1235 | RM35HZ21FM | Complementary | maximum measuring cycle | 200 ms measurement cycle as true rms value
1236 | RM35HZ21FM | Complementary | delay at power up | 0.5 s
1237 | RM35HZ21FM | Complementary | hysteresis | 0.3 % fixed
1238 | RM35HZ21FM | Complementary | measurement accuracy | +/- 10 % of the full scale value in input +/- 10 % of the full scale value in time delay
1239 | RM35HZ21FM | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 0.5 % for time delay
1240 | RM35HZ21FM | Complementary | measurement error | +/- 0.05 %/°C with temperature variation < +/- 1 % over the whole range with voltage variation
1241 | RM35HZ21FM | Complementary | threshold setting | -2...10 Hz -10...2 Hz
1242 | RM35HZ21FM | Complementary | marking | CE : 73/23/EEC CE : EMC 89/336/EEC
1243 | RM35HZ21FM | Complementary | overvoltage category | III conforming to IEC 60664-1
1244 | RM35HZ21FM | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
1245 | RM35HZ21FM | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
1246 | RM35HZ21FM | Complementary | operating voltage tolerance | - 15 % + 10 % Un
1247 | RM35HZ21FM | Complementary | supply frequency | 50/60 Hz +/- 10 %
1248 | RM35HZ21FM | Complementary | insulation | No galvanic insulation between supply and measurement
1249 | RM35HZ21FM | Complementary | operating position | Any position without derating
1250 | RM35HZ21FM | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
1251 | RM35HZ21FM | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
1252 | RM35HZ21FM | Complementary | housing material | Self-extinguishing plastic
1253 | RM35HZ21FM | Complementary | local signalling | 1 LED green for power ON 1 LED yellow for correct frequency (high R1) 1 LED yellow for correct frequency (low R2)
1254 | RM35HZ21FM | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
1255 | RM35HZ21FM | Complementary | electrical durability | 100000 cycles
1256 | RM35HZ21FM | Complementary | mechanical durability | 30000000 cycles
1257 | RM35HZ21FM | Complementary | operating rate | <= 360 operations/hour full load
1258 | RM35HZ21FM | Environment | immunity to microbreaks | 10 ms
1259 | RM35HZ21FM | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
1260 | RM35HZ21FM | Environment | standards | IEC 60255-6 NF EN 60255-6
1261 | RM35HZ21FM | Environment | product certifications | GL UL CSA C-Tick GOST
1262 | RM35HZ21FM | Environment | ambient air temperature for storage | -40…70 °C
1263 | RM35HZ21FM | Environment | ambient air temperature for operation | -20…50 °C
1264 | RM35HZ21FM | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
1265 | RM35HZ21FM | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1
1266 | RM35HZ21FM | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
1267 | RM35HZ21FM | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
1268 | RM35HZ21FM | Environment | pollution degree | 3 conforming to IEC 60664-1
1269 | RM35HZ21FM | Environment | dielectric test voltage | 2 kV AC 50 Hz
1270 | RM35HZ21FM | Environment | non-dissipating shock wave | 4 kV
1271 | RM35HZ21FM | Offer Sustainability | Sustainable offer status | Green Premium product
1272 | RM35HZ21FM | Offer Sustainability | REACh Regulation | REACh Declaration
1273 | RM35HZ21FM | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
1274 | RM35HZ21FM | Offer Sustainability | Mercury free | Yes
1275 | RM35HZ21FM | Offer Sustainability | RoHS exemption information | Yes
1276 | RM35HZ21FM | Offer Sustainability | China RoHS Regulation | China RoHS declaration
1277 | RM35HZ21FM | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
1278 | RM35HZ21FM | Offer Sustainability | Circularity Profile | End of Life Information
1279 | RM35HZ21FM | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
1280 | RM35HZ21FM | Contractual warranty | Warranty | 18 months
1281 | RM35JA31MW | Main | range of product | Zelio Control
1282 | RM35JA31MW | Main | product or component type | Modular measurement and control relays
1283 | RM35JA31MW | Main | relay type | Current control relay
1284 | RM35JA31MW | Main | relay name | RM35JA
1285 | RM35JA31MW | Main | relay monitored parameters | Overcurrent or undercurrent in window mode Overcurrent or undercurrent detection
1286 | RM35JA31MW | Main | time delay | Adjustable 1...20 s, 0 + 10 % on energisation Ti Adjustable 0.3...30 s, 0 + 10 % on crossing the threshold Tt
1287 | RM35JA31MW | Main | switching capacity in VA | 1250 VA
1288 | RM35JA31MW | Main | minimum switching current | 10 mA at 5 V DC
1289 | RM35JA31MW | Main | maximum switching current | 5 A AC
1290 | RM35JA31MW | Main | maximum power consumption in VA | 3.5 VA AC
1291 | RM35JA31MW | Main | measurement range | 10...100 mA E2-M terminals 2...20 mA E1-M terminals 2...500 mA current 50...500 mA E3-M terminals
1292 | RM35JA31MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
1293 | RM35JA31MW | Complementary | reset time | 1500 ms time delay
1294 | RM35JA31MW | Complementary | maximum switching voltage | 250 V AC
1295 | RM35JA31MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
1296 | RM35JA31MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
1297 | RM35JA31MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
1298 | RM35JA31MW | Complementary | maximum power consumption in W | 0.6 W DC
1299 | RM35JA31MW | Complementary | control circuit frequency | 40...70 Hz +/- 10 %
1300 | RM35JA31MW | Complementary | resistance across terminals | 1 Ohm at E2-M terminals 5 Ohm at E1-M terminals 0.2 Ohm at E3-M terminals
1301 | RM35JA31MW | Complementary | output contacts | 2 C/O
1302 | RM35JA31MW | Complementary | nominal output current | 5 A
1303 | RM35JA31MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value
1304 | RM35JA31MW | Complementary | hysteresis | 5…50 % of threshold setting
1305 | RM35JA31MW | Complementary | delay at power up | 0.3 s
1306 | RM35JA31MW | Complementary | measurement accuracy | +/- 10 % of the full scale value
1307 | RM35JA31MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay
1308 | RM35JA31MW | Complementary | measurement error | 0.05 %/°C with temperature variation 1 by volt over the whole range with voltage variation
1309 | RM35JA31MW | Complementary | polarity | No DC
1310 | RM35JA31MW | Complementary | threshold setting | 10...100 %
1311 | RM35JA31MW | Complementary | marking | CE : EMC 89/336/EEC CE : 73/23/EEC
1312 | RM35JA31MW | Complementary | overvoltage category | III conforming to IEC 60664-1
1313 | RM35JA31MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
1314 | RM35JA31MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1
1315 | RM35JA31MW | Complementary | operating position | Any position without derating
1316 | RM35JA31MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
1317 | RM35JA31MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
1318 | RM35JA31MW | Complementary | housing material | Self-extinguishing plastic
1319 | RM35JA31MW | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
1320 | RM35JA31MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
1321 | RM35JA31MW | Complementary | electrical durability | 100000 cycles
1322 | RM35JA31MW | Complementary | mechanical durability | 30000000 cycles
1323 | RM35JA31MW | Complementary | operating rate | <= 360 operations/hour full load
1324 | RM35JA31MW | Complementary | safety reliability data | MTTFd = 296.8 years B10d = 270000
1325 | RM35JA31MW | Complementary | contacts material | Cadmium free
1326 | RM35JA31MW | Complementary | width | 35 mm
1327 | RM35JA31MW | Complementary | net weight | 0.13 kg
1328 | RM35JA31MW | Environment | immunity to microbreaks | 50 ms
1329 | RM35JA31MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
1330 | RM35JA31MW | Environment | standards | EN/IEC 60255-6
1331 | RM35JA31MW | Environment | product certifications | GL CSA GOST UL C-Tick
1332 | RM35JA31MW | Environment | ambient air temperature for storage | -40…70 °C
1333 | RM35JA31MW | Environment | ambient air temperature for operation | -20…50 °C
1334 | RM35JA31MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
1335 | RM35JA31MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
1336 | RM35JA31MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
1337 | RM35JA31MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
1338 | RM35JA31MW | Environment | pollution degree | 3 conforming to IEC 60664-1
1339 | RM35JA31MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
1340 | RM35JA31MW | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
1341 | RM35JA31MW | Offer Sustainability | Sustainable offer status | Green Premium product
1342 | RM35JA31MW | Offer Sustainability | REACh Regulation | REACh Declaration
1343 | RM35JA31MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
1344 | RM35JA31MW | Offer Sustainability | Mercury free | Yes
1345 | RM35JA31MW | Offer Sustainability | RoHS exemption information | Yes
1346 | RM35JA31MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
1347 | RM35JA31MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
1348 | RM35JA31MW | Offer Sustainability | Circularity Profile | End of Life Information
1349 | RM35JA31MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
1350 | RM35JA31MW | Contractual warranty | Warranty | 18 months
1351 | RM35JA32MW | Main | range of product | Zelio Control
1352 | RM35JA32MW | Main | product or component type | Modular measurement and control relays
1353 | RM35JA32MW | Main | relay type | Current control relay
1354 | RM35JA32MW | Main | relay name | RM35JA
1355 | RM35JA32MW | Main | relay monitored parameters | Overcurrent or undercurrent detection
1356 | RM35JA32MW | Main | time delay | Adjustable 1...20 s, 0 + 10 % on energisation Ti Adjustable 0.3...30 s, 0 + 10 % on crossing the threshold Tt
1357 | RM35JA32MW | Main | switching capacity in VA | 1250 VA
1358 | RM35JA32MW | Main | minimum switching current | 10 mA at 5 V DC
1359 | RM35JA32MW | Main | maximum switching current | 5 A AC/DC
1360 | RM35JA32MW | Main | maximum power consumption in VA | 3.5 VA AC
1361 | RM35JA32MW | Main | measurement range | 0.15...1.5 A E1-M terminals 0.5...5 A E2-M terminals 1.5...15 A E3-M terminals 150 mA...15 A current
1362 | RM35JA32MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
1363 | RM35JA32MW | Complementary | reset time | 1500 ms time delay
1364 | RM35JA32MW | Complementary | maximum switching voltage | 250 V AC/DC
1365 | RM35JA32MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
1366 | RM35JA32MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
1367 | RM35JA32MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
1368 | RM35JA32MW | Complementary | maximum power consumption in W | 0.6 W DC
1369 | RM35JA32MW | Complementary | control circuit frequency | 40...70 Hz +/- 10 %
1370 | RM35JA32MW | Complementary | resistance across terminals | 0.005 Ohm at E3-M terminals 0.015 Ohm at E2-M terminals 0.05 Ohm at E1-M terminals
1371 | RM35JA32MW | Complementary | output contacts | 2 C/O
1372 | RM35JA32MW | Complementary | nominal output current | 5 A
1373 | RM35JA32MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value
1374 | RM35JA32MW | Complementary | hysteresis | 5…50 % of threshold setting
1375 | RM35JA32MW | Complementary | delay at power up | 0.3 s
1376 | RM35JA32MW | Complementary | measurement accuracy | +/- 10 % of the full scale value
1377 | RM35JA32MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay
1378 | RM35JA32MW | Complementary | measurement error | 0.05 %/°C with temperature variation 1 by volt over the whole range with voltage variation
1379 | RM35JA32MW | Complementary | polarity | No DC
1380 | RM35JA32MW | Complementary | threshold setting | 10...100 %
1381 | RM35JA32MW | Complementary | marking | CE : EMC 89/336/EEC CE : 73/23/EEC
1382 | RM35JA32MW | Complementary | overvoltage category | III conforming to IEC 60664-1
1383 | RM35JA32MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
1384 | RM35JA32MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1
1385 | RM35JA32MW | Complementary | operating position | Any position without derating
1386 | RM35JA32MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
1387 | RM35JA32MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
1388 | RM35JA32MW | Complementary | housing material | Self-extinguishing plastic
1389 | RM35JA32MW | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
1390 | RM35JA32MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
1391 | RM35JA32MW | Complementary | electrical durability | 100000 cycles
1392 | RM35JA32MW | Complementary | mechanical durability | 30000000 cycles
1393 | RM35JA32MW | Complementary | operating rate | <= 360 operations/hour full load
1394 | RM35JA32MW | Complementary | safety reliability data | MTTFd = 296.8 years B10d = 270000
1395 | RM35JA32MW | Complementary | contacts material | Cadmium free
1396 | RM35JA32MW | Complementary | width | 35 mm
1397 | RM35JA32MW | Complementary | net weight | 0.13 kg
1398 | RM35JA32MW | Environment | immunity to microbreaks | 50 ms
1399 | RM35JA32MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
1400 | RM35JA32MW | Environment | standards | EN/IEC 60255-6
1401 | RM35JA32MW | Environment | product certifications | GL UL GOST C-Tick CSA
1402 | RM35JA32MW | Environment | ambient air temperature for storage | -40…70 °C
1403 | RM35JA32MW | Environment | ambient air temperature for operation | -20…50 °C
1404 | RM35JA32MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
1405 | RM35JA32MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
1406 | RM35JA32MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
1407 | RM35JA32MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
1408 | RM35JA32MW | Environment | pollution degree | 3 conforming to IEC 60664-1
1409 | RM35JA32MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
1410 | RM35JA32MW | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
1411 | RM35JA32MW | Offer Sustainability | Sustainable offer status | Green Premium product
1412 | RM35JA32MW | Offer Sustainability | REACh Regulation | REACh Declaration
1413 | RM35JA32MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
1414 | RM35JA32MW | Offer Sustainability | Mercury free | Yes
1415 | RM35JA32MW | Offer Sustainability | RoHS exemption information | Yes
1416 | RM35JA32MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
1417 | RM35JA32MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
1418 | RM35JA32MW | Offer Sustainability | Circularity Profile | End of Life Information
1419 | RM35JA32MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
1420 | RM35JA32MW | Contractual warranty | Warranty | 18 months
1421 | RM35LM33MW | Main | range of product | Zelio Control
1422 | RM35LM33MW | Main | product or component type | Modular measurement and control relays
1423 | RM35LM33MW | Main | relay type | Level control relay
1424 | RM35LM33MW | Main | relay name | RM35L
1425 | RM35LM33MW | Main | relay monitored parameters | Detection by resistive probes
1426 | RM35LM33MW | Main | time delay | Adjustable 0.1...5 s, +/- 10 %
1427 | RM35LM33MW | Main | switching capacity in VA | 1250 VA
1428 | RM35LM33MW | Main | minimum switching current | 10 mA at 5 V DC
1429 | RM35LM33MW | Main | maximum switching current | 5 A AC/DC
1430 | RM35LM33MW | Main | power consumption | 5 VA AC
1431 | RM35LM33MW | Main | measurement range | 250 Ohm...1 MOhm
1432 | RM35LM33MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
1433 | RM35LM33MW | Complementary | reset time | 1750 ms
1434 | RM35LM33MW | Complementary | maximum switching voltage | 250 V AC/DC
1435 | RM35LM33MW | Complementary | [Un] rated nominal voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
1436 | RM35LM33MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
1437 | RM35LM33MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
1438 | RM35LM33MW | Complementary | power consumption | 1.5 W DC
1439 | RM35LM33MW | Complementary | output contacts | 2 C/O
1440 | RM35LM33MW | Complementary | nominal output current | 5 A
1441 | RM35LM33MW | Complementary | delay at power up | 0.6 s
1442 | RM35LM33MW | Complementary | measurement accuracy | +/- 10 % of the full scale value +/- 20 % for the HS range
1443 | RM35LM33MW | Complementary | repeat accuracy | +/- 2 % for time delay
1444 | RM35LM33MW | Complementary | measurement error | 0.5 %/°C with temperature variation
1445 | RM35LM33MW | Complementary | maximum cable distance between devices | 100 m
1446 | RM35LM33MW | Complementary | sensitivity scale | 0.25...5 kOhm LS (Low Sensitivity) 5...100 kOhm St (Standard Sensitivity) 50...1000 kOhm HS (High Sensitivity)
1447 | RM35LM33MW | Complementary | sensitivity adjustment | 5…100 %
1448 | RM35LM33MW | Complementary | maximum supply current for sensors | 1 mA
1449 | RM35LM33MW | Complementary | cable capacitance | 1 nF at HS (High Sensitivity) for probe cable 2.2 nF at St (Standard Sensitivity) for probe cable 4.7 nF at LS (Low Sensitivity)
1450 | RM35LM33MW | Complementary | marking | CE : 73/23/EEC CE : EMC 89/336/EEC
1451 | RM35LM33MW | Complementary | overvoltage category | III conforming to IEC 60664-1
1452 | RM35LM33MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
1453 | RM35LM33MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1
1454 | RM35LM33MW | Complementary | operating position | Any position without derating
1455 | RM35LM33MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end
1456 | RM35LM33MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
1457 | RM35LM33MW | Complementary | housing material | Self-extinguishing plastic
1458 | RM35LM33MW | Complementary | local signalling | LED (yellow) for relay ON LED (green) for power ON LED (yellow) for timer ON
1459 | RM35LM33MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
1460 | RM35LM33MW | Complementary | electrical durability | 100000 cycles
1461 | RM35LM33MW | Complementary | mechanical durability | 30000000 cycles
1462 | RM35LM33MW | Complementary | operating rate | <= 360 operations/hour full load
1463 | RM35LM33MW | Complementary | safety reliability data | B10d = 170000 MTTFd = 182.6 years
1464 | RM35LM33MW | Complementary | width | 35 mm
1465 | RM35LM33MW | Environment | immunity to microbreaks | 100 ms DC 90 ms AC
1466 | RM35LM33MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
1467 | RM35LM33MW | Environment | standards | EN/IEC 60255-6
1468 | RM35LM33MW | Environment | product certifications | CSA GL UL C-Tick GOST
1469 | RM35LM33MW | Environment | ambient air temperature for storage | -40…70 °C
1470 | RM35LM33MW | Environment | ambient air temperature for operation | -20…50 °C
1471 | RM35LM33MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
1472 | RM35LM33MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
1473 | RM35LM33MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
1474 | RM35LM33MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
1475 | RM35LM33MW | Environment | pollution degree | 3 conforming to IEC 60664-1
1476 | RM35LM33MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
1477 | RM35LM33MW | Offer Sustainability | Sustainable offer status | Green Premium product
1478 | RM35LM33MW | Offer Sustainability | REACh Regulation | REACh Declaration
1479 | RM35LM33MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
1480 | RM35LM33MW | Offer Sustainability | Mercury free | Yes
1481 | RM35LM33MW | Offer Sustainability | RoHS exemption information | Yes
1482 | RM35LM33MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
1483 | RM35LM33MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
1484 | RM35LM33MW | Offer Sustainability | Circularity Profile | End of Life Information
1485 | RM35LM33MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
1486 | RM35LM33MW | Contractual warranty | Warranty | 18 months
1487 | RM35LV14MW | Main | range of product | Zelio Control
1488 | RM35LV14MW | Main | product or component type | Modular measurement and control relays
1489 | RM35LV14MW | Main | relay type | Level control relay
1490 | RM35LV14MW | Main | relay name | RM35L
1491 | RM35LV14MW | Main | relay monitored parameters | Detection by discrete sensors
1492 | RM35LV14MW | Main | time delay | Adjustable 0.1...5 s, +/- 10 %
1493 | RM35LV14MW | Main | switching capacity in VA | 1250 VA
1494 | RM35LV14MW | Main | minimum switching current | 10 mA at 5 V DC
1495 | RM35LV14MW | Main | maximum switching current | 5 A AC/DC
1496 | RM35LV14MW | Main | power consumption | 5 VA AC
1497 | RM35LV14MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
1498 | RM35LV14MW | Complementary | reset time | 1000 ms 4000 ms
1499 | RM35LV14MW | Complementary | maximum switching voltage | 250 V AC/DC
1500 | RM35LV14MW | Complementary | [Un] rated nominal voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
1501 | RM35LV14MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
1502 | RM35LV14MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
1503 | RM35LV14MW | Complementary | power consumption | 1.5 W DC
1504 | RM35LV14MW | Complementary | output contacts | 1 C/O
1505 | RM35LV14MW | Complementary | nominal output current | 5 A
1506 | RM35LV14MW | Complementary | delay at power up | 0.5 s
1507 | RM35LV14MW | Complementary | measurement accuracy | +/- 10 % of the full scale value +/- 20 % for the HS range
1508 | RM35LV14MW | Complementary | repeat accuracy | +/- 2 % for time delay
1509 | RM35LV14MW | Complementary | measurement error | 0.5 %/°C with temperature variation
1510 | RM35LV14MW | Complementary | maximum cable distance between devices | 100 m
1511 | RM35LV14MW | Complementary | sensitivity adjustment | 5…100 %
1512 | RM35LV14MW | Complementary | maximum supply current for sensors | 40 mA
1513 | RM35LV14MW | Complementary | cable capacitance | 10 nF for probe cable
1514 | RM35LV14MW | Complementary | marking | CE : EMC 89/336/EEC CE : 73/23/EEC
1515 | RM35LV14MW | Complementary | overvoltage category | III conforming to IEC 60664-1
1516 | RM35LV14MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
1517 | RM35LV14MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1
1518 | RM35LV14MW | Complementary | operating position | Any position without derating
1519 | RM35LV14MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end
1520 | RM35LV14MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
1521 | RM35LV14MW | Complementary | housing material | Self-extinguishing plastic
1522 | RM35LV14MW | Complementary | local signalling | LED (yellow) for relay ON LED (green) for power ON LED (yellow) for timer ON
1523 | RM35LV14MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
1524 | RM35LV14MW | Complementary | electrical durability | 100000 cycles
1525 | RM35LV14MW | Complementary | mechanical durability | 30000000 cycles
1526 | RM35LV14MW | Complementary | operating rate | <= 360 operations/hour full load
1527 | RM35LV14MW | Complementary | safety reliability data | B10d = 170000 MTTFd = 182.6 years
1528 | RM35LV14MW | Complementary | width | 35 mm
1529 | RM35LV14MW | Environment | immunity to microbreaks | 100 ms DC 90 ms AC
1530 | RM35LV14MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
1531 | RM35LV14MW | Environment | standards | EN/IEC 60255-6
1532 | RM35LV14MW | Environment | product certifications | GOST CSA UL GL C-Tick
1533 | RM35LV14MW | Environment | ambient air temperature for storage | -40…70 °C
1534 | RM35LV14MW | Environment | ambient air temperature for operation | -20…50 °C
1535 | RM35LV14MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
1536 | RM35LV14MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
1537 | RM35LV14MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
1538 | RM35LV14MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
1539 | RM35LV14MW | Environment | pollution degree | 3 conforming to IEC 60664-1
1540 | RM35LV14MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
1541 | RM35LV14MW | Offer Sustainability | Sustainable offer status | Green Premium product
1542 | RM35LV14MW | Offer Sustainability | REACh Regulation | REACh Declaration
1543 | RM35LV14MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
1544 | RM35LV14MW | Offer Sustainability | Mercury free | Yes
1545 | RM35LV14MW | Offer Sustainability | RoHS exemption information | Yes
1546 | RM35LV14MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
1547 | RM35LV14MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
1548 | RM35LV14MW | Offer Sustainability | Circularity Profile | End of Life Information
1549 | RM35LV14MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
1550 | RM35LV14MW | Contractual warranty | Warranty | 18 months
1551 | RM35S0MW | Main | range of product | Zelio Control
1552 | RM35S0MW | Main | product or component type | Modular measurement and control relays
1553 | RM35S0MW | Main | relay type | Speed control relays
1554 | RM35S0MW | Main | relay name | RM35S
1555 | RM35S0MW | Main | relay monitored parameters | Overspeed Underspeed
1556 | RM35S0MW | Main | time delay range | 0.6...60 s adjustable on energisation delay (tolerance: 0...10 % of the full scale value)
1557 | RM35S0MW | Main | switching capacity in VA | 1250 VA
1558 | RM35S0MW | Main | minimum switching current | 10 mA at 5 V DC
1559 | RM35S0MW | Main | [Us] rated supply voltage | 24...240 V AC/DC
1560 | RM35S0MW | Main | maximum power consumption in VA | 5 VA AC
1561 | RM35S0MW | Main | measurement range | 0.05...0.5 s 0.5...5 min 1...10 min 1...10 s 0.5...5 s 0.1...1 s 0.1...1 min
1562 | RM35S0MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
1563 | RM35S0MW | Complementary | rest time in memory mode | 50 ms contact S2 in memory mode on time delay 1 s supply Un in memory mode on time delay
1564 | RM35S0MW | Complementary | maximum switching voltage | 250 V AC/DC
1565 | RM35S0MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
1566 | RM35S0MW | Complementary | maximum power consumption in W | 3 W DC
1567 | RM35S0MW | Complementary | width | 35 mm
1568 | RM35S0MW | Complementary | output contacts | 1 C/O
1569 | RM35S0MW | Complementary | contacts material | Cadmium free
1570 | RM35S0MW | Complementary | nominal output current | 5 A
1571 | RM35S0MW | Complementary | delay at power up | 0.05 s
1572 | RM35S0MW | Complementary | hysteresis | 5 % of threshold
1573 | RM35S0MW | Complementary | measurement accuracy | +/- 10 % of the full scale value
1574 | RM35S0MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 0.5 % for time delay
1575 | RM35S0MW | Complementary | measurement error | +/- 0.1 %/°C with temperature variation < +/- 1 % over the whole range with voltage variation
1576 | RM35S0MW | Complementary | input frequency | 0.0017…20 Hz
1577 | RM35S0MW | Complementary | response time | 15 ms max (on crossing the threshold)
1578 | RM35S0MW | Complementary | polarity | Reversible polarity on DC supply
1579 | RM35S0MW | Complementary | threshold setting | 10...100 %
1580 | RM35S0MW | Complementary | supply voltage for sensor | 11.5...12.5 V
1581 | RM35S0MW | Complementary | maximum supply current for sensors | 40 mA for < 24 V AC at 25 °C 40 mA for < 24 V DC at 25 °C 50 mA for 24...240 V AC 50 mA for 24...240 V DC
1582 | RM35S0MW | Complementary | impulse duration | >= 5 ms high state >= 5 ms low state
1583 | RM35S0MW | Complementary | input compatibility | 3-wire sensor (E1) PNP or NPN, 12 V, 50 mA NAMUR sensor (E2), 12 V, 1.5 kOhm Voltage input (E1), 0...30 V, 9.5 kOhm, high state >= 4.5 V low state <= 1 V Volt-free contact input (E1), 12 V, 9.5 kOhm
1584 | RM35S0MW | Complementary | marking | CE : EMC 89/336/EEC CE : 73/23/EEC
1585 | RM35S0MW | Complementary | overvoltage category | III conforming to IEC 60664-1
1586 | RM35S0MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
1587 | RM35S0MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1
1588 | RM35S0MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
1589 | RM35S0MW | Complementary | supply frequency | 50/60 Hz +/- 10 %
1590 | RM35S0MW | Complementary | operating position | Any position without derating
1591 | RM35S0MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
1592 | RM35S0MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
1593 | RM35S0MW | Complementary | housing material | Self-extinguishing plastic
1594 | RM35S0MW | Complementary | status LED | 1 LED green for power ON 1 LED yellow for inhibit 1 LED yellow for relay (R)
1595 | RM35S0MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
1596 | RM35S0MW | Complementary | electrical durability | 100000 cycles
1597 | RM35S0MW | Complementary | mechanical durability | 30000000 cycles
1598 | RM35S0MW | Complementary | operating rate | <= 360 operations/hour full load
1599 | RM35S0MW | Environment | immunity to microbreaks | 50 ms
1600 | RM35S0MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
1601 | RM35S0MW | Environment | standards | NF EN 60255-6 IEC 60255-6
1602 | RM35S0MW | Environment | product certifications | C-Tick GOST UL GL CSA
1603 | RM35S0MW | Environment | ambient air temperature for storage | -40…70 °C
1604 | RM35S0MW | Environment | ambient air temperature for operation | -20…50 °C
1605 | RM35S0MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
1606 | RM35S0MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1
1607 | RM35S0MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
1608 | RM35S0MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
1609 | RM35S0MW | Environment | pollution degree | 3 conforming to IEC 60664-1
1610 | RM35S0MW | Environment | dielectric test voltage | 2 kV AC 50 Hz
1611 | RM35S0MW | Environment | non-dissipating shock wave | 4 kV
1612 | RM35S0MW | Offer Sustainability | Sustainable offer status | Green Premium product
1613 | RM35S0MW | Offer Sustainability | REACh Regulation | REACh Declaration
1614 | RM35S0MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
1615 | RM35S0MW | Offer Sustainability | Mercury free | Yes
1616 | RM35S0MW | Offer Sustainability | RoHS exemption information | Yes
1617 | RM35S0MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
1618 | RM35S0MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
1619 | RM35S0MW | Offer Sustainability | Circularity Profile | End of Life Information
1620 | RM35S0MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
1621 | RM35S0MW | Contractual warranty | Warranty | 18 months
1622 | RM35TF30 | Main | range of product | Zelio Control
1623 | RM35TF30 | Main | product or component type | Modular measurement and control relays
1624 | RM35TF30 | Main | relay type | Multifunction control relay
1625 | RM35TF30 | Main | product specific application | For 3-phase supply
1626 | RM35TF30 | Main | relay name | RM35TF
1627 | RM35TF30 | Main | relay monitored parameters | Undervoltage and overvoltage in window mode Phase sequence Phase failure detection Asymmetry
1628 | RM35TF30 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value
1629 | RM35TF30 | Main | switching capacity in VA | 1250 VA
1630 | RM35TF30 | Main | measurement range | 208...480 V voltage AC
1631 | RM35TF30 | Complementary | reset time | 1500 ms at 480 V
1632 | RM35TF30 | Complementary | maximum switching voltage | 250 V AC 250 V DC
1633 | RM35TF30 | Complementary | minimum switching current | 10 mA at 5 V DC
1634 | RM35TF30 | Complementary | maximum switching current | 5 A AC 5 A DC
1635 | RM35TF30 | Complementary | supply voltage limits | 194…528 V AC, 3 phases
1636 | RM35TF30 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
1637 | RM35TF30 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
1638 | RM35TF30 | Complementary | voltage detection threshold | < 194 V
1639 | RM35TF30 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
1640 | RM35TF30 | Complementary | output contacts | 2 C/O
1641 | RM35TF30 | Complementary | nominal output current | 5 A
1642 | RM35TF30 | Complementary | measurement voltage limits | 176…528 V AC
1643 | RM35TF30 | Complementary | hysteresis | 2 %
1644 | RM35TF30 | Complementary | delay at power up | 650 ms
1645 | RM35TF30 | Complementary | maximum measuring cycle | 140 ms measurement cycle as true rms value
1646 | RM35TF30 | Complementary | threshold adjustment voltage | -20...-2 % in the range 380...480 V AC 2...20 % of Un selected -12...-2 % in the range 220 V AC +2...+20 % in the range 220...440 V AC +2...+10 % in the range 480 V AC
1647 | RM35TF30 | Complementary | voltage range | 220...480 V phase to phase
1648 | RM35TF30 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
1649 | RM35TF30 | Complementary | repeat accuracy | 0.3 % for time delay 0.5 % for input and measurement circuit
1650 | RM35TF30 | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
1651 | RM35TF30 | Complementary | response time | < 200 ms (in the event of a fault)
1652 | RM35TF30 | Complementary | marking | CE
1653 | RM35TF30 | Complementary | overvoltage category | III conforming to IEC 60664-1
1654 | RM35TF30 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
1655 | RM35TF30 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
1656 | RM35TF30 | Complementary | supply frequency | 50/60 Hz +/- 10 %
1657 | RM35TF30 | Complementary | operating position | Any position without derating
1658 | RM35TF30 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
1659 | RM35TF30 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
1660 | RM35TF30 | Complementary | housing material | Self-extinguishing plastic
1661 | RM35TF30 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON LED (yellow) for fault
1662 | RM35TF30 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
1663 | RM35TF30 | Complementary | electrical durability | 100000 cycles
1664 | RM35TF30 | Complementary | mechanical durability | 30000000 cycles
1665 | RM35TF30 | Complementary | operating rate | <= 360 operations/hour full load
1666 | RM35TF30 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
1667 | RM35TF30 | Complementary | safety reliability data | MTTFd = 399.5 years B10d = 360000
1668 | RM35TF30 | Complementary | width | 35 mm
1669 | RM35TF30 | Complementary | net weight | 0.13 kg
1670 | RM35TF30 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2
1671 | RM35TF30 | Environment | standards | EN/IEC 60255-1
1672 | RM35TF30 | Environment | product certifications | GL UL CSA GOST C-Tick
1673 | RM35TF30 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
1674 | RM35TF30 | Environment | ambient air temperature for storage | -40…70 °C
1675 | RM35TF30 | Environment | ambient air temperature for operation | -20…50 °C
1676 | RM35TF30 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
1677 | RM35TF30 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
1678 | RM35TF30 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
1679 | RM35TF30 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
1680 | RM35TF30 | Environment | pollution degree | 3 conforming to IEC 60664-1
1681 | RM35TF30 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
1682 | RM35TF30 | Environment | non-dissipating shock wave | 4 kV
1683 | RM35TF30 | Offer Sustainability | Sustainable offer status | Green Premium product
1684 | RM35TF30 | Offer Sustainability | REACh Regulation | REACh Declaration
1685 | RM35TF30 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
1686 | RM35TF30 | Offer Sustainability | Mercury free | Yes
1687 | RM35TF30 | Offer Sustainability | RoHS exemption information | Yes
1688 | RM35TF30 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
1689 | RM35TF30 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
1690 | RM35TF30 | Offer Sustainability | Circularity Profile | End of Life Information
1691 | RM35TF30 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
1692 | RM35TF30 | Contractual warranty | Warranty | 18 months
1693 | RM35TM250MW | Main | range of product | Zelio Control
1694 | RM35TM250MW | Main | product or component type | Modular measurement and control relays
1695 | RM35TM250MW | Main | relay type | Motor temperature control relay
1696 | RM35TM250MW | Main | product specific application | For 3-phase supply
1697 | RM35TM250MW | Main | relay name | RM35TM
1698 | RM35TM250MW | Main | relay monitored parameters | Phase failure detection Phase sequence Test/reset button Motor temperature via PTC probe Selection (with or without memory)
1699 | RM35TM250MW | Main | time delay | Fixed 0.3 s
1700 | RM35TM250MW | Main | switching capacity in VA | 1250 VA
1701 | RM35TM250MW | Main | measurement range | 208...480 V voltage AC 0...20 Ohm short-circuit detection
1702 | RM35TM250MW | Complementary | reset time | 10000 ms output
1703 | RM35TM250MW | Complementary | maximum switching voltage | 250 V AC 250 V DC
1704 | RM35TM250MW | Complementary | minimum switching current | 10 mA at 5 V DC
1705 | RM35TM250MW | Complementary | maximum switching current | 5 A AC 5 A DC
1706 | RM35TM250MW | Complementary | supply voltage limits | 20.4…264 V AC 20.4…264 V DC
1707 | RM35TM250MW | Complementary | power consumption in VA | 0…4 VA at 24...240 V AC
1708 | RM35TM250MW | Complementary | power consumption | 0.5 W DC
1709 | RM35TM250MW | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
1710 | RM35TM250MW | Complementary | resistance across terminals | 602 mOhm
1711 | RM35TM250MW | Complementary | output contacts | 2 NO
1712 | RM35TM250MW | Complementary | nominal output current | 5 A
1713 | RM35TM250MW | Complementary | measurement voltage limits | 176…528 V AC
1714 | RM35TM250MW | Complementary | delay at power up | 500 ms
1715 | RM35TM250MW | Complementary | voltage range | 176...528 V
1716 | RM35TM250MW | Complementary | response time | > 50 ms (input Y1 (contact Y1-T1) and push-button)
1717 | RM35TM250MW | Complementary | [Uc] control circuit voltage | <= 3.6 V of temperature control circuit (T1-T2 terminals open)
1718 | RM35TM250MW | Complementary | short-circuit current | 0.007 A temperature sensing circuit (T1-T2 terminals short circuited)
1719 | RM35TM250MW | Complementary | maximum resistance | 1500 Ohm for temperature sensor at 20 °C
1720 | RM35TM250MW | Complementary | tripping threshold | 3100 Ohm +/- 10 % for temperature control circuit
1721 | RM35TM250MW | Complementary | reset threshold | 1650 Ohm +/- 10 % for temperature control circuit
1722 | RM35TM250MW | Complementary | marking | CE
1723 | RM35TM250MW | Complementary | overvoltage category | III conforming to IEC 60664-1
1724 | RM35TM250MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
1725 | RM35TM250MW | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
1726 | RM35TM250MW | Complementary | supply frequency | 50/60 Hz +/- 10 %
1727 | RM35TM250MW | Complementary | operating position | Any position without derating
1728 | RM35TM250MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
1729 | RM35TM250MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
1730 | RM35TM250MW | Complementary | housing material | Self-extinguishing plastic
1731 | RM35TM250MW | Complementary | local signalling | LED (green) for power ON LED (yellow) for phase of relay (R2) LED (yellow) for temperature of relay (R1)
1732 | RM35TM250MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
1733 | RM35TM250MW | Complementary | electrical durability | 10000 cycles
1734 | RM35TM250MW | Complementary | mechanical durability | 30000000 cycles
1735 | RM35TM250MW | Complementary | operating rate | <= 360 operations/hour full load
1736 | RM35TM250MW | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
1737 | RM35TM250MW | Complementary | width | 35 mm
1738 | RM35TM250MW | Complementary | net weight | 0.13 kg
1739 | RM35TM250MW | Environment | immunity to microbreaks | 20 ms at 20.4 V
1740 | RM35TM250MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2
1741 | RM35TM250MW | Environment | standards | EN/IEC 60255-6 IEC 60034-11-2
1742 | RM35TM250MW | Environment | product certifications | CSA C-Tick GOST UL GL
1743 | RM35TM250MW | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
1744 | RM35TM250MW | Environment | ambient air temperature for storage | -40…70 °C
1745 | RM35TM250MW | Environment | ambient air temperature for operation | -20…50 °C
1746 | RM35TM250MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
1747 | RM35TM250MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
1748 | RM35TM250MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
1749 | RM35TM250MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
1750 | RM35TM250MW | Environment | pollution degree | 3 conforming to IEC 60664-1
1751 | RM35TM250MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
1752 | RM35TM250MW | Environment | non-dissipating shock wave | 4 kV
1753 | RM35TM250MW | Offer Sustainability | Sustainable offer status | Green Premium product
1754 | RM35TM250MW | Offer Sustainability | REACh Regulation | REACh Declaration
1755 | RM35TM250MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
1756 | RM35TM250MW | Offer Sustainability | Mercury free | Yes
1757 | RM35TM250MW | Offer Sustainability | RoHS exemption information | Yes
1758 | RM35TM250MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
1759 | RM35TM250MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
1760 | RM35TM250MW | Offer Sustainability | Circularity Profile | End of Life Information
1761 | RM35TM250MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
1762 | RM35TM250MW | Contractual warranty | Warranty | 18 months
1763 | RM35TM50MW | Main | range of product | Zelio Control
1764 | RM35TM50MW | Main | product or component type | Modular measurement and control relays
1765 | RM35TM50MW | Main | relay type | Motor temperature control relay
1766 | RM35TM50MW | Main | product specific application | For 3-phase supply
1767 | RM35TM50MW | Main | relay name | RM35TM
1768 | RM35TM50MW | Main | relay monitored parameters | Phase sequence Motor temperature via PTC probe Phase failure detection
1769 | RM35TM50MW | Main | time delay | Fixed 0.3 s
1770 | RM35TM50MW | Main | switching capacity in VA | 1250 VA
1771 | RM35TM50MW | Main | measurement range | 208...480 V voltage AC 0...20 Ohm short-circuit detection
1772 | RM35TM50MW | Complementary | reset time | 10000 ms output
1773 | RM35TM50MW | Complementary | maximum switching voltage | 250 V AC 250 V DC
1774 | RM35TM50MW | Complementary | minimum switching current | 10 mA at 5 V DC
1775 | RM35TM50MW | Complementary | maximum switching current | 5 A AC 5 A DC
1776 | RM35TM50MW | Complementary | supply voltage limits | 20.4…264 V AC 20.4…264 V DC
1777 | RM35TM50MW | Complementary | power consumption in VA | 0…4 VA at 24...240 V AC
1778 | RM35TM50MW | Complementary | power consumption | 0.5 W DC
1779 | RM35TM50MW | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
1780 | RM35TM50MW | Complementary | resistance across terminals | 602 mOhm
1781 | RM35TM50MW | Complementary | output contacts | 2 NO
1782 | RM35TM50MW | Complementary | nominal output current | 5 A
1783 | RM35TM50MW | Complementary | measurement voltage limits | 176…528 V AC
1784 | RM35TM50MW | Complementary | delay at power up | 500 ms
1785 | RM35TM50MW | Complementary | voltage range | 176...528 V
1786 | RM35TM50MW | Complementary | response time | > 50 ms (input Y1 (contact Y1-T1) and push-button)
1787 | RM35TM50MW | Complementary | [Uc] control circuit voltage | <= 3.6 V of temperature control circuit (T1-T2 terminals open)
1788 | RM35TM50MW | Complementary | short-circuit current | 0.007 A temperature sensing circuit (T1-T2 terminals short circuited)
1789 | RM35TM50MW | Complementary | maximum resistance | 1500 Ohm for temperature sensor at 20 °C
1790 | RM35TM50MW | Complementary | tripping threshold | 3100 Ohm +/- 10 % for temperature control circuit
1791 | RM35TM50MW | Complementary | reset threshold | 1650 Ohm +/- 10 % for temperature control circuit
1792 | RM35TM50MW | Complementary | marking | CE
1793 | RM35TM50MW | Complementary | overvoltage category | III conforming to IEC 60664-1
1794 | RM35TM50MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
1795 | RM35TM50MW | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
1796 | RM35TM50MW | Complementary | supply frequency | 50/60 Hz +/- 10 %
1797 | RM35TM50MW | Complementary | operating position | Any position without derating
1798 | RM35TM50MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
1799 | RM35TM50MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
1800 | RM35TM50MW | Complementary | housing material | Self-extinguishing plastic
1801 | RM35TM50MW | Complementary | local signalling | LED (green) for power ON LED (yellow) for phase of relay (R2) LED (yellow) for temperature of relay (R1)
1802 | RM35TM50MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
1803 | RM35TM50MW | Complementary | electrical durability | 10000 cycles
1804 | RM35TM50MW | Complementary | mechanical durability | 30000000 cycles
1805 | RM35TM50MW | Complementary | operating rate | <= 360 operations/hour full load
1806 | RM35TM50MW | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
1807 | RM35TM50MW | Complementary | width | 35 mm
1808 | RM35TM50MW | Complementary | net weight | 0.13 kg
1809 | RM35TM50MW | Environment | immunity to microbreaks | 20 ms at 20.4 V
1810 | RM35TM50MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2
1811 | RM35TM50MW | Environment | standards | EN/IEC 60255-6 IEC 60034-11-2
1812 | RM35TM50MW | Environment | product certifications | GL UL GOST C-Tick CSA
1813 | RM35TM50MW | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
1814 | RM35TM50MW | Environment | ambient air temperature for storage | -40…70 °C
1815 | RM35TM50MW | Environment | ambient air temperature for operation | -20…50 °C
1816 | RM35TM50MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
1817 | RM35TM50MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
1818 | RM35TM50MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
1819 | RM35TM50MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
1820 | RM35TM50MW | Environment | pollution degree | 3 conforming to IEC 60664-1
1821 | RM35TM50MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
1822 | RM35TM50MW | Environment | non-dissipating shock wave | 4 kV
1823 | RM35TM50MW | Offer Sustainability | Sustainable offer status | Green Premium product
1824 | RM35TM50MW | Offer Sustainability | REACh Regulation | REACh Declaration
1825 | RM35TM50MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
1826 | RM35TM50MW | Offer Sustainability | Mercury free | Yes
1827 | RM35TM50MW | Offer Sustainability | RoHS exemption information | Yes
1828 | RM35TM50MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
1829 | RM35TM50MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
1830 | RM35TM50MW | Offer Sustainability | Circularity Profile | End of Life Information
1831 | RM35TM50MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
1832 | RM35TM50MW | Contractual warranty | Warranty | 18 months
1833 | RM35UA11MW | Main | range of product | Zelio Control
1834 | RM35UA11MW | Main | product or component type | Modular measurement and control relays
1835 | RM35UA11MW | Main | relay type | Multifunction voltage control relay
1836 | RM35UA11MW | Main | relay name | RM35UA
1837 | RM35UA11MW | Main | relay monitored parameters | Overvoltage or undervoltage detection
1838 | RM35UA11MW | Main | time delay | Adjustable 0.3...30 s, 0 + 10 % on crossing the threshold
1839 | RM35UA11MW | Main | switching capacity in VA | 1250 VA
1840 | RM35UA11MW | Main | minimum switching current | 10 mA at 5 V DC
1841 | RM35UA11MW | Main | maximum switching current | 5 A AC/DC
1842 | RM35UA11MW | Main | power consumption in VA | 0…3.5 VA AC
1843 | RM35UA11MW | Main | measurement range | 0.05...5 V voltage
1844 | RM35UA11MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
1845 | RM35UA11MW | Complementary | reset time | 1500 ms time delay
1846 | RM35UA11MW | Complementary | maximum switching voltage | 250 V AC/DC
1847 | RM35UA11MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
1848 | RM35UA11MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
1849 | RM35UA11MW | Complementary | maximum power consumption in W | 0.6 W DC
1850 | RM35UA11MW | Complementary | immunity to microbreaks | 10 ms
1851 | RM35UA11MW | Complementary | control circuit frequency | 40...70 Hz +/- 10 %
1852 | RM35UA11MW | Complementary | resistance across terminals | 30 mOhm at E2-M terminals 5 mOhm at E1-M terminals 50 mOhm at E3-M terminals
1853 | RM35UA11MW | Complementary | output contacts | 2 C/O
1854 | RM35UA11MW | Complementary | nominal output current | 5 A
1855 | RM35UA11MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value
1856 | RM35UA11MW | Complementary | hysteresis | 5…50 % of threshold setting
1857 | RM35UA11MW | Complementary | delay at power up | 600 ms
1858 | RM35UA11MW | Complementary | measurement accuracy | +/- 10 % of the full scale value
1859 | RM35UA11MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay
1860 | RM35UA11MW | Complementary | measurement error | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation
1861 | RM35UA11MW | Complementary | polarity | Non reversible polarity on DC supply
1862 | RM35UA11MW | Complementary | sensitivity scale | 0.05...0.5 V E1-M terminals 0.3...3 V E2-M terminals 0.5...5 V E3-M terminals
1863 | RM35UA11MW | Complementary | threshold setting | 10...100 %
1864 | RM35UA11MW | Complementary | quality labels | CE
1865 | RM35UA11MW | Complementary | overvoltage category | III conforming to IEC 60664-1
1866 | RM35UA11MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
1867 | RM35UA11MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1 600 V conforming to IEC 60664-1
1868 | RM35UA11MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
1869 | RM35UA11MW | Complementary | operating position | Any position without derating
1870 | RM35UA11MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
1871 | RM35UA11MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
1872 | RM35UA11MW | Complementary | housing material | Self-extinguishing plastic
1873 | RM35UA11MW | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
1874 | RM35UA11MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
1875 | RM35UA11MW | Complementary | electrical durability | 100000 cycles
1876 | RM35UA11MW | Complementary | mechanical durability | 30000000 cycles
1877 | RM35UA11MW | Complementary | operating rate | <= 360 operations/hour full load
1878 | RM35UA11MW | Complementary | safety reliability data | B10d = 290000 MTTFd = 308.2 years
1879 | RM35UA11MW | Complementary | width | 35 mm
1880 | RM35UA11MW | Complementary | net weight | 0.08 kg
1881 | RM35UA11MW | Complementary | compatibility code | RM3
1882 | RM35UA11MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
1883 | RM35UA11MW | Environment | standards | EN/IEC 60255-6
1884 | RM35UA11MW | Environment | product certifications | GOST CSA GL UL C-Tick
1885 | RM35UA11MW | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
1886 | RM35UA11MW | Environment | ambient air temperature for storage | -40…70 °C
1887 | RM35UA11MW | Environment | ambient air temperature for operation | -20…50 °C
1888 | RM35UA11MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
1889 | RM35UA11MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
1890 | RM35UA11MW | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
1891 | RM35UA11MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
1892 | RM35UA11MW | Environment | pollution degree | 3 conforming to IEC 60664-1
1893 | RM35UA11MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
1894 | RM35UA11MW | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
1895 | RM35UA11MW | Offer Sustainability | Sustainable offer status | Green Premium product
1896 | RM35UA11MW | Offer Sustainability | REACh Regulation | REACh Declaration
1897 | RM35UA11MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
1898 | RM35UA11MW | Offer Sustainability | Mercury free | Yes
1899 | RM35UA11MW | Offer Sustainability | RoHS exemption information | Yes
1900 | RM35UA11MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
1901 | RM35UA11MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
1902 | RM35UA11MW | Offer Sustainability | Circularity Profile | End of Life Information
1903 | RM35UA11MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
1904 | RM35UA11MW | Contractual warranty | Warranty | 18 months
1905 | RM35UA12MW | Main | range of product | Zelio Control
1906 | RM35UA12MW | Main | product or component type | Modular measurement and control relays
1907 | RM35UA12MW | Main | relay type | Multifunction voltage control relay
1908 | RM35UA12MW | Main | relay name | RM35UA
1909 | RM35UA12MW | Main | relay monitored parameters | Overvoltage or undervoltage detection
1910 | RM35UA12MW | Main | time delay | Adjustable 0.3...30 s, 0 + 10 % on crossing the threshold
1911 | RM35UA12MW | Main | switching capacity in VA | 1250 VA
1912 | RM35UA12MW | Main | minimum switching current | 10 mA at 5 V DC
1913 | RM35UA12MW | Main | maximum switching current | 5 A AC/DC
1914 | RM35UA12MW | Main | power consumption in VA | 0…3.5 VA AC
1915 | RM35UA12MW | Main | measurement range | 1...100 V voltage
1916 | RM35UA12MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
1917 | RM35UA12MW | Complementary | reset time | 1500 ms time delay
1918 | RM35UA12MW | Complementary | maximum switching voltage | 250 V AC/DC
1919 | RM35UA12MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
1920 | RM35UA12MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
1921 | RM35UA12MW | Complementary | maximum power consumption in W | 0.6 W DC
1922 | RM35UA12MW | Complementary | immunity to microbreaks | 10 ms
1923 | RM35UA12MW | Complementary | control circuit frequency | 40...70 Hz +/- 10 %
1924 | RM35UA12MW | Complementary | resistance across terminals | 110 mOhm at E2-M terminals 22 mOhm at E1-M terminals 220 mOhm at E3-M terminals
1925 | RM35UA12MW | Complementary | output contacts | 2 C/O
1926 | RM35UA12MW | Complementary | nominal output current | 5 A
1927 | RM35UA12MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value
1928 | RM35UA12MW | Complementary | hysteresis | 5…50 % of threshold setting
1929 | RM35UA12MW | Complementary | delay at power up | 600 ms
1930 | RM35UA12MW | Complementary | measurement accuracy | +/- 10 % of the full scale value
1931 | RM35UA12MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay
1932 | RM35UA12MW | Complementary | measurement error | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation
1933 | RM35UA12MW | Complementary | polarity | Non reversible polarity on DC supply
1934 | RM35UA12MW | Complementary | sensitivity scale | 1...10 V E1-M terminals 10...100 V E3-M terminals 5...50 V E2-M terminals
1935 | RM35UA12MW | Complementary | threshold setting | 10...100 %
1936 | RM35UA12MW | Complementary | quality labels | CE
1937 | RM35UA12MW | Complementary | overvoltage category | III conforming to IEC 60664-1
1938 | RM35UA12MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
1939 | RM35UA12MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1 600 V conforming to IEC 60664-1
1940 | RM35UA12MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
1941 | RM35UA12MW | Complementary | operating position | Any position without derating
1942 | RM35UA12MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
1943 | RM35UA12MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
1944 | RM35UA12MW | Complementary | housing material | Self-extinguishing plastic
1945 | RM35UA12MW | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
1946 | RM35UA12MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
1947 | RM35UA12MW | Complementary | electrical durability | 100000 cycles
1948 | RM35UA12MW | Complementary | mechanical durability | 30000000 cycles
1949 | RM35UA12MW | Complementary | operating rate | <= 360 operations/hour full load
1950 | RM35UA12MW | Complementary | safety reliability data | B10d = 290000 MTTFd = 308.2 years
1951 | RM35UA12MW | Complementary | width | 35 mm
1952 | RM35UA12MW | Complementary | net weight | 0.08 kg
1953 | RM35UA12MW | Complementary | compatibility code | RM3
1954 | RM35UA12MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
1955 | RM35UA12MW | Environment | standards | EN/IEC 60255-6
1956 | RM35UA12MW | Environment | product certifications | GOST C-Tick UL GL CSA
1957 | RM35UA12MW | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
1958 | RM35UA12MW | Environment | ambient air temperature for storage | -40…70 °C
1959 | RM35UA12MW | Environment | ambient air temperature for operation | -20…50 °C
1960 | RM35UA12MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
1961 | RM35UA12MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
1962 | RM35UA12MW | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
1963 | RM35UA12MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
1964 | RM35UA12MW | Environment | pollution degree | 3 conforming to IEC 60664-1
1965 | RM35UA12MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
1966 | RM35UA12MW | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
1967 | RM35UA12MW | Offer Sustainability | Sustainable offer status | Green Premium product
1968 | RM35UA12MW | Offer Sustainability | REACh Regulation | REACh Declaration
1969 | RM35UA12MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
1970 | RM35UA12MW | Offer Sustainability | Mercury free | Yes
1971 | RM35UA12MW | Offer Sustainability | RoHS exemption information | Yes
1972 | RM35UA12MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
1973 | RM35UA12MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
1974 | RM35UA12MW | Offer Sustainability | Circularity Profile | End of Life Information
1975 | RM35UA12MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
1976 | RM35UA12MW | Contractual warranty | Warranty | 18 months
1977 | RM35UA13MW | Main | range of product | Zelio Control
1978 | RM35UA13MW | Main | product or component type | Modular measurement and control relays
1979 | RM35UA13MW | Main | relay type | Multifunction voltage control relay
1980 | RM35UA13MW | Main | relay name | RM35UA
1981 | RM35UA13MW | Main | relay monitored parameters | Overvoltage or undervoltage detection
1982 | RM35UA13MW | Main | time delay | Adjustable 0.3...30 s, 0 + 10 % on crossing the threshold
1983 | RM35UA13MW | Main | switching capacity in VA | 1250 VA
1984 | RM35UA13MW | Main | minimum switching current | 10 mA at 5 V DC
1985 | RM35UA13MW | Main | maximum switching current | 5 A AC/DC
1986 | RM35UA13MW | Main | power consumption in VA | 0…3.5 VA AC
1987 | RM35UA13MW | Main | measurement range | 15...600 V voltage
1988 | RM35UA13MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
1989 | RM35UA13MW | Complementary | reset time | 1500 ms time delay
1990 | RM35UA13MW | Complementary | maximum switching voltage | 250 V AC/DC
1991 | RM35UA13MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
1992 | RM35UA13MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
1993 | RM35UA13MW | Complementary | maximum power consumption in W | 0.6 W DC
1994 | RM35UA13MW | Complementary | immunity to microbreaks | 10 ms
1995 | RM35UA13MW | Complementary | control circuit frequency | 40...70 Hz +/- 10 %
1996 | RM35UA13MW | Complementary | resistance across terminals | 150 mOhm at E1-M terminals 300 mOhm at E2-M terminals 600 mOhm at E3-M terminals
1997 | RM35UA13MW | Complementary | output contacts | 2 C/O
1998 | RM35UA13MW | Complementary | nominal output current | 5 A
1999 | RM35UA13MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value
2000 | RM35UA13MW | Complementary | hysteresis | 5…50 % of threshold setting
2001 | RM35UA13MW | Complementary | delay at power up | 600 ms
2002 | RM35UA13MW | Complementary | measurement accuracy | +/- 10 % of the full scale value
2003 | RM35UA13MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay
2004 | RM35UA13MW | Complementary | measurement error | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation
2005 | RM35UA13MW | Complementary | polarity | Non reversible polarity on DC supply
2006 | RM35UA13MW | Complementary | sensitivity scale | 15...150 V E1-M terminals 30...300 V E2-M terminals 60...600 V E3-M terminals
2007 | RM35UA13MW | Complementary | threshold setting | 10...100 %
2008 | RM35UA13MW | Complementary | quality labels | CE
2009 | RM35UA13MW | Complementary | overvoltage category | III conforming to IEC 60664-1
2010 | RM35UA13MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
2011 | RM35UA13MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1 600 V conforming to IEC 60664-1
2012 | RM35UA13MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
2013 | RM35UA13MW | Complementary | operating position | Any position without derating
2014 | RM35UA13MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
2015 | RM35UA13MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
2016 | RM35UA13MW | Complementary | housing material | Self-extinguishing plastic
2017 | RM35UA13MW | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
2018 | RM35UA13MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
2019 | RM35UA13MW | Complementary | electrical durability | 100000 cycles
2020 | RM35UA13MW | Complementary | mechanical durability | 30000000 cycles
2021 | RM35UA13MW | Complementary | operating rate | <= 360 operations/hour full load
2022 | RM35UA13MW | Complementary | safety reliability data | B10d = 290000 MTTFd = 308.2 years
2023 | RM35UA13MW | Complementary | width | 35 mm
2024 | RM35UA13MW | Complementary | net weight | 0.08 kg
2025 | RM35UA13MW | Complementary | compatibility code | RM3
2026 | RM35UA13MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
2027 | RM35UA13MW | Environment | standards | EN/IEC 60255-6
2028 | RM35UA13MW | Environment | product certifications | GOST UL GL C-Tick CSA
2029 | RM35UA13MW | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
2030 | RM35UA13MW | Environment | ambient air temperature for storage | -40…70 °C
2031 | RM35UA13MW | Environment | ambient air temperature for operation | -20…50 °C
2032 | RM35UA13MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
2033 | RM35UA13MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
2034 | RM35UA13MW | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
2035 | RM35UA13MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
2036 | RM35UA13MW | Environment | pollution degree | 3 conforming to IEC 60664-1
2037 | RM35UA13MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
2038 | RM35UA13MW | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
2039 | RM35UA13MW | Offer Sustainability | Sustainable offer status | Green Premium product
2040 | RM35UA13MW | Offer Sustainability | REACh Regulation | REACh Declaration
2041 | RM35UA13MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
2042 | RM35UA13MW | Offer Sustainability | Mercury free | Yes
2043 | RM35UA13MW | Offer Sustainability | RoHS exemption information | Yes
2044 | RM35UA13MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
2045 | RM35UA13MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
2046 | RM35UA13MW | Offer Sustainability | Circularity Profile | End of Life Information
2047 | RM35UA13MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
2048 | RM35UA13MW | Contractual warranty | Warranty | 18 months
2049 | RM35UB330 | Main | range of product | Zelio Control
2050 | RM35UB330 | Main | product or component type | Modular measurement and control relays
2051 | RM35UB330 | Main | relay type | Voltage control relay
2052 | RM35UB330 | Main | product specific application | For 3-phase supply
2053 | RM35UB330 | Main | relay name | RM35UB3
2054 | RM35UB330 | Main | relay monitored parameters | Overvoltage and undervoltage between phases
2055 | RM35UB330 | Main | time delay | Adjustable 0.3...30 s, 0 + 10 % on crossing the threshold
2056 | RM35UB330 | Main | switching capacity in VA | 1250 VA
2057 | RM35UB330 | Main | minimum switching current | 10 mA at 5 V DC
2058 | RM35UB330 | Main | maximum switching current | 5 A AC/DC
2059 | RM35UB330 | Main | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
2060 | RM35UB330 | Main | measurement range | 194...528 V voltage AC 50/60 Hz
2061 | RM35UB330 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
2062 | RM35UB330 | Complementary | reset time | 1500 ms time delay
2063 | RM35UB330 | Complementary | maximum switching voltage | 250 V AC/DC
2064 | RM35UB330 | Complementary | [Us] rated supply voltage | 220...480 V AC 50/60 Hz +/- 10 %
2065 | RM35UB330 | Complementary | supply voltage limits | 194…528 V AC
2066 | RM35UB330 | Complementary | voltage detection threshold | 194 V
2067 | RM35UB330 | Complementary | control circuit frequency | 50...60 Hz +/- 15 %
2068 | RM35UB330 | Complementary | output contacts | 1 C/O + 1 C/O, 1 per threshold
2069 | RM35UB330 | Complementary | nominal output current | 5 A
2070 | RM35UB330 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
2071 | RM35UB330 | Complementary | hysteresis | 2 %
2072 | RM35UB330 | Complementary | delay at power up | 650 ms
2073 | RM35UB330 | Complementary | measurement accuracy | +/- 10 % of the full scale value
2074 | RM35UB330 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay
2075 | RM35UB330 | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
2076 | RM35UB330 | Complementary | response time | < 200 ms (in the event of a fault)
2077 | RM35UB330 | Complementary | quality labels | CE
2078 | RM35UB330 | Complementary | overvoltage category | III conforming to IEC 60664-1
2079 | RM35UB330 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
2080 | RM35UB330 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
2081 | RM35UB330 | Complementary | operating position | Any position without derating
2082 | RM35UB330 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
2083 | RM35UB330 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
2084 | RM35UB330 | Complementary | housing material | Self-extinguishing plastic
2085 | RM35UB330 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
2086 | RM35UB330 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
2087 | RM35UB330 | Complementary | electrical durability | 10000 cycles
2088 | RM35UB330 | Complementary | mechanical durability | 30000000 cycles
2089 | RM35UB330 | Complementary | operating rate | <= 360 operations/hour full load
2090 | RM35UB330 | Complementary | safety reliability data | B10d = 300000 MTTFd = 319.6 years
2091 | RM35UB330 | Complementary | width | 35 mm
2092 | RM35UB330 | Complementary | net weight | 0.08 kg
2093 | RM35UB330 | Complementary | functionality | Overvoltage and undervoltage detection
2094 | RM35UB330 | Complementary | compatibility code | RM3
2095 | RM35UB330 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
2096 | RM35UB330 | Environment | standards | EN/IEC 60255-1
2097 | RM35UB330 | Environment | product certifications | C-Tick GOST CSA GL UL
2098 | RM35UB330 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
2099 | RM35UB330 | Environment | ambient air temperature for storage | -40…70 °C
2100 | RM35UB330 | Environment | ambient air temperature for operation | -20…50 °C
2101 | RM35UB330 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
2102 | RM35UB330 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
2103 | RM35UB330 | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
2104 | RM35UB330 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
2105 | RM35UB330 | Environment | pollution degree | 3 conforming to IEC 60664-1
2106 | RM35UB330 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
2107 | RM35UB330 | Environment | non-dissipating shock wave | 4 kV
2108 | RM35UB330 | Offer Sustainability | Sustainable offer status | Green Premium product
2109 | RM35UB330 | Offer Sustainability | REACh Regulation | REACh Declaration
2110 | RM35UB330 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
2111 | RM35UB330 | Offer Sustainability | Mercury free | Yes
2112 | RM35UB330 | Offer Sustainability | RoHS exemption information | Yes
2113 | RM35UB330 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
2114 | RM35UB330 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
2115 | RM35UB330 | Offer Sustainability | Circularity Profile | End of Life Information
2116 | RM35UB330 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
2117 | RM35UB330 | Contractual warranty | Warranty | 18 months
2118 | RM35UB3N30 | Main | range of product | Zelio Control
2119 | RM35UB3N30 | Main | product or component type | Modular measurement and control relays
2120 | RM35UB3N30 | Main | relay type | Voltage control relay
2121 | RM35UB3N30 | Main | product specific application | For 3-phase supply
2122 | RM35UB3N30 | Main | relay name | RM35UB3
2123 | RM35UB3N30 | Main | relay monitored parameters | Absence of neutral Overvoltage and undervoltage between phases Overvoltage and undervoltage between neutral
2124 | RM35UB3N30 | Main | time delay | Adjustable 0.3...30 s, 0 + 10 % on crossing the threshold
2125 | RM35UB3N30 | Main | switching capacity in VA | 1250 VA
2126 | RM35UB3N30 | Main | minimum switching current | 10 mA at 5 V DC
2127 | RM35UB3N30 | Main | maximum switching current | 5 A AC/DC
2128 | RM35UB3N30 | Main | power consumption in VA | 0…3.9 VA AC
2129 | RM35UB3N30 | Main | measurement range | 114...329 V voltage AC 50/60 Hz
2130 | RM35UB3N30 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
2131 | RM35UB3N30 | Complementary | reset time | 1500 ms time delay
2132 | RM35UB3N30 | Complementary | maximum switching voltage | 250 V AC/DC
2133 | RM35UB3N30 | Complementary | [Us] rated supply voltage | 120...277 V AC 50/60 Hz +/- 10 %
2134 | RM35UB3N30 | Complementary | supply voltage limits | 114…329 V AC
2135 | RM35UB3N30 | Complementary | voltage detection threshold | 114 V
2136 | RM35UB3N30 | Complementary | control circuit frequency | 50...60 Hz +/- 15 %
2137 | RM35UB3N30 | Complementary | output contacts | 1 C/O + 1 C/O, 1 per threshold
2138 | RM35UB3N30 | Complementary | nominal output current | 5 A
2139 | RM35UB3N30 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
2140 | RM35UB3N30 | Complementary | hysteresis | 2 %
2141 | RM35UB3N30 | Complementary | delay at power up | 650 ms
2142 | RM35UB3N30 | Complementary | measurement accuracy | +/- 10 % of the full scale value
2143 | RM35UB3N30 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay
2144 | RM35UB3N30 | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
2145 | RM35UB3N30 | Complementary | response time | < 200 ms (in the event of a fault)
2146 | RM35UB3N30 | Complementary | quality labels | CE
2147 | RM35UB3N30 | Complementary | overvoltage category | III conforming to IEC 60664-1
2148 | RM35UB3N30 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
2149 | RM35UB3N30 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
2150 | RM35UB3N30 | Complementary | operating position | Any position without derating
2151 | RM35UB3N30 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
2152 | RM35UB3N30 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
2153 | RM35UB3N30 | Complementary | housing material | Self-extinguishing plastic
2154 | RM35UB3N30 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
2155 | RM35UB3N30 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
2156 | RM35UB3N30 | Complementary | electrical durability | 10000 cycles
2157 | RM35UB3N30 | Complementary | mechanical durability | 30000000 cycles
2158 | RM35UB3N30 | Complementary | operating rate | <= 360 operations/hour full load
2159 | RM35UB3N30 | Complementary | safety reliability data | B10d = 470000 MTTFd = 502.2 years
2160 | RM35UB3N30 | Complementary | width | 35 mm
2161 | RM35UB3N30 | Complementary | net weight | 0.08 kg
2162 | RM35UB3N30 | Complementary | functionality | Overvoltage and undervoltage detection
2163 | RM35UB3N30 | Complementary | compatibility code | RM3
2164 | RM35UB3N30 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
2165 | RM35UB3N30 | Environment | standards | EN/IEC 60255-1
2166 | RM35UB3N30 | Environment | product certifications | UL C-Tick GL CSA GOST
2167 | RM35UB3N30 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
2168 | RM35UB3N30 | Environment | ambient air temperature for storage | -40…70 °C
2169 | RM35UB3N30 | Environment | ambient air temperature for operation | -20…50 °C
2170 | RM35UB3N30 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
2171 | RM35UB3N30 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
2172 | RM35UB3N30 | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
2173 | RM35UB3N30 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
2174 | RM35UB3N30 | Environment | pollution degree | 3 conforming to IEC 60664-1
2175 | RM35UB3N30 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
2176 | RM35UB3N30 | Environment | non-dissipating shock wave | 4 kV
2177 | RM35UB3N30 | Offer Sustainability | Sustainable offer status | Green Premium product
2178 | RM35UB3N30 | Offer Sustainability | REACh Regulation | REACh Declaration
2179 | RM35UB3N30 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
2180 | RM35UB3N30 | Offer Sustainability | Mercury free | Yes
2181 | RM35UB3N30 | Offer Sustainability | RoHS exemption information | Yes
2182 | RM35UB3N30 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
2183 | RM35UB3N30 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
2184 | RM35UB3N30 | Offer Sustainability | Circularity Profile | End of Life Information
2185 | RM35UB3N30 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
2186 | RM35UB3N30 | Contractual warranty | Warranty | 18 months
2187 | RM22JA21MR | Main | range of product | Zelio Control
2188 | RM22JA21MR | Main | product or component type | Modular measurement and control relays
2189 | RM22JA21MR | Main | relay type | Current control relay
2190 | RM22JA21MR | Main | relay name | RM22JA
2191 | RM22JA21MR | Main | relay monitored parameters | Overcurrent detection
2192 | RM22JA21MR | Main | time delay type | Without
2193 | RM22JA21MR | Main | switching capacity in VA | 2000 VA
2194 | RM22JA21MR | Main | measurement range | 4...40 mA E1-M terminals 20...200 mA E2-M terminals 100...1000 mA E3-M terminals 4 mA...1 A current AC/DC 50/60 Hz
2195 | RM22JA21MR | Complementary | reset time | 1500 ms at maximum voltage
2196 | RM22JA21MR | Complementary | maximum switching voltage | 250 V AC
2197 | RM22JA21MR | Complementary | minimum switching current | 10 mA at 5 V DC
2198 | RM22JA21MR | Complementary | maximum switching current | 8 A AC
2199 | RM22JA21MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
2200 | RM22JA21MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
2201 | RM22JA21MR | Complementary | operating limits | - 15 % + 10 % Un
2202 | RM22JA21MR | Complementary | power consumption in VA | 3.5 VA AC
2203 | RM22JA21MR | Complementary | maximum power consumption in W | 1.5 W DC
2204 | RM22JA21MR | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
2205 | RM22JA21MR | Complementary | resistance across terminals | 2.5 Ohm at E1-M terminals 0.5 Ohm at E2-M terminals 0.1 Ohm at E3-M terminals
2206 | RM22JA21MR | Complementary | output contacts | 2 C/O
2207 | RM22JA21MR | Complementary | nominal output current | 8 A
2208 | RM22JA21MR | Complementary | internal input resistance | 0.1 Ohm 2.5 Ohm 0.5 Ohm
2209 | RM22JA21MR | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
2210 | RM22JA21MR | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
2211 | RM22JA21MR | Complementary | setting accuracy of time delay | 10 %
2212 | RM22JA21MR | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
2213 | RM22JA21MR | Complementary | hysteresis | 5…50 % adjustable of threshold setting
2214 | RM22JA21MR | Complementary | run-up delay at power-up | 0.3 s
2215 | RM22JA21MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
2216 | RM22JA21MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 0.2 % for time delay
2217 | RM22JA21MR | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
2218 | RM22JA21MR | Complementary | response time | <= 500 ms
2219 | RM22JA21MR | Complementary | threshold setting | 10...100 %
2220 | RM22JA21MR | Complementary | overvoltage category | III conforming to IEC 60664-1 III conforming to UL 508
2221 | RM22JA21MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
2222 | RM22JA21MR | Complementary | insulation | Between supply and measurement
2223 | RM22JA21MR | Complementary | mounting position | Any position
2224 | RM22JA21MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
2225 | RM22JA21MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
2226 | RM22JA21MR | Complementary | housing material | Self-extinguishing plastic
2227 | RM22JA21MR | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
2228 | RM22JA21MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
2229 | RM22JA21MR | Complementary | electrical durability | 100000 cycles
2230 | RM22JA21MR | Complementary | mechanical durability | 10000000 cycles
2231 | RM22JA21MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
2232 | RM22JA21MR | Complementary | safety reliability data | MTTFd = 296.8 years B10d = 270000
2233 | RM22JA21MR | Complementary | contacts material | Cadmium free
2234 | RM22JA21MR | Complementary | width | 22.5 mm
2235 | RM22JA21MR | Complementary | net weight | 0.11 kg
2236 | RM22JA21MR | Environment | immunity to microbreaks | 50 ms
2237 | RM22JA21MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
2238 | RM22JA21MR | Environment | standards | EN/IEC 60255-1
2239 | RM22JA21MR | Environment | product certifications | EAC CSA China RoHS CE RCM CCC UL GL
2240 | RM22JA21MR | Environment | ambient air temperature for storage | -40…70 °C
2241 | RM22JA21MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
2242 | RM22JA21MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
2243 | RM22JA21MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
2244 | RM22JA21MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
2245 | RM22JA21MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
2246 | RM22JA21MR | Environment | pollution degree | 3 conforming to IEC 60664-1 3 conforming to UL 508
2247 | RM22JA21MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
2248 | RM22JA21MR | Offer Sustainability | Sustainable offer status | Green Premium product
2249 | RM22JA21MR | Offer Sustainability | REACh Regulation | REACh Declaration
2250 | RM22JA21MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
2251 | RM22JA21MR | Offer Sustainability | Mercury free | Yes
2252 | RM22JA21MR | Offer Sustainability | RoHS exemption information | Yes
2253 | RM22JA21MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
2254 | RM22JA21MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
2255 | RM22JA21MR | Offer Sustainability | Circularity Profile | End of Life Information
2256 | RM22JA21MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
2257 | RM22JA31MR | Main | range of product | Zelio Control
2258 | RM22JA31MR | Main | product or component type | Modular measurement and control relays
2259 | RM22JA31MR | Main | relay type | Current control relay
2260 | RM22JA31MR | Main | relay name | RM22JA
2261 | RM22JA31MR | Main | relay monitored parameters | Overcurrent or undercurrent detection Overcurrent or undercurrent in window mode
2262 | RM22JA31MR | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
2263 | RM22JA31MR | Main | switching capacity in VA | 2000 VA
2264 | RM22JA31MR | Main | measurement range | 4...40 mA E1-M terminals 20...200 mA E2-M terminals 100...1000 mA E3-M terminals 4 mA...1 A current AC/DC 50/60 Hz
2265 | RM22JA31MR | Complementary | reset time | 1500 ms at maximum voltage
2266 | RM22JA31MR | Complementary | maximum switching voltage | 250 V AC
2267 | RM22JA31MR | Complementary | minimum switching current | 10 mA at 5 V DC
2268 | RM22JA31MR | Complementary | maximum switching current | 8 A AC
2269 | RM22JA31MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
2270 | RM22JA31MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
2271 | RM22JA31MR | Complementary | operating limits | - 15 % + 10 % Un
2272 | RM22JA31MR | Complementary | power consumption in VA | 3.5 VA AC
2273 | RM22JA31MR | Complementary | maximum power consumption in W | 1.5 W DC
2274 | RM22JA31MR | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
2275 | RM22JA31MR | Complementary | resistance across terminals | 2.5 Ohm at E1-M terminals 0.5 Ohm at E2-M terminals 0.1 Ohm at E3-M terminals
2276 | RM22JA31MR | Complementary | output contacts | 2 C/O
2277 | RM22JA31MR | Complementary | nominal output current | 8 A
2278 | RM22JA31MR | Complementary | internal input resistance | 0.5 Ohm 2.5 Ohm 0.1 Ohm
2279 | RM22JA31MR | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
2280 | RM22JA31MR | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
2281 | RM22JA31MR | Complementary | setting accuracy of time delay | 10 P
2282 | RM22JA31MR | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
2283 | RM22JA31MR | Complementary | hysteresis | 5…50 % adjustable of threshold setting for overcurrent or undercurrent detection 3 % fixed of full scale for window mode
2284 | RM22JA31MR | Complementary | run-up delay at power-up | 0.3 s
2285 | RM22JA31MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
2286 | RM22JA31MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 0.2 % for time delay
2287 | RM22JA31MR | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
2288 | RM22JA31MR | Complementary | response time | <= 500 ms
2289 | RM22JA31MR | Complementary | threshold setting | 10...100 %
2290 | RM22JA31MR | Complementary | overvoltage category | III conforming to IEC 60664-1 III conforming to UL 508
2291 | RM22JA31MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
2292 | RM22JA31MR | Complementary | insulation | Between supply and measurement
2293 | RM22JA31MR | Complementary | mounting position | Any position
2294 | RM22JA31MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
2295 | RM22JA31MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
2296 | RM22JA31MR | Complementary | housing material | Self-extinguishing plastic
2297 | RM22JA31MR | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
2298 | RM22JA31MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
2299 | RM22JA31MR | Complementary | electrical durability | 100000 cycles
2300 | RM22JA31MR | Complementary | mechanical durability | 10000000 cycles
2301 | RM22JA31MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
2302 | RM22JA31MR | Complementary | safety reliability data | MTTFd = 296.8 years B10d = 270000
2303 | RM22JA31MR | Complementary | contacts material | Cadmium free
2304 | RM22JA31MR | Complementary | width | 22.5 mm
2305 | RM22JA31MR | Complementary | net weight | 0.11 kg
2306 | RM22JA31MR | Environment | immunity to microbreaks | 50 ms
2307 | RM22JA31MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
2308 | RM22JA31MR | Environment | standards | EN/IEC 60255-1
2309 | RM22JA31MR | Environment | product certifications | CSA CE EAC CCC GL RCM China RoHS UL
2310 | RM22JA31MR | Environment | ambient air temperature for storage | -40…70 °C
2311 | RM22JA31MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
2312 | RM22JA31MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
2313 | RM22JA31MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
2314 | RM22JA31MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
2315 | RM22JA31MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
2316 | RM22JA31MR | Environment | pollution degree | 3 conforming to IEC 60664-1 3 conforming to UL 508
2317 | RM22JA31MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
2318 | RM22JA31MR | Offer Sustainability | Sustainable offer status | Green Premium product
2319 | RM22JA31MR | Offer Sustainability | REACh Regulation | REACh Declaration
2320 | RM22JA31MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
2321 | RM22JA31MR | Offer Sustainability | Mercury free | Yes
2322 | RM22JA31MR | Offer Sustainability | RoHS exemption information | Yes
2323 | RM22JA31MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
2324 | RM22JA31MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
2325 | RM22JA31MR | Offer Sustainability | Circularity Profile | End of Life Information
2326 | RM22JA31MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
2327 | RM22LA32MR | Main | range of product | Zelio Control
2328 | RM22LA32MR | Main | product or component type | Modular measurement and control relays
2329 | RM22LA32MR | Main | relay type | Level control relay
2330 | RM22LA32MR | Main | relay name | RM22L
2331 | RM22LA32MR | Main | relay monitored parameters | Detection by resistive probes
2332 | RM22LA32MR | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
2333 | RM22LA32MR | Main | switching capacity in VA | 2000 VA
2334 | RM22LA32MR | Main | measurement range | 250 Ohm...1 MOhm
2335 | RM22LA32MR | Complementary | reset time | 1750 ms
2336 | RM22LA32MR | Complementary | maximum switching voltage | 250 V AC
2337 | RM22LA32MR | Complementary | minimum switching current | 10 mA at 5 V DC
2338 | RM22LA32MR | Complementary | maximum switching current | 8 A AC
2339 | RM22LA32MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
2340 | RM22LA32MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
2341 | RM22LA32MR | Complementary | operating limits | - 15 % + 10 % Un
2342 | RM22LA32MR | Complementary | power consumption in VA | 5 VA AC
2343 | RM22LA32MR | Complementary | maximum power consumption in W | 1.5 W DC
2344 | RM22LA32MR | Complementary | output contacts | 2 C/O
2345 | RM22LA32MR | Complementary | nominal output current | 8 A
2346 | RM22LA32MR | Complementary | run-up delay at power-up | 2.5 s 0.6 s
2347 | RM22LA32MR | Complementary | maximum electrode voltage | 12 V AC
2348 | RM22LA32MR | Complementary | maximum electrode current | 1 mA
2349 | RM22LA32MR | Complementary | repeat accuracy | +/- 2 % for time delay
2350 | RM22LA32MR | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
2351 | RM22LA32MR | Complementary | sensitivity scale | 0.25...5 kOhm LS (Low Sensitivity) 5...100 kOhm St (Standard Sensitivity) 50...1000 kOhm HS (High Sensitivity)
2352 | RM22LA32MR | Complementary | sensitivity adjustment | 5…100 %
2353 | RM22LA32MR | Complementary | maximum supply current for sensors | 1 mA
2354 | RM22LA32MR | Complementary | maximum cable distance between devices | 1000 m between probe and delay
2355 | RM22LA32MR | Complementary | cable capacitance | 1 nF at HS (High Sensitivity) for probe cable 2.2 nF at St (Standard Sensitivity) for probe cable 4.7 nF at LS (Low Sensitivity) for probe cable
2356 | RM22LA32MR | Complementary | overvoltage category | III conforming to IEC 60664-1
2357 | RM22LA32MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
2358 | RM22LA32MR | Complementary | insulation | Between supply and measurement
2359 | RM22LA32MR | Complementary | mounting position | Any position
2360 | RM22LA32MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
2361 | RM22LA32MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
2362 | RM22LA32MR | Complementary | housing material | Self-extinguishing plastic
2363 | RM22LA32MR | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
2364 | RM22LA32MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
2365 | RM22LA32MR | Complementary | electrical durability | 100000 cycles
2366 | RM22LA32MR | Complementary | mechanical durability | 10000000 cycles
2367 | RM22LA32MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
2368 | RM22LA32MR | Complementary | safety reliability data | MTTFd = 182.6 years B10d = 170000
2369 | RM22LA32MR | Complementary | contacts material | Cadmium free
2370 | RM22LA32MR | Complementary | width | 22.5 mm
2371 | RM22LA32MR | Complementary | net weight | 0.11 kg
2372 | RM22LA32MR | Environment | immunity to microbreaks | 100 ms DC 90 ms AC
2373 | RM22LA32MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
2374 | RM22LA32MR | Environment | standards | EN/IEC 60255-1
2375 | RM22LA32MR | Environment | product certifications | China RoHS UL RCM CSA GL CCC CE EAC
2376 | RM22LA32MR | Environment | ambient air temperature for storage | -40…70 °C
2377 | RM22LA32MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
2378 | RM22LA32MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
2379 | RM22LA32MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
2380 | RM22LA32MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
2381 | RM22LA32MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
2382 | RM22LA32MR | Environment | pollution degree | 3 conforming to IEC 60664-1
2383 | RM22LA32MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
2384 | RM22LA32MR | Offer Sustainability | Sustainable offer status | Green Premium product
2385 | RM22LA32MR | Offer Sustainability | REACh Regulation | REACh Declaration
2386 | RM22LA32MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
2387 | RM22LA32MR | Offer Sustainability | Mercury free | Yes
2388 | RM22LA32MR | Offer Sustainability | RoHS exemption information | Yes
2389 | RM22LA32MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
2390 | RM22LA32MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
2391 | RM22LA32MR | Offer Sustainability | Circularity Profile | End of Life Information
2392 | RM22LA32MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
2393 | RM22LA32MT | Main | range of product | Zelio Control
2394 | RM22LA32MT | Main | product or component type | Modular measurement and control relays
2395 | RM22LA32MT | Main | relay type | Level control relay
2396 | RM22LA32MT | Main | relay name | RM22L
2397 | RM22LA32MT | Main | relay monitored parameters | Detection by resistive probes
2398 | RM22LA32MT | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
2399 | RM22LA32MT | Main | switching capacity in VA | 2000 VA
2400 | RM22LA32MT | Main | measurement range | 250 Ohm...1 MOhm
2401 | RM22LA32MT | Complementary | reset time | 1750 ms
2402 | RM22LA32MT | Complementary | maximum switching voltage | 250 V AC
2403 | RM22LA32MT | Complementary | minimum switching current | 10 mA at 5 V DC
2404 | RM22LA32MT | Complementary | maximum switching current | 8 A AC
2405 | RM22LA32MT | Complementary | [Us] rated supply voltage | 380...415 V AC 50/60 Hz
2406 | RM22LA32MT | Complementary | supply voltage limits | 323…456.5 V AC
2407 | RM22LA32MT | Complementary | operating limits | - 15 % + 10 % Un
2408 | RM22LA32MT | Complementary | power consumption in VA | 8 VA AC
2409 | RM22LA32MT | Complementary | output contacts | 2 C/O
2410 | RM22LA32MT | Complementary | nominal output current | 8 A
2411 | RM22LA32MT | Complementary | run-up delay at power-up | 2.5 s 0.6 s
2412 | RM22LA32MT | Complementary | maximum electrode voltage | 12 V AC
2413 | RM22LA32MT | Complementary | maximum electrode current | 1 mA
2414 | RM22LA32MT | Complementary | repeat accuracy | +/- 2 % for time delay
2415 | RM22LA32MT | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
2416 | RM22LA32MT | Complementary | sensitivity scale | 0.25...5 kOhm LS (Low Sensitivity) 5...100 kOhm St (Standard Sensitivity) 50...1000 kOhm HS (High Sensitivity)
2417 | RM22LA32MT | Complementary | sensitivity adjustment | 5…100 %
2418 | RM22LA32MT | Complementary | maximum supply current for sensors | 1 mA
2419 | RM22LA32MT | Complementary | maximum cable distance between devices | 1000 m between probe and delay
2420 | RM22LA32MT | Complementary | cable capacitance | 1 nF at HS (High Sensitivity) for probe cable 2.2 nF at St (Standard Sensitivity) for probe cable 4.7 nF at LS (Low Sensitivity) for probe cable
2421 | RM22LA32MT | Complementary | overvoltage category | III conforming to IEC 60664-1
2422 | RM22LA32MT | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
2423 | RM22LA32MT | Complementary | insulation | Between supply and measurement
2424 | RM22LA32MT | Complementary | mounting position | Any position
2425 | RM22LA32MT | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
2426 | RM22LA32MT | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
2427 | RM22LA32MT | Complementary | housing material | Self-extinguishing plastic
2428 | RM22LA32MT | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
2429 | RM22LA32MT | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
2430 | RM22LA32MT | Complementary | electrical durability | 100000 cycles
2431 | RM22LA32MT | Complementary | mechanical durability | 10000000 cycles
2432 | RM22LA32MT | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
2433 | RM22LA32MT | Complementary | safety reliability data | MTTFd = 182.6 years B10d = 170000
2434 | RM22LA32MT | Complementary | contacts material | Cadmium free
2435 | RM22LA32MT | Complementary | width | 22.5 mm
2436 | RM22LA32MT | Complementary | net weight | 0.11 kg
2437 | RM22LA32MT | Environment | immunity to microbreaks | 100 ms DC 90 ms AC
2438 | RM22LA32MT | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
2439 | RM22LA32MT | Environment | standards | EN/IEC 60255-1
2440 | RM22LA32MT | Environment | product certifications | GL UL CCC EAC RCM CE CSA China RoHS
2441 | RM22LA32MT | Environment | ambient air temperature for storage | -40…70 °C
2442 | RM22LA32MT | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
2443 | RM22LA32MT | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
2444 | RM22LA32MT | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
2445 | RM22LA32MT | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
2446 | RM22LA32MT | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
2447 | RM22LA32MT | Environment | pollution degree | 3 conforming to IEC 60664-1
2448 | RM22LA32MT | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
2449 | RM22LA32MT | Offer Sustainability | Sustainable offer status | Green Premium product
2450 | RM22LA32MT | Offer Sustainability | REACh Regulation | REACh Declaration
2451 | RM22LA32MT | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
2452 | RM22LA32MT | Offer Sustainability | Mercury free | Yes
2453 | RM22LA32MT | Offer Sustainability | RoHS exemption information | Yes
2454 | RM22LA32MT | Offer Sustainability | China RoHS Regulation | China RoHS declaration
2455 | RM22LA32MT | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
2456 | RM22LA32MT | Offer Sustainability | Circularity Profile | End of Life Information
2457 | RM22LA32MT | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
2458 | RM22LG11MR | Main | range of product | Zelio Control
2459 | RM22LG11MR | Main | product or component type | Modular measurement and control relays
2460 | RM22LG11MR | Main | relay type | Level control relay
2461 | RM22LG11MR | Main | relay name | RM22L
2462 | RM22LG11MR | Main | relay monitored parameters | Detection by resistive probes
2463 | RM22LG11MR | Main | time delay type | Without
2464 | RM22LG11MR | Main | switching capacity in VA | 2000 VA
2465 | RM22LG11MR | Main | measurement range | 5...100 kOhm
2466 | RM22LG11MR | Complementary | reset time | 1750 ms
2467 | RM22LG11MR | Complementary | maximum switching voltage | 250 V AC
2468 | RM22LG11MR | Complementary | minimum switching current | 10 mA at 5 V DC
2469 | RM22LG11MR | Complementary | maximum switching current | 8 A AC
2470 | RM22LG11MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
2471 | RM22LG11MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
2472 | RM22LG11MR | Complementary | operating limits | - 15 % + 10 % Un
2473 | RM22LG11MR | Complementary | power consumption in VA | 5 VA AC
2474 | RM22LG11MR | Complementary | maximum power consumption in W | 1.5 W DC
2475 | RM22LG11MR | Complementary | output contacts | 2 C/O
2476 | RM22LG11MR | Complementary | nominal output current | 8 A
2477 | RM22LG11MR | Complementary | run-up delay at power-up | 0.6 s
2478 | RM22LG11MR | Complementary | maximum electrode voltage | 12 V AC
2479 | RM22LG11MR | Complementary | maximum electrode current | 1 mA
2480 | RM22LG11MR | Complementary | repeat accuracy | +/- 2 % for time delay
2481 | RM22LG11MR | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
2482 | RM22LG11MR | Complementary | sensitivity scale | 5...100 kOhm St (Standard Sensitivity)
2483 | RM22LG11MR | Complementary | sensitivity adjustment | 5…100 %
2484 | RM22LG11MR | Complementary | maximum supply current for sensors | 1 mA
2485 | RM22LG11MR | Complementary | maximum cable distance between devices | 1000 m between probe and delay
2486 | RM22LG11MR | Complementary | cable capacitance | 1 nF at HS (High Sensitivity) for probe cable 2.2 nF at St (Standard Sensitivity) for probe cable 4.7 nF at LS (Low Sensitivity) for probe cable
2487 | RM22LG11MR | Complementary | overvoltage category | III conforming to IEC 60664-1
2488 | RM22LG11MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
2489 | RM22LG11MR | Complementary | insulation | Between supply and measurement
2490 | RM22LG11MR | Complementary | mounting position | Any position
2491 | RM22LG11MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
2492 | RM22LG11MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
2493 | RM22LG11MR | Complementary | housing material | Self-extinguishing plastic
2494 | RM22LG11MR | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
2495 | RM22LG11MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
2496 | RM22LG11MR | Complementary | electrical durability | 100000 cycles
2497 | RM22LG11MR | Complementary | mechanical durability | 10000000 cycles
2498 | RM22LG11MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
2499 | RM22LG11MR | Complementary | safety reliability data | B10d = 120000 MTTFd = 125.5 years
2500 | RM22LG11MR | Complementary | contacts material | Cadmium free
2501 | RM22LG11MR | Complementary | width | 22.5 mm
2502 | RM22LG11MR | Complementary | net weight | 0.1 kg
2503 | RM22LG11MR | Environment | immunity to microbreaks | 100 ms DC 90 ms AC
2504 | RM22LG11MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
2505 | RM22LG11MR | Environment | standards | EN/IEC 60255-1
2506 | RM22LG11MR | Environment | product certifications | GL RCM CCC CSA UL China RoHS EAC CE
2507 | RM22LG11MR | Environment | ambient air temperature for storage | -40…70 °C
2508 | RM22LG11MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
2509 | RM22LG11MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
2510 | RM22LG11MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
2511 | RM22LG11MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
2512 | RM22LG11MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
2513 | RM22LG11MR | Environment | pollution degree | 3 conforming to IEC 60664-1
2514 | RM22LG11MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
2515 | RM22LG11MR | Offer Sustainability | Sustainable offer status | Green Premium product
2516 | RM22LG11MR | Offer Sustainability | REACh Regulation | REACh Declaration
2517 | RM22LG11MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
2518 | RM22LG11MR | Offer Sustainability | Mercury free | Yes
2519 | RM22LG11MR | Offer Sustainability | RoHS exemption information | Yes
2520 | RM22LG11MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
2521 | RM22LG11MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
2522 | RM22LG11MR | Offer Sustainability | Circularity Profile | End of Life Information
2523 | RM22LG11MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
2524 | RM22LG11MT | Main | range of product | Zelio Control
2525 | RM22LG11MT | Main | product or component type | Modular measurement and control relays
2526 | RM22LG11MT | Main | relay type | Level control relay
2527 | RM22LG11MT | Main | relay name | RM22L
2528 | RM22LG11MT | Main | relay monitored parameters | Detection by resistive probes
2529 | RM22LG11MT | Main | time delay type | Without
2530 | RM22LG11MT | Main | switching capacity in VA | 2000 VA
2531 | RM22LG11MT | Main | measurement range | 5...100 kOhm
2532 | RM22LG11MT | Complementary | reset time | 1750 ms
2533 | RM22LG11MT | Complementary | maximum switching voltage | 250 V AC
2534 | RM22LG11MT | Complementary | minimum switching current | 10 mA at 5 V DC
2535 | RM22LG11MT | Complementary | maximum switching current | 8 A AC
2536 | RM22LG11MT | Complementary | [Us] rated supply voltage | 380...415 V AC 50/60 Hz
2537 | RM22LG11MT | Complementary | supply voltage limits | 323…456.5 V AC
2538 | RM22LG11MT | Complementary | operating limits | - 15 % + 10 % Un
2539 | RM22LG11MT | Complementary | power consumption in VA | 8 VA AC
2540 | RM22LG11MT | Complementary | output contacts | 2 C/O
2541 | RM22LG11MT | Complementary | nominal output current | 8 A
2542 | RM22LG11MT | Complementary | run-up delay at power-up | 0.6 s
2543 | RM22LG11MT | Complementary | maximum electrode voltage | 12 V AC
2544 | RM22LG11MT | Complementary | maximum electrode current | 1 mA
2545 | RM22LG11MT | Complementary | repeat accuracy | +/- 2 % for time delay
2546 | RM22LG11MT | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
2547 | RM22LG11MT | Complementary | sensitivity scale | 5...100 kOhm St (Standard Sensitivity)
2548 | RM22LG11MT | Complementary | sensitivity adjustment | 5…100 %
2549 | RM22LG11MT | Complementary | maximum supply current for sensors | 1 mA
2550 | RM22LG11MT | Complementary | maximum cable distance between devices | 1000 m between probe and delay
2551 | RM22LG11MT | Complementary | cable capacitance | 1 nF at HS (High Sensitivity) for probe cable 2.2 nF at St (Standard Sensitivity) for probe cable 4.7 nF at LS (Low Sensitivity) for probe cable
2552 | RM22LG11MT | Complementary | overvoltage category | III conforming to IEC 60664-1
2553 | RM22LG11MT | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
2554 | RM22LG11MT | Complementary | insulation | Between supply and measurement
2555 | RM22LG11MT | Complementary | mounting position | Any position
2556 | RM22LG11MT | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
2557 | RM22LG11MT | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
2558 | RM22LG11MT | Complementary | housing material | Self-extinguishing plastic
2559 | RM22LG11MT | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
2560 | RM22LG11MT | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
2561 | RM22LG11MT | Complementary | electrical durability | 100000 cycles
2562 | RM22LG11MT | Complementary | mechanical durability | 10000000 cycles
2563 | RM22LG11MT | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
2564 | RM22LG11MT | Complementary | safety reliability data | MTTFd = 125.5 years B10d = 120000
2565 | RM22LG11MT | Complementary | contacts material | Cadmium free
2566 | RM22LG11MT | Complementary | width | 22.5 mm
2567 | RM22LG11MT | Complementary | net weight | 0.1 kg
2568 | RM22LG11MT | Environment | immunity to microbreaks | 100 ms DC 90 ms AC
2569 | RM22LG11MT | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
2570 | RM22LG11MT | Environment | standards | EN/IEC 60255-1
2571 | RM22LG11MT | Environment | product certifications | CSA GL RCM UL China RoHS EAC CE CCC
2572 | RM22LG11MT | Environment | ambient air temperature for storage | -40…70 °C
2573 | RM22LG11MT | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
2574 | RM22LG11MT | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
2575 | RM22LG11MT | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
2576 | RM22LG11MT | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
2577 | RM22LG11MT | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
2578 | RM22LG11MT | Environment | pollution degree | 3 conforming to IEC 60664-1
2579 | RM22LG11MT | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
2580 | RM22LG11MT | Offer Sustainability | Sustainable offer status | Green Premium product
2581 | RM22LG11MT | Offer Sustainability | REACh Regulation | REACh Declaration
2582 | RM22LG11MT | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
2583 | RM22LG11MT | Offer Sustainability | Mercury free | Yes
2584 | RM22LG11MT | Offer Sustainability | RoHS exemption information | Yes
2585 | RM22LG11MT | Offer Sustainability | China RoHS Regulation | China RoHS declaration
2586 | RM22LG11MT | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
2587 | RM22LG11MT | Offer Sustainability | Circularity Profile | End of Life Information
2588 | RM22LG11MT | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
2589 | RM22TA31 | Main | range of product | Zelio Control
2590 | RM22TA31 | Main | product or component type | Modular measurement and control relays
2591 | RM22TA31 | Main | relay type | Control relay
2592 | RM22TA31 | Main | network number of phases | 3 phases
2593 | RM22TA31 | Main | relay name | RM22TA
2594 | RM22TA31 | Main | relay monitored parameters | Asymmetry Phase failure detection Phase sequence
2595 | RM22TA31 | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
2596 | RM22TA31 | Main | switching capacity in VA | 2000 VA
2597 | RM22TA31 | Main | measurement range | 200...240 V voltage AC
2598 | RM22TA31 | Complementary | reset time | 1500 ms at maximum voltage
2599 | RM22TA31 | Complementary | maximum switching voltage | 250 V AC
2600 | RM22TA31 | Complementary | minimum switching current | 10 mA at 5 V DC
2601 | RM22TA31 | Complementary | maximum switching current | 8 A AC
2602 | RM22TA31 | Complementary | [Us] rated supply voltage | 200...240 V AC
2603 | RM22TA31 | Complementary | supply voltage limits | 160…288 V AC
2604 | RM22TA31 | Complementary | operating limits | - 20 % + 20 % Un
2605 | RM22TA31 | Complementary | power consumption in VA | 10 VA at 240 V AC 60 Hz
2606 | RM22TA31 | Complementary | voltage detection threshold | < 100 V AC
2607 | RM22TA31 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
2608 | RM22TA31 | Complementary | output contacts | 2 C/O
2609 | RM22TA31 | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
2610 | RM22TA31 | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
2611 | RM22TA31 | Complementary | setting accuracy of time delay | 10 %
2612 | RM22TA31 | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
2613 | RM22TA31 | Complementary | hysteresis | 2 % fixed of selectable
2614 | RM22TA31 | Complementary | run-up delay at power-up | 650 ms
2615 | RM22TA31 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
2616 | RM22TA31 | Complementary | threshold adjustment voltage | 2...20 % of Un selected
2617 | RM22TA31 | Complementary | voltage range | 200...240 V phase to phase
2618 | RM22TA31 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
2619 | RM22TA31 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 3 % for time delay
2620 | RM22TA31 | Complementary | measurement error | < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation
2621 | RM22TA31 | Complementary | response time | <= 300 ms
2622 | RM22TA31 | Complementary | overvoltage category | III conforming to IEC 60664-1 III conforming to UL 508
2623 | RM22TA31 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
2624 | RM22TA31 | Complementary | mounting position | Any position
2625 | RM22TA31 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
2626 | RM22TA31 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
2627 | RM22TA31 | Complementary | housing material | Self-extinguishing plastic
2628 | RM22TA31 | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
2629 | RM22TA31 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
2630 | RM22TA31 | Complementary | electrical durability | 100000 cycles
2631 | RM22TA31 | Complementary | mechanical durability | 10000000 cycles
2632 | RM22TA31 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
2633 | RM22TA31 | Complementary | safety reliability data | MTTFd = 388.1 years B10d = 350000
2634 | RM22TA31 | Complementary | contacts material | Cadmium free
2635 | RM22TA31 | Complementary | width | 22.5 mm
2636 | RM22TA31 | Complementary | net weight | 0.09 kg
2637 | RM22TA31 | Environment | immunity to microbreaks | 10 ms
2638 | RM22TA31 | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
2639 | RM22TA31 | Environment | standards | EN/IEC 60255-1
2640 | RM22TA31 | Environment | product certifications | GL EAC China RoHS UL CSA RCM CCC CE
2641 | RM22TA31 | Environment | ambient air temperature for storage | -40…70 °C
2642 | RM22TA31 | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
2643 | RM22TA31 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
2644 | RM22TA31 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
2645 | RM22TA31 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
2646 | RM22TA31 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
2647 | RM22TA31 | Environment | pollution degree | 3 conforming to IEC 60664-1 3 conforming to UL 508
2648 | RM22TA31 | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
2649 | RM22TA31 | Offer Sustainability | Sustainable offer status | Green Premium product
2650 | RM22TA31 | Offer Sustainability | REACh Regulation | REACh Declaration
2651 | RM22TA31 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
2652 | RM22TA31 | Offer Sustainability | Mercury free | Yes
2653 | RM22TA31 | Offer Sustainability | RoHS exemption information | Yes
2654 | RM22TA31 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
2655 | RM22TA31 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
2656 | RM22TA31 | Offer Sustainability | Circularity Profile | End of Life Information
2657 | RM22TA31 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
2658 | RM22TA33 | Main | range of product | Zelio Control
2659 | RM22TA33 | Main | product or component type | Modular measurement and control relays
2660 | RM22TA33 | Main | relay type | Control relay
2661 | RM22TA33 | Main | network number of phases | 3 phases
2662 | RM22TA33 | Main | relay name | RM22TA
2663 | RM22TA33 | Main | relay monitored parameters | Phase sequence Phase failure detection Asymmetry
2664 | RM22TA33 | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
2665 | RM22TA33 | Main | switching capacity in VA | 2000 VA
2666 | RM22TA33 | Main | measurement range | 380...480 V voltage AC
2667 | RM22TA33 | Complementary | reset time | 1500 ms at maximum voltage
2668 | RM22TA33 | Complementary | maximum switching voltage | 250 V AC
2669 | RM22TA33 | Complementary | minimum switching current | 10 mA at 5 V DC
2670 | RM22TA33 | Complementary | maximum switching current | 8 A AC
2671 | RM22TA33 | Complementary | [Us] rated supply voltage | 380...480 V AC
2672 | RM22TA33 | Complementary | supply voltage limits | 304…576 V AC
2673 | RM22TA33 | Complementary | operating limits | - 20 % + 20 % Un
2674 | RM22TA33 | Complementary | power consumption in VA | 15 VA at 480 V AC 60 Hz
2675 | RM22TA33 | Complementary | voltage detection threshold | < 100 V AC
2676 | RM22TA33 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
2677 | RM22TA33 | Complementary | output contacts | 2 C/O
2678 | RM22TA33 | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
2679 | RM22TA33 | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
2680 | RM22TA33 | Complementary | setting accuracy of time delay | 10 %
2681 | RM22TA33 | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
2682 | RM22TA33 | Complementary | hysteresis | 2 % fixed of selectable
2683 | RM22TA33 | Complementary | run-up delay at power-up | 650 ms
2684 | RM22TA33 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
2685 | RM22TA33 | Complementary | threshold adjustment voltage | 2...20 % of Un selected
2686 | RM22TA33 | Complementary | voltage range | 380...480 V phase to phase
2687 | RM22TA33 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
2688 | RM22TA33 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 3 % for time delay
2689 | RM22TA33 | Complementary | measurement error | < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation
2690 | RM22TA33 | Complementary | response time | <= 300 ms
2691 | RM22TA33 | Complementary | overvoltage category | III conforming to IEC 60664-1 III conforming to UL 508
2692 | RM22TA33 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
2693 | RM22TA33 | Complementary | mounting position | Any position
2694 | RM22TA33 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
2695 | RM22TA33 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
2696 | RM22TA33 | Complementary | housing material | Self-extinguishing plastic
2697 | RM22TA33 | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
2698 | RM22TA33 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
2699 | RM22TA33 | Complementary | electrical durability | 100000 cycles
2700 | RM22TA33 | Complementary | mechanical durability | 10000000 cycles
2701 | RM22TA33 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
2702 | RM22TA33 | Complementary | safety reliability data | MTTFd = 388.1 years B10d = 350000
2703 | RM22TA33 | Complementary | contacts material | Cadmium free
2704 | RM22TA33 | Complementary | width | 22.5 mm
2705 | RM22TA33 | Complementary | net weight | 0.09 kg
2706 | RM22TA33 | Environment | immunity to microbreaks | 10 ms
2707 | RM22TA33 | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
2708 | RM22TA33 | Environment | standards | EN/IEC 60255-1
2709 | RM22TA33 | Environment | product certifications | GL EAC CCC CE CSA China RoHS UL RCM
2710 | RM22TA33 | Environment | ambient air temperature for storage | -40…70 °C
2711 | RM22TA33 | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
2712 | RM22TA33 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
2713 | RM22TA33 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
2714 | RM22TA33 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
2715 | RM22TA33 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
2716 | RM22TA33 | Environment | pollution degree | 3 conforming to IEC 60664-1 3 conforming to UL 508
2717 | RM22TA33 | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
2718 | RM22TA33 | Offer Sustainability | Sustainable offer status | Green Premium product
2719 | RM22TA33 | Offer Sustainability | REACh Regulation | REACh Declaration
2720 | RM22TA33 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
2721 | RM22TA33 | Offer Sustainability | Mercury free | Yes
2722 | RM22TA33 | Offer Sustainability | RoHS exemption information | Yes
2723 | RM22TA33 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
2724 | RM22TA33 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
2725 | RM22TA33 | Offer Sustainability | Circularity Profile | End of Life Information
2726 | RM22TA33 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
2727 | RM22TG20 | Main | range of product | Zelio Control
2728 | RM22TG20 | Main | product or component type | Modular measurement and control relays
2729 | RM22TG20 | Main | relay type | Control relay
2730 | RM22TG20 | Main | network number of phases | 3 phases
2731 | RM22TG20 | Main | relay name | RM22TG
2732 | RM22TG20 | Main | relay monitored parameters | Phase sequence Phase failure detection (2 or more phase cut)
2733 | RM22TG20 | Main | time delay type | Without
2734 | RM22TG20 | Main | switching capacity in VA | 2000 VA
2735 | RM22TG20 | Main | measurement range | 183...528 V voltage AC
2736 | RM22TG20 | Complementary | reset time | 1500 ms at maximum voltage
2737 | RM22TG20 | Complementary | maximum switching voltage | 250 V AC
2738 | RM22TG20 | Complementary | minimum switching current | 10 mA at 5 V DC
2739 | RM22TG20 | Complementary | maximum switching current | 8 A AC
2740 | RM22TG20 | Complementary | [Us] rated supply voltage | 208...480 V AC
2741 | RM22TG20 | Complementary | supply voltage limits | 183…528 V AC
2742 | RM22TG20 | Complementary | operating limits | 183...528 V AC
2743 | RM22TG20 | Complementary | power consumption in VA | 15 VA at 480 V AC 60 Hz
2744 | RM22TG20 | Complementary | voltage detection threshold | < 100 V AC
2745 | RM22TG20 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
2746 | RM22TG20 | Complementary | output contacts | 2 C/O
2747 | RM22TG20 | Complementary | run-up delay at power-up | 650 ms
2748 | RM22TG20 | Complementary | response time | <= 200 ms
2749 | RM22TG20 | Complementary | overvoltage category | III conforming to IEC 60664-1 III conforming to UL 508
2750 | RM22TG20 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
2751 | RM22TG20 | Complementary | mounting position | Any position
2752 | RM22TG20 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
2753 | RM22TG20 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
2754 | RM22TG20 | Complementary | housing material | Self-extinguishing plastic
2755 | RM22TG20 | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
2756 | RM22TG20 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
2757 | RM22TG20 | Complementary | electrical durability | 100000 cycles
2758 | RM22TG20 | Complementary | mechanical durability | 10000000 cycles
2759 | RM22TG20 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
2760 | RM22TG20 | Complementary | safety reliability data | MTTFd = 924.6 years B10d = 850000
2761 | RM22TG20 | Complementary | contacts material | Cadmium free
2762 | RM22TG20 | Complementary | width | 22.5 mm
2763 | RM22TG20 | Complementary | net weight | 0.09 kg
2764 | RM22TG20 | Environment | immunity to microbreaks | 10 ms
2765 | RM22TG20 | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
2766 | RM22TG20 | Environment | standards | EN/IEC 60255-1
2767 | RM22TG20 | Environment | product certifications | CE EAC China RoHS RCM GL CSA UL CCC
2768 | RM22TG20 | Environment | ambient air temperature for storage | -40…70 °C
2769 | RM22TG20 | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
2770 | RM22TG20 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
2771 | RM22TG20 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
2772 | RM22TG20 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
2773 | RM22TG20 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
2774 | RM22TG20 | Environment | pollution degree | 3 conforming to IEC 60664-1 3 conforming to UL 508
2775 | RM22TG20 | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
2776 | RM22TG20 | Offer Sustainability | Sustainable offer status | Green Premium product
2777 | RM22TG20 | Offer Sustainability | REACh Regulation | REACh Declaration
2778 | RM22TG20 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
2779 | RM22TG20 | Offer Sustainability | Mercury free | Yes
2780 | RM22TG20 | Offer Sustainability | RoHS exemption information | Yes
2781 | RM22TG20 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
2782 | RM22TG20 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
2783 | RM22TG20 | Offer Sustainability | Circularity Profile | End of Life Information
2784 | RM22TG20 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
2785 | RM22TR31 | Main | range of product | Zelio Control
2786 | RM22TR31 | Main | product or component type | Modular measurement and control relays
2787 | RM22TR31 | Main | relay type | Control relay
2788 | RM22TR31 | Main | network number of phases | 3 phases
2789 | RM22TR31 | Main | relay name | RM22TR
2790 | RM22TR31 | Main | relay monitored parameters | Phase sequence Phase failure detection Overvoltage and undervoltage detection
2791 | RM22TR31 | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
2792 | RM22TR31 | Main | switching capacity in VA | 2000 VA
2793 | RM22TR31 | Main | measurement range | 200...240 V voltage AC
2794 | RM22TR31 | Complementary | reset time | 1500 ms at maximum voltage
2795 | RM22TR31 | Complementary | maximum switching voltage | 250 V AC
2796 | RM22TR31 | Complementary | minimum switching current | 10 mA at 5 V DC
2797 | RM22TR31 | Complementary | maximum switching current | 8 A AC
2798 | RM22TR31 | Complementary | [Us] rated supply voltage | 200...240 V AC
2799 | RM22TR31 | Complementary | supply voltage limits | 160…288 V AC
2800 | RM22TR31 | Complementary | operating limits | - 20 % + 20 % Un
2801 | RM22TR31 | Complementary | power consumption in VA | 10 VA at 240 V AC 60 Hz
2802 | RM22TR31 | Complementary | voltage detection threshold | < 100 V AC
2803 | RM22TR31 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
2804 | RM22TR31 | Complementary | output contacts | 2 C/O
2805 | RM22TR31 | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
2806 | RM22TR31 | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
2807 | RM22TR31 | Complementary | setting accuracy of time delay | 10 %
2808 | RM22TR31 | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
2809 | RM22TR31 | Complementary | hysteresis | 2 % fixed of selectable
2810 | RM22TR31 | Complementary | run-up delay at power-up | 650 ms
2811 | RM22TR31 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
2812 | RM22TR31 | Complementary | threshold adjustment voltage | 2...20 % of Un selected
2813 | RM22TR31 | Complementary | voltage range | 200...240 V phase to phase
2814 | RM22TR31 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 3 % for time delay
2815 | RM22TR31 | Complementary | measurement error | < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation
2816 | RM22TR31 | Complementary | response time | <= 300 ms
2817 | RM22TR31 | Complementary | overvoltage category | III conforming to IEC 60664-1 III conforming to UL 508
2818 | RM22TR31 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
2819 | RM22TR31 | Complementary | mounting position | Any position
2820 | RM22TR31 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
2821 | RM22TR31 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
2822 | RM22TR31 | Complementary | housing material | Self-extinguishing plastic
2823 | RM22TR31 | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
2824 | RM22TR31 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
2825 | RM22TR31 | Complementary | electrical durability | 100000 cycles
2826 | RM22TR31 | Complementary | mechanical durability | 10000000 cycles
2827 | RM22TR31 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
2828 | RM22TR31 | Complementary | safety reliability data | MTTFd = 388.1 years B10d = 350000
2829 | RM22TR31 | Complementary | contacts material | Cadmium free
2830 | RM22TR31 | Complementary | width | 22.5 mm
2831 | RM22TR31 | Complementary | net weight | 0.09 kg
2832 | RM22TR31 | Environment | immunity to microbreaks | 10 ms
2833 | RM22TR31 | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
2834 | RM22TR31 | Environment | standards | EN/IEC 60255-1
2835 | RM22TR31 | Environment | product certifications | CSA CCC EAC China RoHS RCM CE GL UL
2836 | RM22TR31 | Environment | ambient air temperature for storage | -40…70 °C
2837 | RM22TR31 | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
2838 | RM22TR31 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
2839 | RM22TR31 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
2840 | RM22TR31 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
2841 | RM22TR31 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
2842 | RM22TR31 | Environment | pollution degree | 3 conforming to IEC 60664-1 3 conforming to UL 508
2843 | RM22TR31 | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
2844 | RM22TR31 | Offer Sustainability | Sustainable offer status | Green Premium product
2845 | RM22TR31 | Offer Sustainability | REACh Regulation | REACh Declaration
2846 | RM22TR31 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
2847 | RM22TR31 | Offer Sustainability | Mercury free | Yes
2848 | RM22TR31 | Offer Sustainability | RoHS exemption information | Yes
2849 | RM22TR31 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
2850 | RM22TR31 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
2851 | RM22TR31 | Offer Sustainability | Circularity Profile | End of Life Information
2852 | RM22TR31 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
2853 | RM22TR33 | Main | range of product | Zelio Control
2854 | RM22TR33 | Main | product or component type | Modular measurement and control relays
2855 | RM22TR33 | Main | relay type | Control relay
2856 | RM22TR33 | Main | network number of phases | 3 phases
2857 | RM22TR33 | Main | relay name | RM22TR
2858 | RM22TR33 | Main | relay monitored parameters | Overvoltage and undervoltage detection Phase sequence Phase failure detection
2859 | RM22TR33 | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
2860 | RM22TR33 | Main | switching capacity in VA | 2000 VA
2861 | RM22TR33 | Main | measurement range | 380...480 V voltage AC
2862 | RM22TR33 | Complementary | reset time | 1500 ms at maximum voltage
2863 | RM22TR33 | Complementary | maximum switching voltage | 250 V AC
2864 | RM22TR33 | Complementary | minimum switching current | 10 mA at 5 V DC
2865 | RM22TR33 | Complementary | maximum switching current | 8 A AC
2866 | RM22TR33 | Complementary | [Us] rated supply voltage | 380...480 V AC
2867 | RM22TR33 | Complementary | supply voltage limits | 304…576 V AC
2868 | RM22TR33 | Complementary | operating limits | - 20 % + 20 % Un
2869 | RM22TR33 | Complementary | power consumption in VA | 15 VA at 480 V AC 60 Hz
2870 | RM22TR33 | Complementary | voltage detection threshold | < 100 V AC
2871 | RM22TR33 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
2872 | RM22TR33 | Complementary | output contacts | 2 C/O
2873 | RM22TR33 | Complementary | nominal output current | 8 A
2874 | RM22TR33 | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
2875 | RM22TR33 | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
2876 | RM22TR33 | Complementary | setting accuracy of time delay | 10 P
2877 | RM22TR33 | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
2878 | RM22TR33 | Complementary | hysteresis | 2 % fixed of selectable
2879 | RM22TR33 | Complementary | run-up delay at power-up | 650 ms
2880 | RM22TR33 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
2881 | RM22TR33 | Complementary | threshold adjustment voltage | 2...20 % of Un selected
2882 | RM22TR33 | Complementary | voltage range | 380...480 V phase to phase
2883 | RM22TR33 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 3 % for time delay
2884 | RM22TR33 | Complementary | measurement error | < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation
2885 | RM22TR33 | Complementary | response time | <= 300 ms
2886 | RM22TR33 | Complementary | overvoltage category | III conforming to IEC 60664-1 III conforming to UL 508
2887 | RM22TR33 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
2888 | RM22TR33 | Complementary | mounting position | Any position
2889 | RM22TR33 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
2890 | RM22TR33 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
2891 | RM22TR33 | Complementary | housing material | Self-extinguishing plastic
2892 | RM22TR33 | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
2893 | RM22TR33 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
2894 | RM22TR33 | Complementary | electrical durability | 100000 cycles
2895 | RM22TR33 | Complementary | mechanical durability | 10000000 cycles
2896 | RM22TR33 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
2897 | RM22TR33 | Complementary | safety reliability data | MTTFd = 388.1 years B10d = 350000
2898 | RM22TR33 | Complementary | contacts material | Cadmium free
2899 | RM22TR33 | Complementary | width | 22.5 mm
2900 | RM22TR33 | Complementary | net weight | 0.09 kg
2901 | RM22TR33 | Environment | immunity to microbreaks | 10 ms
2902 | RM22TR33 | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
2903 | RM22TR33 | Environment | standards | EN/IEC 60255-1
2904 | RM22TR33 | Environment | product certifications | GL China RoHS CSA RCM CE EAC CCC UL
2905 | RM22TR33 | Environment | ambient air temperature for storage | -40…70 °C
2906 | RM22TR33 | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
2907 | RM22TR33 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
2908 | RM22TR33 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
2909 | RM22TR33 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
2910 | RM22TR33 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
2911 | RM22TR33 | Environment | pollution degree | 3 conforming to IEC 60664-1 3 conforming to UL 508
2912 | RM22TR33 | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
2913 | RM22TR33 | Offer Sustainability | Sustainable offer status | Green Premium product
2914 | RM22TR33 | Offer Sustainability | REACh Regulation | REACh Declaration
2915 | RM22TR33 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
2916 | RM22TR33 | Offer Sustainability | Mercury free | Yes
2917 | RM22TR33 | Offer Sustainability | RoHS exemption information | Yes
2918 | RM22TR33 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
2919 | RM22TR33 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
2920 | RM22TR33 | Offer Sustainability | Circularity Profile | End of Life Information
2921 | RM22TR33 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
2922 | RM22TU21 | Main | range of product | Zelio Control
2923 | RM22TU21 | Main | product or component type | Modular measurement and control relays
2924 | RM22TU21 | Main | relay type | Control relay
2925 | RM22TU21 | Main | network number of phases | 3 phases
2926 | RM22TU21 | Main | relay name | RM22TR
2927 | RM22TU21 | Main | relay monitored parameters | Undervoltage detection Phase sequence Phase failure detection
2928 | RM22TU21 | Main | time delay type | Without
2929 | RM22TU21 | Main | switching capacity in VA | 2000 VA
2930 | RM22TU21 | Main | measurement range | 200...240 V voltage AC
2931 | RM22TU21 | Complementary | reset time | 1500 ms at maximum voltage
2932 | RM22TU21 | Complementary | maximum switching voltage | 250 V AC
2933 | RM22TU21 | Complementary | minimum switching current | 10 mA at 5 V DC
2934 | RM22TU21 | Complementary | maximum switching current | 8 A AC
2935 | RM22TU21 | Complementary | [Us] rated supply voltage | 200...240 V AC
2936 | RM22TU21 | Complementary | supply voltage limits | 160…288 V AC
2937 | RM22TU21 | Complementary | operating limits | - 20 % + 20 % Un
2938 | RM22TU21 | Complementary | power consumption in VA | 10 VA at 240 V AC 60 Hz
2939 | RM22TU21 | Complementary | voltage detection threshold | < 100 V AC
2940 | RM22TU21 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
2941 | RM22TU21 | Complementary | output contacts | 2 C/O
2942 | RM22TU21 | Complementary | nominal output current | 8 A
2943 | RM22TU21 | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
2944 | RM22TU21 | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
2945 | RM22TU21 | Complementary | setting accuracy of time delay | 10 %
2946 | RM22TU21 | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
2947 | RM22TU21 | Complementary | hysteresis | 2 % fixed of selectable
2948 | RM22TU21 | Complementary | run-up delay at power-up | 650 ms
2949 | RM22TU21 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
2950 | RM22TU21 | Complementary | threshold adjustment voltage | 2...20 % of Un selected
2951 | RM22TU21 | Complementary | voltage range | 200...240 V phase to phase
2952 | RM22TU21 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit
2953 | RM22TU21 | Complementary | measurement error | < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation
2954 | RM22TU21 | Complementary | response time | <= 300 ms
2955 | RM22TU21 | Complementary | overvoltage category | III conforming to IEC 60664-1 III conforming to UL 508
2956 | RM22TU21 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
2957 | RM22TU21 | Complementary | mounting position | Any position
2958 | RM22TU21 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
2959 | RM22TU21 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
2960 | RM22TU21 | Complementary | housing material | Self-extinguishing plastic
2961 | RM22TU21 | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
2962 | RM22TU21 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
2963 | RM22TU21 | Complementary | electrical durability | 100000 cycles
2964 | RM22TU21 | Complementary | mechanical durability | 10000000 cycles
2965 | RM22TU21 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
2966 | RM22TU21 | Complementary | safety reliability data | B10d = 350000 MTTFd = 388.1 years
2967 | RM22TU21 | Complementary | contacts material | Cadmium free
2968 | RM22TU21 | Complementary | width | 22.5 mm
2969 | RM22TU21 | Complementary | net weight | 0.09 kg
2970 | RM22TU21 | Environment | immunity to microbreaks | 10 ms
2971 | RM22TU21 | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
2972 | RM22TU21 | Environment | standards | EN/IEC 60255-1
2973 | RM22TU21 | Environment | product certifications | RCM CE China RoHS CSA GL CCC UL EAC
2974 | RM22TU21 | Environment | ambient air temperature for storage | -40…70 °C
2975 | RM22TU21 | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
2976 | RM22TU21 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
2977 | RM22TU21 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
2978 | RM22TU21 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
2979 | RM22TU21 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
2980 | RM22TU21 | Environment | pollution degree | 3 conforming to IEC 60664-1 3 conforming to UL 508
2981 | RM22TU21 | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
2982 | RM22TU21 | Offer Sustainability | Sustainable offer status | Green Premium product
2983 | RM22TU21 | Offer Sustainability | REACh Regulation | REACh Declaration
2984 | RM22TU21 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
2985 | RM22TU21 | Offer Sustainability | Mercury free | Yes
2986 | RM22TU21 | Offer Sustainability | RoHS exemption information | Yes
2987 | RM22TU21 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
2988 | RM22TU21 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
2989 | RM22TU21 | Offer Sustainability | Circularity Profile | End of Life Information
2990 | RM22TU21 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
2991 | RM22TU23 | Main | range of product | Zelio Control
2992 | RM22TU23 | Main | product or component type | Modular measurement and control relays
2993 | RM22TU23 | Main | relay type | Control relay
2994 | RM22TU23 | Main | network number of phases | 3 phases
2995 | RM22TU23 | Main | relay name | RM22TR
2996 | RM22TU23 | Main | relay monitored parameters | Undervoltage detection Phase sequence Phase failure detection
2997 | RM22TU23 | Main | time delay type | Without
2998 | RM22TU23 | Main | switching capacity in VA | 2000 VA
2999 | RM22TU23 | Main | measurement range | 380...480 V voltage AC
3000 | RM22TU23 | Complementary | reset time | 1500 ms at maximum voltage
3001 | RM22TU23 | Complementary | maximum switching voltage | 250 V AC
3002 | RM22TU23 | Complementary | minimum switching current | 10 mA at 5 V DC
3003 | RM22TU23 | Complementary | maximum switching current | 8 A AC
3004 | RM22TU23 | Complementary | [Us] rated supply voltage | 380...480 V AC
3005 | RM22TU23 | Complementary | supply voltage limits | 304…576 V AC
3006 | RM22TU23 | Complementary | operating limits | - 20 % + 20 % Un
3007 | RM22TU23 | Complementary | power consumption in VA | 15 VA at 480 V AC 60 Hz
3008 | RM22TU23 | Complementary | voltage detection threshold | < 100 V AC
3009 | RM22TU23 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
3010 | RM22TU23 | Complementary | output contacts | 2 C/O
3011 | RM22TU23 | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
3012 | RM22TU23 | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
3013 | RM22TU23 | Complementary | setting accuracy of time delay | 10 %
3014 | RM22TU23 | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
3015 | RM22TU23 | Complementary | hysteresis | 2 % fixed of selectable
3016 | RM22TU23 | Complementary | run-up delay at power-up | 650 ms
3017 | RM22TU23 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
3018 | RM22TU23 | Complementary | threshold adjustment voltage | 2...20 % of Un selected
3019 | RM22TU23 | Complementary | voltage range | 380...480 V phase to phase
3020 | RM22TU23 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit
3021 | RM22TU23 | Complementary | measurement error | < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation
3022 | RM22TU23 | Complementary | response time | <= 300 ms
3023 | RM22TU23 | Complementary | overvoltage category | III conforming to IEC 60664-1 III conforming to UL 508
3024 | RM22TU23 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
3025 | RM22TU23 | Complementary | mounting position | Any position
3026 | RM22TU23 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
3027 | RM22TU23 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
3028 | RM22TU23 | Complementary | housing material | Self-extinguishing plastic
3029 | RM22TU23 | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
3030 | RM22TU23 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
3031 | RM22TU23 | Complementary | electrical durability | 100000 cycles
3032 | RM22TU23 | Complementary | mechanical durability | 10000000 cycles
3033 | RM22TU23 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
3034 | RM22TU23 | Complementary | safety reliability data | MTTFd = 388.1 years B10d = 350000
3035 | RM22TU23 | Complementary | contacts material | Cadmium free
3036 | RM22TU23 | Complementary | width | 22.5 mm
3037 | RM22TU23 | Complementary | net weight | 0.09 kg
3038 | RM22TU23 | Environment | immunity to microbreaks | 10 ms
3039 | RM22TU23 | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
3040 | RM22TU23 | Environment | standards | EN/IEC 60255-1
3041 | RM22TU23 | Environment | product certifications | CSA RCM UL GL China RoHS CE CCC EAC
3042 | RM22TU23 | Environment | ambient air temperature for storage | -40…70 °C
3043 | RM22TU23 | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
3044 | RM22TU23 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
3045 | RM22TU23 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
3046 | RM22TU23 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
3047 | RM22TU23 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
3048 | RM22TU23 | Environment | pollution degree | 3 conforming to IEC 60664-1 3 conforming to UL 508
3049 | RM22TU23 | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
3050 | RM22TU23 | Offer Sustainability | Sustainable offer status | Green Premium product
3051 | RM22TU23 | Offer Sustainability | REACh Regulation | REACh Declaration
3052 | RM22TU23 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
3053 | RM22TU23 | Offer Sustainability | Mercury free | Yes
3054 | RM22TU23 | Offer Sustainability | RoHS exemption information | Yes
3055 | RM22TU23 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
3056 | RM22TU23 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
3057 | RM22TU23 | Offer Sustainability | Circularity Profile | End of Life Information
3058 | RM22TU23 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
3059 | RM22UA21MR | Main | range of product | Zelio Control
3060 | RM22UA21MR | Main | product or component type | Modular measurement and control relays
3061 | RM22UA21MR | Main | relay type | Voltage control relay
3062 | RM22UA21MR | Main | network number of phases | 1 phase
3063 | RM22UA21MR | Main | supply circuit type | DC
3064 | RM22UA21MR | Main | relay name | RM22UA
3065 | RM22UA21MR | Main | relay monitored parameters | Overvoltage detection
3066 | RM22UA21MR | Main | time delay type | Without
3067 | RM22UA21MR | Main | switching capacity in VA | 2000 VA
3068 | RM22UA21MR | Main | measurement range | 50 mV...5 V voltage AC/DC 50/60 Hz
3069 | RM22UA21MR | Complementary | reset time | 1500 ms at maximum voltage
3070 | RM22UA21MR | Complementary | maximum switching voltage | 250 V AC
3071 | RM22UA21MR | Complementary | minimum switching current | 10 mA at 5 V DC
3072 | RM22UA21MR | Complementary | maximum switching current | 8 A AC
3073 | RM22UA21MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
3074 | RM22UA21MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
3075 | RM22UA21MR | Complementary | power consumption in VA | 3.5 VA AC
3076 | RM22UA21MR | Complementary | maximum power consumption in W | 1.5 W DC
3077 | RM22UA21MR | Complementary | supply voltage frequency | 40...70 Hz +/- 10 %
3078 | RM22UA21MR | Complementary | resistance across terminals | 30 kOhm at E2-M terminals 5 kOhm at E1-M terminals 50 kOhm at E3-M terminals
3079 | RM22UA21MR | Complementary | output contacts | 2 C/O
3080 | RM22UA21MR | Complementary | hysteresis | 5…50 % adjustable of threshold setting
3081 | RM22UA21MR | Complementary | run-up delay at power-up | 600 ms
3082 | RM22UA21MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
3083 | RM22UA21MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit
3084 | RM22UA21MR | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
3085 | RM22UA21MR | Complementary | response time | <= 500 ms
3086 | RM22UA21MR | Complementary | overvoltage category | III conforming to IEC 60664-1
3087 | RM22UA21MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
3088 | RM22UA21MR | Complementary | insulation | Between supply and measurement
3089 | RM22UA21MR | Complementary | mounting position | Any position
3090 | RM22UA21MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
3091 | RM22UA21MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
3092 | RM22UA21MR | Complementary | housing material | Self-extinguishing plastic
3093 | RM22UA21MR | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
3094 | RM22UA21MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
3095 | RM22UA21MR | Complementary | electrical durability | 100000 cycles
3096 | RM22UA21MR | Complementary | mechanical durability | 10000000 cycles
3097 | RM22UA21MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
3098 | RM22UA21MR | Complementary | safety reliability data | B10d = 290000 MTTFd = 308.2 years
3099 | RM22UA21MR | Complementary | contacts material | Cadmium free
3100 | RM22UA21MR | Complementary | width | 22.5 mm
3101 | RM22UA21MR | Complementary | net weight | 0.11 kg
3102 | RM22UA21MR | Environment | immunity to microbreaks | 10 ms
3103 | RM22UA21MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
3104 | RM22UA21MR | Environment | standards | EN/IEC 60255-1
3105 | RM22UA21MR | Environment | product certifications | UL China RoHS EAC CSA GL CCC RCM CE
3106 | RM22UA21MR | Environment | ambient air temperature for storage | -40…70 °C
3107 | RM22UA21MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
3108 | RM22UA21MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
3109 | RM22UA21MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
3110 | RM22UA21MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
3111 | RM22UA21MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
3112 | RM22UA21MR | Environment | pollution degree | 3 conforming to IEC 60664-1
3113 | RM22UA21MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
3114 | RM22UA21MR | Offer Sustainability | Sustainable offer status | Green Premium product
3115 | RM22UA21MR | Offer Sustainability | REACh Regulation | REACh Declaration
3116 | RM22UA21MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
3117 | RM22UA21MR | Offer Sustainability | Mercury free | Yes
3118 | RM22UA21MR | Offer Sustainability | RoHS exemption information | Yes
3119 | RM22UA21MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
3120 | RM22UA21MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
3121 | RM22UA21MR | Offer Sustainability | Circularity Profile | End of Life Information
3122 | RM22UA21MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
3123 | RM22UA22MR | Main | range of product | Zelio Control
3124 | RM22UA22MR | Main | product or component type | Modular measurement and control relays
3125 | RM22UA22MR | Main | relay type | Voltage control relay
3126 | RM22UA22MR | Main | network number of phases | 1 phase
3127 | RM22UA22MR | Main | supply circuit type | DC
3128 | RM22UA22MR | Main | relay name | RM22UA
3129 | RM22UA22MR | Main | relay monitored parameters | Overvoltage detection
3130 | RM22UA22MR | Main | time delay type | Without
3131 | RM22UA22MR | Main | switching capacity in VA | 2000 VA
3132 | RM22UA22MR | Main | measurement range | 1...100 V voltage AC/DC 50/60 Hz
3133 | RM22UA22MR | Complementary | reset time | 1500 ms at maximum voltage
3134 | RM22UA22MR | Complementary | maximum switching voltage | 250 V AC
3135 | RM22UA22MR | Complementary | minimum switching current | 10 mA at 5 V DC
3136 | RM22UA22MR | Complementary | maximum switching current | 8 A AC
3137 | RM22UA22MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
3138 | RM22UA22MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
3139 | RM22UA22MR | Complementary | power consumption in VA | 3.5 VA AC
3140 | RM22UA22MR | Complementary | maximum power consumption in W | 1.5 W DC
3141 | RM22UA22MR | Complementary | supply voltage frequency | 40...70 Hz +/- 10 %
3142 | RM22UA22MR | Complementary | resistance across terminals | 110 kOhm at E2-M terminals 22 kOhm at E1-M terminals 220 kOhm at E3-M terminals
3143 | RM22UA22MR | Complementary | output contacts | 2 C/O
3144 | RM22UA22MR | Complementary | hysteresis | 5…50 % adjustable of threshold setting
3145 | RM22UA22MR | Complementary | run-up delay at power-up | 600 ms
3146 | RM22UA22MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
3147 | RM22UA22MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit
3148 | RM22UA22MR | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
3149 | RM22UA22MR | Complementary | response time | <= 500 ms
3150 | RM22UA22MR | Complementary | overvoltage category | III conforming to IEC 60664-1
3151 | RM22UA22MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
3152 | RM22UA22MR | Complementary | insulation | Between supply and measurement
3153 | RM22UA22MR | Complementary | mounting position | Any position
3154 | RM22UA22MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
3155 | RM22UA22MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
3156 | RM22UA22MR | Complementary | housing material | Self-extinguishing plastic
3157 | RM22UA22MR | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
3158 | RM22UA22MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
3159 | RM22UA22MR | Complementary | electrical durability | 100000 cycles
3160 | RM22UA22MR | Complementary | mechanical durability | 10000000 cycles
3161 | RM22UA22MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
3162 | RM22UA22MR | Complementary | safety reliability data | B10d = 290000 MTTFd = 308.2 years
3163 | RM22UA22MR | Complementary | contacts material | Cadmium free
3164 | RM22UA22MR | Complementary | width | 22.5 mm
3165 | RM22UA22MR | Complementary | net weight | 0.11 kg
3166 | RM22UA22MR | Environment | immunity to microbreaks | 10 ms
3167 | RM22UA22MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
3168 | RM22UA22MR | Environment | standards | EN/IEC 60255-1
3169 | RM22UA22MR | Environment | product certifications | CE China RoHS CCC EAC CSA RCM UL GL
3170 | RM22UA22MR | Environment | ambient air temperature for storage | -40…70 °C
3171 | RM22UA22MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
3172 | RM22UA22MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
3173 | RM22UA22MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
3174 | RM22UA22MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
3175 | RM22UA22MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
3176 | RM22UA22MR | Environment | pollution degree | 3 conforming to IEC 60664-1
3177 | RM22UA22MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
3178 | RM22UA22MR | Offer Sustainability | Sustainable offer status | Green Premium product
3179 | RM22UA22MR | Offer Sustainability | REACh Regulation | REACh Declaration
3180 | RM22UA22MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
3181 | RM22UA22MR | Offer Sustainability | Mercury free | Yes
3182 | RM22UA22MR | Offer Sustainability | RoHS exemption information | Yes
3183 | RM22UA22MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
3184 | RM22UA22MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
3185 | RM22UA22MR | Offer Sustainability | Circularity Profile | End of Life Information
3186 | RM22UA22MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
3187 | RM22UA23MR | Main | range of product | Zelio Control
3188 | RM22UA23MR | Main | product or component type | Modular measurement and control relays
3189 | RM22UA23MR | Main | relay type | Voltage control relay
3190 | RM22UA23MR | Main | network number of phases | 1 phase
3191 | RM22UA23MR | Main | supply circuit type | DC
3192 | RM22UA23MR | Main | relay name | RM22UA
3193 | RM22UA23MR | Main | relay monitored parameters | Overvoltage detection
3194 | RM22UA23MR | Main | time delay type | Without
3195 | RM22UA23MR | Main | switching capacity in VA | 2000 VA
3196 | RM22UA23MR | Main | measurement range | 15...500 V voltage AC/DC 50/60 Hz
3197 | RM22UA23MR | Complementary | reset time | 1500 ms at maximum voltage
3198 | RM22UA23MR | Complementary | maximum switching voltage | 250 V AC
3199 | RM22UA23MR | Complementary | minimum switching current | 10 mA at 5 V DC
3200 | RM22UA23MR | Complementary | maximum switching current | 8 A AC
3201 | RM22UA23MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
3202 | RM22UA23MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
3203 | RM22UA23MR | Complementary | power consumption in VA | 3.5 VA AC
3204 | RM22UA23MR | Complementary | maximum power consumption in W | 1.5 W DC
3205 | RM22UA23MR | Complementary | supply voltage frequency | 40...70 Hz +/- 10 %
3206 | RM22UA23MR | Complementary | resistance across terminals | 150 kOhm at E2-M terminals 300 kOhm at E1-M terminals 500 kOhm at E3-M terminals
3207 | RM22UA23MR | Complementary | output contacts | 2 C/O
3208 | RM22UA23MR | Complementary | hysteresis | 5…50 % adjustable of threshold setting
3209 | RM22UA23MR | Complementary | run-up delay at power-up | 600 ms
3210 | RM22UA23MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
3211 | RM22UA23MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit
3212 | RM22UA23MR | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
3213 | RM22UA23MR | Complementary | response time | <= 500 ms
3214 | RM22UA23MR | Complementary | overvoltage category | III conforming to IEC 60664-1
3215 | RM22UA23MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
3216 | RM22UA23MR | Complementary | insulation | Between supply and measurement
3217 | RM22UA23MR | Complementary | mounting position | Any position
3218 | RM22UA23MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
3219 | RM22UA23MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
3220 | RM22UA23MR | Complementary | housing material | Self-extinguishing plastic
3221 | RM22UA23MR | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
3222 | RM22UA23MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
3223 | RM22UA23MR | Complementary | electrical durability | 100000 cycles
3224 | RM22UA23MR | Complementary | mechanical durability | 10000000 cycles
3225 | RM22UA23MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
3226 | RM22UA23MR | Complementary | safety reliability data | MTTFd = 308.2 years B10d = 290000
3227 | RM22UA23MR | Complementary | contacts material | Cadmium free
3228 | RM22UA23MR | Complementary | width | 22.5 mm
3229 | RM22UA23MR | Complementary | net weight | 0.11 kg
3230 | RM22UA23MR | Environment | immunity to microbreaks | 10 ms
3231 | RM22UA23MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
3232 | RM22UA23MR | Environment | standards | EN/IEC 60255-1
3233 | RM22UA23MR | Environment | product certifications | CE China RoHS CCC GL RCM UL EAC CSA
3234 | RM22UA23MR | Environment | ambient air temperature for storage | -40…70 °C
3235 | RM22UA23MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
3236 | RM22UA23MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
3237 | RM22UA23MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
3238 | RM22UA23MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
3239 | RM22UA23MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
3240 | RM22UA23MR | Environment | pollution degree | 3 conforming to IEC 60664-1
3241 | RM22UA23MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
3242 | RM22UA23MR | Offer Sustainability | Sustainable offer status | Green Premium product
3243 | RM22UA23MR | Offer Sustainability | REACh Regulation | REACh Declaration
3244 | RM22UA23MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
3245 | RM22UA23MR | Offer Sustainability | Mercury free | Yes
3246 | RM22UA23MR | Offer Sustainability | RoHS exemption information | Yes
3247 | RM22UA23MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
3248 | RM22UA23MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
3249 | RM22UA23MR | Offer Sustainability | Circularity Profile | End of Life Information
3250 | RM22UA23MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
3251 | RM22UA31MR | Main | range of product | Zelio Control
3252 | RM22UA31MR | Main | product or component type | Modular measurement and control relays
3253 | RM22UA31MR | Main | relay type | Voltage control relay
3254 | RM22UA31MR | Main | network number of phases | 1 phase
3255 | RM22UA31MR | Main | supply circuit type | DC
3256 | RM22UA31MR | Main | relay name | RM22UA
3257 | RM22UA31MR | Main | relay monitored parameters | Undervoltage and overvoltage in window mode Overvoltage or undervoltage detection
3258 | RM22UA31MR | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
3259 | RM22UA31MR | Main | switching capacity in VA | 2000 VA
3260 | RM22UA31MR | Main | measurement range | 50 mV...5 V voltage AC/DC 50/60 Hz
3261 | RM22UA31MR | Complementary | reset time | 1500 ms at maximum voltage
3262 | RM22UA31MR | Complementary | maximum switching voltage | 250 V AC
3263 | RM22UA31MR | Complementary | minimum switching current | 10 mA at 5 V DC
3264 | RM22UA31MR | Complementary | maximum switching current | 8 A AC
3265 | RM22UA31MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
3266 | RM22UA31MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
3267 | RM22UA31MR | Complementary | power consumption in VA | 3.5 VA AC
3268 | RM22UA31MR | Complementary | maximum power consumption in W | 1.5 W DC
3269 | RM22UA31MR | Complementary | supply voltage frequency | 40...70 Hz +/- 10 %
3270 | RM22UA31MR | Complementary | resistance across terminals | 30 kOhm at E2-M terminals 5 kOhm at E1-M terminals 50 kOhm at E3-M terminals
3271 | RM22UA31MR | Complementary | output contacts | 2 C/O
3272 | RM22UA31MR | Complementary | nominal output current | 8 A
3273 | RM22UA31MR | Complementary | hysteresis | 3 % fixed of full scale for window mode 5…50 % adjustable of threshold setting for overvoltage or undervoltage detection
3274 | RM22UA31MR | Complementary | run-up delay at power-up | 600 ms
3275 | RM22UA31MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
3276 | RM22UA31MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay
3277 | RM22UA31MR | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
3278 | RM22UA31MR | Complementary | response time | <= 500 ms
3279 | RM22UA31MR | Complementary | overvoltage category | III conforming to IEC 60664-1
3280 | RM22UA31MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
3281 | RM22UA31MR | Complementary | insulation | Between supply and measurement
3282 | RM22UA31MR | Complementary | mounting position | Any position
3283 | RM22UA31MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
3284 | RM22UA31MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
3285 | RM22UA31MR | Complementary | housing material | Self-extinguishing plastic
3286 | RM22UA31MR | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
3287 | RM22UA31MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
3288 | RM22UA31MR | Complementary | electrical durability | 100000 cycles
3289 | RM22UA31MR | Complementary | mechanical durability | 10000000 cycles
3290 | RM22UA31MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
3291 | RM22UA31MR | Complementary | safety reliability data | MTTFd = 308.2 years B10d = 290000
3292 | RM22UA31MR | Complementary | contacts material | Cadmium free
3293 | RM22UA31MR | Complementary | width | 22.5 mm
3294 | RM22UA31MR | Complementary | net weight | 0.11 kg
3295 | RM22UA31MR | Environment | immunity to microbreaks | 10 ms
3296 | RM22UA31MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
3297 | RM22UA31MR | Environment | standards | EN/IEC 60255-1
3298 | RM22UA31MR | Environment | product certifications | CE CSA RCM GL China RoHS CCC EAC UL
3299 | RM22UA31MR | Environment | ambient air temperature for storage | -40…70 °C
3300 | RM22UA31MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
3301 | RM22UA31MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
3302 | RM22UA31MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
3303 | RM22UA31MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
3304 | RM22UA31MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
3305 | RM22UA31MR | Environment | pollution degree | 3 conforming to IEC 60664-1
3306 | RM22UA31MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
3307 | RM22UA31MR | Offer Sustainability | Sustainable offer status | Green Premium product
3308 | RM22UA31MR | Offer Sustainability | REACh Regulation | REACh Declaration
3309 | RM22UA31MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
3310 | RM22UA31MR | Offer Sustainability | Mercury free | Yes
3311 | RM22UA31MR | Offer Sustainability | RoHS exemption information | Yes
3312 | RM22UA31MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
3313 | RM22UA31MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
3314 | RM22UA31MR | Offer Sustainability | Circularity Profile | End of Life Information
3315 | RM22UA31MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
3316 | RM22UA32MR | Main | range of product | Zelio Control
3317 | RM22UA32MR | Main | product or component type | Modular measurement and control relays
3318 | RM22UA32MR | Main | relay type | Voltage control relay
3319 | RM22UA32MR | Main | network number of phases | 1 phase
3320 | RM22UA32MR | Main | supply circuit type | DC
3321 | RM22UA32MR | Main | relay name | RM22UA
3322 | RM22UA32MR | Main | relay monitored parameters | Undervoltage and overvoltage in window mode Overvoltage or undervoltage detection
3323 | RM22UA32MR | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
3324 | RM22UA32MR | Main | switching capacity in VA | 2000 VA
3325 | RM22UA32MR | Main | measurement range | 1...100 V voltage AC/DC 50/60 Hz
3326 | RM22UA32MR | Complementary | reset time | 1500 ms at maximum voltage
3327 | RM22UA32MR | Complementary | maximum switching voltage | 250 V AC
3328 | RM22UA32MR | Complementary | minimum switching current | 10 mA at 5 V DC
3329 | RM22UA32MR | Complementary | maximum switching current | 8 A AC
3330 | RM22UA32MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
3331 | RM22UA32MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
3332 | RM22UA32MR | Complementary | power consumption in VA | 3.5 VA AC
3333 | RM22UA32MR | Complementary | maximum power consumption in W | 1.5 W DC
3334 | RM22UA32MR | Complementary | supply voltage frequency | 40...70 Hz +/- 10 %
3335 | RM22UA32MR | Complementary | resistance across terminals | 110 kOhm at E2-M terminals 22 kOhm at E1-M terminals 220 kOhm at E3-M terminals
3336 | RM22UA32MR | Complementary | output contacts | 2 C/O
3337 | RM22UA32MR | Complementary | nominal output current | 8 A
3338 | RM22UA32MR | Complementary | hysteresis | 3 % fixed of full scale for window mode 5…50 % adjustable of threshold setting for overvoltage or undervoltage detection
3339 | RM22UA32MR | Complementary | run-up delay at power-up | 600 ms
3340 | RM22UA32MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
3341 | RM22UA32MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay
3342 | RM22UA32MR | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
3343 | RM22UA32MR | Complementary | response time | <= 500 ms
3344 | RM22UA32MR | Complementary | overvoltage category | III conforming to IEC 60664-1
3345 | RM22UA32MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
3346 | RM22UA32MR | Complementary | insulation | Between supply and measurement
3347 | RM22UA32MR | Complementary | mounting position | Any position
3348 | RM22UA32MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
3349 | RM22UA32MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
3350 | RM22UA32MR | Complementary | housing material | Self-extinguishing plastic
3351 | RM22UA32MR | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
3352 | RM22UA32MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
3353 | RM22UA32MR | Complementary | electrical durability | 100000 cycles
3354 | RM22UA32MR | Complementary | mechanical durability | 10000000 cycles
3355 | RM22UA32MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
3356 | RM22UA32MR | Complementary | safety reliability data | B10d = 290000 MTTFd = 308.2 years
3357 | RM22UA32MR | Complementary | contacts material | Cadmium free
3358 | RM22UA32MR | Complementary | width | 22.5 mm
3359 | RM22UA32MR | Complementary | net weight | 0.11 kg
3360 | RM22UA32MR | Environment | immunity to microbreaks | 10 ms
3361 | RM22UA32MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
3362 | RM22UA32MR | Environment | standards | EN/IEC 60255-1
3363 | RM22UA32MR | Environment | product certifications | GL UL CCC EAC CE China RoHS RCM CSA
3364 | RM22UA32MR | Environment | ambient air temperature for storage | -40…70 °C
3365 | RM22UA32MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
3366 | RM22UA32MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
3367 | RM22UA32MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
3368 | RM22UA32MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
3369 | RM22UA32MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
3370 | RM22UA32MR | Environment | pollution degree | 3 conforming to IEC 60664-1
3371 | RM22UA32MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
3372 | RM22UA32MR | Offer Sustainability | Sustainable offer status | Green Premium product
3373 | RM22UA32MR | Offer Sustainability | REACh Regulation | REACh Declaration
3374 | RM22UA32MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
3375 | RM22UA32MR | Offer Sustainability | Mercury free | Yes
3376 | RM22UA32MR | Offer Sustainability | RoHS exemption information | Yes
3377 | RM22UA32MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
3378 | RM22UA32MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
3379 | RM22UA32MR | Offer Sustainability | Circularity Profile | End of Life Information
3380 | RM22UA32MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
3381 | RM22UA33MR | Main | range of product | Zelio Control
3382 | RM22UA33MR | Main | product or component type | Modular measurement and control relays
3383 | RM22UA33MR | Main | relay type | Voltage control relay
3384 | RM22UA33MR | Main | network number of phases | 1 phase
3385 | RM22UA33MR | Main | supply circuit type | DC
3386 | RM22UA33MR | Main | relay name | RM22UA
3387 | RM22UA33MR | Main | relay monitored parameters | Undervoltage and overvoltage in window mode Overvoltage or undervoltage detection
3388 | RM22UA33MR | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
3389 | RM22UA33MR | Main | switching capacity in VA | 2000 VA
3390 | RM22UA33MR | Main | measurement range | 15...500 V voltage AC/DC 50/60 Hz
3391 | RM22UA33MR | Complementary | reset time | 1500 ms at maximum voltage
3392 | RM22UA33MR | Complementary | maximum switching voltage | 250 V AC
3393 | RM22UA33MR | Complementary | minimum switching current | 10 mA at 5 V DC
3394 | RM22UA33MR | Complementary | maximum switching current | 8 A AC
3395 | RM22UA33MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
3396 | RM22UA33MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
3397 | RM22UA33MR | Complementary | power consumption in VA | 3.5 VA AC
3398 | RM22UA33MR | Complementary | maximum power consumption in W | 1.5 W DC
3399 | RM22UA33MR | Complementary | supply voltage frequency | 40...70 Hz +/- 10 %
3400 | RM22UA33MR | Complementary | resistance across terminals | 150 kOhm at E2-M terminals 300 kOhm at E1-M terminals 500 kOhm at E3-M terminals
3401 | RM22UA33MR | Complementary | output contacts | 2 C/O
3402 | RM22UA33MR | Complementary | nominal output current | 8 A
3403 | RM22UA33MR | Complementary | hysteresis | 3 % fixed of full scale for window mode 5…50 % adjustable of threshold setting for overvoltage or undervoltage detection
3404 | RM22UA33MR | Complementary | run-up delay at power-up | 600 ms
3405 | RM22UA33MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
3406 | RM22UA33MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay
3407 | RM22UA33MR | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
3408 | RM22UA33MR | Complementary | response time | <= 500 ms
3409 | RM22UA33MR | Complementary | overvoltage category | III conforming to IEC 60664-1
3410 | RM22UA33MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
3411 | RM22UA33MR | Complementary | insulation | Between supply and measurement
3412 | RM22UA33MR | Complementary | mounting position | Any position
3413 | RM22UA33MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
3414 | RM22UA33MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
3415 | RM22UA33MR | Complementary | housing material | Self-extinguishing plastic
3416 | RM22UA33MR | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
3417 | RM22UA33MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
3418 | RM22UA33MR | Complementary | electrical durability | 100000 cycles
3419 | RM22UA33MR | Complementary | mechanical durability | 10000000 cycles
3420 | RM22UA33MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
3421 | RM22UA33MR | Complementary | safety reliability data | MTTFd = 308.2 years B10d = 290000
3422 | RM22UA33MR | Complementary | contacts material | Cadmium free
3423 | RM22UA33MR | Complementary | width | 22.5 mm
3424 | RM22UA33MR | Complementary | net weight | 0.11 kg
3425 | RM22UA33MR | Environment | immunity to microbreaks | 10 ms
3426 | RM22UA33MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
3427 | RM22UA33MR | Environment | standards | EN/IEC 60255-1
3428 | RM22UA33MR | Environment | product certifications | RCM UL China RoHS EAC CSA CE GL CCC
3429 | RM22UA33MR | Environment | ambient air temperature for storage | -40…70 °C
3430 | RM22UA33MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
3431 | RM22UA33MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
3432 | RM22UA33MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
3433 | RM22UA33MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
3434 | RM22UA33MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
3435 | RM22UA33MR | Environment | pollution degree | 3 conforming to IEC 60664-1
3436 | RM22UA33MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
3437 | RM22UA33MR | Offer Sustainability | Sustainable offer status | Green Premium product
3438 | RM22UA33MR | Offer Sustainability | REACh Regulation | REACh Declaration
3439 | RM22UA33MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
3440 | RM22UA33MR | Offer Sustainability | Mercury free | Yes
3441 | RM22UA33MR | Offer Sustainability | RoHS exemption information | Yes
3442 | RM22UA33MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
3443 | RM22UA33MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
3444 | RM22UA33MR | Offer Sustainability | Circularity Profile | End of Life Information
3445 | RM22UA33MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
3446 | RM22UB34 | Main | range of product | Zelio Control
3447 | RM22UB34 | Main | product or component type | Modular measurement and control relays
3448 | RM22UB34 | Main | relay type | Voltage control relay
3449 | RM22UB34 | Main | network number of phases | 1 phase
3450 | RM22UB34 | Main | supply circuit type | DC
3451 | RM22UB34 | Main | relay name | RM22UA
3452 | RM22UB34 | Main | relay monitored parameters | Overvoltage and undervoltage detection
3453 | RM22UB34 | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
3454 | RM22UB34 | Main | switching capacity in VA | 2000 VA
3455 | RM22UB34 | Main | measurement range | 80...300 V voltage AC/DC 50/60 Hz
3456 | RM22UB34 | Complementary | reset time | 1500 ms at maximum voltage
3457 | RM22UB34 | Complementary | maximum switching voltage | 250 V AC
3458 | RM22UB34 | Complementary | minimum switching current | 10 mA at 5 V DC
3459 | RM22UB34 | Complementary | maximum switching current | 8 A AC
3460 | RM22UB34 | Complementary | [Us] rated supply voltage | 110...240 V AC 50/60 Hz
3461 | RM22UB34 | Complementary | supply voltage limits | 60…280 V AC
3462 | RM22UB34 | Complementary | power consumption in VA | 5 VA AC
3463 | RM22UB34 | Complementary | maximum power consumption in W | 2 W DC
3464 | RM22UB34 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
3465 | RM22UB34 | Complementary | output contacts | 2 C/O
3466 | RM22UB34 | Complementary | nominal output current | 8 A
3467 | RM22UB34 | Complementary | hysteresis | 5…50 % adjustable of threshold setting
3468 | RM22UB34 | Complementary | run-up delay at power-up | 600 ms
3469 | RM22UB34 | Complementary | maximum measuring cycle | 250 ms measurement cycle as true rms value
3470 | RM22UB34 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay
3471 | RM22UB34 | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.2 %/°C with temperature variation
3472 | RM22UB34 | Complementary | response time | <= 500 ms
3473 | RM22UB34 | Complementary | overvoltage category | III conforming to IEC 60664-1
3474 | RM22UB34 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
3475 | RM22UB34 | Complementary | mounting position | Any position
3476 | RM22UB34 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
3477 | RM22UB34 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
3478 | RM22UB34 | Complementary | housing material | Self-extinguishing plastic
3479 | RM22UB34 | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
3480 | RM22UB34 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
3481 | RM22UB34 | Complementary | electrical durability | 100000 cycles
3482 | RM22UB34 | Complementary | mechanical durability | 10000000 cycles
3483 | RM22UB34 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
3484 | RM22UB34 | Complementary | safety reliability data | MTTFd = 433.7 years B10d = 400000
3485 | RM22UB34 | Complementary | contacts material | Cadmium free
3486 | RM22UB34 | Complementary | width | 22.5 mm
3487 | RM22UB34 | Complementary | net weight | 0.09 kg
3488 | RM22UB34 | Environment | immunity to microbreaks | 20 ms
3489 | RM22UB34 | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22
3490 | RM22UB34 | Environment | standards | EN/IEC 60255-1
3491 | RM22UB34 | Environment | product certifications | CCC China RoHS CE CSA EAC UL GL RCM
3492 | RM22UB34 | Environment | ambient air temperature for storage | -40…70 °C
3493 | RM22UB34 | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
3494 | RM22UB34 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
3495 | RM22UB34 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
3496 | RM22UB34 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
3497 | RM22UB34 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
3498 | RM22UB34 | Environment | pollution degree | 3 conforming to IEC 60664-1
3499 | RM22UB34 | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
3500 | RM22UB34 | Offer Sustainability | Sustainable offer status | Green Premium product
3501 | RM22UB34 | Offer Sustainability | REACh Regulation | REACh Declaration
3502 | RM22UB34 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
3503 | RM22UB34 | Offer Sustainability | Mercury free | Yes
3504 | RM22UB34 | Offer Sustainability | RoHS exemption information | Yes
3505 | RM22UB34 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
3506 | RM22UB34 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
3507 | RM22UB34 | Offer Sustainability | Circularity Profile | End of Life Information
3508 | RM22UB34 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
3509 | RM35JA32MR | Main | range of product | Zelio Control
3510 | RM35JA32MR | Main | product or component type | Modular measurement and control relays
3511 | RM35JA32MR | Main | relay type | Current control relay
3512 | RM35JA32MR | Main | relay name | RM35JA
3513 | RM35JA32MR | Main | relay monitored parameters | Overcurrent or undercurrent in window mode Overcurrent or undercurrent detection
3514 | RM35JA32MR | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
3515 | RM35JA32MR | Main | switching capacity in VA | 2000 VA
3516 | RM35JA32MR | Main | measurement range | 0.15...1.5 A E1-M terminals 0.5...5 A E2-M terminals 1.5...15 A E3-M terminals 150 mA...15 A current AC/DC 50/60 Hz
3517 | RM35JA32MR | Complementary | reset time | 1500 ms at maximum voltage
3518 | RM35JA32MR | Complementary | maximum switching voltage | 250 V AC
3519 | RM35JA32MR | Complementary | minimum switching current | 10 mA at 5 V DC
3520 | RM35JA32MR | Complementary | maximum switching current | 8 A AC
3521 | RM35JA32MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
3522 | RM35JA32MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
3523 | RM35JA32MR | Complementary | operating limits | - 15 % + 10 % Un
3524 | RM35JA32MR | Complementary | power consumption in VA | 3.5 VA AC
3525 | RM35JA32MR | Complementary | maximum power consumption in W | 1.5 W DC
3526 | RM35JA32MR | Complementary | resistance across terminals | 0.005 Ohm at E3-M terminals 0.015 Ohm at E2-M terminals 0.05 Ohm at E1-M terminals
3527 | RM35JA32MR | Complementary | output contacts | 2 C/O
3528 | RM35JA32MR | Complementary | nominal output current | 8 A
3529 | RM35JA32MR | Complementary | internal input resistance | 0.015 Ohm 0.005 Ohm 0.05 Ohm
3530 | RM35JA32MR | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
3531 | RM35JA32MR | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
3532 | RM35JA32MR | Complementary | setting accuracy of time delay | 10 P
3533 | RM35JA32MR | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
3534 | RM35JA32MR | Complementary | hysteresis | 5…50 % adjustable of threshold setting for overcurrent or undercurrent detection 3 % fixed of full scale for window mode
3535 | RM35JA32MR | Complementary | run-up delay at power-up | 0.3 s
3536 | RM35JA32MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
3537 | RM35JA32MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay
3538 | RM35JA32MR | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
3539 | RM35JA32MR | Complementary | response time | <= 500 ms (on crossing the threshold)
3540 | RM35JA32MR | Complementary | threshold setting | 10...100 %
3541 | RM35JA32MR | Complementary | overvoltage category | III conforming to IEC 60664-1 III conforming to UL 508
3542 | RM35JA32MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
3543 | RM35JA32MR | Complementary | insulation | Between supply and measurement
3544 | RM35JA32MR | Complementary | mounting position | Any position
3545 | RM35JA32MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
3546 | RM35JA32MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
3547 | RM35JA32MR | Complementary | housing material | Self-extinguishing plastic
3548 | RM35JA32MR | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
3549 | RM35JA32MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
3550 | RM35JA32MR | Complementary | electrical durability | 100000 cycles
3551 | RM35JA32MR | Complementary | mechanical durability | 10000000 cycles
3552 | RM35JA32MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
3553 | RM35JA32MR | Complementary | safety reliability data | MTTFd = 296.8 years B10d = 270000
3554 | RM35JA32MR | Complementary | contacts material | Cadmium free
3555 | RM35JA32MR | Complementary | width | 35 mm
3556 | RM35JA32MR | Complementary | net weight | 0.12 kg
3557 | RM35JA32MR | Environment | immunity to microbreaks | 50 ms
3558 | RM35JA32MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 Emission standard for residential, commercial and light-industrial environments (except radiated emission) conforming to EN/IEC 61000-6-3
3559 | RM35JA32MR | Environment | standards | EN/IEC 60255-1
3560 | RM35JA32MR | Environment | product certifications | CE GL CCC EAC RCM China RoHS UL CSA
3561 | RM35JA32MR | Environment | ambient air temperature for storage | -40…70 °C
3562 | RM35JA32MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
3563 | RM35JA32MR | Environment | environmental characteristic | 3K3 C
3564 | RM35JA32MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
3565 | RM35JA32MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
3566 | RM35JA32MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
3567 | RM35JA32MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 IP30 (housing) conforming to IEC 60529
3568 | RM35JA32MR | Environment | pollution degree | 3 conforming to IEC 60664-1 3 conforming to UL 508
3569 | RM35JA32MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
3570 | RM35JA32MR | Offer Sustainability | Sustainable offer status | Green Premium product
3571 | RM35JA32MR | Offer Sustainability | REACh Regulation | REACh Declaration
3572 | RM35JA32MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
3573 | RM35JA32MR | Offer Sustainability | Mercury free | Yes
3574 | RM35JA32MR | Offer Sustainability | RoHS exemption information | Yes
3575 | RM35JA32MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
3576 | RM35JA32MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
3577 | RM35JA32MR | Offer Sustainability | Circularity Profile | End of Life Information
3578 | RM35JA32MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
3579 | RM35JA32MT | Main | range of product | Zelio Control
3580 | RM35JA32MT | Main | product or component type | Modular measurement and control relays
3581 | RM35JA32MT | Main | relay type | Current control relay
3582 | RM35JA32MT | Main | relay name | RM35JA
3583 | RM35JA32MT | Main | relay monitored parameters | Overcurrent or undercurrent detection Overcurrent or undercurrent in window mode
3584 | RM35JA32MT | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
3585 | RM35JA32MT | Main | switching capacity in VA | 2000 VA
3586 | RM35JA32MT | Main | measurement range | 0.15...1.5 A E1-M terminals 0.5...5 A E2-M terminals 1.5...15 A E3-M terminals 150 mA...15 A current AC/DC 50/60 Hz
3587 | RM35JA32MT | Complementary | reset time | 1500 ms at maximum voltage
3588 | RM35JA32MT | Complementary | maximum switching voltage | 250 V AC
3589 | RM35JA32MT | Complementary | minimum switching current | 10 mA at 5 V DC
3590 | RM35JA32MT | Complementary | maximum switching current | 8 A AC
3591 | RM35JA32MT | Complementary | [Us] rated supply voltage | 380...415 V AC 50/60 Hz +/- 10 %
3592 | RM35JA32MT | Complementary | supply voltage limits | 323…456.5 V AC
3593 | RM35JA32MT | Complementary | operating limits | - 15 % + 10 % Un
3594 | RM35JA32MT | Complementary | power consumption in VA | 8 VA AC
3595 | RM35JA32MT | Complementary | resistance across terminals | 0.005 Ohm at E3-M terminals 0.015 Ohm at E2-M terminals 0.05 Ohm at E1-M terminals
3596 | RM35JA32MT | Complementary | output contacts | 2 C/O
3597 | RM35JA32MT | Complementary | nominal output current | 8 A
3598 | RM35JA32MT | Complementary | internal input resistance | 0.005 Ohm 0.015 Ohm 0.05 Ohm
3599 | RM35JA32MT | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale for 1.5 A +/- 10 % of the full scale for 5 A +/- 20 % of the full scale for 15 A
3600 | RM35JA32MT | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
3601 | RM35JA32MT | Complementary | setting accuracy of time delay | 10 %
3602 | RM35JA32MT | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range
3603 | RM35JA32MT | Complementary | hysteresis | 5…50 % adjustable of threshold setting for overcurrent or undercurrent detection 3 % fixed of full scale for window mode
3604 | RM35JA32MT | Complementary | run-up delay at power-up | 0.3 s
3605 | RM35JA32MT | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
3606 | RM35JA32MT | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay
3607 | RM35JA32MT | Complementary | measurement error | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation
3608 | RM35JA32MT | Complementary | response time | <= 500 ms (on crossing the threshold)
3609 | RM35JA32MT | Complementary | threshold setting | 10...100 %
3610 | RM35JA32MT | Complementary | overvoltage category | III conforming to IEC 60664-1 III conforming to UL 508
3611 | RM35JA32MT | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
3612 | RM35JA32MT | Complementary | insulation | Between supply and measurement
3613 | RM35JA32MT | Complementary | mounting position | Any position
3614 | RM35JA32MT | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
3615 | RM35JA32MT | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
3616 | RM35JA32MT | Complementary | housing material | Self-extinguishing plastic
3617 | RM35JA32MT | Complementary | status LED | LED (yellow)relay ON: LED (green)power ON:
3618 | RM35JA32MT | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
3619 | RM35JA32MT | Complementary | electrical durability | 100000 cycles
3620 | RM35JA32MT | Complementary | mechanical durability | 10000000 cycles
3621 | RM35JA32MT | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
3622 | RM35JA32MT | Complementary | safety reliability data | MTTFd = 296.8 years B10d = 270000
3623 | RM35JA32MT | Complementary | contacts material | Cadmium free
3624 | RM35JA32MT | Complementary | width | 35 mm
3625 | RM35JA32MT | Complementary | net weight | 0.12 kg
3626 | RM35JA32MT | Environment | immunity to microbreaks | 50 ms
3627 | RM35JA32MT | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 Emission standard for residential, commercial and light-industrial environments (except radiated emission) conforming to EN/IEC 61000-6-3
3628 | RM35JA32MT | Environment | standards | EN/IEC 60255-1
3629 | RM35JA32MT | Environment | product certifications | CCC EAC CSA China RoHS RCM UL GL CE
3630 | RM35JA32MT | Environment | ambient air temperature for storage | -40…70 °C
3631 | RM35JA32MT | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC
3632 | RM35JA32MT | Environment | environmental characteristic | 3K3 C
3633 | RM35JA32MT | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
3634 | RM35JA32MT | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
3635 | RM35JA32MT | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
3636 | RM35JA32MT | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 IP30 (housing) conforming to IEC 60529
3637 | RM35JA32MT | Environment | pollution degree | 3 conforming to IEC 60664-1 3 conforming to UL 508
3638 | RM35JA32MT | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
3639 | RM35JA32MT | Offer Sustainability | Sustainable offer status | Green Premium product
3640 | RM35JA32MT | Offer Sustainability | REACh Regulation | REACh Declaration
3641 | RM35JA32MT | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
3642 | RM35JA32MT | Offer Sustainability | Mercury free | Yes
3643 | RM35JA32MT | Offer Sustainability | RoHS exemption information | Yes
3644 | RM35JA32MT | Offer Sustainability | China RoHS Regulation | China RoHS declaration
3645 | RM35JA32MT | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
3646 | RM35JA32MT | Offer Sustainability | Circularity Profile | End of Life Information
3647 | RM35JA32MT | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
3648 | RMNF22TB30 | Main | range of product | Zelio Control
3649 | RMNF22TB30 | Main | product or component type | Monitoring relay
3650 | RMNF22TB30 | Main | relay type | Control relay
3651 | RMNF22TB30 | Main | network number of phases | 3 phases
3652 | RMNF22TB30 | Main | relay name | RMNF22
3653 | RMNF22TB30 | Main | relay monitored parameters | Phase sequence Phase failure detection Overvoltage detection Undervoltage detection Overfrequency and underfrequency Asymmetry
3654 | RMNF22TB30 | Main | Supported OS | Android
3655 | RMNF22TB30 | Main | software version | V4.4 and above
3656 | RMNF22TB30 | Main | App for product | Zelio NFC (downloadable from Google Play store)
3657 | RMNF22TB30 | Main | product compatibility | NFC enabled mobile device
3658 | RMNF22TB30 | Main | time delay type | On-delay 0.1 s...60 min Off-delay 0.1 s...60 min
3659 | RMNF22TB30 | Main | switching capacity in VA | 2000 VA
3660 | RMNF22TB30 | Complementary | NFC operating frequency | 13.56 MHz
3661 | RMNF22TB30 | Complementary | Maximum RF power transmitted | 0.0002 mW
3662 | RMNF22TB30 | Complementary | reset time | 1500 ms at maximum voltage
3663 | RMNF22TB30 | Complementary | maximum switching voltage | 250 V AC
3664 | RMNF22TB30 | Complementary | minimum switching current | 100 mA at 6 V
3665 | RMNF22TB30 | Complementary | maximum switching current | 8 A AC
3666 | RMNF22TB30 | Complementary | [Us] rated supply voltage | 208...480 V AC line to line 120...277 V AC line to neutral
3667 | RMNF22TB30 | Complementary | supply voltage limits | 166.4…576 V AC line to line 96…332.4 V AC line to neutral
3668 | RMNF22TB30 | Complementary | power consumption in VA | 4 VA at 480 V AC 60 Hz
3669 | RMNF22TB30 | Complementary | on-load factor | 100 %
3670 | RMNF22TB30 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
3671 | RMNF22TB30 | Complementary | output contacts | 2 C/O
3672 | RMNF22TB30 | Complementary | setting accuracy of the switching threshold | +/- (1.5 % + 1 V)
3673 | RMNF22TB30 | Complementary | setting accuracy of time delay | +/- 3 % for 10 s...60 min time delay range +/- 300 ms for 0...10 s time delay range
3674 | RMNF22TB30 | Complementary | hysteresis | 3 % of fixed for phase failure detection
3675 | RMNF22TB30 | Complementary | alarm threshold | 166...576 V adjustable overvoltage and undervoltage detection (line to line) 96...332 V adjustable overvoltage and undervoltage detection (line to neutral) 5...150 V adjustable asymmetry 45...66 Hz adjustable overfrequency or underfrequency
3676 | RMNF22TB30 | Complementary | Run-up delay at power-up max | 650 ms
3677 | RMNF22TB30 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
3678 | RMNF22TB30 | Complementary | repeat accuracy | +/- 0.5 % for input circuit +/- 3 % for time delay
3679 | RMNF22TB30 | Complementary | setting accuracy of the switching threshold | +/- (1.5 % + 1 V)
3680 | RMNF22TB30 | Complementary | measurement error | < 0.05 %/Hz with frequency variation < 0.05 %/°C with temperature variation
3681 | RMNF22TB30 | Complementary | response time | <= 300 ms
3682 | RMNF22TB30 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
3683 | RMNF22TB30 | Complementary | [Ui] rated insulation voltage | 400 V
3684 | RMNF22TB30 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV during 1.2/50 µs
3685 | RMNF22TB30 | Complementary | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
3686 | RMNF22TB30 | Complementary | mounting position | Any position
3687 | RMNF22TB30 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.5...2 x 1.5 mm² (AWG 20...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.5...1 x 2.5 mm² (AWG 20...AWG 14) flexible with cable end
3688 | RMNF22TB30 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 0.60…0.99 N.m conforming to IEC 60947-1
3689 | RMNF22TB30 | Complementary | housing material | Self-extinguishing plastic
3690 | RMNF22TB30 | Complementary | local signalling | LED Un: (steady), green for power ON LED R1: (steady), amber for relay energised LED R1: (blinking), amber for timing in progress LED R2: (steady), amber for relay energised LED R2: (blinking), amber for timing in progress LED PL: (steady), red for alarm phase failure triggered LED PS: (blinking), red for alarm phase sequence failure triggered LED UV: (steady), red for alarm undervoltage failure triggered LED OV: (blinking), red for alarm overvoltage failure triggered LED UF: (steady), red for alarm underfrequency failure triggered LED OF: (blinking), red for alarm overfrequency failure triggered LED ASYM: (steady), red for alarm asymmentry failure triggered
3691 | RMNF22TB30 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
3692 | RMNF22TB30 | Complementary | electrical durability | 100000 cycles
3693 | RMNF22TB30 | Complementary | mechanical durability | 10000000 cycles
3694 | RMNF22TB30 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
3695 | RMNF22TB30 | Complementary | [Ith] conventional free air thermal current | 8 A
3696 | RMNF22TB30 | Complementary | contacts material | Cadmium free
3697 | RMNF22TB30 | Complementary | width | 22.5 mm
3698 | RMNF22TB30 | Complementary | height | 90 mm
3699 | RMNF22TB30 | Complementary | depth | 99 mm
3700 | RMNF22TB30 | Complementary | net weight | 0.125 kg
3701 | RMNF22TB30 | Environment | immunity to microbreaks | 10 ms
3702 | RMNF22TB30 | Environment | electromagnetic compatibility | Voltage dips and interruptions immunity test - test level: 70 % (25/30 cycles) conforming to IEC 61000-4-11 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 1 MHz damped oscillating wave - test level: 2.5 kV CM, 1 kV DM criteria B conforming to IEC 61000-4-18 Voltage dips and interruptions immunity test - test level: 0 % (0.5...25 cycles) conforming to IEC 61000-4-11 Magnetic field at power frequency - test level: 30 A/m (continuous)-300 A/m (1-3 s) level 4 conforming to IEC 61000-4-8 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Voltage dips and interruptions immunity test - test level: 40 % (10/12 cycles) conforming to IEC 61000-4-11 Voltage interruptions - test level: 0 % criteria C (250/300 cycles) conforming to IEC 61000-4-29 Electrical fast transient/burst immunity test - test level: 4 kV criteria B (direct) conforming to IEC 61000-4-4 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Conducted RF disturbances level 3 conforming to IEC 61000-4-6
3703 | RMNF22TB30 | Environment | standards | EN/IEC 60255-1
3704 | RMNF22TB30 | Environment | product certifications | CE UL CSA CCC EAC RCM
3705 | RMNF22TB30 | Environment | directives | 2014/30/EU - electromagnetic compatibility 2014/35/EU - low voltage directive 2014/53/EU - radio equipment directive 2015/863/EU - RoHS directive
3706 | RMNF22TB30 | Environment | ambient air temperature for storage | -40…70 °C
3707 | RMNF22TB30 | Environment | ambient air temperature for operation | -20…60 °C
3708 | RMNF22TB30 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
3709 | RMNF22TB30 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 58.1…150 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 10…58.1 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
3710 | RMNF22TB30 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
3711 | RMNF22TB30 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP40 (front panel) conforming to IEC 60529
3712 | RMNF22TB30 | Environment | pollution degree | 3 conforming to IEC 60664-1 3 conforming to UL 508
3713 | RMNF22TB30 | Environment | overvoltage category | III conforming to IEC 60664-1 III conforming to UL 508
3714 | RMNF22TB30 | Packing Units | Package 1 Weight | 136 g
3715 | RMNF22TB30 | Packing Units | Package 2 Weight | 5.578 kg
3716 | RMNF22TB30 | Offer Sustainability | Sustainable offer status | Green Premium product
3717 | RMNF22TB30 | Offer Sustainability | REACh Regulation | REACh Declaration
3718 | RMNF22TB30 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
3719 | RMNF22TB30 | Offer Sustainability | Mercury free | Yes
3720 | RMNF22TB30 | Offer Sustainability | RoHS exemption information | Yes
3721 | RMNF22TB30 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
3722 | RMNF22TB30 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
3723 | RMNF22TB30 | Offer Sustainability | Circularity Profile | End of Life Information
3724 | RMNF22TB30 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
3725 | RE17LAMW | Main | range of product | Zelio Time
3726 | RE17LAMW | Main | product or component type | Modular timing relay
3727 | RE17LAMW | Main | discrete output type | Solid state
3728 | RE17LAMW | Main | width | 17.5 mm
3729 | RE17LAMW | Main | component name | RE17L
3730 | RE17LAMW | Main | time delay type | A
3731 | RE17LAMW | Main | time delay range | 1...10 s 10...100 h 6...60 s 0.1...1 s 1...10 min 6...60 min 1...10 h
3732 | RE17LAMW | Main | nominal output current | 0.7 A
3733 | RE17LAMW | Complementary | control type | Selector switch front panel
3734 | RE17LAMW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
3735 | RE17LAMW | Complementary | voltage range | 0.85...1.1 Us
3736 | RE17LAMW | Complementary | supply frequency | 50...60 Hz +/- 5 %
3737 | RE17LAMW | Complementary | control signal pulse width | 0.05 s typical
3738 | RE17LAMW | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
3739 | RE17LAMW | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
3740 | RE17LAMW | Complementary | power on delay | 100 ms
3741 | RE17LAMW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
3742 | RE17LAMW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
3743 | RE17LAMW | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
3744 | RE17LAMW | Complementary | housing material | Self-extinguishing
3745 | RE17LAMW | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
3746 | RE17LAMW | Complementary | temperature drift | +/- 0.05 %/°C
3747 | RE17LAMW | Complementary | voltage drift | +/- 0.2 %/V
3748 | RE17LAMW | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
3749 | RE17LAMW | Complementary | reset time | 350 ms on de-energisation typical
3750 | RE17LAMW | Complementary | on-load factor | 100 %
3751 | RE17LAMW | Complementary | power consumption in VA | 0…3 VA at 240 V AC
3752 | RE17LAMW | Complementary | maximum power consumption in W | 1.5 W at 240 V DC
3753 | RE17LAMW | Complementary | breaking capacity | 0.5 A AC/DC conforming to UL 0.7 A AC/DC at 20 °C
3754 | RE17LAMW | Complementary | operating frequency | 10 Hz
3755 | RE17LAMW | Complementary | maximum output current | 20 A
3756 | RE17LAMW | Complementary | minimum switching current | 10 mA
3757 | RE17LAMW | Complementary | maximum leakage current | 5 mA
3758 | RE17LAMW | Complementary | maximum switching voltage | 250 V AC/DC
3759 | RE17LAMW | Complementary | maximum voltage drop | <4 V 3-wire <8 V 2-wire
3760 | RE17LAMW | Complementary | electrical durability | 100000000 cycles
3761 | RE17LAMW | Complementary | marking | CE
3762 | RE17LAMW | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
3763 | RE17LAMW | Complementary | safety reliability data | MTTFd = 353.8 years B10d = 320000
3764 | RE17LAMW | Complementary | mounting position | Any position in relation to normal vertical mounting plane
3765 | RE17LAMW | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
3766 | RE17LAMW | Complementary | net weight | 0.068 kg
3767 | RE17LAMW | Complementary | time delay type | A
3768 | RE17LAMW | Complementary | functionality | On-delay timing
3769 | RE17LAMW | Complementary | compatibility code | RE17
3770 | RE17LAMW | Environment | immunity to microbreaks | 20 ms
3771 | RE17LAMW | Environment | derating factor | 5 mA/°C
3772 | RE17LAMW | Environment | standards | 2004/108/EC EN 61000-6-1 2006/95/EC EN 61000-6-3 EN 61000-6-2 IEC 61812-1 EN 61000-6-4
3773 | RE17LAMW | Environment | product certifications | GL CSA CULus
3774 | RE17LAMW | Environment | ambient air temperature for storage | -30…60 °C
3775 | RE17LAMW | Environment | ambient air temperature for operation | -20…60 °C
3776 | RE17LAMW | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
3777 | RE17LAMW | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
3778 | RE17LAMW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
3779 | RE17LAMW | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
3780 | RE17LAMW | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
3781 | RE17LAMW | Offer Sustainability | Sustainable offer status | Green Premium product
3782 | RE17LAMW | Offer Sustainability | REACh Regulation | REACh Declaration
3783 | RE17LAMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
3784 | RE17LAMW | Offer Sustainability | Mercury free | Yes
3785 | RE17LAMW | Offer Sustainability | RoHS exemption information | Yes
3786 | RE17LAMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
3787 | RE17LAMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
3788 | RE17LAMW | Offer Sustainability | Circularity Profile | End of Life Information
3789 | RE17LCBM | Main | range of product | Zelio Time
3790 | RE17LCBM | Main | product or component type | Modular timing relay
3791 | RE17LCBM | Main | discrete output type | Solid state
3792 | RE17LCBM | Main | width | 17.5 mm
3793 | RE17LCBM | Main | component name | RE17L
3794 | RE17LCBM | Main | time delay type | C
3795 | RE17LCBM | Main | time delay range | 10...100 h 6...60 s 6...60 min 1...10 h 1...10 s 1...10 min 0.1...1 s
3796 | RE17LCBM | Main | nominal output current | 0.7 A
3797 | RE17LCBM | Complementary | control type | Selector switch front panel
3798 | RE17LCBM | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz
3799 | RE17LCBM | Complementary | voltage range | 0.85...1.1 Us
3800 | RE17LCBM | Complementary | supply frequency | 50...60 Hz +/- 5 %
3801 | RE17LCBM | Complementary | release of input voltage | 7 V
3802 | RE17LCBM | Complementary | control signal pulse width | 0.05 s typical
3803 | RE17LCBM | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
3804 | RE17LCBM | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
3805 | RE17LCBM | Complementary | power on delay | 100 ms
3806 | RE17LCBM | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
3807 | RE17LCBM | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
3808 | RE17LCBM | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
3809 | RE17LCBM | Complementary | housing material | Self-extinguishing
3810 | RE17LCBM | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
3811 | RE17LCBM | Complementary | temperature drift | +/- 0.05 %/°C
3812 | RE17LCBM | Complementary | voltage drift | +/- 0.2 %/V
3813 | RE17LCBM | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
3814 | RE17LCBM | Complementary | reset time | 350 ms on de-energisation typical
3815 | RE17LCBM | Complementary | on-load factor | 100 %
3816 | RE17LCBM | Complementary | power consumption in VA | 0…3 VA at 240 V AC
3817 | RE17LCBM | Complementary | maximum power consumption in W | 1.5 W at 240 V DC
3818 | RE17LCBM | Complementary | breaking capacity | 0.5 A AC/DC conforming to UL 0.7 A AC/DC at 20 °C
3819 | RE17LCBM | Complementary | operating frequency | 10 Hz
3820 | RE17LCBM | Complementary | maximum output current | 20 A
3821 | RE17LCBM | Complementary | minimum switching current | 10 mA
3822 | RE17LCBM | Complementary | maximum leakage current | 5 mA
3823 | RE17LCBM | Complementary | maximum switching voltage | 250 V AC
3824 | RE17LCBM | Complementary | maximum voltage drop | <4 V 3-wire <8 V 2-wire
3825 | RE17LCBM | Complementary | electrical durability | 100000000 cycles
3826 | RE17LCBM | Complementary | marking | CE
3827 | RE17LCBM | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
3828 | RE17LCBM | Complementary | safety reliability data | MTTFd = 353.8 years B10d = 320000
3829 | RE17LCBM | Complementary | mounting position | Any position in relation to normal vertical mounting plane
3830 | RE17LCBM | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
3831 | RE17LCBM | Complementary | net weight | 0.068 kg
3832 | RE17LCBM | Complementary | time delay type | C
3833 | RE17LCBM | Complementary | functionality | Off-delay timing
3834 | RE17LCBM | Complementary | compatibility code | RE17
3835 | RE17LCBM | Environment | immunity to microbreaks | 20 ms
3836 | RE17LCBM | Environment | derating factor | 5 mA/°C
3837 | RE17LCBM | Environment | standards | 2004/108/EC EN 61000-6-3 2006/95/EC EN 61000-6-2 IEC 61812-1 EN 61000-6-4 EN 61000-6-1
3838 | RE17LCBM | Environment | product certifications | CSA GL CULus
3839 | RE17LCBM | Environment | ambient air temperature for storage | -30…60 °C
3840 | RE17LCBM | Environment | ambient air temperature for operation | -20…60 °C
3841 | RE17LCBM | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
3842 | RE17LCBM | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
3843 | RE17LCBM | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
3844 | RE17LCBM | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
3845 | RE17LCBM | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
3846 | RE17LCBM | Offer Sustainability | Sustainable offer status | Green Premium product
3847 | RE17LCBM | Offer Sustainability | REACh Regulation | REACh Declaration
3848 | RE17LCBM | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
3849 | RE17LCBM | Offer Sustainability | Mercury free | Yes
3850 | RE17LCBM | Offer Sustainability | RoHS exemption information | Yes
3851 | RE17LCBM | Offer Sustainability | China RoHS Regulation | China RoHS declaration
3852 | RE17LCBM | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
3853 | RE17LCBM | Offer Sustainability | Circularity Profile | End of Life Information
3854 | RE17LHBM | Main | range of product | Zelio Time
3855 | RE17LHBM | Main | product or component type | Modular timing relay
3856 | RE17LHBM | Main | discrete output type | Solid state
3857 | RE17LHBM | Main | width | 17.5 mm
3858 | RE17LHBM | Main | component name | RE17L
3859 | RE17LHBM | Main | time delay type | H
3860 | RE17LHBM | Main | time delay range | 1...10 s 1...10 h 0.1...1 s 6...60 s 6...60 min 1...10 min 10...100 h
3861 | RE17LHBM | Main | nominal output current | 0.7 A
3862 | RE17LHBM | Complementary | control type | Selector switch front panel
3863 | RE17LHBM | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz
3864 | RE17LHBM | Complementary | voltage range | 0.85...1.1 Us
3865 | RE17LHBM | Complementary | supply frequency | 50...60 Hz +/- 5 %
3866 | RE17LHBM | Complementary | release of input voltage | 9 V
3867 | RE17LHBM | Complementary | control signal pulse width | 0.05 s typical
3868 | RE17LHBM | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
3869 | RE17LHBM | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
3870 | RE17LHBM | Complementary | power on delay | 100 ms
3871 | RE17LHBM | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
3872 | RE17LHBM | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
3873 | RE17LHBM | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
3874 | RE17LHBM | Complementary | housing material | Self-extinguishing
3875 | RE17LHBM | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
3876 | RE17LHBM | Complementary | temperature drift | +/- 0.05 %/°C
3877 | RE17LHBM | Complementary | voltage drift | +/- 0.2 %/V
3878 | RE17LHBM | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
3879 | RE17LHBM | Complementary | reset time | 350 ms on de-energisation typical
3880 | RE17LHBM | Complementary | on-load factor | 100 %
3881 | RE17LHBM | Complementary | power consumption in VA | 0…3 VA at 240 V AC
3882 | RE17LHBM | Complementary | maximum power consumption in W | 1.5 W at 240 V DC
3883 | RE17LHBM | Complementary | breaking capacity | 0.5 A AC/DC conforming to UL 0.7 A AC/DC at 20 °C
3884 | RE17LHBM | Complementary | operating frequency | 10 Hz
3885 | RE17LHBM | Complementary | maximum output current | 20 A
3886 | RE17LHBM | Complementary | minimum switching current | 10 mA
3887 | RE17LHBM | Complementary | maximum leakage current | 5 mA
3888 | RE17LHBM | Complementary | maximum switching voltage | 250 V AC
3889 | RE17LHBM | Complementary | maximum voltage drop | <4 V 3-wire <8 V 2-wire
3890 | RE17LHBM | Complementary | electrical durability | 100000000 cycles
3891 | RE17LHBM | Complementary | marking | CE
3892 | RE17LHBM | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
3893 | RE17LHBM | Complementary | safety reliability data | MTTFd = 353.8 years B10d = 320000
3894 | RE17LHBM | Complementary | mounting position | Any position in relation to normal vertical mounting plane
3895 | RE17LHBM | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
3896 | RE17LHBM | Complementary | net weight | 0.068 kg
3897 | RE17LHBM | Complementary | time delay type | H
3898 | RE17LHBM | Complementary | functionality | On-delay timing
3899 | RE17LHBM | Complementary | compatibility code | RE17
3900 | RE17LHBM | Environment | immunity to microbreaks | 20 ms
3901 | RE17LHBM | Environment | derating factor | 5 mA/°C
3902 | RE17LHBM | Environment | standards | 2006/95/EC EN 61000-6-1 EN 61000-6-3 EN 61000-6-2 IEC 61812-1 EN 61000-6-4 2004/108/EC
3903 | RE17LHBM | Environment | product certifications | CULus CSA GL
3904 | RE17LHBM | Environment | ambient air temperature for storage | -30…60 °C
3905 | RE17LHBM | Environment | ambient air temperature for operation | -20…60 °C
3906 | RE17LHBM | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
3907 | RE17LHBM | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
3908 | RE17LHBM | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
3909 | RE17LHBM | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
3910 | RE17LHBM | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
3911 | RE17LHBM | Offer Sustainability | Sustainable offer status | Green Premium product
3912 | RE17LHBM | Offer Sustainability | REACh Regulation | REACh Declaration
3913 | RE17LHBM | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
3914 | RE17LHBM | Offer Sustainability | Mercury free | Yes
3915 | RE17LHBM | Offer Sustainability | RoHS exemption information | Yes
3916 | RE17LHBM | Offer Sustainability | China RoHS Regulation | China RoHS declaration
3917 | RE17LHBM | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
3918 | RE17LHBM | Offer Sustainability | Circularity Profile | End of Life Information
3919 | RE17LLBM | Main | range of product | Zelio Time
3920 | RE17LLBM | Main | product or component type | Modular timing relay
3921 | RE17LLBM | Main | discrete output type | Solid state
3922 | RE17LLBM | Main | width | 17.5 mm
3923 | RE17LLBM | Main | component name | RE17L
3924 | RE17LLBM | Main | time delay type | Li L
3925 | RE17LLBM | Main | time delay range | 6...60 s 6...60 min 1...10 min 0.1...1 s 1...10 h 10...100 h 1...10 s
3926 | RE17LLBM | Main | nominal output current | 0.7 A
3927 | RE17LLBM | Complementary | control type | Selector switch front panel
3928 | RE17LLBM | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz
3929 | RE17LLBM | Complementary | voltage range | 0.85...1.1 Us
3930 | RE17LLBM | Complementary | supply frequency | 50...60 Hz +/- 5 %
3931 | RE17LLBM | Complementary | release of input voltage | 7 V
3932 | RE17LLBM | Complementary | control signal pulse width | 0.05 s typical
3933 | RE17LLBM | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
3934 | RE17LLBM | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
3935 | RE17LLBM | Complementary | power on delay | 100 ms
3936 | RE17LLBM | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
3937 | RE17LLBM | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
3938 | RE17LLBM | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
3939 | RE17LLBM | Complementary | housing material | Self-extinguishing
3940 | RE17LLBM | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
3941 | RE17LLBM | Complementary | temperature drift | +/- 0.05 %/°C
3942 | RE17LLBM | Complementary | voltage drift | +/- 0.2 %/V
3943 | RE17LLBM | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
3944 | RE17LLBM | Complementary | reset time | 350 ms on de-energisation typical
3945 | RE17LLBM | Complementary | on-load factor | 100 %
3946 | RE17LLBM | Complementary | power consumption in VA | 0…3 VA at 240 V AC
3947 | RE17LLBM | Complementary | breaking capacity | 0.5 A AC conforming to UL 0.7 A AC at 20 °C
3948 | RE17LLBM | Complementary | operating frequency | 10 Hz
3949 | RE17LLBM | Complementary | maximum output current | 20 A
3950 | RE17LLBM | Complementary | minimum switching current | 10 mA
3951 | RE17LLBM | Complementary | maximum leakage current | 5 mA
3952 | RE17LLBM | Complementary | maximum switching voltage | 250 V AC
3953 | RE17LLBM | Complementary | maximum voltage drop | <4 V 3-wire <8 V 2-wire
3954 | RE17LLBM | Complementary | electrical durability | 100000000 cycles
3955 | RE17LLBM | Complementary | marking | CE
3956 | RE17LLBM | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
3957 | RE17LLBM | Complementary | safety reliability data | B10d = 320000 MTTFd = 353.8 years
3958 | RE17LLBM | Complementary | mounting position | Any position in relation to normal vertical mounting plane
3959 | RE17LLBM | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
3960 | RE17LLBM | Complementary | net weight | 0.068 kg
3961 | RE17LLBM | Complementary | time delay type | L, Li
3962 | RE17LLBM | Complementary | functionality | Asymmetrical flashing timer
3963 | RE17LLBM | Complementary | compatibility code | RE17
3964 | RE17LLBM | Environment | immunity to microbreaks | 20 ms
3965 | RE17LLBM | Environment | derating factor | 5 mA/°C
3966 | RE17LLBM | Environment | standards | EN 61000-6-2 EN 61000-6-4 IEC 61812-1 EN 61000-6-1 EN 61000-6-3 2006/95/EC 2004/108/EC
3967 | RE17LLBM | Environment | product certifications | CULus GL CSA
3968 | RE17LLBM | Environment | ambient air temperature for storage | -30…60 °C
3969 | RE17LLBM | Environment | ambient air temperature for operation | -20…60 °C
3970 | RE17LLBM | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
3971 | RE17LLBM | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
3972 | RE17LLBM | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
3973 | RE17LLBM | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
3974 | RE17LLBM | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
3975 | RE17LLBM | Offer Sustainability | Sustainable offer status | Green Premium product
3976 | RE17LLBM | Offer Sustainability | REACh Regulation | REACh Declaration
3977 | RE17LLBM | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
3978 | RE17LLBM | Offer Sustainability | Mercury free | Yes
3979 | RE17LLBM | Offer Sustainability | RoHS exemption information | Yes
3980 | RE17LLBM | Offer Sustainability | China RoHS Regulation | China RoHS declaration
3981 | RE17LLBM | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
3982 | RE17LLBM | Offer Sustainability | Circularity Profile | End of Life Information
3983 | RE17LMBM | Main | range of product | Zelio Time
3984 | RE17LMBM | Main | product or component type | Modular timing relay
3985 | RE17LMBM | Main | discrete output type | Solid state
3986 | RE17LMBM | Main | width | 17.5 mm
3987 | RE17LMBM | Main | component name | RE17L
3988 | RE17LMBM | Main | time delay type | D A B H Ac At Ht Di C Bw
3989 | RE17LMBM | Main | time delay range | 1...10 s 6...60 s 6...60 min 1...10 h 10...100 h 1...10 min 0.1...1 s
3990 | RE17LMBM | Main | nominal output current | 0.7 A
3991 | RE17LMBM | Complementary | control type | Selector switch front panel
3992 | RE17LMBM | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz
3993 | RE17LMBM | Complementary | voltage range | 0.85...1.1 Us
3994 | RE17LMBM | Complementary | supply frequency | 50...60 Hz +/- 5 %
3995 | RE17LMBM | Complementary | release of input voltage | 8 V
3996 | RE17LMBM | Complementary | control signal pulse width | 0.05 s typical
3997 | RE17LMBM | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
3998 | RE17LMBM | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
3999 | RE17LMBM | Complementary | power on delay | 100 ms
4000 | RE17LMBM | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
4001 | RE17LMBM | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
4002 | RE17LMBM | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
4003 | RE17LMBM | Complementary | housing material | Self-extinguishing
4004 | RE17LMBM | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
4005 | RE17LMBM | Complementary | temperature drift | +/- 0.05 %/°C
4006 | RE17LMBM | Complementary | voltage drift | +/- 0.2 %/V
4007 | RE17LMBM | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
4008 | RE17LMBM | Complementary | reset time | 350 ms on de-energisation typical
4009 | RE17LMBM | Complementary | on-load factor | 100 %
4010 | RE17LMBM | Complementary | power consumption in VA | 0…3 VA at 240 V AC
4011 | RE17LMBM | Complementary | maximum power consumption in W | 1.5 W at 240 V DC
4012 | RE17LMBM | Complementary | breaking capacity | 0.5 A AC conforming to UL 0.7 A AC at 20 °C
4013 | RE17LMBM | Complementary | operating frequency | 10 Hz
4014 | RE17LMBM | Complementary | maximum output current | 20 A
4015 | RE17LMBM | Complementary | minimum switching current | 10 mA
4016 | RE17LMBM | Complementary | maximum leakage current | 5 mA
4017 | RE17LMBM | Complementary | maximum switching voltage | 250 V AC
4018 | RE17LMBM | Complementary | maximum voltage drop | <4 V 3-wire <8 V 2-wire
4019 | RE17LMBM | Complementary | electrical durability | 100000000 cycles
4020 | RE17LMBM | Complementary | marking | CE
4021 | RE17LMBM | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
4022 | RE17LMBM | Complementary | safety reliability data | MTTFd = 353.8 years B10d = 320000
4023 | RE17LMBM | Complementary | mounting position | Any position in relation to normal vertical mounting plane
4024 | RE17LMBM | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
4025 | RE17LMBM | Complementary | net weight | 0.068 kg
4026 | RE17LMBM | Complementary | time delay type | A, Ac, At, B, Bw, C, D, Di, H, Ht
4027 | RE17LMBM | Complementary | functionality | Multifunction
4028 | RE17LMBM | Complementary | compatibility code | RE17
4029 | RE17LMBM | Environment | immunity to microbreaks | 20 ms
4030 | RE17LMBM | Environment | derating factor | 5 mA/°C
4031 | RE17LMBM | Environment | standards | 2004/108/EC EN 61000-6-2 IEC 61812-1 EN 61000-6-4 EN 61000-6-1 2006/95/EC EN 61000-6-3
4032 | RE17LMBM | Environment | product certifications | GL CULus CSA
4033 | RE17LMBM | Environment | ambient air temperature for storage | -30…60 °C
4034 | RE17LMBM | Environment | ambient air temperature for operation | -20…60 °C
4035 | RE17LMBM | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
4036 | RE17LMBM | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
4037 | RE17LMBM | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
4038 | RE17LMBM | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
4039 | RE17LMBM | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
4040 | RE17LMBM | Offer Sustainability | Sustainable offer status | Green Premium product
4041 | RE17LMBM | Offer Sustainability | REACh Regulation | REACh Declaration
4042 | RE17LMBM | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
4043 | RE17LMBM | Offer Sustainability | Mercury free | Yes
4044 | RE17LMBM | Offer Sustainability | RoHS exemption information | Yes
4045 | RE17LMBM | Offer Sustainability | China RoHS Regulation | China RoHS declaration
4046 | RE17LMBM | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
4047 | RE17LMBM | Offer Sustainability | Circularity Profile | End of Life Information
4048 | RE17RAMU | Main | range of product | Zelio Time
4049 | RE17RAMU | Main | product or component type | Modular timing relay
4050 | RE17RAMU | Main | discrete output type | Relay
4051 | RE17RAMU | Main | width | 17.5 mm
4052 | RE17RAMU | Main | device short name | RE17R
4053 | RE17RAMU | Main | time delay type | At A
4054 | RE17RAMU | Main | time delay range | 1...10 min 10...100 h 0.1...1 s 6...60 s 6...60 min 1...10 s 1...10 h
4055 | RE17RAMU | Main | nominal output current | 8 A
4056 | RE17RAMU | Complementary | contacts type and composition | 1 C/O
4057 | RE17RAMU | Complementary | contacts material | Cadmium free
4058 | RE17RAMU | Complementary | height | 90 mm
4059 | RE17RAMU | Complementary | depth | 72 mm
4060 | RE17RAMU | Complementary | control type | Selector switch front panel
4061 | RE17RAMU | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz 24 V DC
4062 | RE17RAMU | Complementary | voltage range | 0.85...1.1 Us
4063 | RE17RAMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
4064 | RE17RAMU | Complementary | release of input voltage | 10 V
4065 | RE17RAMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
4066 | RE17RAMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
4067 | RE17RAMU | Complementary | housing material | Self-extinguishing
4068 | RE17RAMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
4069 | RE17RAMU | Complementary | temperature drift | +/- 0.05 %/°C
4070 | RE17RAMU | Complementary | voltage drift | +/- 0.2 %/V
4071 | RE17RAMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
4072 | RE17RAMU | Complementary | control signal pulse width | 100 ms with load in parallel typical 30 ms typical
4073 | RE17RAMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
4074 | RE17RAMU | Complementary | reset time | 120 ms on de-energisation typical
4075 | RE17RAMU | Complementary | on-load factor | 100 %
4076 | RE17RAMU | Complementary | power consumption in VA | 0…32 VA at 240 V AC
4077 | RE17RAMU | Complementary | maximum power consumption in W | 0.6 W at 24 V DC
4078 | RE17RAMU | Complementary | minimum switching current | 10 mA at 5 V DC
4079 | RE17RAMU | Complementary | maximum switching current | 8 A AC/DC
4080 | RE17RAMU | Complementary | maximum switching voltage | 250 V AC
4081 | RE17RAMU | Complementary | breaking capacity | 2000 VA
4082 | RE17RAMU | Complementary | operating frequency | 10 Hz
4083 | RE17RAMU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
4084 | RE17RAMU | Complementary | mechanical durability | 10000000 cycles
4085 | RE17RAMU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
4086 | RE17RAMU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
4087 | RE17RAMU | Complementary | power on delay | 100 ms
4088 | RE17RAMU | Complementary | marking | CE
4089 | RE17RAMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
4090 | RE17RAMU | Complementary | safety reliability data | B10d = 270000 MTTFd = 296.8 years
4091 | RE17RAMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
4092 | RE17RAMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
4093 | RE17RAMU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
4094 | RE17RAMU | Complementary | net weight | 0.07 kg
4095 | RE17RAMU | Complementary | time delay type | A, At
4096 | RE17RAMU | Complementary | functionality | On-delay timing
4097 | RE17RAMU | Complementary | compatibility code | RE17
4098 | RE17RAMU | Environment | immunity to microbreaks | 20 ms
4099 | RE17RAMU | Environment | standards | 2006/95/EC 2004/108/EC IEC 61812-1 EN 61000-6-3 EN 61000-6-1 EN 61000-6-4 EN 61000-6-2
4100 | RE17RAMU | Environment | product certifications | CSA CULus GL
4101 | RE17RAMU | Environment | ambient air temperature for storage | -30…60 °C
4102 | RE17RAMU | Environment | ambient air temperature for operation | -20…60 °C
4103 | RE17RAMU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
4104 | RE17RAMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
4105 | RE17RAMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
4106 | RE17RAMU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
4107 | RE17RAMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
4108 | RE17RAMU | Offer Sustainability | Sustainable offer status | Green Premium product
4109 | RE17RAMU | Offer Sustainability | REACh Regulation | REACh Declaration
4110 | RE17RAMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
4111 | RE17RAMU | Offer Sustainability | Mercury free | Yes
4112 | RE17RAMU | Offer Sustainability | RoHS exemption information | Yes
4113 | RE17RAMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
4114 | RE17RAMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
4115 | RE17RAMU | Offer Sustainability | Circularity Profile | End of Life Information
4116 | RE17RAMU | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
4117 | RE17RBMU | Main | range of product | Zelio Time
4118 | RE17RBMU | Main | product or component type | Modular timing relay
4119 | RE17RBMU | Main | discrete output type | Relay
4120 | RE17RBMU | Main | width | 17.5 mm
4121 | RE17RBMU | Main | device short name | RE17R
4122 | RE17RBMU | Main | time delay type | B
4123 | RE17RBMU | Main | time delay range | 10...100 h 1...10 min 6...60 min 1...10 s 6...60 s 1...10 h 0.1...1 s
4124 | RE17RBMU | Main | nominal output current | 8 A
4125 | RE17RBMU | Complementary | contacts type and composition | 1 C/O
4126 | RE17RBMU | Complementary | contacts material | Cadmium free
4127 | RE17RBMU | Complementary | height | 90 mm
4128 | RE17RBMU | Complementary | depth | 72 mm
4129 | RE17RBMU | Complementary | control type | Selector switch front panel
4130 | RE17RBMU | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz 24 V DC
4131 | RE17RBMU | Complementary | voltage range | 0.85...1.1 Us
4132 | RE17RBMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
4133 | RE17RBMU | Complementary | release of input voltage | 10 V
4134 | RE17RBMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
4135 | RE17RBMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
4136 | RE17RBMU | Complementary | housing material | Self-extinguishing
4137 | RE17RBMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
4138 | RE17RBMU | Complementary | temperature drift | +/- 0.05 %/°C
4139 | RE17RBMU | Complementary | voltage drift | +/- 0.2 %/V
4140 | RE17RBMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
4141 | RE17RBMU | Complementary | control signal pulse width | 100 ms with load in parallel typical 30 ms typical
4142 | RE17RBMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
4143 | RE17RBMU | Complementary | reset time | 120 ms on de-energisation typical
4144 | RE17RBMU | Complementary | on-load factor | 100 %
4145 | RE17RBMU | Complementary | power consumption in VA | 0…32 VA at 240 V AC
4146 | RE17RBMU | Complementary | maximum power consumption in W | 0.6 W at 24 V DC
4147 | RE17RBMU | Complementary | minimum switching current | 10 mA at 5 V DC
4148 | RE17RBMU | Complementary | maximum switching current | 8 A AC/DC
4149 | RE17RBMU | Complementary | maximum switching voltage | 250 V AC
4150 | RE17RBMU | Complementary | breaking capacity | 2000 VA
4151 | RE17RBMU | Complementary | operating frequency | 10 Hz
4152 | RE17RBMU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
4153 | RE17RBMU | Complementary | mechanical durability | 10000000 cycles
4154 | RE17RBMU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
4155 | RE17RBMU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
4156 | RE17RBMU | Complementary | power on delay | 100 ms
4157 | RE17RBMU | Complementary | marking | CE
4158 | RE17RBMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
4159 | RE17RBMU | Complementary | safety reliability data | MTTFd = 296.8 years B10d = 270000
4160 | RE17RBMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
4161 | RE17RBMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
4162 | RE17RBMU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
4163 | RE17RBMU | Complementary | net weight | 0.07 kg
4164 | RE17RBMU | Complementary | time delay type | B
4165 | RE17RBMU | Complementary | functionality | Pulse signal
4166 | RE17RBMU | Complementary | compatibility code | RE17
4167 | RE17RBMU | Environment | immunity to microbreaks | 20 ms
4168 | RE17RBMU | Environment | standards | 2006/95/EC EN 61000-6-2 EN 61000-6-3 EN 61000-6-4 IEC 61812-1 EN 61000-6-1 2004/108/EC
4169 | RE17RBMU | Environment | product certifications | GL CULus CSA
4170 | RE17RBMU | Environment | ambient air temperature for storage | -30…60 °C
4171 | RE17RBMU | Environment | ambient air temperature for operation | -20…60 °C
4172 | RE17RBMU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
4173 | RE17RBMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
4174 | RE17RBMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
4175 | RE17RBMU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
4176 | RE17RBMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
4177 | RE17RBMU | Offer Sustainability | Sustainable offer status | Green Premium product
4178 | RE17RBMU | Offer Sustainability | REACh Regulation | REACh Declaration
4179 | RE17RBMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
4180 | RE17RBMU | Offer Sustainability | Mercury free | Yes
4181 | RE17RBMU | Offer Sustainability | RoHS exemption information | Yes
4182 | RE17RBMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
4183 | RE17RBMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
4184 | RE17RBMU | Offer Sustainability | Circularity Profile | End of Life Information
4185 | RE17RCMU | Main | range of product | Zelio Time
4186 | RE17RCMU | Main | product or component type | Modular timing relay
4187 | RE17RCMU | Main | discrete output type | Relay
4188 | RE17RCMU | Main | width | 17.5 mm
4189 | RE17RCMU | Main | device short name | RE17R
4190 | RE17RCMU | Main | time delay type | C
4191 | RE17RCMU | Main | time delay range | 6...60 s 1...10 h 1...10 min 6...60 min 0.1...1 s 1...10 s 10...100 h
4192 | RE17RCMU | Main | nominal output current | 8 A
4193 | RE17RCMU | Complementary | contacts type and composition | 1 C/O
4194 | RE17RCMU | Complementary | contacts material | Cadmium free
4195 | RE17RCMU | Complementary | height | 90 mm
4196 | RE17RCMU | Complementary | depth | 72 mm
4197 | RE17RCMU | Complementary | control type | Selector switch front panel
4198 | RE17RCMU | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz 24 V DC
4199 | RE17RCMU | Complementary | voltage range | 0.85...1.1 Us
4200 | RE17RCMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
4201 | RE17RCMU | Complementary | release of input voltage | 10 V
4202 | RE17RCMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
4203 | RE17RCMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
4204 | RE17RCMU | Complementary | housing material | Self-extinguishing
4205 | RE17RCMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
4206 | RE17RCMU | Complementary | temperature drift | +/- 0.05 %/°C
4207 | RE17RCMU | Complementary | voltage drift | +/- 0.2 %/V
4208 | RE17RCMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
4209 | RE17RCMU | Complementary | control signal pulse width | 100 ms with load in parallel typical 30 ms typical
4210 | RE17RCMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
4211 | RE17RCMU | Complementary | reset time | 120 ms on de-energisation typical
4212 | RE17RCMU | Complementary | on-load factor | 100 %
4213 | RE17RCMU | Complementary | power consumption in VA | 0…32 VA at 240 V AC
4214 | RE17RCMU | Complementary | maximum power consumption in W | 0.6 W at 24 V DC
4215 | RE17RCMU | Complementary | minimum switching current | 10 mA at 5 V DC
4216 | RE17RCMU | Complementary | maximum switching current | 8 A AC/DC
4217 | RE17RCMU | Complementary | maximum switching voltage | 250 V AC
4218 | RE17RCMU | Complementary | breaking capacity | 2000 VA
4219 | RE17RCMU | Complementary | operating frequency | 10 Hz
4220 | RE17RCMU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
4221 | RE17RCMU | Complementary | mechanical durability | 10000000 cycles
4222 | RE17RCMU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
4223 | RE17RCMU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
4224 | RE17RCMU | Complementary | power on delay | 100 ms
4225 | RE17RCMU | Complementary | marking | CE
4226 | RE17RCMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
4227 | RE17RCMU | Complementary | safety reliability data | B10d = 270000 MTTFd = 296.8 years
4228 | RE17RCMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
4229 | RE17RCMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
4230 | RE17RCMU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
4231 | RE17RCMU | Complementary | net weight | 0.07 kg
4232 | RE17RCMU | Complementary | time delay type | C
4233 | RE17RCMU | Complementary | functionality | Off-delay timing
4234 | RE17RCMU | Complementary | compatibility code | RE17
4235 | RE17RCMU | Environment | immunity to microbreaks | 20 ms
4236 | RE17RCMU | Environment | standards | EN 61000-6-4 EN 61000-6-2 EN 61000-6-3 2004/108/EC 2006/95/EC IEC 61812-1 EN 61000-6-1
4237 | RE17RCMU | Environment | product certifications | CULus GL CSA
4238 | RE17RCMU | Environment | ambient air temperature for storage | -30…60 °C
4239 | RE17RCMU | Environment | ambient air temperature for operation | -20…60 °C
4240 | RE17RCMU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
4241 | RE17RCMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
4242 | RE17RCMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
4243 | RE17RCMU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
4244 | RE17RCMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
4245 | RE17RCMU | Offer Sustainability | Sustainable offer status | Green Premium product
4246 | RE17RCMU | Offer Sustainability | REACh Regulation | REACh Declaration
4247 | RE17RCMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
4248 | RE17RCMU | Offer Sustainability | Mercury free | Yes
4249 | RE17RCMU | Offer Sustainability | RoHS exemption information | Yes
4250 | RE17RCMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
4251 | RE17RCMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
4252 | RE17RCMU | Offer Sustainability | Circularity Profile | End of Life Information
4253 | RE17RHMU | Main | range of product | Zelio Time
4254 | RE17RHMU | Main | product or component type | Modular timing relay
4255 | RE17RHMU | Main | discrete output type | Relay
4256 | RE17RHMU | Main | width | 17.5 mm
4257 | RE17RHMU | Main | device short name | RE17R
4258 | RE17RHMU | Main | time delay type | H Ht
4259 | RE17RHMU | Main | time delay range | 10...100 h 0.1...1 s 6...60 min 1...10 s 1...10 min 6...60 s 1...10 h
4260 | RE17RHMU | Main | nominal output current | 8 A
4261 | RE17RHMU | Complementary | contacts type and composition | 1 C/O
4262 | RE17RHMU | Complementary | contacts material | Cadmium free
4263 | RE17RHMU | Complementary | height | 90 mm
4264 | RE17RHMU | Complementary | depth | 72 mm
4265 | RE17RHMU | Complementary | control type | Selector switch front panel
4266 | RE17RHMU | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz 24 V DC
4267 | RE17RHMU | Complementary | voltage range | 0.85...1.1 Us
4268 | RE17RHMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
4269 | RE17RHMU | Complementary | release of input voltage | 10 V
4270 | RE17RHMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
4271 | RE17RHMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
4272 | RE17RHMU | Complementary | housing material | Self-extinguishing
4273 | RE17RHMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
4274 | RE17RHMU | Complementary | temperature drift | +/- 0.05 %/°C
4275 | RE17RHMU | Complementary | voltage drift | +/- 0.2 %/V
4276 | RE17RHMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
4277 | RE17RHMU | Complementary | control signal pulse width | 100 ms with load in parallel typical 30 ms typical
4278 | RE17RHMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
4279 | RE17RHMU | Complementary | reset time | 120 ms on de-energisation typical
4280 | RE17RHMU | Complementary | on-load factor | 100 %
4281 | RE17RHMU | Complementary | power consumption in VA | 0…32 VA at 240 V AC
4282 | RE17RHMU | Complementary | maximum power consumption in W | 0.6 W at 24 V DC
4283 | RE17RHMU | Complementary | minimum switching current | 10 mA at 5 V DC
4284 | RE17RHMU | Complementary | maximum switching current | 8 A AC/DC
4285 | RE17RHMU | Complementary | maximum switching voltage | 250 V AC
4286 | RE17RHMU | Complementary | breaking capacity | 2000 VA
4287 | RE17RHMU | Complementary | operating frequency | 10 Hz
4288 | RE17RHMU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
4289 | RE17RHMU | Complementary | mechanical durability | 10000000 cycles
4290 | RE17RHMU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
4291 | RE17RHMU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
4292 | RE17RHMU | Complementary | power on delay | 100 ms
4293 | RE17RHMU | Complementary | marking | CE
4294 | RE17RHMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
4295 | RE17RHMU | Complementary | safety reliability data | B10d = 270000 MTTFd = 296.8 years
4296 | RE17RHMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
4297 | RE17RHMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
4298 | RE17RHMU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
4299 | RE17RHMU | Complementary | net weight | 0.07 kg
4300 | RE17RHMU | Complementary | time delay type | H, Ht
4301 | RE17RHMU | Complementary | functionality | On-delay timing
4302 | RE17RHMU | Complementary | compatibility code | RE17
4303 | RE17RHMU | Environment | immunity to microbreaks | 20 ms
4304 | RE17RHMU | Environment | standards | EN 61000-6-4 EN 61000-6-1 2006/95/EC EN 61000-6-3 IEC 61812-1 2004/108/EC EN 61000-6-2
4305 | RE17RHMU | Environment | product certifications | CULus CSA GL
4306 | RE17RHMU | Environment | ambient air temperature for storage | -30…60 °C
4307 | RE17RHMU | Environment | ambient air temperature for operation | -20…60 °C
4308 | RE17RHMU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
4309 | RE17RHMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
4310 | RE17RHMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
4311 | RE17RHMU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
4312 | RE17RHMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
4313 | RE17RHMU | Offer Sustainability | Sustainable offer status | Green Premium product
4314 | RE17RHMU | Offer Sustainability | REACh Regulation | REACh Declaration
4315 | RE17RHMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
4316 | RE17RHMU | Offer Sustainability | Mercury free | Yes
4317 | RE17RHMU | Offer Sustainability | RoHS exemption information | Yes
4318 | RE17RHMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
4319 | RE17RHMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
4320 | RE17RHMU | Offer Sustainability | Circularity Profile | End of Life Information
4321 | RE17RLJU | Main | range of product | Zelio Time
4322 | RE17RLJU | Main | product or component type | Modular timing relay
4323 | RE17RLJU | Main | discrete output type | Relay
4324 | RE17RLJU | Main | width | 17.5 mm
4325 | RE17RLJU | Main | device short name | RE17R
4326 | RE17RLJU | Main | time delay type | L Li
4327 | RE17RLJU | Main | time delay range | 6...60 min 1...10 h 6...60 s 1...10 s 10...100 h 0.1...1 s 1...10 min
4328 | RE17RLJU | Main | nominal output current | 8 A
4329 | RE17RLJU | Complementary | contacts type and composition | 1 C/O
4330 | RE17RLJU | Complementary | contacts material | Cadmium free
4331 | RE17RLJU | Complementary | height | 90 mm
4332 | RE17RLJU | Complementary | depth | 72 mm
4333 | RE17RLJU | Complementary | control type | Selector switch front panel
4334 | RE17RLJU | Complementary | [Us] rated supply voltage | 12 V AC/DC 50/60 Hz
4335 | RE17RLJU | Complementary | voltage range | 0.9...1.2 Us
4336 | RE17RLJU | Complementary | supply frequency | 50...60 Hz +/- 5 %
4337 | RE17RLJU | Complementary | release of input voltage | 5 V
4338 | RE17RLJU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
4339 | RE17RLJU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
4340 | RE17RLJU | Complementary | housing material | Self-extinguishing
4341 | RE17RLJU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
4342 | RE17RLJU | Complementary | temperature drift | +/- 0.05 %/°C
4343 | RE17RLJU | Complementary | voltage drift | +/- 0.2 %/V
4344 | RE17RLJU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
4345 | RE17RLJU | Complementary | control signal pulse width | 100 ms with load in parallel typical 30 ms typical
4346 | RE17RLJU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
4347 | RE17RLJU | Complementary | reset time | 120 ms on de-energisation typical
4348 | RE17RLJU | Complementary | on-load factor | 100 %
4349 | RE17RLJU | Complementary | power consumption in VA | 0…0.7 VA at 12 V AC
4350 | RE17RLJU | Complementary | maximum power consumption in W | 0.5 W at 12 V DC
4351 | RE17RLJU | Complementary | minimum switching current | 10 mA at 5 V DC
4352 | RE17RLJU | Complementary | maximum switching current | 8 A AC/DC
4353 | RE17RLJU | Complementary | maximum switching voltage | 250 V AC
4354 | RE17RLJU | Complementary | breaking capacity | 2000 VA
4355 | RE17RLJU | Complementary | operating frequency | 10 Hz
4356 | RE17RLJU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
4357 | RE17RLJU | Complementary | mechanical durability | 10000000 cycles
4358 | RE17RLJU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
4359 | RE17RLJU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
4360 | RE17RLJU | Complementary | power on delay | 100 ms
4361 | RE17RLJU | Complementary | marking | CE
4362 | RE17RLJU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
4363 | RE17RLJU | Complementary | safety reliability data | B10d = 270000 MTTFd = 296.8 years
4364 | RE17RLJU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
4365 | RE17RLJU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
4366 | RE17RLJU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF
4367 | RE17RLJU | Complementary | net weight | 0.07 kg
4368 | RE17RLJU | Complementary | time delay type | L, Li
4369 | RE17RLJU | Complementary | functionality | Asymmetrical flashing timer
4370 | RE17RLJU | Complementary | compatibility code | RE17
4371 | RE17RLJU | Environment | immunity to microbreaks | 20 ms
4372 | RE17RLJU | Environment | standards | 2006/95/EC 2004/108/EC EN 61000-6-4 IEC 61812-1 EN 61000-6-3 EN 61000-6-2 EN 61000-6-1
4373 | RE17RLJU | Environment | product certifications | CSA CULus GL
4374 | RE17RLJU | Environment | ambient air temperature for storage | -30…60 °C
4375 | RE17RLJU | Environment | ambient air temperature for operation | -20…60 °C
4376 | RE17RLJU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
4377 | RE17RLJU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
4378 | RE17RLJU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
4379 | RE17RLJU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
4380 | RE17RLJU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
4381 | RE17RLJU | Offer Sustainability | Sustainable offer status | Green Premium product
4382 | RE17RLJU | Offer Sustainability | REACh Regulation | REACh Declaration
4383 | RE17RLJU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
4384 | RE17RLJU | Offer Sustainability | Mercury free | Yes
4385 | RE17RLJU | Offer Sustainability | RoHS exemption information | Yes
4386 | RE17RLJU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
4387 | RE17RLJU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
4388 | RE17RLJU | Offer Sustainability | Circularity Profile | End of Life Information
4389 | RE17RLMU | Main | range of product | Zelio Time
4390 | RE17RLMU | Main | product or component type | Modular timing relay
4391 | RE17RLMU | Main | discrete output type | Relay
4392 | RE17RLMU | Main | width | 17.5 mm
4393 | RE17RLMU | Main | device short name | RE17R
4394 | RE17RLMU | Main | time delay type | Li L
4395 | RE17RLMU | Main | time delay range | 1...10 h 1...10 s 0.1...1 s 6...60 min 1...10 min 10...100 h 6...60 s
4396 | RE17RLMU | Main | nominal output current | 8 A
4397 | RE17RLMU | Complementary | contacts type and composition | 1 C/O
4398 | RE17RLMU | Complementary | contacts material | Cadmium free
4399 | RE17RLMU | Complementary | height | 90 mm
4400 | RE17RLMU | Complementary | depth | 72 mm
4401 | RE17RLMU | Complementary | control type | Selector switch front panel
4402 | RE17RLMU | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz 24 V DC
4403 | RE17RLMU | Complementary | voltage range | 0.85...1.1 Us
4404 | RE17RLMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
4405 | RE17RLMU | Complementary | release of input voltage | 10 V
4406 | RE17RLMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
4407 | RE17RLMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
4408 | RE17RLMU | Complementary | housing material | Self-extinguishing
4409 | RE17RLMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
4410 | RE17RLMU | Complementary | temperature drift | +/- 0.05 %/°C
4411 | RE17RLMU | Complementary | voltage drift | +/- 0.2 %/V
4412 | RE17RLMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
4413 | RE17RLMU | Complementary | control signal pulse width | 100 ms with load in parallel typical 30 ms typical
4414 | RE17RLMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
4415 | RE17RLMU | Complementary | reset time | 120 ms on de-energisation typical
4416 | RE17RLMU | Complementary | on-load factor | 100 %
4417 | RE17RLMU | Complementary | power consumption in VA | 0…32 VA at 240 V AC
4418 | RE17RLMU | Complementary | maximum power consumption in W | 0.6 W at 24 V DC
4419 | RE17RLMU | Complementary | minimum switching current | 10 mA at 5 V DC
4420 | RE17RLMU | Complementary | maximum switching current | 8 A AC/DC
4421 | RE17RLMU | Complementary | maximum switching voltage | 250 V AC
4422 | RE17RLMU | Complementary | breaking capacity | 2000 VA
4423 | RE17RLMU | Complementary | operating frequency | 10 Hz
4424 | RE17RLMU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
4425 | RE17RLMU | Complementary | mechanical durability | 10000000 cycles
4426 | RE17RLMU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
4427 | RE17RLMU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
4428 | RE17RLMU | Complementary | power on delay | 100 ms
4429 | RE17RLMU | Complementary | marking | CE
4430 | RE17RLMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
4431 | RE17RLMU | Complementary | safety reliability data | MTTFd = 296.8 years B10d = 270000
4432 | RE17RLMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
4433 | RE17RLMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
4434 | RE17RLMU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF
4435 | RE17RLMU | Complementary | net weight | 0.07 kg
4436 | RE17RLMU | Complementary | time delay type | L, Li
4437 | RE17RLMU | Complementary | functionality | Asymmetrical flashing timer
4438 | RE17RLMU | Complementary | compatibility code | RE17
4439 | RE17RLMU | Environment | immunity to microbreaks | 20 ms
4440 | RE17RLMU | Environment | standards | 2006/95/EC EN 61000-6-2 EN 61000-6-4 2004/108/EC IEC 61812-1 EN 61000-6-3 EN 61000-6-1
4441 | RE17RLMU | Environment | product certifications | GL CULus CSA
4442 | RE17RLMU | Environment | ambient air temperature for storage | -30…60 °C
4443 | RE17RLMU | Environment | ambient air temperature for operation | -20…60 °C
4444 | RE17RLMU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
4445 | RE17RLMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
4446 | RE17RLMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
4447 | RE17RLMU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
4448 | RE17RLMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
4449 | RE17RLMU | Offer Sustainability | Sustainable offer status | Green Premium product
4450 | RE17RLMU | Offer Sustainability | REACh Regulation | REACh Declaration
4451 | RE17RLMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
4452 | RE17RLMU | Offer Sustainability | Mercury free | Yes
4453 | RE17RLMU | Offer Sustainability | RoHS exemption information | Yes
4454 | RE17RLMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
4455 | RE17RLMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
4456 | RE17RLMU | Offer Sustainability | Circularity Profile | End of Life Information
4457 | RE17RMEMU | Main | range of product | Zelio Time
4458 | RE17RMEMU | Main | product or component type | Modular timing relay
4459 | RE17RMEMU | Main | discrete output type | Relay
4460 | RE17RMEMU | Main | width | 17.5 mm
4461 | RE17RMEMU | Main | device short name | RE17R
4462 | RE17RMEMU | Main | time delay type | A Ht H Di At D B C
4463 | RE17RMEMU | Main | time delay range | 6...60 min 1...10 min 1...10 s 1...10 h 6...60 s 0.1...1 s
4464 | RE17RMEMU | Main | nominal output current | 8 A
4465 | RE17RMEMU | Complementary | contacts type and composition | 1 C/O
4466 | RE17RMEMU | Complementary | contacts material | Cadmium free
4467 | RE17RMEMU | Complementary | height | 90 mm
4468 | RE17RMEMU | Complementary | depth | 72 mm
4469 | RE17RMEMU | Complementary | control type | Selector switch front panel
4470 | RE17RMEMU | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz 24 V DC
4471 | RE17RMEMU | Complementary | voltage range | 0.85...1.1 Us
4472 | RE17RMEMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
4473 | RE17RMEMU | Complementary | release of input voltage | 10 V
4474 | RE17RMEMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
4475 | RE17RMEMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
4476 | RE17RMEMU | Complementary | housing material | Self-extinguishing
4477 | RE17RMEMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
4478 | RE17RMEMU | Complementary | temperature drift | +/- 0.05 %/°C
4479 | RE17RMEMU | Complementary | voltage drift | +/- 0.2 %/V
4480 | RE17RMEMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
4481 | RE17RMEMU | Complementary | control signal pulse width | 100 ms with load in parallel typical 30 ms typical
4482 | RE17RMEMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
4483 | RE17RMEMU | Complementary | reset time | 120 ms on de-energisation typical
4484 | RE17RMEMU | Complementary | on-load factor | 100 %
4485 | RE17RMEMU | Complementary | power consumption in VA | 0…32 VA at 240 V AC
4486 | RE17RMEMU | Complementary | maximum power consumption in W | 0.6 W at 24 V DC
4487 | RE17RMEMU | Complementary | minimum switching current | 10 mA at 5 V DC
4488 | RE17RMEMU | Complementary | maximum switching current | 8 A AC/DC
4489 | RE17RMEMU | Complementary | maximum switching voltage | 250 V AC
4490 | RE17RMEMU | Complementary | breaking capacity | 2000 VA
4491 | RE17RMEMU | Complementary | operating frequency | 10 Hz
4492 | RE17RMEMU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
4493 | RE17RMEMU | Complementary | mechanical durability | 10000000 cycles
4494 | RE17RMEMU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
4495 | RE17RMEMU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
4496 | RE17RMEMU | Complementary | power on delay | 100 ms
4497 | RE17RMEMU | Complementary | marking | CE
4498 | RE17RMEMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
4499 | RE17RMEMU | Complementary | safety reliability data | MTTFd = 296.8 years B10d = 270000
4500 | RE17RMEMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
4501 | RE17RMEMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
4502 | RE17RMEMU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
4503 | RE17RMEMU | Complementary | net weight | 0.07 kg
4504 | RE17RMEMU | Complementary | time delay type | A, At, B, C, D, Di, H, Ht
4505 | RE17RMEMU | Complementary | functionality | Multifunction
4506 | RE17RMEMU | Complementary | compatibility code | RE17
4507 | RE17RMEMU | Environment | immunity to microbreaks | 20 ms
4508 | RE17RMEMU | Environment | standards | 2004/108/EC EN 61000-6-2 EN 61000-6-3 EN 61000-6-1 2006/95/EC IEC 61812-1 EN 61000-6-4
4509 | RE17RMEMU | Environment | product certifications | CSA CULus
4510 | RE17RMEMU | Environment | ambient air temperature for storage | -30…60 °C
4511 | RE17RMEMU | Environment | ambient air temperature for operation | -20…60 °C
4512 | RE17RMEMU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
4513 | RE17RMEMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
4514 | RE17RMEMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
4515 | RE17RMEMU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
4516 | RE17RMEMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
4517 | RE17RMEMU | Offer Sustainability | Sustainable offer status | Green Premium product
4518 | RE17RMEMU | Offer Sustainability | REACh Regulation | REACh Declaration
4519 | RE17RMEMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
4520 | RE17RMEMU | Offer Sustainability | Mercury free | Yes
4521 | RE17RMEMU | Offer Sustainability | RoHS exemption information | Yes
4522 | RE17RMEMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
4523 | RE17RMEMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
4524 | RE17RMEMU | Offer Sustainability | Circularity Profile | End of Life Information
4525 | RE17RMJU | Main | range of product | Zelio Time
4526 | RE17RMJU | Main | product or component type | Modular timing relay
4527 | RE17RMJU | Main | discrete output type | Relay
4528 | RE17RMJU | Main | width | 17.5 mm
4529 | RE17RMJU | Main | device short name | RE17R
4530 | RE17RMJU | Main | time delay type | H A C Ac Ht D Bw Di B At
4531 | RE17RMJU | Main | time delay range | 1...10 s 6...60 s 10...100 h 1...10 min 1...10 h 0.1...1 s 6...60 min
4532 | RE17RMJU | Main | nominal output current | 8 A
4533 | RE17RMJU | Complementary | contacts type and composition | 1 C/O
4534 | RE17RMJU | Complementary | contacts material | Cadmium free
4535 | RE17RMJU | Complementary | height | 90 mm
4536 | RE17RMJU | Complementary | depth | 72 mm
4537 | RE17RMJU | Complementary | control type | Selector switch front panel
4538 | RE17RMJU | Complementary | [Us] rated supply voltage | 12 V AC/DC 50/60 Hz
4539 | RE17RMJU | Complementary | voltage range | 0.9...1.2 Us
4540 | RE17RMJU | Complementary | supply frequency | 50...60 Hz +/- 5 %
4541 | RE17RMJU | Complementary | release of input voltage | 5 V
4542 | RE17RMJU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
4543 | RE17RMJU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
4544 | RE17RMJU | Complementary | housing material | Self-extinguishing
4545 | RE17RMJU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
4546 | RE17RMJU | Complementary | temperature drift | +/- 0.05 %/°C
4547 | RE17RMJU | Complementary | voltage drift | +/- 0.2 %/V
4548 | RE17RMJU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
4549 | RE17RMJU | Complementary | control signal pulse width | 100 ms with load in parallel typical 30 ms typical
4550 | RE17RMJU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
4551 | RE17RMJU | Complementary | reset time | 120 ms on de-energisation typical
4552 | RE17RMJU | Complementary | on-load factor | 100 %
4553 | RE17RMJU | Complementary | power consumption in VA | 0…0.7 VA at 12 V AC
4554 | RE17RMJU | Complementary | maximum power consumption in W | 0.5 W at 12 V DC
4555 | RE17RMJU | Complementary | minimum switching current | 10 mA at 5 V DC
4556 | RE17RMJU | Complementary | maximum switching current | 8 A AC/DC
4557 | RE17RMJU | Complementary | maximum switching voltage | 250 V AC
4558 | RE17RMJU | Complementary | breaking capacity | 2000 VA
4559 | RE17RMJU | Complementary | operating frequency | 10 Hz
4560 | RE17RMJU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
4561 | RE17RMJU | Complementary | mechanical durability | 10000000 cycles
4562 | RE17RMJU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
4563 | RE17RMJU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
4564 | RE17RMJU | Complementary | power on delay | 100 ms
4565 | RE17RMJU | Complementary | marking | CE
4566 | RE17RMJU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
4567 | RE17RMJU | Complementary | safety reliability data | MTTFd = 296.8 years B10d = 270000
4568 | RE17RMJU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
4569 | RE17RMJU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
4570 | RE17RMJU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
4571 | RE17RMJU | Complementary | net weight | 0.07 kg
4572 | RE17RMJU | Complementary | time delay type | A, Ac, At, B, Bw, C, D, Di, H, Ht
4573 | RE17RMJU | Complementary | functionality | Multifunction
4574 | RE17RMJU | Complementary | compatibility code | RE17
4575 | RE17RMJU | Environment | immunity to microbreaks | 20 ms
4576 | RE17RMJU | Environment | standards | 2006/95/EC 2004/108/EC EN 61000-6-4 EN 61000-6-1 EN 61000-6-3 IEC 61812-1 EN 61000-6-2
4577 | RE17RMJU | Environment | product certifications | CSA GL CULus
4578 | RE17RMJU | Environment | ambient air temperature for storage | -30…60 °C
4579 | RE17RMJU | Environment | ambient air temperature for operation | -20…60 °C
4580 | RE17RMJU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
4581 | RE17RMJU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
4582 | RE17RMJU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
4583 | RE17RMJU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
4584 | RE17RMJU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
4585 | RE17RMJU | Offer Sustainability | Sustainable offer status | Green Premium product
4586 | RE17RMJU | Offer Sustainability | REACh Regulation | REACh Declaration
4587 | RE17RMJU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
4588 | RE17RMJU | Offer Sustainability | Mercury free | Yes
4589 | RE17RMJU | Offer Sustainability | RoHS exemption information | Yes
4590 | RE17RMJU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
4591 | RE17RMJU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
4592 | RE17RMJU | Offer Sustainability | Circularity Profile | End of Life Information
4593 | RE17RMMU | Main | range of product | Zelio Time
4594 | RE17RMMU | Main | product or component type | Modular timing relay
4595 | RE17RMMU | Main | discrete output type | Relay
4596 | RE17RMMU | Main | width | 17.5 mm
4597 | RE17RMMU | Main | device short name | RE17R
4598 | RE17RMMU | Main | time delay type | C A B At D Ht Bw Di H Ac
4599 | RE17RMMU | Main | time delay range | 6...60 min 1...10 h 0.1...1 s 1...10 s 1...10 min 10...100 h 6...60 s
4600 | RE17RMMU | Main | nominal output current | 8 A
4601 | RE17RMMU | Complementary | contacts type and composition | 1 C/O
4602 | RE17RMMU | Complementary | contacts material | Cadmium free
4603 | RE17RMMU | Complementary | height | 90 mm
4604 | RE17RMMU | Complementary | depth | 72 mm
4605 | RE17RMMU | Complementary | control type | Selector switch front panel
4606 | RE17RMMU | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz 24 V DC
4607 | RE17RMMU | Complementary | voltage range | 0.85...1.1 Us
4608 | RE17RMMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
4609 | RE17RMMU | Complementary | release of input voltage | 10 V
4610 | RE17RMMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
4611 | RE17RMMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
4612 | RE17RMMU | Complementary | housing material | Self-extinguishing
4613 | RE17RMMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
4614 | RE17RMMU | Complementary | temperature drift | +/- 0.05 %/°C
4615 | RE17RMMU | Complementary | voltage drift | +/- 0.2 %/V
4616 | RE17RMMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
4617 | RE17RMMU | Complementary | control signal pulse width | 100 ms with load in parallel typical 30 ms typical
4618 | RE17RMMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
4619 | RE17RMMU | Complementary | reset time | 120 ms on de-energisation typical
4620 | RE17RMMU | Complementary | on-load factor | 100 %
4621 | RE17RMMU | Complementary | power consumption in VA | 0…32 VA at 240 V AC
4622 | RE17RMMU | Complementary | maximum power consumption in W | 0.6 W at 24 V DC
4623 | RE17RMMU | Complementary | minimum switching current | 10 mA at 5 V DC
4624 | RE17RMMU | Complementary | maximum switching current | 8 A AC/DC
4625 | RE17RMMU | Complementary | maximum switching voltage | 250 V AC
4626 | RE17RMMU | Complementary | breaking capacity | 2000 VA
4627 | RE17RMMU | Complementary | operating frequency | 10 Hz
4628 | RE17RMMU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
4629 | RE17RMMU | Complementary | mechanical durability | 10000000 cycles
4630 | RE17RMMU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
4631 | RE17RMMU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
4632 | RE17RMMU | Complementary | power on delay | 100 ms
4633 | RE17RMMU | Complementary | marking | CE
4634 | RE17RMMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
4635 | RE17RMMU | Complementary | safety reliability data | B10d = 270000 MTTFd = 296.8 years
4636 | RE17RMMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
4637 | RE17RMMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
4638 | RE17RMMU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
4639 | RE17RMMU | Complementary | net weight | 0.07 kg
4640 | RE17RMMU | Complementary | time delay type | A, Ac, At, B, Bw, C, D, Di, H, Ht
4641 | RE17RMMU | Complementary | functionality | Multifunction
4642 | RE17RMMU | Complementary | compatibility code | RE17
4643 | RE17RMMU | Environment | immunity to microbreaks | 20 ms
4644 | RE17RMMU | Environment | standards | 2006/95/EC 2004/108/EC IEC 61812-1 EN 61000-6-2 EN 61000-6-3 EN 61000-6-4 EN 61000-6-1
4645 | RE17RMMU | Environment | product certifications | CSA GL CULus
4646 | RE17RMMU | Environment | ambient air temperature for storage | -30…60 °C
4647 | RE17RMMU | Environment | ambient air temperature for operation | -20…60 °C
4648 | RE17RMMU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
4649 | RE17RMMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
4650 | RE17RMMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
4651 | RE17RMMU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
4652 | RE17RMMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
4653 | RE17RMMU | Offer Sustainability | Sustainable offer status | Green Premium product
4654 | RE17RMMU | Offer Sustainability | REACh Regulation | REACh Declaration
4655 | RE17RMMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
4656 | RE17RMMU | Offer Sustainability | Mercury free | Yes
4657 | RE17RMMU | Offer Sustainability | RoHS exemption information | Yes
4658 | RE17RMMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
4659 | RE17RMMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
4660 | RE17RMMU | Offer Sustainability | Circularity Profile | End of Life Information
4661 | RE17RMMW | Main | range of product | Zelio Time
4662 | RE17RMMW | Main | product or component type | Modular timing relay
4663 | RE17RMMW | Main | discrete output type | Relay
4664 | RE17RMMW | Main | width | 17.5 mm
4665 | RE17RMMW | Main | device short name | RE17R
4666 | RE17RMMW | Main | time delay type | At Di Ht H C Ac A D B Bw
4667 | RE17RMMW | Main | time delay range | 1...10 h 0.1...1 s 6...60 s 10...100 h 6...60 min 1...10 s 1...10 min
4668 | RE17RMMW | Main | nominal output current | 8 A
4669 | RE17RMMW | Complementary | contacts type and composition | 1 C/O
4670 | RE17RMMW | Complementary | contacts material | Cadmium free
4671 | RE17RMMW | Complementary | height | 90 mm
4672 | RE17RMMW | Complementary | depth | 72 mm
4673 | RE17RMMW | Complementary | control type | Selector switch front panel
4674 | RE17RMMW | Complementary | [Us] rated supply voltage | 12...240 V AC/DC 50/60 Hz
4675 | RE17RMMW | Complementary | voltage range | 0.85...1.1 Us
4676 | RE17RMMW | Complementary | supply frequency | 50...60 Hz +/- 5 %
4677 | RE17RMMW | Complementary | release of input voltage | 5 V
4678 | RE17RMMW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
4679 | RE17RMMW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
4680 | RE17RMMW | Complementary | housing material | Self-extinguishing
4681 | RE17RMMW | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
4682 | RE17RMMW | Complementary | temperature drift | +/- 0.05 %/°C
4683 | RE17RMMW | Complementary | voltage drift | +/- 0.2 %/V
4684 | RE17RMMW | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
4685 | RE17RMMW | Complementary | control signal pulse width | 100 ms with load in parallel typical 30 ms typical
4686 | RE17RMMW | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
4687 | RE17RMMW | Complementary | reset time | 120 ms on de-energisation typical
4688 | RE17RMMW | Complementary | on-load factor | 100 %
4689 | RE17RMMW | Complementary | power consumption in VA | 0…3 VA at 240 V AC
4690 | RE17RMMW | Complementary | maximum power consumption in W | 1.5 W at 240 V DC
4691 | RE17RMMW | Complementary | minimum switching current | 10 mA at 5 V DC
4692 | RE17RMMW | Complementary | maximum switching current | 8 A AC/DC
4693 | RE17RMMW | Complementary | maximum switching voltage | 250 V AC
4694 | RE17RMMW | Complementary | breaking capacity | 2000 VA
4695 | RE17RMMW | Complementary | operating frequency | 10 Hz
4696 | RE17RMMW | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
4697 | RE17RMMW | Complementary | mechanical durability | 10000000 cycles
4698 | RE17RMMW | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
4699 | RE17RMMW | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
4700 | RE17RMMW | Complementary | power on delay | 100 ms
4701 | RE17RMMW | Complementary | marking | CE
4702 | RE17RMMW | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
4703 | RE17RMMW | Complementary | safety reliability data | MTTFd = 296.8 years B10d = 270000
4704 | RE17RMMW | Complementary | mounting position | Any position in relation to normal vertical mounting plane
4705 | RE17RMMW | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
4706 | RE17RMMW | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
4707 | RE17RMMW | Complementary | net weight | 0.07 kg
4708 | RE17RMMW | Complementary | time delay type | A, Ac, At, B, Bw, C, D, Di, H, Ht
4709 | RE17RMMW | Complementary | functionality | Multifunction
4710 | RE17RMMW | Complementary | compatibility code | RE17
4711 | RE17RMMW | Environment | immunity to microbreaks | 20 ms
4712 | RE17RMMW | Environment | standards | 2006/95/EC EN 61000-6-3 IEC 61812-1 EN 61000-6-2 EN 61000-6-1 2004/108/EC EN 61000-6-4
4713 | RE17RMMW | Environment | product certifications | CSA GL CULus
4714 | RE17RMMW | Environment | ambient air temperature for storage | -30…60 °C
4715 | RE17RMMW | Environment | ambient air temperature for operation | -20…60 °C
4716 | RE17RMMW | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
4717 | RE17RMMW | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
4718 | RE17RMMW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
4719 | RE17RMMW | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
4720 | RE17RMMW | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
4721 | RE17RMMW | Offer Sustainability | Sustainable offer status | Green Premium product
4722 | RE17RMMW | Offer Sustainability | REACh Regulation | REACh Declaration
4723 | RE17RMMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
4724 | RE17RMMW | Offer Sustainability | Mercury free | Yes
4725 | RE17RMMW | Offer Sustainability | RoHS exemption information | Yes
4726 | RE17RMMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
4727 | RE17RMMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
4728 | RE17RMMW | Offer Sustainability | Circularity Profile | End of Life Information
4729 | RE17RMMWS | Main | range of product | Zelio Time
4730 | RE17RMMWS | Main | product or component type | Modular timing relay
4731 | RE17RMMWS | Main | discrete output type | Relay
4732 | RE17RMMWS | Main | width | 17.5 mm
4733 | RE17RMMWS | Main | device short name | RE17R
4734 | RE17RMMWS | Main | time delay type | D B At Bw Ac A Di Ht C H
4735 | RE17RMMWS | Main | time delay range | 6...60 min 6...60 s 1...10 min 1...10 h 0.1...1 s 10...100 h 1...10 s
4736 | RE17RMMWS | Main | nominal output current | 8 A
4737 | RE17RMMWS | Complementary | contacts type and composition | 1 C/O
4738 | RE17RMMWS | Complementary | contacts material | Cadmium free
4739 | RE17RMMWS | Complementary | height | 90 mm
4740 | RE17RMMWS | Complementary | depth | 72 mm
4741 | RE17RMMWS | Complementary | control type | Selector switch front panel
4742 | RE17RMMWS | Complementary | [Us] rated supply voltage | 12...240 V AC/DC 50/60 Hz
4743 | RE17RMMWS | Complementary | voltage range | 0.85...1.1 Us
4744 | RE17RMMWS | Complementary | supply frequency | 50...60 Hz +/- 5 %
4745 | RE17RMMWS | Complementary | release of input voltage | 5 V
4746 | RE17RMMWS | Complementary | connections - terminals | Spring terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) solid without cable end Spring terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
4747 | RE17RMMWS | Complementary | housing material | Self-extinguishing
4748 | RE17RMMWS | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
4749 | RE17RMMWS | Complementary | temperature drift | +/- 0.05 %/°C
4750 | RE17RMMWS | Complementary | voltage drift | +/- 0.2 %/V
4751 | RE17RMMWS | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
4752 | RE17RMMWS | Complementary | control signal pulse width | 100 ms with load in parallel typical 30 ms typical
4753 | RE17RMMWS | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
4754 | RE17RMMWS | Complementary | reset time | 120 ms on de-energisation typical
4755 | RE17RMMWS | Complementary | on-load factor | 100 %
4756 | RE17RMMWS | Complementary | power consumption in VA | 0…3 VA at 240 V AC
4757 | RE17RMMWS | Complementary | maximum power consumption in W | 1.5 W at 240 V DC
4758 | RE17RMMWS | Complementary | minimum switching current | 10 mA at 5 V DC
4759 | RE17RMMWS | Complementary | maximum switching current | 8 A AC/DC
4760 | RE17RMMWS | Complementary | maximum switching voltage | 250 V AC
4761 | RE17RMMWS | Complementary | breaking capacity | 2000 VA
4762 | RE17RMMWS | Complementary | operating frequency | 10 Hz
4763 | RE17RMMWS | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
4764 | RE17RMMWS | Complementary | mechanical durability | 10000000 cycles
4765 | RE17RMMWS | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
4766 | RE17RMMWS | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
4767 | RE17RMMWS | Complementary | power on delay | 100 ms
4768 | RE17RMMWS | Complementary | marking | CE
4769 | RE17RMMWS | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
4770 | RE17RMMWS | Complementary | safety reliability data | MTTFd = 296.8 years B10d = 270000
4771 | RE17RMMWS | Complementary | mounting position | Any position in relation to normal vertical mounting plane
4772 | RE17RMMWS | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
4773 | RE17RMMWS | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
4774 | RE17RMMWS | Complementary | net weight | 0.07 kg
4775 | RE17RMMWS | Complementary | time delay type | A, Ac, At, B, Bw, C, D, Di, H, Ht
4776 | RE17RMMWS | Complementary | functionality | Multifunction
4777 | RE17RMMWS | Complementary | compatibility code | RE17
4778 | RE17RMMWS | Environment | immunity to microbreaks | 20 ms
4779 | RE17RMMWS | Environment | standards | 2006/95/EC EN 61000-6-4 2004/108/EC EN 61000-6-3 IEC 61812-1 EN 61000-6-2 EN 61000-6-1
4780 | RE17RMMWS | Environment | product certifications | GL CULus CSA
4781 | RE17RMMWS | Environment | ambient air temperature for storage | -30…60 °C
4782 | RE17RMMWS | Environment | ambient air temperature for operation | -20…60 °C
4783 | RE17RMMWS | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
4784 | RE17RMMWS | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
4785 | RE17RMMWS | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
4786 | RE17RMMWS | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
4787 | RE17RMMWS | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
4788 | RE17RMMWS | Offer Sustainability | Sustainable offer status | Green Premium product
4789 | RE17RMMWS | Offer Sustainability | REACh Regulation | REACh Declaration
4790 | RE17RMMWS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
4791 | RE17RMMWS | Offer Sustainability | Mercury free | Yes
4792 | RE17RMMWS | Offer Sustainability | RoHS exemption information | Yes
4793 | RE17RMMWS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
4794 | RE17RMMWS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
4795 | RE17RMMWS | Offer Sustainability | Circularity Profile | End of Life Information
4796 | RE17RMXMU | Main | range of product | Zelio Time
4797 | RE17RMXMU | Main | product or component type | Modular timing relay
4798 | RE17RMXMU | Main | discrete output type | Relay
4799 | RE17RMXMU | Main | width | 17.5 mm
4800 | RE17RMXMU | Main | device short name | RE17R
4801 | RE17RMXMU | Main | time delay type | Ah Tl N Tt Ad Pt O W P
4802 | RE17RMXMU | Main | time delay range | 6...60 s 1...10 min 0.1...1 s 1...10 h 1...10 s 6...60 min 10...100 h
4803 | RE17RMXMU | Main | nominal output current | 8 A
4804 | RE17RMXMU | Complementary | contacts type and composition | 1 C/O
4805 | RE17RMXMU | Complementary | contacts material | Cadmium free
4806 | RE17RMXMU | Complementary | height | 90 mm
4807 | RE17RMXMU | Complementary | depth | 72 mm
4808 | RE17RMXMU | Complementary | control type | Selector switch front panel
4809 | RE17RMXMU | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz 24 V DC
4810 | RE17RMXMU | Complementary | voltage range | 0.85...1.1 Us
4811 | RE17RMXMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
4812 | RE17RMXMU | Complementary | release of input voltage | 10 V
4813 | RE17RMXMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
4814 | RE17RMXMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
4815 | RE17RMXMU | Complementary | housing material | Self-extinguishing
4816 | RE17RMXMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
4817 | RE17RMXMU | Complementary | temperature drift | +/- 0.05 %/°C
4818 | RE17RMXMU | Complementary | voltage drift | +/- 0.2 %/V
4819 | RE17RMXMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
4820 | RE17RMXMU | Complementary | control signal pulse width | 100 ms with load in parallel typical 30 ms typical
4821 | RE17RMXMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
4822 | RE17RMXMU | Complementary | reset time | 120 ms on de-energisation typical
4823 | RE17RMXMU | Complementary | on-load factor | 100 %
4824 | RE17RMXMU | Complementary | power consumption in VA | 0…32 VA at 240 V AC
4825 | RE17RMXMU | Complementary | maximum power consumption in W | 0.6 W at 24 V DC
4826 | RE17RMXMU | Complementary | minimum switching current | 10 mA at 5 V DC
4827 | RE17RMXMU | Complementary | maximum switching current | 8 A AC/DC
4828 | RE17RMXMU | Complementary | maximum switching voltage | 250 V AC
4829 | RE17RMXMU | Complementary | breaking capacity | 2000 VA
4830 | RE17RMXMU | Complementary | operating frequency | 10 Hz
4831 | RE17RMXMU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
4832 | RE17RMXMU | Complementary | mechanical durability | 10000000 cycles
4833 | RE17RMXMU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
4834 | RE17RMXMU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
4835 | RE17RMXMU | Complementary | power on delay | 100 ms
4836 | RE17RMXMU | Complementary | marking | CE
4837 | RE17RMXMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
4838 | RE17RMXMU | Complementary | safety reliability data | MTTFd = 296.8 years B10d = 270000
4839 | RE17RMXMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
4840 | RE17RMXMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
4841 | RE17RMXMU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
4842 | RE17RMXMU | Complementary | net weight | 0.07 kg
4843 | RE17RMXMU | Complementary | time delay type | Ad, Ah, N, O, P, Pt, TI, Tt, W
4844 | RE17RMXMU | Complementary | functionality | Multifunction
4845 | RE17RMXMU | Complementary | compatibility code | RE17
4846 | RE17RMXMU | Environment | immunity to microbreaks | 20 ms
4847 | RE17RMXMU | Environment | standards | 2006/95/EC 2004/108/EC EN 61000-6-1 EN 61000-6-4 EN 61000-6-2 EN 61000-6-3 IEC 61812-1
4848 | RE17RMXMU | Environment | product certifications | CULus GL CSA
4849 | RE17RMXMU | Environment | ambient air temperature for storage | -30…60 °C
4850 | RE17RMXMU | Environment | ambient air temperature for operation | -20…60 °C
4851 | RE17RMXMU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529
4852 | RE17RMXMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
4853 | RE17RMXMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
4854 | RE17RMXMU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
4855 | RE17RMXMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022
4856 | RE17RMXMU | Offer Sustainability | Sustainable offer status | Green Premium product
4857 | RE17RMXMU | Offer Sustainability | REACh Regulation | REACh Declaration
4858 | RE17RMXMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
4859 | RE17RMXMU | Offer Sustainability | Mercury free | Yes
4860 | RE17RMXMU | Offer Sustainability | RoHS exemption information | Yes
4861 | RE17RMXMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
4862 | RE17RMXMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
4863 | RE17RMXMU | Offer Sustainability | Circularity Profile | End of Life Information
4864 | RE22R1QMU | Main | range of product | Zelio Time
4865 | RE22R1QMU | Main | product or component type | Modular timing relay
4866 | RE22R1QMU | Main | discrete output type | Relay
4867 | RE22R1QMU | Main | device short name | RE22
4868 | RE22R1QMU | Main | nominal output current | 8 A
4869 | RE22R1QMU | Complementary | contacts type and composition | 1 C/O timed contact
4870 | RE22R1QMU | Complementary | time delay type | Q
4871 | RE22R1QMU | Complementary | time delay range | 1...10 min 6...60 s 0.1...1 s 1...10 h 1...10 s 6...60 min 10...100 h
4872 | RE22R1QMU | Complementary | control type | Rotary knob front panel
4873 | RE22R1QMU | Complementary | [Us] rated supply voltage | 24...240 V AC 24 V DC
4874 | RE22R1QMU | Complementary | voltage range | 0.85...1.1 Us
4875 | RE22R1QMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
4876 | RE22R1QMU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² with cable end Screw terminals, 2 x 2.5 mm² without cable end
4877 | RE22R1QMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
4878 | RE22R1QMU | Complementary | housing material | Self-extinguishing
4879 | RE22R1QMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
4880 | RE22R1QMU | Complementary | temperature drift | +/- 0.05 %/°C
4881 | RE22R1QMU | Complementary | voltage drift | +/- 0.2 %/V
4882 | RE22R1QMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
4883 | RE22R1QMU | Complementary | Control signal pulse width | 30 ms 100 ms under load
4884 | RE22R1QMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
4885 | RE22R1QMU | Complementary | Recovery time | 120 ms on de-energisation
4886 | RE22R1QMU | Complementary | immunity to microbreaks | 10 ms
4887 | RE22R1QMU | Complementary | power consumption in VA | 50 VA at 240 V AC
4888 | RE22R1QMU | Complementary | power consumption in W | 0.7 W at 24 V DC
4889 | RE22R1QMU | Complementary | breaking capacity | 2000 VA
4890 | RE22R1QMU | Complementary | minimum switching current | 10 mA at 5 V
4891 | RE22R1QMU | Complementary | maximum switching current | 8 mA
4892 | RE22R1QMU | Complementary | maximum switching voltage | 250 V
4893 | RE22R1QMU | Complementary | electrical durability | 100000 cycles for resistive load, 8 A at 250 V, AC
4894 | RE22R1QMU | Complementary | mechanical durability | 10000000 cycles
4895 | RE22R1QMU | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV conforming to IEC 61812-1
4896 | RE22R1QMU | Complementary | Power on delay | 100 ms
4897 | RE22R1QMU | Complementary | safety reliability data | MTTFd = 182.6 years B10d = 170000
4898 | RE22R1QMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
4899 | RE22R1QMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
4900 | RE22R1QMU | Complementary | status LED | LED green (flashing) for timing in progress LED green (steady) for power ON LED yellow for relay energised
4901 | RE22R1QMU | Complementary | width | 22.5 mm
4902 | RE22R1QMU | Complementary | net weight | 0.086 kg
4903 | RE22R1QMU | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1
4904 | RE22R1QMU | Environment | standards | EN 61000-6-4 EN 61000-6-2 EN 61000-6-3 EN 61000-6-1 IEC 61812-1
4905 | RE22R1QMU | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
4906 | RE22R1QMU | Environment | product certifications | CSA China RoHS EAC RCM CE CCC GL CULus
4907 | RE22R1QMU | Environment | ambient air temperature for operation | -20…60 °C
4908 | RE22R1QMU | Environment | ambient air temperature for storage | -30…60 °C
4909 | RE22R1QMU | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminal block: conforming to IEC 60529 IP40 front face: conforming to IEC 60529
4910 | RE22R1QMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
4911 | RE22R1QMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
4912 | RE22R1QMU | Environment | relative humidity | 93 %, without condensation conforming to IEC 60068-2-30
4913 | RE22R1QMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Conducted and radiated emissions class B conforming to EN 55022
4914 | RE22R1QMU | Offer Sustainability | Sustainable offer status | Green Premium product
4915 | RE22R1QMU | Offer Sustainability | REACh Regulation | REACh Declaration
4916 | RE22R1QMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
4917 | RE22R1QMU | Offer Sustainability | Mercury free | Yes
4918 | RE22R1QMU | Offer Sustainability | RoHS exemption information | Yes
4919 | RE22R1QMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
4920 | RE22R1QMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
4921 | RE22R1QMU | Offer Sustainability | Circularity Profile | End of Life Information
4922 | RE22R1QMQ | Main | range of product | Zelio Time
4923 | RE22R1QMQ | Main | product or component type | Modular timing relay
4924 | RE22R1QMQ | Main | discrete output type | Relay
4925 | RE22R1QMQ | Main | device short name | RE22
4926 | RE22R1QMQ | Main | nominal output current | 8 A
4927 | RE22R1QMQ | Complementary | contacts type and composition | 1 C/O timed contact
4928 | RE22R1QMQ | Complementary | time delay type | Q
4929 | RE22R1QMQ | Complementary | time delay range | 1...10 h 10...100 h 6...60 s 1...10 min 0.1...1 s 1...10 s 6...60 min
4930 | RE22R1QMQ | Complementary | control type | Rotary knob front panel
4931 | RE22R1QMQ | Complementary | [Us] rated supply voltage | 380...440 V AC 230...240 V AC
4932 | RE22R1QMQ | Complementary | voltage range | 0.85...1.1 Us
4933 | RE22R1QMQ | Complementary | supply frequency | 50...60 Hz +/- 5 %
4934 | RE22R1QMQ | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² with cable end Screw terminals, 2 x 2.5 mm² without cable end
4935 | RE22R1QMQ | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
4936 | RE22R1QMQ | Complementary | housing material | Self-extinguishing
4937 | RE22R1QMQ | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
4938 | RE22R1QMQ | Complementary | temperature drift | +/- 0.05 %/°C
4939 | RE22R1QMQ | Complementary | voltage drift | +/- 0.2 %/V
4940 | RE22R1QMQ | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
4941 | RE22R1QMQ | Complementary | Control signal pulse width | 30 ms 100 ms under load
4942 | RE22R1QMQ | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
4943 | RE22R1QMQ | Complementary | Recovery time | 120 ms on de-energisation
4944 | RE22R1QMQ | Complementary | immunity to microbreaks | 10 ms
4945 | RE22R1QMQ | Complementary | power consumption in VA | 8 VA at 230...240 V 17 VA at 380...440 V
4946 | RE22R1QMQ | Complementary | breaking capacity | 2000 VA
4947 | RE22R1QMQ | Complementary | minimum switching current | 10 mA at 5 V
4948 | RE22R1QMQ | Complementary | maximum switching current | 8 mA
4949 | RE22R1QMQ | Complementary | maximum switching voltage | 250 V
4950 | RE22R1QMQ | Complementary | electrical durability | 100000 cycles for resistive load, 8 A at 250 V, AC
4951 | RE22R1QMQ | Complementary | mechanical durability | 10000000 cycles
4952 | RE22R1QMQ | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV conforming to IEC 61812-1
4953 | RE22R1QMQ | Complementary | Power on delay | 100 ms
4954 | RE22R1QMQ | Complementary | safety reliability data | B10d = 260000 MTTFd = 273.9 years
4955 | RE22R1QMQ | Complementary | mounting position | Any position in relation to normal vertical mounting plane
4956 | RE22R1QMQ | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
4957 | RE22R1QMQ | Complementary | status LED | LED green (flashing) for timing in progress LED green (steady) for power ON LED yellow for relay energised
4958 | RE22R1QMQ | Complementary | width | 22.5 mm
4959 | RE22R1QMQ | Complementary | net weight | 0.093 kg
4960 | RE22R1QMQ | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1
4961 | RE22R1QMQ | Environment | standards | EN 61000-6-4 IEC 61812-1 EN 61000-6-1 EN 61000-6-3 EN 61000-6-2
4962 | RE22R1QMQ | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive
4963 | RE22R1QMQ | Environment | product certifications | CULus RCM CSA China RoHS EAC GL CCC CE
4964 | RE22R1QMQ | Environment | ambient air temperature for operation | -20…60 °C
4965 | RE22R1QMQ | Environment | ambient air temperature for storage | -30…60 °C
4966 | RE22R1QMQ | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminal block: conforming to IEC 60529 IP40 front face: conforming to IEC 60529
4967 | RE22R1QMQ | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
4968 | RE22R1QMQ | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
4969 | RE22R1QMQ | Environment | relative humidity | 93 %, without condensation conforming to IEC 60068-2-30
4970 | RE22R1QMQ | Environment | electromagnetic compatibility | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Conducted and radiated emissions class B conforming to EN 55022
4971 | RE22R1QMQ | Offer Sustainability | Sustainable offer status | Green Premium product
4972 | RE22R1QMQ | Offer Sustainability | REACh Regulation | REACh Declaration
4973 | RE22R1QMQ | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
4974 | RE22R1QMQ | Offer Sustainability | Mercury free | Yes
4975 | RE22R1QMQ | Offer Sustainability | RoHS exemption information | Yes
4976 | RE22R1QMQ | Offer Sustainability | China RoHS Regulation | China RoHS declaration
4977 | RE22R1QMQ | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
4978 | RE22R1QMQ | Offer Sustainability | Circularity Profile | End of Life Information
4979 | RE22R2AMU | Main | range of product | Zelio Time
4980 | RE22R2AMU | Main | product or component type | Modular timing relay
4981 | RE22R2AMU | Main | discrete output type | Relay
4982 | RE22R2AMU | Main | device short name | RE22
4983 | RE22R2AMU | Main | nominal output current | 8 A
4984 | RE22R2AMU | Complementary | contacts type and composition | 2 C/O timed contact
4985 | RE22R2AMU | Complementary | time delay type | At A
4986 | RE22R2AMU | Complementary | time delay range | 1...10 min 10...100 h 1...10 s 0.1...1 s 6...60 s 6...60 min 1...10 h
4987 | RE22R2AMU | Complementary | control type | Rotary knob front panel
4988 | RE22R2AMU | Complementary | [Us] rated supply voltage | 24...240 V AC 24 V DC
4989 | RE22R2AMU | Complementary | voltage range | 0.85...1.1 Us
4990 | RE22R2AMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
4991 | RE22R2AMU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² with cable end Screw terminals, 2 x 2.5 mm² without cable end
4992 | RE22R2AMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
4993 | RE22R2AMU | Complementary | housing material | Self-extinguishing
4994 | RE22R2AMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
4995 | RE22R2AMU | Complementary | temperature drift | +/- 0.05 %/°C
4996 | RE22R2AMU | Complementary | voltage drift | +/- 0.2 %/V
4997 | RE22R2AMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
4998 | RE22R2AMU | Complementary | Control signal pulse width | 30 ms 100 ms under load
4999 | RE22R2AMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5000 | RE22R2AMU | Complementary | Recovery time | 120 ms on de-energisation
5001 | RE22R2AMU | Complementary | immunity to microbreaks | 10 ms
5002 | RE22R2AMU | Complementary | power consumption in VA | 50 VA at 240 V AC
5003 | RE22R2AMU | Complementary | power consumption in W | 0.7 W at 24 V DC
5004 | RE22R2AMU | Complementary | breaking capacity | 2000 VA
5005 | RE22R2AMU | Complementary | minimum switching current | 10 mA at 5 V
5006 | RE22R2AMU | Complementary | maximum switching current | 8 mA
5007 | RE22R2AMU | Complementary | maximum switching voltage | 250 V
5008 | RE22R2AMU | Complementary | electrical durability | 100000 cycles for resistive load, 8 A at 250 V, AC
5009 | RE22R2AMU | Complementary | mechanical durability | 10000000 cycles
5010 | RE22R2AMU | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV conforming to IEC 61812-1
5011 | RE22R2AMU | Complementary | Power on delay | 100 ms
5012 | RE22R2AMU | Complementary | safety reliability data | MTTFd = 182.6 years B10d = 170000
5013 | RE22R2AMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
5014 | RE22R2AMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5015 | RE22R2AMU | Complementary | status LED | LED green (flashing) for timing in progress LED green (steady) for power ON LED yellow for relay energised
5016 | RE22R2AMU | Complementary | width | 22.5 mm
5017 | RE22R2AMU | Complementary | net weight | 0.09 kg
5018 | RE22R2AMU | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1
5019 | RE22R2AMU | Environment | standards | EN 61000-6-3 EN 61000-6-4 EN 61000-6-2 IEC 61812-1 EN 61000-6-1
5020 | RE22R2AMU | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive
5021 | RE22R2AMU | Environment | product certifications | CULus CE EAC CSA RCM CCC China RoHS GL
5022 | RE22R2AMU | Environment | ambient air temperature for operation | -20…60 °C
5023 | RE22R2AMU | Environment | ambient air temperature for storage | -30…60 °C
5024 | RE22R2AMU | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminal block: conforming to IEC 60529 IP40 front face: conforming to IEC 60529
5025 | RE22R2AMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
5026 | RE22R2AMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
5027 | RE22R2AMU | Environment | relative humidity | 93 %, without condensation conforming to IEC 60068-2-30
5028 | RE22R2AMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Conducted and radiated emissions class B conforming to EN 55022
5029 | RE22R2AMU | Offer Sustainability | Sustainable offer status | Green Premium product
5030 | RE22R2AMU | Offer Sustainability | REACh Regulation | REACh Declaration
5031 | RE22R2AMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
5032 | RE22R2AMU | Offer Sustainability | Mercury free | Yes
5033 | RE22R2AMU | Offer Sustainability | RoHS exemption information | Yes
5034 | RE22R2AMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
5035 | RE22R2AMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
5036 | RE22R2AMU | Offer Sustainability | Circularity Profile | End of Life Information
5037 | RE22R2MJU | Main | range of product | Zelio Time
5038 | RE22R2MJU | Main | product or component type | Modular timing relay
5039 | RE22R2MJU | Main | discrete output type | Relay
5040 | RE22R2MJU | Main | device short name | RE22
5041 | RE22R2MJU | Main | nominal output current | 8 A
5042 | RE22R2MJU | Complementary | contacts type and composition | 1 C/O timed contact 1 C/O timed or instantaneous contact
5043 | RE22R2MJU | Complementary | time delay type | B C Di Ht Bw Ac H At A D
5044 | RE22R2MJU | Complementary | time delay range | 1...10 min 6...60 min 0.1...1 s 6...60 s 1...10 s 1...10 h 10...100 h
5045 | RE22R2MJU | Complementary | control type | Rotary knob front panel
5046 | RE22R2MJU | Complementary | [Us] rated supply voltage | 12 V AC/DC
5047 | RE22R2MJU | Complementary | voltage range | 0.9...1.2 Us
5048 | RE22R2MJU | Complementary | supply frequency | 50...60 Hz +/- 5 %
5049 | RE22R2MJU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² with cable end Screw terminals, 2 x 2.5 mm² without cable end
5050 | RE22R2MJU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
5051 | RE22R2MJU | Complementary | housing material | Self-extinguishing
5052 | RE22R2MJU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
5053 | RE22R2MJU | Complementary | temperature drift | +/- 0.05 %/°C
5054 | RE22R2MJU | Complementary | voltage drift | +/- 0.2 %/V
5055 | RE22R2MJU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
5056 | RE22R2MJU | Complementary | Control signal pulse width | 30 ms 100 ms under load
5057 | RE22R2MJU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5058 | RE22R2MJU | Complementary | Recovery time | 120 ms on de-energisation
5059 | RE22R2MJU | Complementary | immunity to microbreaks | 10 ms
5060 | RE22R2MJU | Complementary | power consumption in VA | 1.2 VA at 12 V AC
5061 | RE22R2MJU | Complementary | power consumption in W | 0.5 W at 12 V DC
5062 | RE22R2MJU | Complementary | breaking capacity | 2000 VA
5063 | RE22R2MJU | Complementary | minimum switching current | 10 mA at 5 V
5064 | RE22R2MJU | Complementary | maximum switching current | 8 mA
5065 | RE22R2MJU | Complementary | maximum switching voltage | 250 V
5066 | RE22R2MJU | Complementary | electrical durability | 100000 cycles for resistive load, 8 A at 250 V, AC
5067 | RE22R2MJU | Complementary | mechanical durability | 10000000 cycles
5068 | RE22R2MJU | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV conforming to IEC 61812-1
5069 | RE22R2MJU | Complementary | Power on delay | 100 ms
5070 | RE22R2MJU | Complementary | safety reliability data | B10d = 190000 MTTFd = 205.4 years
5071 | RE22R2MJU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
5072 | RE22R2MJU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5073 | RE22R2MJU | Complementary | status LED | LED green (flashing) for timing in progress LED green (steady) for power ON LED yellow for relay energised
5074 | RE22R2MJU | Complementary | width | 22.5 mm
5075 | RE22R2MJU | Complementary | net weight | 0.09 kg
5076 | RE22R2MJU | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1
5077 | RE22R2MJU | Environment | standards | EN 61000-6-1 IEC 61812-1 EN 61000-6-4 EN 61000-6-3 EN 61000-6-2
5078 | RE22R2MJU | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
5079 | RE22R2MJU | Environment | product certifications | CSA CULus China RoHS CE EAC GL CCC RCM
5080 | RE22R2MJU | Environment | ambient air temperature for operation | -20…60 °C
5081 | RE22R2MJU | Environment | ambient air temperature for storage | -30…60 °C
5082 | RE22R2MJU | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminal block: conforming to IEC 60529 IP40 front face: conforming to IEC 60529
5083 | RE22R2MJU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
5084 | RE22R2MJU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
5085 | RE22R2MJU | Environment | relative humidity | 93 %, without condensation conforming to IEC 60068-2-30
5086 | RE22R2MJU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Conducted and radiated emissions class B conforming to EN 55022
5087 | RE22R2MJU | Offer Sustainability | Sustainable offer status | Green Premium product
5088 | RE22R2MJU | Offer Sustainability | REACh Regulation | REACh Declaration
5089 | RE22R2MJU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
5090 | RE22R2MJU | Offer Sustainability | Mercury free | Yes
5091 | RE22R2MJU | Offer Sustainability | RoHS exemption information | Yes
5092 | RE22R2MJU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
5093 | RE22R2MJU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
5094 | RE22R2MJU | Offer Sustainability | Circularity Profile | End of Life Information
5095 | RE22R2MMW | Main | range of product | Zelio Time
5096 | RE22R2MMW | Main | product or component type | Modular timing relay
5097 | RE22R2MMW | Main | discrete output type | Relay
5098 | RE22R2MMW | Main | device short name | RE22
5099 | RE22R2MMW | Main | nominal output current | 8 A
5100 | RE22R2MMW | Complementary | contacts type and composition | 1 C/O timed contact 1 C/O timed or instantaneous contact
5101 | RE22R2MMW | Complementary | time delay type | C Di D B At H Bw Ac A
5102 | RE22R2MMW | Complementary | time delay range | 0.1...1 s 6...60 s 1...10 h 1...10 min 1...10 s 10...100 h 6...60 min
5103 | RE22R2MMW | Complementary | control type | Rotary knob front panel
5104 | RE22R2MMW | Complementary | [Us] rated supply voltage | 12...240 V AC/DC
5105 | RE22R2MMW | Complementary | voltage range | 0.85...1.1 Us
5106 | RE22R2MMW | Complementary | supply frequency | 50...60 Hz +/- 5 %
5107 | RE22R2MMW | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² with cable end Screw terminals, 2 x 2.5 mm² without cable end
5108 | RE22R2MMW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
5109 | RE22R2MMW | Complementary | housing material | Self-extinguishing
5110 | RE22R2MMW | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
5111 | RE22R2MMW | Complementary | temperature drift | +/- 0.05 %/°C
5112 | RE22R2MMW | Complementary | voltage drift | +/- 0.2 %/V
5113 | RE22R2MMW | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
5114 | RE22R2MMW | Complementary | Control signal pulse width | 30 ms 100 ms under load
5115 | RE22R2MMW | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5116 | RE22R2MMW | Complementary | Recovery time | 120 ms on de-energisation
5117 | RE22R2MMW | Complementary | immunity to microbreaks | 10 ms
5118 | RE22R2MMW | Complementary | power consumption in VA | 3 VA at 240 V AC
5119 | RE22R2MMW | Complementary | power consumption in W | 1.5 W at 240 V DC
5120 | RE22R2MMW | Complementary | breaking capacity | 2000 VA
5121 | RE22R2MMW | Complementary | minimum switching current | 10 mA at 5 V
5122 | RE22R2MMW | Complementary | maximum switching current | 8 mA
5123 | RE22R2MMW | Complementary | maximum switching voltage | 250 V
5124 | RE22R2MMW | Complementary | electrical durability | 100000 cycles for resistive load, 8 A at 250 V, AC
5125 | RE22R2MMW | Complementary | mechanical durability | 10000000 cycles
5126 | RE22R2MMW | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV conforming to IEC 61812-1
5127 | RE22R2MMW | Complementary | Power on delay | 100 ms
5128 | RE22R2MMW | Complementary | safety reliability data | B10d = 230000 MTTFd = 251.1 years
5129 | RE22R2MMW | Complementary | mounting position | Any position in relation to normal vertical mounting plane
5130 | RE22R2MMW | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5131 | RE22R2MMW | Complementary | status LED | LED green (flashing) for timing in progress LED green (steady) for power ON LED yellow for relay energised
5132 | RE22R2MMW | Complementary | width | 22.5 mm
5133 | RE22R2MMW | Complementary | net weight | 0.093 kg
5134 | RE22R2MMW | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1
5135 | RE22R2MMW | Environment | standards | IEC 61812-1 EN 61000-6-2 EN 61000-6-1 EN 61000-6-4 EN 61000-6-3
5136 | RE22R2MMW | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive
5137 | RE22R2MMW | Environment | product certifications | CSA CE CULus GL RCM CCC China RoHS EAC
5138 | RE22R2MMW | Environment | ambient air temperature for operation | -20…60 °C
5139 | RE22R2MMW | Environment | ambient air temperature for storage | -30…60 °C
5140 | RE22R2MMW | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminal block: conforming to IEC 60529 IP40 front face: conforming to IEC 60529
5141 | RE22R2MMW | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
5142 | RE22R2MMW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
5143 | RE22R2MMW | Environment | relative humidity | 93 %, without condensation conforming to IEC 60068-2-30
5144 | RE22R2MMW | Environment | electromagnetic compatibility | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Conducted and radiated emissions class B conforming to EN 55022
5145 | RE22R2MMW | Offer Sustainability | Sustainable offer status | Green Premium product
5146 | RE22R2MMW | Offer Sustainability | REACh Regulation | REACh Declaration
5147 | RE22R2MMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
5148 | RE22R2MMW | Offer Sustainability | Mercury free | Yes
5149 | RE22R2MMW | Offer Sustainability | RoHS exemption information | Yes
5150 | RE22R2MMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
5151 | RE22R2MMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
5152 | RE22R2MMW | Offer Sustainability | Circularity Profile | End of Life Information
5153 | RE22R2MMU | Main | range of product | Zelio Time
5154 | RE22R2MMU | Main | product or component type | Modular timing relay
5155 | RE22R2MMU | Main | discrete output type | Relay
5156 | RE22R2MMU | Main | device short name | RE22
5157 | RE22R2MMU | Main | nominal output current | 8 A
5158 | RE22R2MMU | Complementary | contacts type and composition | 1 C/O timed contact 1 C/O timed or instantaneous contact
5159 | RE22R2MMU | Complementary | time delay type | Ht At Bw C Di B Ac H A D
5160 | RE22R2MMU | Complementary | time delay range | 10...100 h 6...60 s 0.1...1 s 1...10 h 1...10 s 1...10 min 6...60 min
5161 | RE22R2MMU | Complementary | control type | Rotary knob front panel
5162 | RE22R2MMU | Complementary | [Us] rated supply voltage | 24...240 V AC 24 V DC
5163 | RE22R2MMU | Complementary | voltage range | 0.85...1.1 Us
5164 | RE22R2MMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
5165 | RE22R2MMU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² with cable end Screw terminals, 2 x 2.5 mm² without cable end
5166 | RE22R2MMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
5167 | RE22R2MMU | Complementary | housing material | Self-extinguishing
5168 | RE22R2MMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
5169 | RE22R2MMU | Complementary | temperature drift | +/- 0.05 %/°C
5170 | RE22R2MMU | Complementary | voltage drift | +/- 0.2 %/V
5171 | RE22R2MMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
5172 | RE22R2MMU | Complementary | Control signal pulse width | 30 ms 100 ms under load
5173 | RE22R2MMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5174 | RE22R2MMU | Complementary | Recovery time | 120 ms on de-energisation
5175 | RE22R2MMU | Complementary | immunity to microbreaks | 10 ms
5176 | RE22R2MMU | Complementary | power consumption in VA | 50 VA at 240 V AC
5177 | RE22R2MMU | Complementary | power consumption in W | 0.7 W at 24 V DC
5178 | RE22R2MMU | Complementary | breaking capacity | 2000 VA
5179 | RE22R2MMU | Complementary | minimum switching current | 10 mA at 5 V
5180 | RE22R2MMU | Complementary | maximum switching current | 8 mA
5181 | RE22R2MMU | Complementary | maximum switching voltage | 250 V
5182 | RE22R2MMU | Complementary | electrical durability | 100000 cycles for resistive load, 8 A at 250 V, AC
5183 | RE22R2MMU | Complementary | mechanical durability | 10000000 cycles
5184 | RE22R2MMU | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV conforming to IEC 61812-1
5185 | RE22R2MMU | Complementary | Power on delay | 100 ms
5186 | RE22R2MMU | Complementary | safety reliability data | MTTFd = 182.6 years B10d = 170000
5187 | RE22R2MMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
5188 | RE22R2MMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5189 | RE22R2MMU | Complementary | status LED | LED green (flashing) for timing in progress LED green (steady) for power ON LED yellow for relay energised
5190 | RE22R2MMU | Complementary | width | 22.5 mm
5191 | RE22R2MMU | Complementary | net weight | 0.09 kg
5192 | RE22R2MMU | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1
5193 | RE22R2MMU | Environment | standards | IEC 61812-1 EN 61000-6-1 EN 61000-6-2 EN 61000-6-3 EN 61000-6-4
5194 | RE22R2MMU | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive
5195 | RE22R2MMU | Environment | product certifications | CULus CSA CE China RoHS CCC RCM GL EAC
5196 | RE22R2MMU | Environment | ambient air temperature for operation | -20…60 °C
5197 | RE22R2MMU | Environment | ambient air temperature for storage | -30…60 °C
5198 | RE22R2MMU | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminal block: conforming to IEC 60529 IP40 front face: conforming to IEC 60529
5199 | RE22R2MMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
5200 | RE22R2MMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
5201 | RE22R2MMU | Environment | relative humidity | 93 %, without condensation conforming to IEC 60068-2-30
5202 | RE22R2MMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Conducted and radiated emissions class B conforming to EN 55022
5203 | RE22R2MMU | Offer Sustainability | Sustainable offer status | Green Premium product
5204 | RE22R2MMU | Offer Sustainability | REACh Regulation | REACh Declaration
5205 | RE22R2MMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
5206 | RE22R2MMU | Offer Sustainability | Mercury free | Yes
5207 | RE22R2MMU | Offer Sustainability | RoHS exemption information | Yes
5208 | RE22R2MMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
5209 | RE22R2MMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
5210 | RE22R2MMU | Offer Sustainability | Circularity Profile | End of Life Information
5211 | RE22R2MXMU | Main | range of product | Zelio Time
5212 | RE22R2MXMU | Main | product or component type | Modular timing relay
5213 | RE22R2MXMU | Main | discrete output type | Relay
5214 | RE22R2MXMU | Main | device short name | RE22
5215 | RE22R2MXMU | Main | nominal output current | 8 A
5216 | RE22R2MXMU | Complementary | contacts type and composition | 1 C/O timed contact 1 C/O timed or instantaneous contact
5217 | RE22R2MXMU | Complementary | time delay type | Pt O P A Tl Ah N Tt W
5218 | RE22R2MXMU | Complementary | time delay range | 0.1...1 s 1...10 h 1...10 s 6...60 min 10...100 h 6...60 s 1...10 min
5219 | RE22R2MXMU | Complementary | control type | Rotary knob front panel
5220 | RE22R2MXMU | Complementary | [Us] rated supply voltage | 24...240 V AC 24 V DC
5221 | RE22R2MXMU | Complementary | voltage range | 0.85...1.1 Us
5222 | RE22R2MXMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
5223 | RE22R2MXMU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² with cable end Screw terminals, 2 x 2.5 mm² without cable end
5224 | RE22R2MXMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
5225 | RE22R2MXMU | Complementary | housing material | Self-extinguishing
5226 | RE22R2MXMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
5227 | RE22R2MXMU | Complementary | temperature drift | +/- 0.05 %/°C
5228 | RE22R2MXMU | Complementary | voltage drift | +/- 0.2 %/V
5229 | RE22R2MXMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
5230 | RE22R2MXMU | Complementary | Control signal pulse width | 30 ms 100 ms under load
5231 | RE22R2MXMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5232 | RE22R2MXMU | Complementary | Recovery time | 120 ms on de-energisation
5233 | RE22R2MXMU | Complementary | immunity to microbreaks | 10 ms
5234 | RE22R2MXMU | Complementary | power consumption in VA | 50 VA at 240 V AC
5235 | RE22R2MXMU | Complementary | power consumption in W | 0.7 W at 24 V DC
5236 | RE22R2MXMU | Complementary | breaking capacity | 2000 VA
5237 | RE22R2MXMU | Complementary | minimum switching current | 10 mA at 5 V
5238 | RE22R2MXMU | Complementary | maximum switching current | 8 mA
5239 | RE22R2MXMU | Complementary | maximum switching voltage | 250 V
5240 | RE22R2MXMU | Complementary | electrical durability | 100000 cycles for resistive load, 8 A at 250 V, AC
5241 | RE22R2MXMU | Complementary | mechanical durability | 10000000 cycles
5242 | RE22R2MXMU | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV conforming to IEC 61812-1
5243 | RE22R2MXMU | Complementary | Power on delay | 100 ms
5244 | RE22R2MXMU | Complementary | safety reliability data | B10d = 170000 MTTFd = 182.6 years
5245 | RE22R2MXMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
5246 | RE22R2MXMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5247 | RE22R2MXMU | Complementary | status LED | LED green (flashing) for timing in progress LED green (steady) for power ON LED yellow for relay energised
5248 | RE22R2MXMU | Complementary | width | 22.5 mm
5249 | RE22R2MXMU | Complementary | net weight | 0.09 kg
5250 | RE22R2MXMU | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1
5251 | RE22R2MXMU | Environment | standards | IEC 61812-1 EN 61000-6-1 EN 61000-6-3 EN 61000-6-4 EN 61000-6-2
5252 | RE22R2MXMU | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
5253 | RE22R2MXMU | Environment | product certifications | China RoHS CSA CCC GL CULus EAC CE RCM
5254 | RE22R2MXMU | Environment | ambient air temperature for operation | -20…60 °C
5255 | RE22R2MXMU | Environment | ambient air temperature for storage | -30…60 °C
5256 | RE22R2MXMU | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminal block: conforming to IEC 60529
5257 | RE22R2MXMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
5258 | RE22R2MXMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
5259 | RE22R2MXMU | Environment | relative humidity | 93 %, without condensation conforming to IEC 60068-2-30
5260 | RE22R2MXMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
5261 | RE22R2MXMU | Offer Sustainability | Sustainable offer status | Green Premium product
5262 | RE22R2MXMU | Offer Sustainability | REACh Regulation | REACh Declaration
5263 | RE22R2MXMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
5264 | RE22R2MXMU | Offer Sustainability | Mercury free | Yes
5265 | RE22R2MXMU | Offer Sustainability | RoHS exemption information | Yes
5266 | RE22R2MXMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
5267 | RE22R2MXMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
5268 | RE22R2MXMU | Offer Sustainability | Circularity Profile | End of Life Information
5269 | RE22R1ACMR | Main | range of product | Zelio Time
5270 | RE22R1ACMR | Main | product or component type | Modular timing relay
5271 | RE22R1ACMR | Main | discrete output type | Relay
5272 | RE22R1ACMR | Main | device short name | RE22
5273 | RE22R1ACMR | Main | nominal output current | 8 A
5274 | RE22R1ACMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
5275 | RE22R1ACMR | Complementary | time delay type | Ac Act
5276 | RE22R1ACMR | Complementary | time delay range | 3...30 min 1...10 s 30...300 s 10...100 s 3...30 s 30...300 min 30...300 h 0.3...3 s 0.05...1 s 3...30 h
5277 | RE22R1ACMR | Complementary | control type | Rotary knob Diagnostic button Potentiometer external
5278 | RE22R1ACMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
5279 | RE22R1ACMR | Complementary | Release input voltage | <= 2.4 V
5280 | RE22R1ACMR | Complementary | voltage range | 0.85...1.1 Us
5281 | RE22R1ACMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
5282 | RE22R1ACMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
5283 | RE22R1ACMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
5284 | RE22R1ACMR | Complementary | housing material | Self-extinguishing
5285 | RE22R1ACMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
5286 | RE22R1ACMR | Complementary | temperature drift | +/- 0.05 %/°C
5287 | RE22R1ACMR | Complementary | voltage drift | +/- 0.2 %/V
5288 | RE22R1ACMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
5289 | RE22R1ACMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
5290 | RE22R1ACMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5291 | RE22R1ACMR | Complementary | Recovery time | 120 ms on de-energisation
5292 | RE22R1ACMR | Complementary | immunity to microbreaks | 10 ms
5293 | RE22R1ACMR | Complementary | power consumption in VA | 3 VA at 240 V AC
5294 | RE22R1ACMR | Complementary | power consumption in W | 1.5 W at 240 V DC
5295 | RE22R1ACMR | Complementary | switching capacity in VA | 2000 VA
5296 | RE22R1ACMR | Complementary | minimum switching current | 10 mA at 5 V DC
5297 | RE22R1ACMR | Complementary | maximum switching current | 8 A
5298 | RE22R1ACMR | Complementary | maximum switching voltage | 250 V AC
5299 | RE22R1ACMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
5300 | RE22R1ACMR | Complementary | mechanical durability | 10000000 cycles
5301 | RE22R1ACMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
5302 | RE22R1ACMR | Complementary | Power on delay | 100 ms
5303 | RE22R1ACMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
5304 | RE22R1ACMR | Complementary | overvoltage category | III conforming to IEC 60664-1
5305 | RE22R1ACMR | Complementary | safety reliability data | B10d = 190000 MTTFd = 205.4 years
5306 | RE22R1ACMR | Complementary | mounting position | Any position
5307 | RE22R1ACMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5308 | RE22R1ACMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
5309 | RE22R1ACMR | Complementary | width | 22.5 mm
5310 | RE22R1ACMR | Complementary | net weight | 0.1 kg
5311 | RE22R1ACMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
5312 | RE22R1ACMR | Environment | standards | IEC 61812-1 UL 508
5313 | RE22R1ACMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
5314 | RE22R1ACMR | Environment | product certifications | CE CCC GL UL China RoHS CSA EAC RCM
5315 | RE22R1ACMR | Environment | ambient air temperature for operation | -20…60 °C
5316 | RE22R1ACMR | Environment | ambient air temperature for storage | -40…70 °C
5317 | RE22R1ACMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529
5318 | RE22R1ACMR | Environment | pollution degree | 3 conforming to IEC 60664-1
5319 | RE22R1ACMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
5320 | RE22R1ACMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
5321 | RE22R1ACMR | Environment | relative humidity | 95 % at 25…55 °C
5322 | RE22R1ACMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
5323 | RE22R1ACMR | Offer Sustainability | Sustainable offer status | Green Premium product
5324 | RE22R1ACMR | Offer Sustainability | REACh Regulation | REACh Declaration
5325 | RE22R1ACMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
5326 | RE22R1ACMR | Offer Sustainability | Mercury free | Yes
5327 | RE22R1ACMR | Offer Sustainability | RoHS exemption information | Yes
5328 | RE22R1ACMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
5329 | RE22R1ACMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
5330 | RE22R1ACMR | Offer Sustainability | Circularity Profile | End of Life Information
5331 | RE22R1AKMR | Main | range of product | Zelio Time
5332 | RE22R1AKMR | Main | product or component type | Modular timing relay
5333 | RE22R1AKMR | Main | discrete output type | Relay
5334 | RE22R1AKMR | Main | device short name | RE22
5335 | RE22R1AKMR | Main | nominal output current | 8 A
5336 | RE22R1AKMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
5337 | RE22R1AKMR | Complementary | time delay type | Ak Akt
5338 | RE22R1AKMR | Complementary | time delay range | 30...300 h 3...30 min 30...300 s 0.05...1 s 30...300 min 10...100 s 0.3...3 s 3...30 h 1...10 s
5339 | RE22R1AKMR | Complementary | control type | Rotary knob Diagnostic button Potentiometer external
5340 | RE22R1AKMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
5341 | RE22R1AKMR | Complementary | Release input voltage | <= 2.4 V
5342 | RE22R1AKMR | Complementary | voltage range | 0.85...1.1 Us
5343 | RE22R1AKMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
5344 | RE22R1AKMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
5345 | RE22R1AKMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
5346 | RE22R1AKMR | Complementary | housing material | Self-extinguishing
5347 | RE22R1AKMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
5348 | RE22R1AKMR | Complementary | temperature drift | +/- 0.05 %/°C
5349 | RE22R1AKMR | Complementary | voltage drift | +/- 0.2 %/V
5350 | RE22R1AKMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
5351 | RE22R1AKMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
5352 | RE22R1AKMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5353 | RE22R1AKMR | Complementary | Recovery time | 120 ms on de-energisation
5354 | RE22R1AKMR | Complementary | immunity to microbreaks | 10 ms
5355 | RE22R1AKMR | Complementary | power consumption in VA | 3 VA at 240 V AC
5356 | RE22R1AKMR | Complementary | power consumption in W | 1.5 W at 240 V DC
5357 | RE22R1AKMR | Complementary | switching capacity in VA | 2000 VA
5358 | RE22R1AKMR | Complementary | minimum switching current | 10 mA at 5 V DC
5359 | RE22R1AKMR | Complementary | maximum switching current | 8 A
5360 | RE22R1AKMR | Complementary | maximum switching voltage | 250 V AC
5361 | RE22R1AKMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
5362 | RE22R1AKMR | Complementary | mechanical durability | 10000000 cycles
5363 | RE22R1AKMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
5364 | RE22R1AKMR | Complementary | Power on delay | 100 ms
5365 | RE22R1AKMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
5366 | RE22R1AKMR | Complementary | overvoltage category | III conforming to IEC 60664-1
5367 | RE22R1AKMR | Complementary | safety reliability data | B10d = 180000 MTTFd = 194 years
5368 | RE22R1AKMR | Complementary | mounting position | Any position
5369 | RE22R1AKMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5370 | RE22R1AKMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
5371 | RE22R1AKMR | Complementary | width | 22.5 mm
5372 | RE22R1AKMR | Complementary | net weight | 0.1 kg
5373 | RE22R1AKMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
5374 | RE22R1AKMR | Environment | standards | UL 508 IEC 61812-1
5375 | RE22R1AKMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
5376 | RE22R1AKMR | Environment | product certifications | China RoHS EAC CSA UL RCM CCC GL CE
5377 | RE22R1AKMR | Environment | ambient air temperature for operation | -20…60 °C
5378 | RE22R1AKMR | Environment | ambient air temperature for storage | -40…70 °C
5379 | RE22R1AKMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529
5380 | RE22R1AKMR | Environment | pollution degree | 3 conforming to IEC 60664-1
5381 | RE22R1AKMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
5382 | RE22R1AKMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
5383 | RE22R1AKMR | Environment | relative humidity | 95 % at 25…55 °C
5384 | RE22R1AKMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
5385 | RE22R1AKMR | Offer Sustainability | Sustainable offer status | Green Premium product
5386 | RE22R1AKMR | Offer Sustainability | REACh Regulation | REACh Declaration
5387 | RE22R1AKMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
5388 | RE22R1AKMR | Offer Sustainability | Mercury free | Yes
5389 | RE22R1AKMR | Offer Sustainability | RoHS exemption information | Yes
5390 | RE22R1AKMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
5391 | RE22R1AKMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
5392 | RE22R1AKMR | Offer Sustainability | Circularity Profile | End of Life Information
5393 | RE22R1AMR | Main | range of product | Zelio Time
5394 | RE22R1AMR | Main | product or component type | Modular timing relay
5395 | RE22R1AMR | Main | discrete output type | Relay
5396 | RE22R1AMR | Main | device short name | RE22
5397 | RE22R1AMR | Main | nominal output current | 8 A
5398 | RE22R1AMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
5399 | RE22R1AMR | Complementary | time delay type | A Aw
5400 | RE22R1AMR | Complementary | time delay range | 3...30 s 30...300 s 10...100 s 0.05...1 s 1...10 s 30...300 h 30...300 min 0.3...3 s 3...30 h 3...30 min
5401 | RE22R1AMR | Complementary | control type | Rotary knob Diagnostic button
5402 | RE22R1AMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
5403 | RE22R1AMR | Complementary | Release input voltage | <= 2.4 V
5404 | RE22R1AMR | Complementary | voltage range | 0.85...1.1 Us
5405 | RE22R1AMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
5406 | RE22R1AMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
5407 | RE22R1AMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
5408 | RE22R1AMR | Complementary | housing material | Self-extinguishing
5409 | RE22R1AMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
5410 | RE22R1AMR | Complementary | temperature drift | +/- 0.05 %/°C
5411 | RE22R1AMR | Complementary | voltage drift | +/- 0.2 %/V
5412 | RE22R1AMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
5413 | RE22R1AMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
5414 | RE22R1AMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5415 | RE22R1AMR | Complementary | Recovery time | 120 ms on de-energisation
5416 | RE22R1AMR | Complementary | immunity to microbreaks | 10 ms
5417 | RE22R1AMR | Complementary | power consumption in VA | 3 VA at 240 V AC
5418 | RE22R1AMR | Complementary | power consumption in W | 1.5 W at 240 V DC
5419 | RE22R1AMR | Complementary | switching capacity in VA | 2000 VA
5420 | RE22R1AMR | Complementary | minimum switching current | 10 mA at 5 V DC
5421 | RE22R1AMR | Complementary | maximum switching current | 8 A
5422 | RE22R1AMR | Complementary | maximum switching voltage | 250 V AC
5423 | RE22R1AMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
5424 | RE22R1AMR | Complementary | mechanical durability | 10000000 cycles
5425 | RE22R1AMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
5426 | RE22R1AMR | Complementary | Power on delay | 100 ms
5427 | RE22R1AMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
5428 | RE22R1AMR | Complementary | overvoltage category | III conforming to IEC 60664-1
5429 | RE22R1AMR | Complementary | safety reliability data | MTTFd = 308.2 years B10d = 280000
5430 | RE22R1AMR | Complementary | mounting position | Any position
5431 | RE22R1AMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5432 | RE22R1AMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
5433 | RE22R1AMR | Complementary | width | 22.5 mm
5434 | RE22R1AMR | Complementary | net weight | 0.1 kg
5435 | RE22R1AMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
5436 | RE22R1AMR | Environment | standards | UL 508 IEC 61812-1
5437 | RE22R1AMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
5438 | RE22R1AMR | Environment | product certifications | CE UL GL CCC China RoHS EAC RCM CSA
5439 | RE22R1AMR | Environment | ambient air temperature for operation | -20…60 °C
5440 | RE22R1AMR | Environment | ambient air temperature for storage | -40…70 °C
5441 | RE22R1AMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529
5442 | RE22R1AMR | Environment | pollution degree | 3 conforming to IEC 60664-1
5443 | RE22R1AMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
5444 | RE22R1AMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
5445 | RE22R1AMR | Environment | relative humidity | 95 % at 25…55 °C
5446 | RE22R1AMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
5447 | RE22R1AMR | Offer Sustainability | Sustainable offer status | Green Premium product
5448 | RE22R1AMR | Offer Sustainability | REACh Regulation | REACh Declaration
5449 | RE22R1AMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
5450 | RE22R1AMR | Offer Sustainability | Mercury free | Yes
5451 | RE22R1AMR | Offer Sustainability | RoHS exemption information | Yes
5452 | RE22R1AMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
5453 | RE22R1AMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
5454 | RE22R1AMR | Offer Sustainability | Circularity Profile | End of Life Information
5455 | RE22R1CMR | Main | range of product | Zelio Time
5456 | RE22R1CMR | Main | product or component type | Modular timing relay
5457 | RE22R1CMR | Main | discrete output type | Relay
5458 | RE22R1CMR | Main | device short name | RE22
5459 | RE22R1CMR | Main | nominal output current | 8 A
5460 | RE22R1CMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
5461 | RE22R1CMR | Complementary | time delay type | C Ct
5462 | RE22R1CMR | Complementary | time delay range | 10...100 s 3...30 s 0.05...1 s 30...300 s 30...300 h 30...300 min 3...30 min 3...30 h 0.3...3 s 1...10 s
5463 | RE22R1CMR | Complementary | control type | Rotary knob Diagnostic button Potentiometer external
5464 | RE22R1CMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
5465 | RE22R1CMR | Complementary | Release input voltage | <= 2.4 V
5466 | RE22R1CMR | Complementary | voltage range | 0.85...1.1 Us
5467 | RE22R1CMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
5468 | RE22R1CMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
5469 | RE22R1CMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
5470 | RE22R1CMR | Complementary | housing material | Self-extinguishing
5471 | RE22R1CMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
5472 | RE22R1CMR | Complementary | temperature drift | +/- 0.05 %/°C
5473 | RE22R1CMR | Complementary | voltage drift | +/- 0.2 %/V
5474 | RE22R1CMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
5475 | RE22R1CMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
5476 | RE22R1CMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5477 | RE22R1CMR | Complementary | Recovery time | 120 ms on de-energisation
5478 | RE22R1CMR | Complementary | immunity to microbreaks | 10 ms
5479 | RE22R1CMR | Complementary | power consumption in VA | 3 VA at 240 V AC
5480 | RE22R1CMR | Complementary | power consumption in W | 1.5 W at 240 V DC
5481 | RE22R1CMR | Complementary | switching capacity in VA | 2000 VA
5482 | RE22R1CMR | Complementary | minimum switching current | 10 mA at 5 V DC
5483 | RE22R1CMR | Complementary | maximum switching current | 8 A
5484 | RE22R1CMR | Complementary | maximum switching voltage | 250 V AC
5485 | RE22R1CMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
5486 | RE22R1CMR | Complementary | mechanical durability | 10000000 cycles
5487 | RE22R1CMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
5488 | RE22R1CMR | Complementary | Power on delay | 100 ms
5489 | RE22R1CMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
5490 | RE22R1CMR | Complementary | overvoltage category | III conforming to IEC 60664-1
5491 | RE22R1CMR | Complementary | safety reliability data | MTTFd = 205.4 years B10d = 190000
5492 | RE22R1CMR | Complementary | mounting position | Any position
5493 | RE22R1CMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5494 | RE22R1CMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
5495 | RE22R1CMR | Complementary | width | 22.5 mm
5496 | RE22R1CMR | Complementary | net weight | 0.1 kg
5497 | RE22R1CMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
5498 | RE22R1CMR | Environment | standards | UL 508 IEC 61812-1
5499 | RE22R1CMR | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive
5500 | RE22R1CMR | Environment | product certifications | UL CE CCC CSA China RoHS GL RCM EAC
5501 | RE22R1CMR | Environment | ambient air temperature for operation | -20…60 °C
5502 | RE22R1CMR | Environment | ambient air temperature for storage | -40…70 °C
5503 | RE22R1CMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529
5504 | RE22R1CMR | Environment | pollution degree | 3 conforming to IEC 60664-1
5505 | RE22R1CMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
5506 | RE22R1CMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
5507 | RE22R1CMR | Environment | relative humidity | 95 % at 25…55 °C
5508 | RE22R1CMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
5509 | RE22R1CMR | Offer Sustainability | Sustainable offer status | Green Premium product
5510 | RE22R1CMR | Offer Sustainability | REACh Regulation | REACh Declaration
5511 | RE22R1CMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
5512 | RE22R1CMR | Offer Sustainability | Mercury free | Yes
5513 | RE22R1CMR | Offer Sustainability | RoHS exemption information | Yes
5514 | RE22R1CMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
5515 | RE22R1CMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
5516 | RE22R1CMR | Offer Sustainability | Circularity Profile | End of Life Information
5517 | RE22R1CMR | Main | range of product | Zelio Time
5518 | RE22R1CMR | Main | product or component type | Modular timing relay
5519 | RE22R1CMR | Main | discrete output type | Relay
5520 | RE22R1CMR | Main | device short name | RE22
5521 | RE22R1CMR | Main | nominal output current | 8 A
5522 | RE22R1CMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
5523 | RE22R1CMR | Complementary | time delay type | C Ct
5524 | RE22R1CMR | Complementary | time delay range | 10...100 s 3...30 s 0.05...1 s 30...300 s 30...300 h 30...300 min 3...30 min 3...30 h 0.3...3 s 1...10 s
5525 | RE22R1CMR | Complementary | control type | Rotary knob Diagnostic button Potentiometer external
5526 | RE22R1CMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
5527 | RE22R1CMR | Complementary | Release input voltage | <= 2.4 V
5528 | RE22R1CMR | Complementary | voltage range | 0.85...1.1 Us
5529 | RE22R1CMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
5530 | RE22R1CMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
5531 | RE22R1CMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
5532 | RE22R1CMR | Complementary | housing material | Self-extinguishing
5533 | RE22R1CMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
5534 | RE22R1CMR | Complementary | temperature drift | +/- 0.05 %/°C
5535 | RE22R1CMR | Complementary | voltage drift | +/- 0.2 %/V
5536 | RE22R1CMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
5537 | RE22R1CMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
5538 | RE22R1CMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5539 | RE22R1CMR | Complementary | Recovery time | 120 ms on de-energisation
5540 | RE22R1CMR | Complementary | immunity to microbreaks | 10 ms
5541 | RE22R1CMR | Complementary | power consumption in VA | 3 VA at 240 V AC
5542 | RE22R1CMR | Complementary | power consumption in W | 1.5 W at 240 V DC
5543 | RE22R1CMR | Complementary | switching capacity in VA | 2000 VA
5544 | RE22R1CMR | Complementary | minimum switching current | 10 mA at 5 V DC
5545 | RE22R1CMR | Complementary | maximum switching current | 8 A
5546 | RE22R1CMR | Complementary | maximum switching voltage | 250 V AC
5547 | RE22R1CMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
5548 | RE22R1CMR | Complementary | mechanical durability | 10000000 cycles
5549 | RE22R1CMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
5550 | RE22R1CMR | Complementary | Power on delay | 100 ms
5551 | RE22R1CMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
5552 | RE22R1CMR | Complementary | overvoltage category | III conforming to IEC 60664-1
5553 | RE22R1CMR | Complementary | safety reliability data | MTTFd = 205.4 years B10d = 190000
5554 | RE22R1CMR | Complementary | mounting position | Any position
5555 | RE22R1CMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5556 | RE22R1CMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
5557 | RE22R1CMR | Complementary | width | 22.5 mm
5558 | RE22R1CMR | Complementary | net weight | 0.1 kg
5559 | RE22R1CMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
5560 | RE22R1CMR | Environment | standards | UL 508 IEC 61812-1
5561 | RE22R1CMR | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive
5562 | RE22R1CMR | Environment | product certifications | UL CE CCC CSA China RoHS GL RCM EAC
5563 | RE22R1CMR | Environment | ambient air temperature for operation | -20…60 °C
5564 | RE22R1CMR | Environment | ambient air temperature for storage | -40…70 °C
5565 | RE22R1CMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529
5566 | RE22R1CMR | Environment | pollution degree | 3 conforming to IEC 60664-1
5567 | RE22R1CMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
5568 | RE22R1CMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
5569 | RE22R1CMR | Environment | relative humidity | 95 % at 25…55 °C
5570 | RE22R1CMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
5571 | RE22R1CMR | Offer Sustainability | Sustainable offer status | Green Premium product
5572 | RE22R1CMR | Offer Sustainability | REACh Regulation | REACh Declaration
5573 | RE22R1CMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
5574 | RE22R1CMR | Offer Sustainability | Mercury free | Yes
5575 | RE22R1CMR | Offer Sustainability | RoHS exemption information | Yes
5576 | RE22R1CMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
5577 | RE22R1CMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
5578 | RE22R1CMR | Offer Sustainability | Circularity Profile | End of Life Information
5579 | RE22R1DMR | Main | range of product | Zelio Time
5580 | RE22R1DMR | Main | product or component type | Modular timing relay
5581 | RE22R1DMR | Main | discrete output type | Relay
5582 | RE22R1DMR | Main | device short name | RE22
5583 | RE22R1DMR | Main | nominal output current | 8 A
5584 | RE22R1DMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
5585 | RE22R1DMR | Complementary | time delay type | Dw D
5586 | RE22R1DMR | Complementary | time delay range | 0.05...1 s 30...300 h 30...300 min 30...300 s 3...30 min 1...10 s 3...30 s 0.3...3 s 10...100 s 3...30 h
5587 | RE22R1DMR | Complementary | control type | Rotary knob Diagnostic button
5588 | RE22R1DMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
5589 | RE22R1DMR | Complementary | Release input voltage | <= 2.4 V
5590 | RE22R1DMR | Complementary | voltage range | 0.85...1.1 Us
5591 | RE22R1DMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
5592 | RE22R1DMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
5593 | RE22R1DMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
5594 | RE22R1DMR | Complementary | housing material | Self-extinguishing
5595 | RE22R1DMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
5596 | RE22R1DMR | Complementary | temperature drift | +/- 0.05 %/°C
5597 | RE22R1DMR | Complementary | voltage drift | +/- 0.2 %/V
5598 | RE22R1DMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
5599 | RE22R1DMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
5600 | RE22R1DMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5601 | RE22R1DMR | Complementary | Recovery time | 120 ms on de-energisation
5602 | RE22R1DMR | Complementary | immunity to microbreaks | 10 ms
5603 | RE22R1DMR | Complementary | power consumption in VA | 3 VA at 240 V AC
5604 | RE22R1DMR | Complementary | power consumption in W | 1.5 W at 240 V DC
5605 | RE22R1DMR | Complementary | switching capacity in VA | 2000 VA
5606 | RE22R1DMR | Complementary | minimum switching current | 10 mA at 5 V DC
5607 | RE22R1DMR | Complementary | maximum switching current | 8 A
5608 | RE22R1DMR | Complementary | maximum switching voltage | 250 V AC
5609 | RE22R1DMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
5610 | RE22R1DMR | Complementary | mechanical durability | 10000000 cycles
5611 | RE22R1DMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
5612 | RE22R1DMR | Complementary | Power on delay | 100 ms
5613 | RE22R1DMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
5614 | RE22R1DMR | Complementary | overvoltage category | III conforming to IEC 60664-1
5615 | RE22R1DMR | Complementary | safety reliability data | B10d = 280000 MTTFd = 308.2 years
5616 | RE22R1DMR | Complementary | mounting position | Any position
5617 | RE22R1DMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5618 | RE22R1DMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
5619 | RE22R1DMR | Complementary | width | 22.5 mm
5620 | RE22R1DMR | Complementary | net weight | 0.1 kg
5621 | RE22R1DMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
5622 | RE22R1DMR | Environment | standards | UL 508 IEC 61812-1
5623 | RE22R1DMR | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive
5624 | RE22R1DMR | Environment | product certifications | China RoHS GL EAC UL CCC CSA CE RCM
5625 | RE22R1DMR | Environment | ambient air temperature for operation | -20…60 °C
5626 | RE22R1DMR | Environment | ambient air temperature for storage | -40…70 °C
5627 | RE22R1DMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529
5628 | RE22R1DMR | Environment | pollution degree | 3 conforming to IEC 60664-1
5629 | RE22R1DMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
5630 | RE22R1DMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
5631 | RE22R1DMR | Environment | relative humidity | 95 % at 25…55 °C
5632 | RE22R1DMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
5633 | RE22R1DMR | Offer Sustainability | Sustainable offer status | Green Premium product
5634 | RE22R1DMR | Offer Sustainability | REACh Regulation | REACh Declaration
5635 | RE22R1DMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
5636 | RE22R1DMR | Offer Sustainability | Mercury free | Yes
5637 | RE22R1DMR | Offer Sustainability | RoHS exemption information | Yes
5638 | RE22R1DMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
5639 | RE22R1DMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
5640 | RE22R1DMR | Offer Sustainability | Circularity Profile | End of Life Information
5641 | RE22R1HMR | Main | range of product | Zelio Time
5642 | RE22R1HMR | Main | product or component type | Modular timing relay
5643 | RE22R1HMR | Main | discrete output type | Relay
5644 | RE22R1HMR | Main | device short name | RE22
5645 | RE22R1HMR | Main | nominal output current | 8 A
5646 | RE22R1HMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
5647 | RE22R1HMR | Complementary | time delay type | Hw H
5648 | RE22R1HMR | Complementary | time delay range | 3...30 s 0.3...3 s 30...300 s 30...300 h 0.05...1 s 1...10 s 3...30 min 30...300 min 3...30 h 10...100 s
5649 | RE22R1HMR | Complementary | control type | Rotary knob Diagnostic button
5650 | RE22R1HMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
5651 | RE22R1HMR | Complementary | Release input voltage | <= 2.4 V
5652 | RE22R1HMR | Complementary | voltage range | 0.85...1.1 Us
5653 | RE22R1HMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
5654 | RE22R1HMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
5655 | RE22R1HMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
5656 | RE22R1HMR | Complementary | housing material | Self-extinguishing
5657 | RE22R1HMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
5658 | RE22R1HMR | Complementary | temperature drift | +/- 0.05 %/°C
5659 | RE22R1HMR | Complementary | voltage drift | +/- 0.2 %/V
5660 | RE22R1HMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
5661 | RE22R1HMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
5662 | RE22R1HMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5663 | RE22R1HMR | Complementary | Recovery time | 120 ms on de-energisation
5664 | RE22R1HMR | Complementary | immunity to microbreaks | 10 ms
5665 | RE22R1HMR | Complementary | power consumption in VA | 3 VA at 240 V AC
5666 | RE22R1HMR | Complementary | power consumption in W | 1.5 W at 240 V DC
5667 | RE22R1HMR | Complementary | switching capacity in VA | 2000 VA
5668 | RE22R1HMR | Complementary | minimum switching current | 10 mA at 5 V DC
5669 | RE22R1HMR | Complementary | maximum switching current | 8 A
5670 | RE22R1HMR | Complementary | maximum switching voltage | 250 V AC
5671 | RE22R1HMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
5672 | RE22R1HMR | Complementary | mechanical durability | 10000000 cycles
5673 | RE22R1HMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
5674 | RE22R1HMR | Complementary | Power on delay | 100 ms
5675 | RE22R1HMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
5676 | RE22R1HMR | Complementary | overvoltage category | III conforming to IEC 60664-1
5677 | RE22R1HMR | Complementary | safety reliability data | B10d = 280000 MTTFd = 308.2 years
5678 | RE22R1HMR | Complementary | mounting position | Any position
5679 | RE22R1HMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5680 | RE22R1HMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
5681 | RE22R1HMR | Complementary | width | 22.5 mm
5682 | RE22R1HMR | Complementary | net weight | 0.1 kg
5683 | RE22R1HMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
5684 | RE22R1HMR | Environment | standards | UL 508 IEC 61812-1
5685 | RE22R1HMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
5686 | RE22R1HMR | Environment | product certifications | CE EAC CSA RCM China RoHS CCC GL UL
5687 | RE22R1HMR | Environment | ambient air temperature for operation | -20…60 °C
5688 | RE22R1HMR | Environment | ambient air temperature for storage | -40…70 °C
5689 | RE22R1HMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529
5690 | RE22R1HMR | Environment | pollution degree | 3 conforming to IEC 60664-1
5691 | RE22R1HMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
5692 | RE22R1HMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
5693 | RE22R1HMR | Environment | relative humidity | 95 % at 25…55 °C
5694 | RE22R1HMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
5695 | RE22R1HMR | Offer Sustainability | Sustainable offer status | Green Premium product
5696 | RE22R1HMR | Offer Sustainability | REACh Regulation | REACh Declaration
5697 | RE22R1HMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
5698 | RE22R1HMR | Offer Sustainability | Mercury free | Yes
5699 | RE22R1HMR | Offer Sustainability | RoHS exemption information | Yes
5700 | RE22R1HMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
5701 | RE22R1HMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
5702 | RE22R1HMR | Offer Sustainability | Circularity Profile | End of Life Information
5703 | RE22R1KMR | Main | range of product | Zelio Time
5704 | RE22R1KMR | Main | product or component type | Modular timing relay
5705 | RE22R1KMR | Main | discrete output type | Relay
5706 | RE22R1KMR | Main | device short name | RE22
5707 | RE22R1KMR | Main | nominal output current | 5 A
5708 | RE22R1KMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
5709 | RE22R1KMR | Complementary | time delay type | K
5710 | RE22R1KMR | Complementary | time delay range | 10...100 s 1...10 min 1...10 s 0.3...3 s 3...30 s 0.05...1 s 30...300 s
5711 | RE22R1KMR | Complementary | control type | Rotary knob
5712 | RE22R1KMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
5713 | RE22R1KMR | Complementary | Release input voltage | <= 2.4 V
5714 | RE22R1KMR | Complementary | voltage range | 0.85...1.1 Us
5715 | RE22R1KMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
5716 | RE22R1KMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
5717 | RE22R1KMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
5718 | RE22R1KMR | Complementary | housing material | Self-extinguishing
5719 | RE22R1KMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
5720 | RE22R1KMR | Complementary | temperature drift | +/- 0.05 %/°C
5721 | RE22R1KMR | Complementary | voltage drift | +/- 0.2 %/V
5722 | RE22R1KMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
5723 | RE22R1KMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5724 | RE22R1KMR | Complementary | Recovery time | 100 ms on de-energisation
5725 | RE22R1KMR | Complementary | immunity to microbreaks | 10 ms
5726 | RE22R1KMR | Complementary | power consumption in VA | 3 VA at 240 V AC
5727 | RE22R1KMR | Complementary | power consumption in W | 2 W at 240 V DC
5728 | RE22R1KMR | Complementary | switching capacity in VA | 1250 VA
5729 | RE22R1KMR | Complementary | minimum switching current | 10 mA at 5 V DC
5730 | RE22R1KMR | Complementary | maximum switching current | 5 A
5731 | RE22R1KMR | Complementary | maximum switching voltage | 250 V AC
5732 | RE22R1KMR | Complementary | electrical durability | 100000 cycles, 2 A at 24 V, DC-1 100000 cycles, 5 A at 250 V, AC-1
5733 | RE22R1KMR | Complementary | mechanical durability | 10000000 cycles
5734 | RE22R1KMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
5735 | RE22R1KMR | Complementary | Power on delay | 200 ms
5736 | RE22R1KMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
5737 | RE22R1KMR | Complementary | overvoltage category | III conforming to IEC 60664-1
5738 | RE22R1KMR | Complementary | safety reliability data | MTTFd = 194 years B10d = 180000
5739 | RE22R1KMR | Complementary | mounting position | Any position
5740 | RE22R1KMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5741 | RE22R1KMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (steady) for power ON
5742 | RE22R1KMR | Complementary | width | 22.5 mm
5743 | RE22R1KMR | Complementary | net weight | 0.1 kg
5744 | RE22R1KMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
5745 | RE22R1KMR | Environment | standards | IEC 61812-1 UL 508
5746 | RE22R1KMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
5747 | RE22R1KMR | Environment | product certifications | CCC CSA GL China RoHS RCM CE EAC UL
5748 | RE22R1KMR | Environment | ambient air temperature for operation | -20…60 °C
5749 | RE22R1KMR | Environment | ambient air temperature for storage | -40…70 °C
5750 | RE22R1KMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529
5751 | RE22R1KMR | Environment | pollution degree | 3 conforming to IEC 60664-1
5752 | RE22R1KMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
5753 | RE22R1KMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
5754 | RE22R1KMR | Environment | relative humidity | 95 % at 25…55 °C
5755 | RE22R1KMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
5756 | RE22R1KMR | Offer Sustainability | Sustainable offer status | Green Premium product
5757 | RE22R1KMR | Offer Sustainability | REACh Regulation | REACh Declaration
5758 | RE22R1KMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
5759 | RE22R1KMR | Offer Sustainability | Mercury free | Yes
5760 | RE22R1KMR | Offer Sustainability | RoHS exemption information | Yes
5761 | RE22R1KMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
5762 | RE22R1KMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
5763 | RE22R1KMR | Offer Sustainability | Circularity Profile | End of Life Information
5764 | RE22R1MAMR | Main | range of product | Zelio Time
5765 | RE22R1MAMR | Main | product or component type | Modular timing relay
5766 | RE22R1MAMR | Main | discrete output type | Relay
5767 | RE22R1MAMR | Main | device short name | RE22
5768 | RE22R1MAMR | Main | nominal output current | 8 A
5769 | RE22R1MAMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
5770 | RE22R1MAMR | Complementary | time delay type | A At Aw
5771 | RE22R1MAMR | Complementary | time delay range | 3...30 h 0.05...1 s 30...300 s 3...30 min 3...30 s 30...300 h 30...300 min 0.3...3 s 10...100 s 1...10 s
5772 | RE22R1MAMR | Complementary | control type | Rotary knob Diagnostic button Potentiometer external
5773 | RE22R1MAMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
5774 | RE22R1MAMR | Complementary | Release input voltage | <= 2.4 V
5775 | RE22R1MAMR | Complementary | voltage range | 0.85...1.1 Us
5776 | RE22R1MAMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
5777 | RE22R1MAMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
5778 | RE22R1MAMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
5779 | RE22R1MAMR | Complementary | housing material | Self-extinguishing
5780 | RE22R1MAMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
5781 | RE22R1MAMR | Complementary | temperature drift | +/- 0.05 %/°C
5782 | RE22R1MAMR | Complementary | voltage drift | +/- 0.2 %/V
5783 | RE22R1MAMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
5784 | RE22R1MAMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
5785 | RE22R1MAMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5786 | RE22R1MAMR | Complementary | Recovery time | 120 ms on de-energisation
5787 | RE22R1MAMR | Complementary | immunity to microbreaks | 10 ms
5788 | RE22R1MAMR | Complementary | power consumption in VA | 3 VA at 240 V AC
5789 | RE22R1MAMR | Complementary | power consumption in W | 1.5 W at 240 V DC
5790 | RE22R1MAMR | Complementary | switching capacity in VA | 2000 VA
5791 | RE22R1MAMR | Complementary | minimum switching current | 10 mA at 5 V DC
5792 | RE22R1MAMR | Complementary | maximum switching current | 8 A
5793 | RE22R1MAMR | Complementary | maximum switching voltage | 250 V AC
5794 | RE22R1MAMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
5795 | RE22R1MAMR | Complementary | mechanical durability | 10000000 cycles
5796 | RE22R1MAMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
5797 | RE22R1MAMR | Complementary | Power on delay | 100 ms
5798 | RE22R1MAMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
5799 | RE22R1MAMR | Complementary | overvoltage category | III conforming to IEC 60664-1
5800 | RE22R1MAMR | Complementary | safety reliability data | B10d = 190000 MTTFd = 205.4 years
5801 | RE22R1MAMR | Complementary | mounting position | Any position
5802 | RE22R1MAMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5803 | RE22R1MAMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
5804 | RE22R1MAMR | Complementary | width | 22.5 mm
5805 | RE22R1MAMR | Complementary | net weight | 0.1 kg
5806 | RE22R1MAMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
5807 | RE22R1MAMR | Environment | standards | UL 508 IEC 61812-1
5808 | RE22R1MAMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
5809 | RE22R1MAMR | Environment | product certifications | EAC CSA RCM UL China RoHS GL CE CCC
5810 | RE22R1MAMR | Environment | ambient air temperature for operation | -20…60 °C
5811 | RE22R1MAMR | Environment | ambient air temperature for storage | -40…70 °C
5812 | RE22R1MAMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529
5813 | RE22R1MAMR | Environment | pollution degree | 3 conforming to IEC 60664-1
5814 | RE22R1MAMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
5815 | RE22R1MAMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
5816 | RE22R1MAMR | Environment | relative humidity | 95 % at 25…55 °C
5817 | RE22R1MAMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
5818 | RE22R1MAMR | Offer Sustainability | Sustainable offer status | Green Premium product
5819 | RE22R1MAMR | Offer Sustainability | REACh Regulation | REACh Declaration
5820 | RE22R1MAMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
5821 | RE22R1MAMR | Offer Sustainability | Mercury free | Yes
5822 | RE22R1MAMR | Offer Sustainability | RoHS exemption information | Yes
5823 | RE22R1MAMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
5824 | RE22R1MAMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
5825 | RE22R1MAMR | Offer Sustainability | Circularity Profile | End of Life Information
5826 | RE22R1MKMR | Main | range of product | Zelio Time
5827 | RE22R1MKMR | Main | product or component type | Modular timing relay
5828 | RE22R1MKMR | Main | discrete output type | Relay
5829 | RE22R1MKMR | Main | device short name | RE22
5830 | RE22R1MKMR | Main | nominal output current | 5 A
5831 | RE22R1MKMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
5832 | RE22R1MKMR | Complementary | time delay type | K He
5833 | RE22R1MKMR | Complementary | time delay range | 0.3...3 s 0.05...0.5 s 3...30 s 0.1...1 s 30...300 s 10...100 s 1...10 s
5834 | RE22R1MKMR | Complementary | control type | Rotary knob
5835 | RE22R1MKMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
5836 | RE22R1MKMR | Complementary | Release input voltage | <= 2.4 V
5837 | RE22R1MKMR | Complementary | voltage range | 0.85...1.1 Us
5838 | RE22R1MKMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
5839 | RE22R1MKMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
5840 | RE22R1MKMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
5841 | RE22R1MKMR | Complementary | housing material | Self-extinguishing
5842 | RE22R1MKMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
5843 | RE22R1MKMR | Complementary | temperature drift | +/- 0.05 %/°C
5844 | RE22R1MKMR | Complementary | voltage drift | +/- 0.2 %/V
5845 | RE22R1MKMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
5846 | RE22R1MKMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5847 | RE22R1MKMR | Complementary | Recovery time | 50 ms on de-energisation
5848 | RE22R1MKMR | Complementary | immunity to microbreaks | 10 ms
5849 | RE22R1MKMR | Complementary | power consumption in VA | 3 VA at 240 V AC
5850 | RE22R1MKMR | Complementary | power consumption in W | 2 W at 240 V DC
5851 | RE22R1MKMR | Complementary | switching capacity in VA | 1250 VA
5852 | RE22R1MKMR | Complementary | minimum switching current | 10 mA at 5 V DC
5853 | RE22R1MKMR | Complementary | maximum switching current | 5 A
5854 | RE22R1MKMR | Complementary | maximum switching voltage | 250 V AC
5855 | RE22R1MKMR | Complementary | electrical durability | 100000 cycles, 2 A at 24 V, DC-1 100000 cycles, 5 A at 250 V, AC-1
5856 | RE22R1MKMR | Complementary | mechanical durability | 10000000 cycles
5857 | RE22R1MKMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
5858 | RE22R1MKMR | Complementary | Power on delay | 100 ms
5859 | RE22R1MKMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
5860 | RE22R1MKMR | Complementary | overvoltage category | III conforming to IEC 60664-1
5861 | RE22R1MKMR | Complementary | safety reliability data | B10d = 180000 MTTFd = 194 years
5862 | RE22R1MKMR | Complementary | mounting position | Any position
5863 | RE22R1MKMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5864 | RE22R1MKMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (steady) for power ON
5865 | RE22R1MKMR | Complementary | width | 22.5 mm
5866 | RE22R1MKMR | Complementary | net weight | 0.1 kg
5867 | RE22R1MKMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
5868 | RE22R1MKMR | Environment | standards | IEC 61812-1 UL 508
5869 | RE22R1MKMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
5870 | RE22R1MKMR | Environment | product certifications | GL UL CSA RCM CCC China RoHS CE EAC
5871 | RE22R1MKMR | Environment | ambient air temperature for operation | -20…60 °C
5872 | RE22R1MKMR | Environment | ambient air temperature for storage | -40…70 °C
5873 | RE22R1MKMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529
5874 | RE22R1MKMR | Environment | pollution degree | 3 conforming to IEC 60664-1
5875 | RE22R1MKMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
5876 | RE22R1MKMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
5877 | RE22R1MKMR | Environment | relative humidity | 95 % at 25…55 °C
5878 | RE22R1MKMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
5879 | RE22R1MKMR | Offer Sustainability | Sustainable offer status | Green Premium product
5880 | RE22R1MKMR | Offer Sustainability | REACh Regulation | REACh Declaration
5881 | RE22R1MKMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
5882 | RE22R1MKMR | Offer Sustainability | Mercury free | Yes
5883 | RE22R1MKMR | Offer Sustainability | RoHS exemption information | Yes
5884 | RE22R1MKMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
5885 | RE22R1MKMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
5886 | RE22R1MKMR | Offer Sustainability | Circularity Profile | End of Life Information
5887 | RE22R1MLMR | Main | range of product | Zelio Time
5888 | RE22R1MLMR | Main | product or component type | Modular timing relay
5889 | RE22R1MLMR | Main | discrete output type | Relay
5890 | RE22R1MLMR | Main | device short name | RE22
5891 | RE22R1MLMR | Main | nominal output current | 8 A
5892 | RE22R1MLMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
5893 | RE22R1MLMR | Complementary | time delay type | Li Lit L Lt
5894 | RE22R1MLMR | Complementary | time delay range | 0.05...1 s 30...300 min 30...300 h 30...300 s 3...30 h 0.3...3 s 3...30 min 3...30 s 10...100 s 1...10 s
5895 | RE22R1MLMR | Complementary | control type | Rotary knob Diagnostic button Potentiometer external
5896 | RE22R1MLMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
5897 | RE22R1MLMR | Complementary | Release input voltage | <= 2.4 V
5898 | RE22R1MLMR | Complementary | voltage range | 0.85...1.1 Us
5899 | RE22R1MLMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
5900 | RE22R1MLMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
5901 | RE22R1MLMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
5902 | RE22R1MLMR | Complementary | housing material | Self-extinguishing
5903 | RE22R1MLMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
5904 | RE22R1MLMR | Complementary | temperature drift | +/- 0.05 %/°C
5905 | RE22R1MLMR | Complementary | voltage drift | +/- 0.2 %/V
5906 | RE22R1MLMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
5907 | RE22R1MLMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
5908 | RE22R1MLMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5909 | RE22R1MLMR | Complementary | Recovery time | 120 ms on de-energisation
5910 | RE22R1MLMR | Complementary | immunity to microbreaks | 10 ms
5911 | RE22R1MLMR | Complementary | power consumption in VA | 3 VA at 240 V AC
5912 | RE22R1MLMR | Complementary | power consumption in W | 1.5 W at 240 V DC
5913 | RE22R1MLMR | Complementary | switching capacity in VA | 2000 VA
5914 | RE22R1MLMR | Complementary | minimum switching current | 10 mA at 5 V DC
5915 | RE22R1MLMR | Complementary | maximum switching current | 8 A
5916 | RE22R1MLMR | Complementary | maximum switching voltage | 250 V AC
5917 | RE22R1MLMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
5918 | RE22R1MLMR | Complementary | mechanical durability | 10000000 cycles
5919 | RE22R1MLMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
5920 | RE22R1MLMR | Complementary | Power on delay | 100 ms
5921 | RE22R1MLMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
5922 | RE22R1MLMR | Complementary | overvoltage category | III conforming to IEC 60664-1
5923 | RE22R1MLMR | Complementary | safety reliability data | MTTFd = 194 years B10d = 180000
5924 | RE22R1MLMR | Complementary | mounting position | Any position
5925 | RE22R1MLMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5926 | RE22R1MLMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
5927 | RE22R1MLMR | Complementary | width | 22.5 mm
5928 | RE22R1MLMR | Complementary | net weight | 0.1 kg
5929 | RE22R1MLMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
5930 | RE22R1MLMR | Environment | standards | IEC 61812-1 UL 508
5931 | RE22R1MLMR | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive
5932 | RE22R1MLMR | Environment | product certifications | EAC UL GL China RoHS CSA RCM CCC CE
5933 | RE22R1MLMR | Environment | ambient air temperature for operation | -20…60 °C
5934 | RE22R1MLMR | Environment | ambient air temperature for storage | -40…70 °C
5935 | RE22R1MLMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529
5936 | RE22R1MLMR | Environment | pollution degree | 3 conforming to IEC 60664-1
5937 | RE22R1MLMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
5938 | RE22R1MLMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
5939 | RE22R1MLMR | Environment | relative humidity | 95 % at 25…55 °C
5940 | RE22R1MLMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
5941 | RE22R1MLMR | Offer Sustainability | Sustainable offer status | Green Premium product
5942 | RE22R1MLMR | Offer Sustainability | REACh Regulation | REACh Declaration
5943 | RE22R1MLMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
5944 | RE22R1MLMR | Offer Sustainability | Mercury free | Yes
5945 | RE22R1MLMR | Offer Sustainability | RoHS exemption information | Yes
5946 | RE22R1MLMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
5947 | RE22R1MLMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
5948 | RE22R1MLMR | Offer Sustainability | Circularity Profile | End of Life Information
5949 | RE22R1MYMR | Main | range of product | Zelio Time
5950 | RE22R1MYMR | Main | product or component type | Modular timing relay
5951 | RE22R1MYMR | Main | discrete output type | Relay
5952 | RE22R1MYMR | Main | device short name | RE22
5953 | RE22R1MYMR | Main | nominal output current | 8 A
5954 | RE22R1MYMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
5955 | RE22R1MYMR | Complementary | time delay type | Dw Ac C Dit Ht D A Di Hw W Ct Act At Wt H Dt Diw Aw
5956 | RE22R1MYMR | Complementary | time delay range | 30...300 s 10...100 s 3...30 s 30...300 min 3...30 min 0.3...3 s 0.05...1 s 30...300 h 1...10 s 3...30 h
5957 | RE22R1MYMR | Complementary | control type | Rotary knob Diagnostic button Potentiometer external
5958 | RE22R1MYMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
5959 | RE22R1MYMR | Complementary | Release input voltage | <= 2.4 V
5960 | RE22R1MYMR | Complementary | voltage range | 0.85...1.1 Us
5961 | RE22R1MYMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
5962 | RE22R1MYMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
5963 | RE22R1MYMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
5964 | RE22R1MYMR | Complementary | housing material | Self-extinguishing
5965 | RE22R1MYMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
5966 | RE22R1MYMR | Complementary | temperature drift | +/- 0.05 %/°C
5967 | RE22R1MYMR | Complementary | voltage drift | +/- 0.2 %/V
5968 | RE22R1MYMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
5969 | RE22R1MYMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
5970 | RE22R1MYMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
5971 | RE22R1MYMR | Complementary | Recovery time | 120 ms on de-energisation
5972 | RE22R1MYMR | Complementary | immunity to microbreaks | 10 ms
5973 | RE22R1MYMR | Complementary | power consumption in VA | 3 VA at 240 V AC
5974 | RE22R1MYMR | Complementary | power consumption in W | 1.5 W at 240 V DC
5975 | RE22R1MYMR | Complementary | switching capacity in VA | 2000 VA
5976 | RE22R1MYMR | Complementary | minimum switching current | 10 mA at 5 V DC
5977 | RE22R1MYMR | Complementary | maximum switching current | 8 A
5978 | RE22R1MYMR | Complementary | maximum switching voltage | 250 V AC
5979 | RE22R1MYMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
5980 | RE22R1MYMR | Complementary | mechanical durability | 10000000 cycles
5981 | RE22R1MYMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
5982 | RE22R1MYMR | Complementary | Power on delay | 100 ms
5983 | RE22R1MYMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
5984 | RE22R1MYMR | Complementary | overvoltage category | III conforming to IEC 60664-1
5985 | RE22R1MYMR | Complementary | safety reliability data | MTTFd = 205.4 years B10d = 190000
5986 | RE22R1MYMR | Complementary | mounting position | Any position
5987 | RE22R1MYMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
5988 | RE22R1MYMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
5989 | RE22R1MYMR | Complementary | width | 22.5 mm
5990 | RE22R1MYMR | Complementary | net weight | 0.1 kg
5991 | RE22R1MYMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
5992 | RE22R1MYMR | Environment | standards | IEC 61812-1 UL 508
5993 | RE22R1MYMR | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive
5994 | RE22R1MYMR | Environment | product certifications | RCM GL EAC CE CSA CCC China RoHS UL
5995 | RE22R1MYMR | Environment | ambient air temperature for operation | -20…60 °C
5996 | RE22R1MYMR | Environment | ambient air temperature for storage | -40…70 °C
5997 | RE22R1MYMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529
5998 | RE22R1MYMR | Environment | pollution degree | 3 conforming to IEC 60664-1
5999 | RE22R1MYMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
6000 | RE22R1MYMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
6001 | RE22R1MYMR | Environment | relative humidity | 95 % at 25…55 °C
6002 | RE22R1MYMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
6003 | RE22R1MYMR | Offer Sustainability | Sustainable offer status | Green Premium product
6004 | RE22R1MYMR | Offer Sustainability | REACh Regulation | REACh Declaration
6005 | RE22R1MYMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6006 | RE22R1MYMR | Offer Sustainability | Mercury free | Yes
6007 | RE22R1MYMR | Offer Sustainability | RoHS exemption information | Yes
6008 | RE22R1MYMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
6009 | RE22R1MYMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
6010 | RE22R1MYMR | Offer Sustainability | Circularity Profile | End of Life Information
6011 | RE22R1QCMU | Main | range of product | Zelio Time
6012 | RE22R1QCMU | Main | product or component type | Modular timing relay
6013 | RE22R1QCMU | Main | discrete output type | Relay
6014 | RE22R1QCMU | Main | device short name | RE22
6015 | RE22R1QCMU | Main | nominal output current | 8 A
6016 | RE22R1QCMU | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
6017 | RE22R1QCMU | Complementary | time delay type | Qc
6018 | RE22R1QCMU | Complementary | time delay range | 10...100 s 3...30 s 0.1...1 s 0.3...3 s 0.05...0.5 s 1...10 s 30...300 s
6019 | RE22R1QCMU | Complementary | control type | Rotary knob Diagnostic button
6020 | RE22R1QCMU | Complementary | [Us] rated supply voltage | 24 V DC 24...240 V AC 50/60 Hz
6021 | RE22R1QCMU | Complementary | Release input voltage | <= 2.4 V
6022 | RE22R1QCMU | Complementary | voltage range | 0.85...1.1 Us
6023 | RE22R1QCMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
6024 | RE22R1QCMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
6025 | RE22R1QCMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
6026 | RE22R1QCMU | Complementary | housing material | Self-extinguishing
6027 | RE22R1QCMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
6028 | RE22R1QCMU | Complementary | temperature drift | +/- 0.05 %/°C
6029 | RE22R1QCMU | Complementary | voltage drift | +/- 0.2 %/V
6030 | RE22R1QCMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
6031 | RE22R1QCMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
6032 | RE22R1QCMU | Complementary | Recovery time | 120 ms on de-energisation
6033 | RE22R1QCMU | Complementary | immunity to microbreaks | 10 ms
6034 | RE22R1QCMU | Complementary | power consumption in VA | 35 VA at 240 V AC
6035 | RE22R1QCMU | Complementary | power consumption in W | 0.6 W at 24 V DC
6036 | RE22R1QCMU | Complementary | switching capacity in VA | 2000 VA
6037 | RE22R1QCMU | Complementary | minimum switching current | 10 mA at 5 V DC
6038 | RE22R1QCMU | Complementary | maximum switching current | 8 A
6039 | RE22R1QCMU | Complementary | maximum switching voltage | 250 V AC
6040 | RE22R1QCMU | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
6041 | RE22R1QCMU | Complementary | mechanical durability | 10000000 cycles
6042 | RE22R1QCMU | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
6043 | RE22R1QCMU | Complementary | Power on delay | 100 ms
6044 | RE22R1QCMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
6045 | RE22R1QCMU | Complementary | overvoltage category | III conforming to IEC 60664-1
6046 | RE22R1QCMU | Complementary | safety reliability data | MTTFd = 285.3 years B10d = 270000
6047 | RE22R1QCMU | Complementary | mounting position | Any position
6048 | RE22R1QCMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
6049 | RE22R1QCMU | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
6050 | RE22R1QCMU | Complementary | width | 22.5 mm
6051 | RE22R1QCMU | Complementary | net weight | 0.08 kg
6052 | RE22R1QCMU | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
6053 | RE22R1QCMU | Environment | standards | UL 508 IEC 61812-1
6054 | RE22R1QCMU | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive
6055 | RE22R1QCMU | Environment | product certifications | GL China RoHS CE CCC EAC UL CSA RCM
6056 | RE22R1QCMU | Environment | ambient air temperature for operation | -20…60 °C
6057 | RE22R1QCMU | Environment | ambient air temperature for storage | -40…70 °C
6058 | RE22R1QCMU | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529
6059 | RE22R1QCMU | Environment | pollution degree | 3 conforming to IEC 60664-1
6060 | RE22R1QCMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
6061 | RE22R1QCMU | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
6062 | RE22R1QCMU | Environment | relative humidity | 95 % at 25…55 °C
6063 | RE22R1QCMU | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
6064 | RE22R1QCMU | Offer Sustainability | Sustainable offer status | Green Premium product
6065 | RE22R1QCMU | Offer Sustainability | REACh Regulation | REACh Declaration
6066 | RE22R1QCMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6067 | RE22R1QCMU | Offer Sustainability | Mercury free | Yes
6068 | RE22R1QCMU | Offer Sustainability | RoHS exemption information | Yes
6069 | RE22R1QCMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
6070 | RE22R1QCMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
6071 | RE22R1QCMU | Offer Sustainability | Circularity Profile | End of Life Information
6072 | RE22R2ACMR | Main | range of product | Zelio Time
6073 | RE22R2ACMR | Main | product or component type | Modular timing relay
6074 | RE22R2ACMR | Main | discrete output type | Relay
6075 | RE22R2ACMR | Main | device short name | RE22
6076 | RE22R2ACMR | Main | nominal output current | 8 A
6077 | RE22R2ACMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free
6078 | RE22R2ACMR | Complementary | time delay type | Ac
6079 | RE22R2ACMR | Complementary | time delay range | 3...30 h 30...300 h 0.05...1 s 30...300 s 0.3...3 s 10...100 s 1...10 s 3...30 min 30...300 min 3...30 s
6080 | RE22R2ACMR | Complementary | control type | Rotary knob Diagnostic button
6081 | RE22R2ACMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
6082 | RE22R2ACMR | Complementary | Release input voltage | <= 2.4 V
6083 | RE22R2ACMR | Complementary | voltage range | 0.85...1.1 Us
6084 | RE22R2ACMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
6085 | RE22R2ACMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
6086 | RE22R2ACMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
6087 | RE22R2ACMR | Complementary | housing material | Self-extinguishing
6088 | RE22R2ACMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
6089 | RE22R2ACMR | Complementary | temperature drift | +/- 0.05 %/°C
6090 | RE22R2ACMR | Complementary | voltage drift | +/- 0.2 %/V
6091 | RE22R2ACMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
6092 | RE22R2ACMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
6093 | RE22R2ACMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
6094 | RE22R2ACMR | Complementary | Recovery time | 120 ms on de-energisation
6095 | RE22R2ACMR | Complementary | immunity to microbreaks | 10 ms
6096 | RE22R2ACMR | Complementary | power consumption in VA | 3 VA at 240 V AC
6097 | RE22R2ACMR | Complementary | power consumption in W | 1.5 W at 240 V DC
6098 | RE22R2ACMR | Complementary | switching capacity in VA | 2000 VA
6099 | RE22R2ACMR | Complementary | minimum switching current | 10 mA at 5 V DC
6100 | RE22R2ACMR | Complementary | maximum switching current | 8 A
6101 | RE22R2ACMR | Complementary | maximum switching voltage | 250 V AC
6102 | RE22R2ACMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
6103 | RE22R2ACMR | Complementary | mechanical durability | 10000000 cycles
6104 | RE22R2ACMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
6105 | RE22R2ACMR | Complementary | Power on delay | 100 ms
6106 | RE22R2ACMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
6107 | RE22R2ACMR | Complementary | overvoltage category | III conforming to IEC 60664-1
6108 | RE22R2ACMR | Complementary | safety reliability data | MTTFd = 251.1 years B10d = 230000
6109 | RE22R2ACMR | Complementary | mounting position | Any position
6110 | RE22R2ACMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
6111 | RE22R2ACMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
6112 | RE22R2ACMR | Complementary | width | 22.5 mm
6113 | RE22R2ACMR | Complementary | net weight | 0.105 kg
6114 | RE22R2ACMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
6115 | RE22R2ACMR | Environment | standards | UL 508 IEC 61812-1
6116 | RE22R2ACMR | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive
6117 | RE22R2ACMR | Environment | product certifications | China RoHS RCM CCC CSA UL EAC CE GL
6118 | RE22R2ACMR | Environment | ambient air temperature for operation | -20…60 °C
6119 | RE22R2ACMR | Environment | ambient air temperature for storage | -40…70 °C
6120 | RE22R2ACMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529
6121 | RE22R2ACMR | Environment | pollution degree | 3 conforming to IEC 60664-1
6122 | RE22R2ACMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
6123 | RE22R2ACMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
6124 | RE22R2ACMR | Environment | relative humidity | 95 % at 25…55 °C
6125 | RE22R2ACMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
6126 | RE22R2ACMR | Offer Sustainability | Sustainable offer status | Green Premium product
6127 | RE22R2ACMR | Offer Sustainability | REACh Regulation | REACh Declaration
6128 | RE22R2ACMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6129 | RE22R2ACMR | Offer Sustainability | Mercury free | Yes
6130 | RE22R2ACMR | Offer Sustainability | RoHS exemption information | Yes
6131 | RE22R2ACMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
6132 | RE22R2ACMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
6133 | RE22R2ACMR | Offer Sustainability | Circularity Profile | End of Life Information
6134 | RE22R2AMR | Main | range of product | Zelio Time
6135 | RE22R2AMR | Main | product or component type | Modular timing relay
6136 | RE22R2AMR | Main | discrete output type | Relay
6137 | RE22R2AMR | Main | device short name | RE22
6138 | RE22R2AMR | Main | nominal output current | 8 A
6139 | RE22R2AMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free
6140 | RE22R2AMR | Complementary | time delay type | Aw A
6141 | RE22R2AMR | Complementary | time delay range | 0.05...1 s 0.3...3 s 3...30 h 30...300 min 10...100 s 30...300 s 3...30 s 30...300 h 1...10 s 3...30 min
6142 | RE22R2AMR | Complementary | control type | Rotary knob Diagnostic button Potentiometer external
6143 | RE22R2AMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
6144 | RE22R2AMR | Complementary | Release input voltage | <= 2.4 V
6145 | RE22R2AMR | Complementary | voltage range | 0.85...1.1 Us
6146 | RE22R2AMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
6147 | RE22R2AMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
6148 | RE22R2AMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
6149 | RE22R2AMR | Complementary | housing material | Self-extinguishing
6150 | RE22R2AMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
6151 | RE22R2AMR | Complementary | temperature drift | +/- 0.05 %/°C
6152 | RE22R2AMR | Complementary | voltage drift | +/- 0.2 %/V
6153 | RE22R2AMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
6154 | RE22R2AMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
6155 | RE22R2AMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
6156 | RE22R2AMR | Complementary | Recovery time | 120 ms on de-energisation
6157 | RE22R2AMR | Complementary | immunity to microbreaks | 10 ms
6158 | RE22R2AMR | Complementary | power consumption in VA | 3 VA at 240 V AC
6159 | RE22R2AMR | Complementary | power consumption in W | 1.5 W at 240 V DC
6160 | RE22R2AMR | Complementary | switching capacity in VA | 2000 VA
6161 | RE22R2AMR | Complementary | minimum switching current | 10 mA at 5 V DC
6162 | RE22R2AMR | Complementary | maximum switching current | 8 A
6163 | RE22R2AMR | Complementary | maximum switching voltage | 250 V AC
6164 | RE22R2AMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
6165 | RE22R2AMR | Complementary | mechanical durability | 10000000 cycles
6166 | RE22R2AMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
6167 | RE22R2AMR | Complementary | Power on delay | 100 ms
6168 | RE22R2AMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
6169 | RE22R2AMR | Complementary | overvoltage category | III conforming to IEC 60664-1
6170 | RE22R2AMR | Complementary | safety reliability data | B10d = 200000 MTTFd = 216.8 years
6171 | RE22R2AMR | Complementary | mounting position | Any position
6172 | RE22R2AMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
6173 | RE22R2AMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
6174 | RE22R2AMR | Complementary | width | 22.5 mm
6175 | RE22R2AMR | Complementary | net weight | 0.105 kg
6176 | RE22R2AMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
6177 | RE22R2AMR | Environment | standards | UL 508 IEC 61812-1
6178 | RE22R2AMR | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive
6179 | RE22R2AMR | Environment | product certifications | CE CCC GL China RoHS UL RCM EAC CSA
6180 | RE22R2AMR | Environment | ambient air temperature for operation | -20…60 °C
6181 | RE22R2AMR | Environment | ambient air temperature for storage | -40…70 °C
6182 | RE22R2AMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529
6183 | RE22R2AMR | Environment | pollution degree | 3 conforming to IEC 60664-1
6184 | RE22R2AMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
6185 | RE22R2AMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
6186 | RE22R2AMR | Environment | relative humidity | 95 % at 25…55 °C
6187 | RE22R2AMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
6188 | RE22R2AMR | Offer Sustainability | Sustainable offer status | Green Premium product
6189 | RE22R2AMR | Offer Sustainability | REACh Regulation | REACh Declaration
6190 | RE22R2AMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6191 | RE22R2AMR | Offer Sustainability | Mercury free | Yes
6192 | RE22R2AMR | Offer Sustainability | RoHS exemption information | Yes
6193 | RE22R2AMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
6194 | RE22R2AMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
6195 | RE22R2AMR | Offer Sustainability | Circularity Profile | End of Life Information
6196 | RE22R2CMR | Main | range of product | Zelio Time
6197 | RE22R2CMR | Main | product or component type | Modular timing relay
6198 | RE22R2CMR | Main | discrete output type | Relay
6199 | RE22R2CMR | Main | device short name | RE22
6200 | RE22R2CMR | Main | nominal output current | 8 A
6201 | RE22R2CMR | Complementary | contacts type and composition | 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free
6202 | RE22R2CMR | Complementary | time delay type | C
6203 | RE22R2CMR | Complementary | time delay range | 10...100 s 3...30 h 1...10 s 3...30 s 30...300 h 0.3...3 s 0.05...1 s 30...300 min 30...300 s 3...30 min
6204 | RE22R2CMR | Complementary | control type | Rotary knob Diagnostic button
6205 | RE22R2CMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
6206 | RE22R2CMR | Complementary | Release input voltage | <= 2.4 V
6207 | RE22R2CMR | Complementary | voltage range | 0.85...1.1 Us
6208 | RE22R2CMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
6209 | RE22R2CMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
6210 | RE22R2CMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
6211 | RE22R2CMR | Complementary | housing material | Self-extinguishing
6212 | RE22R2CMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
6213 | RE22R2CMR | Complementary | temperature drift | +/- 0.05 %/°C
6214 | RE22R2CMR | Complementary | voltage drift | +/- 0.2 %/V
6215 | RE22R2CMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
6216 | RE22R2CMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
6217 | RE22R2CMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
6218 | RE22R2CMR | Complementary | Recovery time | 120 ms on de-energisation
6219 | RE22R2CMR | Complementary | immunity to microbreaks | 10 ms
6220 | RE22R2CMR | Complementary | power consumption in VA | 3 VA at 240 V AC
6221 | RE22R2CMR | Complementary | power consumption in W | 1.5 W at 240 V DC
6222 | RE22R2CMR | Complementary | switching capacity in VA | 2000 VA
6223 | RE22R2CMR | Complementary | minimum switching current | 10 mA at 5 V DC
6224 | RE22R2CMR | Complementary | maximum switching current | 8 A
6225 | RE22R2CMR | Complementary | maximum switching voltage | 250 V AC
6226 | RE22R2CMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
6227 | RE22R2CMR | Complementary | mechanical durability | 10000000 cycles
6228 | RE22R2CMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
6229 | RE22R2CMR | Complementary | Power on delay | 100 ms
6230 | RE22R2CMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
6231 | RE22R2CMR | Complementary | overvoltage category | III conforming to IEC 60664-1
6232 | RE22R2CMR | Complementary | safety reliability data | MTTFd = 251.1 years B10d = 230000
6233 | RE22R2CMR | Complementary | mounting position | Any position
6234 | RE22R2CMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
6235 | RE22R2CMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
6236 | RE22R2CMR | Complementary | width | 22.5 mm
6237 | RE22R2CMR | Complementary | net weight | 0.105 kg
6238 | RE22R2CMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
6239 | RE22R2CMR | Environment | standards | UL 508 IEC 61812-1
6240 | RE22R2CMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
6241 | RE22R2CMR | Environment | product certifications | CSA CCC RCM China RoHS CE GL UL EAC
6242 | RE22R2CMR | Environment | ambient air temperature for operation | -20…60 °C
6243 | RE22R2CMR | Environment | ambient air temperature for storage | -40…70 °C
6244 | RE22R2CMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529
6245 | RE22R2CMR | Environment | pollution degree | 3 conforming to IEC 60664-1
6246 | RE22R2CMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
6247 | RE22R2CMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
6248 | RE22R2CMR | Environment | relative humidity | 95 % at 25…55 °C
6249 | RE22R2CMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
6250 | RE22R2CMR | Offer Sustainability | Sustainable offer status | Green Premium product
6251 | RE22R2CMR | Offer Sustainability | REACh Regulation | REACh Declaration
6252 | RE22R2CMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6253 | RE22R2CMR | Offer Sustainability | Mercury free | Yes
6254 | RE22R2CMR | Offer Sustainability | RoHS exemption information | Yes
6255 | RE22R2CMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
6256 | RE22R2CMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
6257 | RE22R2CMR | Offer Sustainability | Circularity Profile | End of Life Information
6258 | RE22R2DMR | Main | range of product | Zelio Time
6259 | RE22R2DMR | Main | product or component type | Modular timing relay
6260 | RE22R2DMR | Main | discrete output type | Relay
6261 | RE22R2DMR | Main | device short name | RE22
6262 | RE22R2DMR | Main | nominal output current | 8 A
6263 | RE22R2DMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free
6264 | RE22R2DMR | Complementary | time delay type | D Dw
6265 | RE22R2DMR | Complementary | time delay range | 1...10 s 30...300 min 3...30 s 10...100 s 30...300 h 30...300 s 3...30 min 0.3...3 s 0.05...1 s 3...30 h
6266 | RE22R2DMR | Complementary | control type | Rotary knob Diagnostic button Potentiometer external
6267 | RE22R2DMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
6268 | RE22R2DMR | Complementary | Release input voltage | <= 2.4 V
6269 | RE22R2DMR | Complementary | voltage range | 0.85...1.1 Us
6270 | RE22R2DMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
6271 | RE22R2DMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
6272 | RE22R2DMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
6273 | RE22R2DMR | Complementary | housing material | Self-extinguishing
6274 | RE22R2DMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
6275 | RE22R2DMR | Complementary | temperature drift | +/- 0.05 %/°C
6276 | RE22R2DMR | Complementary | voltage drift | +/- 0.2 %/V
6277 | RE22R2DMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
6278 | RE22R2DMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
6279 | RE22R2DMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
6280 | RE22R2DMR | Complementary | Recovery time | 120 ms on de-energisation
6281 | RE22R2DMR | Complementary | immunity to microbreaks | 10 ms
6282 | RE22R2DMR | Complementary | power consumption in VA | 3 VA at 240 V AC
6283 | RE22R2DMR | Complementary | power consumption in W | 1.5 W at 240 V DC
6284 | RE22R2DMR | Complementary | switching capacity in VA | 2000 VA
6285 | RE22R2DMR | Complementary | minimum switching current | 10 mA at 5 V DC
6286 | RE22R2DMR | Complementary | maximum switching current | 8 A
6287 | RE22R2DMR | Complementary | maximum switching voltage | 250 V AC
6288 | RE22R2DMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
6289 | RE22R2DMR | Complementary | mechanical durability | 10000000 cycles
6290 | RE22R2DMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
6291 | RE22R2DMR | Complementary | Power on delay | 100 ms
6292 | RE22R2DMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
6293 | RE22R2DMR | Complementary | overvoltage category | III conforming to IEC 60664-1
6294 | RE22R2DMR | Complementary | safety reliability data | B10d = 200000 MTTFd = 216.8 years
6295 | RE22R2DMR | Complementary | mounting position | Any position
6296 | RE22R2DMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
6297 | RE22R2DMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
6298 | RE22R2DMR | Complementary | width | 22.5 mm
6299 | RE22R2DMR | Complementary | net weight | 0.105 kg
6300 | RE22R2DMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
6301 | RE22R2DMR | Environment | standards | IEC 61812-1 UL 508
6302 | RE22R2DMR | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive
6303 | RE22R2DMR | Environment | product certifications | CCC China RoHS CSA RCM GL CE UL EAC
6304 | RE22R2DMR | Environment | ambient air temperature for operation | -20…60 °C
6305 | RE22R2DMR | Environment | ambient air temperature for storage | -40…70 °C
6306 | RE22R2DMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529
6307 | RE22R2DMR | Environment | pollution degree | 3 conforming to IEC 60664-1
6308 | RE22R2DMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
6309 | RE22R2DMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
6310 | RE22R2DMR | Environment | relative humidity | 95 % at 25…55 °C
6311 | RE22R2DMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
6312 | RE22R2DMR | Offer Sustainability | Sustainable offer status | Green Premium product
6313 | RE22R2DMR | Offer Sustainability | REACh Regulation | REACh Declaration
6314 | RE22R2DMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6315 | RE22R2DMR | Offer Sustainability | Mercury free | Yes
6316 | RE22R2DMR | Offer Sustainability | RoHS exemption information | Yes
6317 | RE22R2DMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
6318 | RE22R2DMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
6319 | RE22R2DMR | Offer Sustainability | Circularity Profile | End of Life Information
6320 | RE22R2HMR | Main | range of product | Zelio Time
6321 | RE22R2HMR | Main | product or component type | Modular timing relay
6322 | RE22R2HMR | Main | discrete output type | Relay
6323 | RE22R2HMR | Main | device short name | RE22
6324 | RE22R2HMR | Main | nominal output current | 8 A
6325 | RE22R2HMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free
6326 | RE22R2HMR | Complementary | time delay type | H Hw
6327 | RE22R2HMR | Complementary | time delay range | 1...10 s 3...30 h 10...100 s 30...300 s 0.05...1 s 3...30 min 0.3...3 s 3...30 s 30...300 min 30...300 h
6328 | RE22R2HMR | Complementary | control type | Rotary knob Diagnostic button Potentiometer external
6329 | RE22R2HMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
6330 | RE22R2HMR | Complementary | Release input voltage | <= 2.4 V
6331 | RE22R2HMR | Complementary | voltage range | 0.85...1.1 Us
6332 | RE22R2HMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
6333 | RE22R2HMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
6334 | RE22R2HMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
6335 | RE22R2HMR | Complementary | housing material | Self-extinguishing
6336 | RE22R2HMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
6337 | RE22R2HMR | Complementary | temperature drift | +/- 0.05 %/°C
6338 | RE22R2HMR | Complementary | voltage drift | +/- 0.2 %/V
6339 | RE22R2HMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
6340 | RE22R2HMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
6341 | RE22R2HMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
6342 | RE22R2HMR | Complementary | Recovery time | 120 ms on de-energisation
6343 | RE22R2HMR | Complementary | immunity to microbreaks | 10 ms
6344 | RE22R2HMR | Complementary | power consumption in VA | 3 VA at 240 V AC
6345 | RE22R2HMR | Complementary | power consumption in W | 1.5 W at 240 V DC
6346 | RE22R2HMR | Complementary | switching capacity in VA | 2000 VA
6347 | RE22R2HMR | Complementary | minimum switching current | 10 mA at 5 V DC
6348 | RE22R2HMR | Complementary | maximum switching current | 8 A
6349 | RE22R2HMR | Complementary | maximum switching voltage | 250 V AC
6350 | RE22R2HMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
6351 | RE22R2HMR | Complementary | mechanical durability | 10000000 cycles
6352 | RE22R2HMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
6353 | RE22R2HMR | Complementary | Power on delay | 100 ms
6354 | RE22R2HMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
6355 | RE22R2HMR | Complementary | overvoltage category | III conforming to IEC 60664-1
6356 | RE22R2HMR | Complementary | safety reliability data | B10d = 200000 MTTFd = 216.8 years
6357 | RE22R2HMR | Complementary | mounting position | Any position
6358 | RE22R2HMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
6359 | RE22R2HMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
6360 | RE22R2HMR | Complementary | width | 22.5 mm
6361 | RE22R2HMR | Complementary | net weight | 0.105 kg
6362 | RE22R2HMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
6363 | RE22R2HMR | Environment | standards | IEC 61812-1 UL 508
6364 | RE22R2HMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
6365 | RE22R2HMR | Environment | product certifications | RCM CSA CE EAC UL CCC GL China RoHS
6366 | RE22R2HMR | Environment | ambient air temperature for operation | -20…60 °C
6367 | RE22R2HMR | Environment | ambient air temperature for storage | -40…70 °C
6368 | RE22R2HMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529
6369 | RE22R2HMR | Environment | pollution degree | 3 conforming to IEC 60664-1
6370 | RE22R2HMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
6371 | RE22R2HMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
6372 | RE22R2HMR | Environment | relative humidity | 95 % at 25…55 °C
6373 | RE22R2HMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
6374 | RE22R2HMR | Offer Sustainability | Sustainable offer status | Green Premium product
6375 | RE22R2HMR | Offer Sustainability | REACh Regulation | REACh Declaration
6376 | RE22R2HMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6377 | RE22R2HMR | Offer Sustainability | Mercury free | Yes
6378 | RE22R2HMR | Offer Sustainability | RoHS exemption information | Yes
6379 | RE22R2HMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
6380 | RE22R2HMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
6381 | RE22R2HMR | Offer Sustainability | Circularity Profile | End of Life Information
6382 | RE22R2KMR | Main | range of product | Zelio Time
6383 | RE22R2KMR | Main | product or component type | Modular timing relay
6384 | RE22R2KMR | Main | discrete output type | Relay
6385 | RE22R2KMR | Main | device short name | RE22
6386 | RE22R2KMR | Main | nominal output current | 5 A
6387 | RE22R2KMR | Complementary | contacts type and composition | 2 C/O timed contact, cadmium free
6388 | RE22R2KMR | Complementary | time delay type | K
6389 | RE22R2KMR | Complementary | time delay range | 10...100 s 0.05...1 s 30...300 s 3...30 s 1...10 min 1...10 s 0.3...3 s
6390 | RE22R2KMR | Complementary | control type | Rotary knob Potentiometer external
6391 | RE22R2KMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
6392 | RE22R2KMR | Complementary | Release input voltage | <= 2.4 V
6393 | RE22R2KMR | Complementary | voltage range | 0.85...1.1 Us
6394 | RE22R2KMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
6395 | RE22R2KMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
6396 | RE22R2KMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
6397 | RE22R2KMR | Complementary | housing material | Self-extinguishing
6398 | RE22R2KMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
6399 | RE22R2KMR | Complementary | temperature drift | +/- 0.05 %/°C
6400 | RE22R2KMR | Complementary | voltage drift | +/- 0.2 %/V
6401 | RE22R2KMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
6402 | RE22R2KMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
6403 | RE22R2KMR | Complementary | Recovery time | 100 ms on de-energisation
6404 | RE22R2KMR | Complementary | immunity to microbreaks | 10 ms
6405 | RE22R2KMR | Complementary | power consumption in VA | 3 VA at 240 V AC
6406 | RE22R2KMR | Complementary | power consumption in W | 2 W at 240 V DC
6407 | RE22R2KMR | Complementary | switching capacity in VA | 1250 VA
6408 | RE22R2KMR | Complementary | minimum switching current | 10 mA at 5 V DC
6409 | RE22R2KMR | Complementary | maximum switching current | 5 A
6410 | RE22R2KMR | Complementary | maximum switching voltage | 250 V AC
6411 | RE22R2KMR | Complementary | electrical durability | 100000 cycles, 2 A at 24 V, DC-1 100000 cycles, 5 A at 250 V, AC-1
6412 | RE22R2KMR | Complementary | mechanical durability | 10000000 cycles
6413 | RE22R2KMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
6414 | RE22R2KMR | Complementary | Power on delay | 200 ms
6415 | RE22R2KMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
6416 | RE22R2KMR | Complementary | overvoltage category | III conforming to IEC 60664-1
6417 | RE22R2KMR | Complementary | safety reliability data | B10d = 160000 MTTFd = 171.2 years
6418 | RE22R2KMR | Complementary | mounting position | Any position
6419 | RE22R2KMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
6420 | RE22R2KMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (steady) for power ON
6421 | RE22R2KMR | Complementary | width | 22.5 mm
6422 | RE22R2KMR | Complementary | net weight | 0.1 kg
6423 | RE22R2KMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
6424 | RE22R2KMR | Environment | standards | IEC 61812-1 UL 508
6425 | RE22R2KMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
6426 | RE22R2KMR | Environment | product certifications | China RoHS EAC UL RCM GL CCC CSA CE
6427 | RE22R2KMR | Environment | ambient air temperature for operation | -20…60 °C
6428 | RE22R2KMR | Environment | ambient air temperature for storage | -40…70 °C
6429 | RE22R2KMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529
6430 | RE22R2KMR | Environment | pollution degree | 3 conforming to IEC 60664-1
6431 | RE22R2KMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
6432 | RE22R2KMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
6433 | RE22R2KMR | Environment | relative humidity | 95 % at 25…55 °C
6434 | RE22R2KMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
6435 | RE22R2KMR | Offer Sustainability | Sustainable offer status | Green Premium product
6436 | RE22R2KMR | Offer Sustainability | REACh Regulation | REACh Declaration
6437 | RE22R2KMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6438 | RE22R2KMR | Offer Sustainability | Mercury free | Yes
6439 | RE22R2KMR | Offer Sustainability | RoHS exemption information | Yes
6440 | RE22R2KMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
6441 | RE22R2KMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
6442 | RE22R2KMR | Offer Sustainability | Circularity Profile | End of Life Information
6443 | RE22R2MWMR | Main | range of product | Zelio Time
6444 | RE22R2MWMR | Main | product or component type | Modular timing relay
6445 | RE22R2MWMR | Main | discrete output type | Relay
6446 | RE22R2MWMR | Main | device short name | RE22
6447 | RE22R2MWMR | Main | nominal output current | 8 A
6448 | RE22R2MWMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free
6449 | RE22R2MWMR | Complementary | time delay type | W Wt
6450 | RE22R2MWMR | Complementary | time delay range | 0.05...1 s 30...300 min 30...300 s 3...30 h 0.3...3 s 1...10 s 3...30 s 30...300 h 3...30 min 10...100 s
6451 | RE22R2MWMR | Complementary | control type | Rotary knob Diagnostic button Potentiometer external
6452 | RE22R2MWMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
6453 | RE22R2MWMR | Complementary | Release input voltage | <= 2.4 V
6454 | RE22R2MWMR | Complementary | voltage range | 0.85...1.1 Us
6455 | RE22R2MWMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
6456 | RE22R2MWMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
6457 | RE22R2MWMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
6458 | RE22R2MWMR | Complementary | housing material | Self-extinguishing
6459 | RE22R2MWMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
6460 | RE22R2MWMR | Complementary | temperature drift | +/- 0.05 %/°C
6461 | RE22R2MWMR | Complementary | voltage drift | +/- 0.2 %/V
6462 | RE22R2MWMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
6463 | RE22R2MWMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
6464 | RE22R2MWMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
6465 | RE22R2MWMR | Complementary | Recovery time | 120 ms on de-energisation
6466 | RE22R2MWMR | Complementary | immunity to microbreaks | 10 ms
6467 | RE22R2MWMR | Complementary | power consumption in VA | 3 VA at 240 V AC
6468 | RE22R2MWMR | Complementary | power consumption in W | 1.5 W at 240 V DC
6469 | RE22R2MWMR | Complementary | switching capacity in VA | 2000 VA
6470 | RE22R2MWMR | Complementary | minimum switching current | 10 mA at 5 V DC
6471 | RE22R2MWMR | Complementary | maximum switching current | 8 A
6472 | RE22R2MWMR | Complementary | maximum switching voltage | 250 V AC
6473 | RE22R2MWMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
6474 | RE22R2MWMR | Complementary | mechanical durability | 10000000 cycles
6475 | RE22R2MWMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
6476 | RE22R2MWMR | Complementary | Power on delay | 100 ms
6477 | RE22R2MWMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
6478 | RE22R2MWMR | Complementary | overvoltage category | III conforming to IEC 60664-1
6479 | RE22R2MWMR | Complementary | safety reliability data | B10d = 160000 MTTFd = 171.2 years
6480 | RE22R2MWMR | Complementary | mounting position | Any position
6481 | RE22R2MWMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
6482 | RE22R2MWMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
6483 | RE22R2MWMR | Complementary | width | 22.5 mm
6484 | RE22R2MWMR | Complementary | net weight | 0.105 kg
6485 | RE22R2MWMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
6486 | RE22R2MWMR | Environment | standards | UL 508 IEC 61812-1
6487 | RE22R2MWMR | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive
6488 | RE22R2MWMR | Environment | product certifications | UL GL CE China RoHS CSA RCM EAC CCC
6489 | RE22R2MWMR | Environment | ambient air temperature for operation | -20…60 °C
6490 | RE22R2MWMR | Environment | ambient air temperature for storage | -40…70 °C
6491 | RE22R2MWMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529
6492 | RE22R2MWMR | Environment | pollution degree | 3 conforming to IEC 60664-1
6493 | RE22R2MWMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
6494 | RE22R2MWMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
6495 | RE22R2MWMR | Environment | relative humidity | 95 % at 25…55 °C
6496 | RE22R2MWMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
6497 | RE22R2MWMR | Offer Sustainability | Sustainable offer status | Green Premium product
6498 | RE22R2MWMR | Offer Sustainability | REACh Regulation | REACh Declaration
6499 | RE22R2MWMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6500 | RE22R2MWMR | Offer Sustainability | Mercury free | Yes
6501 | RE22R2MWMR | Offer Sustainability | RoHS exemption information | Yes
6502 | RE22R2MWMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
6503 | RE22R2MWMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
6504 | RE22R2MWMR | Offer Sustainability | Circularity Profile | End of Life Information
6505 | RE22R2MYMR | Main | range of product | Zelio Time
6506 | RE22R2MYMR | Main | product or component type | Modular timing relay
6507 | RE22R2MYMR | Main | discrete output type | Relay
6508 | RE22R2MYMR | Main | device short name | RE22
6509 | RE22R2MYMR | Main | nominal output current | 8 A
6510 | RE22R2MYMR | Complementary | contacts type and composition | 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free
6511 | RE22R2MYMR | Complementary | time delay type | Ht Dit Qgt D Dt W Ct Dw A Qt Qtt Diw C Wt Di Hw Qg At Aw H
6512 | RE22R2MYMR | Complementary | time delay range | 3...30 min 30...300 min 0.3...3 s 3...30 h 10...100 s 1...10 s 0.05...1 s 30...300 s 30...300 h 3...30 s
6513 | RE22R2MYMR | Complementary | control type | Rotary knob Diagnostic button Potentiometer external
6514 | RE22R2MYMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
6515 | RE22R2MYMR | Complementary | Release input voltage | <= 2.4 V
6516 | RE22R2MYMR | Complementary | voltage range | 0.85...1.1 Us
6517 | RE22R2MYMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
6518 | RE22R2MYMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
6519 | RE22R2MYMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
6520 | RE22R2MYMR | Complementary | housing material | Self-extinguishing
6521 | RE22R2MYMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
6522 | RE22R2MYMR | Complementary | temperature drift | +/- 0.05 %/°C
6523 | RE22R2MYMR | Complementary | voltage drift | +/- 0.2 %/V
6524 | RE22R2MYMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
6525 | RE22R2MYMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
6526 | RE22R2MYMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
6527 | RE22R2MYMR | Complementary | Recovery time | 120 ms on de-energisation
6528 | RE22R2MYMR | Complementary | immunity to microbreaks | 10 ms
6529 | RE22R2MYMR | Complementary | power consumption in VA | 3 VA at 240 V AC
6530 | RE22R2MYMR | Complementary | power consumption in W | 1.5 W at 240 V DC
6531 | RE22R2MYMR | Complementary | switching capacity in VA | 2000 VA
6532 | RE22R2MYMR | Complementary | minimum switching current | 10 mA at 5 V DC
6533 | RE22R2MYMR | Complementary | maximum switching current | 8 A
6534 | RE22R2MYMR | Complementary | maximum switching voltage | 250 V AC
6535 | RE22R2MYMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
6536 | RE22R2MYMR | Complementary | mechanical durability | 10000000 cycles
6537 | RE22R2MYMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
6538 | RE22R2MYMR | Complementary | Power on delay | 100 ms
6539 | RE22R2MYMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
6540 | RE22R2MYMR | Complementary | overvoltage category | III conforming to IEC 60664-1
6541 | RE22R2MYMR | Complementary | safety reliability data | B10d = 160000 MTTFd = 171.2 years
6542 | RE22R2MYMR | Complementary | mounting position | Any position
6543 | RE22R2MYMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
6544 | RE22R2MYMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
6545 | RE22R2MYMR | Complementary | width | 22.5 mm
6546 | RE22R2MYMR | Complementary | net weight | 0.105 kg
6547 | RE22R2MYMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
6548 | RE22R2MYMR | Environment | standards | UL 508 IEC 61812-1
6549 | RE22R2MYMR | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive
6550 | RE22R2MYMR | Environment | product certifications | RCM CE China RoHS EAC CSA CCC UL GL
6551 | RE22R2MYMR | Environment | ambient air temperature for operation | -20…60 °C
6552 | RE22R2MYMR | Environment | ambient air temperature for storage | -40…70 °C
6553 | RE22R2MYMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529
6554 | RE22R2MYMR | Environment | pollution degree | 3 conforming to IEC 60664-1
6555 | RE22R2MYMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
6556 | RE22R2MYMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
6557 | RE22R2MYMR | Environment | relative humidity | 95 % at 25…55 °C
6558 | RE22R2MYMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
6559 | RE22R2MYMR | Offer Sustainability | Sustainable offer status | Green Premium product
6560 | RE22R2MYMR | Offer Sustainability | REACh Regulation | REACh Declaration
6561 | RE22R2MYMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6562 | RE22R2MYMR | Offer Sustainability | Mercury free | Yes
6563 | RE22R2MYMR | Offer Sustainability | RoHS exemption information | Yes
6564 | RE22R2MYMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
6565 | RE22R2MYMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
6566 | RE22R2MYMR | Offer Sustainability | Circularity Profile | End of Life Information
6567 | RE22R2QEMR | Main | range of product | Zelio Time
6568 | RE22R2QEMR | Main | product or component type | Modular timing relay
6569 | RE22R2QEMR | Main | discrete output type | Relay
6570 | RE22R2QEMR | Main | device short name | RE22
6571 | RE22R2QEMR | Main | nominal output current | 8 A
6572 | RE22R2QEMR | Complementary | contacts type and composition | 2 C/O timed contact, cadmium free
6573 | RE22R2QEMR | Complementary | time delay type | Qe
6574 | RE22R2QEMR | Complementary | time delay range | 0.3...30 s
6575 | RE22R2QEMR | Complementary | control type | Rotary knob Diagnostic button
6576 | RE22R2QEMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
6577 | RE22R2QEMR | Complementary | Release input voltage | <= 2.4 V
6578 | RE22R2QEMR | Complementary | voltage range | 0.85...1.1 Us
6579 | RE22R2QEMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
6580 | RE22R2QEMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
6581 | RE22R2QEMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
6582 | RE22R2QEMR | Complementary | housing material | Self-extinguishing
6583 | RE22R2QEMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
6584 | RE22R2QEMR | Complementary | temperature drift | +/- 0.05 %/°C
6585 | RE22R2QEMR | Complementary | voltage drift | +/- 0.2 %/V
6586 | RE22R2QEMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
6587 | RE22R2QEMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
6588 | RE22R2QEMR | Complementary | Recovery time | 120 ms on de-energisation
6589 | RE22R2QEMR | Complementary | immunity to microbreaks | 10 ms
6590 | RE22R2QEMR | Complementary | power consumption in VA | 3 VA at 240 V AC
6591 | RE22R2QEMR | Complementary | power consumption in W | 1.5 W at 240 V DC
6592 | RE22R2QEMR | Complementary | switching capacity in VA | 2000 VA
6593 | RE22R2QEMR | Complementary | minimum switching current | 10 mA at 5 V DC
6594 | RE22R2QEMR | Complementary | maximum switching current | 8 A
6595 | RE22R2QEMR | Complementary | maximum switching voltage | 250 V AC
6596 | RE22R2QEMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
6597 | RE22R2QEMR | Complementary | mechanical durability | 10000000 cycles
6598 | RE22R2QEMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
6599 | RE22R2QEMR | Complementary | Power on delay | 100 ms
6600 | RE22R2QEMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
6601 | RE22R2QEMR | Complementary | overvoltage category | III conforming to IEC 60664-1
6602 | RE22R2QEMR | Complementary | safety reliability data | B10d = 320000 MTTFd = 353.8 years
6603 | RE22R2QEMR | Complementary | mounting position | Any position
6604 | RE22R2QEMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
6605 | RE22R2QEMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
6606 | RE22R2QEMR | Complementary | width | 22.5 mm
6607 | RE22R2QEMR | Complementary | net weight | 0.09 kg
6608 | RE22R2QEMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
6609 | RE22R2QEMR | Environment | standards | IEC 61812-1 UL 508
6610 | RE22R2QEMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
6611 | RE22R2QEMR | Environment | product certifications | CE CSA GL China RoHS EAC UL RCM CCC
6612 | RE22R2QEMR | Environment | ambient air temperature for operation | -20…60 °C
6613 | RE22R2QEMR | Environment | ambient air temperature for storage | -40…70 °C
6614 | RE22R2QEMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529
6615 | RE22R2QEMR | Environment | pollution degree | 3 conforming to IEC 60664-1
6616 | RE22R2QEMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
6617 | RE22R2QEMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
6618 | RE22R2QEMR | Environment | relative humidity | 95 % at 25…55 °C
6619 | RE22R2QEMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
6620 | RE22R2QEMR | Offer Sustainability | Sustainable offer status | Green Premium product
6621 | RE22R2QEMR | Offer Sustainability | REACh Regulation | REACh Declaration
6622 | RE22R2QEMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6623 | RE22R2QEMR | Offer Sustainability | Mercury free | Yes
6624 | RE22R2QEMR | Offer Sustainability | RoHS exemption information | Yes
6625 | RE22R2QEMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
6626 | RE22R2QEMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
6627 | RE22R2QEMR | Offer Sustainability | Circularity Profile | End of Life Information
6628 | RE22R2QEMT | Main | range of product | Zelio Time
6629 | RE22R2QEMT | Main | product or component type | Modular timing relay
6630 | RE22R2QEMT | Main | discrete output type | Relay
6631 | RE22R2QEMT | Main | device short name | RE22
6632 | RE22R2QEMT | Main | nominal output current | 8 A
6633 | RE22R2QEMT | Complementary | contacts type and composition | 2 C/O timed contact, cadmium free
6634 | RE22R2QEMT | Complementary | time delay type | Qe
6635 | RE22R2QEMT | Complementary | time delay range | 0.3...30 s
6636 | RE22R2QEMT | Complementary | control type | Rotary knob Diagnostic button
6637 | RE22R2QEMT | Complementary | [Us] rated supply voltage | 380...415 V AC 50/60 Hz
6638 | RE22R2QEMT | Complementary | Release input voltage | <= 38 V
6639 | RE22R2QEMT | Complementary | voltage range | 0.85...1.16 Us
6640 | RE22R2QEMT | Complementary | supply frequency | 50...60 Hz +/- 5 %
6641 | RE22R2QEMT | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
6642 | RE22R2QEMT | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
6643 | RE22R2QEMT | Complementary | housing material | Self-extinguishing
6644 | RE22R2QEMT | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
6645 | RE22R2QEMT | Complementary | temperature drift | +/- 0.05 %/°C
6646 | RE22R2QEMT | Complementary | voltage drift | +/- 0.2 %/V
6647 | RE22R2QEMT | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
6648 | RE22R2QEMT | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
6649 | RE22R2QEMT | Complementary | Recovery time | 120 ms on de-energisation
6650 | RE22R2QEMT | Complementary | immunity to microbreaks | 10 ms
6651 | RE22R2QEMT | Complementary | power consumption in VA | 15 VA at 380 V AC
6652 | RE22R2QEMT | Complementary | switching capacity in VA | 2000 VA
6653 | RE22R2QEMT | Complementary | minimum switching current | 10 mA at 5 V DC
6654 | RE22R2QEMT | Complementary | maximum switching current | 8 A
6655 | RE22R2QEMT | Complementary | maximum switching voltage | 250 V AC
6656 | RE22R2QEMT | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
6657 | RE22R2QEMT | Complementary | mechanical durability | 10000000 cycles
6658 | RE22R2QEMT | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
6659 | RE22R2QEMT | Complementary | Power on delay | 100 ms
6660 | RE22R2QEMT | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
6661 | RE22R2QEMT | Complementary | overvoltage category | III conforming to IEC 60664-1
6662 | RE22R2QEMT | Complementary | safety reliability data | B10d = 250000 MTTFd = 273.9 years
6663 | RE22R2QEMT | Complementary | mounting position | Any position
6664 | RE22R2QEMT | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
6665 | RE22R2QEMT | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
6666 | RE22R2QEMT | Complementary | width | 22.5 mm
6667 | RE22R2QEMT | Complementary | net weight | 0.09 kg
6668 | RE22R2QEMT | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
6669 | RE22R2QEMT | Environment | standards | IEC 61812-1 UL 508
6670 | RE22R2QEMT | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
6671 | RE22R2QEMT | Environment | product certifications | EAC GL CSA China RoHS UL CCC RCM CE
6672 | RE22R2QEMT | Environment | ambient air temperature for operation | -20…60 °C
6673 | RE22R2QEMT | Environment | ambient air temperature for storage | -40…70 °C
6674 | RE22R2QEMT | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529
6675 | RE22R2QEMT | Environment | pollution degree | 3 conforming to IEC 60664-1
6676 | RE22R2QEMT | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
6677 | RE22R2QEMT | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
6678 | RE22R2QEMT | Environment | relative humidity | 95 % at 25…55 °C
6679 | RE22R2QEMT | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Surge immunity test - test level: 2 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 4 kV level 3 (common mode) conforming to IEC 61000-4-5
6680 | RE22R2QEMT | Offer Sustainability | Sustainable offer status | Green Premium product
6681 | RE22R2QEMT | Offer Sustainability | REACh Regulation | REACh Declaration
6682 | RE22R2QEMT | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6683 | RE22R2QEMT | Offer Sustainability | Mercury free | Yes
6684 | RE22R2QEMT | Offer Sustainability | RoHS exemption information | Yes
6685 | RE22R2QEMT | Offer Sustainability | China RoHS Regulation | China RoHS declaration
6686 | RE22R2QEMT | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
6687 | RE22R2QEMT | Offer Sustainability | Circularity Profile | End of Life Information
6688 | RE22R2QGMR | Main | range of product | Zelio Time
6689 | RE22R2QGMR | Main | product or component type | Modular timing relay
6690 | RE22R2QGMR | Main | discrete output type | Relay
6691 | RE22R2QGMR | Main | device short name | RE22
6692 | RE22R2QGMR | Main | nominal output current | 8 A
6693 | RE22R2QGMR | Complementary | contacts type and composition | 2 C/O timed contact, cadmium free
6694 | RE22R2QGMR | Complementary | time delay type | Qg
6695 | RE22R2QGMR | Complementary | time delay range | 3...30 s 0.05...1 s 30...300 s 30...300 min 0.3...3 s 1...10 s 3...30 h 10...100 s 30...300 h 3...30 min
6696 | RE22R2QGMR | Complementary | control type | Rotary knob Diagnostic button
6697 | RE22R2QGMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
6698 | RE22R2QGMR | Complementary | Release input voltage | <= 2.4 V
6699 | RE22R2QGMR | Complementary | voltage range | 0.85...1.1 Us
6700 | RE22R2QGMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
6701 | RE22R2QGMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
6702 | RE22R2QGMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
6703 | RE22R2QGMR | Complementary | housing material | Self-extinguishing
6704 | RE22R2QGMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
6705 | RE22R2QGMR | Complementary | temperature drift | +/- 0.05 %/°C
6706 | RE22R2QGMR | Complementary | voltage drift | +/- 0.2 %/V
6707 | RE22R2QGMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
6708 | RE22R2QGMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
6709 | RE22R2QGMR | Complementary | Recovery time | 120 ms on de-energisation
6710 | RE22R2QGMR | Complementary | immunity to microbreaks | 10 ms
6711 | RE22R2QGMR | Complementary | power consumption in VA | 3 VA at 240 V AC
6712 | RE22R2QGMR | Complementary | power consumption in W | 1.5 W at 240 V DC
6713 | RE22R2QGMR | Complementary | switching capacity in VA | 2000 VA
6714 | RE22R2QGMR | Complementary | minimum switching current | 10 mA at 5 V DC
6715 | RE22R2QGMR | Complementary | maximum switching current | 8 A
6716 | RE22R2QGMR | Complementary | maximum switching voltage | 250 V AC
6717 | RE22R2QGMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
6718 | RE22R2QGMR | Complementary | mechanical durability | 10000000 cycles
6719 | RE22R2QGMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
6720 | RE22R2QGMR | Complementary | Power on delay | 100 ms
6721 | RE22R2QGMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
6722 | RE22R2QGMR | Complementary | overvoltage category | III conforming to IEC 60664-1
6723 | RE22R2QGMR | Complementary | safety reliability data | MTTFd = 342.4 years B10d = 320000
6724 | RE22R2QGMR | Complementary | mounting position | Any position
6725 | RE22R2QGMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
6726 | RE22R2QGMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
6727 | RE22R2QGMR | Complementary | width | 22.5 mm
6728 | RE22R2QGMR | Complementary | net weight | 0.105 kg
6729 | RE22R2QGMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
6730 | RE22R2QGMR | Environment | standards | UL 508 IEC 61812-1
6731 | RE22R2QGMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
6732 | RE22R2QGMR | Environment | product certifications | CCC CSA RCM GL EAC CE UL China RoHS
6733 | RE22R2QGMR | Environment | ambient air temperature for operation | -20…60 °C
6734 | RE22R2QGMR | Environment | ambient air temperature for storage | -40…70 °C
6735 | RE22R2QGMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529
6736 | RE22R2QGMR | Environment | pollution degree | 3 conforming to IEC 60664-1
6737 | RE22R2QGMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
6738 | RE22R2QGMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
6739 | RE22R2QGMR | Environment | relative humidity | 95 % at 25…55 °C
6740 | RE22R2QGMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
6741 | RE22R2QGMR | Offer Sustainability | Sustainable offer status | Green Premium product
6742 | RE22R2QGMR | Offer Sustainability | REACh Regulation | REACh Declaration
6743 | RE22R2QGMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6744 | RE22R2QGMR | Offer Sustainability | Mercury free | Yes
6745 | RE22R2QGMR | Offer Sustainability | RoHS exemption information | Yes
6746 | RE22R2QGMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
6747 | RE22R2QGMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
6748 | RE22R2QGMR | Offer Sustainability | Circularity Profile | End of Life Information
6749 | RE22R2QTMR | Main | range of product | Zelio Time
6750 | RE22R2QTMR | Main | product or component type | Modular timing relay
6751 | RE22R2QTMR | Main | discrete output type | Relay
6752 | RE22R2QTMR | Main | device short name | RE22
6753 | RE22R2QTMR | Main | nominal output current | 8 A
6754 | RE22R2QTMR | Complementary | contacts type and composition | 2 C/O timed contact, cadmium free
6755 | RE22R2QTMR | Complementary | time delay type | Qt
6756 | RE22R2QTMR | Complementary | time delay range | 1...10 s 3...30 s 10...100 s 30...300 min 0.05...1 s 3...30 min 0.3...3 s 30...300 s 3...30 h 30...300 h
6757 | RE22R2QTMR | Complementary | control type | Rotary knob Diagnostic button
6758 | RE22R2QTMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
6759 | RE22R2QTMR | Complementary | Release input voltage | <= 2.4 V
6760 | RE22R2QTMR | Complementary | voltage range | 0.85...1.1 Us
6761 | RE22R2QTMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
6762 | RE22R2QTMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
6763 | RE22R2QTMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
6764 | RE22R2QTMR | Complementary | housing material | Self-extinguishing
6765 | RE22R2QTMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
6766 | RE22R2QTMR | Complementary | temperature drift | +/- 0.05 %/°C
6767 | RE22R2QTMR | Complementary | voltage drift | +/- 0.2 %/V
6768 | RE22R2QTMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
6769 | RE22R2QTMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
6770 | RE22R2QTMR | Complementary | Recovery time | 120 ms on de-energisation
6771 | RE22R2QTMR | Complementary | immunity to microbreaks | 10 ms
6772 | RE22R2QTMR | Complementary | power consumption in VA | 3 VA at 240 V AC
6773 | RE22R2QTMR | Complementary | power consumption in W | 1.5 W at 240 V DC
6774 | RE22R2QTMR | Complementary | switching capacity in VA | 2000 VA
6775 | RE22R2QTMR | Complementary | minimum switching current | 10 mA at 5 V DC
6776 | RE22R2QTMR | Complementary | maximum switching current | 8 A
6777 | RE22R2QTMR | Complementary | maximum switching voltage | 250 V AC
6778 | RE22R2QTMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
6779 | RE22R2QTMR | Complementary | mechanical durability | 10000000 cycles
6780 | RE22R2QTMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
6781 | RE22R2QTMR | Complementary | Power on delay | 100 ms
6782 | RE22R2QTMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
6783 | RE22R2QTMR | Complementary | overvoltage category | III conforming to IEC 60664-1
6784 | RE22R2QTMR | Complementary | safety reliability data | MTTFd = 342.4 years B10d = 320000
6785 | RE22R2QTMR | Complementary | mounting position | Any position
6786 | RE22R2QTMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
6787 | RE22R2QTMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
6788 | RE22R2QTMR | Complementary | width | 22.5 mm
6789 | RE22R2QTMR | Complementary | net weight | 0.105 kg
6790 | RE22R2QTMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
6791 | RE22R2QTMR | Environment | standards | IEC 61812-1 UL 508
6792 | RE22R2QTMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
6793 | RE22R2QTMR | Environment | product certifications | CCC GL UL EAC RCM CSA China RoHS CE
6794 | RE22R2QTMR | Environment | ambient air temperature for operation | -20…60 °C
6795 | RE22R2QTMR | Environment | ambient air temperature for storage | -40…70 °C
6796 | RE22R2QTMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529
6797 | RE22R2QTMR | Environment | pollution degree | 3 conforming to IEC 60664-1
6798 | RE22R2QTMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
6799 | RE22R2QTMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
6800 | RE22R2QTMR | Environment | relative humidity | 95 % at 25…55 °C
6801 | RE22R2QTMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
6802 | RE22R2QTMR | Offer Sustainability | Sustainable offer status | Green Premium product
6803 | RE22R2QTMR | Offer Sustainability | REACh Regulation | REACh Declaration
6804 | RE22R2QTMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6805 | RE22R2QTMR | Offer Sustainability | Mercury free | Yes
6806 | RE22R2QTMR | Offer Sustainability | RoHS exemption information | Yes
6807 | RE22R2QTMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
6808 | RE22R2QTMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
6809 | RE22R2QTMR | Offer Sustainability | Circularity Profile | End of Life Information
6810 | RENF22R2MMW | Main | range of product | Zelio Time
6811 | RENF22R2MMW | Main | product or component type | Modular timing relay
6812 | RENF22R2MMW | Main | device short name | RENF22
6813 | RENF22R2MMW | Main | Supported OS | Android
6814 | RENF22R2MMW | Main | software version | V4.4 and above
6815 | RENF22R2MMW | Main | App for product | Zelio NFC (downloadable from Google Play store)
6816 | RENF22R2MMW | Complementary | discrete output type | Relay
6817 | RENF22R2MMW | Complementary | nominal output current | 8 A
6818 | RENF22R2MMW | Complementary | contacts type and composition | 2 C/O timed contact, cadmium free 1 C/O timed and instantaneous contact, cadmium free
6819 | RENF22R2MMW | Complementary | time delay type | Tt Ak Ah Di Pt H At Dt Ad A Qt N Li L Qtt O Ht Lit C Lt W Tl P Ac Dit B D Bw
6820 | RENF22R2MMW | Complementary | time delay range | 0.1 s...999 h
6821 | RENF22R2MMW | Complementary | product compatibility | NFC enabled mobile device
6822 | RENF22R2MMW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC
6823 | RENF22R2MMW | Complementary | Release input voltage | <= 2.4 V
6824 | RENF22R2MMW | Complementary | voltage range | 0.85...1.1 Un
6825 | RENF22R2MMW | Complementary | Maximum RF power transmitted | 0.0002 mW
6826 | RENF22R2MMW | Complementary | NFC operating frequency | 13.56 MHz
6827 | RENF22R2MMW | Complementary | supply frequency | 50...60 Hz +/- 5 %
6828 | RENF22R2MMW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
6829 | RENF22R2MMW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 0.60…0.99 N.m conforming to IEC 60947-1
6830 | RENF22R2MMW | Complementary | housing material | Self-extinguishing
6831 | RENF22R2MMW | Complementary | repeat accuracy | +/- 0.2 % for 10 s...999 h time delay range +/- 0.5 % for 100 ms...10 s time delay range
6832 | RENF22R2MMW | Complementary | temperature drift | +/- 0.05 %/°C
6833 | RENF22R2MMW | Complementary | voltage drift | +/- 0.2 %/V
6834 | RENF22R2MMW | Complementary | setting accuracy of time delay | +/- 1 % for 1...999 h time delay range at 25 °C +/- 2 % for 1 h time delay range at 25 °C +/- 20 ms for 100 ms...10 s time delay range at 25 °C
6835 | RENF22R2MMW | Complementary | Control signal pulse width | 100 ms with load in parallel 60 ms no-load
6836 | RENF22R2MMW | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
6837 | RENF22R2MMW | Complementary | Recovery time | 120 ms on de-energisation
6838 | RENF22R2MMW | Complementary | power consumption in VA | 3 VA at 240 V AC
6839 | RENF22R2MMW | Complementary | power consumption in W | 1.5 W at 240 V DC 0.6 W at 24 V DC
6840 | RENF22R2MMW | Complementary | switching capacity in VA | 2000 VA
6841 | RENF22R2MMW | Complementary | minimum switching current | 10 mA at 5 V
6842 | RENF22R2MMW | Complementary | maximum switching current | 8 A
6843 | RENF22R2MMW | Complementary | maximum switching voltage | 250 V
6844 | RENF22R2MMW | Complementary | electrical durability | 100000 cycles for resistive load, 8 A at 250 V, AC
6845 | RENF22R2MMW | Complementary | mechanical durability | 10000000 cycles
6846 | RENF22R2MMW | Complementary | Rated impulse withstand voltage | 5 kV 1.2/50 µs conforming to IEC 60664-1
6847 | RENF22R2MMW | Complementary | power on delay | 100 ms
6848 | RENF22R2MMW | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
6849 | RENF22R2MMW | Complementary | overvoltage category | III conforming to IEC 60664-1
6850 | RENF22R2MMW | Complementary | safety reliability data | MTTFd = 227.5 years 100 % duty cycle continuous operating condition at 30 °C
6851 | RENF22R2MMW | Complementary | mounting position | Any position
6852 | RENF22R2MMW | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
6853 | RENF22R2MMW | Complementary | status LED | LED Un: (steady), green for power ON LED R1: (steady), amber for relay energised LED R2: (steady), amber for relay energised LED pairing: (steady), green for communication status LED Un: (fast blinking), green for diagnosis mode LED R1: (blinking), amber for timing in progress LED R2: (blinking), amber for timing in progress
6854 | RENF22R2MMW | Complementary | Maximum communication distance | 10 mm
6855 | RENF22R2MMW | Complementary | response time | 2 s
6856 | RENF22R2MMW | Complementary | width | 22.5 mm
6857 | RENF22R2MMW | Complementary | net weight | 0.0904 kg
6858 | RENF22R2MMW | Environment | immunity to microbreaks | 10 ms
6859 | RENF22R2MMW | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz with between relay output and power supply with basic insulation with basic insulation
6860 | RENF22R2MMW | Environment | standards | EN 61000-6-1 EN 61000-6-2 EN 61000-6-4 EN 61812-1 EN 61000-6-3
6861 | RENF22R2MMW | Environment | directives | 2014/35/EU - low voltage directive 2014/53/EU - radio equipment directive 2014/30/EU - electromagnetic compatibility
6862 | RENF22R2MMW | Environment | product certifications | CE CSA KC UL CCC EAC DNV-GL
6863 | RENF22R2MMW | Environment | ambient air temperature for operation | -20…60 °C
6864 | RENF22R2MMW | Environment | ambient air temperature for storage | -40…70 °C
6865 | RENF22R2MMW | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP40 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529
6866 | RENF22R2MMW | Environment | pollution degree | 3 conforming to IEC 60664-1
6867 | RENF22R2MMW | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
6868 | RENF22R2MMW | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
6869 | RENF22R2MMW | Environment | relative humidity | 95 % at 25…55 °C
6870 | RENF22R2MMW | Environment | electromagnetic compatibility | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Radiated emission class B conforming to EN 55022 Conducted emission class A conforming to EN 55022 Electromagnetic field immunity test - test level: 3 V/m level 2 (1.4 GHz...2 GHz) conforming to IEC 61000-4-3 Electromagnetic field immunity test - test level: 1 V/m level 1 (2...2.7 GHz) conforming to IEC 61000-4-3
6871 | RENF22R2MMW | Offer Sustainability | Sustainable offer status | Green Premium product
6872 | RENF22R2MMW | Offer Sustainability | REACh Regulation | REACh Declaration
6873 | RENF22R2MMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6874 | RENF22R2MMW | Offer Sustainability | Mercury free | Yes
6875 | RENF22R2MMW | Offer Sustainability | RoHS exemption information | Yes
6876 | RENF22R2MMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
6877 | RENF22R2MMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
6878 | RENF22R2MMW | Offer Sustainability | Circularity Profile | End of Life Information
6879 | RE48AML12MW | Main | range of product | Zelio Time
6880 | RE48AML12MW | Main | product or component type | Electronic timing relay
6881 | RE48AML12MW | Main | electrical connection | Plug-in sub-base 11 pin(s)
6882 | RE48AML12MW | Main | discrete output type | Relay
6883 | RE48AML12MW | Main | contacts type and composition | 2 C/O timed contacts, AgNi (cadmium free)
6884 | RE48AML12MW | Main | component name | RE48A
6885 | RE48AML12MW | Main | time delay type | B Di A C
6886 | RE48AML12MW | Main | time delay range | 0.5...30 s 5...300 s 0.2...12 min 0.5...30 h 2...120 s 0.05...3 s 0.2...12 s 0.02...1.2 s 2...120 min 5...300 min 0.5...30 min 5...300 h 2...120 h 0.2...12 h
6887 | RE48AML12MW | Main | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
6888 | RE48AML12MW | Main | voltage range | 0.85...1.1 Us AC 0.9...1.1 Us DC
6889 | RE48AML12MW | Main | [In] rated current | 5 A
6890 | RE48AML12MW | Complementary | product front plate size | 48 x 48 mm
6891 | RE48AML12MW | Complementary | control type | Selector switch front panel
6892 | RE48AML12MW | Complementary | housing material | Self-extinguishing
6893 | RE48AML12MW | Complementary | repeat accuracy | +/- 0.2 % of the maximum setting value conforming to IEC 61812-1
6894 | RE48AML12MW | Complementary | temperature drift | +/- 0.02 %/°C of the maximum setting value conforming to IEC 61812-1
6895 | RE48AML12MW | Complementary | voltage drift | +/- 0.2 %/V of the maximum setting value at 48...240 V +/- 1 %/V of the maximum setting value at 24...48 V
6896 | RE48AML12MW | Complementary | setting accuracy of time delay | +/- 5 % of full scale at 25 °C conforming to IEC 61812-1
6897 | RE48AML12MW | Complementary | minimum pulse duration | 20 ms
6898 | RE48AML12MW | Complementary | reset time | 25 ms on de-energisation
6899 | RE48AML12MW | Complementary | pick up duration | 55 ms
6900 | RE48AML12MW | Complementary | on-load factor | 100 %
6901 | RE48AML12MW | Complementary | power consumption in VA | 1.1 VA at 24 V 4.8 VA at 240 V
6902 | RE48AML12MW | Complementary | power consumption in W | 0.5 W at 24 V 1.7 W at 240 V
6903 | RE48AML12MW | Complementary | breaking capacity | 1250 VA
6904 | RE48AML12MW | Complementary | minimum switching current | 100 mA
6905 | RE48AML12MW | Complementary | maximum switching current | 5 A
6906 | RE48AML12MW | Complementary | maximum switching voltage | 250 V AC/DC
6907 | RE48AML12MW | Complementary | electrical durability | 100000 cycles
6908 | RE48AML12MW | Complementary | mechanical durability | 30000000 cycles
6909 | RE48AML12MW | Complementary | output voltage | 240 V at 5 A AC-12 30 V at 2 A DC-13 240 V at 1.5 A AC-15
6910 | RE48AML12MW | Complementary | marking | CE
6911 | RE48AML12MW | Complementary | surge withstand | 1 kV differential mode conforming to IEC 61000-4-5 level 3 2 kV common mode conforming to IEC 61000-4-5 level 3
6912 | RE48AML12MW | Complementary | mounting support | Base mounted: socket Panel mounted: system supplied with the product
6913 | RE48AML12MW | Complementary | local signalling | 1 LED (yellow) for output relay state LED indicator (green) for flashing: relay energised timing in progress LED indicator (green) for on steady: relay energised, no timing in progress
6914 | RE48AML12MW | Complementary | net weight | 0.14 kg
6915 | RE48AML12MW | Environment | humidity drift | +/- 0.05 %/%RH of the maximum setting value conforming to IEC 61812-1
6916 | RE48AML12MW | Environment | immunity to microbreaks | 10 ms
6917 | RE48AML12MW | Environment | dielectric strength | 1 kV 1 mA/1 minute conforming to IEC 61812-1
6918 | RE48AML12MW | Environment | protection against electric shocks | 4 kV class III conforming to IEC 60664-1 4 kV class III conforming to IEC 61812-1
6919 | RE48AML12MW | Environment | standards | IEC 61812-1 EN 50081-1/2 93/68/EEC 89/336/EEC EN 50082-1/2 IEC 60669-2-3 73/23/EEC
6920 | RE48AML12MW | Environment | product certifications | GL UL CULus CSA C-Tick
6921 | RE48AML12MW | Environment | ambient air temperature for storage | -40…70 °C
6922 | RE48AML12MW | Environment | ambient air temperature for operation | -20…50 °C
6923 | RE48AML12MW | Environment | IP degree of protection | IP40 (housing) conforming to IEC 60529 IP50 (front face) conforming to IEC 60529
6924 | RE48AML12MW | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
6925 | RE48AML12MW | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-3
6926 | RE48AML12MW | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3
6927 | RE48AML12MW | Environment | resistance to electromagnetic fields | 10 V/m 26 MHz to 1 GHz conforming to IEC 61000-4-3 level 3
6928 | RE48AML12MW | Environment | resistance to fast transients | 2 kV (capacitive connecting clip) conforming to EN/IEC 61000-4-4 level 4 4 kV (direct) conforming to EN/IEC 61000-4-4 level 4
6929 | RE48AML12MW | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
6930 | RE48AML12MW | Environment | immunity to voltage dips | 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 95 % / 5 s conforming to EN/IEC 61000-4-11
6931 | RE48AML12MW | Environment | disturbance radiated/conducted | Class B 0.15...30 MHz conforming to EN 55022 (EN 55011 group 1)
6932 | RE48AML12MW | Offer Sustainability | Sustainable offer status | Green Premium product
6933 | RE48AML12MW | Offer Sustainability | REACh Regulation | REACh Declaration
6934 | RE48AML12MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6935 | RE48AML12MW | Offer Sustainability | Mercury free | Yes
6936 | RE48AML12MW | Offer Sustainability | RoHS exemption information | Yes
6937 | RE48AML12MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
6938 | RE48AML12MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
6939 | RE48AML12MW | Offer Sustainability | Circularity Profile | End of Life Information
6940 | RE48AML12MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
6941 | RE48AML12MW | Contractual warranty | Warranty | 18 months
6942 | RE48ATM12MW | Main | range of product | Zelio Time
6943 | RE48ATM12MW | Main | product or component type | Electronic timing relay
6944 | RE48ATM12MW | Main | electrical connection | Plug-in sub-base 8 pin(s)
6945 | RE48ATM12MW | Main | discrete output type | Relay
6946 | RE48ATM12MW | Main | contacts type and composition | 2 C/O timed contacts, AgNi (cadmium free)
6947 | RE48ATM12MW | Main | component name | RE48
6948 | RE48ATM12MW | Main | time delay type | A
6949 | RE48ATM12MW | Main | time delay range | 5...300 h 2...120 min 0.5...30 h 0.2...12 h 0.2...12 min 0.2...12 s 0.5...30 min 2...120 h 2...120 s 0.02...1.2 s 0.5...30 s 5...300 s 0.05...3 s 5...300 min
6950 | RE48ATM12MW | Main | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
6951 | RE48ATM12MW | Main | voltage range | 0.85...1.1 Us AC 0.9...1.1 Us DC
6952 | RE48ATM12MW | Main | [In] rated current | 5 A
6953 | RE48ATM12MW | Complementary | product front plate size | 48 x 48 mm
6954 | RE48ATM12MW | Complementary | control type | Selector switch front panel
6955 | RE48ATM12MW | Complementary | housing material | Self-extinguishing
6956 | RE48ATM12MW | Complementary | repeat accuracy | +/- 0.2 % of the maximum setting value conforming to IEC 61812-1
6957 | RE48ATM12MW | Complementary | temperature drift | +/- 0.02 %/°C of the maximum setting value conforming to IEC 61812-1
6958 | RE48ATM12MW | Complementary | voltage drift | +/- 0.2 %/V of the maximum setting value at 48...240 V +/- 1 %/V of the maximum setting value at 24...48 V
6959 | RE48ATM12MW | Complementary | setting accuracy of time delay | +/- 5 % of full scale at 25 °C conforming to IEC 61812-1
6960 | RE48ATM12MW | Complementary | minimum pulse duration | 20 ms
6961 | RE48ATM12MW | Complementary | reset time | 25 ms on de-energisation
6962 | RE48ATM12MW | Complementary | pick up duration | 55 ms
6963 | RE48ATM12MW | Complementary | on-load factor | 100 %
6964 | RE48ATM12MW | Complementary | power consumption in VA | 1.1 VA at 24 V 4.8 VA at 240 V
6965 | RE48ATM12MW | Complementary | power consumption in W | 0.5 W at 24 V 1.7 W at 240 V
6966 | RE48ATM12MW | Complementary | breaking capacity | 1250 VA
6967 | RE48ATM12MW | Complementary | minimum switching current | 100 mA
6968 | RE48ATM12MW | Complementary | maximum switching current | 5 A
6969 | RE48ATM12MW | Complementary | maximum switching voltage | 250 V AC/DC
6970 | RE48ATM12MW | Complementary | electrical durability | 100000 cycles
6971 | RE48ATM12MW | Complementary | mechanical durability | 30000000 cycles
6972 | RE48ATM12MW | Complementary | output voltage | 240 V at 5 A AC-12 30 V at 2 A DC-13 240 V at 1.5 A AC-15
6973 | RE48ATM12MW | Complementary | marking | CE
6974 | RE48ATM12MW | Complementary | surge withstand | 1 kV differential mode conforming to IEC 61000-4-5 level 3 2 kV common mode conforming to IEC 61000-4-5 level 3
6975 | RE48ATM12MW | Complementary | mounting support | Panel mounted: system supplied with the product Base mounted: socket
6976 | RE48ATM12MW | Complementary | local signalling | 1 LED (yellow) for output relay state LED indicator (green) for flashing: relay energised timing in progress LED indicator (green) for on steady: relay energised, no timing in progress
6977 | RE48ATM12MW | Complementary | net weight | 0.14 kg
6978 | RE48ATM12MW | Environment | humidity drift | +/- 0.05 %/%RH of the maximum setting value conforming to IEC 61812-1
6979 | RE48ATM12MW | Environment | immunity to microbreaks | 10 ms
6980 | RE48ATM12MW | Environment | dielectric strength | 1 kV 1 mA/1 minute conforming to IEC 61812-1
6981 | RE48ATM12MW | Environment | protection against electric shocks | 4 kV class III conforming to IEC 60664-1 4 kV class III conforming to IEC 61812-1
6982 | RE48ATM12MW | Environment | standards | 73/23/EEC 93/68/EEC EN 50082-1/2 89/336/EEC EN 50081-1/2 IEC 61812-1 IEC 60669-2-3
6983 | RE48ATM12MW | Environment | product certifications | GL UL CULus C-Tick CSA
6984 | RE48ATM12MW | Environment | ambient air temperature for storage | -40…70 °C
6985 | RE48ATM12MW | Environment | ambient air temperature for operation | -20…50 °C
6986 | RE48ATM12MW | Environment | IP degree of protection | IP40 (housing) conforming to IEC 60529 IP50 (front face) conforming to IEC 60529
6987 | RE48ATM12MW | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
6988 | RE48ATM12MW | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-3
6989 | RE48ATM12MW | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3
6990 | RE48ATM12MW | Environment | resistance to electromagnetic fields | 10 V/m 26 MHz to 1 GHz conforming to IEC 61000-4-3 level 3
6991 | RE48ATM12MW | Environment | resistance to fast transients | 2 kV (capacitive connecting clip) conforming to EN/IEC 61000-4-4 level 4 4 kV (direct) conforming to EN/IEC 61000-4-4 level 4
6992 | RE48ATM12MW | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
6993 | RE48ATM12MW | Environment | immunity to voltage dips | 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 95 % / 5 s conforming to EN/IEC 61000-4-11
6994 | RE48ATM12MW | Environment | disturbance radiated/conducted | Class B 0.15...30 MHz conforming to EN 55022 (EN 55011 group 1)
6995 | RE48ATM12MW | Offer Sustainability | Sustainable offer status | Green Premium product
6996 | RE48ATM12MW | Offer Sustainability | REACh Regulation | REACh Declaration
6997 | RE48ATM12MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
6998 | RE48ATM12MW | Offer Sustainability | Mercury free | Yes
6999 | RE48ATM12MW | Offer Sustainability | RoHS exemption information | Yes
7000 | RE48ATM12MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7001 | RE48ATM12MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7002 | RE48ATM12MW | Offer Sustainability | Circularity Profile | End of Life Information
7003 | RE48ATM12MW | Contractual warranty | Warranty | 18 months
7004 | RE48AMH13MW | Main | range of product | Zelio Time
7005 | RE48AMH13MW | Main | product or component type | Electronic timing relay
7006 | RE48AMH13MW | Main | electrical connection | Plug-in sub-base 8 pin(s)
7007 | RE48AMH13MW | Main | discrete output type | Relay
7008 | RE48AMH13MW | Main | contacts type and composition | 1 C/O + 1 C/O timed or instantaneous contact, AgNi (cadmium free)
7009 | RE48AMH13MW | Main | component name | RE48
7010 | RE48AMH13MW | Main | time delay type | H1 A2 A1 H2
7011 | RE48AMH13MW | Main | time delay range | 2...120 h 5...300 min 0.2...12 min 2...120 s 0.2...12 h 0.02...1.2 s 0.5...30 h 0.2...12 s 5...300 h 0.5...30 s 0.05...3 s 5...300 s 2...120 min 0.5...30 min
7012 | RE48AMH13MW | Main | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
7013 | RE48AMH13MW | Main | voltage range | 0.85...1.1 Us AC 0.9...1.1 Us DC
7014 | RE48AMH13MW | Main | [In] rated current | 5 A
7015 | RE48AMH13MW | Complementary | product front plate size | 48 x 48 mm
7016 | RE48AMH13MW | Complementary | control type | Selector switch front panel
7017 | RE48AMH13MW | Complementary | housing material | Self-extinguishing
7018 | RE48AMH13MW | Complementary | repeat accuracy | +/- 0.2 % of the maximum setting value conforming to IEC 61812-1
7019 | RE48AMH13MW | Complementary | temperature drift | +/- 0.02 %/°C of the maximum setting value conforming to IEC 61812-1
7020 | RE48AMH13MW | Complementary | voltage drift | +/- 0.2 %/V of the maximum setting value at 48...240 V +/- 1 %/V of the maximum setting value at 24...48 V
7021 | RE48AMH13MW | Complementary | setting accuracy of time delay | +/- 5 % of full scale at 25 °C conforming to IEC 61812-1
7022 | RE48AMH13MW | Complementary | minimum pulse duration | 20 ms
7023 | RE48AMH13MW | Complementary | reset time | 25 ms on de-energisation
7024 | RE48AMH13MW | Complementary | pick up duration | 55 ms
7025 | RE48AMH13MW | Complementary | on-load factor | 100 %
7026 | RE48AMH13MW | Complementary | power consumption in VA | 1.1 VA at 24 V 4.8 VA at 240 V
7027 | RE48AMH13MW | Complementary | power consumption in W | 0.5 W at 24 V 1.7 W at 240 V
7028 | RE48AMH13MW | Complementary | breaking capacity | 1250 VA
7029 | RE48AMH13MW | Complementary | minimum switching current | 100 mA
7030 | RE48AMH13MW | Complementary | maximum switching current | 5 A
7031 | RE48AMH13MW | Complementary | maximum switching voltage | 250 V AC/DC
7032 | RE48AMH13MW | Complementary | electrical durability | 100000 cycles
7033 | RE48AMH13MW | Complementary | mechanical durability | 30000000 cycles
7034 | RE48AMH13MW | Complementary | output voltage | 240 V at 5 A AC-12 30 V at 2 A DC-13 240 V at 1.5 A AC-15
7035 | RE48AMH13MW | Complementary | marking | CE
7036 | RE48AMH13MW | Complementary | surge withstand | 1 kV differential mode conforming to IEC 61000-4-5 level 3 2 kV common mode conforming to IEC 61000-4-5 level 3
7037 | RE48AMH13MW | Complementary | mounting support | Base mounted: socket Panel mounted: system supplied with the product
7038 | RE48AMH13MW | Complementary | local signalling | 1 LED (yellow) for output relay state LED indicator (green) for flashing: relay energised timing in progress LED indicator (green) for on steady: relay energised, no timing in progress
7039 | RE48AMH13MW | Complementary | net weight | 0.14 kg
7040 | RE48AMH13MW | Environment | humidity drift | +/- 0.05 %/%RH of the maximum setting value conforming to IEC 61812-1
7041 | RE48AMH13MW | Environment | immunity to microbreaks | 10 ms
7042 | RE48AMH13MW | Environment | dielectric strength | 1 kV 1 mA/1 minute conforming to IEC 61812-1
7043 | RE48AMH13MW | Environment | protection against electric shocks | 4 kV class III conforming to IEC 60664-1 4 kV class III conforming to IEC 61812-1
7044 | RE48AMH13MW | Environment | standards | EN 50082-1/2 EN 50081-1/2 93/68/EEC 73/23/EEC 89/336/EEC IEC 60669-2-3 IEC 61812-1
7045 | RE48AMH13MW | Environment | product certifications | GL CULus UL CSA C-Tick
7046 | RE48AMH13MW | Environment | ambient air temperature for storage | -40…70 °C
7047 | RE48AMH13MW | Environment | ambient air temperature for operation | -20…50 °C
7048 | RE48AMH13MW | Environment | IP degree of protection | IP40 (housing) conforming to IEC 60529 IP50 (front face) conforming to IEC 60529
7049 | RE48AMH13MW | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
7050 | RE48AMH13MW | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-3
7051 | RE48AMH13MW | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3
7052 | RE48AMH13MW | Environment | resistance to electromagnetic fields | 10 V/m 26 MHz to 1 GHz conforming to IEC 61000-4-3 level 3
7053 | RE48AMH13MW | Environment | resistance to fast transients | 2 kV (capacitive connecting clip) conforming to EN/IEC 61000-4-4 level 4 4 kV (direct) conforming to EN/IEC 61000-4-4 level 4
7054 | RE48AMH13MW | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
7055 | RE48AMH13MW | Environment | immunity to voltage dips | 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 95 % / 5 s conforming to EN/IEC 61000-4-11
7056 | RE48AMH13MW | Environment | disturbance radiated/conducted | Class B 0.15...30 MHz conforming to EN 55022 (EN 55011 group 1)
7057 | RE48AMH13MW | Offer Sustainability | Sustainable offer status | Green Premium product
7058 | RE48AMH13MW | Offer Sustainability | REACh Regulation | REACh Declaration
7059 | RE48AMH13MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7060 | RE48AMH13MW | Offer Sustainability | Mercury free | Yes
7061 | RE48AMH13MW | Offer Sustainability | RoHS exemption information | Yes
7062 | RE48AMH13MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7063 | RE48AMH13MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7064 | RE48AMH13MW | Offer Sustainability | Circularity Profile | End of Life Information
7065 | RE48AMH13MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7066 | RE48AMH13MW | Contractual warranty | Warranty | 18 months
7067 | RE48ACV12MW | Main | range of product | Zelio Time
7068 | RE48ACV12MW | Main | product or component type | Electronic timing relay
7069 | RE48ACV12MW | Main | electrical connection | Plug-in sub-base 11 pin(s)
7070 | RE48ACV12MW | Main | discrete output type | Relay
7071 | RE48ACV12MW | Main | contacts type and composition | 2 C/O timed contacts, AgNi (cadmium free)
7072 | RE48ACV12MW | Main | component name | RE48A
7073 | RE48ACV12MW | Main | time delay type | Li L
7074 | RE48ACV12MW | Main | time delay range | 0.2...12 min 5...300 s 0.02...1.2 s 0.5...30 min 5...300 h 0.2...12 h 0.2...12 s 0.5...30 s 2...120 s 0.05...3 s 2...120 min 5...300 min 0.5...30 h 2...120 h
7075 | RE48ACV12MW | Main | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
7076 | RE48ACV12MW | Main | voltage range | 0.85...1.1 Us AC 0.9...1.1 Us DC
7077 | RE48ACV12MW | Main | [In] rated current | 5 A
7078 | RE48ACV12MW | Complementary | product front plate size | 48 x 48 mm
7079 | RE48ACV12MW | Complementary | control type | Selector switch front panel
7080 | RE48ACV12MW | Complementary | housing material | Self-extinguishing
7081 | RE48ACV12MW | Complementary | repeat accuracy | +/- 0.2 % of the maximum setting value conforming to IEC 61812-1
7082 | RE48ACV12MW | Complementary | temperature drift | +/- 0.02 %/°C of the maximum setting value conforming to IEC 61812-1
7083 | RE48ACV12MW | Complementary | voltage drift | +/- 0.2 %/V of the maximum setting value at 48...240 V +/- 1 %/V of the maximum setting value at 24...48 V
7084 | RE48ACV12MW | Complementary | setting accuracy of time delay | +/- 5 % of full scale at 25 °C conforming to IEC 61812-1
7085 | RE48ACV12MW | Complementary | minimum pulse duration | 20 ms
7086 | RE48ACV12MW | Complementary | reset time | 25 ms on de-energisation
7087 | RE48ACV12MW | Complementary | pick up duration | 55 ms
7088 | RE48ACV12MW | Complementary | on-load factor | 100 %
7089 | RE48ACV12MW | Complementary | power consumption in VA | 1.1 VA at 24 V 4.8 VA at 240 V
7090 | RE48ACV12MW | Complementary | power consumption in W | 0.5 W at 24 V 1.7 W at 240 V
7091 | RE48ACV12MW | Complementary | breaking capacity | 1250 VA
7092 | RE48ACV12MW | Complementary | minimum switching current | 100 mA
7093 | RE48ACV12MW | Complementary | maximum switching current | 5 A
7094 | RE48ACV12MW | Complementary | maximum switching voltage | 250 V AC/DC
7095 | RE48ACV12MW | Complementary | electrical durability | 100000 cycles
7096 | RE48ACV12MW | Complementary | mechanical durability | 30000000 cycles
7097 | RE48ACV12MW | Complementary | output voltage | 240 V at 5 A AC-12 30 V at 2 A DC-13 240 V at 1.5 A AC-15
7098 | RE48ACV12MW | Complementary | marking | CE
7099 | RE48ACV12MW | Complementary | surge withstand | 1 kV differential mode conforming to IEC 61000-4-5 level 3 2 kV common mode conforming to IEC 61000-4-5 level 3
7100 | RE48ACV12MW | Complementary | mounting support | Base mounted: socket Panel mounted: system supplied with the product
7101 | RE48ACV12MW | Complementary | local signalling | 1 LED (yellow) for output relay state LED indicator (green) for flashing: relay energised timing in progress LED indicator (green) for on steady: relay energised, no timing in progress
7102 | RE48ACV12MW | Complementary | net weight | 0.14 kg
7103 | RE48ACV12MW | Environment | humidity drift | +/- 0.05 %/%RH of the maximum setting value conforming to IEC 61812-1
7104 | RE48ACV12MW | Environment | immunity to microbreaks | 10 ms
7105 | RE48ACV12MW | Environment | dielectric strength | 1 kV 1 mA/1 minute conforming to IEC 61812-1
7106 | RE48ACV12MW | Environment | protection against electric shocks | 4 kV class III conforming to IEC 60664-1 4 kV class III conforming to IEC 61812-1
7107 | RE48ACV12MW | Environment | standards | EN 50081-1/2 EN 50082-1/2 IEC 61812-1 93/68/EEC 89/336/EEC IEC 60669-2-3 73/23/EEC
7108 | RE48ACV12MW | Environment | product certifications | GL UL C-Tick CULus CSA
7109 | RE48ACV12MW | Environment | ambient air temperature for storage | -40…70 °C
7110 | RE48ACV12MW | Environment | ambient air temperature for operation | -20…50 °C
7111 | RE48ACV12MW | Environment | IP degree of protection | IP40 (housing) conforming to IEC 60529 IP50 (front face) conforming to IEC 60529
7112 | RE48ACV12MW | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
7113 | RE48ACV12MW | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-3
7114 | RE48ACV12MW | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3
7115 | RE48ACV12MW | Environment | resistance to electromagnetic fields | 10 V/m 26 MHz to 1 GHz conforming to EN/IEC 61000-4-3 level 3
7116 | RE48ACV12MW | Environment | resistance to fast transients | 2 kV (capacitive connecting clip) conforming to EN/IEC 61000-4-4 level 4 4 kV (direct) conforming to EN/IEC 61000-4-4 level 4
7117 | RE48ACV12MW | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
7118 | RE48ACV12MW | Environment | immunity to voltage dips | 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 95 % / 5 s conforming to EN/IEC 61000-4-11
7119 | RE48ACV12MW | Environment | disturbance radiated/conducted | Class B 0.15...30 MHz conforming to EN 55022 (EN 55011 group 1)
7120 | RE48ACV12MW | Offer Sustainability | Sustainable offer status | Green Premium product
7121 | RE48ACV12MW | Offer Sustainability | REACh Regulation | REACh Declaration
7122 | RE48ACV12MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7123 | RE48ACV12MW | Offer Sustainability | Mercury free | Yes
7124 | RE48ACV12MW | Offer Sustainability | RoHS exemption information | Yes
7125 | RE48ACV12MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7126 | RE48ACV12MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7127 | RE48ACV12MW | Offer Sustainability | Circularity Profile | End of Life Information
7128 | RE48ACV12MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7129 | RE48ACV12MW | Contractual warranty | Warranty | 18 months
7130 | REXL2TMJD | Main | range of product | Zelio Time
7131 | REXL2TMJD | Main | product or component type | Miniature timing relay
7132 | REXL2TMJD | Main | fixing mode | Plug-in (socket)
7133 | REXL2TMJD | Main | discrete output type | Relay
7134 | REXL2TMJD | Main | contacts type and composition | 2 C/O
7135 | REXL2TMJD | Main | component name | REXL
7136 | REXL2TMJD | Main | time delay type | A
7137 | REXL2TMJD | Main | time delay range | 10...100 h 0.1...1 s 1...10 s 6...60 min 1...10 h 1...10 min 6...60 s
7138 | REXL2TMJD | Complementary | contacts material | Cadmium free
7139 | REXL2TMJD | Complementary | [Us] rated supply voltage | 12 V DC
7140 | REXL2TMJD | Complementary | voltage range | 0.9...1.1 Us
7141 | REXL2TMJD | Complementary | [In] rated current | 5 A AC
7142 | REXL2TMJD | Complementary | repeat accuracy | +/- 0.5 %
7143 | REXL2TMJD | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
7144 | REXL2TMJD | Complementary | temperature drift | 0.05 %/°C
7145 | REXL2TMJD | Complementary | maximum reset time | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation
7146 | REXL2TMJD | Complementary | voltage drift | +/- 0.2 %/V
7147 | REXL2TMJD | Complementary | maximum switching capacity | 4 x 5 A
7148 | REXL2TMJD | Complementary | maximum temporary permissible current | 10 A for < 10 s
7149 | REXL2TMJD | Complementary | minimum switching current | 100 mA
7150 | REXL2TMJD | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
7151 | REXL2TMJD | Complementary | mechanical durability | 10000000 cycles
7152 | REXL2TMJD | Complementary | maximum power consumption | 1.5 W
7153 | REXL2TMJD | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010
7154 | REXL2TMJD | Complementary | output overvoltage protection | 2 J
7155 | REXL2TMJD | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
7156 | REXL2TMJD | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
7157 | REXL2TMJD | Complementary | local signalling | 1 LED (red) for output in operation 1 LED (yellow) for power ON
7158 | REXL2TMJD | Complementary | net weight | 0.05 kg
7159 | REXL2TMJD | Environment | immunity to microbreaks | 5 ms
7160 | REXL2TMJD | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
7161 | REXL2TMJD | Environment | standards | 93/68/EEC EN/IEC 61812-1 EN/IEC 60601-1 89/336/EEC EN/IEC 60601-2 73/23/EEC EN 61000-6-2 EN 50081-2
7162 | REXL2TMJD | Environment | product certifications | UL CUL
7163 | REXL2TMJD | Environment | ambient air temperature for operation | -20…60 °C
7164 | REXL2TMJD | Environment | ambient air temperature for storage | -40…70 °C
7165 | REXL2TMJD | Environment | IP degree of protection | IP50 conforming to IEC 60529
7166 | REXL2TMJD | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
7167 | REXL2TMJD | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
7168 | REXL2TMJD | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3
7169 | REXL2TMJD | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
7170 | REXL2TMJD | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
7171 | REXL2TMJD | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
7172 | REXL2TMJD | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11
7173 | REXL2TMJD | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
7174 | REXL2TMJD | Offer Sustainability | Sustainable offer status | Green Premium product
7175 | REXL2TMJD | Offer Sustainability | REACh Regulation | REACh Declaration
7176 | REXL2TMJD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7177 | REXL2TMJD | Offer Sustainability | Mercury free | Yes
7178 | REXL2TMJD | Offer Sustainability | RoHS exemption information | Yes
7179 | REXL2TMJD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7180 | REXL2TMJD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7181 | REXL2TMJD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7182 | REXL2TMJD | Contractual warranty | Warranty | 18 months
7183 | REXL2TMBD | Main | range of product | Zelio Time
7184 | REXL2TMBD | Main | product or component type | Miniature timing relay
7185 | REXL2TMBD | Main | fixing mode | Plug-in (socket)
7186 | REXL2TMBD | Main | discrete output type | Relay
7187 | REXL2TMBD | Main | contacts type and composition | 2 C/O
7188 | REXL2TMBD | Main | component name | REXL
7189 | REXL2TMBD | Main | time delay type | A
7190 | REXL2TMBD | Main | time delay range | 1...10 s 1...10 min 6...60 min 0.1...1 s 1...10 h 10...100 h 6...60 s
7191 | REXL2TMBD | Complementary | contacts material | Cadmium free
7192 | REXL2TMBD | Complementary | [Us] rated supply voltage | 24 V DC
7193 | REXL2TMBD | Complementary | voltage range | 0.9...1.1 Us
7194 | REXL2TMBD | Complementary | [In] rated current | 5 A AC
7195 | REXL2TMBD | Complementary | repeat accuracy | +/- 0.5 %
7196 | REXL2TMBD | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
7197 | REXL2TMBD | Complementary | temperature drift | 0.05 %/°C
7198 | REXL2TMBD | Complementary | maximum reset time | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation
7199 | REXL2TMBD | Complementary | voltage drift | +/- 0.2 %/V
7200 | REXL2TMBD | Complementary | maximum switching capacity | 4 x 5 A
7201 | REXL2TMBD | Complementary | maximum temporary permissible current | 10 A for < 10 s
7202 | REXL2TMBD | Complementary | minimum switching current | 100 mA
7203 | REXL2TMBD | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
7204 | REXL2TMBD | Complementary | mechanical durability | 10000000 cycles
7205 | REXL2TMBD | Complementary | maximum power consumption | 1.2 W
7206 | REXL2TMBD | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010
7207 | REXL2TMBD | Complementary | output overvoltage protection | 2 J
7208 | REXL2TMBD | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
7209 | REXL2TMBD | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
7210 | REXL2TMBD | Complementary | local signalling | 1 LED (red) for output in operation 1 LED (yellow) for power ON
7211 | REXL2TMBD | Complementary | net weight | 0.05 kg
7212 | REXL2TMBD | Environment | immunity to microbreaks | 5 ms
7213 | REXL2TMBD | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
7214 | REXL2TMBD | Environment | standards | 73/23/EEC EN 50081-2 93/68/EEC EN/IEC 61812-1 EN 61000-6-2 EN/IEC 60601-1 EN/IEC 60601-2 89/336/EEC
7215 | REXL2TMBD | Environment | product certifications | CUL UL
7216 | REXL2TMBD | Environment | ambient air temperature for operation | -20…60 °C
7217 | REXL2TMBD | Environment | ambient air temperature for storage | -40…70 °C
7218 | REXL2TMBD | Environment | IP degree of protection | IP50 conforming to IEC 60529
7219 | REXL2TMBD | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
7220 | REXL2TMBD | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
7221 | REXL2TMBD | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3
7222 | REXL2TMBD | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
7223 | REXL2TMBD | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
7224 | REXL2TMBD | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
7225 | REXL2TMBD | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11
7226 | REXL2TMBD | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
7227 | REXL2TMBD | Offer Sustainability | Sustainable offer status | Green Premium product
7228 | REXL2TMBD | Offer Sustainability | REACh Regulation | REACh Declaration
7229 | REXL2TMBD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7230 | REXL2TMBD | Offer Sustainability | Mercury free | Yes
7231 | REXL2TMBD | Offer Sustainability | RoHS exemption information | Yes
7232 | REXL2TMBD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7233 | REXL2TMBD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7234 | REXL2TMBD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7235 | REXL2TMBD | Contractual warranty | Warranty | 18 months
7236 | REXL2TMB7 | Main | range of product | Zelio Time
7237 | REXL2TMB7 | Main | product or component type | Miniature timing relay
7238 | REXL2TMB7 | Main | fixing mode | Plug-in (socket)
7239 | REXL2TMB7 | Main | discrete output type | Relay
7240 | REXL2TMB7 | Main | contacts type and composition | 2 C/O
7241 | REXL2TMB7 | Main | component name | REXL
7242 | REXL2TMB7 | Main | time delay type | A
7243 | REXL2TMB7 | Main | time delay range | 10...100 h 6...60 min 0.1...1 s 1...10 h 1...10 min 6...60 s 1...10 s
7244 | REXL2TMB7 | Complementary | contacts material | Cadmium free
7245 | REXL2TMB7 | Complementary | [Us] rated supply voltage | 24 V AC 50/60 Hz
7246 | REXL2TMB7 | Complementary | voltage range | 0.85...1.15 Us
7247 | REXL2TMB7 | Complementary | [In] rated current | 5 A AC
7248 | REXL2TMB7 | Complementary | repeat accuracy | +/- 0.5 %
7249 | REXL2TMB7 | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
7250 | REXL2TMB7 | Complementary | temperature drift | 0.05 %/°C
7251 | REXL2TMB7 | Complementary | maximum reset time | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation
7252 | REXL2TMB7 | Complementary | voltage drift | +/- 0.2 %/V
7253 | REXL2TMB7 | Complementary | maximum switching capacity | 4 x 5 A
7254 | REXL2TMB7 | Complementary | maximum temporary permissible current | 10 A for < 10 s
7255 | REXL2TMB7 | Complementary | minimum switching current | 100 mA
7256 | REXL2TMB7 | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
7257 | REXL2TMB7 | Complementary | mechanical durability | 10000000 cycles
7258 | REXL2TMB7 | Complementary | maximum power consumption | 1.7 VA
7259 | REXL2TMB7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010
7260 | REXL2TMB7 | Complementary | output overvoltage protection | 2 J
7261 | REXL2TMB7 | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
7262 | REXL2TMB7 | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
7263 | REXL2TMB7 | Complementary | local signalling | 1 LED (red) for output in operation 1 LED (yellow) for power ON
7264 | REXL2TMB7 | Complementary | net weight | 0.05 kg
7265 | REXL2TMB7 | Environment | immunity to microbreaks | 5 ms
7266 | REXL2TMB7 | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
7267 | REXL2TMB7 | Environment | standards | EN 50081-2 EN 61000-6-2 EN/IEC 60601-2 EN/IEC 61812-1 93/68/EEC 73/23/EEC 89/336/EEC EN/IEC 60601-1
7268 | REXL2TMB7 | Environment | product certifications | UL CUL
7269 | REXL2TMB7 | Environment | ambient air temperature for operation | -20…60 °C
7270 | REXL2TMB7 | Environment | ambient air temperature for storage | -40…70 °C
7271 | REXL2TMB7 | Environment | IP degree of protection | IP50 conforming to IEC 60529
7272 | REXL2TMB7 | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
7273 | REXL2TMB7 | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
7274 | REXL2TMB7 | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3
7275 | REXL2TMB7 | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
7276 | REXL2TMB7 | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
7277 | REXL2TMB7 | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
7278 | REXL2TMB7 | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11
7279 | REXL2TMB7 | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
7280 | REXL2TMB7 | Offer Sustainability | Sustainable offer status | Green Premium product
7281 | REXL2TMB7 | Offer Sustainability | REACh Regulation | REACh Declaration
7282 | REXL2TMB7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7283 | REXL2TMB7 | Offer Sustainability | Mercury free | Yes
7284 | REXL2TMB7 | Offer Sustainability | RoHS exemption information | Yes
7285 | REXL2TMB7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7286 | REXL2TMB7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7287 | REXL2TMB7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7288 | REXL2TMB7 | Contractual warranty | Warranty | 18 months
7289 | REXL2TMF7 | Main | range of product | Zelio Time
7290 | REXL2TMF7 | Main | product or component type | Miniature timing relay
7291 | REXL2TMF7 | Main | fixing mode | Plug-in (socket)
7292 | REXL2TMF7 | Main | discrete output type | Relay
7293 | REXL2TMF7 | Main | contacts type and composition | 2 C/O
7294 | REXL2TMF7 | Main | component name | REXL
7295 | REXL2TMF7 | Main | time delay type | A
7296 | REXL2TMF7 | Main | time delay range | 10...100 h 6...60 s 6...60 min 1...10 min 0.1...1 s 1...10 s 1...10 h
7297 | REXL2TMF7 | Complementary | contacts material | Cadmium free
7298 | REXL2TMF7 | Complementary | [Us] rated supply voltage | 120 V AC 50/60 Hz
7299 | REXL2TMF7 | Complementary | voltage range | 0.85...1.15 Us
7300 | REXL2TMF7 | Complementary | [In] rated current | 5 A AC
7301 | REXL2TMF7 | Complementary | repeat accuracy | +/- 0.5 %
7302 | REXL2TMF7 | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
7303 | REXL2TMF7 | Complementary | temperature drift | 0.05 %/°C
7304 | REXL2TMF7 | Complementary | maximum reset time | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation
7305 | REXL2TMF7 | Complementary | voltage drift | +/- 0.2 %/V
7306 | REXL2TMF7 | Complementary | maximum switching capacity | 4 x 5 A
7307 | REXL2TMF7 | Complementary | maximum temporary permissible current | 10 A for < 10 s
7308 | REXL2TMF7 | Complementary | minimum switching current | 100 mA
7309 | REXL2TMF7 | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
7310 | REXL2TMF7 | Complementary | mechanical durability | 10000000 cycles
7311 | REXL2TMF7 | Complementary | maximum power consumption | 2.6 VA
7312 | REXL2TMF7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010
7313 | REXL2TMF7 | Complementary | output overvoltage protection | 2 J
7314 | REXL2TMF7 | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
7315 | REXL2TMF7 | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
7316 | REXL2TMF7 | Complementary | local signalling | 1 LED (red) for output in operation 1 LED (yellow) for power ON
7317 | REXL2TMF7 | Complementary | net weight | 0.05 kg
7318 | REXL2TMF7 | Environment | immunity to microbreaks | 5 ms
7319 | REXL2TMF7 | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
7320 | REXL2TMF7 | Environment | standards | EN 61000-6-2 93/68/EEC EN 50081-2 EN/IEC 61812-1 73/23/EEC EN/IEC 60601-2 89/336/EEC EN/IEC 60601-1
7321 | REXL2TMF7 | Environment | product certifications | CUL UL
7322 | REXL2TMF7 | Environment | ambient air temperature for operation | -20…60 °C
7323 | REXL2TMF7 | Environment | ambient air temperature for storage | -40…70 °C
7324 | REXL2TMF7 | Environment | IP degree of protection | IP50 conforming to IEC 60529
7325 | REXL2TMF7 | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
7326 | REXL2TMF7 | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
7327 | REXL2TMF7 | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3
7328 | REXL2TMF7 | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
7329 | REXL2TMF7 | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
7330 | REXL2TMF7 | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
7331 | REXL2TMF7 | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11
7332 | REXL2TMF7 | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
7333 | REXL2TMF7 | Offer Sustainability | Sustainable offer status | Green Premium product
7334 | REXL2TMF7 | Offer Sustainability | REACh Regulation | REACh Declaration
7335 | REXL2TMF7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7336 | REXL2TMF7 | Offer Sustainability | Mercury free | Yes
7337 | REXL2TMF7 | Offer Sustainability | RoHS exemption information | Yes
7338 | REXL2TMF7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7339 | REXL2TMF7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7340 | REXL2TMF7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7341 | REXL2TMF7 | Contractual warranty | Warranty | 18 months
7342 | REXL2TMP7 | Main | range of product | Zelio Time
7343 | REXL2TMP7 | Main | product or component type | Miniature timing relay
7344 | REXL2TMP7 | Main | fixing mode | Plug-in (socket)
7345 | REXL2TMP7 | Main | discrete output type | Relay
7346 | REXL2TMP7 | Main | contacts type and composition | 2 C/O
7347 | REXL2TMP7 | Main | component name | REXL
7348 | REXL2TMP7 | Main | time delay type | A
7349 | REXL2TMP7 | Main | time delay range | 10...100 h 1...10 min 1...10 h 0.1...1 s 6...60 min 6...60 s 1...10 s
7350 | REXL2TMP7 | Complementary | contacts material | Cadmium free
7351 | REXL2TMP7 | Complementary | [Us] rated supply voltage | 230 V AC 50/60 Hz
7352 | REXL2TMP7 | Complementary | voltage range | 0.85...1.15 Us
7353 | REXL2TMP7 | Complementary | [In] rated current | 5 A AC
7354 | REXL2TMP7 | Complementary | repeat accuracy | +/- 0.5 %
7355 | REXL2TMP7 | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
7356 | REXL2TMP7 | Complementary | temperature drift | 0.05 %/°C
7357 | REXL2TMP7 | Complementary | maximum reset time | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation
7358 | REXL2TMP7 | Complementary | voltage drift | +/- 0.2 %/V
7359 | REXL2TMP7 | Complementary | maximum switching capacity | 4 x 5 A
7360 | REXL2TMP7 | Complementary | maximum temporary permissible current | 10 A for < 10 s
7361 | REXL2TMP7 | Complementary | minimum switching current | 100 mA
7362 | REXL2TMP7 | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
7363 | REXL2TMP7 | Complementary | mechanical durability | 10000000 cycles
7364 | REXL2TMP7 | Complementary | maximum power consumption | 3 VA
7365 | REXL2TMP7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010
7366 | REXL2TMP7 | Complementary | output overvoltage protection | 2 J
7367 | REXL2TMP7 | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
7368 | REXL2TMP7 | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
7369 | REXL2TMP7 | Complementary | local signalling | 1 LED (red) for output in operation 1 LED (yellow) for power ON
7370 | REXL2TMP7 | Complementary | net weight | 0.05 kg
7371 | REXL2TMP7 | Environment | immunity to microbreaks | 5 ms
7372 | REXL2TMP7 | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
7373 | REXL2TMP7 | Environment | standards | EN/IEC 60601-1 89/336/EEC EN 61000-6-2 EN 50081-2 EN/IEC 61812-1 73/23/EEC EN/IEC 60601-2 93/68/EEC
7374 | REXL2TMP7 | Environment | product certifications | UL CUL
7375 | REXL2TMP7 | Environment | ambient air temperature for operation | -20…60 °C
7376 | REXL2TMP7 | Environment | ambient air temperature for storage | -40…70 °C
7377 | REXL2TMP7 | Environment | IP degree of protection | IP50 conforming to IEC 60529
7378 | REXL2TMP7 | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
7379 | REXL2TMP7 | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
7380 | REXL2TMP7 | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3
7381 | REXL2TMP7 | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
7382 | REXL2TMP7 | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
7383 | REXL2TMP7 | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
7384 | REXL2TMP7 | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11
7385 | REXL2TMP7 | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
7386 | REXL2TMP7 | Offer Sustainability | Sustainable offer status | Green Premium product
7387 | REXL2TMP7 | Offer Sustainability | REACh Regulation | REACh Declaration
7388 | REXL2TMP7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7389 | REXL2TMP7 | Offer Sustainability | Mercury free | Yes
7390 | REXL2TMP7 | Offer Sustainability | RoHS exemption information | Yes
7391 | REXL2TMP7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7392 | REXL2TMP7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7393 | REXL2TMP7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7394 | REXL2TMP7 | Contractual warranty | Warranty | 18 months
7395 | REXL4TMJD | Main | range of product | Zelio Time
7396 | REXL4TMJD | Main | product or component type | Miniature timing relay
7397 | REXL4TMJD | Main | fixing mode | Plug-in (socket)
7398 | REXL4TMJD | Main | discrete output type | Relay
7399 | REXL4TMJD | Main | contacts type and composition | 4 C/O
7400 | REXL4TMJD | Main | component name | REXL
7401 | REXL4TMJD | Main | time delay type | A
7402 | REXL4TMJD | Main | time delay range | 10...100 h 6...60 min 1...10 h 0.1...1 s 6...60 s 1...10 s 1...10 min
7403 | REXL4TMJD | Complementary | contacts material | Cadmium free
7404 | REXL4TMJD | Complementary | [Us] rated supply voltage | 12 V DC
7405 | REXL4TMJD | Complementary | voltage range | 0.9...1.1 Us
7406 | REXL4TMJD | Complementary | [In] rated current | 5 A AC
7407 | REXL4TMJD | Complementary | repeat accuracy | +/- 0.5 %
7408 | REXL4TMJD | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
7409 | REXL4TMJD | Complementary | temperature drift | 0.05 %/°C
7410 | REXL4TMJD | Complementary | maximum reset time | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation
7411 | REXL4TMJD | Complementary | voltage drift | +/- 0.2 %/V
7412 | REXL4TMJD | Complementary | maximum switching capacity | 4 x 5 A
7413 | REXL4TMJD | Complementary | maximum temporary permissible current | 10 A for < 10 s
7414 | REXL4TMJD | Complementary | minimum switching current | 100 mA
7415 | REXL4TMJD | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
7416 | REXL4TMJD | Complementary | mechanical durability | 10000000 cycles
7417 | REXL4TMJD | Complementary | maximum power consumption | 1.5 W
7418 | REXL4TMJD | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010
7419 | REXL4TMJD | Complementary | output overvoltage protection | 2 J
7420 | REXL4TMJD | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
7421 | REXL4TMJD | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
7422 | REXL4TMJD | Complementary | local signalling | 1 LED (red) for output in operation 1 LED (yellow) for power ON
7423 | REXL4TMJD | Complementary | net weight | 0.05 kg
7424 | REXL4TMJD | Environment | immunity to microbreaks | 5 ms
7425 | REXL4TMJD | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
7426 | REXL4TMJD | Environment | standards | 93/68/EEC EN 50081-2 73/23/EEC EN 61000-6-2 EN/IEC 60601-2 EN/IEC 60601-1 89/336/EEC EN/IEC 61812-1
7427 | REXL4TMJD | Environment | product certifications | UL CUL
7428 | REXL4TMJD | Environment | ambient air temperature for operation | -20…60 °C
7429 | REXL4TMJD | Environment | ambient air temperature for storage | -40…70 °C
7430 | REXL4TMJD | Environment | IP degree of protection | IP50 conforming to IEC 60529
7431 | REXL4TMJD | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
7432 | REXL4TMJD | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
7433 | REXL4TMJD | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3
7434 | REXL4TMJD | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
7435 | REXL4TMJD | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
7436 | REXL4TMJD | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
7437 | REXL4TMJD | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11
7438 | REXL4TMJD | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
7439 | REXL4TMJD | Offer Sustainability | Sustainable offer status | Green Premium product
7440 | REXL4TMJD | Offer Sustainability | REACh Regulation | REACh Declaration
7441 | REXL4TMJD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7442 | REXL4TMJD | Offer Sustainability | Mercury free | Yes
7443 | REXL4TMJD | Offer Sustainability | RoHS exemption information | Yes
7444 | REXL4TMJD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7445 | REXL4TMJD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7446 | REXL4TMJD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7447 | REXL4TMJD | Contractual warranty | Warranty | 18 months
7448 | REXL4TMBD | Main | range of product | Zelio Time
7449 | REXL4TMBD | Main | product or component type | Miniature timing relay
7450 | REXL4TMBD | Main | fixing mode | Plug-in (socket)
7451 | REXL4TMBD | Main | discrete output type | Relay
7452 | REXL4TMBD | Main | contacts type and composition | 4 C/O
7453 | REXL4TMBD | Main | component name | REXL
7454 | REXL4TMBD | Main | time delay type | A
7455 | REXL4TMBD | Main | time delay range | 10...100 h 6...60 s 6...60 min 1...10 s 1...10 h 1...10 min 0.1...1 s
7456 | REXL4TMBD | Complementary | contacts material | Cadmium free
7457 | REXL4TMBD | Complementary | [Us] rated supply voltage | 24 V DC
7458 | REXL4TMBD | Complementary | voltage range | 0.9...1.1 Us
7459 | REXL4TMBD | Complementary | [In] rated current | 5 A AC
7460 | REXL4TMBD | Complementary | repeat accuracy | +/- 0.5 %
7461 | REXL4TMBD | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
7462 | REXL4TMBD | Complementary | temperature drift | 0.05 %/°C
7463 | REXL4TMBD | Complementary | maximum reset time | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation
7464 | REXL4TMBD | Complementary | voltage drift | +/- 0.2 %/V
7465 | REXL4TMBD | Complementary | maximum switching capacity | 4 x 5 A
7466 | REXL4TMBD | Complementary | maximum temporary permissible current | 10 A for < 10 s
7467 | REXL4TMBD | Complementary | minimum switching current | 100 mA
7468 | REXL4TMBD | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
7469 | REXL4TMBD | Complementary | mechanical durability | 10000000 cycles
7470 | REXL4TMBD | Complementary | maximum power consumption | 1.2 W
7471 | REXL4TMBD | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010
7472 | REXL4TMBD | Complementary | output overvoltage protection | 2 J
7473 | REXL4TMBD | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
7474 | REXL4TMBD | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
7475 | REXL4TMBD | Complementary | local signalling | 1 LED (red) for output in operation 1 LED (yellow) for power ON
7476 | REXL4TMBD | Complementary | net weight | 0.05 kg
7477 | REXL4TMBD | Environment | immunity to microbreaks | 5 ms
7478 | REXL4TMBD | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
7479 | REXL4TMBD | Environment | standards | EN/IEC 60601-2 EN 61000-6-2 73/23/EEC EN/IEC 61812-1 93/68/EEC EN/IEC 60601-1 89/336/EEC EN 50081-2
7480 | REXL4TMBD | Environment | product certifications | UL CUL
7481 | REXL4TMBD | Environment | ambient air temperature for operation | -20…60 °C
7482 | REXL4TMBD | Environment | ambient air temperature for storage | -40…70 °C
7483 | REXL4TMBD | Environment | IP degree of protection | IP50 conforming to IEC 60529
7484 | REXL4TMBD | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
7485 | REXL4TMBD | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
7486 | REXL4TMBD | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3
7487 | REXL4TMBD | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
7488 | REXL4TMBD | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
7489 | REXL4TMBD | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
7490 | REXL4TMBD | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11
7491 | REXL4TMBD | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
7492 | REXL4TMBD | Offer Sustainability | Sustainable offer status | Green Premium product
7493 | REXL4TMBD | Offer Sustainability | REACh Regulation | REACh Declaration
7494 | REXL4TMBD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7495 | REXL4TMBD | Offer Sustainability | Mercury free | Yes
7496 | REXL4TMBD | Offer Sustainability | RoHS exemption information | Yes
7497 | REXL4TMBD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7498 | REXL4TMBD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7499 | REXL4TMBD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7500 | REXL4TMBD | Contractual warranty | Warranty | 18 months
7501 | REXL4TMB7 | Main | range of product | Zelio Time
7502 | REXL4TMB7 | Main | product or component type | Miniature timing relay
7503 | REXL4TMB7 | Main | fixing mode | Plug-in (socket)
7504 | REXL4TMB7 | Main | discrete output type | Relay
7505 | REXL4TMB7 | Main | contacts type and composition | 4 C/O
7506 | REXL4TMB7 | Main | component name | REXL
7507 | REXL4TMB7 | Main | time delay type | A
7508 | REXL4TMB7 | Main | time delay range | 6...60 s 1...10 s 1...10 h 1...10 min 6...60 min 10...100 h 0.1...1 s
7509 | REXL4TMB7 | Complementary | contacts material | Cadmium free
7510 | REXL4TMB7 | Complementary | [Us] rated supply voltage | 24 V AC 50/60 Hz
7511 | REXL4TMB7 | Complementary | voltage range | 0.85...1.15 Us
7512 | REXL4TMB7 | Complementary | [In] rated current | 5 A AC
7513 | REXL4TMB7 | Complementary | repeat accuracy | +/- 0.5 %
7514 | REXL4TMB7 | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
7515 | REXL4TMB7 | Complementary | temperature drift | 0.05 %/°C
7516 | REXL4TMB7 | Complementary | maximum reset time | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation
7517 | REXL4TMB7 | Complementary | voltage drift | +/- 0.2 %/V
7518 | REXL4TMB7 | Complementary | maximum switching capacity | 4 x 5 A
7519 | REXL4TMB7 | Complementary | maximum temporary permissible current | 10 A for < 10 s
7520 | REXL4TMB7 | Complementary | minimum switching current | 100 mA
7521 | REXL4TMB7 | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
7522 | REXL4TMB7 | Complementary | mechanical durability | 10000000 cycles
7523 | REXL4TMB7 | Complementary | maximum power consumption | 1.7 VA
7524 | REXL4TMB7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010
7525 | REXL4TMB7 | Complementary | output overvoltage protection | 2 J
7526 | REXL4TMB7 | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
7527 | REXL4TMB7 | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
7528 | REXL4TMB7 | Complementary | local signalling | 1 LED (red) for output in operation 1 LED (yellow) for power ON
7529 | REXL4TMB7 | Complementary | net weight | 0.05 kg
7530 | REXL4TMB7 | Environment | immunity to microbreaks | 5 ms
7531 | REXL4TMB7 | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
7532 | REXL4TMB7 | Environment | standards | EN/IEC 60601-1 89/336/EEC EN/IEC 61812-1 EN/IEC 60601-2 73/23/EEC 93/68/EEC EN 61000-6-2 EN 50081-2
7533 | REXL4TMB7 | Environment | product certifications | UL CUL
7534 | REXL4TMB7 | Environment | ambient air temperature for operation | -20…60 °C
7535 | REXL4TMB7 | Environment | ambient air temperature for storage | -40…70 °C
7536 | REXL4TMB7 | Environment | IP degree of protection | IP50 conforming to IEC 60529
7537 | REXL4TMB7 | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
7538 | REXL4TMB7 | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
7539 | REXL4TMB7 | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3
7540 | REXL4TMB7 | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
7541 | REXL4TMB7 | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
7542 | REXL4TMB7 | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
7543 | REXL4TMB7 | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11
7544 | REXL4TMB7 | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
7545 | REXL4TMB7 | Offer Sustainability | Sustainable offer status | Green Premium product
7546 | REXL4TMB7 | Offer Sustainability | REACh Regulation | REACh Declaration
7547 | REXL4TMB7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7548 | REXL4TMB7 | Offer Sustainability | Mercury free | Yes
7549 | REXL4TMB7 | Offer Sustainability | RoHS exemption information | Yes
7550 | REXL4TMB7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7551 | REXL4TMB7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7552 | REXL4TMB7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7553 | REXL4TMB7 | Contractual warranty | Warranty | 18 months
7554 | REXL4TMF7 | Main | range of product | Zelio Time
7555 | REXL4TMF7 | Main | product or component type | Miniature timing relay
7556 | REXL4TMF7 | Main | fixing mode | Plug-in (socket)
7557 | REXL4TMF7 | Main | discrete output type | Relay
7558 | REXL4TMF7 | Main | contacts type and composition | 4 C/O
7559 | REXL4TMF7 | Main | component name | REXL
7560 | REXL4TMF7 | Main | time delay type | A
7561 | REXL4TMF7 | Main | time delay range | 1...10 min 10...100 h 6...60 s 0.1...1 s 1...10 h 6...60 min 1...10 s
7562 | REXL4TMF7 | Complementary | contacts material | Cadmium free
7563 | REXL4TMF7 | Complementary | [Us] rated supply voltage | 120 V AC 50/60 Hz
7564 | REXL4TMF7 | Complementary | voltage range | 0.85...1.15 Us
7565 | REXL4TMF7 | Complementary | [In] rated current | 5 A AC
7566 | REXL4TMF7 | Complementary | repeat accuracy | +/- 0.5 %
7567 | REXL4TMF7 | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
7568 | REXL4TMF7 | Complementary | temperature drift | 0.05 %/°C
7569 | REXL4TMF7 | Complementary | maximum reset time | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation
7570 | REXL4TMF7 | Complementary | voltage drift | +/- 0.2 %/V
7571 | REXL4TMF7 | Complementary | maximum switching capacity | 4 x 5 A
7572 | REXL4TMF7 | Complementary | maximum temporary permissible current | 10 A for < 10 s
7573 | REXL4TMF7 | Complementary | minimum switching current | 100 mA
7574 | REXL4TMF7 | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
7575 | REXL4TMF7 | Complementary | mechanical durability | 10000000 cycles
7576 | REXL4TMF7 | Complementary | maximum power consumption | 2.6 VA
7577 | REXL4TMF7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010
7578 | REXL4TMF7 | Complementary | output overvoltage protection | 2 J
7579 | REXL4TMF7 | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
7580 | REXL4TMF7 | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
7581 | REXL4TMF7 | Complementary | local signalling | 1 LED (red) for output in operation 1 LED (yellow) for power ON
7582 | REXL4TMF7 | Complementary | net weight | 0.05 kg
7583 | REXL4TMF7 | Environment | immunity to microbreaks | 5 ms
7584 | REXL4TMF7 | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
7585 | REXL4TMF7 | Environment | standards | EN 61000-6-2 EN/IEC 60601-1 89/336/EEC 93/68/EEC EN/IEC 61812-1 EN/IEC 60601-2 73/23/EEC EN 50081-2
7586 | REXL4TMF7 | Environment | product certifications | CUL UL
7587 | REXL4TMF7 | Environment | ambient air temperature for operation | -20…60 °C
7588 | REXL4TMF7 | Environment | ambient air temperature for storage | -40…70 °C
7589 | REXL4TMF7 | Environment | IP degree of protection | IP50 conforming to IEC 60529
7590 | REXL4TMF7 | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
7591 | REXL4TMF7 | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
7592 | REXL4TMF7 | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3
7593 | REXL4TMF7 | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
7594 | REXL4TMF7 | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
7595 | REXL4TMF7 | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
7596 | REXL4TMF7 | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11
7597 | REXL4TMF7 | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
7598 | REXL4TMF7 | Offer Sustainability | Sustainable offer status | Green Premium product
7599 | REXL4TMF7 | Offer Sustainability | REACh Regulation | REACh Declaration
7600 | REXL4TMF7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7601 | REXL4TMF7 | Offer Sustainability | Mercury free | Yes
7602 | REXL4TMF7 | Offer Sustainability | RoHS exemption information | Yes
7603 | REXL4TMF7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7604 | REXL4TMF7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7605 | REXL4TMF7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7606 | REXL4TMF7 | Contractual warranty | Warranty | 18 months
7607 | REXL4TMP7 | Main | range of product | Zelio Time
7608 | REXL4TMP7 | Main | product or component type | Miniature timing relay
7609 | REXL4TMP7 | Main | fixing mode | Plug-in (socket)
7610 | REXL4TMP7 | Main | discrete output type | Relay
7611 | REXL4TMP7 | Main | contacts type and composition | 4 C/O
7612 | REXL4TMP7 | Main | component name | REXL
7613 | REXL4TMP7 | Main | time delay type | A
7614 | REXL4TMP7 | Main | time delay range | 6...60 s 1...10 s 6...60 min 1...10 min 0.1...1 s 10...100 h 1...10 h
7615 | REXL4TMP7 | Complementary | contacts material | Cadmium free
7616 | REXL4TMP7 | Complementary | [Us] rated supply voltage | 230 V AC 50/60 Hz
7617 | REXL4TMP7 | Complementary | voltage range | 0.85...1.15 Us
7618 | REXL4TMP7 | Complementary | [In] rated current | 5 A AC
7619 | REXL4TMP7 | Complementary | repeat accuracy | +/- 0.5 %
7620 | REXL4TMP7 | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
7621 | REXL4TMP7 | Complementary | temperature drift | 0.05 %/°C
7622 | REXL4TMP7 | Complementary | maximum reset time | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation
7623 | REXL4TMP7 | Complementary | voltage drift | +/- 0.2 %/V
7624 | REXL4TMP7 | Complementary | maximum switching capacity | 4 x 5 A
7625 | REXL4TMP7 | Complementary | maximum temporary permissible current | 10 A for < 10 s
7626 | REXL4TMP7 | Complementary | minimum switching current | 100 mA
7627 | REXL4TMP7 | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
7628 | REXL4TMP7 | Complementary | mechanical durability | 10000000 cycles
7629 | REXL4TMP7 | Complementary | maximum power consumption | 3 VA
7630 | REXL4TMP7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010
7631 | REXL4TMP7 | Complementary | output overvoltage protection | 2 J
7632 | REXL4TMP7 | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
7633 | REXL4TMP7 | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
7634 | REXL4TMP7 | Complementary | local signalling | 1 LED (red) for output in operation 1 LED (yellow) for power ON
7635 | REXL4TMP7 | Complementary | net weight | 0.05 kg
7636 | REXL4TMP7 | Environment | immunity to microbreaks | 5 ms
7637 | REXL4TMP7 | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
7638 | REXL4TMP7 | Environment | standards | EN 61000-6-2 EN 50081-2 EN/IEC 60601-1 EN/IEC 60601-2 73/23/EEC 93/68/EEC 89/336/EEC EN/IEC 61812-1
7639 | REXL4TMP7 | Environment | product certifications | CUL UL
7640 | REXL4TMP7 | Environment | ambient air temperature for operation | -20…60 °C
7641 | REXL4TMP7 | Environment | ambient air temperature for storage | -40…70 °C
7642 | REXL4TMP7 | Environment | IP degree of protection | IP50 conforming to IEC 60529
7643 | REXL4TMP7 | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
7644 | REXL4TMP7 | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
7645 | REXL4TMP7 | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3
7646 | REXL4TMP7 | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
7647 | REXL4TMP7 | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
7648 | REXL4TMP7 | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
7649 | REXL4TMP7 | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11
7650 | REXL4TMP7 | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
7651 | REXL4TMP7 | Offer Sustainability | Sustainable offer status | Green Premium product
7652 | REXL4TMP7 | Offer Sustainability | REACh Regulation | REACh Declaration
7653 | REXL4TMP7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7654 | REXL4TMP7 | Offer Sustainability | Mercury free | Yes
7655 | REXL4TMP7 | Offer Sustainability | RoHS exemption information | Yes
7656 | REXL4TMP7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7657 | REXL4TMP7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7658 | REXL4TMP7 | Contractual warranty | Warranty | 18 months
7659 | RMPT10BD | Main | range of product | Zelio Analog
7660 | RMPT10BD | Main | product or component type | Converter for Universal Pt100 probes
7661 | RMPT10BD | Main | analogue input type | Temperature probe - 40...40 °C/- 40...104 °F Pt 100 2, 3 or 4 wires
7662 | RMPT10BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
7663 | RMPT10BD | Complementary | protection type | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output Reverse polarity protection on power supply
7664 | RMPT10BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
7665 | RMPT10BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken
7666 | RMPT10BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
7667 | RMPT10BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output
7668 | RMPT10BD | Complementary | local signalling | LED (green)power ON:
7669 | RMPT10BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
7670 | RMPT10BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C
7671 | RMPT10BD | Complementary | temperature coefficient | 150 ppm/°C
7672 | RMPT10BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
7673 | RMPT10BD | Complementary | clamping connection capacity | 1 x 2.5 mm² 2 x 1.5 mm²
7674 | RMPT10BD | Complementary | tightening torque | 0.6…1.1 N.m
7675 | RMPT10BD | Complementary | marking | CE
7676 | RMPT10BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
7677 | RMPT10BD | Complementary | [Ui] rated insulation voltage | 2000 V
7678 | RMPT10BD | Complementary | fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
7679 | RMPT10BD | Complementary | safety reliability data | B10d = 30437 MTTFd = 32.9 years
7680 | RMPT10BD | Complementary | net weight | 0.12 kg
7681 | RMPT10BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
7682 | RMPT10BD | Environment | standards | DIN 43760 EN/IEC 60584-1 EN/IEC 60947-1 EN/IEC 60751
7683 | RMPT10BD | Environment | product certifications | UL GL CSA
7684 | RMPT10BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
7685 | RMPT10BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
7686 | RMPT10BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
7687 | RMPT10BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
7688 | RMPT10BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
7689 | RMPT10BD | Environment | disturbance radiated/conducted | CISPR 11 CISPR 22 group 1 - class B
7690 | RMPT10BD | Environment | ambient air temperature for storage | -40…85 °C
7691 | RMPT10BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
7692 | RMPT10BD | Environment | pollution degree | 2 conforming to IEC 60664-1
7693 | RMPT10BD | Packing Units | Package 1 Weight | 0.125 kg
7694 | RMPT10BD | Packing Units | Package 1 Height | 0.270 dm
7695 | RMPT10BD | Packing Units | Package 1 width | 0.820 dm
7696 | RMPT10BD | Packing Units | Package 1 Length | 0.850 dm
7697 | RMPT10BD | Offer Sustainability | Sustainable offer status | Green Premium product
7698 | RMPT10BD | Offer Sustainability | REACh Regulation | REACh Declaration
7699 | RMPT10BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7700 | RMPT10BD | Offer Sustainability | Mercury free | Yes
7701 | RMPT10BD | Offer Sustainability | RoHS exemption information | Yes
7702 | RMPT10BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7703 | RMPT10BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7704 | RMPT10BD | Offer Sustainability | Circularity Profile | End of Life Information
7705 | RMPT10BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7706 | RMPT10BD | Contractual warranty | Warranty | 18 months
7707 | RMPT20BD | Main | range of product | Zelio Analog
7708 | RMPT20BD | Main | product or component type | Converter for Universal Pt100 probes
7709 | RMPT20BD | Main | analogue input type | Temperature probe - 100...100 °C/- 148...212 °F Pt 100 2, 3 or 4 wires
7710 | RMPT20BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
7711 | RMPT20BD | Complementary | protection type | Reverse polarity protection on output Overvoltage protection on output (+/- 30 V) Reverse polarity protection on power supply Short-circuit protection on output
7712 | RMPT20BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
7713 | RMPT20BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken
7714 | RMPT20BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
7715 | RMPT20BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output
7716 | RMPT20BD | Complementary | local signalling | LED (green)power ON:
7717 | RMPT20BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
7718 | RMPT20BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C
7719 | RMPT20BD | Complementary | temperature coefficient | 150 ppm/°C
7720 | RMPT20BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
7721 | RMPT20BD | Complementary | clamping connection capacity | 1 x 2.5 mm² 2 x 1.5 mm²
7722 | RMPT20BD | Complementary | tightening torque | 0.6…1.1 N.m
7723 | RMPT20BD | Complementary | marking | CE
7724 | RMPT20BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
7725 | RMPT20BD | Complementary | [Ui] rated insulation voltage | 2000 V
7726 | RMPT20BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) Fixed (mounting plate)
7727 | RMPT20BD | Complementary | safety reliability data | MTTFd = 32.9 years B10d = 30437
7728 | RMPT20BD | Complementary | net weight | 0.12 kg
7729 | RMPT20BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
7730 | RMPT20BD | Environment | standards | DIN 43760 EN/IEC 60751 EN/IEC 60584-1 EN/IEC 60947-1
7731 | RMPT20BD | Environment | product certifications | GL CSA UL
7732 | RMPT20BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
7733 | RMPT20BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
7734 | RMPT20BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
7735 | RMPT20BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
7736 | RMPT20BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
7737 | RMPT20BD | Environment | disturbance radiated/conducted | CISPR 11 CISPR 22 group 1 - class B
7738 | RMPT20BD | Environment | ambient air temperature for storage | -40…85 °C
7739 | RMPT20BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
7740 | RMPT20BD | Environment | pollution degree | 2 conforming to IEC 60664-1
7741 | RMPT20BD | Packing Units | Package 1 Weight | 0.108 kg
7742 | RMPT20BD | Packing Units | Package 1 Height | 0.270 dm
7743 | RMPT20BD | Packing Units | Package 1 width | 0.820 dm
7744 | RMPT20BD | Packing Units | Package 1 Length | 0.850 dm
7745 | RMPT20BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7746 | RMPT20BD | Offer Sustainability | Mercury free | Yes
7747 | RMPT20BD | Offer Sustainability | RoHS exemption information | Yes
7748 | RMPT20BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7749 | RMPT20BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7750 | RMPT20BD | Offer Sustainability | Circularity Profile | End of Life Information
7751 | RMPT20BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7752 | RMPT20BD | Contractual warranty | Warranty | 18 months
7753 | RMPT30BD | Main | range of product | Zelio Analog
7754 | RMPT30BD | Main | product or component type | Converter for Universal Pt100 probes
7755 | RMPT30BD | Main | analogue input type | Temperature probe 0...100 °C/32..212 °F Pt 100 2, 3 or 4 wires
7756 | RMPT30BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
7757 | RMPT30BD | Complementary | protection type | Reverse polarity protection on power supply Short-circuit protection on output Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output
7758 | RMPT30BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
7759 | RMPT30BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken
7760 | RMPT30BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
7761 | RMPT30BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output
7762 | RMPT30BD | Complementary | local signalling | LED (green)power ON:
7763 | RMPT30BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
7764 | RMPT30BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C
7765 | RMPT30BD | Complementary | temperature coefficient | 150 ppm/°C
7766 | RMPT30BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
7767 | RMPT30BD | Complementary | clamping connection capacity | 1 x 2.5 mm² 2 x 1.5 mm²
7768 | RMPT30BD | Complementary | tightening torque | 0.6…1.1 N.m
7769 | RMPT30BD | Complementary | marking | CE
7770 | RMPT30BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
7771 | RMPT30BD | Complementary | [Ui] rated insulation voltage | 2000 V
7772 | RMPT30BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) Fixed (mounting plate)
7773 | RMPT30BD | Complementary | safety reliability data | MTTFd = 32.9 years B10d = 30437
7774 | RMPT30BD | Complementary | net weight | 0.12 kg
7775 | RMPT30BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
7776 | RMPT30BD | Environment | standards | DIN 43760 EN/IEC 60751 EN/IEC 60947-1 EN/IEC 60584-1
7777 | RMPT30BD | Environment | product certifications | GL UL CSA
7778 | RMPT30BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
7779 | RMPT30BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
7780 | RMPT30BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
7781 | RMPT30BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
7782 | RMPT30BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
7783 | RMPT30BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B CISPR 11
7784 | RMPT30BD | Environment | ambient air temperature for storage | -40…85 °C
7785 | RMPT30BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
7786 | RMPT30BD | Environment | pollution degree | 2 conforming to IEC 60664-1
7787 | RMPT30BD | Packing Units | Package 1 Weight | 0.108 kg
7788 | RMPT30BD | Packing Units | Package 1 Height | 0.270 dm
7789 | RMPT30BD | Packing Units | Package 1 width | 0.820 dm
7790 | RMPT30BD | Packing Units | Package 1 Length | 0.850 dm
7791 | RMPT30BD | Offer Sustainability | Sustainable offer status | Green Premium product
7792 | RMPT30BD | Offer Sustainability | REACh Regulation | REACh Declaration
7793 | RMPT30BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7794 | RMPT30BD | Offer Sustainability | Mercury free | Yes
7795 | RMPT30BD | Offer Sustainability | RoHS exemption information | Yes
7796 | RMPT30BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7797 | RMPT30BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7798 | RMPT30BD | Offer Sustainability | Circularity Profile | End of Life Information
7799 | RMPT30BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7800 | RMPT30BD | Contractual warranty | Warranty | 18 months
7801 | RMPT50BD | Main | range of product | Zelio Analog
7802 | RMPT50BD | Main | product or component type | Converter for Universal Pt100 probes
7803 | RMPT50BD | Main | analogue input type | Temperature probe 0...250 °C/32...482 °F Pt 100 2, 3 or 4 wires
7804 | RMPT50BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
7805 | RMPT50BD | Complementary | protection type | Reverse polarity protection on output Short-circuit protection on output Reverse polarity protection on power supply Overvoltage protection on output (+/- 30 V)
7806 | RMPT50BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
7807 | RMPT50BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken
7808 | RMPT50BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
7809 | RMPT50BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output
7810 | RMPT50BD | Complementary | local signalling | LED (green)power ON:
7811 | RMPT50BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
7812 | RMPT50BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C
7813 | RMPT50BD | Complementary | temperature coefficient | 150 ppm/°C
7814 | RMPT50BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
7815 | RMPT50BD | Complementary | clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm²
7816 | RMPT50BD | Complementary | tightening torque | 0.6…1.1 N.m
7817 | RMPT50BD | Complementary | marking | CE
7818 | RMPT50BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
7819 | RMPT50BD | Complementary | [Ui] rated insulation voltage | 2000 V
7820 | RMPT50BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) Fixed (mounting plate)
7821 | RMPT50BD | Complementary | safety reliability data | B10d = 30437 MTTFd = 32.9 years
7822 | RMPT50BD | Complementary | net weight | 0.12 kg
7823 | RMPT50BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
7824 | RMPT50BD | Environment | standards | EN/IEC 60947-1 EN/IEC 60584-1 DIN 43760 EN/IEC 60751
7825 | RMPT50BD | Environment | product certifications | CSA UL GL
7826 | RMPT50BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
7827 | RMPT50BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
7828 | RMPT50BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
7829 | RMPT50BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
7830 | RMPT50BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
7831 | RMPT50BD | Environment | disturbance radiated/conducted | CISPR 11 CISPR 22 group 1 - class B
7832 | RMPT50BD | Environment | ambient air temperature for storage | -40…85 °C
7833 | RMPT50BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
7834 | RMPT50BD | Environment | pollution degree | 2 conforming to IEC 60664-1
7835 | RMPT50BD | Packing Units | Package 1 Weight | 0.106 kg
7836 | RMPT50BD | Packing Units | Package 1 Height | 0.270 dm
7837 | RMPT50BD | Packing Units | Package 1 width | 0.820 dm
7838 | RMPT50BD | Packing Units | Package 1 Length | 0.850 dm
7839 | RMPT50BD | Offer Sustainability | Sustainable offer status | Green Premium product
7840 | RMPT50BD | Offer Sustainability | REACh Regulation | REACh Declaration
7841 | RMPT50BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7842 | RMPT50BD | Offer Sustainability | Mercury free | Yes
7843 | RMPT50BD | Offer Sustainability | RoHS exemption information | Yes
7844 | RMPT50BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7845 | RMPT50BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7846 | RMPT50BD | Offer Sustainability | Circularity Profile | End of Life Information
7847 | RMPT50BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7848 | RMPT50BD | Contractual warranty | Warranty | 18 months
7849 | RMPT13BD | Main | range of product | Zelio Analog
7850 | RMPT13BD | Main | product or component type | Converter for Optimum Pt100 probes
7851 | RMPT13BD | Main | analogue input type | Temperature probe - 40...40 °C/- 40...104 °F Pt 100 2, 3 or 4 wires
7852 | RMPT13BD | Main | analogue output type | Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
7853 | RMPT13BD | Complementary | protection type | Reverse polarity protection on output Overvoltage protection on output (+/- 30 V) Reverse polarity protection on power supply Short-circuit protection on output
7854 | RMPT13BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
7855 | RMPT13BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken
7856 | RMPT13BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
7857 | RMPT13BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output
7858 | RMPT13BD | Complementary | local signalling | LED (green)power ON:
7859 | RMPT13BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
7860 | RMPT13BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C
7861 | RMPT13BD | Complementary | temperature coefficient | 150 ppm/°C
7862 | RMPT13BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
7863 | RMPT13BD | Complementary | clamping connection capacity | 1 x 2.5 mm² 2 x 1.5 mm²
7864 | RMPT13BD | Complementary | tightening torque | 0.6…1.1 N.m
7865 | RMPT13BD | Complementary | marking | CE
7866 | RMPT13BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
7867 | RMPT13BD | Complementary | [Ui] rated insulation voltage | 2000 V
7868 | RMPT13BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) Fixed (mounting plate)
7869 | RMPT13BD | Complementary | safety reliability data | B10d = 40564 MTTFd = 43.9 years
7870 | RMPT13BD | Complementary | net weight | 0.12 kg
7871 | RMPT13BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
7872 | RMPT13BD | Environment | standards | EN/IEC 60751 EN/IEC 60584-1 DIN 43760 EN/IEC 60947-1
7873 | RMPT13BD | Environment | product certifications | CSA UL GL
7874 | RMPT13BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
7875 | RMPT13BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
7876 | RMPT13BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
7877 | RMPT13BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
7878 | RMPT13BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
7879 | RMPT13BD | Environment | disturbance radiated/conducted | CISPR 11 CISPR 22 group 1 - class B
7880 | RMPT13BD | Environment | ambient air temperature for storage | -40…85 °C
7881 | RMPT13BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
7882 | RMPT13BD | Environment | pollution degree | 2 conforming to IEC 60664-1
7883 | RMPT13BD | Packing Units | Package 1 Weight | 0.108 kg
7884 | RMPT13BD | Packing Units | Package 1 Height | 0.270 dm
7885 | RMPT13BD | Packing Units | Package 1 width | 0.820 dm
7886 | RMPT13BD | Packing Units | Package 1 Length | 0.850 dm
7887 | RMPT13BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7888 | RMPT13BD | Offer Sustainability | Mercury free | Yes
7889 | RMPT13BD | Offer Sustainability | RoHS exemption information | Yes
7890 | RMPT13BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7891 | RMPT13BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7892 | RMPT13BD | Offer Sustainability | Circularity Profile | End of Life Information
7893 | RMPT13BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7894 | RMPT13BD | Contractual warranty | Warranty | 18 months
7895 | RMPT23BD | Main | range of product | Zelio Analog
7896 | RMPT23BD | Main | product or component type | Converter for Optimum Pt100 probes
7897 | RMPT23BD | Main | analogue input type | Temperature probe - 100...100 °C/- 148...212 °F Pt 100 2, 3 or 4 wires
7898 | RMPT23BD | Main | analogue output type | Voltage 0...10 V >= 100 kOhm
7899 | RMPT23BD | Complementary | protection type | Reverse polarity protection on power supply Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output
7900 | RMPT23BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
7901 | RMPT23BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken
7902 | RMPT23BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
7903 | RMPT23BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output
7904 | RMPT23BD | Complementary | local signalling | LED (green)power ON:
7905 | RMPT23BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
7906 | RMPT23BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C
7907 | RMPT23BD | Complementary | temperature coefficient | 150 ppm/°C
7908 | RMPT23BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
7909 | RMPT23BD | Complementary | clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm²
7910 | RMPT23BD | Complementary | tightening torque | 0.6…1.1 N.m
7911 | RMPT23BD | Complementary | marking | CE
7912 | RMPT23BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
7913 | RMPT23BD | Complementary | [Ui] rated insulation voltage | 2000 V
7914 | RMPT23BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) Fixed (mounting plate)
7915 | RMPT23BD | Complementary | safety reliability data | B10d = 40564 MTTFd = 43.9 years
7916 | RMPT23BD | Complementary | net weight | 0.12 kg
7917 | RMPT23BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
7918 | RMPT23BD | Environment | standards | EN/IEC 60947-1 EN/IEC 60584-1 DIN 43760 EN/IEC 60751
7919 | RMPT23BD | Environment | product certifications | CSA UL GL
7920 | RMPT23BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
7921 | RMPT23BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
7922 | RMPT23BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
7923 | RMPT23BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
7924 | RMPT23BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
7925 | RMPT23BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B CISPR 11
7926 | RMPT23BD | Environment | ambient air temperature for storage | -40…85 °C
7927 | RMPT23BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
7928 | RMPT23BD | Environment | pollution degree | 2 conforming to IEC 60664-1
7929 | RMPT23BD | Packing Units | Package 1 Weight | 0.108 kg
7930 | RMPT23BD | Packing Units | Package 1 Height | 0.270 dm
7931 | RMPT23BD | Packing Units | Package 1 width | 0.820 dm
7932 | RMPT23BD | Packing Units | Package 1 Length | 0.850 dm
7933 | RMPT23BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7934 | RMPT23BD | Offer Sustainability | Mercury free | Yes
7935 | RMPT23BD | Offer Sustainability | RoHS exemption information | Yes
7936 | RMPT23BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7937 | RMPT23BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7938 | RMPT23BD | Offer Sustainability | Circularity Profile | End of Life Information
7939 | RMPT23BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7940 | RMPT23BD | Contractual warranty | Warranty | 18 months
7941 | RMPT33BD | Main | range of product | Zelio Analog
7942 | RMPT33BD | Main | product or component type | Converter for Optimum Pt100 probes
7943 | RMPT33BD | Main | analogue input type | Temperature probe 0...100 °C/32..212 °F Pt 100 2, 3 or 4 wires
7944 | RMPT33BD | Main | analogue output type | Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
7945 | RMPT33BD | Complementary | protection type | Short-circuit protection on output Reverse polarity protection on output Overvoltage protection on output (+/- 30 V) Reverse polarity protection on power supply
7946 | RMPT33BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
7947 | RMPT33BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken
7948 | RMPT33BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
7949 | RMPT33BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output
7950 | RMPT33BD | Complementary | local signalling | LED (green)power ON:
7951 | RMPT33BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
7952 | RMPT33BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C
7953 | RMPT33BD | Complementary | temperature coefficient | 150 ppm/°C
7954 | RMPT33BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
7955 | RMPT33BD | Complementary | clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm²
7956 | RMPT33BD | Complementary | tightening torque | 0.6…1.1 N.m
7957 | RMPT33BD | Complementary | marking | CE
7958 | RMPT33BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
7959 | RMPT33BD | Complementary | [Ui] rated insulation voltage | 2000 V
7960 | RMPT33BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) Fixed (mounting plate)
7961 | RMPT33BD | Complementary | safety reliability data | MTTFd = 43.9 years B10d = 40564
7962 | RMPT33BD | Complementary | net weight | 0.12 kg
7963 | RMPT33BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
7964 | RMPT33BD | Environment | standards | DIN 43760 EN/IEC 60584-1 EN/IEC 60751 EN/IEC 60947-1
7965 | RMPT33BD | Environment | product certifications | UL GL CSA
7966 | RMPT33BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
7967 | RMPT33BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
7968 | RMPT33BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
7969 | RMPT33BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
7970 | RMPT33BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
7971 | RMPT33BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B CISPR 11
7972 | RMPT33BD | Environment | ambient air temperature for storage | -40…85 °C
7973 | RMPT33BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
7974 | RMPT33BD | Environment | pollution degree | 2 conforming to IEC 60664-1
7975 | RMPT33BD | Packing Units | Package 1 Weight | 0.109 kg
7976 | RMPT33BD | Packing Units | Package 1 Height | 0.270 dm
7977 | RMPT33BD | Packing Units | Package 1 width | 0.820 dm
7978 | RMPT33BD | Packing Units | Package 1 Length | 0.850 dm
7979 | RMPT33BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
7980 | RMPT33BD | Offer Sustainability | Mercury free | Yes
7981 | RMPT33BD | Offer Sustainability | RoHS exemption information | Yes
7982 | RMPT33BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
7983 | RMPT33BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
7984 | RMPT33BD | Offer Sustainability | Circularity Profile | End of Life Information
7985 | RMPT33BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
7986 | RMPT33BD | Contractual warranty | Warranty | 18 months
7987 | RMPT53BD | Main | range of product | Zelio Analog
7988 | RMPT53BD | Main | product or component type | Converter for Optimum Pt100 probes
7989 | RMPT53BD | Main | analogue input type | Temperature probe 0...250 °C/32...482 °F Pt 100 2, 3 or 4 wires
7990 | RMPT53BD | Main | analogue output type | Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
7991 | RMPT53BD | Complementary | protection type | Short-circuit protection on output Reverse polarity protection on power supply Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output
7992 | RMPT53BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
7993 | RMPT53BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken
7994 | RMPT53BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
7995 | RMPT53BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output
7996 | RMPT53BD | Complementary | local signalling | LED (green)power ON:
7997 | RMPT53BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
7998 | RMPT53BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C
7999 | RMPT53BD | Complementary | temperature coefficient | 150 ppm/°C
8000 | RMPT53BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
8001 | RMPT53BD | Complementary | clamping connection capacity | 1 x 2.5 mm² 2 x 1.5 mm²
8002 | RMPT53BD | Complementary | tightening torque | 0.6…1.1 N.m
8003 | RMPT53BD | Complementary | marking | CE
8004 | RMPT53BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
8005 | RMPT53BD | Complementary | [Ui] rated insulation voltage | 2000 V
8006 | RMPT53BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) Fixed (mounting plate)
8007 | RMPT53BD | Complementary | safety reliability data | MTTFd = 43.9 years B10d = 40564
8008 | RMPT53BD | Complementary | net weight | 0.12 kg
8009 | RMPT53BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
8010 | RMPT53BD | Environment | standards | DIN 43760 EN/IEC 60751 EN/IEC 60947-1 EN/IEC 60584-1
8011 | RMPT53BD | Environment | product certifications | UL CSA GL
8012 | RMPT53BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
8013 | RMPT53BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
8014 | RMPT53BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
8015 | RMPT53BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
8016 | RMPT53BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
8017 | RMPT53BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B CISPR 11
8018 | RMPT53BD | Environment | ambient air temperature for storage | -40…85 °C
8019 | RMPT53BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
8020 | RMPT53BD | Environment | pollution degree | 2 conforming to IEC 60664-1
8021 | RMPT53BD | Packing Units | Package 1 Weight | 0.102 kg
8022 | RMPT53BD | Packing Units | Package 1 Height | 0.270 dm
8023 | RMPT53BD | Packing Units | Package 1 width | 0.820 dm
8024 | RMPT53BD | Packing Units | Package 1 Length | 0.850 dm
8025 | RMPT53BD | Offer Sustainability | Sustainable offer status | Green Premium product
8026 | RMPT53BD | Offer Sustainability | REACh Regulation | REACh Declaration
8027 | RMPT53BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8028 | RMPT53BD | Offer Sustainability | Mercury free | Yes
8029 | RMPT53BD | Offer Sustainability | RoHS exemption information | Yes
8030 | RMPT53BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8031 | RMPT53BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8032 | RMPT53BD | Offer Sustainability | Circularity Profile | End of Life Information
8033 | RMPT53BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8034 | RMPT53BD | Contractual warranty | Warranty | 18 months
8035 | RMPT73BD | Main | range of product | Zelio Analog
8036 | RMPT73BD | Main | product or component type | Converter for Optimum Pt100 probes
8037 | RMPT73BD | Main | analogue input type | Temperature probe 0...500 °C/32...932 °F Pt 100 2, 3 or 4 wires
8038 | RMPT73BD | Main | analogue output type | Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
8039 | RMPT73BD | Complementary | protection type | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on power supply Short-circuit protection on output Reverse polarity protection on output
8040 | RMPT73BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
8041 | RMPT73BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken
8042 | RMPT73BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
8043 | RMPT73BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output
8044 | RMPT73BD | Complementary | local signalling | LED (green)power ON:
8045 | RMPT73BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
8046 | RMPT73BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C
8047 | RMPT73BD | Complementary | temperature coefficient | 150 ppm/°C
8048 | RMPT73BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
8049 | RMPT73BD | Complementary | clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm²
8050 | RMPT73BD | Complementary | tightening torque | 0.6…1.1 N.m
8051 | RMPT73BD | Complementary | marking | CE
8052 | RMPT73BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
8053 | RMPT73BD | Complementary | [Ui] rated insulation voltage | 2000 V
8054 | RMPT73BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) Fixed (mounting plate)
8055 | RMPT73BD | Complementary | safety reliability data | MTTFd = 43.9 years B10d = 40564
8056 | RMPT73BD | Complementary | net weight | 0.12 kg
8057 | RMPT73BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
8058 | RMPT73BD | Environment | standards | DIN 43760 EN/IEC 60584-1 EN/IEC 60947-1 EN/IEC 60751
8059 | RMPT73BD | Environment | product certifications | GL UL CSA
8060 | RMPT73BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
8061 | RMPT73BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
8062 | RMPT73BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
8063 | RMPT73BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
8064 | RMPT73BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
8065 | RMPT73BD | Environment | disturbance radiated/conducted | CISPR 11 CISPR 22 group 1 - class B
8066 | RMPT73BD | Environment | ambient air temperature for storage | -40…85 °C
8067 | RMPT73BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
8068 | RMPT73BD | Environment | pollution degree | 2 conforming to IEC 60664-1
8069 | RMPT73BD | Packing Units | Package 1 Weight | 0.109 kg
8070 | RMPT73BD | Packing Units | Package 1 Height | 0.270 dm
8071 | RMPT73BD | Packing Units | Package 1 width | 0.820 dm
8072 | RMPT73BD | Packing Units | Package 1 Length | 0.850 dm
8073 | RMPT73BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8074 | RMPT73BD | Offer Sustainability | Mercury free | Yes
8075 | RMPT73BD | Offer Sustainability | RoHS exemption information | Yes
8076 | RMPT73BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8077 | RMPT73BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8078 | RMPT73BD | Offer Sustainability | Circularity Profile | End of Life Information
8079 | RMPT73BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8080 | RMPT73BD | Contractual warranty | Warranty | 18 months
8081 | RMTJ40BD | Main | range of product | Zelio Analog
8082 | RMTJ40BD | Main | product or component type | Converter for thermocouples
8083 | RMTJ40BD | Main | analogue input type | Thermocouple 0...150 °C/32...302 °F thermocouple J conforming to IEC 60584
8084 | RMTJ40BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
8085 | RMTJ40BD | Complementary | protection type | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output
8086 | RMTJ40BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
8087 | RMTJ40BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken
8088 | RMTJ40BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, non isolated
8089 | RMTJ40BD | Complementary | current consumption | <= 60 mA for current output
8090 | RMTJ40BD | Complementary | local signalling | LED (green)power ON:
8091 | RMTJ40BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C
8092 | RMTJ40BD | Complementary | repeat accuracy | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C
8093 | RMTJ40BD | Complementary | temperature coefficient | 200 ppm/°C
8094 | RMTJ40BD | Complementary | cold junction compensation | Built-in, measurement: between 0 and 60 °C
8095 | RMTJ40BD | Complementary | clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm²
8096 | RMTJ40BD | Complementary | tightening torque | 0.6…1.1 N.m
8097 | RMTJ40BD | Complementary | marking | CE
8098 | RMTJ40BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
8099 | RMTJ40BD | Complementary | [Ui] rated insulation voltage | 2 kV
8100 | RMTJ40BD | Complementary | fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
8101 | RMTJ40BD | Complementary | safety reliability data | B10d = 45447 MTTFd = 49.2 years
8102 | RMTJ40BD | Complementary | net weight | 0.12 kg
8103 | RMTJ40BD | Environment | standards | IEC 60947-1 IEC 60584-1
8104 | RMTJ40BD | Environment | product certifications | CSA GL UL
8105 | RMTJ40BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
8106 | RMTJ40BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
8107 | RMTJ40BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
8108 | RMTJ40BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
8109 | RMTJ40BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
8110 | RMTJ40BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
8111 | RMTJ40BD | Environment | disturbance radiated/conducted | CISPR 11 CISPR 22 group 1 - class B
8112 | RMTJ40BD | Environment | ambient air temperature for storage | -40…85 °C
8113 | RMTJ40BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
8114 | RMTJ40BD | Environment | pollution degree | 2 conforming to IEC 60664-1
8115 | RMTJ40BD | Packing Units | Package 1 Weight | 0.101 kg
8116 | RMTJ40BD | Packing Units | Package 1 Height | 0.270 dm
8117 | RMTJ40BD | Packing Units | Package 1 width | 0.820 dm
8118 | RMTJ40BD | Packing Units | Package 1 Length | 0.850 dm
8119 | RMTJ40BD | Offer Sustainability | Sustainable offer status | Green Premium product
8120 | RMTJ40BD | Offer Sustainability | REACh Regulation | REACh Declaration
8121 | RMTJ40BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8122 | RMTJ40BD | Offer Sustainability | Mercury free | Yes
8123 | RMTJ40BD | Offer Sustainability | RoHS exemption information | Yes
8124 | RMTJ40BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8125 | RMTJ40BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8126 | RMTJ40BD | Offer Sustainability | Circularity Profile | End of Life Information
8127 | RMTJ40BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8128 | RMTJ40BD | Contractual warranty | Warranty | 18 months
8129 | RMTJ60BD | Main | range of product | Zelio Analog
8130 | RMTJ60BD | Main | product or component type | Converter for thermocouples
8131 | RMTJ60BD | Main | analogue input type | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584
8132 | RMTJ60BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
8133 | RMTJ60BD | Complementary | protection type | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output
8134 | RMTJ60BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
8135 | RMTJ60BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken
8136 | RMTJ60BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, non isolated
8137 | RMTJ60BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output
8138 | RMTJ60BD | Complementary | local signalling | LED (green)power ON:
8139 | RMTJ60BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C
8140 | RMTJ60BD | Complementary | repeat accuracy | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C
8141 | RMTJ60BD | Complementary | temperature coefficient | 200 ppm/°C
8142 | RMTJ60BD | Complementary | cold junction compensation | Built-in, measurement: between 0 and 60 °C
8143 | RMTJ60BD | Complementary | clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm²
8144 | RMTJ60BD | Complementary | tightening torque | 0.6…1.1 N.m
8145 | RMTJ60BD | Complementary | marking | CE
8146 | RMTJ60BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
8147 | RMTJ60BD | Complementary | [Ui] rated insulation voltage | 2 kV
8148 | RMTJ60BD | Complementary | fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
8149 | RMTJ60BD | Complementary | safety reliability data | B10d = 45447 MTTFd = 49.2 years
8150 | RMTJ60BD | Complementary | net weight | 0.12 kg
8151 | RMTJ60BD | Environment | standards | IEC 60584-1 IEC 60947-1
8152 | RMTJ60BD | Environment | product certifications | CSA GL UL
8153 | RMTJ60BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
8154 | RMTJ60BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
8155 | RMTJ60BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
8156 | RMTJ60BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
8157 | RMTJ60BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
8158 | RMTJ60BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
8159 | RMTJ60BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B CISPR 11
8160 | RMTJ60BD | Environment | ambient air temperature for storage | -40…85 °C
8161 | RMTJ60BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
8162 | RMTJ60BD | Environment | pollution degree | 2 conforming to IEC 60664-1
8163 | RMTJ60BD | Packing Units | Package 1 Weight | 0.101 kg
8164 | RMTJ60BD | Packing Units | Package 1 Height | 0.270 dm
8165 | RMTJ60BD | Packing Units | Package 1 width | 0.820 dm
8166 | RMTJ60BD | Packing Units | Package 1 Length | 0.850 dm
8167 | RMTJ60BD | Offer Sustainability | Sustainable offer status | Green Premium product
8168 | RMTJ60BD | Offer Sustainability | REACh Regulation | REACh Declaration
8169 | RMTJ60BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8170 | RMTJ60BD | Offer Sustainability | Mercury free | Yes
8171 | RMTJ60BD | Offer Sustainability | RoHS exemption information | Yes
8172 | RMTJ60BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8173 | RMTJ60BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8174 | RMTJ60BD | Offer Sustainability | Circularity Profile | End of Life Information
8175 | RMTJ60BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8176 | RMTJ60BD | Contractual warranty | Warranty | 18 months
8177 | RMTJ80BD | Main | range of product | Zelio Analog
8178 | RMTJ80BD | Main | product or component type | Converter for thermocouples
8179 | RMTJ80BD | Main | analogue input type | Thermocouple 0...600 °C/32...1112 °F thermocouple J conforming to IEC 60584
8180 | RMTJ80BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
8181 | RMTJ80BD | Complementary | protection type | Reverse polarity protection on output Overvoltage protection on output (+/- 30 V) Short-circuit protection on output
8182 | RMTJ80BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
8183 | RMTJ80BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken
8184 | RMTJ80BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, non isolated
8185 | RMTJ80BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output
8186 | RMTJ80BD | Complementary | local signalling | LED (green)power ON:
8187 | RMTJ80BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C
8188 | RMTJ80BD | Complementary | repeat accuracy | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C
8189 | RMTJ80BD | Complementary | temperature coefficient | 200 ppm/°C
8190 | RMTJ80BD | Complementary | cold junction compensation | Built-in, measurement: between 0 and 60 °C
8191 | RMTJ80BD | Complementary | clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm²
8192 | RMTJ80BD | Complementary | tightening torque | 0.6…1.1 N.m
8193 | RMTJ80BD | Complementary | marking | CE
8194 | RMTJ80BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
8195 | RMTJ80BD | Complementary | [Ui] rated insulation voltage | 2 kV
8196 | RMTJ80BD | Complementary | fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
8197 | RMTJ80BD | Complementary | safety reliability data | MTTFd = 49.2 years B10d = 45447
8198 | RMTJ80BD | Complementary | net weight | 0.12 kg
8199 | RMTJ80BD | Environment | standards | IEC 60584-1 IEC 60947-1
8200 | RMTJ80BD | Environment | product certifications | UL GL CSA
8201 | RMTJ80BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
8202 | RMTJ80BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
8203 | RMTJ80BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
8204 | RMTJ80BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
8205 | RMTJ80BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
8206 | RMTJ80BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
8207 | RMTJ80BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B CISPR 11
8208 | RMTJ80BD | Environment | ambient air temperature for storage | -40…85 °C
8209 | RMTJ80BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
8210 | RMTJ80BD | Environment | pollution degree | 2 conforming to IEC 60664-1
8211 | RMTJ80BD | Offer Sustainability | Sustainable offer status | Green Premium product
8212 | RMTJ80BD | Offer Sustainability | REACh Regulation | REACh Declaration
8213 | RMTJ80BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8214 | RMTJ80BD | Offer Sustainability | Mercury free | Yes
8215 | RMTJ80BD | Offer Sustainability | RoHS exemption information | Yes
8216 | RMTJ80BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8217 | RMTJ80BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8218 | RMTJ80BD | Offer Sustainability | Circularity Profile | End of Life Information
8219 | RMTJ80BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8220 | RMTJ80BD | Contractual warranty | Warranty | 18 months
8221 | RMTK80BD | Main | range of product | Zelio Analog
8222 | RMTK80BD | Main | product or component type | Converter for thermocouples
8223 | RMTK80BD | Main | analogue input type | Thermocouple 0...600 °C/32...1112 °F thermocouple K conforming to IEC 60584
8224 | RMTK80BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
8225 | RMTK80BD | Complementary | protection type | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output
8226 | RMTK80BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
8227 | RMTK80BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken
8228 | RMTK80BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, non isolated
8229 | RMTK80BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output
8230 | RMTK80BD | Complementary | local signalling | LED (green)power ON:
8231 | RMTK80BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C
8232 | RMTK80BD | Complementary | repeat accuracy | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C
8233 | RMTK80BD | Complementary | temperature coefficient | 200 ppm/°C
8234 | RMTK80BD | Complementary | cold junction compensation | Built-in, measurement: between 0 and 60 °C
8235 | RMTK80BD | Complementary | clamping connection capacity | 1 x 2.5 mm² 2 x 1.5 mm²
8236 | RMTK80BD | Complementary | tightening torque | 0.6…1.1 N.m
8237 | RMTK80BD | Complementary | marking | CE
8238 | RMTK80BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
8239 | RMTK80BD | Complementary | [Ui] rated insulation voltage | 2 kV
8240 | RMTK80BD | Complementary | fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
8241 | RMTK80BD | Complementary | safety reliability data | MTTFd = 49.2 years B10d = 45447
8242 | RMTK80BD | Complementary | net weight | 0.12 kg
8243 | RMTK80BD | Environment | standards | IEC 60584-1 IEC 60947-1
8244 | RMTK80BD | Environment | product certifications | CSA UL GL
8245 | RMTK80BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
8246 | RMTK80BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
8247 | RMTK80BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
8248 | RMTK80BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
8249 | RMTK80BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
8250 | RMTK80BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
8251 | RMTK80BD | Environment | disturbance radiated/conducted | CISPR 11 CISPR 22 group 1 - class B
8252 | RMTK80BD | Environment | ambient air temperature for storage | -40…85 °C
8253 | RMTK80BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
8254 | RMTK80BD | Environment | pollution degree | 2 conforming to IEC 60664-1
8255 | RMTK80BD | Packing Units | Package 1 Weight | 0.101 kg
8256 | RMTK80BD | Packing Units | Package 1 Height | 0.270 dm
8257 | RMTK80BD | Packing Units | Package 1 width | 0.820 dm
8258 | RMTK80BD | Packing Units | Package 1 Length | 0.850 dm
8259 | RMTK80BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8260 | RMTK80BD | Offer Sustainability | Mercury free | Yes
8261 | RMTK80BD | Offer Sustainability | RoHS exemption information | Yes
8262 | RMTK80BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8263 | RMTK80BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8264 | RMTK80BD | Offer Sustainability | Circularity Profile | End of Life Information
8265 | RMTK80BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8266 | RMTK80BD | Contractual warranty | Warranty | 18 months
8267 | RMTK90BD | Main | range of product | Zelio Analog
8268 | RMTK90BD | Main | product or component type | Converter for thermocouples
8269 | RMTK90BD | Main | analogue input type | Thermocouple 0...1200 °C/32...2192 °F thermocouple K conforming to IEC 60584
8270 | RMTK90BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
8271 | RMTK90BD | Complementary | protection type | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output
8272 | RMTK90BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
8273 | RMTK90BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken
8274 | RMTK90BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, non isolated
8275 | RMTK90BD | Complementary | current consumption | <= 40 mA for voltage <= 40 mA for voltage output <= 60 mA for current
8276 | RMTK90BD | Complementary | local signalling | LED (green)power ON:
8277 | RMTK90BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C
8278 | RMTK90BD | Complementary | repeat accuracy | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C
8279 | RMTK90BD | Complementary | temperature coefficient | 200 ppm/°C
8280 | RMTK90BD | Complementary | cold junction compensation | Built-in, measurement: between 0 and 60 °C
8281 | RMTK90BD | Complementary | clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm²
8282 | RMTK90BD | Complementary | tightening torque | 0.6…1.1 N.m
8283 | RMTK90BD | Complementary | marking | CE
8284 | RMTK90BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
8285 | RMTK90BD | Complementary | [Ui] rated insulation voltage | 2 kV
8286 | RMTK90BD | Complementary | fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
8287 | RMTK90BD | Complementary | safety reliability data | MTTFd = 49.2 years B10d = 45447
8288 | RMTK90BD | Complementary | net weight | 0.12 kg
8289 | RMTK90BD | Environment | standards | IEC 60584-1 IEC 60947-1
8290 | RMTK90BD | Environment | product certifications | GL UL CSA
8291 | RMTK90BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
8292 | RMTK90BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
8293 | RMTK90BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
8294 | RMTK90BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
8295 | RMTK90BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
8296 | RMTK90BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
8297 | RMTK90BD | Environment | disturbance radiated/conducted | CISPR 11 CISPR 22 group 1 - class B
8298 | RMTK90BD | Environment | ambient air temperature for storage | -40…85 °C
8299 | RMTK90BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
8300 | RMTK90BD | Environment | pollution degree | 2 conforming to IEC 60664-1
8301 | RMTK90BD | Packing Units | Package 1 Weight | 0.101 kg
8302 | RMTK90BD | Packing Units | Package 1 Height | 0.270 dm
8303 | RMTK90BD | Packing Units | Package 1 width | 0.820 dm
8304 | RMTK90BD | Packing Units | Package 1 Length | 0.850 dm
8305 | RMTK90BD | Offer Sustainability | Sustainable offer status | Green Premium product
8306 | RMTK90BD | Offer Sustainability | REACh Regulation | REACh Declaration
8307 | RMTK90BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8308 | RMTK90BD | Offer Sustainability | Mercury free | Yes
8309 | RMTK90BD | Offer Sustainability | RoHS exemption information | Yes
8310 | RMTK90BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8311 | RMTK90BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8312 | RMTK90BD | Offer Sustainability | Circularity Profile | End of Life Information
8313 | RMTK90BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8314 | RMTK90BD | Contractual warranty | Warranty | 18 months
8315 | RMCN22BD | Main | range of product | Zelio Analog
8316 | RMCN22BD | Main | product or component type | Voltage/current converter
8317 | RMCN22BD | Main | analogue input type | Current 4...20 mA Voltage 0...10 V DC
8318 | RMCN22BD | Main | analogue output type | Current 4...20 mA <= 500 Ohm by cabling Voltage 0...10 V >= 100 kOhm by cabling
8319 | RMCN22BD | Complementary | protection type | Short-circuit protection on output Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output
8320 | RMCN22BD | Complementary | abnormal analogue output voltage | -15...0 V no input or input wire broken
8321 | RMCN22BD | Complementary | abnormal analogue output current | 4…30 mA no input or input wire broken
8322 | RMCN22BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, non isolated
8323 | RMCN22BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output
8324 | RMCN22BD | Complementary | local signalling | LED (green)power ON:
8325 | RMCN22BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C
8326 | RMCN22BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C
8327 | RMCN22BD | Complementary | temperature coefficient | 200 ppm/°C
8328 | RMCN22BD | Complementary | clamping connection capacity | 1 x 2.5 mm² 2 x 1.5 mm²
8329 | RMCN22BD | Complementary | tightening torque | 0.6…1.1 N.m
8330 | RMCN22BD | Complementary | marking | CE
8331 | RMCN22BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
8332 | RMCN22BD | Complementary | [Ui] rated insulation voltage | 2 kV
8333 | RMCN22BD | Complementary | fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
8334 | RMCN22BD | Complementary | safety reliability data | MTTFd = 73.2 years B10d = 67582
8335 | RMCN22BD | Complementary | net weight | 0.12 kg
8336 | RMCN22BD | Environment | standards | IEC 60584-1 IEC 60947-1
8337 | RMCN22BD | Environment | product certifications | GL CSA UL
8338 | RMCN22BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
8339 | RMCN22BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
8340 | RMCN22BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
8341 | RMCN22BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
8342 | RMCN22BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
8343 | RMCN22BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
8344 | RMCN22BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B CISPR 11
8345 | RMCN22BD | Environment | ambient air temperature for storage | -40…85 °C
8346 | RMCN22BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
8347 | RMCN22BD | Environment | pollution degree | 2 conforming to IEC 60664-1
8348 | RMCN22BD | Packing Units | Package 1 Weight | 0.103 kg
8349 | RMCN22BD | Packing Units | Package 1 Height | 0.270 dm
8350 | RMCN22BD | Packing Units | Package 1 width | 0.820 dm
8351 | RMCN22BD | Packing Units | Package 1 Length | 0.850 dm
8352 | RMCN22BD | Offer Sustainability | Sustainable offer status | Green Premium product
8353 | RMCN22BD | Offer Sustainability | REACh Regulation | REACh Declaration
8354 | RMCN22BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8355 | RMCN22BD | Offer Sustainability | Mercury free | Yes
8356 | RMCN22BD | Offer Sustainability | RoHS exemption information | Yes
8357 | RMCN22BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8358 | RMCN22BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8359 | RMCN22BD | Offer Sustainability | Circularity Profile | End of Life Information
8360 | RMCN22BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8361 | RMCN22BD | Contractual warranty | Warranty | 18 months
8362 | RMCL55BD | Main | range of product | Zelio Analog
8363 | RMCL55BD | Main | product or component type | Voltage/current converter
8364 | RMCL55BD | Main | analogue input type | Current 0...20 mA Current 4...20 mA Voltage +/- 10 V DC Voltage 0...10 V DC
8365 | RMCL55BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm switchable Current 4...20 mA <= 500 Ohm switchable Voltage +/- 10 V >= 100 kOhm switchable Voltage 0...10 V >= 100 kOhm switchable
8366 | RMCL55BD | Complementary | protection type | Reverse polarity protection on output Short-circuit protection on output Overvoltage protection on output (+/- 30 V)
8367 | RMCL55BD | Complementary | abnormal analogue output voltage | 11...15 V, output selected - 10...10 V no input or input wire broken voltage 11...15 V, output selected 0...10 V no input or input wire broken voltage -15...0 V, output selected 0...20 mA no input or input wire broken current -15...0 V, output selected 4...20 mA no input or input wire broken current
8368 | RMCL55BD | Complementary | abnormal analogue output current | 22…30 mA, output selected 0...20 mA no input or input wire broken voltage 22…30 mA, output selected 4...20 mA no input or input wire broken voltage -30…0 mA, output selected 0...20 mA no input or input wire broken current 4…30 mA, output selected 4...20 mA no input or input wire broken current
8369 | RMCL55BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, isolated
8370 | RMCL55BD | Complementary | current consumption | <= 70 mA for voltage output <= 90 mA for current output
8371 | RMCL55BD | Complementary | local signalling | LED (green)power ON:
8372 | RMCL55BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C
8373 | RMCL55BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C
8374 | RMCL55BD | Complementary | temperature coefficient | 200 ppm/°C
8375 | RMCL55BD | Complementary | clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm²
8376 | RMCL55BD | Complementary | tightening torque | 0.6…1.1 N.m
8377 | RMCL55BD | Complementary | marking | CE
8378 | RMCL55BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
8379 | RMCL55BD | Complementary | [Ui] rated insulation voltage | 2 kV
8380 | RMCL55BD | Complementary | fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
8381 | RMCL55BD | Complementary | safety reliability data | B10d = 20000 MTTFd = 21.6 years
8382 | RMCL55BD | Complementary | net weight | 0.12 kg
8383 | RMCL55BD | Environment | standards | IEC 60947-1 IEC 60584-1
8384 | RMCL55BD | Environment | product certifications | UL GL CSA
8385 | RMCL55BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
8386 | RMCL55BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
8387 | RMCL55BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
8388 | RMCL55BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
8389 | RMCL55BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
8390 | RMCL55BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
8391 | RMCL55BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B CISPR 11
8392 | RMCL55BD | Environment | ambient air temperature for storage | -40…85 °C
8393 | RMCL55BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
8394 | RMCL55BD | Environment | pollution degree | 2 conforming to IEC 60664-1
8395 | RMCL55BD | Packing Units | Package 1 Weight | 0.119 kg
8396 | RMCL55BD | Packing Units | Package 1 Height | 0.270 dm
8397 | RMCL55BD | Packing Units | Package 1 width | 0.820 dm
8398 | RMCL55BD | Packing Units | Package 1 Length | 0.850 dm
8399 | RMCL55BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8400 | RMCL55BD | Offer Sustainability | Mercury free | Yes
8401 | RMCL55BD | Offer Sustainability | RoHS exemption information | Yes
8402 | RMCL55BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8403 | RMCL55BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8404 | RMCL55BD | Offer Sustainability | Circularity Profile | End of Life Information
8405 | RMCL55BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8406 | RMCL55BD | Contractual warranty | Warranty | 18 months
8407 | RMCV60BD | Main | range of product | Zelio Analog
8408 | RMCV60BD | Main | product or component type | Voltage/current converter
8409 | RMCV60BD | Main | analogue input type | Voltage 0...300 V AC/DC 50/60 Hz Voltage 0...50 V AC/DC 50/60 Hz Voltage 0...500 V AC/DC 50/60 Hz
8410 | RMCV60BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm switchable Current 4...20 mA <= 500 Ohm switchable Voltage 0...10 V >= 100 kOhm switchable
8411 | RMCV60BD | Complementary | protection type | Short-circuit protection on output Reverse polarity protection on output Overvoltage protection on output (+/- 30 V)
8412 | RMCV60BD | Complementary | abnormal analogue output voltage | -15...0 V no input or input wire broken
8413 | RMCV60BD | Complementary | abnormal analogue output current | -30…0 mA, output selected 0...20 mA no input or input wire broken 4…30 mA, output selected 4...20 mA no input or input wire broken
8414 | RMCV60BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, isolated
8415 | RMCV60BD | Complementary | current consumption | <= 70 mA for voltage output <= 90 mA for current output
8416 | RMCV60BD | Complementary | local signalling | LED (green)power ON:
8417 | RMCV60BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 5 % of full scale at 20 °C
8418 | RMCV60BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C
8419 | RMCV60BD | Complementary | temperature coefficient | 200 ppm/°C
8420 | RMCV60BD | Complementary | clamping connection capacity | 1 x 2.5 mm² 2 x 1.5 mm²
8421 | RMCV60BD | Complementary | tightening torque | 0.6…1.1 N.m
8422 | RMCV60BD | Complementary | marking | CE
8423 | RMCV60BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
8424 | RMCV60BD | Complementary | [Ui] rated insulation voltage | 2 kV
8425 | RMCV60BD | Complementary | fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
8426 | RMCV60BD | Complementary | safety reliability data | MTTFd = 21.6 years B10d = 20000
8427 | RMCV60BD | Complementary | net weight | 0.15 kg
8428 | RMCV60BD | Environment | standards | IEC 60584-1 IEC 60947-1
8429 | RMCV60BD | Environment | product certifications | UL GL CSA
8430 | RMCV60BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
8431 | RMCV60BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
8432 | RMCV60BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
8433 | RMCV60BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
8434 | RMCV60BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
8435 | RMCV60BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
8436 | RMCV60BD | Environment | disturbance radiated/conducted | CISPR 11 CISPR 22 group 1 - class B
8437 | RMCV60BD | Environment | ambient air temperature for storage | -40…85 °C
8438 | RMCV60BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
8439 | RMCV60BD | Environment | pollution degree | 2 conforming to IEC 60664-1
8440 | RMCV60BD | Offer Sustainability | Sustainable offer status | Green Premium product
8441 | RMCV60BD | Offer Sustainability | REACh Regulation | REACh Declaration
8442 | RMCV60BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8443 | RMCV60BD | Offer Sustainability | Mercury free | Yes
8444 | RMCV60BD | Offer Sustainability | RoHS exemption information | Yes
8445 | RMCV60BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8446 | RMCV60BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8447 | RMCV60BD | Offer Sustainability | Circularity Profile | End of Life Information
8448 | RMCV60BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8449 | RMCV60BD | Contractual warranty | Warranty | 18 months
8450 | RMCA61BD | Main | range of product | Zelio Analog
8451 | RMCA61BD | Main | product or component type | Voltage/current converter
8452 | RMCA61BD | Main | analogue input type | Current 0...1.5 A AC/DC 50/60 Hz Current 0...15 A AC/DC 50/60 Hz Current 0...5 A AC/DC 50/60 Hz
8453 | RMCA61BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm by cabling Current 4...20 mA <= 500 Ohm by cabling Voltage 0...10 V >= 100 kOhm by cabling
8454 | RMCA61BD | Complementary | protection type | Reverse polarity protection on output Short-circuit protection on output Overvoltage protection on output (+/- 30 V)
8455 | RMCA61BD | Complementary | abnormal analogue output voltage | -15...0 V no input or input wire broken
8456 | RMCA61BD | Complementary | abnormal analogue output current | -30…0 mA, output selected 0...20 mA no input or input wire broken 4…30 mA, output selected 4...20 mA no input or input wire broken
8457 | RMCA61BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, isolated
8458 | RMCA61BD | Complementary | current consumption | <= 70 mA for voltage output <= 90 mA for current output
8459 | RMCA61BD | Complementary | local signalling | LED (green)power ON:
8460 | RMCA61BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 5 % of full scale at 20 °C
8461 | RMCA61BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C
8462 | RMCA61BD | Complementary | temperature coefficient | 1000 ppm/°C, range: 0...5 A 2000 ppm/°C, range: 0...15 A 500 ppm/°C, range: 0...1.5 A
8463 | RMCA61BD | Complementary | clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm²
8464 | RMCA61BD | Complementary | tightening torque | 0.6…1.1 N.m
8465 | RMCA61BD | Complementary | marking | CE
8466 | RMCA61BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
8467 | RMCA61BD | Complementary | [Ui] rated insulation voltage | 2 kV
8468 | RMCA61BD | Complementary | fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
8469 | RMCA61BD | Complementary | safety reliability data | B10d = 22108 MTTFd = 23.9 years
8470 | RMCA61BD | Complementary | net weight | 0.15 kg
8471 | RMCA61BD | Environment | standards | IEC 60947-1 IEC 60584-1
8472 | RMCA61BD | Environment | product certifications | CSA UL GL
8473 | RMCA61BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
8474 | RMCA61BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
8475 | RMCA61BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
8476 | RMCA61BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
8477 | RMCA61BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
8478 | RMCA61BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
8479 | RMCA61BD | Environment | disturbance radiated/conducted | CISPR 11 CISPR 22 group 1 - class B
8480 | RMCA61BD | Environment | ambient air temperature for storage | -40…85 °C
8481 | RMCA61BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
8482 | RMCA61BD | Environment | pollution degree | 2 conforming to IEC 60664-1
8483 | RMCA61BD | Offer Sustainability | Sustainable offer status | Green Premium product
8484 | RMCA61BD | Offer Sustainability | REACh Regulation | REACh Declaration
8485 | RMCA61BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8486 | RMCA61BD | Offer Sustainability | Mercury free | Yes
8487 | RMCA61BD | Offer Sustainability | RoHS exemption information | Yes
8488 | RMCA61BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8489 | RMCA61BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8490 | RMCA61BD | Offer Sustainability | Circularity Profile | End of Life Information
8491 | RMCA61BD | Contractual warranty | Warranty | 18 months
8492 | XVR3M04S | Main | range of product | Harmony XVR
8493 | XVR3M04S | Main | product or component type | Beacon
8494 | XVR3M04S | Main | device short name | XVR3
8495 | XVR3M04S | Main | beacon or indicator bank unit type | LED unit
8496 | XVR3M04S | Main | sound signalling | Buzzer: 70…90 dB at 1 m
8497 | XVR3M04S | Main | mounting diameter | 100 mm
8498 | XVR3M04S | Main | light source | LED, red
8499 | XVR3M04S | Main | device application | Bulldozer Automated guided vehicle (AGV) Forklift
8500 | XVR3M04S | Complementary | signalling type | Rotating Buzzer Blinking Flashing
8501 | XVR3M04S | Complementary | assembly style | Ready assembled
8502 | XVR3M04S | Complementary | material | PC (polycarbonate): lenses PBT (polybutylene terephthalate) + PC (polycarbonate): body EPDM (ethylene propylene diene monomer): base
8503 | XVR3M04S | Complementary | [Us] rated supply voltage | 100...230 V AC
8504 | XVR3M04S | Complementary | [Ue] rated operational voltage | 90...253 V AC
8505 | XVR3M04S | Complementary | inrush current | 0.5 A
8506 | XVR3M04S | Complementary | power consumption in W | 3.2 W
8507 | XVR3M04S | Complementary | marking | CE
8508 | XVR3M04S | Complementary | installation direction | Upright indoor Sideways indoor Inverted indoor Upright outdoor
8509 | XVR3M04S | Complementary | electrical insulation class | Class II
8510 | XVR3M04S | Complementary | current consumption | 500 mA
8511 | XVR3M04S | Complementary | length | 100 mm
8512 | XVR3M04S | Complementary | width | 100 mm
8513 | XVR3M04S | Complementary | height | 139 mm
8514 | XVR3M04S | Complementary | net weight | 0.538 kg
8515 | XVR3M04S | Environment | product certifications | CCC
8516 | XVR3M04S | Environment | ambient air temperature for operation | -10…50 °C
8517 | XVR3M04S | Environment | ambient air temperature for storage | -20…70 °C
8518 | XVR3M04S | Environment | relative humidity | 35…85 % without condensation
8519 | XVR3M04S | Environment | vibration resistance | 4.6 gn (sideways) 4.6 gn (inverted) 4.6 gn (upright)
8520 | XVR3M04S | Environment | IP degree of protection | IP23 (sideways) IP23 (inverted) IP23 (upright)
8521 | XVR3M04S | Packing Units | Package 1 Weight | 3.68 kg
8522 | XVR3M04S | Packing Units | Package 2 Weight | 29.44 kg
8523 | XVR3M05S | Main | range of product | Harmony XVR
8524 | XVR3M05S | Main | product or component type | Beacon
8525 | XVR3M05S | Main | device short name | XVR3
8526 | XVR3M05S | Main | beacon or indicator bank unit type | LED unit
8527 | XVR3M05S | Main | sound signalling | Buzzer: 70…90 dB at 1 m
8528 | XVR3M05S | Main | mounting diameter | 100 mm
8529 | XVR3M05S | Main | light source | LED, orange
8530 | XVR3M05S | Main | device application | Forklift Bulldozer Automated guided vehicle (AGV)
8531 | XVR3M05S | Complementary | signalling type | Rotating Blinking Flashing
8532 | XVR3M05S | Complementary | assembly style | Ready assembled
8533 | XVR3M05S | Complementary | material | PC (polycarbonate): lenses PBT (polybutylene terephthalate) + PC (polycarbonate): body EPDM (ethylene propylene diene monomer): base
8534 | XVR3M05S | Complementary | [Us] rated supply voltage | 100...230 V AC
8535 | XVR3M05S | Complementary | [Ue] rated operational voltage | 90...253 V AC
8536 | XVR3M05S | Complementary | inrush current | 0.5 A
8537 | XVR3M05S | Complementary | power consumption in W | 3.2 W
8538 | XVR3M05S | Complementary | marking | CE
8539 | XVR3M05S | Complementary | installation direction | Upright indoor Sideways indoor Inverted indoor Upright outdoor
8540 | XVR3M05S | Complementary | electrical insulation class | Class II
8541 | XVR3M05S | Complementary | current consumption | 500 mA
8542 | XVR3M05S | Complementary | length | 100 mm
8543 | XVR3M05S | Complementary | width | 100 mm
8544 | XVR3M05S | Complementary | height | 139 mm
8545 | XVR3M05S | Complementary | net weight | 0.538 kg
8546 | XVR3M05S | Environment | product certifications | CCC
8547 | XVR3M05S | Environment | ambient air temperature for operation | -10…50 °C
8548 | XVR3M05S | Environment | ambient air temperature for storage | -20…70 °C
8549 | XVR3M05S | Environment | relative humidity | 35…85 % without condensation
8550 | XVR3M05S | Environment | vibration resistance | 4.6 gn (sideways) 4.6 gn (inverted) 4.6 gn (upright)
8551 | XVR3M05S | Environment | IP degree of protection | IP23 (sideways) IP23 (inverted) IP23 (upright)
8552 | XVR3M05S | Packing Units | Package 1 Weight | 3.68 kg
8553 | XVR3M05S | Packing Units | Package 2 Weight | 29.44 kg
8554 | XVR3M05S | Packing Units | Package 3 Weight | 29.94 kg
8555 | XVR3M06S | Main | range of product | Harmony XVR
8556 | XVR3M06S | Main | product or component type | Beacon
8557 | XVR3M06S | Main | device short name | XVR3
8558 | XVR3M06S | Main | beacon or indicator bank unit type | LED unit
8559 | XVR3M06S | Main | sound signalling | Buzzer: 70…90 dB at 1 m
8560 | XVR3M06S | Main | mounting diameter | 100 mm
8561 | XVR3M06S | Main | light source | LED, blue
8562 | XVR3M06S | Main | device application | Automated guided vehicle (AGV) Forklift Bulldozer
8563 | XVR3M06S | Complementary | signalling type | Blinking Rotating Flashing
8564 | XVR3M06S | Complementary | assembly style | Ready assembled
8565 | XVR3M06S | Complementary | material | PC (polycarbonate): lenses PBT (polybutylene terephthalate) + PC (polycarbonate): body EPDM (ethylene propylene diene monomer): base
8566 | XVR3M06S | Complementary | [Us] rated supply voltage | 100...230 V AC
8567 | XVR3M06S | Complementary | [Ue] rated operational voltage | 90...253 V AC
8568 | XVR3M06S | Complementary | inrush current | 0.5 A
8569 | XVR3M06S | Complementary | power consumption in W | 3.2 W
8570 | XVR3M06S | Complementary | marking | CE
8571 | XVR3M06S | Complementary | installation direction | Upright indoor Sideways indoor Inverted indoor Upright outdoor
8572 | XVR3M06S | Complementary | electrical insulation class | Class II
8573 | XVR3M06S | Complementary | current consumption | 500 mA
8574 | XVR3M06S | Complementary | length | 100 mm
8575 | XVR3M06S | Complementary | width | 100 mm
8576 | XVR3M06S | Complementary | height | 139 mm
8577 | XVR3M06S | Complementary | net weight | 0.538 kg
8578 | XVR3M06S | Environment | product certifications | CCC
8579 | XVR3M06S | Environment | ambient air temperature for operation | -10…50 °C
8580 | XVR3M06S | Environment | ambient air temperature for storage | -20…70 °C
8581 | XVR3M06S | Environment | relative humidity | 35…85 % without condensation
8582 | XVR3M06S | Environment | vibration resistance | 4.6 gn (sideways) 4.6 gn (inverted) 4.6 gn (upright)
8583 | XVR3M06S | Environment | IP degree of protection | IP23 (sideways) IP23 (inverted) IP23 (upright)
8584 | XVR3M06S | Packing Units | Package 1 Weight | 0.678 kg
8585 | XVR3E03 | Main | range of product | Harmony XVR
8586 | XVR3E03 | Main | product or component type | Beacon
8587 | XVR3E03 | Main | device short name | XVR3
8588 | XVR3E03 | Main | beacon or indicator bank unit type | LED unit
8589 | XVR3E03 | Main | mounting diameter | 100 mm
8590 | XVR3E03 | Main | light source | LED, green
8591 | XVR3E03 | Main | device application | Forklift Automated guided vehicle (AGV) Bulldozer
8592 | XVR3E03 | Complementary | signalling type | Flashing Blinking Rotating
8593 | XVR3E03 | Complementary | assembly style | Ready assembled
8594 | XVR3E03 | Complementary | material | PC (polycarbonate): lenses PBT (polybutylene terephthalate) + PC (polycarbonate): body EPDM (ethylene propylene diene monomer): base
8595 | XVR3E03 | Complementary | [Us] rated supply voltage | 48 V DC
8596 | XVR3E03 | Complementary | [Ue] rated operational voltage | 35...60 V DC
8597 | XVR3E03 | Complementary | inrush current | 1 A
8598 | XVR3E03 | Complementary | power consumption in W | 3 W
8599 | XVR3E03 | Complementary | marking | CE
8600 | XVR3E03 | Complementary | installation direction | Upright indoor Sideways indoor Inverted indoor Upright outdoor
8601 | XVR3E03 | Complementary | electrical insulation class | Class II
8602 | XVR3E03 | Complementary | current consumption | 1000 mA
8603 | XVR3E03 | Complementary | length | 100 mm
8604 | XVR3E03 | Complementary | width | 100 mm
8605 | XVR3E03 | Complementary | height | 139 mm
8606 | XVR3E03 | Complementary | net weight | 0.484 kg
8607 | XVR3E03 | Environment | product certifications | CCC
8608 | XVR3E03 | Environment | ambient air temperature for operation | -20…50 °C
8609 | XVR3E03 | Environment | ambient air temperature for storage | -35…70 °C
8610 | XVR3E03 | Environment | relative humidity | 35…85 % without condensation
8611 | XVR3E03 | Environment | vibration resistance | 4.6 gn (sideways) 4.6 gn (inverted) 7.1 gn (upright)
8612 | XVR3E03 | Environment | IP degree of protection | IP65 (upright) IP23 (sideways) IP23 (inverted)
8613 | XVR3E03 | Packing Units | Package 1 Weight | 0.546 kg
8614 | XVR3E04 | Main | range of product | Harmony XVR
8615 | XVR3E04 | Main | product or component type | Beacon
8616 | XVR3E04 | Main | device short name | XVR3
8617 | XVR3E04 | Main | beacon or indicator bank unit type | LED unit
8618 | XVR3E04 | Main | mounting diameter | 100 mm
8619 | XVR3E04 | Main | light source | LED, red
8620 | XVR3E04 | Main | device application | Forklift Automated guided vehicle (AGV) Bulldozer
8621 | XVR3E04 | Complementary | signalling type | Rotating Blinking Flashing
8622 | XVR3E04 | Complementary | assembly style | Ready assembled
8623 | XVR3E04 | Complementary | material | PC (polycarbonate): lenses PBT (polybutylene terephthalate) + PC (polycarbonate): body EPDM (ethylene propylene diene monomer): base
8624 | XVR3E04 | Complementary | [Us] rated supply voltage | 48 V DC
8625 | XVR3E04 | Complementary | [Ue] rated operational voltage | 35...60 V DC
8626 | XVR3E04 | Complementary | inrush current | 1 A
8627 | XVR3E04 | Complementary | power consumption in W | 3 W
8628 | XVR3E04 | Complementary | marking | CE
8629 | XVR3E04 | Complementary | installation direction | Upright indoor Sideways indoor Inverted indoor Upright outdoor
8630 | XVR3E04 | Complementary | electrical insulation class | Class II
8631 | XVR3E04 | Complementary | current consumption | 1000 mA
8632 | XVR3E04 | Complementary | length | 100 mm
8633 | XVR3E04 | Complementary | width | 100 mm
8634 | XVR3E04 | Complementary | height | 139 mm
8635 | XVR3E04 | Complementary | net weight | 0.484 kg
8636 | XVR3E04 | Environment | product certifications | CCC
8637 | XVR3E04 | Environment | ambient air temperature for operation | -20…50 °C
8638 | XVR3E04 | Environment | ambient air temperature for storage | -35…70 °C
8639 | XVR3E04 | Environment | relative humidity | 35…85 % without condensation
8640 | XVR3E04 | Environment | vibration resistance | 4.6 gn (sideways) 4.6 gn (inverted) 7.1 gn (upright)
8641 | XVR3E04 | Environment | IP degree of protection | IP65 (upright) IP23 (sideways) IP23 (inverted)
8642 | XVR3E04 | Packing Units | Package 1 Weight | 0.649 kg
8643 | XVR3E05 | Main | range of product | Harmony XVR
8644 | XVR3E05 | Main | product or component type | Beacon
8645 | XVR3E05 | Main | device short name | XVR3
8646 | XVR3E05 | Main | beacon or indicator bank unit type | LED unit
8647 | XVR3E05 | Main | mounting diameter | 100 mm
8648 | XVR3E05 | Main | light source | LED, orange
8649 | XVR3E05 | Main | device application | Forklift Automated guided vehicle (AGV) Bulldozer
8650 | XVR3E05 | Complementary | signalling type | Flashing Blinking Rotating
8651 | XVR3E05 | Complementary | assembly style | Ready assembled
8652 | XVR3E05 | Complementary | material | PC (polycarbonate): lenses PBT (polybutylene terephthalate) + PC (polycarbonate): body EPDM (ethylene propylene diene monomer): base
8653 | XVR3E05 | Complementary | [Us] rated supply voltage | 48 V DC
8654 | XVR3E05 | Complementary | [Ue] rated operational voltage | 35...60 V DC
8655 | XVR3E05 | Complementary | inrush current | 1 A
8656 | XVR3E05 | Complementary | power consumption in W | 3 W
8657 | XVR3E05 | Complementary | marking | CE
8658 | XVR3E05 | Complementary | installation direction | Upright indoor Sideways indoor Inverted indoor Upright outdoor
8659 | XVR3E05 | Complementary | electrical insulation class | Class II
8660 | XVR3E05 | Complementary | current consumption | 1000 mA
8661 | XVR3E05 | Complementary | length | 100 mm
8662 | XVR3E05 | Complementary | width | 100 mm
8663 | XVR3E05 | Complementary | height | 139 mm
8664 | XVR3E05 | Complementary | net weight | 0.484 kg
8665 | XVR3E05 | Environment | product certifications | CCC
8666 | XVR3E05 | Environment | ambient air temperature for operation | -20…50 °C
8667 | XVR3E05 | Environment | ambient air temperature for storage | -35…70 °C
8668 | XVR3E05 | Environment | relative humidity | 35…85 % without condensation
8669 | XVR3E05 | Environment | vibration resistance | 4.6 gn (sideways) 4.6 gn (inverted) 7.1 gn (upright)
8670 | XVR3E05 | Environment | IP degree of protection | IP65 (upright) IP23 (sideways) IP23 (inverted)
8671 | XVR3E05 | Packing Units | Package 1 Weight | 0.642 kg
8672 | XVR3E06 | Main | range of product | Harmony XVR
8673 | XVR3E06 | Main | product or component type | Beacon
8674 | XVR3E06 | Main | device short name | XVR3
8675 | XVR3E06 | Main | beacon or indicator bank unit type | LED unit
8676 | XVR3E06 | Main | mounting diameter | 100 mm
8677 | XVR3E06 | Main | light source | LED, blue
8678 | XVR3E06 | Main | device application | Forklift Automated guided vehicle (AGV) Bulldozer
8679 | XVR3E06 | Complementary | signalling type | Rotating Flashing Blinking
8680 | XVR3E06 | Complementary | assembly style | Ready assembled
8681 | XVR3E06 | Complementary | material | PC (polycarbonate): lenses PBT (polybutylene terephthalate) + PC (polycarbonate): body EPDM (ethylene propylene diene monomer): base
8682 | XVR3E06 | Complementary | [Us] rated supply voltage | 48 V DC
8683 | XVR3E06 | Complementary | [Ue] rated operational voltage | 35...60 V DC
8684 | XVR3E06 | Complementary | inrush current | 1 A
8685 | XVR3E06 | Complementary | power consumption in W | 3 W
8686 | XVR3E06 | Complementary | marking | CE
8687 | XVR3E06 | Complementary | installation direction | Upright indoor Sideways indoor Inverted indoor Upright outdoor
8688 | XVR3E06 | Complementary | electrical insulation class | Class II
8689 | XVR3E06 | Complementary | current consumption | 1000 mA
8690 | XVR3E06 | Complementary | length | 100 mm
8691 | XVR3E06 | Complementary | width | 100 mm
8692 | XVR3E06 | Complementary | height | 139 mm
8693 | XVR3E06 | Complementary | net weight | 0.484 kg
8694 | XVR3E06 | Environment | product certifications | CCC
8695 | XVR3E06 | Environment | ambient air temperature for operation | -20…50 °C
8696 | XVR3E06 | Environment | ambient air temperature for storage | -35…70 °C
8697 | XVR3E06 | Environment | relative humidity | 35…85 % without condensation
8698 | XVR3E06 | Environment | vibration resistance | 4.6 gn (sideways) 4.6 gn (inverted) 7.1 gn (upright)
8699 | XVR3E06 | Environment | IP degree of protection | IP65 (upright) IP23 (sideways) IP23 (inverted)
8700 | XVR3E06 | Packing Units | Package 1 Weight | 0.546 kg
8701 | XVDLS33 | Main | range of product | Harmony XVD Optimum
8702 | XVDLS33 | Main | product or component type | Complete miniature beacon
8703 | XVDLS33 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
8704 | XVDLS33 | Main | signalling type | Steady
8705 | XVDLS33 | Main | mounting diameter | 45 mm
8706 | XVDLS33 | Main | component name | XVDLS
8707 | XVDLS33 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
8708 | XVDLS33 | Main | light source | Bulb not included, green
8709 | XVDLS33 | Main | bulb type | Incandescent with BA 15d base
8710 | XVDLS33 | Main | [Us] rated supply voltage | <= 230 V
8711 | XVDLS33 | Main | maximum power dissipation in W | 5 W
8712 | XVDLS33 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
8713 | XVDLS33 | Complementary | cable entry | 1 entry tapped for Pg 7
8714 | XVDLS33 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
8715 | XVDLS33 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
8716 | XVDLS33 | Complementary | CAD overall width | 45 mm
8717 | XVDLS33 | Complementary | CAD overall height | 104 mm
8718 | XVDLS33 | Complementary | CAD overall depth | 45 mm
8719 | XVDLS33 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
8720 | XVDLS33 | Complementary | net weight | 0.08 kg
8721 | XVDLS33 | Environment | product certifications | CSA UL
8722 | XVDLS33 | Environment | standards | EN/IEC 60947-5-1
8723 | XVDLS33 | Environment | protective treatment | TC
8724 | XVDLS33 | Environment | ambient air temperature for operation | -25…70 °C
8725 | XVDLS33 | Environment | ambient air temperature for storage | -40…70 °C
8726 | XVDLS33 | Environment | electrical shock protection class | Class II conforming to IEC 60536
8727 | XVDLS33 | Environment | IP degree of protection | IP40 conforming to IEC 60529
8728 | XVDLS33 | Packing Units | Package 1 Weight | 101 g
8729 | XVDLS33 | Packing Units | Package 2 Weight | 1.409 kg
8730 | XVDLS33 | Offer Sustainability | Sustainable offer status | Green Premium product
8731 | XVDLS33 | Offer Sustainability | REACh Regulation | REACh Declaration
8732 | XVDLS33 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8733 | XVDLS33 | Offer Sustainability | Mercury free | Yes
8734 | XVDLS33 | Offer Sustainability | RoHS exemption information | Yes
8735 | XVDLS33 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8736 | XVDLS33 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8737 | XVDLS33 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8738 | XVDLS33 | Contractual warranty | Warranty | 18 months
8739 | XVDLS34 | Main | range of product | Harmony XVD Optimum
8740 | XVDLS34 | Main | product or component type | Complete miniature beacon
8741 | XVDLS34 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
8742 | XVDLS34 | Main | signalling type | Steady
8743 | XVDLS34 | Main | mounting diameter | 45 mm
8744 | XVDLS34 | Main | component name | XVDLS
8745 | XVDLS34 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
8746 | XVDLS34 | Main | light source | Bulb not included, red
8747 | XVDLS34 | Main | bulb type | Incandescent with BA 15d base
8748 | XVDLS34 | Main | [Us] rated supply voltage | <= 230 V
8749 | XVDLS34 | Main | maximum power dissipation in W | 5 W
8750 | XVDLS34 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
8751 | XVDLS34 | Complementary | cable entry | 1 entry tapped for Pg 7
8752 | XVDLS34 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
8753 | XVDLS34 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
8754 | XVDLS34 | Complementary | CAD overall width | 45 mm
8755 | XVDLS34 | Complementary | CAD overall height | 104 mm
8756 | XVDLS34 | Complementary | CAD overall depth | 45 mm
8757 | XVDLS34 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
8758 | XVDLS34 | Complementary | net weight | 0.08 kg
8759 | XVDLS34 | Environment | product certifications | UL CSA
8760 | XVDLS34 | Environment | standards | EN/IEC 60947-5-1
8761 | XVDLS34 | Environment | protective treatment | TC
8762 | XVDLS34 | Environment | ambient air temperature for operation | -25…70 °C
8763 | XVDLS34 | Environment | ambient air temperature for storage | -40…70 °C
8764 | XVDLS34 | Environment | electrical shock protection class | Class II conforming to IEC 60536
8765 | XVDLS34 | Environment | IP degree of protection | IP40 conforming to IEC 60529
8766 | XVDLS34 | Packing Units | Package 1 Weight | 101 g
8767 | XVDLS34 | Packing Units | Package 2 Weight | 1.405 kg
8768 | XVDLS34 | Offer Sustainability | Sustainable offer status | Green Premium product
8769 | XVDLS34 | Offer Sustainability | REACh Regulation | REACh Declaration
8770 | XVDLS34 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8771 | XVDLS34 | Offer Sustainability | Mercury free | Yes
8772 | XVDLS34 | Offer Sustainability | RoHS exemption information | Yes
8773 | XVDLS34 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8774 | XVDLS34 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8775 | XVDLS34 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8776 | XVDLS34 | Contractual warranty | Warranty | 18 months
8777 | XVDLS35 | Main | range of product | Harmony XVD Optimum
8778 | XVDLS35 | Main | product or component type | Complete miniature beacon
8779 | XVDLS35 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
8780 | XVDLS35 | Main | signalling type | Steady
8781 | XVDLS35 | Main | mounting diameter | 45 mm
8782 | XVDLS35 | Main | component name | XVDLS
8783 | XVDLS35 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
8784 | XVDLS35 | Main | light source | Bulb not included, orange
8785 | XVDLS35 | Main | bulb type | Incandescent with BA 15d base
8786 | XVDLS35 | Main | [Us] rated supply voltage | <= 230 V
8787 | XVDLS35 | Main | maximum power dissipation in W | 5 W
8788 | XVDLS35 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
8789 | XVDLS35 | Complementary | cable entry | 1 entry tapped for Pg 7
8790 | XVDLS35 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
8791 | XVDLS35 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
8792 | XVDLS35 | Complementary | CAD overall width | 45 mm
8793 | XVDLS35 | Complementary | CAD overall height | 104 mm
8794 | XVDLS35 | Complementary | CAD overall depth | 45 mm
8795 | XVDLS35 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
8796 | XVDLS35 | Complementary | net weight | 0.08 kg
8797 | XVDLS35 | Environment | product certifications | CSA UL
8798 | XVDLS35 | Environment | standards | EN/IEC 60947-5-1
8799 | XVDLS35 | Environment | protective treatment | TC
8800 | XVDLS35 | Environment | ambient air temperature for operation | -25…70 °C
8801 | XVDLS35 | Environment | ambient air temperature for storage | -40…70 °C
8802 | XVDLS35 | Environment | electrical shock protection class | Class II conforming to IEC 60536
8803 | XVDLS35 | Environment | IP degree of protection | IP40 conforming to IEC 60529
8804 | XVDLS35 | Packing Units | Package 1 Weight | 105 g
8805 | XVDLS35 | Packing Units | Package 2 Weight | 855 g
8806 | XVDLS35 | Offer Sustainability | Sustainable offer status | Green Premium product
8807 | XVDLS35 | Offer Sustainability | REACh Regulation | REACh Declaration
8808 | XVDLS35 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8809 | XVDLS35 | Offer Sustainability | Mercury free | Yes
8810 | XVDLS35 | Offer Sustainability | RoHS exemption information | Yes
8811 | XVDLS35 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8812 | XVDLS35 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8813 | XVDLS35 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8814 | XVDLS35 | Contractual warranty | Warranty | 18 months
8815 | XVDLS36 | Main | range of product | Harmony XVD Optimum
8816 | XVDLS36 | Main | product or component type | Complete miniature beacon
8817 | XVDLS36 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
8818 | XVDLS36 | Main | signalling type | Steady
8819 | XVDLS36 | Main | mounting diameter | 45 mm
8820 | XVDLS36 | Main | component name | XVDLS
8821 | XVDLS36 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
8822 | XVDLS36 | Main | light source | Bulb not included, blue
8823 | XVDLS36 | Main | bulb type | Incandescent with BA 15d base
8824 | XVDLS36 | Main | [Us] rated supply voltage | <= 230 V
8825 | XVDLS36 | Main | maximum power dissipation in W | 5 W
8826 | XVDLS36 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
8827 | XVDLS36 | Complementary | cable entry | 1 entry tapped for Pg 7
8828 | XVDLS36 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
8829 | XVDLS36 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
8830 | XVDLS36 | Complementary | CAD overall width | 45 mm
8831 | XVDLS36 | Complementary | CAD overall height | 104 mm
8832 | XVDLS36 | Complementary | CAD overall depth | 45 mm
8833 | XVDLS36 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
8834 | XVDLS36 | Complementary | net weight | 0.08 kg
8835 | XVDLS36 | Environment | product certifications | UL CSA
8836 | XVDLS36 | Environment | standards | EN/IEC 60947-5-1
8837 | XVDLS36 | Environment | protective treatment | TC
8838 | XVDLS36 | Environment | ambient air temperature for operation | -25…70 °C
8839 | XVDLS36 | Environment | ambient air temperature for storage | -40…70 °C
8840 | XVDLS36 | Environment | electrical shock protection class | Class II conforming to IEC 60536
8841 | XVDLS36 | Environment | IP degree of protection | IP40 conforming to IEC 60529
8842 | XVDLS36 | Packing Units | Package 1 Weight | 101 g
8843 | XVDLS36 | Offer Sustainability | Sustainable offer status | Green Premium product
8844 | XVDLS36 | Offer Sustainability | REACh Regulation | REACh Declaration
8845 | XVDLS36 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8846 | XVDLS36 | Offer Sustainability | Mercury free | Yes
8847 | XVDLS36 | Offer Sustainability | RoHS exemption information | Yes
8848 | XVDLS36 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8849 | XVDLS36 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8850 | XVDLS36 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8851 | XVDLS36 | Contractual warranty | Warranty | 18 months
8852 | XVDLS37 | Main | range of product | Harmony XVD Optimum
8853 | XVDLS37 | Main | product or component type | Complete miniature beacon
8854 | XVDLS37 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
8855 | XVDLS37 | Main | signalling type | Steady
8856 | XVDLS37 | Main | mounting diameter | 45 mm
8857 | XVDLS37 | Main | component name | XVDLS
8858 | XVDLS37 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
8859 | XVDLS37 | Main | light source | Bulb not included, clear
8860 | XVDLS37 | Main | bulb type | Incandescent with BA 15d base
8861 | XVDLS37 | Main | [Us] rated supply voltage | <= 230 V
8862 | XVDLS37 | Main | maximum power dissipation in W | 5 W
8863 | XVDLS37 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
8864 | XVDLS37 | Complementary | cable entry | 1 entry tapped for Pg 7
8865 | XVDLS37 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
8866 | XVDLS37 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
8867 | XVDLS37 | Complementary | CAD overall width | 45 mm
8868 | XVDLS37 | Complementary | CAD overall height | 104 mm
8869 | XVDLS37 | Complementary | CAD overall depth | 45 mm
8870 | XVDLS37 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
8871 | XVDLS37 | Complementary | net weight | 0.08 kg
8872 | XVDLS37 | Environment | product certifications | CSA UL
8873 | XVDLS37 | Environment | standards | EN/IEC 60947-5-1
8874 | XVDLS37 | Environment | protective treatment | TC
8875 | XVDLS37 | Environment | ambient air temperature for operation | -25…70 °C
8876 | XVDLS37 | Environment | ambient air temperature for storage | -40…70 °C
8877 | XVDLS37 | Environment | electrical shock protection class | Class II conforming to IEC 60536
8878 | XVDLS37 | Environment | IP degree of protection | IP40 conforming to IEC 60529
8879 | XVDLS37 | Offer Sustainability | Sustainable offer status | Green Premium product
8880 | XVDLS37 | Offer Sustainability | REACh Regulation | REACh Declaration
8881 | XVDLS37 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8882 | XVDLS37 | Offer Sustainability | Mercury free | Yes
8883 | XVDLS37 | Offer Sustainability | RoHS exemption information | Yes
8884 | XVDLS37 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8885 | XVDLS37 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8886 | XVDLS37 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8887 | XVDLS37 | Contractual warranty | Warranty | 18 months
8888 | XVDLS38 | Main | range of product | Harmony XVD Optimum
8889 | XVDLS38 | Main | product or component type | Complete miniature beacon
8890 | XVDLS38 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
8891 | XVDLS38 | Main | signalling type | Steady
8892 | XVDLS38 | Main | mounting diameter | 45 mm
8893 | XVDLS38 | Main | component name | XVDLS
8894 | XVDLS38 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
8895 | XVDLS38 | Main | light source | Bulb not included, yellow
8896 | XVDLS38 | Main | bulb type | Incandescent with BA 15d base
8897 | XVDLS38 | Main | [Us] rated supply voltage | <= 230 V
8898 | XVDLS38 | Main | maximum power dissipation in W | 5 W
8899 | XVDLS38 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
8900 | XVDLS38 | Complementary | cable entry | 1 entry tapped for Pg 7
8901 | XVDLS38 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
8902 | XVDLS38 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
8903 | XVDLS38 | Complementary | CAD overall width | 45 mm
8904 | XVDLS38 | Complementary | CAD overall height | 104 mm
8905 | XVDLS38 | Complementary | CAD overall depth | 45 mm
8906 | XVDLS38 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
8907 | XVDLS38 | Complementary | net weight | 0.08 kg
8908 | XVDLS38 | Environment | product certifications | CSA UL
8909 | XVDLS38 | Environment | standards | EN/IEC 60947-5-1
8910 | XVDLS38 | Environment | protective treatment | TC
8911 | XVDLS38 | Environment | ambient air temperature for operation | -25…70 °C
8912 | XVDLS38 | Environment | ambient air temperature for storage | -40…70 °C
8913 | XVDLS38 | Environment | electrical shock protection class | Class II conforming to IEC 60536
8914 | XVDLS38 | Environment | IP degree of protection | IP40 conforming to IEC 60529
8915 | XVDLS38 | Packing Units | Package 1 Weight | 0.100 kg
8916 | XVDLS38 | Offer Sustainability | Sustainable offer status | Green Premium product
8917 | XVDLS38 | Offer Sustainability | REACh Regulation | REACh Declaration
8918 | XVDLS38 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8919 | XVDLS38 | Offer Sustainability | Mercury free | Yes
8920 | XVDLS38 | Offer Sustainability | RoHS exemption information | Yes
8921 | XVDLS38 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8922 | XVDLS38 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8923 | XVDLS38 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8924 | XVDLS38 | Contractual warranty | Warranty | 18 months
8925 | DL1BEBS | Main | range compatibility | Harmony XVP
8926 | DL1BEBS | Main | accessory / separate part designation | Incandescent bulb
8927 | DL1BEBS | Main | accessory / separate part type | Incandescent bulb
8928 | DL1BEBS | Main | accessory / separate part category | Lighting accessories
8929 | DL1BEBS | Main | accessory / separate part destination | Beacon and indicator bank
8930 | DL1BEBS | Main | [Us] rated supply voltage | 24 V
8931 | DL1BEBS | Main | signalling type | Steady
8932 | DL1BEBS | Main | power dissipation in W | 4 W
8933 | DL1BEBS | Main | sale per indivisible quantity | 10
8934 | DL1BEBS | Complementary | bulb base | BA 15d
8935 | DL1BEBS | Complementary | net weight | 0.09 kg
8936 | DL1BEBS | Offer Sustainability | Sustainable offer status | Green Premium product
8937 | DL1BEBS | Offer Sustainability | REACh Regulation | REACh Declaration
8938 | DL1BEBS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8939 | DL1BEBS | Offer Sustainability | Mercury free | Yes
8940 | DL1BEBS | Offer Sustainability | RoHS exemption information | Yes
8941 | DL1BEBS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8942 | DL1BEBS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8943 | DL1BEBS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8944 | DL1BEBS | Contractual warranty | Warranty | 18 months
8945 | DL1BEGS | Main | range compatibility | Harmony XVP
8946 | DL1BEGS | Main | accessory / separate part designation | Incandescent bulb
8947 | DL1BEGS | Main | accessory / separate part type | Incandescent bulb
8948 | DL1BEGS | Main | accessory / separate part category | Lighting accessories
8949 | DL1BEGS | Main | accessory / separate part destination | Beacon and indicator bank
8950 | DL1BEGS | Main | [Us] rated supply voltage | 120 V
8951 | DL1BEGS | Main | signalling type | Steady
8952 | DL1BEGS | Main | power dissipation in W | 5 W
8953 | DL1BEGS | Main | sale per indivisible quantity | 10
8954 | DL1BEGS | Complementary | bulb base | BA 15d
8955 | DL1BEGS | Complementary | net weight | 0.09 kg
8956 | DL1BEGS | Contractual warranty | Warranty | 18 months
8957 | DL1BEMS | Main | range compatibility | Harmony XVP
8958 | DL1BEMS | Main | accessory / separate part designation | Incandescent bulb
8959 | DL1BEMS | Main | accessory / separate part type | Incandescent bulb
8960 | DL1BEMS | Main | accessory / separate part category | Lighting accessories
8961 | DL1BEMS | Main | accessory / separate part destination | Beacon and indicator bank
8962 | DL1BEMS | Main | [Us] rated supply voltage | 230 V
8963 | DL1BEMS | Main | signalling type | Steady
8964 | DL1BEMS | Main | power dissipation in W | 5 W
8965 | DL1BEMS | Main | sale per indivisible quantity | 10
8966 | DL1BEMS | Complementary | bulb base | BA 15d
8967 | DL1BEMS | Complementary | net weight | 0.09 kg
8968 | DL1BEMS | Offer Sustainability | Sustainable offer status | Green Premium product
8969 | DL1BEMS | Offer Sustainability | REACh Regulation | REACh Declaration
8970 | DL1BEMS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
8971 | DL1BEMS | Offer Sustainability | Mercury free | Yes
8972 | DL1BEMS | Offer Sustainability | RoHS exemption information | Yes
8973 | DL1BEMS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
8974 | DL1BEMS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
8975 | DL1BEMS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
8976 | DL1BEMS | Contractual warranty | Warranty | 18 months
8977 | XVDLS6B3 | Main | range of product | Harmony XVD Optimum
8978 | XVDLS6B3 | Main | product or component type | Complete miniature beacon
8979 | XVDLS6B3 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
8980 | XVDLS6B3 | Main | signalling type | Flashing
8981 | XVDLS6B3 | Main | mounting diameter | 45 mm
8982 | XVDLS6B3 | Main | component name | XVDLS
8983 | XVDLS6B3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
8984 | XVDLS6B3 | Main | light source | Integral flash discharge tube, green
8985 | XVDLS6B3 | Main | bulb type | Flash discharge tube
8986 | XVDLS6B3 | Main | [Us] rated supply voltage | 24 V AC/DC
8987 | XVDLS6B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
8988 | XVDLS6B3 | Complementary | cable entry | 1 entry tapped for Pg 7
8989 | XVDLS6B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
8990 | XVDLS6B3 | Complementary | current consumption | < 145 mA DC < 90 mA AC
8991 | XVDLS6B3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
8992 | XVDLS6B3 | Complementary | flash energy | 1 J
8993 | XVDLS6B3 | Complementary | CAD overall width | 45 mm
8994 | XVDLS6B3 | Complementary | CAD overall height | 104 mm
8995 | XVDLS6B3 | Complementary | CAD overall depth | 45 mm
8996 | XVDLS6B3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
8997 | XVDLS6B3 | Complementary | net weight | 0.085 kg
8998 | XVDLS6B3 | Environment | product certifications | CSA UL
8999 | XVDLS6B3 | Environment | standards | EN/IEC 60947-5-1
9000 | XVDLS6B3 | Environment | protective treatment | TC
9001 | XVDLS6B3 | Environment | ambient air temperature for operation | -10…50 °C
9002 | XVDLS6B3 | Environment | ambient air temperature for storage | -40…70 °C
9003 | XVDLS6B3 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9004 | XVDLS6B3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9005 | XVDLS6B3 | Offer Sustainability | Sustainable offer status | Green Premium product
9006 | XVDLS6B3 | Offer Sustainability | REACh Regulation | REACh Declaration
9007 | XVDLS6B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9008 | XVDLS6B3 | Offer Sustainability | Mercury free | Yes
9009 | XVDLS6B3 | Offer Sustainability | RoHS exemption information | Yes
9010 | XVDLS6B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9011 | XVDLS6B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9012 | XVDLS6B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
9013 | XVDLS6B3 | Contractual warranty | Warranty | 18 months
9014 | XVDLS6B4 | Main | range of product | Harmony XVD Optimum
9015 | XVDLS6B4 | Main | product or component type | Complete miniature beacon
9016 | XVDLS6B4 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9017 | XVDLS6B4 | Main | signalling type | Flashing
9018 | XVDLS6B4 | Main | mounting diameter | 45 mm
9019 | XVDLS6B4 | Main | component name | XVDLS
9020 | XVDLS6B4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9021 | XVDLS6B4 | Main | light source | Integral flash discharge tube, red
9022 | XVDLS6B4 | Main | bulb type | Flash discharge tube
9023 | XVDLS6B4 | Main | [Us] rated supply voltage | 24 V AC/DC
9024 | XVDLS6B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9025 | XVDLS6B4 | Complementary | cable entry | 1 entry tapped for Pg 7
9026 | XVDLS6B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9027 | XVDLS6B4 | Complementary | current consumption | < 145 mA DC < 90 mA AC
9028 | XVDLS6B4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
9029 | XVDLS6B4 | Complementary | flash energy | 1 J
9030 | XVDLS6B4 | Complementary | CAD overall width | 45 mm
9031 | XVDLS6B4 | Complementary | CAD overall height | 104 mm
9032 | XVDLS6B4 | Complementary | CAD overall depth | 45 mm
9033 | XVDLS6B4 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
9034 | XVDLS6B4 | Complementary | net weight | 0.085 kg
9035 | XVDLS6B4 | Environment | product certifications | UL CSA
9036 | XVDLS6B4 | Environment | standards | EN/IEC 60947-5-1
9037 | XVDLS6B4 | Environment | protective treatment | TC
9038 | XVDLS6B4 | Environment | ambient air temperature for operation | -10…50 °C
9039 | XVDLS6B4 | Environment | ambient air temperature for storage | -40…70 °C
9040 | XVDLS6B4 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9041 | XVDLS6B4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9042 | XVDLS6B4 | Packing Units | Package 1 Weight | 101.9 g
9043 | XVDLS6B4 | Offer Sustainability | Sustainable offer status | Green Premium product
9044 | XVDLS6B4 | Offer Sustainability | REACh Regulation | REACh Declaration
9045 | XVDLS6B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9046 | XVDLS6B4 | Offer Sustainability | Mercury free | Yes
9047 | XVDLS6B4 | Offer Sustainability | RoHS exemption information | Yes
9048 | XVDLS6B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9049 | XVDLS6B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9050 | XVDLS6B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
9051 | XVDLS6B4 | Contractual warranty | Warranty | 18 months
9052 | XVDLS6B5 | Main | range of product | Harmony XVD Optimum
9053 | XVDLS6B5 | Main | product or component type | Complete miniature beacon
9054 | XVDLS6B5 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9055 | XVDLS6B5 | Main | signalling type | Flashing
9056 | XVDLS6B5 | Main | mounting diameter | 45 mm
9057 | XVDLS6B5 | Main | component name | XVDLS
9058 | XVDLS6B5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9059 | XVDLS6B5 | Main | light source | Integral flash discharge tube, orange
9060 | XVDLS6B5 | Main | bulb type | Flash discharge tube
9061 | XVDLS6B5 | Main | [Us] rated supply voltage | 24 V AC/DC
9062 | XVDLS6B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9063 | XVDLS6B5 | Complementary | cable entry | 1 entry tapped for Pg 7
9064 | XVDLS6B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9065 | XVDLS6B5 | Complementary | current consumption | < 145 mA DC < 90 mA AC
9066 | XVDLS6B5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
9067 | XVDLS6B5 | Complementary | flash energy | 1 J
9068 | XVDLS6B5 | Complementary | CAD overall width | 45 mm
9069 | XVDLS6B5 | Complementary | CAD overall height | 104 mm
9070 | XVDLS6B5 | Complementary | CAD overall depth | 45 mm
9071 | XVDLS6B5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
9072 | XVDLS6B5 | Complementary | net weight | 0.085 kg
9073 | XVDLS6B5 | Environment | product certifications | CSA UL
9074 | XVDLS6B5 | Environment | standards | EN/IEC 60947-5-1
9075 | XVDLS6B5 | Environment | protective treatment | TC
9076 | XVDLS6B5 | Environment | ambient air temperature for operation | -10…50 °C
9077 | XVDLS6B5 | Environment | ambient air temperature for storage | -40…70 °C
9078 | XVDLS6B5 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9079 | XVDLS6B5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9080 | XVDLS6B5 | Packing Units | Package 1 Weight | 104 g
9081 | XVDLS6B5 | Offer Sustainability | Sustainable offer status | Green Premium product
9082 | XVDLS6B5 | Offer Sustainability | REACh Regulation | REACh Declaration
9083 | XVDLS6B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9084 | XVDLS6B5 | Offer Sustainability | Mercury free | Yes
9085 | XVDLS6B5 | Offer Sustainability | RoHS exemption information | Yes
9086 | XVDLS6B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9087 | XVDLS6B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9088 | XVDLS6B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
9089 | XVDLS6B5 | Contractual warranty | Warranty | 18 months
9090 | XVDLS6B6 | Main | range of product | Harmony XVD Optimum
9091 | XVDLS6B6 | Main | product or component type | Complete miniature beacon
9092 | XVDLS6B6 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9093 | XVDLS6B6 | Main | signalling type | Flashing
9094 | XVDLS6B6 | Main | mounting diameter | 45 mm
9095 | XVDLS6B6 | Main | component name | XVDLS
9096 | XVDLS6B6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9097 | XVDLS6B6 | Main | light source | Integral flash discharge tube, blue
9098 | XVDLS6B6 | Main | bulb type | Flash discharge tube
9099 | XVDLS6B6 | Main | [Us] rated supply voltage | 24 V AC/DC
9100 | XVDLS6B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9101 | XVDLS6B6 | Complementary | cable entry | 1 entry tapped for Pg 7
9102 | XVDLS6B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9103 | XVDLS6B6 | Complementary | current consumption | < 145 mA DC < 90 mA AC
9104 | XVDLS6B6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
9105 | XVDLS6B6 | Complementary | flash energy | 1 J
9106 | XVDLS6B6 | Complementary | CAD overall width | 45 mm
9107 | XVDLS6B6 | Complementary | CAD overall height | 104 mm
9108 | XVDLS6B6 | Complementary | CAD overall depth | 45 mm
9109 | XVDLS6B6 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
9110 | XVDLS6B6 | Complementary | net weight | 0.085 kg
9111 | XVDLS6B6 | Environment | product certifications | CSA UL
9112 | XVDLS6B6 | Environment | standards | EN/IEC 60947-5-1
9113 | XVDLS6B6 | Environment | protective treatment | TC
9114 | XVDLS6B6 | Environment | ambient air temperature for operation | -10…50 °C
9115 | XVDLS6B6 | Environment | ambient air temperature for storage | -40…70 °C
9116 | XVDLS6B6 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9117 | XVDLS6B6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9118 | XVDLS6B6 | Packing Units | Package 1 Weight | 109 g
9119 | XVDLS6B6 | Offer Sustainability | Sustainable offer status | Green Premium product
9120 | XVDLS6B6 | Offer Sustainability | REACh Regulation | REACh Declaration
9121 | XVDLS6B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9122 | XVDLS6B6 | Offer Sustainability | Mercury free | Yes
9123 | XVDLS6B6 | Offer Sustainability | RoHS exemption information | Yes
9124 | XVDLS6B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9125 | XVDLS6B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9126 | XVDLS6B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
9127 | XVDLS6B6 | Contractual warranty | Warranty | 18 months
9128 | XVDLS6B7 | Main | range of product | Harmony XVD Optimum
9129 | XVDLS6B7 | Main | product or component type | Complete miniature beacon
9130 | XVDLS6B7 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9131 | XVDLS6B7 | Main | signalling type | Flashing
9132 | XVDLS6B7 | Main | mounting diameter | 45 mm
9133 | XVDLS6B7 | Main | component name | XVDLS
9134 | XVDLS6B7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9135 | XVDLS6B7 | Main | light source | Integral flash discharge tube, clear
9136 | XVDLS6B7 | Main | bulb type | Flash discharge tube
9137 | XVDLS6B7 | Main | [Us] rated supply voltage | 24 V AC/DC
9138 | XVDLS6B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9139 | XVDLS6B7 | Complementary | cable entry | 1 entry tapped for Pg 7
9140 | XVDLS6B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9141 | XVDLS6B7 | Complementary | current consumption | < 145 mA DC < 90 mA AC
9142 | XVDLS6B7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
9143 | XVDLS6B7 | Complementary | flash energy | 1 J
9144 | XVDLS6B7 | Complementary | illuminating intensity | 1.4 cd
9145 | XVDLS6B7 | Complementary | CAD overall width | 45 mm
9146 | XVDLS6B7 | Complementary | CAD overall height | 104 mm
9147 | XVDLS6B7 | Complementary | CAD overall depth | 45 mm
9148 | XVDLS6B7 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
9149 | XVDLS6B7 | Complementary | net weight | 0.085 kg
9150 | XVDLS6B7 | Environment | product certifications | UL CSA
9151 | XVDLS6B7 | Environment | standards | EN/IEC 60947-5-1
9152 | XVDLS6B7 | Environment | protective treatment | TC
9153 | XVDLS6B7 | Environment | ambient air temperature for operation | -10…50 °C
9154 | XVDLS6B7 | Environment | ambient air temperature for storage | -40…70 °C
9155 | XVDLS6B7 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9156 | XVDLS6B7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9157 | XVDLS6B7 | Packing Units | Package 1 Weight | 110 g
9158 | XVDLS6B7 | Offer Sustainability | Sustainable offer status | Green Premium product
9159 | XVDLS6B7 | Offer Sustainability | REACh Regulation | REACh Declaration
9160 | XVDLS6B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9161 | XVDLS6B7 | Offer Sustainability | Mercury free | Yes
9162 | XVDLS6B7 | Offer Sustainability | RoHS exemption information | Yes
9163 | XVDLS6B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9164 | XVDLS6B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9165 | XVDLS6B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
9166 | XVDLS6B7 | Contractual warranty | Warranty | 18 months
9167 | XVDLS6B8 | Main | range of product | Harmony XVD Optimum
9168 | XVDLS6B8 | Main | product or component type | Complete miniature beacon
9169 | XVDLS6B8 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9170 | XVDLS6B8 | Main | signalling type | Flashing
9171 | XVDLS6B8 | Main | mounting diameter | 45 mm
9172 | XVDLS6B8 | Main | component name | XVDLS
9173 | XVDLS6B8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9174 | XVDLS6B8 | Main | light source | Integral flash discharge tube, yellow
9175 | XVDLS6B8 | Main | bulb type | Flash discharge tube
9176 | XVDLS6B8 | Main | [Us] rated supply voltage | 24 V AC/DC
9177 | XVDLS6B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9178 | XVDLS6B8 | Complementary | cable entry | 1 entry tapped for Pg 7
9179 | XVDLS6B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9180 | XVDLS6B8 | Complementary | current consumption | < 145 mA DC < 90 mA AC
9181 | XVDLS6B8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
9182 | XVDLS6B8 | Complementary | flash energy | 1 J
9183 | XVDLS6B8 | Complementary | CAD overall width | 45 mm
9184 | XVDLS6B8 | Complementary | CAD overall height | 104 mm
9185 | XVDLS6B8 | Complementary | CAD overall depth | 45 mm
9186 | XVDLS6B8 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
9187 | XVDLS6B8 | Complementary | net weight | 0.085 kg
9188 | XVDLS6B8 | Environment | product certifications | CSA UL
9189 | XVDLS6B8 | Environment | standards | EN/IEC 60947-5-1
9190 | XVDLS6B8 | Environment | protective treatment | TC
9191 | XVDLS6B8 | Environment | ambient air temperature for operation | -10…50 °C
9192 | XVDLS6B8 | Environment | ambient air temperature for storage | -40…70 °C
9193 | XVDLS6B8 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9194 | XVDLS6B8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9195 | XVDLS6B8 | Packing Units | Package 1 Weight | 0.102 kg
9196 | XVDLS6B8 | Offer Sustainability | Sustainable offer status | Green Premium product
9197 | XVDLS6B8 | Offer Sustainability | REACh Regulation | REACh Declaration
9198 | XVDLS6B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9199 | XVDLS6B8 | Offer Sustainability | Mercury free | Yes
9200 | XVDLS6B8 | Offer Sustainability | RoHS exemption information | Yes
9201 | XVDLS6B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9202 | XVDLS6B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9203 | XVDLS6B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
9204 | XVDLS6B8 | Contractual warranty | Warranty | 18 months
9205 | XVDLS6G3 | Main | range of product | Harmony XVD Optimum
9206 | XVDLS6G3 | Main | product or component type | Complete miniature beacon
9207 | XVDLS6G3 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9208 | XVDLS6G3 | Main | signalling type | Flashing
9209 | XVDLS6G3 | Main | mounting diameter | 45 mm
9210 | XVDLS6G3 | Main | component name | XVDLS
9211 | XVDLS6G3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9212 | XVDLS6G3 | Main | light source | Integral flash discharge tube, green
9213 | XVDLS6G3 | Main | bulb type | Flash discharge tube
9214 | XVDLS6G3 | Main | [Us] rated supply voltage | 120 V AC
9215 | XVDLS6G3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9216 | XVDLS6G3 | Complementary | cable entry | 1 entry tapped for Pg 7
9217 | XVDLS6G3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9218 | XVDLS6G3 | Complementary | current consumption | < 35 mA AC
9219 | XVDLS6G3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
9220 | XVDLS6G3 | Complementary | flash energy | 1 J
9221 | XVDLS6G3 | Complementary | CAD overall width | 45 mm
9222 | XVDLS6G3 | Complementary | CAD overall height | 104 mm
9223 | XVDLS6G3 | Complementary | CAD overall depth | 45 mm
9224 | XVDLS6G3 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
9225 | XVDLS6G3 | Complementary | net weight | 0.085 kg
9226 | XVDLS6G3 | Environment | product certifications | CSA UL
9227 | XVDLS6G3 | Environment | standards | EN/IEC 60947-5-1
9228 | XVDLS6G3 | Environment | protective treatment | TC
9229 | XVDLS6G3 | Environment | ambient air temperature for operation | -10…50 °C
9230 | XVDLS6G3 | Environment | ambient air temperature for storage | -40…70 °C
9231 | XVDLS6G3 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9232 | XVDLS6G3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9233 | XVDLS6G3 | Packing Units | Package 1 Weight | 106 g
9234 | XVDLS6G3 | Offer Sustainability | Sustainable offer status | Green Premium product
9235 | XVDLS6G3 | Offer Sustainability | REACh Regulation | REACh Declaration
9236 | XVDLS6G3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9237 | XVDLS6G3 | Offer Sustainability | Mercury free | Yes
9238 | XVDLS6G3 | Offer Sustainability | RoHS exemption information | Yes
9239 | XVDLS6G3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9240 | XVDLS6G3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9241 | XVDLS6G3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
9242 | XVDLS6G3 | Contractual warranty | Warranty | 18 months
9243 | XVDLS6G4 | Main | range of product | Harmony XVD Optimum
9244 | XVDLS6G4 | Main | product or component type | Complete miniature beacon
9245 | XVDLS6G4 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9246 | XVDLS6G4 | Main | signalling type | Flashing
9247 | XVDLS6G4 | Main | mounting diameter | 45 mm
9248 | XVDLS6G4 | Main | component name | XVDLS
9249 | XVDLS6G4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9250 | XVDLS6G4 | Main | light source | Integral flash discharge tube, red
9251 | XVDLS6G4 | Main | bulb type | Flash discharge tube
9252 | XVDLS6G4 | Main | [Us] rated supply voltage | 120 V AC
9253 | XVDLS6G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9254 | XVDLS6G4 | Complementary | cable entry | 1 entry tapped for Pg 7
9255 | XVDLS6G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9256 | XVDLS6G4 | Complementary | current consumption | < 35 mA AC
9257 | XVDLS6G4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
9258 | XVDLS6G4 | Complementary | flash energy | 1 J
9259 | XVDLS6G4 | Complementary | CAD overall width | 45 mm
9260 | XVDLS6G4 | Complementary | CAD overall height | 104 mm
9261 | XVDLS6G4 | Complementary | CAD overall depth | 45 mm
9262 | XVDLS6G4 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
9263 | XVDLS6G4 | Complementary | net weight | 0.085 kg
9264 | XVDLS6G4 | Environment | product certifications | CSA UL
9265 | XVDLS6G4 | Environment | standards | EN/IEC 60947-5-1
9266 | XVDLS6G4 | Environment | protective treatment | TC
9267 | XVDLS6G4 | Environment | ambient air temperature for storage | -40…70 °C
9268 | XVDLS6G4 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9269 | XVDLS6G4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9270 | XVDLS6G4 | Packing Units | Package 1 Weight | 105 g
9271 | XVDLS6G4 | Offer Sustainability | Sustainable offer status | Green Premium product
9272 | XVDLS6G4 | Offer Sustainability | REACh Regulation | REACh Declaration
9273 | XVDLS6G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9274 | XVDLS6G4 | Offer Sustainability | Mercury free | Yes
9275 | XVDLS6G4 | Offer Sustainability | RoHS exemption information | Yes
9276 | XVDLS6G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9277 | XVDLS6G4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9278 | XVDLS6G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
9279 | XVDLS6G4 | Contractual warranty | Warranty | 18 months
9280 | XVDLS6G5 | Main | range of product | Harmony XVD Optimum
9281 | XVDLS6G5 | Main | product or component type | Complete miniature beacon
9282 | XVDLS6G5 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9283 | XVDLS6G5 | Main | signalling type | Flashing
9284 | XVDLS6G5 | Main | mounting diameter | 45 mm
9285 | XVDLS6G5 | Main | component name | XVDLS
9286 | XVDLS6G5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9287 | XVDLS6G5 | Main | light source | Integral flash discharge tube, orange
9288 | XVDLS6G5 | Main | bulb type | Flash discharge tube
9289 | XVDLS6G5 | Main | [Us] rated supply voltage | 120 V AC
9290 | XVDLS6G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9291 | XVDLS6G5 | Complementary | cable entry | 1 entry tapped for Pg 7
9292 | XVDLS6G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9293 | XVDLS6G5 | Complementary | current consumption | < 35 mA AC
9294 | XVDLS6G5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
9295 | XVDLS6G5 | Complementary | flash energy | 1 J
9296 | XVDLS6G5 | Complementary | CAD overall width | 45 mm
9297 | XVDLS6G5 | Complementary | CAD overall height | 104 mm
9298 | XVDLS6G5 | Complementary | CAD overall depth | 45 mm
9299 | XVDLS6G5 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
9300 | XVDLS6G5 | Complementary | net weight | 0.085 kg
9301 | XVDLS6G5 | Environment | product certifications | CSA UL
9302 | XVDLS6G5 | Environment | standards | EN/IEC 60947-5-1
9303 | XVDLS6G5 | Environment | protective treatment | TC
9304 | XVDLS6G5 | Environment | ambient air temperature for storage | -40…70 °C
9305 | XVDLS6G5 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9306 | XVDLS6G5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9307 | XVDLS6G5 | Offer Sustainability | Sustainable offer status | Green Premium product
9308 | XVDLS6G5 | Offer Sustainability | REACh Regulation | REACh Declaration
9309 | XVDLS6G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9310 | XVDLS6G5 | Offer Sustainability | Mercury free | Yes
9311 | XVDLS6G5 | Offer Sustainability | RoHS exemption information | Yes
9312 | XVDLS6G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9313 | XVDLS6G5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9314 | XVDLS6G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
9315 | XVDLS6G5 | Contractual warranty | Warranty | 18 months
9316 | XVDLS6G6 | Main | range of product | Harmony XVD Optimum
9317 | XVDLS6G6 | Main | product or component type | Complete miniature beacon
9318 | XVDLS6G6 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9319 | XVDLS6G6 | Main | signalling type | Flashing
9320 | XVDLS6G6 | Main | mounting diameter | 45 mm
9321 | XVDLS6G6 | Main | component name | XVDLS
9322 | XVDLS6G6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9323 | XVDLS6G6 | Main | light source | Integral flash discharge tube, blue
9324 | XVDLS6G6 | Main | bulb type | Flash discharge tube
9325 | XVDLS6G6 | Main | [Us] rated supply voltage | 120 V AC
9326 | XVDLS6G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9327 | XVDLS6G6 | Complementary | cable entry | 1 entry tapped for Pg 7
9328 | XVDLS6G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9329 | XVDLS6G6 | Complementary | current consumption | < 35 mA AC
9330 | XVDLS6G6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
9331 | XVDLS6G6 | Complementary | flash energy | 1 J
9332 | XVDLS6G6 | Complementary | CAD overall width | 45 mm
9333 | XVDLS6G6 | Complementary | CAD overall height | 104 mm
9334 | XVDLS6G6 | Complementary | CAD overall depth | 45 mm
9335 | XVDLS6G6 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
9336 | XVDLS6G6 | Complementary | net weight | 0.085 kg
9337 | XVDLS6G6 | Environment | product certifications | CSA UL
9338 | XVDLS6G6 | Environment | standards | EN/IEC 60947-5-1
9339 | XVDLS6G6 | Environment | protective treatment | TC
9340 | XVDLS6G6 | Environment | ambient air temperature for storage | -40…70 °C
9341 | XVDLS6G6 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9342 | XVDLS6G6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9343 | XVDLS6G6 | Packing Units | Package 1 Weight | 0.106 kg
9344 | XVDLS6G6 | Offer Sustainability | Sustainable offer status | Green Premium product
9345 | XVDLS6G6 | Offer Sustainability | REACh Regulation | REACh Declaration
9346 | XVDLS6G6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9347 | XVDLS6G6 | Offer Sustainability | Mercury free | Yes
9348 | XVDLS6G6 | Offer Sustainability | RoHS exemption information | Yes
9349 | XVDLS6G6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9350 | XVDLS6G6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9351 | XVDLS6G6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
9352 | XVDLS6G6 | Contractual warranty | Warranty | 18 months
9353 | XVDLS6G7 | Main | range of product | Harmony XVD Optimum
9354 | XVDLS6G7 | Main | product or component type | Complete miniature beacon
9355 | XVDLS6G7 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9356 | XVDLS6G7 | Main | signalling type | Flashing
9357 | XVDLS6G7 | Main | mounting diameter | 45 mm
9358 | XVDLS6G7 | Main | component name | XVDLS
9359 | XVDLS6G7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9360 | XVDLS6G7 | Main | light source | Integral flash discharge tube, clear
9361 | XVDLS6G7 | Main | bulb type | Flash discharge tube
9362 | XVDLS6G7 | Main | [Us] rated supply voltage | 120 V AC
9363 | XVDLS6G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9364 | XVDLS6G7 | Complementary | cable entry | 1 entry tapped for Pg 7
9365 | XVDLS6G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9366 | XVDLS6G7 | Complementary | current consumption | < 35 mA AC
9367 | XVDLS6G7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
9368 | XVDLS6G7 | Complementary | flash energy | 1 J
9369 | XVDLS6G7 | Complementary | illuminating intensity | 1.4 cd
9370 | XVDLS6G7 | Complementary | CAD overall width | 45 mm
9371 | XVDLS6G7 | Complementary | CAD overall height | 104 mm
9372 | XVDLS6G7 | Complementary | CAD overall depth | 45 mm
9373 | XVDLS6G7 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
9374 | XVDLS6G7 | Complementary | net weight | 0.085 kg
9375 | XVDLS6G7 | Environment | product certifications | CSA UL
9376 | XVDLS6G7 | Environment | standards | EN/IEC 60947-5-1
9377 | XVDLS6G7 | Environment | protective treatment | TC
9378 | XVDLS6G7 | Environment | ambient air temperature for storage | -40…70 °C
9379 | XVDLS6G7 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9380 | XVDLS6G7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9381 | XVDLS6G7 | Contractual warranty | Warranty | 18 months
9382 | XVDLS6G8 | Main | range of product | Harmony XVD Optimum
9383 | XVDLS6G8 | Main | product or component type | Complete miniature beacon
9384 | XVDLS6G8 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9385 | XVDLS6G8 | Main | signalling type | Flashing
9386 | XVDLS6G8 | Main | mounting diameter | 45 mm
9387 | XVDLS6G8 | Main | component name | XVDLS
9388 | XVDLS6G8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9389 | XVDLS6G8 | Main | light source | Integral flash discharge tube, yellow
9390 | XVDLS6G8 | Main | bulb type | Flash discharge tube
9391 | XVDLS6G8 | Main | [Us] rated supply voltage | 120 V AC
9392 | XVDLS6G8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9393 | XVDLS6G8 | Complementary | cable entry | 1 entry tapped for Pg 7
9394 | XVDLS6G8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9395 | XVDLS6G8 | Complementary | current consumption | < 35 mA AC
9396 | XVDLS6G8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
9397 | XVDLS6G8 | Complementary | flash energy | 1 J
9398 | XVDLS6G8 | Complementary | CAD overall width | 45 mm
9399 | XVDLS6G8 | Complementary | CAD overall height | 104 mm
9400 | XVDLS6G8 | Complementary | CAD overall depth | 45 mm
9401 | XVDLS6G8 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
9402 | XVDLS6G8 | Complementary | net weight | 0.085 kg
9403 | XVDLS6G8 | Environment | product certifications | UL CSA
9404 | XVDLS6G8 | Environment | standards | EN/IEC 60947-5-1
9405 | XVDLS6G8 | Environment | protective treatment | TC
9406 | XVDLS6G8 | Environment | ambient air temperature for storage | -40…70 °C
9407 | XVDLS6G8 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9408 | XVDLS6G8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9409 | XVDLS6G8 | Packing Units | Package 1 Weight | 0.106 kg
9410 | XVDLS6G8 | Contractual warranty | Warranty | 18 months
9411 | XVDLS6M3 | Main | range of product | Harmony XVD Optimum
9412 | XVDLS6M3 | Main | product or component type | Complete miniature beacon
9413 | XVDLS6M3 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9414 | XVDLS6M3 | Main | signalling type | Flashing
9415 | XVDLS6M3 | Main | mounting diameter | 45 mm
9416 | XVDLS6M3 | Main | component name | XVDLS
9417 | XVDLS6M3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9418 | XVDLS6M3 | Main | light source | Integral flash discharge tube, green
9419 | XVDLS6M3 | Main | bulb type | Flash discharge tube
9420 | XVDLS6M3 | Main | [Us] rated supply voltage | 230 V AC
9421 | XVDLS6M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9422 | XVDLS6M3 | Complementary | cable entry | 1 entry tapped for Pg 7
9423 | XVDLS6M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9424 | XVDLS6M3 | Complementary | current consumption | < 25 mA AC
9425 | XVDLS6M3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
9426 | XVDLS6M3 | Complementary | flash energy | 1 J
9427 | XVDLS6M3 | Complementary | CAD overall width | 45 mm
9428 | XVDLS6M3 | Complementary | CAD overall height | 104 mm
9429 | XVDLS6M3 | Complementary | CAD overall depth | 45 mm
9430 | XVDLS6M3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
9431 | XVDLS6M3 | Complementary | net weight | 0.085 kg
9432 | XVDLS6M3 | Environment | product certifications | CSA UL
9433 | XVDLS6M3 | Environment | standards | EN/IEC 60947-5-1
9434 | XVDLS6M3 | Environment | protective treatment | TC
9435 | XVDLS6M3 | Environment | ambient air temperature for storage | -40…70 °C
9436 | XVDLS6M3 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9437 | XVDLS6M3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9438 | XVDLS6M3 | Packing Units | Package 1 Weight | 0.110 kg
9439 | XVDLS6M3 | Offer Sustainability | Sustainable offer status | Green Premium product
9440 | XVDLS6M3 | Offer Sustainability | REACh Regulation | REACh Declaration
9441 | XVDLS6M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9442 | XVDLS6M3 | Offer Sustainability | Mercury free | Yes
9443 | XVDLS6M3 | Offer Sustainability | RoHS exemption information | Yes
9444 | XVDLS6M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9445 | XVDLS6M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9446 | XVDLS6M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
9447 | XVDLS6M3 | Contractual warranty | Warranty | 18 months
9448 | XVDLS6M4 | Main | range of product | Harmony XVD Optimum
9449 | XVDLS6M4 | Main | product or component type | Complete miniature beacon
9450 | XVDLS6M4 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9451 | XVDLS6M4 | Main | signalling type | Flashing
9452 | XVDLS6M4 | Main | mounting diameter | 45 mm
9453 | XVDLS6M4 | Main | component name | XVDLS
9454 | XVDLS6M4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9455 | XVDLS6M4 | Main | light source | Integral flash discharge tube, red
9456 | XVDLS6M4 | Main | bulb type | Flash discharge tube
9457 | XVDLS6M4 | Main | [Us] rated supply voltage | 230 V AC
9458 | XVDLS6M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9459 | XVDLS6M4 | Complementary | cable entry | 1 entry tapped for Pg 7
9460 | XVDLS6M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9461 | XVDLS6M4 | Complementary | current consumption | < 25 mA AC
9462 | XVDLS6M4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
9463 | XVDLS6M4 | Complementary | flash energy | 1 J
9464 | XVDLS6M4 | Complementary | CAD overall width | 45 mm
9465 | XVDLS6M4 | Complementary | CAD overall height | 104 mm
9466 | XVDLS6M4 | Complementary | CAD overall depth | 45 mm
9467 | XVDLS6M4 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
9468 | XVDLS6M4 | Complementary | net weight | 0.085 kg
9469 | XVDLS6M4 | Environment | product certifications | UL CSA
9470 | XVDLS6M4 | Environment | standards | EN/IEC 60947-5-1
9471 | XVDLS6M4 | Environment | protective treatment | TC
9472 | XVDLS6M4 | Environment | ambient air temperature for storage | -40…70 °C
9473 | XVDLS6M4 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9474 | XVDLS6M4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9475 | XVDLS6M4 | Packing Units | Package 1 Weight | 100 g
9476 | XVDLS6M4 | Packing Units | Package 2 Weight | 1.407 kg
9477 | XVDLS6M4 | Offer Sustainability | Sustainable offer status | Green Premium product
9478 | XVDLS6M4 | Offer Sustainability | REACh Regulation | REACh Declaration
9479 | XVDLS6M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9480 | XVDLS6M4 | Offer Sustainability | Mercury free | Yes
9481 | XVDLS6M4 | Offer Sustainability | RoHS exemption information | Yes
9482 | XVDLS6M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9483 | XVDLS6M4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9484 | XVDLS6M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
9485 | XVDLS6M4 | Contractual warranty | Warranty | 18 months
9486 | XVDLS6M5 | Main | range of product | Harmony XVD Optimum
9487 | XVDLS6M5 | Main | product or component type | Complete miniature beacon
9488 | XVDLS6M5 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9489 | XVDLS6M5 | Main | signalling type | Flashing
9490 | XVDLS6M5 | Main | mounting diameter | 45 mm
9491 | XVDLS6M5 | Main | component name | XVDLS
9492 | XVDLS6M5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9493 | XVDLS6M5 | Main | light source | Integral flash discharge tube, orange
9494 | XVDLS6M5 | Main | bulb type | Flash discharge tube
9495 | XVDLS6M5 | Main | [Us] rated supply voltage | 230 V AC
9496 | XVDLS6M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9497 | XVDLS6M5 | Complementary | cable entry | 1 entry tapped for Pg 7
9498 | XVDLS6M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9499 | XVDLS6M5 | Complementary | current consumption | < 25 mA AC
9500 | XVDLS6M5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
9501 | XVDLS6M5 | Complementary | flash energy | 1 J
9502 | XVDLS6M5 | Complementary | CAD overall width | 45 mm
9503 | XVDLS6M5 | Complementary | CAD overall height | 104 mm
9504 | XVDLS6M5 | Complementary | CAD overall depth | 45 mm
9505 | XVDLS6M5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
9506 | XVDLS6M5 | Complementary | net weight | 0.085 kg
9507 | XVDLS6M5 | Environment | product certifications | CSA UL
9508 | XVDLS6M5 | Environment | standards | EN/IEC 60947-5-1
9509 | XVDLS6M5 | Environment | protective treatment | TC
9510 | XVDLS6M5 | Environment | ambient air temperature for storage | -40…70 °C
9511 | XVDLS6M5 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9512 | XVDLS6M5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9513 | XVDLS6M5 | Packing Units | Package 1 Weight | 100 g
9514 | XVDLS6M5 | Packing Units | Package 2 Weight | 1.394 kg
9515 | XVDLS6M5 | Offer Sustainability | Sustainable offer status | Green Premium product
9516 | XVDLS6M5 | Offer Sustainability | REACh Regulation | REACh Declaration
9517 | XVDLS6M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9518 | XVDLS6M5 | Offer Sustainability | Mercury free | Yes
9519 | XVDLS6M5 | Offer Sustainability | RoHS exemption information | Yes
9520 | XVDLS6M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9521 | XVDLS6M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9522 | XVDLS6M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
9523 | XVDLS6M5 | Contractual warranty | Warranty | 18 months
9524 | XVDLS6M6 | Main | range of product | Harmony XVD Optimum
9525 | XVDLS6M6 | Main | product or component type | Complete miniature beacon
9526 | XVDLS6M6 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9527 | XVDLS6M6 | Main | signalling type | Flashing
9528 | XVDLS6M6 | Main | mounting diameter | 45 mm
9529 | XVDLS6M6 | Main | component name | XVDLS
9530 | XVDLS6M6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9531 | XVDLS6M6 | Main | light source | Integral flash discharge tube, blue
9532 | XVDLS6M6 | Main | bulb type | Flash discharge tube
9533 | XVDLS6M6 | Main | [Us] rated supply voltage | 230 V AC
9534 | XVDLS6M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9535 | XVDLS6M6 | Complementary | cable entry | 1 entry tapped for Pg 7
9536 | XVDLS6M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9537 | XVDLS6M6 | Complementary | current consumption | < 25 mA AC
9538 | XVDLS6M6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
9539 | XVDLS6M6 | Complementary | flash energy | 1 J
9540 | XVDLS6M6 | Complementary | CAD overall width | 45 mm
9541 | XVDLS6M6 | Complementary | CAD overall height | 104 mm
9542 | XVDLS6M6 | Complementary | CAD overall depth | 45 mm
9543 | XVDLS6M6 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
9544 | XVDLS6M6 | Complementary | net weight | 0.085 kg
9545 | XVDLS6M6 | Environment | product certifications | CSA UL
9546 | XVDLS6M6 | Environment | standards | EN/IEC 60947-5-1
9547 | XVDLS6M6 | Environment | protective treatment | TC
9548 | XVDLS6M6 | Environment | ambient air temperature for storage | -40…70 °C
9549 | XVDLS6M6 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9550 | XVDLS6M6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9551 | XVDLS6M6 | Packing Units | Package 1 Weight | 101 g
9552 | XVDLS6M6 | Offer Sustainability | Sustainable offer status | Green Premium product
9553 | XVDLS6M6 | Offer Sustainability | REACh Regulation | REACh Declaration
9554 | XVDLS6M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9555 | XVDLS6M6 | Offer Sustainability | Mercury free | Yes
9556 | XVDLS6M6 | Offer Sustainability | RoHS exemption information | Yes
9557 | XVDLS6M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9558 | XVDLS6M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9559 | XVDLS6M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
9560 | XVDLS6M6 | Contractual warranty | Warranty | 18 months
9561 | XVDLS6M7 | Main | range of product | Harmony XVD Optimum
9562 | XVDLS6M7 | Main | product or component type | Complete miniature beacon
9563 | XVDLS6M7 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9564 | XVDLS6M7 | Main | signalling type | Flashing
9565 | XVDLS6M7 | Main | mounting diameter | 45 mm
9566 | XVDLS6M7 | Main | component name | XVDLS
9567 | XVDLS6M7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9568 | XVDLS6M7 | Main | light source | Integral flash discharge tube, clear
9569 | XVDLS6M7 | Main | bulb type | Flash discharge tube
9570 | XVDLS6M7 | Main | [Us] rated supply voltage | 230 V AC
9571 | XVDLS6M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9572 | XVDLS6M7 | Complementary | cable entry | 1 entry tapped for Pg 7
9573 | XVDLS6M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9574 | XVDLS6M7 | Complementary | current consumption | < 25 mA AC
9575 | XVDLS6M7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
9576 | XVDLS6M7 | Complementary | flash energy | 1 J
9577 | XVDLS6M7 | Complementary | illuminating intensity | 1.4 cd
9578 | XVDLS6M7 | Complementary | CAD overall width | 45 mm
9579 | XVDLS6M7 | Complementary | CAD overall height | 104 mm
9580 | XVDLS6M7 | Complementary | CAD overall depth | 45 mm
9581 | XVDLS6M7 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
9582 | XVDLS6M7 | Complementary | net weight | 0.085 kg
9583 | XVDLS6M7 | Environment | product certifications | UL CSA
9584 | XVDLS6M7 | Environment | standards | EN/IEC 60947-5-1
9585 | XVDLS6M7 | Environment | protective treatment | TC
9586 | XVDLS6M7 | Environment | ambient air temperature for storage | -40…70 °C
9587 | XVDLS6M7 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9588 | XVDLS6M7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9589 | XVDLS6M7 | Packing Units | Package 1 Weight | 0.110 kg
9590 | XVDLS6M7 | Offer Sustainability | Sustainable offer status | Green Premium product
9591 | XVDLS6M7 | Offer Sustainability | REACh Regulation | REACh Declaration
9592 | XVDLS6M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9593 | XVDLS6M7 | Offer Sustainability | Mercury free | Yes
9594 | XVDLS6M7 | Offer Sustainability | RoHS exemption information | Yes
9595 | XVDLS6M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9596 | XVDLS6M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9597 | XVDLS6M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
9598 | XVDLS6M7 | Contractual warranty | Warranty | 18 months
9599 | XVDLS6M8 | Main | range of product | Harmony XVD Optimum
9600 | XVDLS6M8 | Main | product or component type | Complete miniature beacon
9601 | XVDLS6M8 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
9602 | XVDLS6M8 | Main | signalling type | Flashing
9603 | XVDLS6M8 | Main | mounting diameter | 45 mm
9604 | XVDLS6M8 | Main | component name | XVDLS
9605 | XVDLS6M8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
9606 | XVDLS6M8 | Main | light source | Integral flash discharge tube, yellow
9607 | XVDLS6M8 | Main | bulb type | Flash discharge tube
9608 | XVDLS6M8 | Main | [Us] rated supply voltage | 230 V AC
9609 | XVDLS6M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
9610 | XVDLS6M8 | Complementary | cable entry | 1 entry tapped for Pg 7
9611 | XVDLS6M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
9612 | XVDLS6M8 | Complementary | current consumption | < 25 mA AC
9613 | XVDLS6M8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
9614 | XVDLS6M8 | Complementary | flash energy | 1 J
9615 | XVDLS6M8 | Complementary | CAD overall width | 45 mm
9616 | XVDLS6M8 | Complementary | CAD overall height | 104 mm
9617 | XVDLS6M8 | Complementary | CAD overall depth | 45 mm
9618 | XVDLS6M8 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
9619 | XVDLS6M8 | Complementary | net weight | 0.085 kg
9620 | XVDLS6M8 | Environment | product certifications | CSA UL
9621 | XVDLS6M8 | Environment | standards | EN/IEC 60947-5-1
9622 | XVDLS6M8 | Environment | protective treatment | TC
9623 | XVDLS6M8 | Environment | ambient air temperature for storage | -40…70 °C
9624 | XVDLS6M8 | Environment | electrical shock protection class | Class II conforming to IEC 60536
9625 | XVDLS6M8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
9626 | XVDLS6M8 | Packing Units | Package 1 Weight | 102 g
9627 | XVDLS6M8 | Offer Sustainability | Sustainable offer status | Green Premium product
9628 | XVDLS6M8 | Offer Sustainability | REACh Regulation | REACh Declaration
9629 | XVDLS6M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9630 | XVDLS6M8 | Offer Sustainability | Mercury free | Yes
9631 | XVDLS6M8 | Offer Sustainability | RoHS exemption information | Yes
9632 | XVDLS6M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9633 | XVDLS6M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9634 | XVDLS6M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
9635 | XVDLS6M8 | Contractual warranty | Warranty | 18 months
9636 | XVSV7BBN | Main | range of product | Harmony XVS
9637 | XVSV7BBN | Main | product or component type | Editable electronic alarm
9638 | XVSV7BBN | Main | beacon or indicator bank unit type | Sound unit
9639 | XVSV7BBN | Main | device short name | XVSV
9640 | XVSV7BBN | Complementary | colour | Dark grey
9641 | XVSV7BBN | Complementary | input type | Bit: 6 channel input Binary: 63 channel input
9642 | XVSV7BBN | Complementary | assembly style | Ready assembled
9643 | XVSV7BBN | Complementary | material | PC (polycarbonate): body PC (polycarbonate): back cover TPE (thermoplastic elastomer): front panel NBR (nitrile butadiene rubber)
9644 | XVSV7BBN | Complementary | net weight | 0.142 kg
9645 | XVSV7BBN | Complementary | marking | CE
9646 | XVSV7BBN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
9647 | XVSV7BBN | Complementary | mounting support | 72 mm DIN rail
9648 | XVSV7BBN | Complementary | [Us] rated supply voltage | 12...24 V DC
9649 | XVSV7BBN | Complementary | [Ue] rated operational voltage | 10...30 V DC
9650 | XVSV7BBN | Complementary | inrush current | 30 A
9651 | XVSV7BBN | Complementary | associated fuse rating | 1 A
9652 | XVSV7BBN | Complementary | [Uimp] rated impulse withstand voltage | 1 kV
9653 | XVSV7BBN | Complementary | power consumption in W | 1.8 W
9654 | XVSV7BBN | Complementary | current consumption | 75 mA at 24 V DC
9655 | XVSV7BBN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
9656 | XVSV7BBN | Complementary | device application | Printing Subway Packaging
9657 | XVSV7BBN | Complementary | mounting diameter | 80 mm
9658 | XVSV7BBN | Complementary | width | 80 mm
9659 | XVSV7BBN | Complementary | height | 80 mm
9660 | XVSV7BBN | Complementary | depth | 24.9 mm
9661 | XVSV7BBN | Environment | discrete output type | NPN
9662 | XVSV7BBN | Environment | signalling type | Adjustable vocal sound
9663 | XVSV7BBN | Environment | protective treatment | TC
9664 | XVSV7BBN | Environment | ambient air temperature for storage | -20…60 °C
9665 | XVSV7BBN | Environment | ambient air temperature for operation | -10…55 °C
9666 | XVSV7BBN | Environment | relative humidity | 35…85 % without condensation
9667 | XVSV7BBN | Environment | vibration resistance | 7 gn
9668 | XVSV7BBN | Environment | IP degree of protection | Panel mounted: IP65 conforming to EN/IEC 60529 Wall mounted: IP20
9669 | XVSV7BBN | Environment | noise level | 0…89 dB (stop or suppress) at 1 m
9670 | XVSV7BBN | Packing Units | Package 1 Weight | 0.311 kg
9671 | XVSV7BBN | Offer Sustainability | Sustainable offer status | Green Premium product
9672 | XVSV7BBN | Offer Sustainability | REACh Regulation | REACh Declaration
9673 | XVSV7BBN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9674 | XVSV7BBN | Offer Sustainability | Mercury free | Yes
9675 | XVSV7BBN | Offer Sustainability | RoHS exemption information | Yes
9676 | XVSV7BBN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9677 | XVSV7BBN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9678 | XVSV7BBN | Offer Sustainability | Circularity Profile | End of Life Information
9679 | XVSV7BWN | Main | range of product | Harmony XVS
9680 | XVSV7BWN | Main | product or component type | Editable electronic alarm
9681 | XVSV7BWN | Main | beacon or indicator bank unit type | Sound unit
9682 | XVSV7BWN | Main | device short name | XVSV
9683 | XVSV7BWN | Complementary | colour | White
9684 | XVSV7BWN | Complementary | input type | Bit: 6 channel input Binary: 63 channel input
9685 | XVSV7BWN | Complementary | assembly style | Ready assembled
9686 | XVSV7BWN | Complementary | material | PC (polycarbonate): body PC (polycarbonate): back cover TPE (thermoplastic elastomer): front panel NBR (nitrile butadiene rubber)
9687 | XVSV7BWN | Complementary | net weight | 0.142 kg
9688 | XVSV7BWN | Complementary | marking | CE
9689 | XVSV7BWN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
9690 | XVSV7BWN | Complementary | mounting support | 72 mm DIN rail
9691 | XVSV7BWN | Complementary | [Us] rated supply voltage | 12...24 V DC
9692 | XVSV7BWN | Complementary | [Ue] rated operational voltage | 10...30 V DC
9693 | XVSV7BWN | Complementary | inrush current | 30 A
9694 | XVSV7BWN | Complementary | associated fuse rating | 1 A
9695 | XVSV7BWN | Complementary | [Uimp] rated impulse withstand voltage | 1 kV
9696 | XVSV7BWN | Complementary | power consumption in W | 1.8 W
9697 | XVSV7BWN | Complementary | current consumption | 75 mA at 24 V DC
9698 | XVSV7BWN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
9699 | XVSV7BWN | Complementary | device application | Subway Packaging Printing
9700 | XVSV7BWN | Complementary | mounting diameter | 80 mm
9701 | XVSV7BWN | Complementary | width | 80 mm
9702 | XVSV7BWN | Complementary | height | 80 mm
9703 | XVSV7BWN | Complementary | depth | 24.9 mm
9704 | XVSV7BWN | Environment | discrete output type | NPN
9705 | XVSV7BWN | Environment | signalling type | Adjustable vocal sound
9706 | XVSV7BWN | Environment | protective treatment | TC
9707 | XVSV7BWN | Environment | ambient air temperature for storage | -20…60 °C
9708 | XVSV7BWN | Environment | ambient air temperature for operation | -10…55 °C
9709 | XVSV7BWN | Environment | relative humidity | 35…85 % without condensation
9710 | XVSV7BWN | Environment | vibration resistance | 7 gn
9711 | XVSV7BWN | Environment | IP degree of protection | Panel mounted: IP65 conforming to EN/IEC 60529 Wall mounted: IP20
9712 | XVSV7BWN | Environment | noise level | 0…89 dB (stop or suppress) at 1 m
9713 | XVSV7BWN | Packing Units | Package 1 Weight | 0.311 kg
9714 | XVSV7BWN | Offer Sustainability | Sustainable offer status | Green Premium product
9715 | XVSV7BWN | Offer Sustainability | REACh Regulation | REACh Declaration
9716 | XVSV7BWN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9717 | XVSV7BWN | Offer Sustainability | Mercury free | Yes
9718 | XVSV7BWN | Offer Sustainability | RoHS exemption information | Yes
9719 | XVSV7BWN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9720 | XVSV7BWN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9721 | XVSV7BWN | Offer Sustainability | Circularity Profile | End of Life Information
9722 | XVSV7BBP | Main | range of product | Harmony XVS
9723 | XVSV7BBP | Main | product or component type | Editable electronic alarm
9724 | XVSV7BBP | Main | beacon or indicator bank unit type | Sound unit
9725 | XVSV7BBP | Main | device short name | XVSV
9726 | XVSV7BBP | Complementary | colour | Dark grey
9727 | XVSV7BBP | Complementary | input type | Bit: 6 channel input Binary: 63 channel input
9728 | XVSV7BBP | Complementary | assembly style | Ready assembled
9729 | XVSV7BBP | Complementary | material | PC (polycarbonate): body PC (polycarbonate): back cover TPE (thermoplastic elastomer): front panel NBR (nitrile butadiene rubber)
9730 | XVSV7BBP | Complementary | net weight | 0.142 kg
9731 | XVSV7BBP | Complementary | marking | CE
9732 | XVSV7BBP | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
9733 | XVSV7BBP | Complementary | mounting support | 72 mm DIN rail
9734 | XVSV7BBP | Complementary | [Us] rated supply voltage | 12...24 V DC
9735 | XVSV7BBP | Complementary | [Ue] rated operational voltage | 10...30 V DC
9736 | XVSV7BBP | Complementary | inrush current | 30 A
9737 | XVSV7BBP | Complementary | associated fuse rating | 1 A
9738 | XVSV7BBP | Complementary | [Uimp] rated impulse withstand voltage | 1 kV
9739 | XVSV7BBP | Complementary | power consumption in W | 1.8 W
9740 | XVSV7BBP | Complementary | current consumption | 75 mA at 24 V DC
9741 | XVSV7BBP | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
9742 | XVSV7BBP | Complementary | device application | Printing Packaging Subway
9743 | XVSV7BBP | Complementary | mounting diameter | 80 mm
9744 | XVSV7BBP | Complementary | width | 80 mm
9745 | XVSV7BBP | Complementary | height | 80 mm
9746 | XVSV7BBP | Complementary | depth | 24.9 mm
9747 | XVSV7BBP | Environment | discrete output type | PNP
9748 | XVSV7BBP | Environment | signalling type | Adjustable vocal sound
9749 | XVSV7BBP | Environment | protective treatment | TC
9750 | XVSV7BBP | Environment | ambient air temperature for storage | -20…60 °C
9751 | XVSV7BBP | Environment | ambient air temperature for operation | -10…55 °C
9752 | XVSV7BBP | Environment | relative humidity | 35…85 % without condensation
9753 | XVSV7BBP | Environment | vibration resistance | 7 gn
9754 | XVSV7BBP | Environment | IP degree of protection | Panel mounted: IP65 conforming to EN/IEC 60529 Wall mounted: IP20
9755 | XVSV7BBP | Environment | noise level | 0…89 dB (stop or suppress) at 1 m
9756 | XVSV7BBP | Packing Units | Package 1 Weight | 0.318 kg
9757 | XVSV7BBP | Offer Sustainability | Sustainable offer status | Green Premium product
9758 | XVSV7BBP | Offer Sustainability | REACh Regulation | REACh Declaration
9759 | XVSV7BBP | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9760 | XVSV7BBP | Offer Sustainability | Mercury free | Yes
9761 | XVSV7BBP | Offer Sustainability | RoHS exemption information | Yes
9762 | XVSV7BBP | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9763 | XVSV7BBP | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9764 | XVSV7BBP | Offer Sustainability | Circularity Profile | End of Life Information
9765 | XVSV9BBN | Main | range of product | Harmony XVS
9766 | XVSV9BBN | Main | product or component type | Editable electronic alarm
9767 | XVSV9BBN | Main | beacon or indicator bank unit type | Sound unit
9768 | XVSV9BBN | Main | device short name | XVSV
9769 | XVSV9BBN | Complementary | colour | Dark grey
9770 | XVSV9BBN | Complementary | input type | Bit: 6 channel input Binary: 63 channel input
9771 | XVSV9BBN | Complementary | assembly style | Ready assembled
9772 | XVSV9BBN | Complementary | material | PC (polycarbonate): body PC (polycarbonate): back cover TPE (thermoplastic elastomer): front panel NBR (nitrile butadiene rubber)
9773 | XVSV9BBN | Complementary | net weight | 0.268 kg
9774 | XVSV9BBN | Complementary | marking | CE
9775 | XVSV9BBN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
9776 | XVSV9BBN | Complementary | mounting support | 96 mm DIN rail
9777 | XVSV9BBN | Complementary | [Us] rated supply voltage | 12...24 V DC
9778 | XVSV9BBN | Complementary | [Ue] rated operational voltage | 10...30 V DC
9779 | XVSV9BBN | Complementary | inrush current | 30 A
9780 | XVSV9BBN | Complementary | associated fuse rating | 1 A
9781 | XVSV9BBN | Complementary | [Uimp] rated impulse withstand voltage | 1 kV
9782 | XVSV9BBN | Complementary | power consumption in W | 3.8 W
9783 | XVSV9BBN | Complementary | current consumption | 160 mA at 24 V DC
9784 | XVSV9BBN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
9785 | XVSV9BBN | Complementary | device application | Subway Printing Packaging
9786 | XVSV9BBN | Complementary | mounting diameter | 105 mm
9787 | XVSV9BBN | Complementary | width | 105 mm
9788 | XVSV9BBN | Complementary | height | 105 mm
9789 | XVSV9BBN | Complementary | depth | 50.1 mm
9790 | XVSV9BBN | Environment | discrete output type | NPN
9791 | XVSV9BBN | Environment | signalling type | Adjustable vocal sound
9792 | XVSV9BBN | Environment | protective treatment | TC
9793 | XVSV9BBN | Environment | ambient air temperature for storage | -20…60 °C
9794 | XVSV9BBN | Environment | ambient air temperature for operation | -10…55 °C
9795 | XVSV9BBN | Environment | relative humidity | 35…85 % without condensation
9796 | XVSV9BBN | Environment | vibration resistance | 7 gn
9797 | XVSV9BBN | Environment | IP degree of protection | Panel mounted: IP65 conforming to EN/IEC 60529 Wall mounted: IP20
9798 | XVSV9BBN | Environment | noise level | 0…97 dB (stop or suppress) at 1 m
9799 | XVSV9BBN | Packing Units | Package 1 Weight | 0.546 kg
9800 | XVSV9BBN | Offer Sustainability | Sustainable offer status | Green Premium product
9801 | XVSV9BBN | Offer Sustainability | REACh Regulation | REACh Declaration
9802 | XVSV9BBN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9803 | XVSV9BBN | Offer Sustainability | Mercury free | Yes
9804 | XVSV9BBN | Offer Sustainability | RoHS exemption information | Yes
9805 | XVSV9BBN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9806 | XVSV9BBN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9807 | XVSV9BBN | Offer Sustainability | Circularity Profile | End of Life Information
9808 | XVSV9BWN | Main | range of product | Harmony XVS
9809 | XVSV9BWN | Main | product or component type | Editable electronic alarm
9810 | XVSV9BWN | Main | beacon or indicator bank unit type | Sound unit
9811 | XVSV9BWN | Main | device short name | XVSV
9812 | XVSV9BWN | Complementary | colour | White
9813 | XVSV9BWN | Complementary | input type | Bit: 6 channel input Binary: 63 channel input
9814 | XVSV9BWN | Complementary | assembly style | Ready assembled
9815 | XVSV9BWN | Complementary | material | PC (polycarbonate): body PC (polycarbonate): back cover TPE (thermoplastic elastomer): front panel NBR (nitrile butadiene rubber)
9816 | XVSV9BWN | Complementary | net weight | 0.268 kg
9817 | XVSV9BWN | Complementary | marking | CE
9818 | XVSV9BWN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
9819 | XVSV9BWN | Complementary | mounting support | 96 mm DIN rail
9820 | XVSV9BWN | Complementary | [Us] rated supply voltage | 12...24 V DC
9821 | XVSV9BWN | Complementary | [Ue] rated operational voltage | 10...30 V DC
9822 | XVSV9BWN | Complementary | inrush current | 30 A
9823 | XVSV9BWN | Complementary | associated fuse rating | 1 A
9824 | XVSV9BWN | Complementary | [Uimp] rated impulse withstand voltage | 1 kV
9825 | XVSV9BWN | Complementary | power consumption in W | 3.8 W
9826 | XVSV9BWN | Complementary | current consumption | 160 mA at 24 V DC
9827 | XVSV9BWN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
9828 | XVSV9BWN | Complementary | device application | Packaging Printing Subway
9829 | XVSV9BWN | Complementary | mounting diameter | 105 mm
9830 | XVSV9BWN | Complementary | width | 105 mm
9831 | XVSV9BWN | Complementary | height | 105 mm
9832 | XVSV9BWN | Complementary | depth | 50.1 mm
9833 | XVSV9BWN | Environment | discrete output type | NPN
9834 | XVSV9BWN | Environment | signalling type | Adjustable vocal sound
9835 | XVSV9BWN | Environment | protective treatment | TC
9836 | XVSV9BWN | Environment | ambient air temperature for storage | -20…60 °C
9837 | XVSV9BWN | Environment | ambient air temperature for operation | -10…55 °C
9838 | XVSV9BWN | Environment | relative humidity | 35…85 % without condensation
9839 | XVSV9BWN | Environment | vibration resistance | 7 gn
9840 | XVSV9BWN | Environment | IP degree of protection | Panel mounted: IP65 conforming to EN/IEC 60529 Wall mounted: IP20
9841 | XVSV9BWN | Environment | noise level | 0…97 dB (stop or suppress) at 1 m
9842 | XVSV9BWN | Packing Units | Package 1 Weight | 268 g
9843 | XVSV9BWN | Offer Sustainability | Sustainable offer status | Green Premium product
9844 | XVSV9BWN | Offer Sustainability | REACh Regulation | REACh Declaration
9845 | XVSV9BWN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9846 | XVSV9BWN | Offer Sustainability | Mercury free | Yes
9847 | XVSV9BWN | Offer Sustainability | RoHS exemption information | Yes
9848 | XVSV9BWN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9849 | XVSV9BWN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9850 | XVSV9BWN | Offer Sustainability | Circularity Profile | End of Life Information
9851 | XVSV9BBP | Main | range of product | Harmony XVS
9852 | XVSV9BBP | Main | product or component type | Editable electronic alarm
9853 | XVSV9BBP | Main | beacon or indicator bank unit type | Sound unit
9854 | XVSV9BBP | Main | device short name | XVSV
9855 | XVSV9BBP | Complementary | colour | Dark grey
9856 | XVSV9BBP | Complementary | input type | Bit: 6 channel input Binary: 63 channel input
9857 | XVSV9BBP | Complementary | assembly style | Ready assembled
9858 | XVSV9BBP | Complementary | material | PC (polycarbonate): body PC (polycarbonate): back cover TPE (thermoplastic elastomer): front panel NBR (nitrile butadiene rubber)
9859 | XVSV9BBP | Complementary | net weight | 0.268 kg
9860 | XVSV9BBP | Complementary | marking | CE
9861 | XVSV9BBP | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
9862 | XVSV9BBP | Complementary | mounting support | 96 mm DIN rail
9863 | XVSV9BBP | Complementary | [Us] rated supply voltage | 12...24 V DC
9864 | XVSV9BBP | Complementary | [Ue] rated operational voltage | 10...30 V DC
9865 | XVSV9BBP | Complementary | inrush current | 30 A
9866 | XVSV9BBP | Complementary | associated fuse rating | 1 A
9867 | XVSV9BBP | Complementary | [Uimp] rated impulse withstand voltage | 1 kV
9868 | XVSV9BBP | Complementary | power consumption in W | 3.8 W
9869 | XVSV9BBP | Complementary | current consumption | 160 mA at 24 V DC
9870 | XVSV9BBP | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
9871 | XVSV9BBP | Complementary | device application | Printing Packaging Subway
9872 | XVSV9BBP | Complementary | mounting diameter | 105 mm
9873 | XVSV9BBP | Complementary | width | 105 mm
9874 | XVSV9BBP | Complementary | height | 105 mm
9875 | XVSV9BBP | Complementary | depth | 50.1 mm
9876 | XVSV9BBP | Environment | discrete output type | PNP
9877 | XVSV9BBP | Environment | signalling type | Adjustable vocal sound
9878 | XVSV9BBP | Environment | protective treatment | TC
9879 | XVSV9BBP | Environment | ambient air temperature for storage | -20…60 °C
9880 | XVSV9BBP | Environment | ambient air temperature for operation | -10…55 °C
9881 | XVSV9BBP | Environment | relative humidity | 35…85 % without condensation
9882 | XVSV9BBP | Environment | vibration resistance | 7 gn
9883 | XVSV9BBP | Environment | IP degree of protection | Panel mounted: IP65 conforming to EN/IEC 60529 Wall mounted: IP20
9884 | XVSV9BBP | Environment | noise level | 0…97 dB (stop or suppress) at 1 m
9885 | XVSV9BBP | Packing Units | Package 1 Weight | 0.268 kg
9886 | XVSV9BBP | Offer Sustainability | Sustainable offer status | Green Premium product
9887 | XVSV9BBP | Offer Sustainability | REACh Regulation | REACh Declaration
9888 | XVSV9BBP | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9889 | XVSV9BBP | Offer Sustainability | Mercury free | Yes
9890 | XVSV9BBP | Offer Sustainability | RoHS exemption information | Yes
9891 | XVSV9BBP | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9892 | XVSV9BBP | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9893 | XVSV9BBP | Offer Sustainability | Circularity Profile | End of Life Information
9894 | XVSV9MBN | Main | range of product | Harmony XVS
9895 | XVSV9MBN | Main | product or component type | Editable electronic alarm
9896 | XVSV9MBN | Main | beacon or indicator bank unit type | Sound unit
9897 | XVSV9MBN | Main | device short name | XVSV
9898 | XVSV9MBN | Complementary | colour | Dark grey
9899 | XVSV9MBN | Complementary | input type | Bit: 6 channel input Binary: 63 channel input
9900 | XVSV9MBN | Complementary | assembly style | Ready assembled
9901 | XVSV9MBN | Complementary | material | PC (polycarbonate): body PC (polycarbonate): back cover TPE (thermoplastic elastomer): front panel NBR (nitrile butadiene rubber)
9902 | XVSV9MBN | Complementary | net weight | 0.287 kg
9903 | XVSV9MBN | Complementary | marking | CE
9904 | XVSV9MBN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
9905 | XVSV9MBN | Complementary | mounting support | 96 mm DIN rail
9906 | XVSV9MBN | Complementary | [Us] rated supply voltage | 100...230 V AC
9907 | XVSV9MBN | Complementary | [Ue] rated operational voltage | 90...264 V AC
9908 | XVSV9MBN | Complementary | inrush current | 30 A
9909 | XVSV9MBN | Complementary | associated fuse rating | 1 A
9910 | XVSV9MBN | Complementary | [Uimp] rated impulse withstand voltage | 1 kV
9911 | XVSV9MBN | Complementary | power consumption in W | 10 W
9912 | XVSV9MBN | Complementary | current consumption | 100 mA at 100 V AC
9913 | XVSV9MBN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
9914 | XVSV9MBN | Complementary | device application | Subway Packaging Printing
9915 | XVSV9MBN | Complementary | mounting diameter | 105 mm
9916 | XVSV9MBN | Complementary | width | 105 mm
9917 | XVSV9MBN | Complementary | height | 105 mm
9918 | XVSV9MBN | Complementary | depth | 50.1 mm
9919 | XVSV9MBN | Environment | discrete output type | NPN
9920 | XVSV9MBN | Environment | signalling type | Adjustable vocal sound
9921 | XVSV9MBN | Environment | protective treatment | TC
9922 | XVSV9MBN | Environment | ambient air temperature for storage | -20…60 °C
9923 | XVSV9MBN | Environment | ambient air temperature for operation | 0…50 °C
9924 | XVSV9MBN | Environment | relative humidity | 35…85 % without condensation
9925 | XVSV9MBN | Environment | vibration resistance | 7 gn
9926 | XVSV9MBN | Environment | IP degree of protection | Panel mounted: IP65 conforming to EN/IEC 60529 Wall mounted: IP20
9927 | XVSV9MBN | Environment | noise level | 0…97 dB (stop or suppress) at 1 m
9928 | XVSV9MBN | Packing Units | Package 1 Weight | 0.594 kg
9929 | XVSV9MBN | Offer Sustainability | Sustainable offer status | Green Premium product
9930 | XVSV9MBN | Offer Sustainability | REACh Regulation | REACh Declaration
9931 | XVSV9MBN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9932 | XVSV9MBN | Offer Sustainability | Mercury free | Yes
9933 | XVSV9MBN | Offer Sustainability | RoHS exemption information | Yes
9934 | XVSV9MBN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9935 | XVSV9MBN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9936 | XVSV9MBN | Offer Sustainability | Circularity Profile | End of Life Information
9937 | XVSV9MWN | Main | range of product | Harmony XVS
9938 | XVSV9MWN | Main | product or component type | Editable electronic alarm
9939 | XVSV9MWN | Main | beacon or indicator bank unit type | Sound unit
9940 | XVSV9MWN | Main | device short name | XVSV
9941 | XVSV9MWN | Complementary | colour | White
9942 | XVSV9MWN | Complementary | input type | Bit: 6 channel input Binary: 63 channel input
9943 | XVSV9MWN | Complementary | assembly style | Ready assembled
9944 | XVSV9MWN | Complementary | material | PC (polycarbonate): body PC (polycarbonate): back cover TPE (thermoplastic elastomer): front panel NBR (nitrile butadiene rubber)
9945 | XVSV9MWN | Complementary | net weight | 0.287 kg
9946 | XVSV9MWN | Complementary | marking | CE
9947 | XVSV9MWN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
9948 | XVSV9MWN | Complementary | mounting support | 96 mm DIN rail
9949 | XVSV9MWN | Complementary | [Us] rated supply voltage | 100...230 V AC
9950 | XVSV9MWN | Complementary | [Ue] rated operational voltage | 90...264 V AC
9951 | XVSV9MWN | Complementary | inrush current | 30 A
9952 | XVSV9MWN | Complementary | associated fuse rating | 1 A
9953 | XVSV9MWN | Complementary | [Uimp] rated impulse withstand voltage | 1 kV
9954 | XVSV9MWN | Complementary | power consumption in W | 10 W
9955 | XVSV9MWN | Complementary | current consumption | 100 mA at 100 V AC
9956 | XVSV9MWN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
9957 | XVSV9MWN | Complementary | device application | Packaging Subway Printing
9958 | XVSV9MWN | Complementary | mounting diameter | 105 mm
9959 | XVSV9MWN | Complementary | width | 105 mm
9960 | XVSV9MWN | Complementary | height | 105 mm
9961 | XVSV9MWN | Complementary | depth | 50.1 mm
9962 | XVSV9MWN | Environment | discrete output type | NPN
9963 | XVSV9MWN | Environment | signalling type | Adjustable vocal sound
9964 | XVSV9MWN | Environment | protective treatment | TC
9965 | XVSV9MWN | Environment | ambient air temperature for storage | -20…60 °C
9966 | XVSV9MWN | Environment | ambient air temperature for operation | 0…50 °C
9967 | XVSV9MWN | Environment | relative humidity | 35…85 % without condensation
9968 | XVSV9MWN | Environment | vibration resistance | 7 gn
9969 | XVSV9MWN | Environment | IP degree of protection | Panel mounted: IP65 conforming to EN/IEC 60529 Wall mounted: IP20
9970 | XVSV9MWN | Environment | noise level | 0…97 dB (stop or suppress) at 1 m
9971 | XVSV9MWN | Packing Units | Package 1 Weight | 0.287 kg
9972 | XVSV9MWN | Offer Sustainability | Sustainable offer status | Green Premium product
9973 | XVSV9MWN | Offer Sustainability | REACh Regulation | REACh Declaration
9974 | XVSV9MWN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
9975 | XVSV9MWN | Offer Sustainability | Mercury free | Yes
9976 | XVSV9MWN | Offer Sustainability | RoHS exemption information | Yes
9977 | XVSV9MWN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
9978 | XVSV9MWN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
9979 | XVSV9MWN | Offer Sustainability | Circularity Profile | End of Life Information
9980 | XVS10BMW | Main | range of product | Harmony XVS
9981 | XVS10BMW | Main | product or component type | Siren
9982 | XVS10BMW | Main | device short name | XVS
9983 | XVS10BMW | Main | colour | White
9984 | XVS10BMW | Main | signalling type | 2 tones siren
9985 | XVS10BMW | Main | [Us] rated supply voltage | 12 V AC/DC 24 V AC/DC
9986 | XVS10BMW | Main | noise level | 106 dB (continuous or intermittent tone) at 1 m
9987 | XVS10BMW | Complementary | material | PC: body
9988 | XVS10BMW | Complementary | net weight | 0.8 kg
9989 | XVS10BMW | Complementary | marking | CE
9990 | XVS10BMW | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
9991 | XVS10BMW | Complementary | current consumption | 300 mA at 24 V 500 mA
9992 | XVS10BMW | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
9993 | XVS10BMW | Complementary | electrical connection | Cable: 6.5…8.5 mm
9994 | XVS10BMW | Complementary | width | 114 mm
9995 | XVS10BMW | Complementary | height | 114 mm
9996 | XVS10BMW | Complementary | depth | 153.2 mm
9997 | XVS10BMW | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
9998 | XVS10BMW | Environment | protective treatment | TC
9999 | XVS10BMW | Environment | ambient air temperature for storage | -35…70 °C
10000 | XVS10BMW | Environment | ambient air temperature for operation | -30…50 °C
10001 | XVS10BMW | Environment | electrical shock protection class | Class II conforming to EN/IEC 61140
10002 | XVS10BMW | Environment | IP degree of protection | IP53
10003 | XVS10BMW | Packing Units | Package 1 Weight | 1.032 kg
10004 | XVS10BMW | Packing Units | Package 2 Weight | 9.698 kg
10005 | XVS10BMW | Packing Units | Package 3 Weight | 49.792 kg
10006 | XVS10BMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10007 | XVS10BMW | Offer Sustainability | Mercury free | Yes
10008 | XVS10BMW | Offer Sustainability | RoHS exemption information | Yes
10009 | XVS10BMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10010 | XVS10BMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10011 | XVS10BMW | Offer Sustainability | Circularity Profile | End of Life Information
10012 | XVS10BMW | Contractual warranty | Warranty | 18 months
10013 | XVS10GMW | Main | range of product | Harmony XVS
10014 | XVS10GMW | Main | product or component type | Siren
10015 | XVS10GMW | Main | device short name | XVS
10016 | XVS10GMW | Main | colour | White
10017 | XVS10GMW | Main | signalling type | 2 tones siren
10018 | XVS10GMW | Main | [Us] rated supply voltage | 120 V AC
10019 | XVS10GMW | Main | noise level | 106 dB (continuous or intermittent tone) at 1 m
10020 | XVS10GMW | Complementary | material | PC: body
10021 | XVS10GMW | Complementary | net weight | 1 kg
10022 | XVS10GMW | Complementary | marking | CE
10023 | XVS10GMW | Complementary | [Uimp] rated impulse withstand voltage | 4 kV
10024 | XVS10GMW | Complementary | current consumption | 80 mA at 120 V
10025 | XVS10GMW | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
10026 | XVS10GMW | Complementary | electrical connection | Cable: 6.5…8.5 mm
10027 | XVS10GMW | Complementary | width | 114 mm
10028 | XVS10GMW | Complementary | height | 114 mm
10029 | XVS10GMW | Complementary | depth | 153.2 mm
10030 | XVS10GMW | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
10031 | XVS10GMW | Environment | protective treatment | TC
10032 | XVS10GMW | Environment | ambient air temperature for storage | -35…70 °C
10033 | XVS10GMW | Environment | ambient air temperature for operation | -30…50 °C
10034 | XVS10GMW | Environment | electrical shock protection class | Class II conforming to EN/IEC 61140
10035 | XVS10GMW | Environment | IP degree of protection | IP53
10036 | XVS10GMW | Packing Units | Package 1 Weight | 1.226 kg
10037 | XVS10GMW | Packing Units | Package 2 Weight | 11.24 kg
10038 | XVS10GMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10039 | XVS10GMW | Offer Sustainability | Mercury free | Yes
10040 | XVS10GMW | Offer Sustainability | RoHS exemption information | Yes
10041 | XVS10GMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10042 | XVS10GMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10043 | XVS10GMW | Offer Sustainability | Circularity Profile | End of Life Information
10044 | XVS10GMW | Contractual warranty | Warranty | 18 months
10045 | XVS10MMW | Main | range of product | Harmony XVS
10046 | XVS10MMW | Main | product or component type | Siren
10047 | XVS10MMW | Main | device short name | XVS
10048 | XVS10MMW | Main | colour | White
10049 | XVS10MMW | Main | signalling type | 2 tones siren
10050 | XVS10MMW | Main | [Us] rated supply voltage | 230 V AC
10051 | XVS10MMW | Main | noise level | 106 dB (continuous or intermittent tone) at 1 m
10052 | XVS10MMW | Complementary | material | PC: body
10053 | XVS10MMW | Complementary | net weight | 1 kg
10054 | XVS10MMW | Complementary | marking | CE
10055 | XVS10MMW | Complementary | [Uimp] rated impulse withstand voltage | 4 kV
10056 | XVS10MMW | Complementary | current consumption | 40 mA at 230 V
10057 | XVS10MMW | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
10058 | XVS10MMW | Complementary | electrical connection | Cable: 6.5…8.5 mm
10059 | XVS10MMW | Complementary | width | 114 mm
10060 | XVS10MMW | Complementary | height | 114 mm
10061 | XVS10MMW | Complementary | depth | 153.2 mm
10062 | XVS10MMW | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
10063 | XVS10MMW | Environment | protective treatment | TC
10064 | XVS10MMW | Environment | ambient air temperature for storage | -35…70 °C
10065 | XVS10MMW | Environment | ambient air temperature for operation | -30…50 °C
10066 | XVS10MMW | Environment | electrical shock protection class | Class II conforming to EN/IEC 61140
10067 | XVS10MMW | Environment | IP degree of protection | IP53
10068 | XVS10MMW | Packing Units | Package 1 Weight | 1.226 kg
10069 | XVS10MMW | Packing Units | Package 2 Weight | 11.24 kg
10070 | XVS10MMW | Packing Units | Package 3 Weight | 53.96 kg
10071 | XVS10MMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10072 | XVS10MMW | Offer Sustainability | Mercury free | Yes
10073 | XVS10MMW | Offer Sustainability | RoHS exemption information | Yes
10074 | XVS10MMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10075 | XVS10MMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10076 | XVS10MMW | Offer Sustainability | Circularity Profile | End of Life Information
10077 | XVS10MMW | Contractual warranty | Warranty | 18 months
10078 | XVS14BMW | Main | range of product | Harmony XVS
10079 | XVS14BMW | Main | product or component type | Multisound siren
10080 | XVS14BMW | Main | device short name | XVS
10081 | XVS14BMW | Complementary | colour | White
10082 | XVS14BMW | Complementary | material | ASA (Acrylonitrile Styrene Acrylate): front ASA (Acrylonitrile Styrene Acrylate): back PC (polycarbonate): back cover
10083 | XVS14BMW | Complementary | net weight | 1 kg
10084 | XVS14BMW | Complementary | marking | CE
10085 | XVS14BMW | Complementary | mounting support | Bracket
10086 | XVS14BMW | Complementary | fixing mode | 3 holes Ø 9 mm
10087 | XVS14BMW | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
10088 | XVS14BMW | Complementary | current consumption | 350 mA at 24 V 250 mA at 12 V
10089 | XVS14BMW | Complementary | electrical connection | Cable: 6.5…8.5 mm, 0.33 mm² / AWG 22 (signalling circuit) Cable: 6.5…8.5 mm, 0.52 mm² / AWG 20 (power circuit)
10090 | XVS14BMW | Complementary | width | 140 mm
10091 | XVS14BMW | Complementary | height | 114 mm
10092 | XVS14BMW | Complementary | depth | 223 mm
10093 | XVS14BMW | Environment | signalling type | 43 tones siren
10094 | XVS14BMW | Environment | standards | EN 61000-6-2 EN 55014-2 EN 55022 EN 61000-6-3
10095 | XVS14BMW | Environment | product certifications | UL
10096 | XVS14BMW | Environment | protective treatment | TC
10097 | XVS14BMW | Environment | ambient air temperature for storage | -35…70 °C
10098 | XVS14BMW | Environment | ambient air temperature for operation | -10…50 °C
10099 | XVS14BMW | Environment | overvoltage category | Class II conforming to EN/IEC 61140
10100 | XVS14BMW | Environment | IP degree of protection | IP53 conforming to EN/IEC 60529
10101 | XVS14BMW | Environment | [Us] rated supply voltage | 12 V DC 24 V DC
10102 | XVS14BMW | Environment | noise level | 0…105 dB (continuous or intermittent tone) at 1 m
10103 | XVS14BMW | Packing Units | Package 1 Weight | 1.307 kg
10104 | XVS14BMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10105 | XVS14BMW | Offer Sustainability | Mercury free | Yes
10106 | XVS14BMW | Offer Sustainability | RoHS exemption information | Yes
10107 | XVS14BMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10108 | XVS14BMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10109 | XVS14BMW | Offer Sustainability | Circularity Profile | End of Life Information
10110 | XVS14BMW | Contractual warranty | Warranty | 18 months
10111 | XVS14GMW | Main | range of product | Harmony XVS
10112 | XVS14GMW | Main | product or component type | Multisound siren
10113 | XVS14GMW | Main | device short name | XVS
10114 | XVS14GMW | Complementary | colour | White
10115 | XVS14GMW | Complementary | material | PC (polycarbonate): back cover PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): front PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): back
10116 | XVS14GMW | Complementary | net weight | 1.2 kg
10117 | XVS14GMW | Complementary | marking | CE
10118 | XVS14GMW | Complementary | mounting support | Bracket
10119 | XVS14GMW | Complementary | fixing mode | 3 holes Ø 9 mm
10120 | XVS14GMW | Complementary | [Uimp] rated impulse withstand voltage | 4 kV
10121 | XVS14GMW | Complementary | current consumption | 100 mA at 120 V
10122 | XVS14GMW | Complementary | electrical connection | Cable: 6.5…8.5 mm, 0.33 mm² / AWG 22 (signalling circuit) Cable: 6.5…8.5 mm, 0.52 mm² / AWG 20 (power circuit)
10123 | XVS14GMW | Complementary | width | 140 mm
10124 | XVS14GMW | Complementary | height | 114 mm
10125 | XVS14GMW | Complementary | depth | 223 mm
10126 | XVS14GMW | Environment | signalling type | 43 tones siren
10127 | XVS14GMW | Environment | standards | EN 61000-6-2 EN 61000-6-3 EN 60947 EN 60947-5
10128 | XVS14GMW | Environment | product certifications | UL
10129 | XVS14GMW | Environment | protective treatment | TC
10130 | XVS14GMW | Environment | ambient air temperature for storage | -35…70 °C
10131 | XVS14GMW | Environment | ambient air temperature for operation | -10…50 °C
10132 | XVS14GMW | Environment | overvoltage category | Class II conforming to EN/IEC 61140
10133 | XVS14GMW | Environment | IP degree of protection | IP53 conforming to EN/IEC 60529
10134 | XVS14GMW | Environment | [Us] rated supply voltage | 120 V AC
10135 | XVS14GMW | Environment | noise level | 0…105 dB (continuous or intermittent tone) at 1 m
10136 | XVS14GMW | Packing Units | Package 1 Weight | 1.586 kg
10137 | XVS14GMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10138 | XVS14GMW | Offer Sustainability | Mercury free | Yes
10139 | XVS14GMW | Offer Sustainability | RoHS exemption information | Yes
10140 | XVS14GMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10141 | XVS14GMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10142 | XVS14GMW | Offer Sustainability | Circularity Profile | End of Life Information
10143 | XVS14GMW | Contractual warranty | Warranty | 18 months
10144 | XVS14MMW | Main | range of product | Harmony XVS
10145 | XVS14MMW | Main | product or component type | Multisound siren
10146 | XVS14MMW | Main | device short name | XVS
10147 | XVS14MMW | Complementary | colour | White
10148 | XVS14MMW | Complementary | material | PC (polycarbonate): back cover PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): front PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): back
10149 | XVS14MMW | Complementary | net weight | 1.2 kg
10150 | XVS14MMW | Complementary | marking | CE
10151 | XVS14MMW | Complementary | mounting support | Bracket
10152 | XVS14MMW | Complementary | fixing mode | 3 holes Ø 9 mm
10153 | XVS14MMW | Complementary | [Uimp] rated impulse withstand voltage | 4 kV
10154 | XVS14MMW | Complementary | current consumption | 50 mA at 240 V
10155 | XVS14MMW | Complementary | electrical connection | Cable: 6.5…8.5 mm, 0.33 mm² / AWG 22 (signalling circuit) Cable: 6.5…8.5 mm, 0.52 mm² / AWG 20 (power circuit)
10156 | XVS14MMW | Complementary | width | 140 mm
10157 | XVS14MMW | Complementary | height | 114 mm
10158 | XVS14MMW | Complementary | depth | 223 mm
10159 | XVS14MMW | Environment | signalling type | 43 tones siren
10160 | XVS14MMW | Environment | standards | EN 61000-6-3 EN 60947-5-1 EN 60947-01 EN 61000-6-2
10161 | XVS14MMW | Environment | product certifications | UL
10162 | XVS14MMW | Environment | protective treatment | TC
10163 | XVS14MMW | Environment | ambient air temperature for storage | -35…70 °C
10164 | XVS14MMW | Environment | ambient air temperature for operation | -10…50 °C
10165 | XVS14MMW | Environment | overvoltage category | Class II conforming to EN/IEC 61140
10166 | XVS14MMW | Environment | IP degree of protection | IP53 conforming to EN/IEC 60529
10167 | XVS14MMW | Environment | [Us] rated supply voltage | 240 V AC
10168 | XVS14MMW | Environment | noise level | 0…105 dB (continuous or intermittent tone) at 1 m
10169 | XVS14MMW | Packing Units | Package 1 Weight | 1.55 kg
10170 | XVS14MMW | Packing Units | Package 2 Weight | 10.676 kg
10171 | XVS14MMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10172 | XVS14MMW | Offer Sustainability | Mercury free | Yes
10173 | XVS14MMW | Offer Sustainability | RoHS exemption information | Yes
10174 | XVS14MMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10175 | XVS14MMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10176 | XVS14MMW | Offer Sustainability | Circularity Profile | End of Life Information
10177 | XVS14MMW | Contractual warranty | Warranty | 18 months
10178 | XVS72BMBP | Main | range of product | Harmony XVS
10179 | XVS72BMBP | Main | product or component type | Electronic alarm
10180 | XVS72BMBP | Main | device short name | XVS
10181 | XVS72BMBP | Complementary | colour | Black
10182 | XVS72BMBP | Complementary | material | ABS (acrylonitrile butadiene-styrene): body PC (polycarbonate): terminal cover
10183 | XVS72BMBP | Complementary | net weight | 0.18 kg
10184 | XVS72BMBP | Complementary | marking | CE
10185 | XVS72BMBP | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
10186 | XVS72BMBP | Complementary | mounting support | 72 mm DIN rail
10187 | XVS72BMBP | Complementary | [Us] rated supply voltage | 12...24 V DC
10188 | XVS72BMBP | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
10189 | XVS72BMBP | Complementary | current consumption | 117 mA at 12 V 125 mA at 24 V 158 mA at 12 V 200 mA at 24 V
10190 | XVS72BMBP | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
10191 | XVS72BMBP | Complementary | width | 72 mm
10192 | XVS72BMBP | Complementary | height | 72 mm
10193 | XVS72BMBP | Complementary | depth | 69.3 mm
10194 | XVS72BMBP | Environment | discrete output type | PNP
10195 | XVS72BMBP | Environment | signalling type | 16 tones alarm
10196 | XVS72BMBP | Environment | standards | UL 464 EN/IEC 61000-6-3 EN/IEC 61000-6-2
10197 | XVS72BMBP | Environment | product certifications | UR
10198 | XVS72BMBP | Environment | protective treatment | TC
10199 | XVS72BMBP | Environment | ambient air temperature for storage | -35…70 °C
10200 | XVS72BMBP | Environment | ambient air temperature for operation | -10…50 °C
10201 | XVS72BMBP | Environment | IP degree of protection | Panel mounted: IP54 conforming to EN/IEC 60529
10202 | XVS72BMBP | Environment | noise level | 0…90 dB (continuous or intermittent tone) at 1 m
10203 | XVS72BMBP | Packing Units | Package 1 Weight | 0.266 kg
10204 | XVS72BMBP | Offer Sustainability | Sustainable offer status | Green Premium product
10205 | XVS72BMBP | Offer Sustainability | REACh Regulation | REACh Declaration
10206 | XVS72BMBP | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10207 | XVS72BMBP | Offer Sustainability | Mercury free | Yes
10208 | XVS72BMBP | Offer Sustainability | RoHS exemption information | Yes
10209 | XVS72BMBP | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10210 | XVS72BMBP | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10211 | XVS72BMBP | Offer Sustainability | Circularity Profile | End of Life Information
10212 | XVS72BMBP | Contractual warranty | Warranty | 18 months
10213 | XVS72BMWP | Main | range of product | Harmony XVS
10214 | XVS72BMWP | Main | product or component type | Electronic alarm
10215 | XVS72BMWP | Main | device short name | XVS
10216 | XVS72BMWP | Complementary | colour | White
10217 | XVS72BMWP | Complementary | material | ABS (acrylonitrile butadiene-styrene): body PC (polycarbonate): terminal cover
10218 | XVS72BMWP | Complementary | net weight | 0.18 kg
10219 | XVS72BMWP | Complementary | marking | CE
10220 | XVS72BMWP | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
10221 | XVS72BMWP | Complementary | mounting support | 72 mm DIN rail
10222 | XVS72BMWP | Complementary | [Us] rated supply voltage | 12...24 V DC
10223 | XVS72BMWP | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
10224 | XVS72BMWP | Complementary | current consumption | 117 mA at 12 V 125 mA at 24 V 158 mA at 12 V 200 mA at 24 V
10225 | XVS72BMWP | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
10226 | XVS72BMWP | Complementary | width | 72 mm
10227 | XVS72BMWP | Complementary | height | 72 mm
10228 | XVS72BMWP | Complementary | depth | 69.3 mm
10229 | XVS72BMWP | Environment | discrete output type | PNP
10230 | XVS72BMWP | Environment | signalling type | 16 tones alarm
10231 | XVS72BMWP | Environment | standards | EN/IEC 61000-6-3 EN/IEC 61000-6-2 UL 464
10232 | XVS72BMWP | Environment | product certifications | UR
10233 | XVS72BMWP | Environment | protective treatment | TC
10234 | XVS72BMWP | Environment | ambient air temperature for storage | -35…70 °C
10235 | XVS72BMWP | Environment | ambient air temperature for operation | -10…50 °C
10236 | XVS72BMWP | Environment | IP degree of protection | Panel mounted: IP54 conforming to EN/IEC 60529
10237 | XVS72BMWP | Environment | noise level | 0…90 dB (continuous or intermittent tone) at 1 m
10238 | XVS72BMWP | Packing Units | Package 1 Weight | 0.265 kg
10239 | XVS72BMWP | Offer Sustainability | Sustainable offer status | Green Premium product
10240 | XVS72BMWP | Offer Sustainability | REACh Regulation | REACh Declaration
10241 | XVS72BMWP | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10242 | XVS72BMWP | Offer Sustainability | Mercury free | Yes
10243 | XVS72BMWP | Offer Sustainability | RoHS exemption information | Yes
10244 | XVS72BMWP | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10245 | XVS72BMWP | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10246 | XVS72BMWP | Offer Sustainability | Circularity Profile | End of Life Information
10247 | XVS72BMWP | Contractual warranty | Warranty | 18 months
10248 | XVS72BMBN | Main | range of product | Harmony XVS
10249 | XVS72BMBN | Main | product or component type | Electronic alarm
10250 | XVS72BMBN | Main | device short name | XVS
10251 | XVS72BMBN | Complementary | colour | Black
10252 | XVS72BMBN | Complementary | material | ABS (acrylonitrile butadiene-styrene): body PC (polycarbonate): terminal cover
10253 | XVS72BMBN | Complementary | net weight | 0.18 kg
10254 | XVS72BMBN | Complementary | marking | CE
10255 | XVS72BMBN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
10256 | XVS72BMBN | Complementary | mounting support | 72 mm DIN rail
10257 | XVS72BMBN | Complementary | [Us] rated supply voltage | 12...24 V DC
10258 | XVS72BMBN | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
10259 | XVS72BMBN | Complementary | current consumption | 117 mA at 12 V 125 mA at 24 V 158 mA at 12 V 200 mA at 24 V
10260 | XVS72BMBN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
10261 | XVS72BMBN | Complementary | width | 72 mm
10262 | XVS72BMBN | Complementary | height | 72 mm
10263 | XVS72BMBN | Complementary | depth | 69.3 mm
10264 | XVS72BMBN | Environment | discrete output type | NPN
10265 | XVS72BMBN | Environment | signalling type | 16 tones alarm
10266 | XVS72BMBN | Environment | standards | UL 464 EN/IEC 61000-6-3 EN/IEC 61000-6-2
10267 | XVS72BMBN | Environment | product certifications | UR
10268 | XVS72BMBN | Environment | protective treatment | TC
10269 | XVS72BMBN | Environment | ambient air temperature for storage | -35…70 °C
10270 | XVS72BMBN | Environment | ambient air temperature for operation | -10…50 °C
10271 | XVS72BMBN | Environment | IP degree of protection | Panel mounted: IP54 conforming to EN/IEC 60529
10272 | XVS72BMBN | Environment | noise level | 0…90 dB (continuous or intermittent tone) at 1 m
10273 | XVS72BMBN | Packing Units | Package 1 Weight | 0.266 kg
10274 | XVS72BMBN | Offer Sustainability | Sustainable offer status | Green Premium product
10275 | XVS72BMBN | Offer Sustainability | REACh Regulation | REACh Declaration
10276 | XVS72BMBN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10277 | XVS72BMBN | Offer Sustainability | Mercury free | Yes
10278 | XVS72BMBN | Offer Sustainability | RoHS exemption information | Yes
10279 | XVS72BMBN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10280 | XVS72BMBN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10281 | XVS72BMBN | Offer Sustainability | Circularity Profile | End of Life Information
10282 | XVS72BMBN | Contractual warranty | Warranty | 18 months
10283 | XVS72BMWN | Main | range of product | Harmony XVS
10284 | XVS72BMWN | Main | product or component type | Electronic alarm
10285 | XVS72BMWN | Main | device short name | XVS
10286 | XVS72BMWN | Complementary | colour | White
10287 | XVS72BMWN | Complementary | material | ABS (acrylonitrile butadiene-styrene): body PC (polycarbonate): terminal cover
10288 | XVS72BMWN | Complementary | net weight | 0.18 kg
10289 | XVS72BMWN | Complementary | marking | CE
10290 | XVS72BMWN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
10291 | XVS72BMWN | Complementary | mounting support | 72 mm DIN rail
10292 | XVS72BMWN | Complementary | [Us] rated supply voltage | 12...24 V DC
10293 | XVS72BMWN | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
10294 | XVS72BMWN | Complementary | current consumption | 117 mA at 12 V 125 mA at 24 V 158 mA at 12 V 200 mA at 24 V
10295 | XVS72BMWN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
10296 | XVS72BMWN | Complementary | width | 72 mm
10297 | XVS72BMWN | Complementary | height | 72 mm
10298 | XVS72BMWN | Complementary | depth | 69.3 mm
10299 | XVS72BMWN | Environment | discrete output type | NPN
10300 | XVS72BMWN | Environment | signalling type | 16 tones alarm
10301 | XVS72BMWN | Environment | standards | EN/IEC 61000-6-2 UL 464 EN/IEC 61000-6-3
10302 | XVS72BMWN | Environment | product certifications | UR
10303 | XVS72BMWN | Environment | protective treatment | TC
10304 | XVS72BMWN | Environment | ambient air temperature for storage | -35…70 °C
10305 | XVS72BMWN | Environment | ambient air temperature for operation | -10…50 °C
10306 | XVS72BMWN | Environment | IP degree of protection | Panel mounted: IP54 conforming to EN/IEC 60529
10307 | XVS72BMWN | Environment | noise level | 0…90 dB (continuous or intermittent tone) at 1 m
10308 | XVS72BMWN | Packing Units | Package 1 Weight | 0.264 kg
10309 | XVS72BMWN | Offer Sustainability | Sustainable offer status | Green Premium product
10310 | XVS72BMWN | Offer Sustainability | REACh Regulation | REACh Declaration
10311 | XVS72BMWN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10312 | XVS72BMWN | Offer Sustainability | Mercury free | Yes
10313 | XVS72BMWN | Offer Sustainability | RoHS exemption information | Yes
10314 | XVS72BMWN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10315 | XVS72BMWN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10316 | XVS72BMWN | Offer Sustainability | Circularity Profile | End of Life Information
10317 | XVS72BMWN | Contractual warranty | Warranty | 18 months
10318 | XVS96BMBP | Main | range of product | Harmony XVS
10319 | XVS96BMBP | Main | product or component type | Electronic alarm
10320 | XVS96BMBP | Main | device short name | XVS
10321 | XVS96BMBP | Complementary | colour | Black
10322 | XVS96BMBP | Complementary | material | PC (polycarbonate): terminal cover PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): body
10323 | XVS96BMBP | Complementary | net weight | 0.4 kg
10324 | XVS96BMBP | Complementary | marking | CE
10325 | XVS96BMBP | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
10326 | XVS96BMBP | Complementary | mounting support | 96 mm DIN rail
10327 | XVS96BMBP | Complementary | [Us] rated supply voltage | 12...24 V DC
10328 | XVS96BMBP | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
10329 | XVS96BMBP | Complementary | current consumption | 250 mA at 12 V 292 mA at 12 V 292 mA at 24 V 354 mA at 24 V
10330 | XVS96BMBP | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
10331 | XVS96BMBP | Complementary | width | 96 mm
10332 | XVS96BMBP | Complementary | height | 96 mm
10333 | XVS96BMBP | Complementary | depth | 58.1 mm
10334 | XVS96BMBP | Environment | discrete output type | PNP
10335 | XVS96BMBP | Environment | signalling type | 16 tones alarm
10336 | XVS96BMBP | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
10337 | XVS96BMBP | Environment | protective treatment | TC
10338 | XVS96BMBP | Environment | ambient air temperature for storage | -35…70 °C
10339 | XVS96BMBP | Environment | ambient air temperature for operation | -20…50 °C
10340 | XVS96BMBP | Environment | IP degree of protection | Panel mounted: IP54 conforming to EN/IEC 60529
10341 | XVS96BMBP | Environment | noise level | 0…96 dB (continuous or intermittent tone) at 1 m
10342 | XVS96BMBP | Packing Units | Package 1 Weight | 0.536 kg
10343 | XVS96BMBP | Offer Sustainability | Sustainable offer status | Green Premium product
10344 | XVS96BMBP | Offer Sustainability | REACh Regulation | REACh Declaration
10345 | XVS96BMBP | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10346 | XVS96BMBP | Offer Sustainability | Mercury free | Yes
10347 | XVS96BMBP | Offer Sustainability | RoHS exemption information | Yes
10348 | XVS96BMBP | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10349 | XVS96BMBP | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10350 | XVS96BMBP | Offer Sustainability | Circularity Profile | End of Life Information
10351 | XVS96BMBP | Contractual warranty | Warranty | 18 months
10352 | XVS96BMWP | Main | range of product | Harmony XVS
10353 | XVS96BMWP | Main | product or component type | Electronic alarm
10354 | XVS96BMWP | Main | device short name | XVS
10355 | XVS96BMWP | Complementary | colour | White
10356 | XVS96BMWP | Complementary | material | PC (polycarbonate): terminal cover PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): body
10357 | XVS96BMWP | Complementary | net weight | 0.4 kg
10358 | XVS96BMWP | Complementary | marking | CE
10359 | XVS96BMWP | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
10360 | XVS96BMWP | Complementary | mounting support | 96 mm DIN rail
10361 | XVS96BMWP | Complementary | [Us] rated supply voltage | 12...24 V DC
10362 | XVS96BMWP | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
10363 | XVS96BMWP | Complementary | current consumption | 250 mA at 12 V 292 mA at 12 V 292 mA at 24 V 354 mA at 24 V
10364 | XVS96BMWP | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
10365 | XVS96BMWP | Complementary | width | 96 mm
10366 | XVS96BMWP | Complementary | height | 96 mm
10367 | XVS96BMWP | Complementary | depth | 58.1 mm
10368 | XVS96BMWP | Environment | discrete output type | PNP
10369 | XVS96BMWP | Environment | signalling type | 16 tones alarm
10370 | XVS96BMWP | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
10371 | XVS96BMWP | Environment | protective treatment | TC
10372 | XVS96BMWP | Environment | ambient air temperature for storage | -35…70 °C
10373 | XVS96BMWP | Environment | ambient air temperature for operation | -20…50 °C
10374 | XVS96BMWP | Environment | IP degree of protection | Panel mounted: IP54 conforming to EN/IEC 60529
10375 | XVS96BMWP | Environment | noise level | 0…96 dB (continuous or intermittent tone) at 1 m
10376 | XVS96BMWP | Packing Units | Package 1 Weight | 533 g
10377 | XVS96BMWP | Packing Units | Package 2 Weight | 9.634 kg
10378 | XVS96BMWP | Offer Sustainability | Sustainable offer status | Green Premium product
10379 | XVS96BMWP | Offer Sustainability | REACh Regulation | REACh Declaration
10380 | XVS96BMWP | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10381 | XVS96BMWP | Offer Sustainability | Mercury free | Yes
10382 | XVS96BMWP | Offer Sustainability | RoHS exemption information | Yes
10383 | XVS96BMWP | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10384 | XVS96BMWP | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10385 | XVS96BMWP | Offer Sustainability | Circularity Profile | End of Life Information
10386 | XVS96BMWP | Contractual warranty | Warranty | 18 months
10387 | XVS96BMBN | Main | range of product | Harmony XVS
10388 | XVS96BMBN | Main | product or component type | Electronic alarm
10389 | XVS96BMBN | Main | device short name | XVS
10390 | XVS96BMBN | Complementary | colour | Black
10391 | XVS96BMBN | Complementary | material | PC (polycarbonate): terminal cover PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): body
10392 | XVS96BMBN | Complementary | net weight | 0.4 kg
10393 | XVS96BMBN | Complementary | marking | CE
10394 | XVS96BMBN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
10395 | XVS96BMBN | Complementary | mounting support | 96 mm DIN rail
10396 | XVS96BMBN | Complementary | [Us] rated supply voltage | 12...24 V DC
10397 | XVS96BMBN | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
10398 | XVS96BMBN | Complementary | current consumption | 250 mA at 12 V 292 mA at 12 V 292 mA at 24 V 354 mA at 24 V
10399 | XVS96BMBN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
10400 | XVS96BMBN | Complementary | width | 96 mm
10401 | XVS96BMBN | Complementary | height | 96 mm
10402 | XVS96BMBN | Complementary | depth | 58.1 mm
10403 | XVS96BMBN | Environment | discrete output type | NPN
10404 | XVS96BMBN | Environment | signalling type | 16 tones alarm
10405 | XVS96BMBN | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
10406 | XVS96BMBN | Environment | protective treatment | TC
10407 | XVS96BMBN | Environment | ambient air temperature for storage | -35…70 °C
10408 | XVS96BMBN | Environment | ambient air temperature for operation | -20…50 °C
10409 | XVS96BMBN | Environment | IP degree of protection | Panel mounted: IP54 conforming to EN/IEC 60529
10410 | XVS96BMBN | Environment | noise level | 0…96 dB (continuous or intermittent tone) at 1 m
10411 | XVS96BMBN | Packing Units | Package 1 Weight | 0.529 kg
10412 | XVS96BMBN | Offer Sustainability | Sustainable offer status | Green Premium product
10413 | XVS96BMBN | Offer Sustainability | REACh Regulation | REACh Declaration
10414 | XVS96BMBN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10415 | XVS96BMBN | Offer Sustainability | Mercury free | Yes
10416 | XVS96BMBN | Offer Sustainability | RoHS exemption information | Yes
10417 | XVS96BMBN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10418 | XVS96BMBN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10419 | XVS96BMBN | Offer Sustainability | Circularity Profile | End of Life Information
10420 | XVS96BMBN | Contractual warranty | Warranty | 18 months
10421 | XVS96BMWN | Main | range of product | Harmony XVS
10422 | XVS96BMWN | Main | product or component type | Electronic alarm
10423 | XVS96BMWN | Main | device short name | XVS
10424 | XVS96BMWN | Complementary | colour | White
10425 | XVS96BMWN | Complementary | material | PC (polycarbonate): terminal cover PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): body
10426 | XVS96BMWN | Complementary | net weight | 0.4 kg
10427 | XVS96BMWN | Complementary | marking | CE
10428 | XVS96BMWN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
10429 | XVS96BMWN | Complementary | mounting support | 96 mm DIN rail
10430 | XVS96BMWN | Complementary | [Us] rated supply voltage | 12...24 V DC
10431 | XVS96BMWN | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
10432 | XVS96BMWN | Complementary | current consumption | 250 mA at 12 V 292 mA at 12 V 292 mA at 24 V 354 mA at 24 V
10433 | XVS96BMWN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
10434 | XVS96BMWN | Complementary | width | 96 mm
10435 | XVS96BMWN | Complementary | height | 96 mm
10436 | XVS96BMWN | Complementary | depth | 58.1 mm
10437 | XVS96BMWN | Environment | discrete output type | NPN
10438 | XVS96BMWN | Environment | signalling type | 16 tones alarm
10439 | XVS96BMWN | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
10440 | XVS96BMWN | Environment | protective treatment | TC
10441 | XVS96BMWN | Environment | ambient air temperature for storage | -35…70 °C
10442 | XVS96BMWN | Environment | ambient air temperature for operation | -20…50 °C
10443 | XVS96BMWN | Environment | IP degree of protection | Panel mounted: IP54 conforming to EN/IEC 60529
10444 | XVS96BMWN | Environment | noise level | 0…96 dB (continuous or intermittent tone) at 1 m
10445 | XVS96BMWN | Packing Units | Package 1 Weight | 534 g
10446 | XVS96BMWN | Offer Sustainability | Sustainable offer status | Green Premium product
10447 | XVS96BMWN | Offer Sustainability | REACh Regulation | REACh Declaration
10448 | XVS96BMWN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10449 | XVS96BMWN | Offer Sustainability | Mercury free | Yes
10450 | XVS96BMWN | Offer Sustainability | RoHS exemption information | Yes
10451 | XVS96BMWN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10452 | XVS96BMWN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10453 | XVS96BMWN | Offer Sustainability | Circularity Profile | End of Life Information
10454 | XVS96BMWN | Contractual warranty | Warranty | 18 months
10455 | DL1EDBS | Main | range compatibility | Harmony XVM Optimum
10456 | DL1EDBS | Main | accessory / separate part category | Lighting accessory
10457 | DL1EDBS | Main | accessory / separate part type | Incandescent bulb
10458 | DL1EDBS | Main | accessory / separate part designation | Incandescent bulb
10459 | DL1EDBS | Main | accessory / separate part destination | Beacon and indicator bank
10460 | DL1EDBS | Main | bulb base | BA 15d
10461 | DL1EDBS | Main | signalling type | Steady
10462 | DL1EDBS | Main | [Us] rated supply voltage | 24 V AC/DC
10463 | DL1EDBS | Main | luminance | 650 cd/m²
10464 | DL1EDBS | Main | sale per indivisible quantity | 10
10465 | DL1EDBS | Complementary | maximum power dissipation in W | 5 W
10466 | DL1EDBS | Complementary | net weight | 0.007 kg
10467 | DL1EDBS | Offer Sustainability | Sustainable offer status | Green Premium product
10468 | DL1EDBS | Offer Sustainability | REACh Regulation | REACh Declaration
10469 | DL1EDBS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10470 | DL1EDBS | Offer Sustainability | Mercury free | Yes
10471 | DL1EDBS | Offer Sustainability | RoHS exemption information | Yes
10472 | DL1EDBS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10473 | DL1EDBS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10474 | DL1EDBS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10475 | DL1EDBS | Contractual warranty | Warranty | 18 months
10476 | DL1EDGS | Main | range compatibility | Harmony XVM Optimum
10477 | DL1EDGS | Main | accessory / separate part category | Lighting accessory
10478 | DL1EDGS | Main | accessory / separate part type | Incandescent bulb
10479 | DL1EDGS | Main | accessory / separate part designation | Incandescent bulb
10480 | DL1EDGS | Main | accessory / separate part destination | Beacon and indicator bank
10481 | DL1EDGS | Main | bulb base | BA 15d
10482 | DL1EDGS | Main | signalling type | Steady
10483 | DL1EDGS | Main | [Us] rated supply voltage | 120 V AC/DC
10484 | DL1EDGS | Main | luminance | 650 cd/m²
10485 | DL1EDGS | Main | sale per indivisible quantity | 10
10486 | DL1EDGS | Complementary | maximum power dissipation in W | 5 W
10487 | DL1EDGS | Complementary | net weight | 0.007 kg
10488 | DL1EDGS | Offer Sustainability | Sustainable offer status | Green Premium product
10489 | DL1EDGS | Offer Sustainability | REACh Regulation | REACh Declaration
10490 | DL1EDGS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10491 | DL1EDGS | Offer Sustainability | Mercury free | Yes
10492 | DL1EDGS | Offer Sustainability | RoHS exemption information | Yes
10493 | DL1EDGS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10494 | DL1EDGS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10495 | DL1EDGS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10496 | DL1EDGS | Contractual warranty | Warranty | 18 months
10497 | DL1EDMS | Main | range compatibility | Harmony XVM Optimum
10498 | DL1EDMS | Main | accessory / separate part category | Lighting accessory
10499 | DL1EDMS | Main | accessory / separate part type | Incandescent bulb
10500 | DL1EDMS | Main | accessory / separate part designation | Incandescent bulb
10501 | DL1EDMS | Main | accessory / separate part destination | Beacon and indicator bank
10502 | DL1EDMS | Main | bulb base | BA 15d
10503 | DL1EDMS | Main | signalling type | Steady
10504 | DL1EDMS | Main | [Us] rated supply voltage | 230 V AC/DC
10505 | DL1EDMS | Main | luminance | 650 cd/m²
10506 | DL1EDMS | Main | sale per indivisible quantity | 10
10507 | DL1EDMS | Complementary | maximum power dissipation in W | 5 W
10508 | DL1EDMS | Complementary | net weight | 0.007 kg
10509 | DL1EDMS | Offer Sustainability | Sustainable offer status | Green Premium product
10510 | DL1EDMS | Offer Sustainability | REACh Regulation | REACh Declaration
10511 | DL1EDMS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10512 | DL1EDMS | Offer Sustainability | Mercury free | Yes
10513 | DL1EDMS | Offer Sustainability | RoHS exemption information | Yes
10514 | DL1EDMS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10515 | DL1EDMS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10516 | DL1EDMS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10517 | DL1EDMS | Contractual warranty | Warranty | 18 months
10518 | DL2EDB1SB | Main | range compatibility | Harmony XVM Optimum
10519 | DL2EDB1SB | Main | accessory / separate part category | Lighting accessory
10520 | DL2EDB1SB | Main | accessory / separate part type | Super bright LED
10521 | DL2EDB1SB | Main | accessory / separate part destination | Beacon and indicator bank
10522 | DL2EDB1SB | Main | bulb base | BA 15d
10523 | DL2EDB1SB | Main | signalling type | Steady
10524 | DL2EDB1SB | Main | signalling colour | White
10525 | DL2EDB1SB | Main | [Us] rated supply voltage | 24 V AC/DC
10526 | DL2EDB1SB | Main | luminance | 900 cd/m²
10527 | DL2EDB1SB | Main | sale per indivisible quantity | 1
10528 | DL2EDB1SB | Complementary | net weight | 0.009 kg
10529 | DL2EDB1SB | Offer Sustainability | Sustainable offer status | Green Premium product
10530 | DL2EDB1SB | Offer Sustainability | REACh Regulation | REACh Declaration
10531 | DL2EDB1SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10532 | DL2EDB1SB | Offer Sustainability | Mercury free | Yes
10533 | DL2EDB1SB | Offer Sustainability | RoHS exemption information | Yes
10534 | DL2EDB1SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10535 | DL2EDB1SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10536 | DL2EDB1SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10537 | DL2EDB1SB | Contractual warranty | Warranty | 18 months
10538 | DL2EDB3SB | Main | range compatibility | Harmony XVM Optimum
10539 | DL2EDB3SB | Main | accessory / separate part category | Lighting accessory
10540 | DL2EDB3SB | Main | accessory / separate part type | Super bright LED
10541 | DL2EDB3SB | Main | accessory / separate part destination | Beacon and indicator bank
10542 | DL2EDB3SB | Main | bulb base | BA 15d
10543 | DL2EDB3SB | Main | signalling type | Steady
10544 | DL2EDB3SB | Main | signalling colour | Green
10545 | DL2EDB3SB | Main | [Us] rated supply voltage | 24 V AC/DC
10546 | DL2EDB3SB | Main | luminance | 900 cd/m²
10547 | DL2EDB3SB | Main | sale per indivisible quantity | 1
10548 | DL2EDB3SB | Complementary | net weight | 0.009 kg
10549 | DL2EDB3SB | Offer Sustainability | Sustainable offer status | Green Premium product
10550 | DL2EDB3SB | Offer Sustainability | REACh Regulation | REACh Declaration
10551 | DL2EDB3SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10552 | DL2EDB3SB | Offer Sustainability | Mercury free | Yes
10553 | DL2EDB3SB | Offer Sustainability | RoHS exemption information | Yes
10554 | DL2EDB3SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10555 | DL2EDB3SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10556 | DL2EDB3SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10557 | DL2EDB3SB | Contractual warranty | Warranty | 18 months
10558 | DL2EDB4SB | Main | range compatibility | Harmony XVM Optimum
10559 | DL2EDB4SB | Main | accessory / separate part category | Lighting accessory
10560 | DL2EDB4SB | Main | accessory / separate part type | Super bright LED
10561 | DL2EDB4SB | Main | accessory / separate part destination | Beacon and indicator bank
10562 | DL2EDB4SB | Main | bulb base | BA 15d
10563 | DL2EDB4SB | Main | signalling type | Steady
10564 | DL2EDB4SB | Main | signalling colour | Red
10565 | DL2EDB4SB | Main | [Us] rated supply voltage | 24 V AC/DC
10566 | DL2EDB4SB | Main | luminance | 900 cd/m²
10567 | DL2EDB4SB | Main | sale per indivisible quantity | 1
10568 | DL2EDB4SB | Complementary | net weight | 0.009 kg
10569 | DL2EDB4SB | Offer Sustainability | Sustainable offer status | Green Premium product
10570 | DL2EDB4SB | Offer Sustainability | REACh Regulation | REACh Declaration
10571 | DL2EDB4SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10572 | DL2EDB4SB | Offer Sustainability | Mercury free | Yes
10573 | DL2EDB4SB | Offer Sustainability | RoHS exemption information | Yes
10574 | DL2EDB4SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10575 | DL2EDB4SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10576 | DL2EDB4SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10577 | DL2EDB4SB | Contractual warranty | Warranty | 18 months
10578 | DL2EDB6SB | Main | range compatibility | Harmony XVM Optimum
10579 | DL2EDB6SB | Main | accessory / separate part category | Lighting accessory
10580 | DL2EDB6SB | Main | accessory / separate part type | Super bright LED
10581 | DL2EDB6SB | Main | accessory / separate part destination | Beacon and indicator bank
10582 | DL2EDB6SB | Main | bulb base | BA 15d
10583 | DL2EDB6SB | Main | signalling type | Steady
10584 | DL2EDB6SB | Main | signalling colour | Blue
10585 | DL2EDB6SB | Main | [Us] rated supply voltage | 24 V AC/DC
10586 | DL2EDB6SB | Main | luminance | 900 cd/m²
10587 | DL2EDB6SB | Main | sale per indivisible quantity | 1
10588 | DL2EDB6SB | Complementary | net weight | 0.009 kg
10589 | DL2EDB6SB | Offer Sustainability | Sustainable offer status | Green Premium product
10590 | DL2EDB6SB | Offer Sustainability | REACh Regulation | REACh Declaration
10591 | DL2EDB6SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10592 | DL2EDB6SB | Offer Sustainability | Mercury free | Yes
10593 | DL2EDB6SB | Offer Sustainability | RoHS exemption information | Yes
10594 | DL2EDB6SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10595 | DL2EDB6SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10596 | DL2EDB6SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10597 | DL2EDB6SB | Contractual warranty | Warranty | 18 months
10598 | DL2EDB8SB | Main | range compatibility | Harmony XVM Optimum
10599 | DL2EDB8SB | Main | accessory / separate part category | Lighting accessory
10600 | DL2EDB8SB | Main | accessory / separate part type | Super bright LED
10601 | DL2EDB8SB | Main | accessory / separate part destination | Beacon and indicator bank
10602 | DL2EDB8SB | Main | bulb base | BA 15d
10603 | DL2EDB8SB | Main | signalling type | Steady
10604 | DL2EDB8SB | Main | signalling colour | Orange
10605 | DL2EDB8SB | Main | [Us] rated supply voltage | 24 V AC/DC
10606 | DL2EDB8SB | Main | luminance | 900 cd/m²
10607 | DL2EDB8SB | Main | sale per indivisible quantity | 1
10608 | DL2EDB8SB | Complementary | net weight | 0.009 kg
10609 | DL2EDB8SB | Offer Sustainability | Sustainable offer status | Green Premium product
10610 | DL2EDB8SB | Offer Sustainability | REACh Regulation | REACh Declaration
10611 | DL2EDB8SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10612 | DL2EDB8SB | Offer Sustainability | Mercury free | Yes
10613 | DL2EDB8SB | Offer Sustainability | RoHS exemption information | Yes
10614 | DL2EDB8SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10615 | DL2EDB8SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10616 | DL2EDB8SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10617 | DL2EDB8SB | Contractual warranty | Warranty | 18 months
10618 | DL2EDG1SB | Main | range compatibility | Harmony XVM Optimum
10619 | DL2EDG1SB | Main | accessory / separate part category | Lighting accessory
10620 | DL2EDG1SB | Main | accessory / separate part type | Super bright LED
10621 | DL2EDG1SB | Main | accessory / separate part destination | Beacon and indicator bank
10622 | DL2EDG1SB | Main | bulb base | BA 15d
10623 | DL2EDG1SB | Main | signalling type | Steady
10624 | DL2EDG1SB | Main | signalling colour | White
10625 | DL2EDG1SB | Main | [Us] rated supply voltage | 120 V AC
10626 | DL2EDG1SB | Main | luminance | 900 cd/m²
10627 | DL2EDG1SB | Main | sale per indivisible quantity | 1
10628 | DL2EDG1SB | Complementary | net weight | 0.009 kg
10629 | DL2EDG1SB | Offer Sustainability | Sustainable offer status | Green Premium product
10630 | DL2EDG1SB | Offer Sustainability | REACh Regulation | REACh Declaration
10631 | DL2EDG1SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10632 | DL2EDG1SB | Offer Sustainability | Mercury free | Yes
10633 | DL2EDG1SB | Offer Sustainability | RoHS exemption information | Yes
10634 | DL2EDG1SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10635 | DL2EDG1SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10636 | DL2EDG1SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10637 | DL2EDG1SB | Contractual warranty | Warranty | 18 months
10638 | DL2EDG3SB | Main | range compatibility | Harmony XVM Optimum
10639 | DL2EDG3SB | Main | accessory / separate part category | Lighting accessory
10640 | DL2EDG3SB | Main | accessory / separate part type | Super bright LED
10641 | DL2EDG3SB | Main | accessory / separate part destination | Beacon and indicator bank
10642 | DL2EDG3SB | Main | bulb base | BA 15d
10643 | DL2EDG3SB | Main | signalling type | Steady
10644 | DL2EDG3SB | Main | signalling colour | Green
10645 | DL2EDG3SB | Main | [Us] rated supply voltage | 120 V AC
10646 | DL2EDG3SB | Main | luminance | 900 cd/m²
10647 | DL2EDG3SB | Main | sale per indivisible quantity | 1
10648 | DL2EDG3SB | Complementary | net weight | 0.009 kg
10649 | DL2EDG3SB | Offer Sustainability | Sustainable offer status | Green Premium product
10650 | DL2EDG3SB | Offer Sustainability | REACh Regulation | REACh Declaration
10651 | DL2EDG3SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10652 | DL2EDG3SB | Offer Sustainability | Mercury free | Yes
10653 | DL2EDG3SB | Offer Sustainability | RoHS exemption information | Yes
10654 | DL2EDG3SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10655 | DL2EDG3SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10656 | DL2EDG3SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10657 | DL2EDG3SB | Contractual warranty | Warranty | 18 months
10658 | DL2EDG4SB | Main | range compatibility | Harmony XVM Optimum
10659 | DL2EDG4SB | Main | accessory / separate part category | Lighting accessory
10660 | DL2EDG4SB | Main | accessory / separate part type | Super bright LED
10661 | DL2EDG4SB | Main | accessory / separate part destination | Beacon and indicator bank
10662 | DL2EDG4SB | Main | bulb base | BA 15d
10663 | DL2EDG4SB | Main | signalling type | Steady
10664 | DL2EDG4SB | Main | signalling colour | Red
10665 | DL2EDG4SB | Main | [Us] rated supply voltage | 120 V AC
10666 | DL2EDG4SB | Main | luminance | 900 cd/m²
10667 | DL2EDG4SB | Main | sale per indivisible quantity | 1
10668 | DL2EDG4SB | Complementary | net weight | 0.009 kg
10669 | DL2EDG4SB | Offer Sustainability | Sustainable offer status | Green Premium product
10670 | DL2EDG4SB | Offer Sustainability | REACh Regulation | REACh Declaration
10671 | DL2EDG4SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10672 | DL2EDG4SB | Offer Sustainability | Mercury free | Yes
10673 | DL2EDG4SB | Offer Sustainability | RoHS exemption information | Yes
10674 | DL2EDG4SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10675 | DL2EDG4SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10676 | DL2EDG4SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10677 | DL2EDG4SB | Contractual warranty | Warranty | 18 months
10678 | DL2EDG6SB | Main | range compatibility | Harmony XVM Optimum
10679 | DL2EDG6SB | Main | accessory / separate part category | Lighting accessory
10680 | DL2EDG6SB | Main | accessory / separate part type | Super bright LED
10681 | DL2EDG6SB | Main | accessory / separate part destination | Beacon and indicator bank
10682 | DL2EDG6SB | Main | bulb base | BA 15d
10683 | DL2EDG6SB | Main | signalling type | Steady
10684 | DL2EDG6SB | Main | signalling colour | Blue
10685 | DL2EDG6SB | Main | [Us] rated supply voltage | 120 V AC
10686 | DL2EDG6SB | Main | luminance | 900 cd/m²
10687 | DL2EDG6SB | Main | sale per indivisible quantity | 1
10688 | DL2EDG6SB | Complementary | net weight | 0.009 kg
10689 | DL2EDG6SB | Offer Sustainability | Sustainable offer status | Green Premium product
10690 | DL2EDG6SB | Offer Sustainability | REACh Regulation | REACh Declaration
10691 | DL2EDG6SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10692 | DL2EDG6SB | Offer Sustainability | Mercury free | Yes
10693 | DL2EDG6SB | Offer Sustainability | RoHS exemption information | Yes
10694 | DL2EDG6SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10695 | DL2EDG6SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10696 | DL2EDG6SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10697 | DL2EDG6SB | Contractual warranty | Warranty | 18 months
10698 | DL2EDG8SB | Main | range compatibility | Harmony XVM Optimum
10699 | DL2EDG8SB | Main | accessory / separate part category | Lighting accessory
10700 | DL2EDG8SB | Main | accessory / separate part type | Super bright LED
10701 | DL2EDG8SB | Main | accessory / separate part destination | Beacon and indicator bank
10702 | DL2EDG8SB | Main | bulb base | BA 15d
10703 | DL2EDG8SB | Main | signalling type | Steady
10704 | DL2EDG8SB | Main | signalling colour | Orange
10705 | DL2EDG8SB | Main | [Us] rated supply voltage | 120 V AC
10706 | DL2EDG8SB | Main | luminance | 900 cd/m²
10707 | DL2EDG8SB | Main | sale per indivisible quantity | 1
10708 | DL2EDG8SB | Complementary | net weight | 0.009 kg
10709 | DL2EDG8SB | Offer Sustainability | Sustainable offer status | Green Premium product
10710 | DL2EDG8SB | Offer Sustainability | REACh Regulation | REACh Declaration
10711 | DL2EDG8SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10712 | DL2EDG8SB | Offer Sustainability | Mercury free | Yes
10713 | DL2EDG8SB | Offer Sustainability | RoHS exemption information | Yes
10714 | DL2EDG8SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10715 | DL2EDG8SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10716 | DL2EDG8SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10717 | DL2EDG8SB | Contractual warranty | Warranty | 18 months
10718 | DL2EDM1SB | Main | range compatibility | Harmony XVM Optimum
10719 | DL2EDM1SB | Main | accessory / separate part category | Lighting accessory
10720 | DL2EDM1SB | Main | accessory / separate part type | Super bright LED
10721 | DL2EDM1SB | Main | accessory / separate part destination | Beacon and indicator bank
10722 | DL2EDM1SB | Main | bulb base | BA 15d
10723 | DL2EDM1SB | Main | signalling type | Steady
10724 | DL2EDM1SB | Main | signalling colour | White
10725 | DL2EDM1SB | Main | [Us] rated supply voltage | 230 V AC
10726 | DL2EDM1SB | Main | luminance | 900 cd/m²
10727 | DL2EDM1SB | Main | sale per indivisible quantity | 1
10728 | DL2EDM1SB | Complementary | net weight | 0.009 kg
10729 | DL2EDM1SB | Offer Sustainability | Sustainable offer status | Green Premium product
10730 | DL2EDM1SB | Offer Sustainability | REACh Regulation | REACh Declaration
10731 | DL2EDM1SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10732 | DL2EDM1SB | Offer Sustainability | Mercury free | Yes
10733 | DL2EDM1SB | Offer Sustainability | RoHS exemption information | Yes
10734 | DL2EDM1SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10735 | DL2EDM1SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10736 | DL2EDM1SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10737 | DL2EDM1SB | Contractual warranty | Warranty | 18 months
10738 | DL2EDM3SB | Main | range compatibility | Harmony XVM Optimum
10739 | DL2EDM3SB | Main | accessory / separate part category | Lighting accessory
10740 | DL2EDM3SB | Main | accessory / separate part type | Super bright LED
10741 | DL2EDM3SB | Main | accessory / separate part destination | Beacon and indicator bank
10742 | DL2EDM3SB | Main | bulb base | BA 15d
10743 | DL2EDM3SB | Main | signalling type | Steady
10744 | DL2EDM3SB | Main | signalling colour | Green
10745 | DL2EDM3SB | Main | [Us] rated supply voltage | 230 V AC
10746 | DL2EDM3SB | Main | luminance | 900 cd/m²
10747 | DL2EDM3SB | Main | sale per indivisible quantity | 1
10748 | DL2EDM3SB | Complementary | net weight | 0.009 kg
10749 | DL2EDM3SB | Offer Sustainability | Sustainable offer status | Green Premium product
10750 | DL2EDM3SB | Offer Sustainability | REACh Regulation | REACh Declaration
10751 | DL2EDM3SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10752 | DL2EDM3SB | Offer Sustainability | Mercury free | Yes
10753 | DL2EDM3SB | Offer Sustainability | RoHS exemption information | Yes
10754 | DL2EDM3SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10755 | DL2EDM3SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10756 | DL2EDM3SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10757 | DL2EDM3SB | Contractual warranty | Warranty | 18 months
10758 | DL2EDM4SB | Main | range compatibility | Harmony XVM Optimum
10759 | DL2EDM4SB | Main | accessory / separate part category | Lighting accessory
10760 | DL2EDM4SB | Main | accessory / separate part type | Super bright LED
10761 | DL2EDM4SB | Main | accessory / separate part destination | Beacon and indicator bank
10762 | DL2EDM4SB | Main | bulb base | BA 15d
10763 | DL2EDM4SB | Main | signalling type | Steady
10764 | DL2EDM4SB | Main | signalling colour | Red
10765 | DL2EDM4SB | Main | [Us] rated supply voltage | 230 V AC
10766 | DL2EDM4SB | Main | luminance | 900 cd/m²
10767 | DL2EDM4SB | Main | sale per indivisible quantity | 1
10768 | DL2EDM4SB | Complementary | net weight | 0.009 kg
10769 | DL2EDM4SB | Offer Sustainability | Sustainable offer status | Green Premium product
10770 | DL2EDM4SB | Offer Sustainability | REACh Regulation | REACh Declaration
10771 | DL2EDM4SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10772 | DL2EDM4SB | Offer Sustainability | Mercury free | Yes
10773 | DL2EDM4SB | Offer Sustainability | RoHS exemption information | Yes
10774 | DL2EDM4SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10775 | DL2EDM4SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10776 | DL2EDM4SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10777 | DL2EDM4SB | Contractual warranty | Warranty | 18 months
10778 | DL2EDM6SB | Main | range compatibility | Harmony XVM Optimum
10779 | DL2EDM6SB | Main | accessory / separate part category | Lighting accessory
10780 | DL2EDM6SB | Main | accessory / separate part type | Super bright LED
10781 | DL2EDM6SB | Main | accessory / separate part destination | Beacon and indicator bank
10782 | DL2EDM6SB | Main | bulb base | BA 15d
10783 | DL2EDM6SB | Main | signalling type | Steady
10784 | DL2EDM6SB | Main | signalling colour | Blue
10785 | DL2EDM6SB | Main | [Us] rated supply voltage | 230 V AC
10786 | DL2EDM6SB | Main | luminance | 900 cd/m²
10787 | DL2EDM6SB | Main | sale per indivisible quantity | 1
10788 | DL2EDM6SB | Complementary | net weight | 0.009 kg
10789 | DL2EDM6SB | Offer Sustainability | Sustainable offer status | Green Premium product
10790 | DL2EDM6SB | Offer Sustainability | REACh Regulation | REACh Declaration
10791 | DL2EDM6SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10792 | DL2EDM6SB | Offer Sustainability | Mercury free | Yes
10793 | DL2EDM6SB | Offer Sustainability | RoHS exemption information | Yes
10794 | DL2EDM6SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10795 | DL2EDM6SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10796 | DL2EDM6SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10797 | DL2EDM6SB | Contractual warranty | Warranty | 18 months
10798 | DL2EDM8SB | Main | range compatibility | Harmony XVM Optimum
10799 | DL2EDM8SB | Main | accessory / separate part category | Lighting accessory
10800 | DL2EDM8SB | Main | accessory / separate part type | Super bright LED
10801 | DL2EDM8SB | Main | accessory / separate part destination | Beacon and indicator bank
10802 | DL2EDM8SB | Main | bulb base | BA 15d
10803 | DL2EDM8SB | Main | signalling type | Steady
10804 | DL2EDM8SB | Main | signalling colour | Orange
10805 | DL2EDM8SB | Main | [Us] rated supply voltage | 230 V AC
10806 | DL2EDM8SB | Main | luminance | 900 cd/m²
10807 | DL2EDM8SB | Main | sale per indivisible quantity | 1
10808 | DL2EDM8SB | Complementary | net weight | 0.009 kg
10809 | DL2EDM8SB | Offer Sustainability | Sustainable offer status | Green Premium product
10810 | DL2EDM8SB | Offer Sustainability | REACh Regulation | REACh Declaration
10811 | DL2EDM8SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10812 | DL2EDM8SB | Offer Sustainability | Mercury free | Yes
10813 | DL2EDM8SB | Offer Sustainability | RoHS exemption information | Yes
10814 | DL2EDM8SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10815 | DL2EDM8SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10816 | DL2EDM8SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10817 | DL2EDM8SB | Contractual warranty | Warranty | 18 months
10818 | DL2EKB1SB | Main | range compatibility | Harmony XVM Optimum
10819 | DL2EKB1SB | Main | accessory / separate part category | Lighting accessory
10820 | DL2EKB1SB | Main | accessory / separate part type | Super bright LED
10821 | DL2EKB1SB | Main | accessory / separate part destination | Beacon and indicator bank
10822 | DL2EKB1SB | Main | bulb base | BA 15d
10823 | DL2EKB1SB | Main | signalling type | Flashing
10824 | DL2EKB1SB | Main | signalling colour | White
10825 | DL2EKB1SB | Main | [Us] rated supply voltage | 24 V AC/DC
10826 | DL2EKB1SB | Main | luminance | 900 cd/m²
10827 | DL2EKB1SB | Main | sale per indivisible quantity | 1
10828 | DL2EKB1SB | Complementary | flashing frequency | 1 Hz
10829 | DL2EKB1SB | Complementary | net weight | 0.009 kg
10830 | DL2EKB1SB | Offer Sustainability | Sustainable offer status | Green Premium product
10831 | DL2EKB1SB | Offer Sustainability | REACh Regulation | REACh Declaration
10832 | DL2EKB1SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10833 | DL2EKB1SB | Offer Sustainability | Mercury free | Yes
10834 | DL2EKB1SB | Offer Sustainability | RoHS exemption information | Yes
10835 | DL2EKB1SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10836 | DL2EKB1SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10837 | DL2EKB1SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10838 | DL2EKB1SB | Contractual warranty | Warranty | 18 months
10839 | DL2EKB3SB | Main | range compatibility | Harmony XVM Optimum
10840 | DL2EKB3SB | Main | accessory / separate part category | Lighting accessory
10841 | DL2EKB3SB | Main | accessory / separate part type | Super bright LED
10842 | DL2EKB3SB | Main | accessory / separate part destination | Beacon and indicator bank
10843 | DL2EKB3SB | Main | bulb base | BA 15d
10844 | DL2EKB3SB | Main | signalling type | Flashing
10845 | DL2EKB3SB | Main | signalling colour | Green
10846 | DL2EKB3SB | Main | [Us] rated supply voltage | 24 V AC/DC
10847 | DL2EKB3SB | Main | luminance | 900 cd/m²
10848 | DL2EKB3SB | Main | sale per indivisible quantity | 1
10849 | DL2EKB3SB | Complementary | flashing frequency | 1 Hz
10850 | DL2EKB3SB | Complementary | net weight | 0.009 kg
10851 | DL2EKB3SB | Offer Sustainability | Sustainable offer status | Green Premium product
10852 | DL2EKB3SB | Offer Sustainability | REACh Regulation | REACh Declaration
10853 | DL2EKB3SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10854 | DL2EKB3SB | Offer Sustainability | Mercury free | Yes
10855 | DL2EKB3SB | Offer Sustainability | RoHS exemption information | Yes
10856 | DL2EKB3SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10857 | DL2EKB3SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10858 | DL2EKB3SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10859 | DL2EKB3SB | Contractual warranty | Warranty | 18 months
10860 | DL2EKB4SB | Main | range compatibility | Harmony XVM Optimum
10861 | DL2EKB4SB | Main | accessory / separate part category | Lighting accessory
10862 | DL2EKB4SB | Main | accessory / separate part type | Super bright LED
10863 | DL2EKB4SB | Main | accessory / separate part destination | Beacon and indicator bank
10864 | DL2EKB4SB | Main | bulb base | BA 15d
10865 | DL2EKB4SB | Main | signalling type | Flashing
10866 | DL2EKB4SB | Main | signalling colour | Red
10867 | DL2EKB4SB | Main | [Us] rated supply voltage | 24 V AC/DC
10868 | DL2EKB4SB | Main | luminance | 900 cd/m²
10869 | DL2EKB4SB | Main | sale per indivisible quantity | 1
10870 | DL2EKB4SB | Complementary | flashing frequency | 1 Hz
10871 | DL2EKB4SB | Complementary | net weight | 0.009 kg
10872 | DL2EKB4SB | Offer Sustainability | Sustainable offer status | Green Premium product
10873 | DL2EKB4SB | Offer Sustainability | REACh Regulation | REACh Declaration
10874 | DL2EKB4SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10875 | DL2EKB4SB | Offer Sustainability | Mercury free | Yes
10876 | DL2EKB4SB | Offer Sustainability | RoHS exemption information | Yes
10877 | DL2EKB4SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10878 | DL2EKB4SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10879 | DL2EKB4SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10880 | DL2EKB4SB | Contractual warranty | Warranty | 18 months
10881 | DL2EKB6SB | Main | range compatibility | Harmony XVM Optimum
10882 | DL2EKB6SB | Main | accessory / separate part category | Lighting accessory
10883 | DL2EKB6SB | Main | accessory / separate part type | Super bright LED
10884 | DL2EKB6SB | Main | accessory / separate part destination | Beacon and indicator bank
10885 | DL2EKB6SB | Main | bulb base | BA 15d
10886 | DL2EKB6SB | Main | signalling type | Flashing
10887 | DL2EKB6SB | Main | signalling colour | Blue
10888 | DL2EKB6SB | Main | [Us] rated supply voltage | 24 V AC/DC
10889 | DL2EKB6SB | Main | luminance | 900 cd/m²
10890 | DL2EKB6SB | Main | sale per indivisible quantity | 1
10891 | DL2EKB6SB | Complementary | flashing frequency | 1 Hz
10892 | DL2EKB6SB | Complementary | net weight | 0.009 kg
10893 | DL2EKB6SB | Offer Sustainability | Sustainable offer status | Green Premium product
10894 | DL2EKB6SB | Offer Sustainability | REACh Regulation | REACh Declaration
10895 | DL2EKB6SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10896 | DL2EKB6SB | Offer Sustainability | Mercury free | Yes
10897 | DL2EKB6SB | Offer Sustainability | RoHS exemption information | Yes
10898 | DL2EKB6SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10899 | DL2EKB6SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10900 | DL2EKB6SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10901 | DL2EKB6SB | Contractual warranty | Warranty | 18 months
10902 | DL2EKB8SB | Main | range compatibility | Harmony XVM Optimum
10903 | DL2EKB8SB | Main | accessory / separate part category | Lighting accessory
10904 | DL2EKB8SB | Main | accessory / separate part type | Super bright LED
10905 | DL2EKB8SB | Main | accessory / separate part destination | Beacon and indicator bank
10906 | DL2EKB8SB | Main | bulb base | BA 15d
10907 | DL2EKB8SB | Main | signalling type | Flashing
10908 | DL2EKB8SB | Main | signalling colour | Orange
10909 | DL2EKB8SB | Main | [Us] rated supply voltage | 24 V AC/DC
10910 | DL2EKB8SB | Main | luminance | 900 cd/m²
10911 | DL2EKB8SB | Main | sale per indivisible quantity | 1
10912 | DL2EKB8SB | Complementary | flashing frequency | 1 Hz
10913 | DL2EKB8SB | Complementary | net weight | 0.009 kg
10914 | DL2EKB8SB | Offer Sustainability | Sustainable offer status | Green Premium product
10915 | DL2EKB8SB | Offer Sustainability | REACh Regulation | REACh Declaration
10916 | DL2EKB8SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10917 | DL2EKB8SB | Offer Sustainability | Mercury free | Yes
10918 | DL2EKB8SB | Offer Sustainability | RoHS exemption information | Yes
10919 | DL2EKB8SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10920 | DL2EKB8SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10921 | DL2EKB8SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10922 | DL2EKB8SB | Contractual warranty | Warranty | 18 months
10923 | DL2EKG1SB | Main | range compatibility | Harmony XVM Optimum
10924 | DL2EKG1SB | Main | accessory / separate part category | Lighting accessory
10925 | DL2EKG1SB | Main | accessory / separate part type | Super bright LED
10926 | DL2EKG1SB | Main | accessory / separate part destination | Beacon and indicator bank
10927 | DL2EKG1SB | Main | bulb base | BA 15d
10928 | DL2EKG1SB | Main | signalling type | Flashing
10929 | DL2EKG1SB | Main | signalling colour | White
10930 | DL2EKG1SB | Main | [Us] rated supply voltage | 120 V AC
10931 | DL2EKG1SB | Main | luminance | 900 cd/m²
10932 | DL2EKG1SB | Main | sale per indivisible quantity | 1
10933 | DL2EKG1SB | Complementary | flashing frequency | 1 Hz
10934 | DL2EKG1SB | Complementary | net weight | 0.009 kg
10935 | DL2EKG1SB | Offer Sustainability | Sustainable offer status | Green Premium product
10936 | DL2EKG1SB | Offer Sustainability | REACh Regulation | REACh Declaration
10937 | DL2EKG1SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10938 | DL2EKG1SB | Offer Sustainability | Mercury free | Yes
10939 | DL2EKG1SB | Offer Sustainability | RoHS exemption information | Yes
10940 | DL2EKG1SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10941 | DL2EKG1SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10942 | DL2EKG1SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10943 | DL2EKG1SB | Contractual warranty | Warranty | 18 months
10944 | DL2EKG3SB | Main | range compatibility | Harmony XVM Optimum
10945 | DL2EKG3SB | Main | accessory / separate part category | Lighting accessory
10946 | DL2EKG3SB | Main | accessory / separate part type | Super bright LED
10947 | DL2EKG3SB | Main | accessory / separate part destination | Beacon and indicator bank
10948 | DL2EKG3SB | Main | bulb base | BA 15d
10949 | DL2EKG3SB | Main | signalling type | Flashing
10950 | DL2EKG3SB | Main | signalling colour | Green
10951 | DL2EKG3SB | Main | [Us] rated supply voltage | 120 V AC
10952 | DL2EKG3SB | Main | luminance | 900 cd/m²
10953 | DL2EKG3SB | Main | sale per indivisible quantity | 1
10954 | DL2EKG3SB | Complementary | flashing frequency | 1 Hz
10955 | DL2EKG3SB | Complementary | net weight | 0.009 kg
10956 | DL2EKG3SB | Offer Sustainability | Sustainable offer status | Green Premium product
10957 | DL2EKG3SB | Offer Sustainability | REACh Regulation | REACh Declaration
10958 | DL2EKG3SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10959 | DL2EKG3SB | Offer Sustainability | Mercury free | Yes
10960 | DL2EKG3SB | Offer Sustainability | RoHS exemption information | Yes
10961 | DL2EKG3SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10962 | DL2EKG3SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10963 | DL2EKG3SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10964 | DL2EKG3SB | Contractual warranty | Warranty | 18 months
10965 | DL2EKG4SB | Main | range compatibility | Harmony XVM Optimum
10966 | DL2EKG4SB | Main | accessory / separate part category | Lighting accessory
10967 | DL2EKG4SB | Main | accessory / separate part type | Super bright LED
10968 | DL2EKG4SB | Main | accessory / separate part destination | Beacon and indicator bank
10969 | DL2EKG4SB | Main | bulb base | BA 15d
10970 | DL2EKG4SB | Main | signalling type | Flashing
10971 | DL2EKG4SB | Main | signalling colour | Red
10972 | DL2EKG4SB | Main | [Us] rated supply voltage | 120 V AC
10973 | DL2EKG4SB | Main | luminance | 900 cd/m²
10974 | DL2EKG4SB | Main | sale per indivisible quantity | 1
10975 | DL2EKG4SB | Complementary | flashing frequency | 1 Hz
10976 | DL2EKG4SB | Complementary | net weight | 0.009 kg
10977 | DL2EKG4SB | Offer Sustainability | Sustainable offer status | Green Premium product
10978 | DL2EKG4SB | Offer Sustainability | REACh Regulation | REACh Declaration
10979 | DL2EKG4SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
10980 | DL2EKG4SB | Offer Sustainability | Mercury free | Yes
10981 | DL2EKG4SB | Offer Sustainability | RoHS exemption information | Yes
10982 | DL2EKG4SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
10983 | DL2EKG4SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
10984 | DL2EKG4SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
10985 | DL2EKG4SB | Contractual warranty | Warranty | 18 months
10986 | DL2EKG6SB | Main | range compatibility | Harmony XVM Optimum
10987 | DL2EKG6SB | Main | accessory / separate part category | Lighting accessory
10988 | DL2EKG6SB | Main | accessory / separate part type | Super bright LED
10989 | DL2EKG6SB | Main | accessory / separate part destination | Beacon and indicator bank
10990 | DL2EKG6SB | Main | bulb base | BA 15d
10991 | DL2EKG6SB | Main | signalling type | Flashing
10992 | DL2EKG6SB | Main | signalling colour | Blue
10993 | DL2EKG6SB | Main | [Us] rated supply voltage | 120 V AC
10994 | DL2EKG6SB | Main | luminance | 900 cd/m²
10995 | DL2EKG6SB | Main | sale per indivisible quantity | 1
10996 | DL2EKG6SB | Complementary | flashing frequency | 1 Hz
10997 | DL2EKG6SB | Complementary | net weight | 0.009 kg
10998 | DL2EKG6SB | Offer Sustainability | Sustainable offer status | Green Premium product
10999 | DL2EKG6SB | Offer Sustainability | REACh Regulation | REACh Declaration
11000 | DL2EKG6SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11001 | DL2EKG6SB | Offer Sustainability | Mercury free | Yes
11002 | DL2EKG6SB | Offer Sustainability | RoHS exemption information | Yes
11003 | DL2EKG6SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11004 | DL2EKG6SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11005 | DL2EKG6SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11006 | DL2EKG6SB | Contractual warranty | Warranty | 18 months
11007 | DL2EKG8SB | Main | range compatibility | Harmony XVM Optimum
11008 | DL2EKG8SB | Main | accessory / separate part category | Lighting accessory
11009 | DL2EKG8SB | Main | accessory / separate part type | Super bright LED
11010 | DL2EKG8SB | Main | accessory / separate part destination | Beacon and indicator bank
11011 | DL2EKG8SB | Main | bulb base | BA 15d
11012 | DL2EKG8SB | Main | signalling type | Flashing
11013 | DL2EKG8SB | Main | signalling colour | Orange
11014 | DL2EKG8SB | Main | [Us] rated supply voltage | 120 V AC
11015 | DL2EKG8SB | Main | luminance | 900 cd/m²
11016 | DL2EKG8SB | Main | sale per indivisible quantity | 1
11017 | DL2EKG8SB | Complementary | flashing frequency | 1 Hz
11018 | DL2EKG8SB | Complementary | net weight | 0.009 kg
11019 | DL2EKG8SB | Offer Sustainability | Sustainable offer status | Green Premium product
11020 | DL2EKG8SB | Offer Sustainability | REACh Regulation | REACh Declaration
11021 | DL2EKG8SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11022 | DL2EKG8SB | Offer Sustainability | Mercury free | Yes
11023 | DL2EKG8SB | Offer Sustainability | RoHS exemption information | Yes
11024 | DL2EKG8SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11025 | DL2EKG8SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11026 | DL2EKG8SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11027 | DL2EKG8SB | Contractual warranty | Warranty | 18 months
11028 | DL2EKM1SB | Main | range compatibility | Harmony XVM Optimum
11029 | DL2EKM1SB | Main | accessory / separate part category | Lighting accessory
11030 | DL2EKM1SB | Main | accessory / separate part type | Super bright LED
11031 | DL2EKM1SB | Main | accessory / separate part destination | Beacon and indicator bank
11032 | DL2EKM1SB | Main | bulb base | BA 15d
11033 | DL2EKM1SB | Main | signalling type | Flashing
11034 | DL2EKM1SB | Main | signalling colour | White
11035 | DL2EKM1SB | Main | [Us] rated supply voltage | 230 V AC
11036 | DL2EKM1SB | Main | luminance | 900 cd/m²
11037 | DL2EKM1SB | Main | sale per indivisible quantity | 1
11038 | DL2EKM1SB | Complementary | flashing frequency | 1 Hz
11039 | DL2EKM1SB | Complementary | net weight | 0.009 kg
11040 | DL2EKM1SB | Offer Sustainability | Sustainable offer status | Green Premium product
11041 | DL2EKM1SB | Offer Sustainability | REACh Regulation | REACh Declaration
11042 | DL2EKM1SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11043 | DL2EKM1SB | Offer Sustainability | Mercury free | Yes
11044 | DL2EKM1SB | Offer Sustainability | RoHS exemption information | Yes
11045 | DL2EKM1SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11046 | DL2EKM1SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11047 | DL2EKM1SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11048 | DL2EKM1SB | Contractual warranty | Warranty | 18 months
11049 | DL2EKM3SB | Main | range compatibility | Harmony XVM Optimum
11050 | DL2EKM3SB | Main | accessory / separate part category | Lighting accessory
11051 | DL2EKM3SB | Main | accessory / separate part type | Super bright LED
11052 | DL2EKM3SB | Main | accessory / separate part destination | Beacon and indicator bank
11053 | DL2EKM3SB | Main | bulb base | BA 15d
11054 | DL2EKM3SB | Main | signalling type | Flashing
11055 | DL2EKM3SB | Main | signalling colour | Green
11056 | DL2EKM3SB | Main | [Us] rated supply voltage | 230 V AC
11057 | DL2EKM3SB | Main | luminance | 900 cd/m²
11058 | DL2EKM3SB | Main | sale per indivisible quantity | 1
11059 | DL2EKM3SB | Complementary | flashing frequency | 1 Hz
11060 | DL2EKM3SB | Complementary | net weight | 0.009 kg
11061 | DL2EKM3SB | Offer Sustainability | Sustainable offer status | Green Premium product
11062 | DL2EKM3SB | Offer Sustainability | REACh Regulation | REACh Declaration
11063 | DL2EKM3SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11064 | DL2EKM3SB | Offer Sustainability | Mercury free | Yes
11065 | DL2EKM3SB | Offer Sustainability | RoHS exemption information | Yes
11066 | DL2EKM3SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11067 | DL2EKM3SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11068 | DL2EKM3SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11069 | DL2EKM3SB | Contractual warranty | Warranty | 18 months
11070 | DL2EKM4SB | Main | range compatibility | Harmony XVM Optimum
11071 | DL2EKM4SB | Main | accessory / separate part category | Lighting accessory
11072 | DL2EKM4SB | Main | accessory / separate part type | Super bright LED
11073 | DL2EKM4SB | Main | accessory / separate part destination | Beacon and indicator bank
11074 | DL2EKM4SB | Main | bulb base | BA 15d
11075 | DL2EKM4SB | Main | signalling type | Flashing
11076 | DL2EKM4SB | Main | signalling colour | Red
11077 | DL2EKM4SB | Main | [Us] rated supply voltage | 230 V AC
11078 | DL2EKM4SB | Main | luminance | 900 cd/m²
11079 | DL2EKM4SB | Main | sale per indivisible quantity | 1
11080 | DL2EKM4SB | Complementary | flashing frequency | 1 Hz
11081 | DL2EKM4SB | Complementary | net weight | 0.009 kg
11082 | DL2EKM4SB | Offer Sustainability | Sustainable offer status | Green Premium product
11083 | DL2EKM4SB | Offer Sustainability | REACh Regulation | REACh Declaration
11084 | DL2EKM4SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11085 | DL2EKM4SB | Offer Sustainability | Mercury free | Yes
11086 | DL2EKM4SB | Offer Sustainability | RoHS exemption information | Yes
11087 | DL2EKM4SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11088 | DL2EKM4SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11089 | DL2EKM4SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11090 | DL2EKM4SB | Contractual warranty | Warranty | 18 months
11091 | DL2EKM6SB | Main | range compatibility | Harmony XVM Optimum
11092 | DL2EKM6SB | Main | accessory / separate part category | Lighting accessory
11093 | DL2EKM6SB | Main | accessory / separate part type | Super bright LED
11094 | DL2EKM6SB | Main | accessory / separate part destination | Beacon and indicator bank
11095 | DL2EKM6SB | Main | bulb base | BA 15d
11096 | DL2EKM6SB | Main | signalling type | Flashing
11097 | DL2EKM6SB | Main | signalling colour | Blue
11098 | DL2EKM6SB | Main | [Us] rated supply voltage | 230 V AC
11099 | DL2EKM6SB | Main | luminance | 900 cd/m²
11100 | DL2EKM6SB | Main | sale per indivisible quantity | 1
11101 | DL2EKM6SB | Complementary | flashing frequency | 1 Hz
11102 | DL2EKM6SB | Complementary | net weight | 0.009 kg
11103 | DL2EKM6SB | Offer Sustainability | Sustainable offer status | Green Premium product
11104 | DL2EKM6SB | Offer Sustainability | REACh Regulation | REACh Declaration
11105 | DL2EKM6SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11106 | DL2EKM6SB | Offer Sustainability | Mercury free | Yes
11107 | DL2EKM6SB | Offer Sustainability | RoHS exemption information | Yes
11108 | DL2EKM6SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11109 | DL2EKM6SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11110 | DL2EKM6SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11111 | DL2EKM6SB | Contractual warranty | Warranty | 18 months
11112 | DL2EKM8SB | Main | range compatibility | Harmony XVM Optimum
11113 | DL2EKM8SB | Main | accessory / separate part category | Lighting accessory
11114 | DL2EKM8SB | Main | accessory / separate part type | Super bright LED
11115 | DL2EKM8SB | Main | accessory / separate part destination | Beacon and indicator bank
11116 | DL2EKM8SB | Main | bulb base | BA 15d
11117 | DL2EKM8SB | Main | signalling type | Flashing
11118 | DL2EKM8SB | Main | signalling colour | Orange
11119 | DL2EKM8SB | Main | [Us] rated supply voltage | 230 V AC
11120 | DL2EKM8SB | Main | luminance | 900 cd/m²
11121 | DL2EKM8SB | Main | sale per indivisible quantity | 1
11122 | DL2EKM8SB | Complementary | flashing frequency | 1 Hz
11123 | DL2EKM8SB | Complementary | net weight | 0.009 kg
11124 | DL2EKM8SB | Offer Sustainability | Sustainable offer status | Green Premium product
11125 | DL2EKM8SB | Offer Sustainability | REACh Regulation | REACh Declaration
11126 | DL2EKM8SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11127 | DL2EKM8SB | Offer Sustainability | Mercury free | Yes
11128 | DL2EKM8SB | Offer Sustainability | RoHS exemption information | Yes
11129 | DL2EKM8SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11130 | DL2EKM8SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11131 | DL2EKM8SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11132 | DL2EKM8SB | Contractual warranty | Warranty | 18 months
11133 | DL6BB | Main | range compatibility | Harmony XVM Optimum
11134 | DL6BB | Main | accessory / separate part category | Lighting accessory
11135 | DL6BB | Main | accessory / separate part type | Flash discharge tube
11136 | DL6BB | Main | accessory / separate part designation | Flash discharge tube
11137 | DL6BB | Main | accessory / separate part destination | Beacon and indicator bank
11138 | DL6BB | Main | bulb base | BA 15d
11139 | DL6BB | Main | signalling type | Flashing
11140 | DL6BB | Main | [Us] rated supply voltage | 24 V AC/DC
11141 | DL6BB | Main | sale per indivisible quantity | 1
11142 | DL6BB | Complementary | flash energy | 0.8 J
11143 | DL6BB | Complementary | flashing frequency | 0.8 Hz
11144 | DL6BB | Complementary | net weight | 0.022 kg
11145 | DL6BB | Offer Sustainability | Sustainable offer status | Green Premium product
11146 | DL6BB | Offer Sustainability | REACh Regulation | REACh Declaration
11147 | DL6BB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11148 | DL6BB | Offer Sustainability | Mercury free | Yes
11149 | DL6BB | Offer Sustainability | RoHS exemption information | Yes
11150 | DL6BB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11151 | DL6BB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11152 | DL6BB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11153 | DL6BB | Contractual warranty | Warranty | 18 months
11154 | DL6BG | Main | range compatibility | Harmony XVM Optimum
11155 | DL6BG | Main | accessory / separate part category | Lighting accessory
11156 | DL6BG | Main | accessory / separate part type | Flash discharge tube
11157 | DL6BG | Main | accessory / separate part designation | Flash discharge tube
11158 | DL6BG | Main | accessory / separate part destination | Beacon and indicator bank
11159 | DL6BG | Main | bulb base | BA 15d
11160 | DL6BG | Main | signalling type | Flashing
11161 | DL6BG | Main | [Us] rated supply voltage | 120 V AC
11162 | DL6BG | Main | sale per indivisible quantity | 1
11163 | DL6BG | Complementary | flash energy | 0.8 J
11164 | DL6BG | Complementary | flashing frequency | 0.8 Hz
11165 | DL6BG | Complementary | net weight | 0.022 kg
11166 | DL6BG | Offer Sustainability | Sustainable offer status | Green Premium product
11167 | DL6BG | Offer Sustainability | REACh Regulation | REACh Declaration
11168 | DL6BG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11169 | DL6BG | Offer Sustainability | Mercury free | Yes
11170 | DL6BG | Offer Sustainability | RoHS exemption information | Yes
11171 | DL6BG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11172 | DL6BG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11173 | DL6BG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11174 | DL6BG | Contractual warranty | Warranty | 18 months
11175 | DL6BM | Main | range compatibility | Harmony XVM Optimum
11176 | DL6BM | Main | accessory / separate part category | Lighting accessory
11177 | DL6BM | Main | accessory / separate part type | Flash discharge tube
11178 | DL6BM | Main | accessory / separate part designation | Flash discharge tube
11179 | DL6BM | Main | accessory / separate part destination | Beacon and indicator bank
11180 | DL6BM | Main | bulb base | BA 15d
11181 | DL6BM | Main | signalling type | Flashing
11182 | DL6BM | Main | [Us] rated supply voltage | 230 V AC
11183 | DL6BM | Main | sale per indivisible quantity | 1
11184 | DL6BM | Complementary | flash energy | 0.8 J
11185 | DL6BM | Complementary | flashing frequency | 0.8 Hz
11186 | DL6BM | Complementary | net weight | 0.022 kg
11187 | DL6BM | Offer Sustainability | Sustainable offer status | Green Premium product
11188 | DL6BM | Offer Sustainability | REACh Regulation | REACh Declaration
11189 | DL6BM | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11190 | DL6BM | Offer Sustainability | Mercury free | Yes
11191 | DL6BM | Offer Sustainability | RoHS exemption information | Yes
11192 | DL6BM | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11193 | DL6BM | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11194 | DL6BM | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11195 | DL6BM | Contractual warranty | Warranty | 18 months
11196 | XVMC21 | Main | range of product | Harmony XVM
11197 | XVMC21 | Main | product or component type | Base unit with cover
11198 | XVMC21 | Main | kit composition | Cover Base unit
11199 | XVMC21 | Main | component name | XVM
11200 | XVMC21 | Main | indicator bank base type | Base without buzzer
11201 | XVMC21 | Complementary | mounting diameter | 45 mm
11202 | XVMC21 | Complementary | housing colour | White
11203 | XVMC21 | Complementary | connections - terminals | Screw terminals, 1 x 0.325...1 x 1.5 mm²
11204 | XVMC21 | Complementary | marking | CE
11205 | XVMC21 | Complementary | net weight | 0.055 kg
11206 | XVMC21 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
11207 | XVMC21 | Environment | product certifications | CCC
11208 | XVMC21 | Environment | ambient air temperature for storage | -25…70 °C
11209 | XVMC21 | Environment | ambient air temperature for operation | -10…50 °C
11210 | XVMC21 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 60947-1 Class I aluminium tube mounting conforming to IEC 60947-5-1 Class I aluminium tube mounting conforming to IEC 61140
11211 | XVMC21 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
11212 | XVMC21 | Environment | protective treatment | TC
11213 | XVMC21 | Packing Units | Package 1 Weight | 60 g
11214 | XVMC21 | Packing Units | Package 2 Weight | 1.623 kg
11215 | XVMC21 | Offer Sustainability | Sustainable offer status | Green Premium product
11216 | XVMC21 | Offer Sustainability | REACh Regulation | REACh Declaration
11217 | XVMC21 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11218 | XVMC21 | Offer Sustainability | Mercury free | Yes
11219 | XVMC21 | Offer Sustainability | RoHS exemption information | Yes
11220 | XVMC21 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11221 | XVMC21 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11222 | XVMC21 | Contractual warranty | Warranty | 18 months
11223 | XVMC29B | Main | range of product | Harmony XVM
11224 | XVMC29B | Main | product or component type | Base unit with cover
11225 | XVMC29B | Main | kit composition | Base unit Cover
11226 | XVMC29B | Main | component name | XVM
11227 | XVMC29B | Main | indicator bank base type | Base with integrated buzzer
11228 | XVMC29B | Main | [Us] rated supply voltage | 24 V
11229 | XVMC29B | Complementary | mounting diameter | 45 mm
11230 | XVMC29B | Complementary | signalling type | Continuous or intermittent buzzer
11231 | XVMC29B | Complementary | supply circuit type | AC/DC
11232 | XVMC29B | Complementary | housing colour | White
11233 | XVMC29B | Complementary | connections - terminals | Screw terminals, 1 x 0.325...1 x 1.5 mm²
11234 | XVMC29B | Complementary | marking | CE
11235 | XVMC29B | Complementary | current consumption | < 15 mA
11236 | XVMC29B | Complementary | fundamental frequency | 4 kHz
11237 | XVMC29B | Complementary | net weight | 0.065 kg
11238 | XVMC29B | Environment | noise level | 0…80 dB at 1 m
11239 | XVMC29B | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
11240 | XVMC29B | Environment | product certifications | CCC
11241 | XVMC29B | Environment | ambient air temperature for storage | -25…70 °C
11242 | XVMC29B | Environment | ambient air temperature for operation | -10…50 °C
11243 | XVMC29B | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 60947-1 Class I aluminium tube mounting conforming to IEC 60947-5-1 Class I aluminium tube mounting conforming to IEC 61140
11244 | XVMC29B | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
11245 | XVMC29B | Environment | protective treatment | TC
11246 | XVMC29B | Packing Units | Package 1 Weight | 69 g
11247 | XVMC29B | Packing Units | Package 2 Weight | 1.782 kg
11248 | XVMC29B | Offer Sustainability | Sustainable offer status | Green Premium product
11249 | XVMC29B | Offer Sustainability | REACh Regulation | REACh Declaration
11250 | XVMC29B | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11251 | XVMC29B | Offer Sustainability | Mercury free | Yes
11252 | XVMC29B | Offer Sustainability | RoHS exemption information | Yes
11253 | XVMC29B | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11254 | XVMC29B | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11255 | XVMC29B | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11256 | XVMC29B | Contractual warranty | Warranty | 18 months
11257 | XVMC29G | Main | range of product | Harmony XVM
11258 | XVMC29G | Main | product or component type | Base unit with cover
11259 | XVMC29G | Main | kit composition | Base unit Cover
11260 | XVMC29G | Main | component name | XVM
11261 | XVMC29G | Main | indicator bank base type | Base with integrated buzzer
11262 | XVMC29G | Main | [Us] rated supply voltage | 120 V
11263 | XVMC29G | Complementary | mounting diameter | 45 mm
11264 | XVMC29G | Complementary | signalling type | Continuous or intermittent buzzer
11265 | XVMC29G | Complementary | supply circuit type | AC
11266 | XVMC29G | Complementary | housing colour | White
11267 | XVMC29G | Complementary | connections - terminals | Screw terminals, 1 x 0.325...1 x 1.5 mm²
11268 | XVMC29G | Complementary | marking | CE
11269 | XVMC29G | Complementary | current consumption | < 18 mA
11270 | XVMC29G | Complementary | fundamental frequency | 4 kHz
11271 | XVMC29G | Complementary | net weight | 0.065 kg
11272 | XVMC29G | Environment | noise level | 0…80 dB at 1 m
11273 | XVMC29G | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
11274 | XVMC29G | Environment | product certifications | CCC
11275 | XVMC29G | Environment | ambient air temperature for storage | -25…70 °C
11276 | XVMC29G | Environment | ambient air temperature for operation | -10…50 °C
11277 | XVMC29G | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 60947-1 Class I aluminium tube mounting conforming to IEC 60947-5-1 Class I aluminium tube mounting conforming to IEC 61140
11278 | XVMC29G | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
11279 | XVMC29G | Environment | protective treatment | TC
11280 | XVMC29G | Offer Sustainability | Sustainable offer status | Green Premium product
11281 | XVMC29G | Offer Sustainability | REACh Regulation | REACh Declaration
11282 | XVMC29G | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11283 | XVMC29G | Offer Sustainability | Mercury free | Yes
11284 | XVMC29G | Offer Sustainability | RoHS exemption information | Yes
11285 | XVMC29G | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11286 | XVMC29G | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11287 | XVMC29G | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11288 | XVMC29G | Contractual warranty | Warranty | 18 months
11289 | XVMC29M | Main | range of product | Harmony XVM
11290 | XVMC29M | Main | product or component type | Base unit with cover
11291 | XVMC29M | Main | kit composition | Cover Base unit
11292 | XVMC29M | Main | component name | XVM
11293 | XVMC29M | Main | indicator bank base type | Base with integrated buzzer
11294 | XVMC29M | Main | [Us] rated supply voltage | 230 V
11295 | XVMC29M | Complementary | mounting diameter | 45 mm
11296 | XVMC29M | Complementary | signalling type | Continuous or intermittent buzzer
11297 | XVMC29M | Complementary | supply circuit type | AC
11298 | XVMC29M | Complementary | housing colour | White
11299 | XVMC29M | Complementary | connections - terminals | Screw terminals, 1 x 0.325...1 x 1.5 mm²
11300 | XVMC29M | Complementary | marking | CE
11301 | XVMC29M | Complementary | current consumption | < 18 mA
11302 | XVMC29M | Complementary | fundamental frequency | 4 kHz
11303 | XVMC29M | Complementary | net weight | 0.065 kg
11304 | XVMC29M | Environment | noise level | 0…80 dB at 1 m
11305 | XVMC29M | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
11306 | XVMC29M | Environment | product certifications | CCC
11307 | XVMC29M | Environment | ambient air temperature for storage | -25…70 °C
11308 | XVMC29M | Environment | ambient air temperature for operation | -10…50 °C
11309 | XVMC29M | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 60947-1 Class I aluminium tube mounting conforming to IEC 60947-5-1 Class I aluminium tube mounting conforming to IEC 61140
11310 | XVMC29M | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
11311 | XVMC29M | Environment | protective treatment | TC
11312 | XVMC29M | Packing Units | Package 1 Weight | 72 g
11313 | XVMC29M | Packing Units | Package 2 Weight | 1.762 kg
11314 | XVMC29M | Offer Sustainability | Sustainable offer status | Green Premium product
11315 | XVMC29M | Offer Sustainability | REACh Regulation | REACh Declaration
11316 | XVMC29M | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11317 | XVMC29M | Offer Sustainability | Mercury free | Yes
11318 | XVMC29M | Offer Sustainability | RoHS exemption information | Yes
11319 | XVMC29M | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11320 | XVMC29M | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11321 | XVMC29M | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11322 | XVMC29M | Contractual warranty | Warranty | 18 months
11323 | DL1BEJ | Main | range compatibility | Harmony XVD Harmony XVB Harmony XVP
11324 | DL1BEJ | Main | accessory / separate part designation | Incandescent bulb
11325 | DL1BEJ | Main | accessory / separate part type | Incandescent bulb
11326 | DL1BEJ | Main | accessory / separate part category | Lighting accessories
11327 | DL1BEJ | Main | accessory / separate part destination | Beacon and indicator bank
11328 | DL1BEJ | Main | [Us] rated supply voltage | 12 V
11329 | DL1BEJ | Main | signalling type | Steady
11330 | DL1BEJ | Main | power dissipation in W | 7 W
11331 | DL1BEJ | Main | sale per indivisible quantity | 10
11332 | DL1BEJ | Complementary | bulb base | BA 15d
11333 | DL1BEJ | Complementary | net weight | 0.09 kg
11334 | DL1BEJ | Offer Sustainability | Sustainable offer status | Green Premium product
11335 | DL1BEJ | Offer Sustainability | REACh Regulation | REACh Declaration
11336 | DL1BEJ | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11337 | DL1BEJ | Offer Sustainability | Mercury free | Yes
11338 | DL1BEJ | Offer Sustainability | RoHS exemption information | Yes
11339 | DL1BEJ | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11340 | DL1BEJ | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11341 | DL1BEJ | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11342 | DL1BEJ | Contractual warranty | Warranty | 18 months
11343 | DL1BEB | Main | range compatibility | Harmony XVP Harmony XVB Harmony XVD
11344 | DL1BEB | Main | accessory / separate part designation | Incandescent bulb
11345 | DL1BEB | Main | accessory / separate part type | Incandescent bulb
11346 | DL1BEB | Main | accessory / separate part category | Lighting accessories
11347 | DL1BEB | Main | accessory / separate part destination | Beacon and indicator bank
11348 | DL1BEB | Main | [Us] rated supply voltage | 24 V
11349 | DL1BEB | Main | signalling type | Steady
11350 | DL1BEB | Main | power dissipation in W | 6.5 W
11351 | DL1BEB | Main | sale per indivisible quantity | 10
11352 | DL1BEB | Complementary | bulb base | BA 15d
11353 | DL1BEB | Complementary | net weight | 0.09 kg
11354 | DL1BEB | Offer Sustainability | Sustainable offer status | Green Premium product
11355 | DL1BEB | Offer Sustainability | REACh Regulation | REACh Declaration
11356 | DL1BEB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11357 | DL1BEB | Offer Sustainability | Mercury free | Yes
11358 | DL1BEB | Offer Sustainability | RoHS exemption information | Yes
11359 | DL1BEB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11360 | DL1BEB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11361 | DL1BEB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11362 | DL1BEB | Contractual warranty | Warranty | 18 months
11363 | DL1BEE | Main | range compatibility | Harmony XVP Harmony XVB Harmony XVD
11364 | DL1BEE | Main | accessory / separate part designation | Incandescent bulb
11365 | DL1BEE | Main | accessory / separate part type | Incandescent bulb
11366 | DL1BEE | Main | accessory / separate part category | Lighting accessories
11367 | DL1BEE | Main | accessory / separate part destination | Beacon and indicator bank
11368 | DL1BEE | Main | [Us] rated supply voltage | 48 V
11369 | DL1BEE | Main | signalling type | Steady
11370 | DL1BEE | Main | power dissipation in W | 6 W
11371 | DL1BEE | Main | sale per indivisible quantity | 10
11372 | DL1BEE | Complementary | bulb base | BA 15d
11373 | DL1BEE | Complementary | net weight | 0.09 kg
11374 | DL1BEE | Offer Sustainability | Sustainable offer status | Green Premium product
11375 | DL1BEE | Offer Sustainability | REACh Regulation | REACh Declaration
11376 | DL1BEE | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11377 | DL1BEE | Offer Sustainability | Mercury free | Yes
11378 | DL1BEE | Offer Sustainability | RoHS exemption information | Yes
11379 | DL1BEE | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11380 | DL1BEE | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11381 | DL1BEE | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11382 | DL1BEE | Contractual warranty | Warranty | 18 months
11383 | DL1BEG | Main | range compatibility | Harmony XVB Harmony XVP Harmony XVD
11384 | DL1BEG | Main | accessory / separate part designation | Incandescent bulb
11385 | DL1BEG | Main | accessory / separate part type | Incandescent bulb
11386 | DL1BEG | Main | accessory / separate part category | Lighting accessories
11387 | DL1BEG | Main | accessory / separate part destination | Beacon and indicator bank
11388 | DL1BEG | Main | [Us] rated supply voltage | 120 V
11389 | DL1BEG | Main | signalling type | Steady
11390 | DL1BEG | Main | power dissipation in W | 7 W
11391 | DL1BEG | Main | sale per indivisible quantity | 10
11392 | DL1BEG | Complementary | bulb base | BA 15d
11393 | DL1BEG | Complementary | net weight | 0.09 kg
11394 | DL1BEG | Offer Sustainability | Sustainable offer status | Green Premium product
11395 | DL1BEG | Offer Sustainability | REACh Regulation | REACh Declaration
11396 | DL1BEG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11397 | DL1BEG | Offer Sustainability | Mercury free | Yes
11398 | DL1BEG | Offer Sustainability | RoHS exemption information | Yes
11399 | DL1BEG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11400 | DL1BEG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11401 | DL1BEG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11402 | DL1BEG | Contractual warranty | Warranty | 18 months
11403 | DL1BEM | Main | range compatibility | Harmony XVB Harmony XVD Harmony XVP
11404 | DL1BEM | Main | accessory / separate part designation | Incandescent bulb
11405 | DL1BEM | Main | accessory / separate part type | Incandescent bulb
11406 | DL1BEM | Main | accessory / separate part category | Lighting accessories
11407 | DL1BEM | Main | accessory / separate part destination | Beacon and indicator bank
11408 | DL1BEM | Main | [Us] rated supply voltage | 230 V
11409 | DL1BEM | Main | signalling type | Steady
11410 | DL1BEM | Main | power dissipation in W | 7 W
11411 | DL1BEM | Main | sale per indivisible quantity | 10
11412 | DL1BEM | Complementary | bulb base | BA 15d
11413 | DL1BEM | Complementary | net weight | 0.09 kg
11414 | DL1BEM | Offer Sustainability | Sustainable offer status | Green Premium product
11415 | DL1BEM | Offer Sustainability | REACh Regulation | REACh Declaration
11416 | DL1BEM | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11417 | DL1BEM | Offer Sustainability | Mercury free | Yes
11418 | DL1BEM | Offer Sustainability | RoHS exemption information | Yes
11419 | DL1BEM | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11420 | DL1BEM | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11421 | DL1BEM | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11422 | DL1BEM | Contractual warranty | Warranty | 18 months
11423 | DL1BDB1 | Main | range compatibility | Harmony XVD Harmony XVB Harmony XVP
11424 | DL1BDB1 | Main | accessory / separate part designation | Protected LED bulb
11425 | DL1BDB1 | Main | accessory / separate part type | LED bulb
11426 | DL1BDB1 | Main | accessory / separate part category | Lighting accessories
11427 | DL1BDB1 | Main | accessory / separate part destination | Beacon and indicator bank
11428 | DL1BDB1 | Main | [Us] rated supply voltage | 24 V AC/DC
11429 | DL1BDB1 | Main | signalling type | Steady
11430 | DL1BDB1 | Main | signalling colour | White
11431 | DL1BDB1 | Main | sale per indivisible quantity | 1
11432 | DL1BDB1 | Complementary | current consumption | 47 mA
11433 | DL1BDB1 | Complementary | bulb base | BA 15d
11434 | DL1BDB1 | Complementary | net weight | 0.015 kg
11435 | DL1BDB1 | Offer Sustainability | Sustainable offer status | Green Premium product
11436 | DL1BDB1 | Offer Sustainability | REACh Regulation | REACh Declaration
11437 | DL1BDB1 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11438 | DL1BDB1 | Offer Sustainability | Mercury free | Yes
11439 | DL1BDB1 | Offer Sustainability | RoHS exemption information | Yes
11440 | DL1BDB1 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11441 | DL1BDB1 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11442 | DL1BDB1 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11443 | DL1BDB1 | Contractual warranty | Warranty | 18 months
11444 | DL1BDB3 | Main | range compatibility | Harmony XVB Harmony XVD Harmony XVP
11445 | DL1BDB3 | Main | accessory / separate part designation | Protected LED bulb
11446 | DL1BDB3 | Main | accessory / separate part type | LED bulb
11447 | DL1BDB3 | Main | accessory / separate part category | Lighting accessories
11448 | DL1BDB3 | Main | accessory / separate part destination | Beacon and indicator bank
11449 | DL1BDB3 | Main | [Us] rated supply voltage | 24 V AC/DC
11450 | DL1BDB3 | Main | signalling type | Steady
11451 | DL1BDB3 | Main | signalling colour | Green
11452 | DL1BDB3 | Main | sale per indivisible quantity | 1
11453 | DL1BDB3 | Complementary | current consumption | 47 mA
11454 | DL1BDB3 | Complementary | bulb base | BA 15d
11455 | DL1BDB3 | Complementary | net weight | 0.015 kg
11456 | DL1BDB3 | Offer Sustainability | Sustainable offer status | Green Premium product
11457 | DL1BDB3 | Offer Sustainability | REACh Regulation | REACh Declaration
11458 | DL1BDB3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11459 | DL1BDB3 | Offer Sustainability | Mercury free | Yes
11460 | DL1BDB3 | Offer Sustainability | RoHS exemption information | Yes
11461 | DL1BDB3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11462 | DL1BDB3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11463 | DL1BDB3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11464 | DL1BDB3 | Contractual warranty | Warranty | 18 months
11465 | DL1BDB4 | Main | range compatibility | Harmony XVP Harmony XVD Harmony XVB
11466 | DL1BDB4 | Main | accessory / separate part designation | Protected LED bulb
11467 | DL1BDB4 | Main | accessory / separate part type | LED bulb
11468 | DL1BDB4 | Main | accessory / separate part category | Lighting accessories
11469 | DL1BDB4 | Main | accessory / separate part destination | Beacon and indicator bank
11470 | DL1BDB4 | Main | [Us] rated supply voltage | 24 V AC/DC
11471 | DL1BDB4 | Main | signalling type | Steady
11472 | DL1BDB4 | Main | signalling colour | Red
11473 | DL1BDB4 | Main | sale per indivisible quantity | 1
11474 | DL1BDB4 | Complementary | current consumption | 47 mA
11475 | DL1BDB4 | Complementary | bulb base | BA 15d
11476 | DL1BDB4 | Complementary | net weight | 0.015 kg
11477 | DL1BDB4 | Offer Sustainability | Sustainable offer status | Green Premium product
11478 | DL1BDB4 | Offer Sustainability | REACh Regulation | REACh Declaration
11479 | DL1BDB4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11480 | DL1BDB4 | Offer Sustainability | Mercury free | Yes
11481 | DL1BDB4 | Offer Sustainability | RoHS exemption information | Yes
11482 | DL1BDB4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11483 | DL1BDB4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11484 | DL1BDB4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11485 | DL1BDB4 | Contractual warranty | Warranty | 18 months
11486 | DL1BDB5 | Main | range compatibility | Harmony XVD Harmony XVP Harmony XVB
11487 | DL1BDB5 | Main | accessory / separate part designation | Protected LED bulb
11488 | DL1BDB5 | Main | accessory / separate part type | LED bulb
11489 | DL1BDB5 | Main | accessory / separate part category | Lighting accessories
11490 | DL1BDB5 | Main | accessory / separate part destination | Beacon and indicator bank
11491 | DL1BDB5 | Main | [Us] rated supply voltage | 24 V AC/DC
11492 | DL1BDB5 | Main | signalling type | Steady
11493 | DL1BDB5 | Main | signalling colour | Orange
11494 | DL1BDB5 | Main | sale per indivisible quantity | 1
11495 | DL1BDB5 | Complementary | current consumption | 47 mA
11496 | DL1BDB5 | Complementary | bulb base | BA 15d
11497 | DL1BDB5 | Complementary | net weight | 0.015 kg
11498 | DL1BDB5 | Offer Sustainability | Sustainable offer status | Green Premium product
11499 | DL1BDB5 | Offer Sustainability | REACh Regulation | REACh Declaration
11500 | DL1BDB5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11501 | DL1BDB5 | Offer Sustainability | Mercury free | Yes
11502 | DL1BDB5 | Offer Sustainability | RoHS exemption information | Yes
11503 | DL1BDB5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11504 | DL1BDB5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11505 | DL1BDB5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11506 | DL1BDB5 | Contractual warranty | Warranty | 18 months
11507 | DL1BDB6 | Main | range compatibility | Harmony XVB Harmony XVP Harmony XVD
11508 | DL1BDB6 | Main | accessory / separate part designation | Protected LED bulb
11509 | DL1BDB6 | Main | accessory / separate part type | LED bulb
11510 | DL1BDB6 | Main | accessory / separate part category | Lighting accessories
11511 | DL1BDB6 | Main | accessory / separate part destination | Beacon and indicator bank
11512 | DL1BDB6 | Main | [Us] rated supply voltage | 24 V AC/DC
11513 | DL1BDB6 | Main | signalling type | Steady
11514 | DL1BDB6 | Main | signalling colour | Blue
11515 | DL1BDB6 | Main | sale per indivisible quantity | 1
11516 | DL1BDB6 | Complementary | current consumption | 47 mA
11517 | DL1BDB6 | Complementary | bulb base | BA 15d
11518 | DL1BDB6 | Complementary | net weight | 0.015 kg
11519 | DL1BDB6 | Offer Sustainability | Sustainable offer status | Green Premium product
11520 | DL1BDB6 | Offer Sustainability | REACh Regulation | REACh Declaration
11521 | DL1BDB6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11522 | DL1BDB6 | Offer Sustainability | Mercury free | Yes
11523 | DL1BDB6 | Offer Sustainability | RoHS exemption information | Yes
11524 | DL1BDB6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11525 | DL1BDB6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11526 | DL1BDB6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11527 | DL1BDB6 | Contractual warranty | Warranty | 18 months
11528 | DL1BDB8 | Main | range compatibility | Harmony XVP Harmony XVB Harmony XVD
11529 | DL1BDB8 | Main | accessory / separate part designation | Protected LED bulb
11530 | DL1BDB8 | Main | accessory / separate part type | LED bulb
11531 | DL1BDB8 | Main | accessory / separate part category | Lighting accessories
11532 | DL1BDB8 | Main | accessory / separate part destination | Beacon and indicator bank
11533 | DL1BDB8 | Main | [Us] rated supply voltage | 24 V AC/DC
11534 | DL1BDB8 | Main | signalling type | Steady
11535 | DL1BDB8 | Main | signalling colour | Yellow
11536 | DL1BDB8 | Main | sale per indivisible quantity | 1
11537 | DL1BDB8 | Complementary | current consumption | 47 mA
11538 | DL1BDB8 | Complementary | bulb base | BA 15d
11539 | DL1BDB8 | Complementary | net weight | 0.015 kg
11540 | DL1BDB8 | Offer Sustainability | Sustainable offer status | Green Premium product
11541 | DL1BDB8 | Offer Sustainability | REACh Regulation | REACh Declaration
11542 | DL1BDB8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11543 | DL1BDB8 | Offer Sustainability | Mercury free | Yes
11544 | DL1BDB8 | Offer Sustainability | RoHS exemption information | Yes
11545 | DL1BDB8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11546 | DL1BDB8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11547 | DL1BDB8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11548 | DL1BDB8 | Contractual warranty | Warranty | 18 months
11549 | DL1BDG1 | Main | range compatibility | Harmony XVD Harmony XVB Harmony XVP
11550 | DL1BDG1 | Main | accessory / separate part designation | Protected LED bulb
11551 | DL1BDG1 | Main | accessory / separate part type | LED bulb
11552 | DL1BDG1 | Main | accessory / separate part category | Lighting accessories
11553 | DL1BDG1 | Main | accessory / separate part destination | Beacon and indicator bank
11554 | DL1BDG1 | Main | [Us] rated supply voltage | 120 V AC
11555 | DL1BDG1 | Main | signalling type | Steady
11556 | DL1BDG1 | Main | signalling colour | White
11557 | DL1BDG1 | Main | sale per indivisible quantity | 1
11558 | DL1BDG1 | Complementary | current consumption | 17 mA
11559 | DL1BDG1 | Complementary | bulb base | BA 15d
11560 | DL1BDG1 | Complementary | net weight | 0.015 kg
11561 | DL1BDG1 | Offer Sustainability | Sustainable offer status | Green Premium product
11562 | DL1BDG1 | Offer Sustainability | REACh Regulation | REACh Declaration
11563 | DL1BDG1 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11564 | DL1BDG1 | Offer Sustainability | Mercury free | Yes
11565 | DL1BDG1 | Offer Sustainability | RoHS exemption information | Yes
11566 | DL1BDG1 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11567 | DL1BDG1 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11568 | DL1BDG1 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11569 | DL1BDG1 | Contractual warranty | Warranty | 18 months
11570 | DL1BDG3 | Main | range compatibility | Harmony XVD Harmony XVB Harmony XVP
11571 | DL1BDG3 | Main | accessory / separate part designation | Protected LED bulb
11572 | DL1BDG3 | Main | accessory / separate part type | LED bulb
11573 | DL1BDG3 | Main | accessory / separate part category | Lighting accessories
11574 | DL1BDG3 | Main | accessory / separate part destination | Beacon and indicator bank
11575 | DL1BDG3 | Main | [Us] rated supply voltage | 120 V AC
11576 | DL1BDG3 | Main | signalling type | Steady
11577 | DL1BDG3 | Main | signalling colour | Green
11578 | DL1BDG3 | Main | sale per indivisible quantity | 1
11579 | DL1BDG3 | Complementary | current consumption | 17 mA
11580 | DL1BDG3 | Complementary | bulb base | BA 15d
11581 | DL1BDG3 | Complementary | net weight | 0.015 kg
11582 | DL1BDG3 | Offer Sustainability | Sustainable offer status | Green Premium product
11583 | DL1BDG3 | Offer Sustainability | REACh Regulation | REACh Declaration
11584 | DL1BDG3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11585 | DL1BDG3 | Offer Sustainability | Mercury free | Yes
11586 | DL1BDG3 | Offer Sustainability | RoHS exemption information | Yes
11587 | DL1BDG3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11588 | DL1BDG3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11589 | DL1BDG3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11590 | DL1BDG3 | Contractual warranty | Warranty | 18 months
11591 | DL1BDG4 | Main | range compatibility | Harmony XVD Harmony XVB Harmony XVP
11592 | DL1BDG4 | Main | accessory / separate part designation | Protected LED bulb
11593 | DL1BDG4 | Main | accessory / separate part type | LED bulb
11594 | DL1BDG4 | Main | accessory / separate part category | Lighting accessories
11595 | DL1BDG4 | Main | accessory / separate part destination | Beacon and indicator bank
11596 | DL1BDG4 | Main | [Us] rated supply voltage | 120 V AC
11597 | DL1BDG4 | Main | signalling type | Steady
11598 | DL1BDG4 | Main | signalling colour | Red
11599 | DL1BDG4 | Main | sale per indivisible quantity | 1
11600 | DL1BDG4 | Complementary | current consumption | 17 mA
11601 | DL1BDG4 | Complementary | bulb base | BA 15d
11602 | DL1BDG4 | Complementary | net weight | 0.015 kg
11603 | DL1BDG4 | Offer Sustainability | Sustainable offer status | Green Premium product
11604 | DL1BDG4 | Offer Sustainability | REACh Regulation | REACh Declaration
11605 | DL1BDG4 | Offer Sustainability | REACh free of SVHC | Yes
11606 | DL1BDG4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11607 | DL1BDG4 | Offer Sustainability | Toxic heavy metal free | Yes
11608 | DL1BDG4 | Offer Sustainability | Mercury free | Yes
11609 | DL1BDG4 | Offer Sustainability | RoHS exemption information | Yes
11610 | DL1BDG4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11611 | DL1BDG4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11612 | DL1BDG4 | Offer Sustainability | Circularity Profile | End of Life Information
11613 | DL1BDG4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11614 | DL1BDG4 | Contractual warranty | Warranty | 18 months
11615 | DL1BDG5 | Main | range compatibility | Harmony XVB Harmony XVD Harmony XVP
11616 | DL1BDG5 | Main | accessory / separate part designation | Protected LED bulb
11617 | DL1BDG5 | Main | accessory / separate part type | LED bulb
11618 | DL1BDG5 | Main | accessory / separate part category | Lighting accessories
11619 | DL1BDG5 | Main | accessory / separate part destination | Beacon and indicator bank
11620 | DL1BDG5 | Main | [Us] rated supply voltage | 120 V AC
11621 | DL1BDG5 | Main | signalling type | Steady
11622 | DL1BDG5 | Main | signalling colour | Orange
11623 | DL1BDG5 | Main | sale per indivisible quantity | 1
11624 | DL1BDG5 | Complementary | current consumption | 17 mA
11625 | DL1BDG5 | Complementary | bulb base | BA 15d
11626 | DL1BDG5 | Complementary | net weight | 0.015 kg
11627 | DL1BDG5 | Offer Sustainability | Sustainable offer status | Green Premium product
11628 | DL1BDG5 | Offer Sustainability | REACh Regulation | REACh Declaration
11629 | DL1BDG5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11630 | DL1BDG5 | Offer Sustainability | Mercury free | Yes
11631 | DL1BDG5 | Offer Sustainability | RoHS exemption information | Yes
11632 | DL1BDG5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11633 | DL1BDG5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11634 | DL1BDG5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11635 | DL1BDG5 | Contractual warranty | Warranty | 18 months
11636 | DL1BDG6 | Main | range compatibility | Harmony XVD Harmony XVB Harmony XVP
11637 | DL1BDG6 | Main | accessory / separate part designation | Protected LED bulb
11638 | DL1BDG6 | Main | accessory / separate part type | LED bulb
11639 | DL1BDG6 | Main | accessory / separate part category | Lighting accessories
11640 | DL1BDG6 | Main | accessory / separate part destination | Beacon and indicator bank
11641 | DL1BDG6 | Main | [Us] rated supply voltage | 120 V AC
11642 | DL1BDG6 | Main | signalling type | Steady
11643 | DL1BDG6 | Main | signalling colour | Blue
11644 | DL1BDG6 | Main | sale per indivisible quantity | 1
11645 | DL1BDG6 | Complementary | current consumption | 17 mA
11646 | DL1BDG6 | Complementary | bulb base | BA 15d
11647 | DL1BDG6 | Complementary | net weight | 0.015 kg
11648 | DL1BDG6 | Offer Sustainability | Sustainable offer status | Green Premium product
11649 | DL1BDG6 | Offer Sustainability | REACh Regulation | REACh Declaration
11650 | DL1BDG6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11651 | DL1BDG6 | Offer Sustainability | Mercury free | Yes
11652 | DL1BDG6 | Offer Sustainability | RoHS exemption information | Yes
11653 | DL1BDG6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11654 | DL1BDG6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11655 | DL1BDG6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11656 | DL1BDG6 | Contractual warranty | Warranty | 18 months
11657 | DL1BDG8 | Main | range compatibility | Harmony XVP Harmony XVB Harmony XVD
11658 | DL1BDG8 | Main | accessory / separate part designation | Protected LED bulb
11659 | DL1BDG8 | Main | accessory / separate part type | LED bulb
11660 | DL1BDG8 | Main | accessory / separate part category | Lighting accessories
11661 | DL1BDG8 | Main | accessory / separate part destination | Beacon and indicator bank
11662 | DL1BDG8 | Main | [Us] rated supply voltage | 120 V AC
11663 | DL1BDG8 | Main | signalling type | Steady
11664 | DL1BDG8 | Main | signalling colour | Yellow
11665 | DL1BDG8 | Main | sale per indivisible quantity | 1
11666 | DL1BDG8 | Complementary | current consumption | 17 mA
11667 | DL1BDG8 | Complementary | bulb base | BA 15d
11668 | DL1BDG8 | Complementary | net weight | 0.015 kg
11669 | DL1BDG8 | Offer Sustainability | Sustainable offer status | Green Premium product
11670 | DL1BDG8 | Offer Sustainability | REACh Regulation | REACh Declaration
11671 | DL1BDG8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11672 | DL1BDG8 | Offer Sustainability | Mercury free | Yes
11673 | DL1BDG8 | Offer Sustainability | RoHS exemption information | Yes
11674 | DL1BDG8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11675 | DL1BDG8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11676 | DL1BDG8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11677 | DL1BDG8 | Contractual warranty | Warranty | 18 months
11678 | DL1BDM1 | Main | range compatibility | Harmony XVD Harmony XVB Harmony XVP
11679 | DL1BDM1 | Main | accessory / separate part designation | Protected LED bulb
11680 | DL1BDM1 | Main | accessory / separate part type | LED bulb
11681 | DL1BDM1 | Main | accessory / separate part category | Lighting accessories
11682 | DL1BDM1 | Main | accessory / separate part destination | Beacon and indicator bank
11683 | DL1BDM1 | Main | [Us] rated supply voltage | 230 V AC
11684 | DL1BDM1 | Main | signalling type | Steady
11685 | DL1BDM1 | Main | signalling colour | White
11686 | DL1BDM1 | Main | sale per indivisible quantity | 1
11687 | DL1BDM1 | Complementary | current consumption | 17 mA
11688 | DL1BDM1 | Complementary | bulb base | BA 15d
11689 | DL1BDM1 | Complementary | net weight | 0.015 kg
11690 | DL1BDM1 | Offer Sustainability | Sustainable offer status | Green Premium product
11691 | DL1BDM1 | Offer Sustainability | REACh Regulation | REACh Declaration
11692 | DL1BDM1 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11693 | DL1BDM1 | Offer Sustainability | Mercury free | Yes
11694 | DL1BDM1 | Offer Sustainability | RoHS exemption information | Yes
11695 | DL1BDM1 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11696 | DL1BDM1 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11697 | DL1BDM1 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11698 | DL1BDM1 | Contractual warranty | Warranty | 18 months
11699 | DL1BDM3 | Main | range compatibility | Harmony XVD Harmony XVB Harmony XVP
11700 | DL1BDM3 | Main | accessory / separate part designation | Protected LED bulb
11701 | DL1BDM3 | Main | accessory / separate part type | LED bulb
11702 | DL1BDM3 | Main | accessory / separate part category | Lighting accessories
11703 | DL1BDM3 | Main | accessory / separate part destination | Beacon and indicator bank
11704 | DL1BDM3 | Main | [Us] rated supply voltage | 230 V AC
11705 | DL1BDM3 | Main | signalling type | Steady
11706 | DL1BDM3 | Main | signalling colour | Green
11707 | DL1BDM3 | Main | sale per indivisible quantity | 1
11708 | DL1BDM3 | Complementary | current consumption | 17 mA
11709 | DL1BDM3 | Complementary | bulb base | BA 15d
11710 | DL1BDM3 | Complementary | net weight | 0.015 kg
11711 | DL1BDM3 | Offer Sustainability | Sustainable offer status | Green Premium product
11712 | DL1BDM3 | Offer Sustainability | REACh Regulation | REACh Declaration
11713 | DL1BDM3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11714 | DL1BDM3 | Offer Sustainability | Mercury free | Yes
11715 | DL1BDM3 | Offer Sustainability | RoHS exemption information | Yes
11716 | DL1BDM3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11717 | DL1BDM3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11718 | DL1BDM3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11719 | DL1BDM3 | Contractual warranty | Warranty | 18 months
11720 | DL1BDM4 | Main | range compatibility | Harmony XVB Harmony XVD Harmony XVP
11721 | DL1BDM4 | Main | accessory / separate part designation | Protected LED bulb
11722 | DL1BDM4 | Main | accessory / separate part type | LED bulb
11723 | DL1BDM4 | Main | accessory / separate part category | Lighting accessories
11724 | DL1BDM4 | Main | accessory / separate part destination | Beacon and indicator bank
11725 | DL1BDM4 | Main | [Us] rated supply voltage | 230 V AC
11726 | DL1BDM4 | Main | signalling type | Steady
11727 | DL1BDM4 | Main | signalling colour | Red
11728 | DL1BDM4 | Main | sale per indivisible quantity | 1
11729 | DL1BDM4 | Complementary | current consumption | 17 mA
11730 | DL1BDM4 | Complementary | bulb base | BA 15d
11731 | DL1BDM4 | Complementary | net weight | 0.015 kg
11732 | DL1BDM4 | Offer Sustainability | Sustainable offer status | Green Premium product
11733 | DL1BDM4 | Offer Sustainability | REACh Regulation | REACh Declaration
11734 | DL1BDM4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11735 | DL1BDM4 | Offer Sustainability | Mercury free | Yes
11736 | DL1BDM4 | Offer Sustainability | RoHS exemption information | Yes
11737 | DL1BDM4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11738 | DL1BDM4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11739 | DL1BDM4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11740 | DL1BDM4 | Contractual warranty | Warranty | 18 months
11741 | DL1BDM5 | Main | range compatibility | Harmony XVD Harmony XVB Harmony XVP
11742 | DL1BDM5 | Main | accessory / separate part designation | Protected LED bulb
11743 | DL1BDM5 | Main | accessory / separate part type | LED bulb
11744 | DL1BDM5 | Main | accessory / separate part category | Lighting accessories
11745 | DL1BDM5 | Main | accessory / separate part destination | Beacon and indicator bank
11746 | DL1BDM5 | Main | [Us] rated supply voltage | 230 V AC
11747 | DL1BDM5 | Main | signalling type | Steady
11748 | DL1BDM5 | Main | signalling colour | Orange
11749 | DL1BDM5 | Main | sale per indivisible quantity | 1
11750 | DL1BDM5 | Complementary | current consumption | 17 mA
11751 | DL1BDM5 | Complementary | bulb base | BA 15d
11752 | DL1BDM5 | Complementary | net weight | 0.015 kg
11753 | DL1BDM5 | Offer Sustainability | Sustainable offer status | Green Premium product
11754 | DL1BDM5 | Offer Sustainability | REACh Regulation | REACh Declaration
11755 | DL1BDM5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11756 | DL1BDM5 | Offer Sustainability | Mercury free | Yes
11757 | DL1BDM5 | Offer Sustainability | RoHS exemption information | Yes
11758 | DL1BDM5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11759 | DL1BDM5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11760 | DL1BDM5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11761 | DL1BDM5 | Contractual warranty | Warranty | 18 months
11762 | DL1BDM6 | Main | range compatibility | Harmony XVP Harmony XVB Harmony XVD
11763 | DL1BDM6 | Main | accessory / separate part designation | Protected LED bulb
11764 | DL1BDM6 | Main | accessory / separate part type | LED bulb
11765 | DL1BDM6 | Main | accessory / separate part category | Lighting accessories
11766 | DL1BDM6 | Main | accessory / separate part destination | Beacon and indicator bank
11767 | DL1BDM6 | Main | [Us] rated supply voltage | 230 V AC
11768 | DL1BDM6 | Main | signalling type | Steady
11769 | DL1BDM6 | Main | signalling colour | Blue
11770 | DL1BDM6 | Main | sale per indivisible quantity | 1
11771 | DL1BDM6 | Complementary | current consumption | 17 mA
11772 | DL1BDM6 | Complementary | bulb base | BA 15d
11773 | DL1BDM6 | Complementary | net weight | 0.015 kg
11774 | DL1BDM6 | Offer Sustainability | Sustainable offer status | Green Premium product
11775 | DL1BDM6 | Offer Sustainability | REACh Regulation | REACh Declaration
11776 | DL1BDM6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11777 | DL1BDM6 | Offer Sustainability | Mercury free | Yes
11778 | DL1BDM6 | Offer Sustainability | RoHS exemption information | Yes
11779 | DL1BDM6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11780 | DL1BDM6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11781 | DL1BDM6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11782 | DL1BDM6 | Contractual warranty | Warranty | 18 months
11783 | DL1BDM8 | Main | range compatibility | Harmony XVP Harmony XVB Harmony XVD
11784 | DL1BDM8 | Main | accessory / separate part designation | Protected LED bulb
11785 | DL1BDM8 | Main | accessory / separate part type | LED bulb
11786 | DL1BDM8 | Main | accessory / separate part category | Lighting accessories
11787 | DL1BDM8 | Main | accessory / separate part destination | Beacon and indicator bank
11788 | DL1BDM8 | Main | [Us] rated supply voltage | 230 V AC
11789 | DL1BDM8 | Main | signalling type | Steady
11790 | DL1BDM8 | Main | signalling colour | Yellow
11791 | DL1BDM8 | Main | sale per indivisible quantity | 1
11792 | DL1BDM8 | Complementary | current consumption | 17 mA
11793 | DL1BDM8 | Complementary | bulb base | BA 15d
11794 | DL1BDM8 | Complementary | net weight | 0.015 kg
11795 | DL1BDM8 | Offer Sustainability | Sustainable offer status | Green Premium product
11796 | DL1BDM8 | Offer Sustainability | REACh Regulation | REACh Declaration
11797 | DL1BDM8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11798 | DL1BDM8 | Offer Sustainability | Mercury free | Yes
11799 | DL1BDM8 | Offer Sustainability | RoHS exemption information | Yes
11800 | DL1BDM8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11801 | DL1BDM8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11802 | DL1BDM8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11803 | DL1BDM8 | Contractual warranty | Warranty | 18 months
11804 | DL1BKB1 | Main | range compatibility | Harmony XVD Harmony XVB Harmony XVP
11805 | DL1BKB1 | Main | accessory / separate part designation | Protected LED bulb
11806 | DL1BKB1 | Main | accessory / separate part type | LED bulb
11807 | DL1BKB1 | Main | accessory / separate part category | Lighting accessories
11808 | DL1BKB1 | Main | accessory / separate part destination | Beacon and indicator bank
11809 | DL1BKB1 | Main | [Us] rated supply voltage | 24 V AC/DC
11810 | DL1BKB1 | Main | signalling type | Flashing
11811 | DL1BKB1 | Main | signalling colour | White
11812 | DL1BKB1 | Main | sale per indivisible quantity | 1
11813 | DL1BKB1 | Complementary | current consumption | 47 mA
11814 | DL1BKB1 | Complementary | bulb base | BA 15d
11815 | DL1BKB1 | Complementary | net weight | 0.015 kg
11816 | DL1BKB1 | Offer Sustainability | Sustainable offer status | Green Premium product
11817 | DL1BKB1 | Offer Sustainability | REACh Regulation | REACh Declaration
11818 | DL1BKB1 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11819 | DL1BKB1 | Offer Sustainability | Mercury free | Yes
11820 | DL1BKB1 | Offer Sustainability | RoHS exemption information | Yes
11821 | DL1BKB1 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11822 | DL1BKB1 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11823 | DL1BKB1 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11824 | DL1BKB1 | Contractual warranty | Warranty | 18 months
11825 | DL1BKB3 | Main | range compatibility | Harmony XVD Harmony XVP Harmony XVB
11826 | DL1BKB3 | Main | accessory / separate part designation | Protected LED bulb
11827 | DL1BKB3 | Main | accessory / separate part type | LED bulb
11828 | DL1BKB3 | Main | accessory / separate part category | Lighting accessories
11829 | DL1BKB3 | Main | accessory / separate part destination | Beacon and indicator bank
11830 | DL1BKB3 | Main | [Us] rated supply voltage | 24 V AC/DC
11831 | DL1BKB3 | Main | signalling type | Flashing
11832 | DL1BKB3 | Main | signalling colour | Green
11833 | DL1BKB3 | Main | sale per indivisible quantity | 1
11834 | DL1BKB3 | Complementary | current consumption | 47 mA
11835 | DL1BKB3 | Complementary | bulb base | BA 15d
11836 | DL1BKB3 | Complementary | net weight | 0.015 kg
11837 | DL1BKB3 | Offer Sustainability | Sustainable offer status | Green Premium product
11838 | DL1BKB3 | Offer Sustainability | REACh Regulation | REACh Declaration
11839 | DL1BKB3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11840 | DL1BKB3 | Offer Sustainability | Mercury free | Yes
11841 | DL1BKB3 | Offer Sustainability | RoHS exemption information | Yes
11842 | DL1BKB3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11843 | DL1BKB3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11844 | DL1BKB3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11845 | DL1BKB3 | Contractual warranty | Warranty | 18 months
11846 | DL1BKB4 | Main | range compatibility | Harmony XVP Harmony XVB Harmony XVD
11847 | DL1BKB4 | Main | accessory / separate part designation | Protected LED bulb
11848 | DL1BKB4 | Main | accessory / separate part type | LED bulb
11849 | DL1BKB4 | Main | accessory / separate part category | Lighting accessories
11850 | DL1BKB4 | Main | accessory / separate part destination | Beacon and indicator bank
11851 | DL1BKB4 | Main | [Us] rated supply voltage | 24 V AC/DC
11852 | DL1BKB4 | Main | signalling type | Flashing
11853 | DL1BKB4 | Main | signalling colour | Red
11854 | DL1BKB4 | Main | sale per indivisible quantity | 1
11855 | DL1BKB4 | Complementary | current consumption | 47 mA
11856 | DL1BKB4 | Complementary | bulb base | BA 15d
11857 | DL1BKB4 | Complementary | net weight | 0.015 kg
11858 | DL1BKB4 | Offer Sustainability | Sustainable offer status | Green Premium product
11859 | DL1BKB4 | Offer Sustainability | REACh Regulation | REACh Declaration
11860 | DL1BKB4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11861 | DL1BKB4 | Offer Sustainability | Mercury free | Yes
11862 | DL1BKB4 | Offer Sustainability | RoHS exemption information | Yes
11863 | DL1BKB4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11864 | DL1BKB4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11865 | DL1BKB4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11866 | DL1BKB4 | Contractual warranty | Warranty | 18 months
11867 | DL1BKB5 | Main | range compatibility | Harmony XVB Harmony XVD Harmony XVP
11868 | DL1BKB5 | Main | accessory / separate part designation | Protected LED bulb
11869 | DL1BKB5 | Main | accessory / separate part type | LED bulb
11870 | DL1BKB5 | Main | accessory / separate part category | Lighting accessories
11871 | DL1BKB5 | Main | accessory / separate part destination | Beacon and indicator bank
11872 | DL1BKB5 | Main | [Us] rated supply voltage | 24 V AC/DC
11873 | DL1BKB5 | Main | signalling type | Flashing
11874 | DL1BKB5 | Main | signalling colour | Orange
11875 | DL1BKB5 | Main | sale per indivisible quantity | 1
11876 | DL1BKB5 | Complementary | current consumption | 47 mA
11877 | DL1BKB5 | Complementary | bulb base | BA 15d
11878 | DL1BKB5 | Complementary | net weight | 0.015 kg
11879 | DL1BKB5 | Offer Sustainability | Sustainable offer status | Green Premium product
11880 | DL1BKB5 | Offer Sustainability | REACh Regulation | REACh Declaration
11881 | DL1BKB5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11882 | DL1BKB5 | Offer Sustainability | Mercury free | Yes
11883 | DL1BKB5 | Offer Sustainability | RoHS exemption information | Yes
11884 | DL1BKB5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11885 | DL1BKB5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11886 | DL1BKB5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11887 | DL1BKB5 | Contractual warranty | Warranty | 18 months
11888 | DL1BKB6 | Main | range compatibility | Harmony XVD Harmony XVB Harmony XVP
11889 | DL1BKB6 | Main | accessory / separate part designation | Protected LED bulb
11890 | DL1BKB6 | Main | accessory / separate part type | LED bulb
11891 | DL1BKB6 | Main | accessory / separate part category | Lighting accessories
11892 | DL1BKB6 | Main | accessory / separate part destination | Beacon and indicator bank
11893 | DL1BKB6 | Main | [Us] rated supply voltage | 24 V AC/DC
11894 | DL1BKB6 | Main | signalling type | Flashing
11895 | DL1BKB6 | Main | signalling colour | Blue
11896 | DL1BKB6 | Main | sale per indivisible quantity | 1
11897 | DL1BKB6 | Complementary | current consumption | 47 mA
11898 | DL1BKB6 | Complementary | bulb base | BA 15d
11899 | DL1BKB6 | Complementary | net weight | 0.015 kg
11900 | DL1BKB6 | Offer Sustainability | Sustainable offer status | Green Premium product
11901 | DL1BKB6 | Offer Sustainability | REACh Regulation | REACh Declaration
11902 | DL1BKB6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11903 | DL1BKB6 | Offer Sustainability | Mercury free | Yes
11904 | DL1BKB6 | Offer Sustainability | RoHS exemption information | Yes
11905 | DL1BKB6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11906 | DL1BKB6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11907 | DL1BKB6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11908 | DL1BKB6 | Contractual warranty | Warranty | 18 months
11909 | DL1BKB8 | Main | range compatibility | Harmony XVD Harmony XVB Harmony XVP
11910 | DL1BKB8 | Main | accessory / separate part designation | Protected LED bulb
11911 | DL1BKB8 | Main | accessory / separate part type | LED bulb
11912 | DL1BKB8 | Main | accessory / separate part category | Lighting accessories
11913 | DL1BKB8 | Main | accessory / separate part destination | Beacon and indicator bank
11914 | DL1BKB8 | Main | [Us] rated supply voltage | 24 V AC/DC
11915 | DL1BKB8 | Main | signalling type | Flashing
11916 | DL1BKB8 | Main | signalling colour | Yellow
11917 | DL1BKB8 | Main | sale per indivisible quantity | 1
11918 | DL1BKB8 | Complementary | current consumption | 47 mA
11919 | DL1BKB8 | Complementary | bulb base | BA 15d
11920 | DL1BKB8 | Complementary | net weight | 0.015 kg
11921 | DL1BKB8 | Offer Sustainability | Sustainable offer status | Green Premium product
11922 | DL1BKB8 | Offer Sustainability | REACh Regulation | REACh Declaration
11923 | DL1BKB8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11924 | DL1BKB8 | Offer Sustainability | Mercury free | Yes
11925 | DL1BKB8 | Offer Sustainability | RoHS exemption information | Yes
11926 | DL1BKB8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11927 | DL1BKB8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11928 | DL1BKB8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11929 | DL1BKB8 | Contractual warranty | Warranty | 18 months
11930 | DL1BKG1 | Main | range compatibility | Harmony XVP Harmony XVB Harmony XVD
11931 | DL1BKG1 | Main | accessory / separate part designation | Protected LED bulb
11932 | DL1BKG1 | Main | accessory / separate part type | LED bulb
11933 | DL1BKG1 | Main | accessory / separate part category | Lighting accessories
11934 | DL1BKG1 | Main | accessory / separate part destination | Beacon and indicator bank
11935 | DL1BKG1 | Main | [Us] rated supply voltage | 120 V AC
11936 | DL1BKG1 | Main | signalling type | Flashing
11937 | DL1BKG1 | Main | signalling colour | White
11938 | DL1BKG1 | Main | sale per indivisible quantity | 1
11939 | DL1BKG1 | Complementary | current consumption | 17 mA
11940 | DL1BKG1 | Complementary | bulb base | BA 15d
11941 | DL1BKG1 | Complementary | net weight | 0.015 kg
11942 | DL1BKG1 | Offer Sustainability | Sustainable offer status | Green Premium product
11943 | DL1BKG1 | Offer Sustainability | REACh Regulation | REACh Declaration
11944 | DL1BKG1 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11945 | DL1BKG1 | Offer Sustainability | Mercury free | Yes
11946 | DL1BKG1 | Offer Sustainability | RoHS exemption information | Yes
11947 | DL1BKG1 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11948 | DL1BKG1 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11949 | DL1BKG1 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11950 | DL1BKG1 | Contractual warranty | Warranty | 18 months
11951 | DL1BKG3 | Main | range compatibility | Harmony XVD Harmony XVB Harmony XVP
11952 | DL1BKG3 | Main | accessory / separate part designation | Protected LED bulb
11953 | DL1BKG3 | Main | accessory / separate part type | LED bulb
11954 | DL1BKG3 | Main | accessory / separate part category | Lighting accessories
11955 | DL1BKG3 | Main | accessory / separate part destination | Beacon and indicator bank
11956 | DL1BKG3 | Main | [Us] rated supply voltage | 120 V AC
11957 | DL1BKG3 | Main | signalling type | Flashing
11958 | DL1BKG3 | Main | signalling colour | Green
11959 | DL1BKG3 | Main | sale per indivisible quantity | 1
11960 | DL1BKG3 | Complementary | current consumption | 17 mA
11961 | DL1BKG3 | Complementary | bulb base | BA 15d
11962 | DL1BKG3 | Complementary | net weight | 0.015 kg
11963 | DL1BKG3 | Offer Sustainability | Sustainable offer status | Green Premium product
11964 | DL1BKG3 | Offer Sustainability | REACh Regulation | REACh Declaration
11965 | DL1BKG3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11966 | DL1BKG3 | Offer Sustainability | Mercury free | Yes
11967 | DL1BKG3 | Offer Sustainability | RoHS exemption information | Yes
11968 | DL1BKG3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11969 | DL1BKG3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11970 | DL1BKG3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11971 | DL1BKG3 | Contractual warranty | Warranty | 18 months
11972 | DL1BKG4 | Main | range compatibility | Harmony XVB Harmony XVP Harmony XVD
11973 | DL1BKG4 | Main | accessory / separate part designation | Protected LED bulb
11974 | DL1BKG4 | Main | accessory / separate part type | LED bulb
11975 | DL1BKG4 | Main | accessory / separate part category | Lighting accessories
11976 | DL1BKG4 | Main | accessory / separate part destination | Beacon and indicator bank
11977 | DL1BKG4 | Main | [Us] rated supply voltage | 120 V AC
11978 | DL1BKG4 | Main | signalling type | Flashing
11979 | DL1BKG4 | Main | signalling colour | Red
11980 | DL1BKG4 | Main | sale per indivisible quantity | 1
11981 | DL1BKG4 | Complementary | current consumption | 17 mA
11982 | DL1BKG4 | Complementary | bulb base | BA 15d
11983 | DL1BKG4 | Complementary | net weight | 0.015 kg
11984 | DL1BKG4 | Offer Sustainability | Sustainable offer status | Green Premium product
11985 | DL1BKG4 | Offer Sustainability | REACh Regulation | REACh Declaration
11986 | DL1BKG4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
11987 | DL1BKG4 | Offer Sustainability | Mercury free | Yes
11988 | DL1BKG4 | Offer Sustainability | RoHS exemption information | Yes
11989 | DL1BKG4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
11990 | DL1BKG4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
11991 | DL1BKG4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
11992 | DL1BKG4 | Contractual warranty | Warranty | 18 months
11993 | DL1BKG5 | Main | range compatibility | Harmony XVD Harmony XVB Harmony XVP
11994 | DL1BKG5 | Main | accessory / separate part designation | Protected LED bulb
11995 | DL1BKG5 | Main | accessory / separate part type | LED bulb
11996 | DL1BKG5 | Main | accessory / separate part category | Lighting accessories
11997 | DL1BKG5 | Main | accessory / separate part destination | Beacon and indicator bank
11998 | DL1BKG5 | Main | [Us] rated supply voltage | 120 V AC
11999 | DL1BKG5 | Main | signalling type | Flashing
12000 | DL1BKG5 | Main | signalling colour | Orange
12001 | DL1BKG5 | Main | sale per indivisible quantity | 1
12002 | DL1BKG5 | Complementary | current consumption | 17 mA
12003 | DL1BKG5 | Complementary | bulb base | BA 15d
12004 | DL1BKG5 | Complementary | net weight | 0.015 kg
12005 | DL1BKG5 | Offer Sustainability | Sustainable offer status | Green Premium product
12006 | DL1BKG5 | Offer Sustainability | REACh Regulation | REACh Declaration
12007 | DL1BKG5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12008 | DL1BKG5 | Offer Sustainability | Mercury free | Yes
12009 | DL1BKG5 | Offer Sustainability | RoHS exemption information | Yes
12010 | DL1BKG5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12011 | DL1BKG5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12012 | DL1BKG5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12013 | DL1BKG5 | Contractual warranty | Warranty | 18 months
12014 | DL1BKG6 | Main | range compatibility | Harmony XVB Harmony XVP Harmony XVD
12015 | DL1BKG6 | Main | accessory / separate part designation | Protected LED bulb
12016 | DL1BKG6 | Main | accessory / separate part type | LED bulb
12017 | DL1BKG6 | Main | accessory / separate part category | Lighting accessories
12018 | DL1BKG6 | Main | accessory / separate part destination | Beacon and indicator bank
12019 | DL1BKG6 | Main | [Us] rated supply voltage | 120 V AC
12020 | DL1BKG6 | Main | signalling type | Flashing
12021 | DL1BKG6 | Main | signalling colour | Blue
12022 | DL1BKG6 | Main | sale per indivisible quantity | 1
12023 | DL1BKG6 | Complementary | current consumption | 17 mA
12024 | DL1BKG6 | Complementary | bulb base | BA 15d
12025 | DL1BKG6 | Complementary | net weight | 0.015 kg
12026 | DL1BKG6 | Offer Sustainability | Sustainable offer status | Green Premium product
12027 | DL1BKG6 | Offer Sustainability | REACh Regulation | REACh Declaration
12028 | DL1BKG6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12029 | DL1BKG6 | Offer Sustainability | Mercury free | Yes
12030 | DL1BKG6 | Offer Sustainability | RoHS exemption information | Yes
12031 | DL1BKG6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12032 | DL1BKG6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12033 | DL1BKG6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12034 | DL1BKG6 | Contractual warranty | Warranty | 18 months
12035 | DL1BKG8 | Main | range compatibility | Harmony XVP Harmony XVD Harmony XVB
12036 | DL1BKG8 | Main | accessory / separate part designation | Protected LED bulb
12037 | DL1BKG8 | Main | accessory / separate part type | LED bulb
12038 | DL1BKG8 | Main | accessory / separate part category | Lighting accessories
12039 | DL1BKG8 | Main | accessory / separate part destination | Beacon and indicator bank
12040 | DL1BKG8 | Main | [Us] rated supply voltage | 120 V AC
12041 | DL1BKG8 | Main | signalling type | Flashing
12042 | DL1BKG8 | Main | signalling colour | Yellow
12043 | DL1BKG8 | Main | sale per indivisible quantity | 1
12044 | DL1BKG8 | Complementary | current consumption | 17 mA
12045 | DL1BKG8 | Complementary | bulb base | BA 15d
12046 | DL1BKG8 | Complementary | net weight | 0.015 kg
12047 | DL1BKG8 | Offer Sustainability | Sustainable offer status | Green Premium product
12048 | DL1BKG8 | Offer Sustainability | REACh Regulation | REACh Declaration
12049 | DL1BKG8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12050 | DL1BKG8 | Offer Sustainability | Mercury free | Yes
12051 | DL1BKG8 | Offer Sustainability | RoHS exemption information | Yes
12052 | DL1BKG8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12053 | DL1BKG8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12054 | DL1BKG8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12055 | DL1BKG8 | Contractual warranty | Warranty | 18 months
12056 | DL1BKM1 | Main | range compatibility | Harmony XVD Harmony XVP Harmony XVB
12057 | DL1BKM1 | Main | accessory / separate part designation | Protected LED bulb
12058 | DL1BKM1 | Main | accessory / separate part type | LED bulb
12059 | DL1BKM1 | Main | accessory / separate part category | Lighting accessories
12060 | DL1BKM1 | Main | accessory / separate part destination | Beacon and indicator bank
12061 | DL1BKM1 | Main | [Us] rated supply voltage | 230 V AC
12062 | DL1BKM1 | Main | signalling type | Flashing
12063 | DL1BKM1 | Main | signalling colour | White
12064 | DL1BKM1 | Main | sale per indivisible quantity | 1
12065 | DL1BKM1 | Complementary | current consumption | 17 mA
12066 | DL1BKM1 | Complementary | bulb base | BA 15d
12067 | DL1BKM1 | Complementary | net weight | 0.015 kg
12068 | DL1BKM1 | Offer Sustainability | Sustainable offer status | Green Premium product
12069 | DL1BKM1 | Offer Sustainability | REACh Regulation | REACh Declaration
12070 | DL1BKM1 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12071 | DL1BKM1 | Offer Sustainability | Mercury free | Yes
12072 | DL1BKM1 | Offer Sustainability | RoHS exemption information | Yes
12073 | DL1BKM1 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12074 | DL1BKM1 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12075 | DL1BKM1 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12076 | DL1BKM1 | Contractual warranty | Warranty | 18 months
12077 | DL1BKM3 | Main | range compatibility | Harmony XVD Harmony XVB Harmony XVP
12078 | DL1BKM3 | Main | accessory / separate part designation | Protected LED bulb
12079 | DL1BKM3 | Main | accessory / separate part type | LED bulb
12080 | DL1BKM3 | Main | accessory / separate part category | Lighting accessories
12081 | DL1BKM3 | Main | accessory / separate part destination | Beacon and indicator bank
12082 | DL1BKM3 | Main | [Us] rated supply voltage | 230 V AC
12083 | DL1BKM3 | Main | signalling type | Flashing
12084 | DL1BKM3 | Main | signalling colour | Green
12085 | DL1BKM3 | Main | sale per indivisible quantity | 1
12086 | DL1BKM3 | Complementary | current consumption | 17 mA
12087 | DL1BKM3 | Complementary | bulb base | BA 15d
12088 | DL1BKM3 | Complementary | net weight | 0.015 kg
12089 | DL1BKM3 | Offer Sustainability | Sustainable offer status | Green Premium product
12090 | DL1BKM3 | Offer Sustainability | REACh Regulation | REACh Declaration
12091 | DL1BKM3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12092 | DL1BKM3 | Offer Sustainability | Mercury free | Yes
12093 | DL1BKM3 | Offer Sustainability | RoHS exemption information | Yes
12094 | DL1BKM3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12095 | DL1BKM3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12096 | DL1BKM3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12097 | DL1BKM3 | Contractual warranty | Warranty | 18 months
12098 | DL1BKM4 | Main | range compatibility | Harmony XVB Harmony XVP Harmony XVD
12099 | DL1BKM4 | Main | accessory / separate part designation | Protected LED bulb
12100 | DL1BKM4 | Main | accessory / separate part type | LED bulb
12101 | DL1BKM4 | Main | accessory / separate part category | Lighting accessories
12102 | DL1BKM4 | Main | accessory / separate part destination | Beacon and indicator bank
12103 | DL1BKM4 | Main | [Us] rated supply voltage | 230 V AC
12104 | DL1BKM4 | Main | signalling type | Flashing
12105 | DL1BKM4 | Main | signalling colour | Red
12106 | DL1BKM4 | Main | sale per indivisible quantity | 1
12107 | DL1BKM4 | Complementary | current consumption | 17 mA
12108 | DL1BKM4 | Complementary | bulb base | BA 15d
12109 | DL1BKM4 | Complementary | net weight | 0.015 kg
12110 | DL1BKM4 | Offer Sustainability | Sustainable offer status | Green Premium product
12111 | DL1BKM4 | Offer Sustainability | REACh Regulation | REACh Declaration
12112 | DL1BKM4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12113 | DL1BKM4 | Offer Sustainability | Mercury free | Yes
12114 | DL1BKM4 | Offer Sustainability | RoHS exemption information | Yes
12115 | DL1BKM4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12116 | DL1BKM4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12117 | DL1BKM4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12118 | DL1BKM4 | Contractual warranty | Warranty | 18 months
12119 | DL1BKM5 | Main | range compatibility | Harmony XVB Harmony XVP Harmony XVD
12120 | DL1BKM5 | Main | accessory / separate part designation | Protected LED bulb
12121 | DL1BKM5 | Main | accessory / separate part type | LED bulb
12122 | DL1BKM5 | Main | accessory / separate part category | Lighting accessories
12123 | DL1BKM5 | Main | accessory / separate part destination | Beacon and indicator bank
12124 | DL1BKM5 | Main | [Us] rated supply voltage | 230 V AC
12125 | DL1BKM5 | Main | signalling type | Flashing
12126 | DL1BKM5 | Main | signalling colour | Orange
12127 | DL1BKM5 | Main | sale per indivisible quantity | 1
12128 | DL1BKM5 | Complementary | current consumption | 17 mA
12129 | DL1BKM5 | Complementary | bulb base | BA 15d
12130 | DL1BKM5 | Complementary | net weight | 0.015 kg
12131 | DL1BKM5 | Offer Sustainability | Sustainable offer status | Green Premium product
12132 | DL1BKM5 | Offer Sustainability | REACh Regulation | REACh Declaration
12133 | DL1BKM5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12134 | DL1BKM5 | Offer Sustainability | Mercury free | Yes
12135 | DL1BKM5 | Offer Sustainability | RoHS exemption information | Yes
12136 | DL1BKM5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12137 | DL1BKM5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12138 | DL1BKM5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12139 | DL1BKM5 | Contractual warranty | Warranty | 18 months
12140 | DL1BKM6 | Main | range compatibility | Harmony XVP Harmony XVB Harmony XVD
12141 | DL1BKM6 | Main | accessory / separate part designation | Protected LED bulb
12142 | DL1BKM6 | Main | accessory / separate part type | LED bulb
12143 | DL1BKM6 | Main | accessory / separate part category | Lighting accessories
12144 | DL1BKM6 | Main | accessory / separate part destination | Beacon and indicator bank
12145 | DL1BKM6 | Main | [Us] rated supply voltage | 230 V AC
12146 | DL1BKM6 | Main | signalling type | Flashing
12147 | DL1BKM6 | Main | signalling colour | Blue
12148 | DL1BKM6 | Main | sale per indivisible quantity | 1
12149 | DL1BKM6 | Complementary | current consumption | 17 mA
12150 | DL1BKM6 | Complementary | bulb base | BA 15d
12151 | DL1BKM6 | Complementary | net weight | 0.015 kg
12152 | DL1BKM6 | Offer Sustainability | Sustainable offer status | Green Premium product
12153 | DL1BKM6 | Offer Sustainability | REACh Regulation | REACh Declaration
12154 | DL1BKM6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12155 | DL1BKM6 | Offer Sustainability | Mercury free | Yes
12156 | DL1BKM6 | Offer Sustainability | RoHS exemption information | Yes
12157 | DL1BKM6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12158 | DL1BKM6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12159 | DL1BKM6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12160 | DL1BKM6 | Contractual warranty | Warranty | 18 months
12161 | DL1BKM8 | Main | range compatibility | Harmony XVP Harmony XVB Harmony XVD
12162 | DL1BKM8 | Main | accessory / separate part designation | Protected LED bulb
12163 | DL1BKM8 | Main | accessory / separate part type | LED bulb
12164 | DL1BKM8 | Main | accessory / separate part category | Lighting accessories
12165 | DL1BKM8 | Main | accessory / separate part destination | Beacon and indicator bank
12166 | DL1BKM8 | Main | [Us] rated supply voltage | 230 V AC
12167 | DL1BKM8 | Main | signalling type | Flashing
12168 | DL1BKM8 | Main | signalling colour | Yellow
12169 | DL1BKM8 | Main | sale per indivisible quantity | 1
12170 | DL1BKM8 | Complementary | current consumption | 17 mA
12171 | DL1BKM8 | Complementary | bulb base | BA 15d
12172 | DL1BKM8 | Complementary | net weight | 0.015 kg
12173 | DL1BKM8 | Offer Sustainability | Sustainable offer status | Green Premium product
12174 | DL1BKM8 | Offer Sustainability | REACh Regulation | REACh Declaration
12175 | DL1BKM8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12176 | DL1BKM8 | Offer Sustainability | Mercury free | Yes
12177 | DL1BKM8 | Offer Sustainability | RoHS exemption information | Yes
12178 | DL1BKM8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12179 | DL1BKM8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12180 | DL1BKM8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12181 | DL1BKM8 | Contractual warranty | Warranty | 18 months
12182 | XVBC9B | Main | range of product | Harmony XVB Universal
12183 | XVBC9B | Main | product or component type | Indicator bank
12184 | XVBC9B | Main | beacon or indicator bank unit type | Audible unit
12185 | XVBC9B | Main | mounting diameter | 70 mm
12186 | XVBC9B | Main | component name | XVBC
12187 | XVBC9B | Main | noise level | 70…90 dB at 1 m
12188 | XVBC9B | Main | [Us] rated supply voltage | 12...48 V AC/DC
12189 | XVBC9B | Complementary | signalling type | Continuous or intermittent buzzer
12190 | XVBC9B | Complementary | assembly style | Customer assembly, up to 5 units
12191 | XVBC9B | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12192 | XVBC9B | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12193 | XVBC9B | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
12194 | XVBC9B | Complementary | current consumption | < 15 mA
12195 | XVBC9B | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
12196 | XVBC9B | Complementary | fundamental frequency | 2.8 kHz
12197 | XVBC9B | Complementary | CAD overall width | 70 mm
12198 | XVBC9B | Complementary | CAD overall height | 63 mm
12199 | XVBC9B | Complementary | CAD overall depth | 70 mm
12200 | XVBC9B | Complementary | net weight | 0.17 kg
12201 | XVBC9B | Environment | product certifications | CSA C22-2 No 14 GOST UL 508 CCC
12202 | XVBC9B | Environment | standards | EN/IEC 60947-5-1
12203 | XVBC9B | Environment | protective treatment | TC
12204 | XVBC9B | Environment | ambient air temperature for storage | -40…70 °C
12205 | XVBC9B | Environment | ambient air temperature for operation | -25…50 °C
12206 | XVBC9B | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
12207 | XVBC9B | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
12208 | XVBC9B | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
12209 | XVBC9B | Packing Units | Package 1 Weight | 160 g
12210 | XVBC9B | Packing Units | Package 2 Weight | 6.715 kg
12211 | XVBC9B | Packing Units | Package 3 Weight | 60.284 kg
12212 | XVBC9B | Offer Sustainability | Sustainable offer status | Green Premium product
12213 | XVBC9B | Offer Sustainability | REACh Regulation | REACh Declaration
12214 | XVBC9B | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12215 | XVBC9B | Offer Sustainability | Mercury free | Yes
12216 | XVBC9B | Offer Sustainability | RoHS exemption information | Yes
12217 | XVBC9B | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12218 | XVBC9B | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12219 | XVBC9B | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12220 | XVBC9B | Contractual warranty | Warranty | 18 months
12221 | XVBC9M | Main | range of product | Harmony XVB Universal
12222 | XVBC9M | Main | product or component type | Indicator bank
12223 | XVBC9M | Main | beacon or indicator bank unit type | Audible unit
12224 | XVBC9M | Main | mounting diameter | 70 mm
12225 | XVBC9M | Main | component name | XVBC
12226 | XVBC9M | Main | noise level | 70…90 dB at 1 m
12227 | XVBC9M | Main | [Us] rated supply voltage | 120...230 V AC
12228 | XVBC9M | Complementary | signalling type | Continuous or intermittent buzzer
12229 | XVBC9M | Complementary | assembly style | Customer assembly, up to 5 units
12230 | XVBC9M | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12231 | XVBC9M | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12232 | XVBC9M | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
12233 | XVBC9M | Complementary | current consumption | < 25 mA
12234 | XVBC9M | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
12235 | XVBC9M | Complementary | fundamental frequency | 2.8 kHz
12236 | XVBC9M | Complementary | CAD overall width | 70 mm
12237 | XVBC9M | Complementary | CAD overall height | 63 mm
12238 | XVBC9M | Complementary | CAD overall depth | 70 mm
12239 | XVBC9M | Complementary | net weight | 0.18 kg
12240 | XVBC9M | Environment | product certifications | UL 508 GOST CCC CSA C22-2 No 14
12241 | XVBC9M | Environment | standards | EN/IEC 60947-5-1
12242 | XVBC9M | Environment | protective treatment | TC
12243 | XVBC9M | Environment | ambient air temperature for storage | -40…70 °C
12244 | XVBC9M | Environment | ambient air temperature for operation | -25…50 °C
12245 | XVBC9M | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
12246 | XVBC9M | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
12247 | XVBC9M | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
12248 | XVBC9M | Packing Units | Package 1 Weight | 170 g
12249 | XVBC9M | Packing Units | Package 2 Weight | 7 kg
12250 | XVBC9M | Offer Sustainability | Sustainable offer status | Green Premium product
12251 | XVBC9M | Offer Sustainability | REACh Regulation | REACh Declaration
12252 | XVBC9M | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12253 | XVBC9M | Offer Sustainability | Mercury free | Yes
12254 | XVBC9M | Offer Sustainability | RoHS exemption information | Yes
12255 | XVBC9M | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12256 | XVBC9M | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12257 | XVBC9M | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12258 | XVBC9M | Contractual warranty | Warranty | 18 months
12259 | XVBC07 | Main | range of product | Harmony XVB Universal
12260 | XVBC07 | Main | product or component type | Base unit
12261 | XVBC07 | Main | component name | XVBC
12262 | XVBC07 | Main | material | Glass reinforced polyamide: base unit
12263 | XVBC07 | Complementary | fixing mode | Direct or tube fixing
12264 | XVBC07 | Complementary | mounting diameter | 70 mm
12265 | XVBC07 | Complementary | product destination | Banks without flash discharge tube unit
12266 | XVBC07 | Complementary | electrical connection | 1 connector for standard input
12267 | XVBC07 | Complementary | cable entry | Bottom or side entry
12268 | XVBC07 | Complementary | assembly style | Customer assembly, up to 5 units
12269 | XVBC07 | Complementary | terminals description ISO n°1 | (COM-2)PW (COM-3)PW (COM-1)PW (GND)GROUND (COM-4)PW (COM-5)PW
12270 | XVBC07 | Complementary | net weight | 0.16 kg
12271 | XVBC07 | Environment | product certifications | CCC UL 508 CSA C22-2 No 14 GOST
12272 | XVBC07 | Environment | standards | EN/IEC 60947-5-1
12273 | XVBC07 | Environment | protective treatment | TC
12274 | XVBC07 | Environment | ambient air temperature for storage | -40…70 °C
12275 | XVBC07 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
12276 | XVBC07 | Packing Units | Package 1 Weight | 170 g
12277 | XVBC07 | Packing Units | Package 2 Weight | 7 kg
12278 | XVBC07 | Packing Units | Package 3 Weight | 62.588 kg
12279 | XVBC07 | Offer Sustainability | Sustainable offer status | Green Premium product
12280 | XVBC07 | Offer Sustainability | REACh Regulation | REACh Declaration
12281 | XVBC07 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12282 | XVBC07 | Offer Sustainability | Mercury free | Yes
12283 | XVBC07 | Offer Sustainability | RoHS exemption information | Yes
12284 | XVBC07 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12285 | XVBC07 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12286 | XVBC07 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12287 | XVBC07 | Contractual warranty | Warranty | 18 months
12288 | XVBC21 | Main | range of product | Harmony XVB Universal
12289 | XVBC21 | Main | product or component type | Base unit with cover
12290 | XVBC21 | Main | component name | XVBC
12291 | XVBC21 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: cover unit
12292 | XVBC21 | Complementary | fixing mode | Direct or tube fixing
12293 | XVBC21 | Complementary | mounting diameter | 70 mm
12294 | XVBC21 | Complementary | product destination | Banks without flash discharge tube unit
12295 | XVBC21 | Complementary | electrical connection | 1 connector for standard input
12296 | XVBC21 | Complementary | cable entry | Bottom or side entry
12297 | XVBC21 | Complementary | assembly style | Customer assembly, up to 5 units
12298 | XVBC21 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW (COM-4)PW (COM-3)PW (COM-5)PW (COM-2)PW
12299 | XVBC21 | Complementary | net weight | 0.19 kg
12300 | XVBC21 | Environment | product certifications | CCC UL 508 GOST CSA C22-2 No 14
12301 | XVBC21 | Environment | standards | EN/IEC 60947-5-1
12302 | XVBC21 | Environment | protective treatment | TC
12303 | XVBC21 | Environment | ambient air temperature for storage | -40…70 °C
12304 | XVBC21 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
12305 | XVBC21 | Packing Units | Package 1 Weight | 199 g
12306 | XVBC21 | Packing Units | Package 2 Weight | 7.877 kg
12307 | XVBC21 | Packing Units | Package 3 Weight | 71.516 kg
12308 | XVBC21 | Offer Sustainability | Sustainable offer status | Green Premium product
12309 | XVBC21 | Offer Sustainability | REACh Regulation | REACh Declaration
12310 | XVBC21 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12311 | XVBC21 | Offer Sustainability | Mercury free | Yes
12312 | XVBC21 | Offer Sustainability | RoHS exemption information | Yes
12313 | XVBC21 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12314 | XVBC21 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12315 | XVBC21 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12316 | XVBC21 | Contractual warranty | Warranty | 18 months
12317 | XVBC21A | Main | range of product | Harmony XVB Universal
12318 | XVBC21A | Main | product or component type | Base unit with cover
12319 | XVBC21A | Main | component name | XVBC
12320 | XVBC21A | Complementary | range compatibility | AS-Interface cabling system
12321 | XVBC21A | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover unit
12322 | XVBC21A | Complementary | mounting diameter | 70 mm
12323 | XVBC21A | Complementary | [Us] rated supply voltage | External: 19.2...30 V AS-Interface line: 24...31.6 V
12324 | XVBC21A | Complementary | current consumption | 250 mA under load via AS-Interface line 30 mA under load external 30 mA no load
12325 | XVBC21A | Complementary | actuator sensor interface profile [AS-i] | S.7.F
12326 | XVBC21A | Complementary | electrical connection | 1 connector M12 for AS-Interface line
12327 | XVBC21A | Complementary | cable entry | Side entry
12328 | XVBC21A | Complementary | assembly style | Customer assembly, up to 5 units
12329 | XVBC21A | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12330 | XVBC21A | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
12331 | XVBC21A | Complementary | terminals description ISO n°1 | (COM-5)PW (COM-1)PW (COM-4)PW (COM-3)PW (GND)GROUND (COM-2)PW
12332 | XVBC21A | Complementary | net weight | 0.19 kg
12333 | XVBC21A | Environment | product certifications | AS-Interface No 25701 CSA
12334 | XVBC21A | Environment | standards | EN/IEC 60947-5-1
12335 | XVBC21A | Environment | protective treatment | TC
12336 | XVBC21A | Environment | ambient air temperature for storage | -20…70 °C
12337 | XVBC21A | Environment | ambient air temperature for operation | -10…50 °C
12338 | XVBC21A | Environment | shock resistance | 25 gn conforming to IEC 60068-2-27
12339 | XVBC21A | Environment | vibration resistance | 5 gn conforming to IEC 60068-2-6
12340 | XVBC21A | Environment | overvoltage category | Class I conforming to IEC 60536
12341 | XVBC21A | Environment | IP degree of protection | IP65 conforming to IEC 60529 IP65 conforming to NF C 20-010
12342 | XVBC21A | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
12343 | XVBC21A | Packing Units | Package 1 Weight | 238 g
12344 | XVBC21A | Packing Units | Package 2 Weight | 9.079 kg
12345 | XVBC21A | Offer Sustainability | Sustainable offer status | Green Premium product
12346 | XVBC21A | Offer Sustainability | REACh Regulation | REACh Declaration
12347 | XVBC21A | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12348 | XVBC21A | Offer Sustainability | Mercury free | Yes
12349 | XVBC21A | Offer Sustainability | RoHS exemption information | Yes
12350 | XVBC21A | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12351 | XVBC21A | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12352 | XVBC21A | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12353 | XVBC21A | Contractual warranty | Warranty | 18 months
12354 | XVBC21B | Main | range of product | Harmony XVB Universal
12355 | XVBC21B | Main | product or component type | Base unit with cover
12356 | XVBC21B | Main | component name | XVBC
12357 | XVBC21B | Complementary | range compatibility | AS-Interface cabling system
12358 | XVBC21B | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover unit
12359 | XVBC21B | Complementary | mounting diameter | 70 mm
12360 | XVBC21B | Complementary | [Us] rated supply voltage | External: 19.2...30 V AS-Interface line: 24...31.6 V
12361 | XVBC21B | Complementary | current consumption | 250 mA under load via AS-Interface line 30 mA under load external 30 mA no load
12362 | XVBC21B | Complementary | actuator sensor interface profile [AS-i] | S.7.F
12363 | XVBC21B | Complementary | electrical connection | 1 remote connector M12, cable length: 1 m for AS-Interface line
12364 | XVBC21B | Complementary | cable entry | Side entry
12365 | XVBC21B | Complementary | assembly style | Customer assembly, up to 5 units
12366 | XVBC21B | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12367 | XVBC21B | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
12368 | XVBC21B | Complementary | terminals description ISO n°1 | (COM-4)PW (COM-2)PW (COM-3)PW (COM-1)PW (GND)GROUND (COM-5)PW
12369 | XVBC21B | Complementary | net weight | 0.3 kg
12370 | XVBC21B | Environment | product certifications | CSA AS-Interface No 25701
12371 | XVBC21B | Environment | standards | EN/IEC 60947-5-1
12372 | XVBC21B | Environment | protective treatment | TC
12373 | XVBC21B | Environment | ambient air temperature for storage | -20…70 °C
12374 | XVBC21B | Environment | ambient air temperature for operation | -10…50 °C
12375 | XVBC21B | Environment | shock resistance | 25 gn conforming to IEC 60068-2-27
12376 | XVBC21B | Environment | vibration resistance | 5 gn conforming to IEC 60068-2-6
12377 | XVBC21B | Environment | overvoltage category | Class I conforming to IEC 60536
12378 | XVBC21B | Environment | IP degree of protection | IP65 conforming to IEC 60529 IP65 conforming to NF C 20-010
12379 | XVBC21B | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
12380 | XVBC21B | Packing Units | Package 1 Weight | 276 g
12381 | XVBC21B | Packing Units | Package 2 Weight | 5.462 kg
12382 | XVBC21B | Offer Sustainability | Sustainable offer status | Green Premium product
12383 | XVBC21B | Offer Sustainability | REACh Regulation | REACh Declaration
12384 | XVBC21B | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12385 | XVBC21B | Offer Sustainability | Mercury free | Yes
12386 | XVBC21B | Offer Sustainability | RoHS exemption information | Yes
12387 | XVBC21B | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12388 | XVBC21B | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12389 | XVBC21B | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12390 | XVBC21B | Contractual warranty | Warranty | 18 months
12391 | XVDLS33 | Main | range of product | Harmony XVD Optimum
12392 | XVDLS33 | Main | product or component type | Complete miniature beacon
12393 | XVDLS33 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12394 | XVDLS33 | Main | signalling type | Steady
12395 | XVDLS33 | Main | mounting diameter | 45 mm
12396 | XVDLS33 | Main | component name | XVDLS
12397 | XVDLS33 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12398 | XVDLS33 | Main | light source | Bulb not included, green
12399 | XVDLS33 | Main | bulb type | Incandescent with BA 15d base
12400 | XVDLS33 | Main | [Us] rated supply voltage | <= 230 V
12401 | XVDLS33 | Main | maximum power dissipation in W | 5 W
12402 | XVDLS33 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12403 | XVDLS33 | Complementary | cable entry | 1 entry tapped for Pg 7
12404 | XVDLS33 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12405 | XVDLS33 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
12406 | XVDLS33 | Complementary | CAD overall width | 45 mm
12407 | XVDLS33 | Complementary | CAD overall height | 104 mm
12408 | XVDLS33 | Complementary | CAD overall depth | 45 mm
12409 | XVDLS33 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
12410 | XVDLS33 | Complementary | net weight | 0.08 kg
12411 | XVDLS33 | Environment | product certifications | CSA UL
12412 | XVDLS33 | Environment | standards | EN/IEC 60947-5-1
12413 | XVDLS33 | Environment | protective treatment | TC
12414 | XVDLS33 | Environment | ambient air temperature for operation | -25…70 °C
12415 | XVDLS33 | Environment | ambient air temperature for storage | -40…70 °C
12416 | XVDLS33 | Environment | electrical shock protection class | Class II conforming to IEC 60536
12417 | XVDLS33 | Environment | IP degree of protection | IP40 conforming to IEC 60529
12418 | XVDLS33 | Packing Units | Package 1 Weight | 101 g
12419 | XVDLS33 | Packing Units | Package 2 Weight | 1.409 kg
12420 | XVDLS33 | Offer Sustainability | Sustainable offer status | Green Premium product
12421 | XVDLS33 | Offer Sustainability | REACh Regulation | REACh Declaration
12422 | XVDLS33 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12423 | XVDLS33 | Offer Sustainability | Mercury free | Yes
12424 | XVDLS33 | Offer Sustainability | RoHS exemption information | Yes
12425 | XVDLS33 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12426 | XVDLS33 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12427 | XVDLS33 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12428 | XVDLS33 | Contractual warranty | Warranty | 18 months
12429 | XVDLS34 | Main | range of product | Harmony XVD Optimum
12430 | XVDLS34 | Main | product or component type | Complete miniature beacon
12431 | XVDLS34 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12432 | XVDLS34 | Main | signalling type | Steady
12433 | XVDLS34 | Main | mounting diameter | 45 mm
12434 | XVDLS34 | Main | component name | XVDLS
12435 | XVDLS34 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12436 | XVDLS34 | Main | light source | Bulb not included, red
12437 | XVDLS34 | Main | bulb type | Incandescent with BA 15d base
12438 | XVDLS34 | Main | [Us] rated supply voltage | <= 230 V
12439 | XVDLS34 | Main | maximum power dissipation in W | 5 W
12440 | XVDLS34 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12441 | XVDLS34 | Complementary | cable entry | 1 entry tapped for Pg 7
12442 | XVDLS34 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12443 | XVDLS34 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
12444 | XVDLS34 | Complementary | CAD overall width | 45 mm
12445 | XVDLS34 | Complementary | CAD overall height | 104 mm
12446 | XVDLS34 | Complementary | CAD overall depth | 45 mm
12447 | XVDLS34 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
12448 | XVDLS34 | Complementary | net weight | 0.08 kg
12449 | XVDLS34 | Environment | product certifications | UL CSA
12450 | XVDLS34 | Environment | standards | EN/IEC 60947-5-1
12451 | XVDLS34 | Environment | protective treatment | TC
12452 | XVDLS34 | Environment | ambient air temperature for operation | -25…70 °C
12453 | XVDLS34 | Environment | ambient air temperature for storage | -40…70 °C
12454 | XVDLS34 | Environment | electrical shock protection class | Class II conforming to IEC 60536
12455 | XVDLS34 | Environment | IP degree of protection | IP40 conforming to IEC 60529
12456 | XVDLS34 | Packing Units | Package 1 Weight | 101 g
12457 | XVDLS34 | Packing Units | Package 2 Weight | 1.405 kg
12458 | XVDLS34 | Offer Sustainability | Sustainable offer status | Green Premium product
12459 | XVDLS34 | Offer Sustainability | REACh Regulation | REACh Declaration
12460 | XVDLS34 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12461 | XVDLS34 | Offer Sustainability | Mercury free | Yes
12462 | XVDLS34 | Offer Sustainability | RoHS exemption information | Yes
12463 | XVDLS34 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12464 | XVDLS34 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12465 | XVDLS34 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12466 | XVDLS34 | Contractual warranty | Warranty | 18 months
12467 | XVDLS35 | Main | range of product | Harmony XVD Optimum
12468 | XVDLS35 | Main | product or component type | Complete miniature beacon
12469 | XVDLS35 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12470 | XVDLS35 | Main | signalling type | Steady
12471 | XVDLS35 | Main | mounting diameter | 45 mm
12472 | XVDLS35 | Main | component name | XVDLS
12473 | XVDLS35 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12474 | XVDLS35 | Main | light source | Bulb not included, orange
12475 | XVDLS35 | Main | bulb type | Incandescent with BA 15d base
12476 | XVDLS35 | Main | [Us] rated supply voltage | <= 230 V
12477 | XVDLS35 | Main | maximum power dissipation in W | 5 W
12478 | XVDLS35 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12479 | XVDLS35 | Complementary | cable entry | 1 entry tapped for Pg 7
12480 | XVDLS35 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12481 | XVDLS35 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
12482 | XVDLS35 | Complementary | CAD overall width | 45 mm
12483 | XVDLS35 | Complementary | CAD overall height | 104 mm
12484 | XVDLS35 | Complementary | CAD overall depth | 45 mm
12485 | XVDLS35 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
12486 | XVDLS35 | Complementary | net weight | 0.08 kg
12487 | XVDLS35 | Environment | product certifications | CSA UL
12488 | XVDLS35 | Environment | standards | EN/IEC 60947-5-1
12489 | XVDLS35 | Environment | protective treatment | TC
12490 | XVDLS35 | Environment | ambient air temperature for operation | -25…70 °C
12491 | XVDLS35 | Environment | ambient air temperature for storage | -40…70 °C
12492 | XVDLS35 | Environment | electrical shock protection class | Class II conforming to IEC 60536
12493 | XVDLS35 | Environment | IP degree of protection | IP40 conforming to IEC 60529
12494 | XVDLS35 | Packing Units | Package 1 Weight | 105 g
12495 | XVDLS35 | Packing Units | Package 2 Weight | 855 g
12496 | XVDLS35 | Offer Sustainability | Sustainable offer status | Green Premium product
12497 | XVDLS35 | Offer Sustainability | REACh Regulation | REACh Declaration
12498 | XVDLS35 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12499 | XVDLS35 | Offer Sustainability | Mercury free | Yes
12500 | XVDLS35 | Offer Sustainability | RoHS exemption information | Yes
12501 | XVDLS35 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12502 | XVDLS35 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12503 | XVDLS35 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12504 | XVDLS35 | Contractual warranty | Warranty | 18 months
12505 | XVDLS36 | Main | range of product | Harmony XVD Optimum
12506 | XVDLS36 | Main | product or component type | Complete miniature beacon
12507 | XVDLS36 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12508 | XVDLS36 | Main | signalling type | Steady
12509 | XVDLS36 | Main | mounting diameter | 45 mm
12510 | XVDLS36 | Main | component name | XVDLS
12511 | XVDLS36 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12512 | XVDLS36 | Main | light source | Bulb not included, blue
12513 | XVDLS36 | Main | bulb type | Incandescent with BA 15d base
12514 | XVDLS36 | Main | [Us] rated supply voltage | <= 230 V
12515 | XVDLS36 | Main | maximum power dissipation in W | 5 W
12516 | XVDLS36 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12517 | XVDLS36 | Complementary | cable entry | 1 entry tapped for Pg 7
12518 | XVDLS36 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12519 | XVDLS36 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
12520 | XVDLS36 | Complementary | CAD overall width | 45 mm
12521 | XVDLS36 | Complementary | CAD overall height | 104 mm
12522 | XVDLS36 | Complementary | CAD overall depth | 45 mm
12523 | XVDLS36 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
12524 | XVDLS36 | Complementary | net weight | 0.08 kg
12525 | XVDLS36 | Environment | product certifications | UL CSA
12526 | XVDLS36 | Environment | standards | EN/IEC 60947-5-1
12527 | XVDLS36 | Environment | protective treatment | TC
12528 | XVDLS36 | Environment | ambient air temperature for operation | -25…70 °C
12529 | XVDLS36 | Environment | ambient air temperature for storage | -40…70 °C
12530 | XVDLS36 | Environment | electrical shock protection class | Class II conforming to IEC 60536
12531 | XVDLS36 | Environment | IP degree of protection | IP40 conforming to IEC 60529
12532 | XVDLS36 | Packing Units | Package 1 Weight | 101 g
12533 | XVDLS36 | Offer Sustainability | Sustainable offer status | Green Premium product
12534 | XVDLS36 | Offer Sustainability | REACh Regulation | REACh Declaration
12535 | XVDLS36 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12536 | XVDLS36 | Offer Sustainability | Mercury free | Yes
12537 | XVDLS36 | Offer Sustainability | RoHS exemption information | Yes
12538 | XVDLS36 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12539 | XVDLS36 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12540 | XVDLS36 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12541 | XVDLS36 | Contractual warranty | Warranty | 18 months
12542 | XVDLS37 | Main | range of product | Harmony XVD Optimum
12543 | XVDLS37 | Main | product or component type | Complete miniature beacon
12544 | XVDLS37 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12545 | XVDLS37 | Main | signalling type | Steady
12546 | XVDLS37 | Main | mounting diameter | 45 mm
12547 | XVDLS37 | Main | component name | XVDLS
12548 | XVDLS37 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12549 | XVDLS37 | Main | light source | Bulb not included, clear
12550 | XVDLS37 | Main | bulb type | Incandescent with BA 15d base
12551 | XVDLS37 | Main | [Us] rated supply voltage | <= 230 V
12552 | XVDLS37 | Main | maximum power dissipation in W | 5 W
12553 | XVDLS37 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12554 | XVDLS37 | Complementary | cable entry | 1 entry tapped for Pg 7
12555 | XVDLS37 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12556 | XVDLS37 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
12557 | XVDLS37 | Complementary | CAD overall width | 45 mm
12558 | XVDLS37 | Complementary | CAD overall height | 104 mm
12559 | XVDLS37 | Complementary | CAD overall depth | 45 mm
12560 | XVDLS37 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
12561 | XVDLS37 | Complementary | net weight | 0.08 kg
12562 | XVDLS37 | Environment | product certifications | CSA UL
12563 | XVDLS37 | Environment | standards | EN/IEC 60947-5-1
12564 | XVDLS37 | Environment | protective treatment | TC
12565 | XVDLS37 | Environment | ambient air temperature for operation | -25…70 °C
12566 | XVDLS37 | Environment | ambient air temperature for storage | -40…70 °C
12567 | XVDLS37 | Environment | electrical shock protection class | Class II conforming to IEC 60536
12568 | XVDLS37 | Environment | IP degree of protection | IP40 conforming to IEC 60529
12569 | XVDLS37 | Offer Sustainability | Sustainable offer status | Green Premium product
12570 | XVDLS37 | Offer Sustainability | REACh Regulation | REACh Declaration
12571 | XVDLS37 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12572 | XVDLS37 | Offer Sustainability | Mercury free | Yes
12573 | XVDLS37 | Offer Sustainability | RoHS exemption information | Yes
12574 | XVDLS37 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12575 | XVDLS37 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12576 | XVDLS37 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12577 | XVDLS37 | Contractual warranty | Warranty | 18 months
12578 | XVDLS38 | Main | range of product | Harmony XVD Optimum
12579 | XVDLS38 | Main | product or component type | Complete miniature beacon
12580 | XVDLS38 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12581 | XVDLS38 | Main | signalling type | Steady
12582 | XVDLS38 | Main | mounting diameter | 45 mm
12583 | XVDLS38 | Main | component name | XVDLS
12584 | XVDLS38 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12585 | XVDLS38 | Main | light source | Bulb not included, yellow
12586 | XVDLS38 | Main | bulb type | Incandescent with BA 15d base
12587 | XVDLS38 | Main | [Us] rated supply voltage | <= 230 V
12588 | XVDLS38 | Main | maximum power dissipation in W | 5 W
12589 | XVDLS38 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12590 | XVDLS38 | Complementary | cable entry | 1 entry tapped for Pg 7
12591 | XVDLS38 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12592 | XVDLS38 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
12593 | XVDLS38 | Complementary | CAD overall width | 45 mm
12594 | XVDLS38 | Complementary | CAD overall height | 104 mm
12595 | XVDLS38 | Complementary | CAD overall depth | 45 mm
12596 | XVDLS38 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
12597 | XVDLS38 | Complementary | net weight | 0.08 kg
12598 | XVDLS38 | Environment | product certifications | CSA UL
12599 | XVDLS38 | Environment | standards | EN/IEC 60947-5-1
12600 | XVDLS38 | Environment | protective treatment | TC
12601 | XVDLS38 | Environment | ambient air temperature for operation | -25…70 °C
12602 | XVDLS38 | Environment | ambient air temperature for storage | -40…70 °C
12603 | XVDLS38 | Environment | electrical shock protection class | Class II conforming to IEC 60536
12604 | XVDLS38 | Environment | IP degree of protection | IP40 conforming to IEC 60529
12605 | XVDLS38 | Packing Units | Package 1 Weight | 0.100 kg
12606 | XVDLS38 | Offer Sustainability | Sustainable offer status | Green Premium product
12607 | XVDLS38 | Offer Sustainability | REACh Regulation | REACh Declaration
12608 | XVDLS38 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12609 | XVDLS38 | Offer Sustainability | Mercury free | Yes
12610 | XVDLS38 | Offer Sustainability | RoHS exemption information | Yes
12611 | XVDLS38 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12612 | XVDLS38 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12613 | XVDLS38 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12614 | XVDLS38 | Contractual warranty | Warranty | 18 months
12615 | XVDLS6B3 | Main | range of product | Harmony XVD Optimum
12616 | XVDLS6B3 | Main | product or component type | Complete miniature beacon
12617 | XVDLS6B3 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12618 | XVDLS6B3 | Main | signalling type | Flashing
12619 | XVDLS6B3 | Main | mounting diameter | 45 mm
12620 | XVDLS6B3 | Main | component name | XVDLS
12621 | XVDLS6B3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12622 | XVDLS6B3 | Main | light source | Integral flash discharge tube, green
12623 | XVDLS6B3 | Main | bulb type | Flash discharge tube
12624 | XVDLS6B3 | Main | [Us] rated supply voltage | 24 V AC/DC
12625 | XVDLS6B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12626 | XVDLS6B3 | Complementary | cable entry | 1 entry tapped for Pg 7
12627 | XVDLS6B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12628 | XVDLS6B3 | Complementary | current consumption | < 145 mA DC < 90 mA AC
12629 | XVDLS6B3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
12630 | XVDLS6B3 | Complementary | flash energy | 1 J
12631 | XVDLS6B3 | Complementary | CAD overall width | 45 mm
12632 | XVDLS6B3 | Complementary | CAD overall height | 104 mm
12633 | XVDLS6B3 | Complementary | CAD overall depth | 45 mm
12634 | XVDLS6B3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
12635 | XVDLS6B3 | Complementary | net weight | 0.085 kg
12636 | XVDLS6B3 | Environment | product certifications | CSA UL
12637 | XVDLS6B3 | Environment | standards | EN/IEC 60947-5-1
12638 | XVDLS6B3 | Environment | protective treatment | TC
12639 | XVDLS6B3 | Environment | ambient air temperature for operation | -10…50 °C
12640 | XVDLS6B3 | Environment | ambient air temperature for storage | -40…70 °C
12641 | XVDLS6B3 | Environment | electrical shock protection class | Class II conforming to IEC 60536
12642 | XVDLS6B3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
12643 | XVDLS6B3 | Offer Sustainability | Sustainable offer status | Green Premium product
12644 | XVDLS6B3 | Offer Sustainability | REACh Regulation | REACh Declaration
12645 | XVDLS6B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12646 | XVDLS6B3 | Offer Sustainability | Mercury free | Yes
12647 | XVDLS6B3 | Offer Sustainability | RoHS exemption information | Yes
12648 | XVDLS6B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12649 | XVDLS6B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12650 | XVDLS6B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12651 | XVDLS6B3 | Contractual warranty | Warranty | 18 months
12652 | XVDLS6B4 | Main | range of product | Harmony XVD Optimum
12653 | XVDLS6B4 | Main | product or component type | Complete miniature beacon
12654 | XVDLS6B4 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12655 | XVDLS6B4 | Main | signalling type | Flashing
12656 | XVDLS6B4 | Main | mounting diameter | 45 mm
12657 | XVDLS6B4 | Main | component name | XVDLS
12658 | XVDLS6B4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12659 | XVDLS6B4 | Main | light source | Integral flash discharge tube, red
12660 | XVDLS6B4 | Main | bulb type | Flash discharge tube
12661 | XVDLS6B4 | Main | [Us] rated supply voltage | 24 V AC/DC
12662 | XVDLS6B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12663 | XVDLS6B4 | Complementary | cable entry | 1 entry tapped for Pg 7
12664 | XVDLS6B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12665 | XVDLS6B4 | Complementary | current consumption | < 145 mA DC < 90 mA AC
12666 | XVDLS6B4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
12667 | XVDLS6B4 | Complementary | flash energy | 1 J
12668 | XVDLS6B4 | Complementary | CAD overall width | 45 mm
12669 | XVDLS6B4 | Complementary | CAD overall height | 104 mm
12670 | XVDLS6B4 | Complementary | CAD overall depth | 45 mm
12671 | XVDLS6B4 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
12672 | XVDLS6B4 | Complementary | net weight | 0.085 kg
12673 | XVDLS6B4 | Environment | product certifications | UL CSA
12674 | XVDLS6B4 | Environment | standards | EN/IEC 60947-5-1
12675 | XVDLS6B4 | Environment | protective treatment | TC
12676 | XVDLS6B4 | Environment | ambient air temperature for operation | -10…50 °C
12677 | XVDLS6B4 | Environment | ambient air temperature for storage | -40…70 °C
12678 | XVDLS6B4 | Environment | electrical shock protection class | Class II conforming to IEC 60536
12679 | XVDLS6B4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
12680 | XVDLS6B4 | Packing Units | Package 1 Weight | 101.9 g
12681 | XVDLS6B4 | Offer Sustainability | Sustainable offer status | Green Premium product
12682 | XVDLS6B4 | Offer Sustainability | REACh Regulation | REACh Declaration
12683 | XVDLS6B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12684 | XVDLS6B4 | Offer Sustainability | Mercury free | Yes
12685 | XVDLS6B4 | Offer Sustainability | RoHS exemption information | Yes
12686 | XVDLS6B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12687 | XVDLS6B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12688 | XVDLS6B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12689 | XVDLS6B4 | Contractual warranty | Warranty | 18 months
12690 | XVDLS6B5 | Main | range of product | Harmony XVD Optimum
12691 | XVDLS6B5 | Main | product or component type | Complete miniature beacon
12692 | XVDLS6B5 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12693 | XVDLS6B5 | Main | signalling type | Flashing
12694 | XVDLS6B5 | Main | mounting diameter | 45 mm
12695 | XVDLS6B5 | Main | component name | XVDLS
12696 | XVDLS6B5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12697 | XVDLS6B5 | Main | light source | Integral flash discharge tube, orange
12698 | XVDLS6B5 | Main | bulb type | Flash discharge tube
12699 | XVDLS6B5 | Main | [Us] rated supply voltage | 24 V AC/DC
12700 | XVDLS6B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12701 | XVDLS6B5 | Complementary | cable entry | 1 entry tapped for Pg 7
12702 | XVDLS6B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12703 | XVDLS6B5 | Complementary | current consumption | < 145 mA DC < 90 mA AC
12704 | XVDLS6B5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
12705 | XVDLS6B5 | Complementary | flash energy | 1 J
12706 | XVDLS6B5 | Complementary | CAD overall width | 45 mm
12707 | XVDLS6B5 | Complementary | CAD overall height | 104 mm
12708 | XVDLS6B5 | Complementary | CAD overall depth | 45 mm
12709 | XVDLS6B5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
12710 | XVDLS6B5 | Complementary | net weight | 0.085 kg
12711 | XVDLS6B5 | Environment | product certifications | CSA UL
12712 | XVDLS6B5 | Environment | standards | EN/IEC 60947-5-1
12713 | XVDLS6B5 | Environment | protective treatment | TC
12714 | XVDLS6B5 | Environment | ambient air temperature for operation | -10…50 °C
12715 | XVDLS6B5 | Environment | ambient air temperature for storage | -40…70 °C
12716 | XVDLS6B5 | Environment | electrical shock protection class | Class II conforming to IEC 60536
12717 | XVDLS6B5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
12718 | XVDLS6B5 | Packing Units | Package 1 Weight | 104 g
12719 | XVDLS6B5 | Offer Sustainability | Sustainable offer status | Green Premium product
12720 | XVDLS6B5 | Offer Sustainability | REACh Regulation | REACh Declaration
12721 | XVDLS6B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12722 | XVDLS6B5 | Offer Sustainability | Mercury free | Yes
12723 | XVDLS6B5 | Offer Sustainability | RoHS exemption information | Yes
12724 | XVDLS6B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12725 | XVDLS6B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12726 | XVDLS6B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12727 | XVDLS6B5 | Contractual warranty | Warranty | 18 months
12728 | XVDLS6B6 | Main | range of product | Harmony XVD Optimum
12729 | XVDLS6B6 | Main | product or component type | Complete miniature beacon
12730 | XVDLS6B6 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12731 | XVDLS6B6 | Main | signalling type | Flashing
12732 | XVDLS6B6 | Main | mounting diameter | 45 mm
12733 | XVDLS6B6 | Main | component name | XVDLS
12734 | XVDLS6B6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12735 | XVDLS6B6 | Main | light source | Integral flash discharge tube, blue
12736 | XVDLS6B6 | Main | bulb type | Flash discharge tube
12737 | XVDLS6B6 | Main | [Us] rated supply voltage | 24 V AC/DC
12738 | XVDLS6B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12739 | XVDLS6B6 | Complementary | cable entry | 1 entry tapped for Pg 7
12740 | XVDLS6B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12741 | XVDLS6B6 | Complementary | current consumption | < 145 mA DC < 90 mA AC
12742 | XVDLS6B6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
12743 | XVDLS6B6 | Complementary | flash energy | 1 J
12744 | XVDLS6B6 | Complementary | CAD overall width | 45 mm
12745 | XVDLS6B6 | Complementary | CAD overall height | 104 mm
12746 | XVDLS6B6 | Complementary | CAD overall depth | 45 mm
12747 | XVDLS6B6 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
12748 | XVDLS6B6 | Complementary | net weight | 0.085 kg
12749 | XVDLS6B6 | Environment | product certifications | CSA UL
12750 | XVDLS6B6 | Environment | standards | EN/IEC 60947-5-1
12751 | XVDLS6B6 | Environment | protective treatment | TC
12752 | XVDLS6B6 | Environment | ambient air temperature for operation | -10…50 °C
12753 | XVDLS6B6 | Environment | ambient air temperature for storage | -40…70 °C
12754 | XVDLS6B6 | Environment | electrical shock protection class | Class II conforming to IEC 60536
12755 | XVDLS6B6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
12756 | XVDLS6B6 | Packing Units | Package 1 Weight | 109 g
12757 | XVDLS6B6 | Offer Sustainability | Sustainable offer status | Green Premium product
12758 | XVDLS6B6 | Offer Sustainability | REACh Regulation | REACh Declaration
12759 | XVDLS6B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12760 | XVDLS6B6 | Offer Sustainability | Mercury free | Yes
12761 | XVDLS6B6 | Offer Sustainability | RoHS exemption information | Yes
12762 | XVDLS6B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12763 | XVDLS6B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12764 | XVDLS6B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12765 | XVDLS6B6 | Contractual warranty | Warranty | 18 months
12766 | XVDLS6B7 | Main | range of product | Harmony XVD Optimum
12767 | XVDLS6B7 | Main | product or component type | Complete miniature beacon
12768 | XVDLS6B7 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12769 | XVDLS6B7 | Main | signalling type | Flashing
12770 | XVDLS6B7 | Main | mounting diameter | 45 mm
12771 | XVDLS6B7 | Main | component name | XVDLS
12772 | XVDLS6B7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12773 | XVDLS6B7 | Main | light source | Integral flash discharge tube, clear
12774 | XVDLS6B7 | Main | bulb type | Flash discharge tube
12775 | XVDLS6B7 | Main | [Us] rated supply voltage | 24 V AC/DC
12776 | XVDLS6B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12777 | XVDLS6B7 | Complementary | cable entry | 1 entry tapped for Pg 7
12778 | XVDLS6B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12779 | XVDLS6B7 | Complementary | current consumption | < 145 mA DC < 90 mA AC
12780 | XVDLS6B7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
12781 | XVDLS6B7 | Complementary | flash energy | 1 J
12782 | XVDLS6B7 | Complementary | illuminating intensity | 1.4 cd
12783 | XVDLS6B7 | Complementary | CAD overall width | 45 mm
12784 | XVDLS6B7 | Complementary | CAD overall height | 104 mm
12785 | XVDLS6B7 | Complementary | CAD overall depth | 45 mm
12786 | XVDLS6B7 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
12787 | XVDLS6B7 | Complementary | net weight | 0.085 kg
12788 | XVDLS6B7 | Environment | product certifications | UL CSA
12789 | XVDLS6B7 | Environment | standards | EN/IEC 60947-5-1
12790 | XVDLS6B7 | Environment | protective treatment | TC
12791 | XVDLS6B7 | Environment | ambient air temperature for operation | -10…50 °C
12792 | XVDLS6B7 | Environment | ambient air temperature for storage | -40…70 °C
12793 | XVDLS6B7 | Environment | electrical shock protection class | Class II conforming to IEC 60536
12794 | XVDLS6B7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
12795 | XVDLS6B7 | Packing Units | Package 1 Weight | 110 g
12796 | XVDLS6B7 | Offer Sustainability | Sustainable offer status | Green Premium product
12797 | XVDLS6B7 | Offer Sustainability | REACh Regulation | REACh Declaration
12798 | XVDLS6B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12799 | XVDLS6B7 | Offer Sustainability | Mercury free | Yes
12800 | XVDLS6B7 | Offer Sustainability | RoHS exemption information | Yes
12801 | XVDLS6B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12802 | XVDLS6B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12803 | XVDLS6B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12804 | XVDLS6B7 | Contractual warranty | Warranty | 18 months
12805 | XVDLS6B8 | Main | range of product | Harmony XVD Optimum
12806 | XVDLS6B8 | Main | product or component type | Complete miniature beacon
12807 | XVDLS6B8 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12808 | XVDLS6B8 | Main | signalling type | Flashing
12809 | XVDLS6B8 | Main | mounting diameter | 45 mm
12810 | XVDLS6B8 | Main | component name | XVDLS
12811 | XVDLS6B8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12812 | XVDLS6B8 | Main | light source | Integral flash discharge tube, yellow
12813 | XVDLS6B8 | Main | bulb type | Flash discharge tube
12814 | XVDLS6B8 | Main | [Us] rated supply voltage | 24 V AC/DC
12815 | XVDLS6B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12816 | XVDLS6B8 | Complementary | cable entry | 1 entry tapped for Pg 7
12817 | XVDLS6B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12818 | XVDLS6B8 | Complementary | current consumption | < 145 mA DC < 90 mA AC
12819 | XVDLS6B8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
12820 | XVDLS6B8 | Complementary | flash energy | 1 J
12821 | XVDLS6B8 | Complementary | CAD overall width | 45 mm
12822 | XVDLS6B8 | Complementary | CAD overall height | 104 mm
12823 | XVDLS6B8 | Complementary | CAD overall depth | 45 mm
12824 | XVDLS6B8 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
12825 | XVDLS6B8 | Complementary | net weight | 0.085 kg
12826 | XVDLS6B8 | Environment | product certifications | CSA UL
12827 | XVDLS6B8 | Environment | standards | EN/IEC 60947-5-1
12828 | XVDLS6B8 | Environment | protective treatment | TC
12829 | XVDLS6B8 | Environment | ambient air temperature for operation | -10…50 °C
12830 | XVDLS6B8 | Environment | ambient air temperature for storage | -40…70 °C
12831 | XVDLS6B8 | Environment | electrical shock protection class | Class II conforming to IEC 60536
12832 | XVDLS6B8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
12833 | XVDLS6B8 | Packing Units | Package 1 Weight | 0.102 kg
12834 | XVDLS6B8 | Offer Sustainability | Sustainable offer status | Green Premium product
12835 | XVDLS6B8 | Offer Sustainability | REACh Regulation | REACh Declaration
12836 | XVDLS6B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12837 | XVDLS6B8 | Offer Sustainability | Mercury free | Yes
12838 | XVDLS6B8 | Offer Sustainability | RoHS exemption information | Yes
12839 | XVDLS6B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12840 | XVDLS6B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12841 | XVDLS6B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12842 | XVDLS6B8 | Contractual warranty | Warranty | 18 months
12843 | XVDLS6G3 | Main | range of product | Harmony XVD Optimum
12844 | XVDLS6G3 | Main | product or component type | Complete miniature beacon
12845 | XVDLS6G3 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12846 | XVDLS6G3 | Main | signalling type | Flashing
12847 | XVDLS6G3 | Main | mounting diameter | 45 mm
12848 | XVDLS6G3 | Main | component name | XVDLS
12849 | XVDLS6G3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12850 | XVDLS6G3 | Main | light source | Integral flash discharge tube, green
12851 | XVDLS6G3 | Main | bulb type | Flash discharge tube
12852 | XVDLS6G3 | Main | [Us] rated supply voltage | 120 V AC
12853 | XVDLS6G3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12854 | XVDLS6G3 | Complementary | cable entry | 1 entry tapped for Pg 7
12855 | XVDLS6G3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12856 | XVDLS6G3 | Complementary | current consumption | < 35 mA AC
12857 | XVDLS6G3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
12858 | XVDLS6G3 | Complementary | flash energy | 1 J
12859 | XVDLS6G3 | Complementary | CAD overall width | 45 mm
12860 | XVDLS6G3 | Complementary | CAD overall height | 104 mm
12861 | XVDLS6G3 | Complementary | CAD overall depth | 45 mm
12862 | XVDLS6G3 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
12863 | XVDLS6G3 | Complementary | net weight | 0.085 kg
12864 | XVDLS6G3 | Environment | product certifications | CSA UL
12865 | XVDLS6G3 | Environment | standards | EN/IEC 60947-5-1
12866 | XVDLS6G3 | Environment | protective treatment | TC
12867 | XVDLS6G3 | Environment | ambient air temperature for operation | -10…50 °C
12868 | XVDLS6G3 | Environment | ambient air temperature for storage | -40…70 °C
12869 | XVDLS6G3 | Environment | electrical shock protection class | Class II conforming to IEC 60536
12870 | XVDLS6G3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
12871 | XVDLS6G3 | Packing Units | Package 1 Weight | 106 g
12872 | XVDLS6G3 | Offer Sustainability | Sustainable offer status | Green Premium product
12873 | XVDLS6G3 | Offer Sustainability | REACh Regulation | REACh Declaration
12874 | XVDLS6G3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12875 | XVDLS6G3 | Offer Sustainability | Mercury free | Yes
12876 | XVDLS6G3 | Offer Sustainability | RoHS exemption information | Yes
12877 | XVDLS6G3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12878 | XVDLS6G3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12879 | XVDLS6G3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12880 | XVDLS6G3 | Contractual warranty | Warranty | 18 months
12881 | XVDLS6G4 | Main | range of product | Harmony XVD Optimum
12882 | XVDLS6G4 | Main | product or component type | Complete miniature beacon
12883 | XVDLS6G4 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12884 | XVDLS6G4 | Main | signalling type | Flashing
12885 | XVDLS6G4 | Main | mounting diameter | 45 mm
12886 | XVDLS6G4 | Main | component name | XVDLS
12887 | XVDLS6G4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12888 | XVDLS6G4 | Main | light source | Integral flash discharge tube, red
12889 | XVDLS6G4 | Main | bulb type | Flash discharge tube
12890 | XVDLS6G4 | Main | [Us] rated supply voltage | 120 V AC
12891 | XVDLS6G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12892 | XVDLS6G4 | Complementary | cable entry | 1 entry tapped for Pg 7
12893 | XVDLS6G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12894 | XVDLS6G4 | Complementary | current consumption | < 35 mA AC
12895 | XVDLS6G4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
12896 | XVDLS6G4 | Complementary | flash energy | 1 J
12897 | XVDLS6G4 | Complementary | CAD overall width | 45 mm
12898 | XVDLS6G4 | Complementary | CAD overall height | 104 mm
12899 | XVDLS6G4 | Complementary | CAD overall depth | 45 mm
12900 | XVDLS6G4 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
12901 | XVDLS6G4 | Complementary | net weight | 0.085 kg
12902 | XVDLS6G4 | Environment | product certifications | CSA UL
12903 | XVDLS6G4 | Environment | standards | EN/IEC 60947-5-1
12904 | XVDLS6G4 | Environment | protective treatment | TC
12905 | XVDLS6G4 | Environment | ambient air temperature for storage | -40…70 °C
12906 | XVDLS6G4 | Environment | electrical shock protection class | Class II conforming to IEC 60536
12907 | XVDLS6G4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
12908 | XVDLS6G4 | Packing Units | Package 1 Weight | 105 g
12909 | XVDLS6G4 | Offer Sustainability | Sustainable offer status | Green Premium product
12910 | XVDLS6G4 | Offer Sustainability | REACh Regulation | REACh Declaration
12911 | XVDLS6G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12912 | XVDLS6G4 | Offer Sustainability | Mercury free | Yes
12913 | XVDLS6G4 | Offer Sustainability | RoHS exemption information | Yes
12914 | XVDLS6G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12915 | XVDLS6G4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12916 | XVDLS6G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12917 | XVDLS6G4 | Contractual warranty | Warranty | 18 months
12918 | XVDLS6G5 | Main | range of product | Harmony XVD Optimum
12919 | XVDLS6G5 | Main | product or component type | Complete miniature beacon
12920 | XVDLS6G5 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12921 | XVDLS6G5 | Main | signalling type | Flashing
12922 | XVDLS6G5 | Main | mounting diameter | 45 mm
12923 | XVDLS6G5 | Main | component name | XVDLS
12924 | XVDLS6G5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12925 | XVDLS6G5 | Main | light source | Integral flash discharge tube, orange
12926 | XVDLS6G5 | Main | bulb type | Flash discharge tube
12927 | XVDLS6G5 | Main | [Us] rated supply voltage | 120 V AC
12928 | XVDLS6G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12929 | XVDLS6G5 | Complementary | cable entry | 1 entry tapped for Pg 7
12930 | XVDLS6G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12931 | XVDLS6G5 | Complementary | current consumption | < 35 mA AC
12932 | XVDLS6G5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
12933 | XVDLS6G5 | Complementary | flash energy | 1 J
12934 | XVDLS6G5 | Complementary | CAD overall width | 45 mm
12935 | XVDLS6G5 | Complementary | CAD overall height | 104 mm
12936 | XVDLS6G5 | Complementary | CAD overall depth | 45 mm
12937 | XVDLS6G5 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
12938 | XVDLS6G5 | Complementary | net weight | 0.085 kg
12939 | XVDLS6G5 | Environment | product certifications | CSA UL
12940 | XVDLS6G5 | Environment | standards | EN/IEC 60947-5-1
12941 | XVDLS6G5 | Environment | protective treatment | TC
12942 | XVDLS6G5 | Environment | ambient air temperature for storage | -40…70 °C
12943 | XVDLS6G5 | Environment | electrical shock protection class | Class II conforming to IEC 60536
12944 | XVDLS6G5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
12945 | XVDLS6G5 | Offer Sustainability | Sustainable offer status | Green Premium product
12946 | XVDLS6G5 | Offer Sustainability | REACh Regulation | REACh Declaration
12947 | XVDLS6G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12948 | XVDLS6G5 | Offer Sustainability | Mercury free | Yes
12949 | XVDLS6G5 | Offer Sustainability | RoHS exemption information | Yes
12950 | XVDLS6G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12951 | XVDLS6G5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12952 | XVDLS6G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12953 | XVDLS6G5 | Contractual warranty | Warranty | 18 months
12954 | XVDLS6G6 | Main | range of product | Harmony XVD Optimum
12955 | XVDLS6G6 | Main | product or component type | Complete miniature beacon
12956 | XVDLS6G6 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12957 | XVDLS6G6 | Main | signalling type | Flashing
12958 | XVDLS6G6 | Main | mounting diameter | 45 mm
12959 | XVDLS6G6 | Main | component name | XVDLS
12960 | XVDLS6G6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12961 | XVDLS6G6 | Main | light source | Integral flash discharge tube, blue
12962 | XVDLS6G6 | Main | bulb type | Flash discharge tube
12963 | XVDLS6G6 | Main | [Us] rated supply voltage | 120 V AC
12964 | XVDLS6G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
12965 | XVDLS6G6 | Complementary | cable entry | 1 entry tapped for Pg 7
12966 | XVDLS6G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
12967 | XVDLS6G6 | Complementary | current consumption | < 35 mA AC
12968 | XVDLS6G6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
12969 | XVDLS6G6 | Complementary | flash energy | 1 J
12970 | XVDLS6G6 | Complementary | CAD overall width | 45 mm
12971 | XVDLS6G6 | Complementary | CAD overall height | 104 mm
12972 | XVDLS6G6 | Complementary | CAD overall depth | 45 mm
12973 | XVDLS6G6 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
12974 | XVDLS6G6 | Complementary | net weight | 0.085 kg
12975 | XVDLS6G6 | Environment | product certifications | CSA UL
12976 | XVDLS6G6 | Environment | standards | EN/IEC 60947-5-1
12977 | XVDLS6G6 | Environment | protective treatment | TC
12978 | XVDLS6G6 | Environment | ambient air temperature for storage | -40…70 °C
12979 | XVDLS6G6 | Environment | electrical shock protection class | Class II conforming to IEC 60536
12980 | XVDLS6G6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
12981 | XVDLS6G6 | Packing Units | Package 1 Weight | 0.106 kg
12982 | XVDLS6G6 | Offer Sustainability | Sustainable offer status | Green Premium product
12983 | XVDLS6G6 | Offer Sustainability | REACh Regulation | REACh Declaration
12984 | XVDLS6G6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
12985 | XVDLS6G6 | Offer Sustainability | Mercury free | Yes
12986 | XVDLS6G6 | Offer Sustainability | RoHS exemption information | Yes
12987 | XVDLS6G6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
12988 | XVDLS6G6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
12989 | XVDLS6G6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
12990 | XVDLS6G6 | Contractual warranty | Warranty | 18 months
12991 | XVDLS6G7 | Main | range of product | Harmony XVD Optimum
12992 | XVDLS6G7 | Main | product or component type | Complete miniature beacon
12993 | XVDLS6G7 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
12994 | XVDLS6G7 | Main | signalling type | Flashing
12995 | XVDLS6G7 | Main | mounting diameter | 45 mm
12996 | XVDLS6G7 | Main | component name | XVDLS
12997 | XVDLS6G7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
12998 | XVDLS6G7 | Main | light source | Integral flash discharge tube, clear
12999 | XVDLS6G7 | Main | bulb type | Flash discharge tube
13000 | XVDLS6G7 | Main | [Us] rated supply voltage | 120 V AC
13001 | XVDLS6G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
13002 | XVDLS6G7 | Complementary | cable entry | 1 entry tapped for Pg 7
13003 | XVDLS6G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13004 | XVDLS6G7 | Complementary | current consumption | < 35 mA AC
13005 | XVDLS6G7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
13006 | XVDLS6G7 | Complementary | flash energy | 1 J
13007 | XVDLS6G7 | Complementary | illuminating intensity | 1.4 cd
13008 | XVDLS6G7 | Complementary | CAD overall width | 45 mm
13009 | XVDLS6G7 | Complementary | CAD overall height | 104 mm
13010 | XVDLS6G7 | Complementary | CAD overall depth | 45 mm
13011 | XVDLS6G7 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
13012 | XVDLS6G7 | Complementary | net weight | 0.085 kg
13013 | XVDLS6G7 | Environment | product certifications | CSA UL
13014 | XVDLS6G7 | Environment | standards | EN/IEC 60947-5-1
13015 | XVDLS6G7 | Environment | protective treatment | TC
13016 | XVDLS6G7 | Environment | ambient air temperature for storage | -40…70 °C
13017 | XVDLS6G7 | Environment | electrical shock protection class | Class II conforming to IEC 60536
13018 | XVDLS6G7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13019 | XVDLS6G7 | Contractual warranty | Warranty | 18 months
13020 | XVDLS6G8 | Main | range of product | Harmony XVD Optimum
13021 | XVDLS6G8 | Main | product or component type | Complete miniature beacon
13022 | XVDLS6G8 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
13023 | XVDLS6G8 | Main | signalling type | Flashing
13024 | XVDLS6G8 | Main | mounting diameter | 45 mm
13025 | XVDLS6G8 | Main | component name | XVDLS
13026 | XVDLS6G8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13027 | XVDLS6G8 | Main | light source | Integral flash discharge tube, yellow
13028 | XVDLS6G8 | Main | bulb type | Flash discharge tube
13029 | XVDLS6G8 | Main | [Us] rated supply voltage | 120 V AC
13030 | XVDLS6G8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
13031 | XVDLS6G8 | Complementary | cable entry | 1 entry tapped for Pg 7
13032 | XVDLS6G8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13033 | XVDLS6G8 | Complementary | current consumption | < 35 mA AC
13034 | XVDLS6G8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
13035 | XVDLS6G8 | Complementary | flash energy | 1 J
13036 | XVDLS6G8 | Complementary | CAD overall width | 45 mm
13037 | XVDLS6G8 | Complementary | CAD overall height | 104 mm
13038 | XVDLS6G8 | Complementary | CAD overall depth | 45 mm
13039 | XVDLS6G8 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
13040 | XVDLS6G8 | Complementary | net weight | 0.085 kg
13041 | XVDLS6G8 | Environment | product certifications | UL CSA
13042 | XVDLS6G8 | Environment | standards | EN/IEC 60947-5-1
13043 | XVDLS6G8 | Environment | protective treatment | TC
13044 | XVDLS6G8 | Environment | ambient air temperature for storage | -40…70 °C
13045 | XVDLS6G8 | Environment | electrical shock protection class | Class II conforming to IEC 60536
13046 | XVDLS6G8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13047 | XVDLS6G8 | Packing Units | Package 1 Weight | 0.106 kg
13048 | XVDLS6G8 | Contractual warranty | Warranty | 18 months
13049 | XVDLS6M3 | Main | range of product | Harmony XVD Optimum
13050 | XVDLS6M3 | Main | product or component type | Complete miniature beacon
13051 | XVDLS6M3 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
13052 | XVDLS6M3 | Main | signalling type | Flashing
13053 | XVDLS6M3 | Main | mounting diameter | 45 mm
13054 | XVDLS6M3 | Main | component name | XVDLS
13055 | XVDLS6M3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13056 | XVDLS6M3 | Main | light source | Integral flash discharge tube, green
13057 | XVDLS6M3 | Main | bulb type | Flash discharge tube
13058 | XVDLS6M3 | Main | [Us] rated supply voltage | 230 V AC
13059 | XVDLS6M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
13060 | XVDLS6M3 | Complementary | cable entry | 1 entry tapped for Pg 7
13061 | XVDLS6M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13062 | XVDLS6M3 | Complementary | current consumption | < 25 mA AC
13063 | XVDLS6M3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13064 | XVDLS6M3 | Complementary | flash energy | 1 J
13065 | XVDLS6M3 | Complementary | CAD overall width | 45 mm
13066 | XVDLS6M3 | Complementary | CAD overall height | 104 mm
13067 | XVDLS6M3 | Complementary | CAD overall depth | 45 mm
13068 | XVDLS6M3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
13069 | XVDLS6M3 | Complementary | net weight | 0.085 kg
13070 | XVDLS6M3 | Environment | product certifications | CSA UL
13071 | XVDLS6M3 | Environment | standards | EN/IEC 60947-5-1
13072 | XVDLS6M3 | Environment | protective treatment | TC
13073 | XVDLS6M3 | Environment | ambient air temperature for storage | -40…70 °C
13074 | XVDLS6M3 | Environment | electrical shock protection class | Class II conforming to IEC 60536
13075 | XVDLS6M3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13076 | XVDLS6M3 | Packing Units | Package 1 Weight | 0.110 kg
13077 | XVDLS6M3 | Offer Sustainability | Sustainable offer status | Green Premium product
13078 | XVDLS6M3 | Offer Sustainability | REACh Regulation | REACh Declaration
13079 | XVDLS6M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
13080 | XVDLS6M3 | Offer Sustainability | Mercury free | Yes
13081 | XVDLS6M3 | Offer Sustainability | RoHS exemption information | Yes
13082 | XVDLS6M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
13083 | XVDLS6M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
13084 | XVDLS6M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
13085 | XVDLS6M3 | Contractual warranty | Warranty | 18 months
13086 | XVDLS6M4 | Main | range of product | Harmony XVD Optimum
13087 | XVDLS6M4 | Main | product or component type | Complete miniature beacon
13088 | XVDLS6M4 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
13089 | XVDLS6M4 | Main | signalling type | Flashing
13090 | XVDLS6M4 | Main | mounting diameter | 45 mm
13091 | XVDLS6M4 | Main | component name | XVDLS
13092 | XVDLS6M4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13093 | XVDLS6M4 | Main | light source | Integral flash discharge tube, red
13094 | XVDLS6M4 | Main | bulb type | Flash discharge tube
13095 | XVDLS6M4 | Main | [Us] rated supply voltage | 230 V AC
13096 | XVDLS6M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
13097 | XVDLS6M4 | Complementary | cable entry | 1 entry tapped for Pg 7
13098 | XVDLS6M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13099 | XVDLS6M4 | Complementary | current consumption | < 25 mA AC
13100 | XVDLS6M4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
13101 | XVDLS6M4 | Complementary | flash energy | 1 J
13102 | XVDLS6M4 | Complementary | CAD overall width | 45 mm
13103 | XVDLS6M4 | Complementary | CAD overall height | 104 mm
13104 | XVDLS6M4 | Complementary | CAD overall depth | 45 mm
13105 | XVDLS6M4 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
13106 | XVDLS6M4 | Complementary | net weight | 0.085 kg
13107 | XVDLS6M4 | Environment | product certifications | UL CSA
13108 | XVDLS6M4 | Environment | standards | EN/IEC 60947-5-1
13109 | XVDLS6M4 | Environment | protective treatment | TC
13110 | XVDLS6M4 | Environment | ambient air temperature for storage | -40…70 °C
13111 | XVDLS6M4 | Environment | electrical shock protection class | Class II conforming to IEC 60536
13112 | XVDLS6M4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13113 | XVDLS6M4 | Packing Units | Package 1 Weight | 100 g
13114 | XVDLS6M4 | Packing Units | Package 2 Weight | 1.407 kg
13115 | XVDLS6M4 | Offer Sustainability | Sustainable offer status | Green Premium product
13116 | XVDLS6M4 | Offer Sustainability | REACh Regulation | REACh Declaration
13117 | XVDLS6M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
13118 | XVDLS6M4 | Offer Sustainability | Mercury free | Yes
13119 | XVDLS6M4 | Offer Sustainability | RoHS exemption information | Yes
13120 | XVDLS6M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
13121 | XVDLS6M4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
13122 | XVDLS6M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
13123 | XVDLS6M4 | Contractual warranty | Warranty | 18 months
13124 | XVDLS6M5 | Main | range of product | Harmony XVD Optimum
13125 | XVDLS6M5 | Main | product or component type | Complete miniature beacon
13126 | XVDLS6M5 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
13127 | XVDLS6M5 | Main | signalling type | Flashing
13128 | XVDLS6M5 | Main | mounting diameter | 45 mm
13129 | XVDLS6M5 | Main | component name | XVDLS
13130 | XVDLS6M5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13131 | XVDLS6M5 | Main | light source | Integral flash discharge tube, orange
13132 | XVDLS6M5 | Main | bulb type | Flash discharge tube
13133 | XVDLS6M5 | Main | [Us] rated supply voltage | 230 V AC
13134 | XVDLS6M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
13135 | XVDLS6M5 | Complementary | cable entry | 1 entry tapped for Pg 7
13136 | XVDLS6M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13137 | XVDLS6M5 | Complementary | current consumption | < 25 mA AC
13138 | XVDLS6M5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
13139 | XVDLS6M5 | Complementary | flash energy | 1 J
13140 | XVDLS6M5 | Complementary | CAD overall width | 45 mm
13141 | XVDLS6M5 | Complementary | CAD overall height | 104 mm
13142 | XVDLS6M5 | Complementary | CAD overall depth | 45 mm
13143 | XVDLS6M5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
13144 | XVDLS6M5 | Complementary | net weight | 0.085 kg
13145 | XVDLS6M5 | Environment | product certifications | CSA UL
13146 | XVDLS6M5 | Environment | standards | EN/IEC 60947-5-1
13147 | XVDLS6M5 | Environment | protective treatment | TC
13148 | XVDLS6M5 | Environment | ambient air temperature for storage | -40…70 °C
13149 | XVDLS6M5 | Environment | electrical shock protection class | Class II conforming to IEC 60536
13150 | XVDLS6M5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13151 | XVDLS6M5 | Packing Units | Package 1 Weight | 100 g
13152 | XVDLS6M5 | Packing Units | Package 2 Weight | 1.394 kg
13153 | XVDLS6M5 | Offer Sustainability | Sustainable offer status | Green Premium product
13154 | XVDLS6M5 | Offer Sustainability | REACh Regulation | REACh Declaration
13155 | XVDLS6M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
13156 | XVDLS6M5 | Offer Sustainability | Mercury free | Yes
13157 | XVDLS6M5 | Offer Sustainability | RoHS exemption information | Yes
13158 | XVDLS6M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
13159 | XVDLS6M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
13160 | XVDLS6M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
13161 | XVDLS6M5 | Contractual warranty | Warranty | 18 months
13162 | XVDLS6M6 | Main | range of product | Harmony XVD Optimum
13163 | XVDLS6M6 | Main | product or component type | Complete miniature beacon
13164 | XVDLS6M6 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
13165 | XVDLS6M6 | Main | signalling type | Flashing
13166 | XVDLS6M6 | Main | mounting diameter | 45 mm
13167 | XVDLS6M6 | Main | component name | XVDLS
13168 | XVDLS6M6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13169 | XVDLS6M6 | Main | light source | Integral flash discharge tube, blue
13170 | XVDLS6M6 | Main | bulb type | Flash discharge tube
13171 | XVDLS6M6 | Main | [Us] rated supply voltage | 230 V AC
13172 | XVDLS6M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
13173 | XVDLS6M6 | Complementary | cable entry | 1 entry tapped for Pg 7
13174 | XVDLS6M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13175 | XVDLS6M6 | Complementary | current consumption | < 25 mA AC
13176 | XVDLS6M6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13177 | XVDLS6M6 | Complementary | flash energy | 1 J
13178 | XVDLS6M6 | Complementary | CAD overall width | 45 mm
13179 | XVDLS6M6 | Complementary | CAD overall height | 104 mm
13180 | XVDLS6M6 | Complementary | CAD overall depth | 45 mm
13181 | XVDLS6M6 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
13182 | XVDLS6M6 | Complementary | net weight | 0.085 kg
13183 | XVDLS6M6 | Environment | product certifications | CSA UL
13184 | XVDLS6M6 | Environment | standards | EN/IEC 60947-5-1
13185 | XVDLS6M6 | Environment | protective treatment | TC
13186 | XVDLS6M6 | Environment | ambient air temperature for storage | -40…70 °C
13187 | XVDLS6M6 | Environment | electrical shock protection class | Class II conforming to IEC 60536
13188 | XVDLS6M6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13189 | XVDLS6M6 | Packing Units | Package 1 Weight | 101 g
13190 | XVDLS6M6 | Offer Sustainability | Sustainable offer status | Green Premium product
13191 | XVDLS6M6 | Offer Sustainability | REACh Regulation | REACh Declaration
13192 | XVDLS6M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
13193 | XVDLS6M6 | Offer Sustainability | Mercury free | Yes
13194 | XVDLS6M6 | Offer Sustainability | RoHS exemption information | Yes
13195 | XVDLS6M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
13196 | XVDLS6M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
13197 | XVDLS6M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
13198 | XVDLS6M6 | Contractual warranty | Warranty | 18 months
13199 | XVDLS6M7 | Main | range of product | Harmony XVD Optimum
13200 | XVDLS6M7 | Main | product or component type | Complete miniature beacon
13201 | XVDLS6M7 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
13202 | XVDLS6M7 | Main | signalling type | Flashing
13203 | XVDLS6M7 | Main | mounting diameter | 45 mm
13204 | XVDLS6M7 | Main | component name | XVDLS
13205 | XVDLS6M7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13206 | XVDLS6M7 | Main | light source | Integral flash discharge tube, clear
13207 | XVDLS6M7 | Main | bulb type | Flash discharge tube
13208 | XVDLS6M7 | Main | [Us] rated supply voltage | 230 V AC
13209 | XVDLS6M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
13210 | XVDLS6M7 | Complementary | cable entry | 1 entry tapped for Pg 7
13211 | XVDLS6M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13212 | XVDLS6M7 | Complementary | current consumption | < 25 mA AC
13213 | XVDLS6M7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13214 | XVDLS6M7 | Complementary | flash energy | 1 J
13215 | XVDLS6M7 | Complementary | illuminating intensity | 1.4 cd
13216 | XVDLS6M7 | Complementary | CAD overall width | 45 mm
13217 | XVDLS6M7 | Complementary | CAD overall height | 104 mm
13218 | XVDLS6M7 | Complementary | CAD overall depth | 45 mm
13219 | XVDLS6M7 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
13220 | XVDLS6M7 | Complementary | net weight | 0.085 kg
13221 | XVDLS6M7 | Environment | product certifications | UL CSA
13222 | XVDLS6M7 | Environment | standards | EN/IEC 60947-5-1
13223 | XVDLS6M7 | Environment | protective treatment | TC
13224 | XVDLS6M7 | Environment | ambient air temperature for storage | -40…70 °C
13225 | XVDLS6M7 | Environment | electrical shock protection class | Class II conforming to IEC 60536
13226 | XVDLS6M7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13227 | XVDLS6M7 | Packing Units | Package 1 Weight | 0.110 kg
13228 | XVDLS6M7 | Offer Sustainability | Sustainable offer status | Green Premium product
13229 | XVDLS6M7 | Offer Sustainability | REACh Regulation | REACh Declaration
13230 | XVDLS6M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
13231 | XVDLS6M7 | Offer Sustainability | Mercury free | Yes
13232 | XVDLS6M7 | Offer Sustainability | RoHS exemption information | Yes
13233 | XVDLS6M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
13234 | XVDLS6M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
13235 | XVDLS6M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
13236 | XVDLS6M7 | Contractual warranty | Warranty | 18 months
13237 | XVDLS6M8 | Main | range of product | Harmony XVD Optimum
13238 | XVDLS6M8 | Main | product or component type | Complete miniature beacon
13239 | XVDLS6M8 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
13240 | XVDLS6M8 | Main | signalling type | Flashing
13241 | XVDLS6M8 | Main | mounting diameter | 45 mm
13242 | XVDLS6M8 | Main | component name | XVDLS
13243 | XVDLS6M8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13244 | XVDLS6M8 | Main | light source | Integral flash discharge tube, yellow
13245 | XVDLS6M8 | Main | bulb type | Flash discharge tube
13246 | XVDLS6M8 | Main | [Us] rated supply voltage | 230 V AC
13247 | XVDLS6M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
13248 | XVDLS6M8 | Complementary | cable entry | 1 entry tapped for Pg 7
13249 | XVDLS6M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13250 | XVDLS6M8 | Complementary | current consumption | < 25 mA AC
13251 | XVDLS6M8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13252 | XVDLS6M8 | Complementary | flash energy | 1 J
13253 | XVDLS6M8 | Complementary | CAD overall width | 45 mm
13254 | XVDLS6M8 | Complementary | CAD overall height | 104 mm
13255 | XVDLS6M8 | Complementary | CAD overall depth | 45 mm
13256 | XVDLS6M8 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
13257 | XVDLS6M8 | Complementary | net weight | 0.085 kg
13258 | XVDLS6M8 | Environment | product certifications | CSA UL
13259 | XVDLS6M8 | Environment | standards | EN/IEC 60947-5-1
13260 | XVDLS6M8 | Environment | protective treatment | TC
13261 | XVDLS6M8 | Environment | ambient air temperature for storage | -40…70 °C
13262 | XVDLS6M8 | Environment | electrical shock protection class | Class II conforming to IEC 60536
13263 | XVDLS6M8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13264 | XVDLS6M8 | Packing Units | Package 1 Weight | 102 g
13265 | XVDLS6M8 | Offer Sustainability | Sustainable offer status | Green Premium product
13266 | XVDLS6M8 | Offer Sustainability | REACh Regulation | REACh Declaration
13267 | XVDLS6M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
13268 | XVDLS6M8 | Offer Sustainability | Mercury free | Yes
13269 | XVDLS6M8 | Offer Sustainability | RoHS exemption information | Yes
13270 | XVDLS6M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
13271 | XVDLS6M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
13272 | XVDLS6M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
13273 | XVDLS6M8 | Contractual warranty | Warranty | 18 months
13274 | XVDBR6 | Main | range of product | Harmony XVD Application
13275 | XVDBR6 | Main | product or component type | Complete pre-cabled beacon
13276 | XVDBR6 | Main | beacon or indicator bank unit type | 1 illuminated unit
13277 | XVDBR6 | Main | signalling type | Flashing
13278 | XVDBR6 | Main | component name | XVD
13279 | XVDBR6 | Main | light source | Flash discharge tube, red
13280 | XVDBR6 | Main | [Us] rated supply voltage | 24 V AC/DC
13281 | XVDBR6 | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13282 | XVDBR6 | Complementary | mounting diameter | 70 mm
13283 | XVDBR6 | Complementary | flash energy | 5 J
13284 | XVDBR6 | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13285 | XVDBR6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13286 | XVDBR6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13287 | XVDBR6 | Complementary | current consumption | < 350 mA DC < 550 mA AC
13288 | XVDBR6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13289 | XVDBR6 | Complementary | flashing frequency | 1 Hz
13290 | XVDBR6 | Complementary | net weight | 0.6 kg
13291 | XVDBR6 | Environment | standards | EN/IEC 60947-5-1
13292 | XVDBR6 | Environment | product certifications | CSA GOST UL
13293 | XVDBR6 | Environment | protective treatment | TC
13294 | XVDBR6 | Environment | ambient air temperature for operation | -25…50 °C
13295 | XVDBR6 | Environment | ambient air temperature for storage | -40…70 °C
13296 | XVDBR6 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13297 | XVDBR6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13298 | XVDBR6 | Contractual warranty | Warranty | 18 months
13299 | XVDBA6 | Main | range of product | Harmony XVD Application
13300 | XVDBA6 | Main | product or component type | Complete pre-cabled beacon
13301 | XVDBA6 | Main | beacon or indicator bank unit type | 1 illuminated unit
13302 | XVDBA6 | Main | signalling type | Flashing
13303 | XVDBA6 | Main | component name | XVD
13304 | XVDBA6 | Main | light source | Flash discharge tube, orange
13305 | XVDBA6 | Main | [Us] rated supply voltage | 24 V AC/DC
13306 | XVDBA6 | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13307 | XVDBA6 | Complementary | mounting diameter | 70 mm
13308 | XVDBA6 | Complementary | flash energy | 5 J
13309 | XVDBA6 | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13310 | XVDBA6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13311 | XVDBA6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13312 | XVDBA6 | Complementary | current consumption | < 350 mA DC < 550 mA AC
13313 | XVDBA6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
13314 | XVDBA6 | Complementary | flashing frequency | 1 Hz
13315 | XVDBA6 | Complementary | net weight | 0.6 kg
13316 | XVDBA6 | Environment | standards | EN/IEC 60947-5-1
13317 | XVDBA6 | Environment | product certifications | UL CSA GOST
13318 | XVDBA6 | Environment | protective treatment | TC
13319 | XVDBA6 | Environment | ambient air temperature for operation | -25…50 °C
13320 | XVDBA6 | Environment | ambient air temperature for storage | -40…70 °C
13321 | XVDBA6 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13322 | XVDBA6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13323 | XVDBA6 | Contractual warranty | Warranty | 18 months
13324 | XVDMR6 | Main | range of product | Harmony XVD Application
13325 | XVDMR6 | Main | product or component type | Complete pre-cabled beacon
13326 | XVDMR6 | Main | beacon or indicator bank unit type | 1 illuminated unit
13327 | XVDMR6 | Main | signalling type | Flashing
13328 | XVDMR6 | Main | component name | XVD
13329 | XVDMR6 | Main | light source | Flash discharge tube, red
13330 | XVDMR6 | Main | [Us] rated supply voltage | 230 V AC
13331 | XVDMR6 | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13332 | XVDMR6 | Complementary | mounting diameter | 70 mm
13333 | XVDMR6 | Complementary | flash energy | 5 J
13334 | XVDMR6 | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13335 | XVDMR6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13336 | XVDMR6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13337 | XVDMR6 | Complementary | current consumption | < 105 mA AC
13338 | XVDMR6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
13339 | XVDMR6 | Complementary | flashing frequency | 1 Hz
13340 | XVDMR6 | Complementary | net weight | 0.6 kg
13341 | XVDMR6 | Environment | standards | EN/IEC 60947-5-1
13342 | XVDMR6 | Environment | product certifications | CSA UL GOST
13343 | XVDMR6 | Environment | protective treatment | TC
13344 | XVDMR6 | Environment | ambient air temperature for operation | -25…50 °C
13345 | XVDMR6 | Environment | ambient air temperature for storage | -40…70 °C
13346 | XVDMR6 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13347 | XVDMR6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13348 | XVDMR6 | Contractual warranty | Warranty | 18 months
13349 | XVDMA6 | Main | range of product | Harmony XVD Application
13350 | XVDMA6 | Main | product or component type | Complete pre-cabled beacon
13351 | XVDMA6 | Main | beacon or indicator bank unit type | 1 illuminated unit
13352 | XVDMA6 | Main | signalling type | Flashing
13353 | XVDMA6 | Main | component name | XVD
13354 | XVDMA6 | Main | light source | Flash discharge tube, orange
13355 | XVDMA6 | Main | [Us] rated supply voltage | 230 V AC
13356 | XVDMA6 | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13357 | XVDMA6 | Complementary | mounting diameter | 70 mm
13358 | XVDMA6 | Complementary | flash energy | 5 J
13359 | XVDMA6 | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13360 | XVDMA6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13361 | XVDMA6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13362 | XVDMA6 | Complementary | current consumption | < 105 mA AC
13363 | XVDMA6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13364 | XVDMA6 | Complementary | flashing frequency | 1 Hz
13365 | XVDMA6 | Complementary | net weight | 0.6 kg
13366 | XVDMA6 | Environment | standards | EN/IEC 60947-5-1
13367 | XVDMA6 | Environment | product certifications | CSA GOST UL
13368 | XVDMA6 | Environment | protective treatment | TC
13369 | XVDMA6 | Environment | ambient air temperature for operation | -25…50 °C
13370 | XVDMA6 | Environment | ambient air temperature for storage | -40…70 °C
13371 | XVDMA6 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13372 | XVDMA6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13373 | XVDMA6 | Contractual warranty | Warranty | 18 months
13374 | XVDB2GR | Main | range of product | Harmony XVD Application
13375 | XVDB2GR | Main | product or component type | Complete pre-cabled indicator bank
13376 | XVDB2GR | Main | beacon or indicator bank unit type | 2 illuminated units
13377 | XVDB2GR | Main | component name | XVD
13378 | XVDB2GR | Main | light source | Green LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling
13379 | XVDB2GR | Main | light block color | Green/red
13380 | XVDB2GR | Main | [Us] rated supply voltage | 24 V AC/DC
13381 | XVDB2GR | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit
13382 | XVDB2GR | Complementary | mounting diameter | 70 mm
13383 | XVDB2GR | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13384 | XVDB2GR | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13385 | XVDB2GR | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13386 | XVDB2GR | Complementary | current consumption | < 47 mA on LED unit
13387 | XVDB2GR | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13388 | XVDB2GR | Complementary | net weight | 0.553 kg
13389 | XVDB2GR | Environment | standards | EN/IEC 60947-5-1
13390 | XVDB2GR | Environment | product certifications | GOST CSA UL
13391 | XVDB2GR | Environment | protective treatment | TC
13392 | XVDB2GR | Environment | ambient air temperature for storage | -40…70 °C
13393 | XVDB2GR | Environment | ambient air temperature for operation | -25…50 °C
13394 | XVDB2GR | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13395 | XVDB2GR | Environment | IP degree of protection | IP40 conforming to IEC 60529
13396 | XVDB2GR | Contractual warranty | Warranty | 18 months
13397 | XVDB2AR | Main | range of product | Harmony XVD Application
13398 | XVDB2AR | Main | product or component type | Complete pre-cabled indicator bank
13399 | XVDB2AR | Main | beacon or indicator bank unit type | 2 illuminated units
13400 | XVDB2AR | Main | component name | XVD
13401 | XVDB2AR | Main | light source | Orange LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling
13402 | XVDB2AR | Main | light block color | Orange/red
13403 | XVDB2AR | Main | [Us] rated supply voltage | 24 V AC/DC
13404 | XVDB2AR | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit
13405 | XVDB2AR | Complementary | mounting diameter | 70 mm
13406 | XVDB2AR | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13407 | XVDB2AR | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13408 | XVDB2AR | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13409 | XVDB2AR | Complementary | current consumption | < 47 mA on LED unit
13410 | XVDB2AR | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13411 | XVDB2AR | Complementary | net weight | 0.553 kg
13412 | XVDB2AR | Environment | standards | EN/IEC 60947-5-1
13413 | XVDB2AR | Environment | product certifications | GOST UL CSA
13414 | XVDB2AR | Environment | protective treatment | TC
13415 | XVDB2AR | Environment | ambient air temperature for storage | -40…70 °C
13416 | XVDB2AR | Environment | ambient air temperature for operation | -25…50 °C
13417 | XVDB2AR | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13418 | XVDB2AR | Environment | IP degree of protection | IP40 conforming to IEC 60529
13419 | XVDB2AR | Contractual warranty | Warranty | 18 months
13420 | XVDB2GR6 | Main | range of product | Harmony XVD Application
13421 | XVDB2GR6 | Main | product or component type | Complete pre-cabled indicator bank
13422 | XVDB2GR6 | Main | beacon or indicator bank unit type | 2 illuminated units
13423 | XVDB2GR6 | Main | component name | XVD
13424 | XVDB2GR6 | Main | light source | Red flash discharge tubeflashing signalling Green LED with BA 15d base steady signalling
13425 | XVDB2GR6 | Main | light block color | Green/red (flashing)
13426 | XVDB2GR6 | Main | [Us] rated supply voltage | 24 V AC/DC
13427 | XVDB2GR6 | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit
13428 | XVDB2GR6 | Complementary | mounting diameter | 70 mm
13429 | XVDB2GR6 | Complementary | flash energy | 5 J
13430 | XVDB2GR6 | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13431 | XVDB2GR6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13432 | XVDB2GR6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13433 | XVDB2GR6 | Complementary | current consumption | < 350 mA on flash discharge tube unit DC < 47 mA on LED unit < 550 mA on flash discharge tube unit AC
13434 | XVDB2GR6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13435 | XVDB2GR6 | Complementary | flashing frequency | 1 Hz
13436 | XVDB2GR6 | Complementary | net weight | 0.755 kg
13437 | XVDB2GR6 | Environment | standards | EN/IEC 60947-5-1
13438 | XVDB2GR6 | Environment | product certifications | UL GOST CSA
13439 | XVDB2GR6 | Environment | protective treatment | TC
13440 | XVDB2GR6 | Environment | ambient air temperature for storage | -40…70 °C
13441 | XVDB2GR6 | Environment | ambient air temperature for operation | -25…50 °C
13442 | XVDB2GR6 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13443 | XVDB2GR6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13444 | XVDB2GR6 | Contractual warranty | Warranty | 18 months
13445 | XVDBSA6 | Main | range of product | Harmony XVD Application
13446 | XVDBSA6 | Main | product or component type | Complete pre-cabled indicator bank
13447 | XVDBSA6 | Main | beacon or indicator bank unit type | 1 illuminated unit + 1 audible buzzer unit
13448 | XVDBSA6 | Main | component name | XVD
13449 | XVDBSA6 | Main | light source | Orange flash discharge tubeflashing signalling
13450 | XVDBSA6 | Main | light block color | Orange (flashing)
13451 | XVDBSA6 | Main | [Us] rated supply voltage | 24 V AC/DC
13452 | XVDBSA6 | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit
13453 | XVDBSA6 | Complementary | mounting diameter | 70 mm
13454 | XVDBSA6 | Complementary | flash energy | 5 J
13455 | XVDBSA6 | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13456 | XVDBSA6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13457 | XVDBSA6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13458 | XVDBSA6 | Complementary | current consumption | < 20 mA on audible unit < 350 mA on flash discharge tube unit DC < 550 mA on flash discharge tube unit AC
13459 | XVDBSA6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13460 | XVDBSA6 | Complementary | fundamental frequency | 2.8 kHz
13461 | XVDBSA6 | Complementary | flashing frequency | 1 Hz
13462 | XVDBSA6 | Complementary | net weight | 0.775 kg
13463 | XVDBSA6 | Environment | standards | EN/IEC 60947-5-1
13464 | XVDBSA6 | Environment | product certifications | UL GOST CSA
13465 | XVDBSA6 | Environment | protective treatment | TC
13466 | XVDBSA6 | Environment | ambient air temperature for storage | -40…70 °C
13467 | XVDBSA6 | Environment | ambient air temperature for operation | -25…50 °C
13468 | XVDBSA6 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13469 | XVDBSA6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13470 | XVDBSA6 | Environment | noise level | 70…90 dB at 1 m
13471 | XVDBSA6 | Contractual warranty | Warranty | 18 months
13472 | XVDB1GAR | Main | range of product | Harmony XVD Application
13473 | XVDB1GAR | Main | product or component type | Complete pre-cabled indicator bank
13474 | XVDB1GAR | Main | beacon or indicator bank unit type | 3 illuminated units
13475 | XVDB1GAR | Main | component name | XVD
13476 | XVDB1GAR | Main | light source | Green incandescent bulb with BA 15d base steady signalling <10 W Orange incandescent bulb with BA 15d base steady signalling <10 W Red incandescent bulb with BA 15d base steady signalling <10 W
13477 | XVDB1GAR | Main | light block color | Green/orange/red
13478 | XVDB1GAR | Main | [Us] rated supply voltage | 24 V AC/DC
13479 | XVDB1GAR | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit
13480 | XVDB1GAR | Complementary | mounting diameter | 70 mm
13481 | XVDB1GAR | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13482 | XVDB1GAR | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13483 | XVDB1GAR | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13484 | XVDB1GAR | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13485 | XVDB1GAR | Complementary | net weight | 0.923 kg
13486 | XVDB1GAR | Environment | standards | EN/IEC 60947-5-1
13487 | XVDB1GAR | Environment | product certifications | UL CSA GOST
13488 | XVDB1GAR | Environment | protective treatment | TC
13489 | XVDB1GAR | Environment | ambient air temperature for storage | -40…70 °C
13490 | XVDB1GAR | Environment | ambient air temperature for operation | -25…70 °C
13491 | XVDB1GAR | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13492 | XVDB1GAR | Environment | IP degree of protection | IP40 conforming to IEC 60529
13493 | XVDB1GAR | Contractual warranty | Warranty | 18 months
13494 | XVDM1GAR | Main | range of product | Harmony XVD Application
13495 | XVDM1GAR | Main | product or component type | Complete pre-cabled indicator bank
13496 | XVDM1GAR | Main | beacon or indicator bank unit type | 3 illuminated units
13497 | XVDM1GAR | Main | component name | XVD
13498 | XVDM1GAR | Main | light source | Green incandescent bulb with BA 15d base steady signalling <10 W Orange incandescent bulb with BA 15d base steady signalling <10 W Red incandescent bulb with BA 15d base steady signalling <10 W
13499 | XVDM1GAR | Main | light block color | Green/orange/red
13500 | XVDM1GAR | Main | [Us] rated supply voltage | 230 V AC
13501 | XVDM1GAR | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit
13502 | XVDM1GAR | Complementary | mounting diameter | 70 mm
13503 | XVDM1GAR | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13504 | XVDM1GAR | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13505 | XVDM1GAR | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13506 | XVDM1GAR | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13507 | XVDM1GAR | Complementary | net weight | 0.923 kg
13508 | XVDM1GAR | Environment | standards | EN/IEC 60947-5-1
13509 | XVDM1GAR | Environment | product certifications | CSA UL GOST
13510 | XVDM1GAR | Environment | protective treatment | TC
13511 | XVDM1GAR | Environment | ambient air temperature for storage | -40…70 °C
13512 | XVDM1GAR | Environment | ambient air temperature for operation | -25…50 °C
13513 | XVDM1GAR | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13514 | XVDM1GAR | Environment | IP degree of protection | IP40 conforming to IEC 60529
13515 | XVDM1GAR | Contractual warranty | Warranty | 18 months
13516 | XVDB2GAR | Main | range of product | Harmony XVD Application
13517 | XVDB2GAR | Main | product or component type | Complete pre-cabled indicator bank
13518 | XVDB2GAR | Main | beacon or indicator bank unit type | 3 illuminated units
13519 | XVDB2GAR | Main | component name | XVD
13520 | XVDB2GAR | Main | light source | Green LED with BA 15d base steady signalling Orange LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling
13521 | XVDB2GAR | Main | light block color | Green/orange/red
13522 | XVDB2GAR | Main | [Us] rated supply voltage | 24 V AC/DC
13523 | XVDB2GAR | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit
13524 | XVDB2GAR | Complementary | mounting diameter | 70 mm
13525 | XVDB2GAR | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13526 | XVDB2GAR | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13527 | XVDB2GAR | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13528 | XVDB2GAR | Complementary | current consumption | < 47 mA on LED unit
13529 | XVDB2GAR | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13530 | XVDB2GAR | Complementary | net weight | 0.698 kg
13531 | XVDB2GAR | Environment | standards | EN/IEC 60947-5-1
13532 | XVDB2GAR | Environment | product certifications | GOST CSA UL
13533 | XVDB2GAR | Environment | protective treatment | TC
13534 | XVDB2GAR | Environment | ambient air temperature for storage | -40…70 °C
13535 | XVDB2GAR | Environment | ambient air temperature for operation | -25…50 °C
13536 | XVDB2GAR | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13537 | XVDB2GAR | Environment | IP degree of protection | IP40 conforming to IEC 60529
13538 | XVDB2GAR | Contractual warranty | Warranty | 18 months
13539 | XVDM2GAR | Main | range of product | Harmony XVD Application
13540 | XVDM2GAR | Main | product or component type | Complete pre-cabled indicator bank
13541 | XVDM2GAR | Main | beacon or indicator bank unit type | 3 illuminated units
13542 | XVDM2GAR | Main | component name | XVD
13543 | XVDM2GAR | Main | light source | Green LED with BA 15d base steady signalling Orange LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling
13544 | XVDM2GAR | Main | light block color | Green/orange/red
13545 | XVDM2GAR | Main | [Us] rated supply voltage | 230 V AC
13546 | XVDM2GAR | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit
13547 | XVDM2GAR | Complementary | mounting diameter | 70 mm
13548 | XVDM2GAR | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13549 | XVDM2GAR | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13550 | XVDM2GAR | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13551 | XVDM2GAR | Complementary | current consumption | < 17 mA on LED unit
13552 | XVDM2GAR | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13553 | XVDM2GAR | Complementary | net weight | 0.698 kg
13554 | XVDM2GAR | Environment | standards | EN/IEC 60947-5-1
13555 | XVDM2GAR | Environment | product certifications | GOST UL CSA
13556 | XVDM2GAR | Environment | protective treatment | TC
13557 | XVDM2GAR | Environment | ambient air temperature for storage | -40…70 °C
13558 | XVDM2GAR | Environment | ambient air temperature for operation | -25…50 °C
13559 | XVDM2GAR | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13560 | XVDM2GAR | Environment | IP degree of protection | IP40 conforming to IEC 60529
13561 | XVDM2GAR | Contractual warranty | Warranty | 18 months
13562 | XVDB2GAR6 | Main | range of product | Harmony XVD Application
13563 | XVDB2GAR6 | Main | product or component type | Complete pre-cabled indicator bank
13564 | XVDB2GAR6 | Main | beacon or indicator bank unit type | 3 illuminated units
13565 | XVDB2GAR6 | Main | component name | XVD
13566 | XVDB2GAR6 | Main | light source | Red flash discharge tubeflashing signalling Green LED with BA 15d base steady signalling Orange LED with BA 15d base steady signalling
13567 | XVDB2GAR6 | Main | light block color | Green/orange/red (flashing)
13568 | XVDB2GAR6 | Main | [Us] rated supply voltage | 24 V AC/DC
13569 | XVDB2GAR6 | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit
13570 | XVDB2GAR6 | Complementary | mounting diameter | 70 mm
13571 | XVDB2GAR6 | Complementary | flash energy | 5 J
13572 | XVDB2GAR6 | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13573 | XVDB2GAR6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13574 | XVDB2GAR6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13575 | XVDB2GAR6 | Complementary | current consumption | < 350 mA on flash discharge tube unit DC < 47 mA on LED unit < 550 mA on flash discharge tube unit AC
13576 | XVDB2GAR6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13577 | XVDB2GAR6 | Complementary | flashing frequency | 1 Hz
13578 | XVDB2GAR6 | Complementary | net weight | 0.898 kg
13579 | XVDB2GAR6 | Environment | standards | EN/IEC 60947-5-1
13580 | XVDB2GAR6 | Environment | product certifications | CSA GOST UL
13581 | XVDB2GAR6 | Environment | protective treatment | TC
13582 | XVDB2GAR6 | Environment | ambient air temperature for storage | -40…70 °C
13583 | XVDB2GAR6 | Environment | ambient air temperature for operation | -25…50 °C
13584 | XVDB2GAR6 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13585 | XVDB2GAR6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13586 | XVDB2GAR6 | Contractual warranty | Warranty | 18 months
13587 | XVDB2SGR | Main | range of product | Harmony XVD Application
13588 | XVDB2SGR | Main | product or component type | Complete pre-cabled indicator bank
13589 | XVDB2SGR | Main | beacon or indicator bank unit type | 2 illuminated units + 1 audible buzzer unit
13590 | XVDB2SGR | Main | component name | XVD
13591 | XVDB2SGR | Main | light source | Green LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling
13592 | XVDB2SGR | Main | light block color | Green/red
13593 | XVDB2SGR | Main | [Us] rated supply voltage | 24 V AC/DC
13594 | XVDB2SGR | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit
13595 | XVDB2SGR | Complementary | mounting diameter | 70 mm
13596 | XVDB2SGR | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13597 | XVDB2SGR | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13598 | XVDB2SGR | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13599 | XVDB2SGR | Complementary | current consumption | < 20 mA on audible unit < 47 mA on LED unit
13600 | XVDB2SGR | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13601 | XVDB2SGR | Complementary | fundamental frequency | 2.8 kHz
13602 | XVDB2SGR | Complementary | net weight | 0.718 kg
13603 | XVDB2SGR | Environment | standards | EN/IEC 60947-5-1
13604 | XVDB2SGR | Environment | product certifications | UL CSA GOST
13605 | XVDB2SGR | Environment | protective treatment | TC
13606 | XVDB2SGR | Environment | ambient air temperature for storage | -40…70 °C
13607 | XVDB2SGR | Environment | ambient air temperature for operation | -25…50 °C
13608 | XVDB2SGR | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13609 | XVDB2SGR | Environment | IP degree of protection | IP40 conforming to IEC 60529
13610 | XVDB2SGR | Environment | noise level | 70…90 dB at 1 m
13611 | XVDB2SGR | Contractual warranty | Warranty | 18 months
13612 | XVDB2SAR | Main | range of product | Harmony XVD Application
13613 | XVDB2SAR | Main | product or component type | Complete pre-cabled indicator bank
13614 | XVDB2SAR | Main | beacon or indicator bank unit type | 2 illuminated units + 1 audible buzzer unit
13615 | XVDB2SAR | Main | component name | XVD
13616 | XVDB2SAR | Main | light source | Orange LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling
13617 | XVDB2SAR | Main | light block color | Orange/red
13618 | XVDB2SAR | Main | [Us] rated supply voltage | 24 V AC/DC
13619 | XVDB2SAR | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit
13620 | XVDB2SAR | Complementary | mounting diameter | 70 mm
13621 | XVDB2SAR | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13622 | XVDB2SAR | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13623 | XVDB2SAR | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13624 | XVDB2SAR | Complementary | current consumption | < 20 mA on audible unit < 47 mA on LED unit
13625 | XVDB2SAR | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13626 | XVDB2SAR | Complementary | fundamental frequency | 2.8 kHz
13627 | XVDB2SAR | Complementary | net weight | 0.718 kg
13628 | XVDB2SAR | Environment | standards | EN/IEC 60947-5-1
13629 | XVDB2SAR | Environment | product certifications | GOST UL CSA
13630 | XVDB2SAR | Environment | protective treatment | TC
13631 | XVDB2SAR | Environment | ambient air temperature for storage | -40…70 °C
13632 | XVDB2SAR | Environment | ambient air temperature for operation | -25…50 °C
13633 | XVDB2SAR | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13634 | XVDB2SAR | Environment | IP degree of protection | IP40 conforming to IEC 60529
13635 | XVDB2SAR | Environment | noise level | 70…90 dB at 1 m
13636 | XVDB2SAR | Contractual warranty | Warranty | 18 months
13637 | XVDM2SGR | Main | range of product | Harmony XVD Application
13638 | XVDM2SGR | Main | product or component type | Complete pre-cabled indicator bank
13639 | XVDM2SGR | Main | beacon or indicator bank unit type | 2 illuminated units + 1 audible buzzer unit
13640 | XVDM2SGR | Main | component name | XVD
13641 | XVDM2SGR | Main | light source | Green LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling
13642 | XVDM2SGR | Main | light block color | Green/red
13643 | XVDM2SGR | Main | [Us] rated supply voltage | 230 V AC
13644 | XVDM2SGR | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit
13645 | XVDM2SGR | Complementary | mounting diameter | 70 mm
13646 | XVDM2SGR | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13647 | XVDM2SGR | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13648 | XVDM2SGR | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13649 | XVDM2SGR | Complementary | current consumption | < 17 mA on LED unit < 50 mA on audible unit
13650 | XVDM2SGR | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
13651 | XVDM2SGR | Complementary | fundamental frequency | 2.8 kHz
13652 | XVDM2SGR | Complementary | net weight | 0.718 kg
13653 | XVDM2SGR | Environment | standards | EN/IEC 60947-5-1
13654 | XVDM2SGR | Environment | product certifications | GOST UL CSA
13655 | XVDM2SGR | Environment | protective treatment | TC
13656 | XVDM2SGR | Environment | ambient air temperature for storage | -40…70 °C
13657 | XVDM2SGR | Environment | ambient air temperature for operation | -25…50 °C
13658 | XVDM2SGR | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13659 | XVDM2SGR | Environment | IP degree of protection | IP40 conforming to IEC 60529
13660 | XVDM2SGR | Environment | noise level | 70…90 dB at 1 m
13661 | XVDM2SGR | Contractual warranty | Warranty | 18 months
13662 | XVDB2CGAR | Main | range of product | Harmony XVD Application
13663 | XVDB2CGAR | Main | product or component type | Complete pre-cabled indicator bank
13664 | XVDB2CGAR | Main | beacon or indicator bank unit type | 4 illuminated units
13665 | XVDB2CGAR | Main | component name | XVD
13666 | XVDB2CGAR | Main | light source | Clear LED with BA 15d base steady signalling Green LED with BA 15d base steady signalling Orange LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling
13667 | XVDB2CGAR | Main | light block color | Clear/green/orange/red
13668 | XVDB2CGAR | Main | [Us] rated supply voltage | 24 V AC/DC
13669 | XVDB2CGAR | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit
13670 | XVDB2CGAR | Complementary | mounting diameter | 70 mm
13671 | XVDB2CGAR | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13672 | XVDB2CGAR | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13673 | XVDB2CGAR | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13674 | XVDB2CGAR | Complementary | current consumption | < 47 mA on LED unit
13675 | XVDB2CGAR | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13676 | XVDB2CGAR | Complementary | net weight | 0.843 kg
13677 | XVDB2CGAR | Environment | standards | EN/IEC 60947-5-1
13678 | XVDB2CGAR | Environment | product certifications | UL GOST CSA
13679 | XVDB2CGAR | Environment | protective treatment | TC
13680 | XVDB2CGAR | Environment | ambient air temperature for storage | -40…70 °C
13681 | XVDB2CGAR | Environment | ambient air temperature for operation | -25…50 °C
13682 | XVDB2CGAR | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13683 | XVDB2CGAR | Environment | IP degree of protection | IP40 conforming to IEC 60529
13684 | XVDB2CGAR | Contractual warranty | Warranty | 18 months
13685 | XVDB1SGAR | Main | range of product | Harmony XVD Application
13686 | XVDB1SGAR | Main | product or component type | Complete pre-cabled indicator bank
13687 | XVDB1SGAR | Main | beacon or indicator bank unit type | 3 illuminated units + 1 audible buzzer unit
13688 | XVDB1SGAR | Main | component name | XVD
13689 | XVDB1SGAR | Main | light source | Green incandescent bulb with BA 15d base steady signalling <10 W Orange incandescent bulb with BA 15d base steady signalling <10 W Red incandescent bulb with BA 15d base steady signalling <10 W
13690 | XVDB1SGAR | Main | light block color | Green/orange/red
13691 | XVDB1SGAR | Main | [Us] rated supply voltage | 24 V AC/DC
13692 | XVDB1SGAR | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit
13693 | XVDB1SGAR | Complementary | mounting diameter | 70 mm
13694 | XVDB1SGAR | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13695 | XVDB1SGAR | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13696 | XVDB1SGAR | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13697 | XVDB1SGAR | Complementary | current consumption | < 20 mA on audible unit
13698 | XVDB1SGAR | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
13699 | XVDB1SGAR | Complementary | fundamental frequency | 2.8 kHz
13700 | XVDB1SGAR | Complementary | net weight | 1.088 kg
13701 | XVDB1SGAR | Environment | standards | EN/IEC 60947-5-1
13702 | XVDB1SGAR | Environment | product certifications | UL CSA GOST
13703 | XVDB1SGAR | Environment | protective treatment | TC
13704 | XVDB1SGAR | Environment | ambient air temperature for storage | -40…70 °C
13705 | XVDB1SGAR | Environment | ambient air temperature for operation | -25…70 °C
13706 | XVDB1SGAR | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13707 | XVDB1SGAR | Environment | IP degree of protection | IP40 conforming to IEC 60529
13708 | XVDB1SGAR | Environment | noise level | 70…90 dB at 1 m
13709 | XVDB1SGAR | Contractual warranty | Warranty | 18 months
13710 | XVDB2SGAR | Main | range of product | Harmony XVD Application
13711 | XVDB2SGAR | Main | product or component type | Complete pre-cabled indicator bank
13712 | XVDB2SGAR | Main | beacon or indicator bank unit type | 3 illuminated units + 1 audible buzzer unit
13713 | XVDB2SGAR | Main | component name | XVD
13714 | XVDB2SGAR | Main | light source | Green LED with BA 15d base steady signalling Orange LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling
13715 | XVDB2SGAR | Main | light block color | Green/orange/red
13716 | XVDB2SGAR | Main | [Us] rated supply voltage | 24 V AC/DC
13717 | XVDB2SGAR | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit
13718 | XVDB2SGAR | Complementary | mounting diameter | 70 mm
13719 | XVDB2SGAR | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13720 | XVDB2SGAR | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13721 | XVDB2SGAR | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13722 | XVDB2SGAR | Complementary | current consumption | < 20 mA on audible unit < 47 mA on LED unit
13723 | XVDB2SGAR | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13724 | XVDB2SGAR | Complementary | fundamental frequency | 2.8 kHz
13725 | XVDB2SGAR | Complementary | net weight | 0.863 kg
13726 | XVDB2SGAR | Environment | standards | EN/IEC 60947-5-1
13727 | XVDB2SGAR | Environment | product certifications | GOST CSA UL
13728 | XVDB2SGAR | Environment | protective treatment | TC
13729 | XVDB2SGAR | Environment | ambient air temperature for storage | -40…70 °C
13730 | XVDB2SGAR | Environment | ambient air temperature for operation | -25…50 °C
13731 | XVDB2SGAR | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13732 | XVDB2SGAR | Environment | IP degree of protection | IP40 conforming to IEC 60529
13733 | XVDB2SGAR | Environment | noise level | 70…90 dB at 1 m
13734 | XVDB2SGAR | Contractual warranty | Warranty | 18 months
13735 | XVDM2SGAR | Main | range of product | Harmony XVD Application
13736 | XVDM2SGAR | Main | product or component type | Complete pre-cabled indicator bank
13737 | XVDM2SGAR | Main | beacon or indicator bank unit type | 3 illuminated units + 1 audible buzzer unit
13738 | XVDM2SGAR | Main | component name | XVD
13739 | XVDM2SGAR | Main | light source | Green LED with BA 15d base steady signalling Orange LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling
13740 | XVDM2SGAR | Main | light block color | Green/orange/red
13741 | XVDM2SGAR | Main | [Us] rated supply voltage | 230 V AC
13742 | XVDM2SGAR | Complementary | material | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit
13743 | XVDM2SGAR | Complementary | mounting diameter | 70 mm
13744 | XVDM2SGAR | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
13745 | XVDM2SGAR | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13746 | XVDM2SGAR | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13747 | XVDM2SGAR | Complementary | current consumption | < 17 mA on LED unit < 50 mA on audible unit
13748 | XVDM2SGAR | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13749 | XVDM2SGAR | Complementary | fundamental frequency | 2.8 kHz
13750 | XVDM2SGAR | Complementary | net weight | 0.863 kg
13751 | XVDM2SGAR | Environment | standards | EN/IEC 60947-5-1
13752 | XVDM2SGAR | Environment | product certifications | UL CSA GOST
13753 | XVDM2SGAR | Environment | protective treatment | TC
13754 | XVDM2SGAR | Environment | ambient air temperature for storage | -40…70 °C
13755 | XVDM2SGAR | Environment | ambient air temperature for operation | -25…50 °C
13756 | XVDM2SGAR | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13757 | XVDM2SGAR | Environment | IP degree of protection | IP40 conforming to IEC 60529
13758 | XVDM2SGAR | Environment | noise level | 70…90 dB at 1 m
13759 | XVDM2SGAR | Contractual warranty | Warranty | 18 months
13760 | XVDL33 | Main | range of product | Harmony XVD Application
13761 | XVDL33 | Main | product or component type | Beacon
13762 | XVDL33 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
13763 | XVDL33 | Main | signalling type | Steady
13764 | XVDL33 | Main | mounting diameter | 70 mm
13765 | XVDL33 | Main | component name | XVD
13766 | XVDL33 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13767 | XVDL33 | Main | light source | Bulb not included, green
13768 | XVDL33 | Main | bulb type | Incandescent with BA 15d base Protected LED
13769 | XVDL33 | Main | [Us] rated supply voltage | <= 250 V
13770 | XVDL33 | Main | maximum power dissipation in W | 10 W
13771 | XVDL33 | Complementary | assembly style | Customer assembly
13772 | XVDL33 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
13773 | XVDL33 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13774 | XVDL33 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13775 | XVDL33 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
13776 | XVDL33 | Complementary | CAD overall width | 70 mm
13777 | XVDL33 | Complementary | CAD overall height | 133 mm
13778 | XVDL33 | Complementary | CAD overall depth | 70 mm
13779 | XVDL33 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
13780 | XVDL33 | Complementary | net weight | 0.255 kg
13781 | XVDL33 | Environment | pollution degree | 2
13782 | XVDL33 | Environment | product certifications | CSA GOST UL
13783 | XVDL33 | Environment | standards | EN/IEC 60947-5-1
13784 | XVDL33 | Environment | protective treatment | TC
13785 | XVDL33 | Environment | ambient air temperature for operation | -25…50 °C: LED -25…70 °C: incandescent
13786 | XVDL33 | Environment | ambient air temperature for storage | -40…70 °C
13787 | XVDL33 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13788 | XVDL33 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13789 | XVDL33 | Contractual warranty | Warranty | 18 months
13790 | XVDL34 | Main | range of product | Harmony XVD Application
13791 | XVDL34 | Main | product or component type | Beacon
13792 | XVDL34 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
13793 | XVDL34 | Main | signalling type | Steady
13794 | XVDL34 | Main | mounting diameter | 70 mm
13795 | XVDL34 | Main | component name | XVD
13796 | XVDL34 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13797 | XVDL34 | Main | light source | Bulb not included, red
13798 | XVDL34 | Main | bulb type | Incandescent with BA 15d base Protected LED
13799 | XVDL34 | Main | [Us] rated supply voltage | <= 250 V
13800 | XVDL34 | Main | maximum power dissipation in W | 10 W
13801 | XVDL34 | Complementary | assembly style | Customer assembly
13802 | XVDL34 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
13803 | XVDL34 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13804 | XVDL34 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13805 | XVDL34 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13806 | XVDL34 | Complementary | CAD overall width | 70 mm
13807 | XVDL34 | Complementary | CAD overall height | 133 mm
13808 | XVDL34 | Complementary | CAD overall depth | 70 mm
13809 | XVDL34 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
13810 | XVDL34 | Complementary | net weight | 0.255 kg
13811 | XVDL34 | Environment | pollution degree | 2
13812 | XVDL34 | Environment | product certifications | UL CSA GOST
13813 | XVDL34 | Environment | standards | EN/IEC 60947-5-1
13814 | XVDL34 | Environment | protective treatment | TC
13815 | XVDL34 | Environment | ambient air temperature for operation | -25…50 °C: LED -25…70 °C: incandescent
13816 | XVDL34 | Environment | ambient air temperature for storage | -40…70 °C
13817 | XVDL34 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13818 | XVDL34 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13819 | XVDL34 | Contractual warranty | Warranty | 18 months
13820 | XVDL35 | Main | range of product | Harmony XVD Application
13821 | XVDL35 | Main | product or component type | Beacon
13822 | XVDL35 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
13823 | XVDL35 | Main | signalling type | Steady
13824 | XVDL35 | Main | mounting diameter | 70 mm
13825 | XVDL35 | Main | component name | XVD
13826 | XVDL35 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13827 | XVDL35 | Main | light source | Bulb not included, orange
13828 | XVDL35 | Main | bulb type | Incandescent with BA 15d base Protected LED
13829 | XVDL35 | Main | [Us] rated supply voltage | <= 250 V
13830 | XVDL35 | Main | maximum power dissipation in W | 10 W
13831 | XVDL35 | Complementary | assembly style | Customer assembly
13832 | XVDL35 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
13833 | XVDL35 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13834 | XVDL35 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13835 | XVDL35 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13836 | XVDL35 | Complementary | CAD overall width | 70 mm
13837 | XVDL35 | Complementary | CAD overall height | 133 mm
13838 | XVDL35 | Complementary | CAD overall depth | 70 mm
13839 | XVDL35 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
13840 | XVDL35 | Complementary | net weight | 0.255 kg
13841 | XVDL35 | Environment | pollution degree | 2
13842 | XVDL35 | Environment | product certifications | UL CSA GOST
13843 | XVDL35 | Environment | standards | EN/IEC 60947-5-1
13844 | XVDL35 | Environment | protective treatment | TC
13845 | XVDL35 | Environment | ambient air temperature for operation | -25…50 °C: LED -25…70 °C: incandescent
13846 | XVDL35 | Environment | ambient air temperature for storage | -40…70 °C
13847 | XVDL35 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13848 | XVDL35 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13849 | XVDL35 | Contractual warranty | Warranty | 18 months
13850 | XVDL38 | Main | range of product | Harmony XVD Application
13851 | XVDL38 | Main | product or component type | Beacon
13852 | XVDL38 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
13853 | XVDL38 | Main | signalling type | Steady
13854 | XVDL38 | Main | mounting diameter | 70 mm
13855 | XVDL38 | Main | component name | XVD
13856 | XVDL38 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13857 | XVDL38 | Main | light source | Bulb not included, yellow
13858 | XVDL38 | Main | bulb type | Incandescent with BA 15d base Protected LED
13859 | XVDL38 | Main | [Us] rated supply voltage | <= 250 V
13860 | XVDL38 | Main | maximum power dissipation in W | 10 W
13861 | XVDL38 | Complementary | assembly style | Customer assembly
13862 | XVDL38 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
13863 | XVDL38 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13864 | XVDL38 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13865 | XVDL38 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
13866 | XVDL38 | Complementary | CAD overall width | 70 mm
13867 | XVDL38 | Complementary | CAD overall height | 133 mm
13868 | XVDL38 | Complementary | CAD overall depth | 70 mm
13869 | XVDL38 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
13870 | XVDL38 | Complementary | net weight | 0.255 kg
13871 | XVDL38 | Environment | pollution degree | 2
13872 | XVDL38 | Environment | product certifications | GOST UL CSA
13873 | XVDL38 | Environment | standards | EN/IEC 60947-5-1
13874 | XVDL38 | Environment | protective treatment | TC
13875 | XVDL38 | Environment | ambient air temperature for operation | -25…50 °C: LED -25…70 °C: incandescent
13876 | XVDL38 | Environment | ambient air temperature for storage | -40…70 °C
13877 | XVDL38 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13878 | XVDL38 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13879 | XVDL38 | Contractual warranty | Warranty | 18 months
13880 | XVDL4B3 | Main | range of product | Harmony XVD Application
13881 | XVDL4B3 | Main | product or component type | Beacon
13882 | XVDL4B3 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
13883 | XVDL4B3 | Main | signalling type | Flashing
13884 | XVDL4B3 | Main | mounting diameter | 70 mm
13885 | XVDL4B3 | Main | component name | XVD
13886 | XVDL4B3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13887 | XVDL4B3 | Main | light source | Bulb not included, green
13888 | XVDL4B3 | Main | bulb type | Incandescent Incandescent with BA 15d base Protected LED
13889 | XVDL4B3 | Main | [Us] rated supply voltage | 24 V AC 24...48 V DC
13890 | XVDL4B3 | Main | maximum power dissipation in W | 10 W
13891 | XVDL4B3 | Complementary | assembly style | Customer assembly
13892 | XVDL4B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
13893 | XVDL4B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13894 | XVDL4B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13895 | XVDL4B3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13896 | XVDL4B3 | Complementary | flashing frequency | 1 Hz
13897 | XVDL4B3 | Complementary | CAD overall width | 70 mm
13898 | XVDL4B3 | Complementary | CAD overall height | 133 mm
13899 | XVDL4B3 | Complementary | CAD overall depth | 70 mm
13900 | XVDL4B3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
13901 | XVDL4B3 | Complementary | net weight | 0.275 kg
13902 | XVDL4B3 | Environment | pollution degree | 2
13903 | XVDL4B3 | Environment | product certifications | GOST UL CSA
13904 | XVDL4B3 | Environment | standards | EN/IEC 60947-5-1
13905 | XVDL4B3 | Environment | protective treatment | TC
13906 | XVDL4B3 | Environment | ambient air temperature for operation | -25…40 °C: incandescent -25…50 °C: LED
13907 | XVDL4B3 | Environment | ambient air temperature for storage | -40…70 °C
13908 | XVDL4B3 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13909 | XVDL4B3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13910 | XVDL4B3 | Contractual warranty | Warranty | 18 months
13911 | XVDL4B4 | Main | range of product | Harmony XVD Application
13912 | XVDL4B4 | Main | product or component type | Beacon
13913 | XVDL4B4 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
13914 | XVDL4B4 | Main | signalling type | Flashing
13915 | XVDL4B4 | Main | mounting diameter | 70 mm
13916 | XVDL4B4 | Main | component name | XVD
13917 | XVDL4B4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13918 | XVDL4B4 | Main | light source | Bulb not included, red
13919 | XVDL4B4 | Main | bulb type | Incandescent Incandescent with BA 15d base Protected LED
13920 | XVDL4B4 | Main | [Us] rated supply voltage | 24 V AC 24...48 V DC
13921 | XVDL4B4 | Main | maximum power dissipation in W | 10 W
13922 | XVDL4B4 | Complementary | assembly style | Customer assembly
13923 | XVDL4B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
13924 | XVDL4B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13925 | XVDL4B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13926 | XVDL4B4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13927 | XVDL4B4 | Complementary | flashing frequency | 1 Hz
13928 | XVDL4B4 | Complementary | CAD overall width | 70 mm
13929 | XVDL4B4 | Complementary | CAD overall height | 133 mm
13930 | XVDL4B4 | Complementary | CAD overall depth | 70 mm
13931 | XVDL4B4 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
13932 | XVDL4B4 | Complementary | net weight | 0.275 kg
13933 | XVDL4B4 | Environment | pollution degree | 2
13934 | XVDL4B4 | Environment | product certifications | GOST CSA UL
13935 | XVDL4B4 | Environment | standards | EN/IEC 60947-5-1
13936 | XVDL4B4 | Environment | protective treatment | TC
13937 | XVDL4B4 | Environment | ambient air temperature for operation | -25…40 °C: incandescent -25…50 °C: LED
13938 | XVDL4B4 | Environment | ambient air temperature for storage | -40…70 °C
13939 | XVDL4B4 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13940 | XVDL4B4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13941 | XVDL4B4 | Contractual warranty | Warranty | 18 months
13942 | XVDL4B5 | Main | range of product | Harmony XVD Application
13943 | XVDL4B5 | Main | product or component type | Beacon
13944 | XVDL4B5 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
13945 | XVDL4B5 | Main | signalling type | Flashing
13946 | XVDL4B5 | Main | mounting diameter | 70 mm
13947 | XVDL4B5 | Main | component name | XVD
13948 | XVDL4B5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13949 | XVDL4B5 | Main | light source | Bulb not included, orange
13950 | XVDL4B5 | Main | bulb type | Incandescent Incandescent with BA 15d base Protected LED
13951 | XVDL4B5 | Main | [Us] rated supply voltage | 24 V AC 24...48 V DC
13952 | XVDL4B5 | Main | maximum power dissipation in W | 10 W
13953 | XVDL4B5 | Complementary | assembly style | Customer assembly
13954 | XVDL4B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
13955 | XVDL4B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13956 | XVDL4B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13957 | XVDL4B5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13958 | XVDL4B5 | Complementary | flashing frequency | 1 Hz
13959 | XVDL4B5 | Complementary | CAD overall width | 70 mm
13960 | XVDL4B5 | Complementary | CAD overall height | 133 mm
13961 | XVDL4B5 | Complementary | CAD overall depth | 70 mm
13962 | XVDL4B5 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
13963 | XVDL4B5 | Complementary | net weight | 0.275 kg
13964 | XVDL4B5 | Environment | pollution degree | 2
13965 | XVDL4B5 | Environment | product certifications | UL GOST CSA
13966 | XVDL4B5 | Environment | standards | EN/IEC 60947-5-1
13967 | XVDL4B5 | Environment | protective treatment | TC
13968 | XVDL4B5 | Environment | ambient air temperature for operation | -25…40 °C: incandescent -25…50 °C: LED
13969 | XVDL4B5 | Environment | ambient air temperature for storage | -40…70 °C
13970 | XVDL4B5 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
13971 | XVDL4B5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
13972 | XVDL4B5 | Contractual warranty | Warranty | 18 months
13973 | XVDL4B6 | Main | range of product | Harmony XVD Application
13974 | XVDL4B6 | Main | product or component type | Beacon
13975 | XVDL4B6 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
13976 | XVDL4B6 | Main | signalling type | Flashing
13977 | XVDL4B6 | Main | mounting diameter | 70 mm
13978 | XVDL4B6 | Main | component name | XVD
13979 | XVDL4B6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
13980 | XVDL4B6 | Main | light source | Bulb not included, blue
13981 | XVDL4B6 | Main | bulb type | Incandescent Incandescent with BA 15d base Protected LED
13982 | XVDL4B6 | Main | [Us] rated supply voltage | 24 V AC 24...48 V DC
13983 | XVDL4B6 | Main | maximum power dissipation in W | 10 W
13984 | XVDL4B6 | Complementary | assembly style | Customer assembly
13985 | XVDL4B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
13986 | XVDL4B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
13987 | XVDL4B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
13988 | XVDL4B6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
13989 | XVDL4B6 | Complementary | flashing frequency | 1 Hz
13990 | XVDL4B6 | Complementary | CAD overall width | 70 mm
13991 | XVDL4B6 | Complementary | CAD overall height | 133 mm
13992 | XVDL4B6 | Complementary | CAD overall depth | 70 mm
13993 | XVDL4B6 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
13994 | XVDL4B6 | Complementary | net weight | 0.275 kg
13995 | XVDL4B6 | Environment | pollution degree | 2
13996 | XVDL4B6 | Environment | product certifications | CSA GOST UL
13997 | XVDL4B6 | Environment | standards | EN/IEC 60947-5-1
13998 | XVDL4B6 | Environment | protective treatment | TC
13999 | XVDL4B6 | Environment | ambient air temperature for operation | -25…40 °C: incandescent -25…50 °C: LED
14000 | XVDL4B6 | Environment | ambient air temperature for storage | -40…70 °C
14001 | XVDL4B6 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14002 | XVDL4B6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14003 | XVDL4B6 | Contractual warranty | Warranty | 18 months
14004 | XVDL4B7 | Main | range of product | Harmony XVD Application
14005 | XVDL4B7 | Main | product or component type | Beacon
14006 | XVDL4B7 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14007 | XVDL4B7 | Main | signalling type | Flashing
14008 | XVDL4B7 | Main | mounting diameter | 70 mm
14009 | XVDL4B7 | Main | component name | XVD
14010 | XVDL4B7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14011 | XVDL4B7 | Main | light source | Bulb not included, clear
14012 | XVDL4B7 | Main | bulb type | Incandescent Incandescent with BA 15d base Protected LED
14013 | XVDL4B7 | Main | [Us] rated supply voltage | 24 V AC 24...48 V DC
14014 | XVDL4B7 | Main | maximum power dissipation in W | 10 W
14015 | XVDL4B7 | Complementary | assembly style | Customer assembly
14016 | XVDL4B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14017 | XVDL4B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14018 | XVDL4B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14019 | XVDL4B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
14020 | XVDL4B7 | Complementary | flashing frequency | 1 Hz
14021 | XVDL4B7 | Complementary | CAD overall width | 70 mm
14022 | XVDL4B7 | Complementary | CAD overall height | 133 mm
14023 | XVDL4B7 | Complementary | CAD overall depth | 70 mm
14024 | XVDL4B7 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
14025 | XVDL4B7 | Complementary | net weight | 0.275 kg
14026 | XVDL4B7 | Environment | pollution degree | 2
14027 | XVDL4B7 | Environment | product certifications | CSA UL GOST
14028 | XVDL4B7 | Environment | standards | EN/IEC 60947-5-1
14029 | XVDL4B7 | Environment | protective treatment | TC
14030 | XVDL4B7 | Environment | ambient air temperature for operation | -25…40 °C: incandescent -25…50 °C: LED
14031 | XVDL4B7 | Environment | ambient air temperature for storage | -40…70 °C
14032 | XVDL4B7 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14033 | XVDL4B7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14034 | XVDL4B7 | Contractual warranty | Warranty | 18 months
14035 | XVDL4B8 | Main | range of product | Harmony XVD Application
14036 | XVDL4B8 | Main | product or component type | Beacon
14037 | XVDL4B8 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14038 | XVDL4B8 | Main | signalling type | Flashing
14039 | XVDL4B8 | Main | mounting diameter | 70 mm
14040 | XVDL4B8 | Main | component name | XVD
14041 | XVDL4B8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14042 | XVDL4B8 | Main | light source | Bulb not included, yellow
14043 | XVDL4B8 | Main | bulb type | Incandescent Incandescent with BA 15d base Protected LED
14044 | XVDL4B8 | Main | [Us] rated supply voltage | 24 V AC 24...48 V DC
14045 | XVDL4B8 | Main | maximum power dissipation in W | 10 W
14046 | XVDL4B8 | Complementary | assembly style | Customer assembly
14047 | XVDL4B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14048 | XVDL4B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14049 | XVDL4B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14050 | XVDL4B8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
14051 | XVDL4B8 | Complementary | flashing frequency | 1 Hz
14052 | XVDL4B8 | Complementary | CAD overall width | 70 mm
14053 | XVDL4B8 | Complementary | CAD overall height | 133 mm
14054 | XVDL4B8 | Complementary | CAD overall depth | 70 mm
14055 | XVDL4B8 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
14056 | XVDL4B8 | Complementary | net weight | 0.275 kg
14057 | XVDL4B8 | Environment | pollution degree | 2
14058 | XVDL4B8 | Environment | product certifications | GOST CSA UL
14059 | XVDL4B8 | Environment | standards | EN/IEC 60947-5-1
14060 | XVDL4B8 | Environment | protective treatment | TC
14061 | XVDL4B8 | Environment | ambient air temperature for operation | -25…40 °C: incandescent -25…50 °C: LED
14062 | XVDL4B8 | Environment | ambient air temperature for storage | -40…70 °C
14063 | XVDL4B8 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14064 | XVDL4B8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14065 | XVDL4B8 | Contractual warranty | Warranty | 18 months
14066 | XVDL4M3 | Main | range of product | Harmony XVD Application
14067 | XVDL4M3 | Main | product or component type | Beacon
14068 | XVDL4M3 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14069 | XVDL4M3 | Main | signalling type | Flashing
14070 | XVDL4M3 | Main | mounting diameter | 70 mm
14071 | XVDL4M3 | Main | component name | XVD
14072 | XVDL4M3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14073 | XVDL4M3 | Main | light source | Bulb not included, green
14074 | XVDL4M3 | Main | bulb type | Incandescent with BA 15d base Protected LED
14075 | XVDL4M3 | Main | [Us] rated supply voltage | 48...230 V AC
14076 | XVDL4M3 | Main | maximum power dissipation in W | 10 W
14077 | XVDL4M3 | Complementary | assembly style | Customer assembly
14078 | XVDL4M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14079 | XVDL4M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14080 | XVDL4M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14081 | XVDL4M3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
14082 | XVDL4M3 | Complementary | flashing frequency | 1 Hz
14083 | XVDL4M3 | Complementary | CAD overall width | 70 mm
14084 | XVDL4M3 | Complementary | CAD overall height | 133 mm
14085 | XVDL4M3 | Complementary | CAD overall depth | 70 mm
14086 | XVDL4M3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
14087 | XVDL4M3 | Complementary | net weight | 0.275 kg
14088 | XVDL4M3 | Environment | pollution degree | 2
14089 | XVDL4M3 | Environment | product certifications | UL GOST CSA
14090 | XVDL4M3 | Environment | standards | EN/IEC 60947-5-1
14091 | XVDL4M3 | Environment | protective treatment | TC
14092 | XVDL4M3 | Environment | ambient air temperature for operation | -25…40 °C: incandescent -25…50 °C: LED
14093 | XVDL4M3 | Environment | ambient air temperature for storage | -40…70 °C
14094 | XVDL4M3 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14095 | XVDL4M3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14096 | XVDL4M3 | Contractual warranty | Warranty | 18 months
14097 | XVDL4M4 | Main | range of product | Harmony XVD Application
14098 | XVDL4M4 | Main | product or component type | Beacon
14099 | XVDL4M4 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14100 | XVDL4M4 | Main | signalling type | Flashing
14101 | XVDL4M4 | Main | mounting diameter | 70 mm
14102 | XVDL4M4 | Main | component name | XVD
14103 | XVDL4M4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14104 | XVDL4M4 | Main | light source | Bulb not included, red
14105 | XVDL4M4 | Main | bulb type | Incandescent with BA 15d base Protected LED
14106 | XVDL4M4 | Main | [Us] rated supply voltage | 48...230 V AC
14107 | XVDL4M4 | Main | maximum power dissipation in W | 10 W
14108 | XVDL4M4 | Complementary | assembly style | Customer assembly
14109 | XVDL4M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14110 | XVDL4M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14111 | XVDL4M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14112 | XVDL4M4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
14113 | XVDL4M4 | Complementary | flashing frequency | 1 Hz
14114 | XVDL4M4 | Complementary | CAD overall width | 70 mm
14115 | XVDL4M4 | Complementary | CAD overall height | 133 mm
14116 | XVDL4M4 | Complementary | CAD overall depth | 70 mm
14117 | XVDL4M4 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
14118 | XVDL4M4 | Complementary | net weight | 0.275 kg
14119 | XVDL4M4 | Environment | pollution degree | 2
14120 | XVDL4M4 | Environment | product certifications | UL GOST CSA
14121 | XVDL4M4 | Environment | standards | EN/IEC 60947-5-1
14122 | XVDL4M4 | Environment | protective treatment | TC
14123 | XVDL4M4 | Environment | ambient air temperature for operation | -25…40 °C: incandescent -25…50 °C: LED
14124 | XVDL4M4 | Environment | ambient air temperature for storage | -40…70 °C
14125 | XVDL4M4 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14126 | XVDL4M4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14127 | XVDL4M4 | Contractual warranty | Warranty | 18 months
14128 | XVDL4M5 | Main | range of product | Harmony XVD Application
14129 | XVDL4M5 | Main | product or component type | Beacon
14130 | XVDL4M5 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14131 | XVDL4M5 | Main | signalling type | Flashing
14132 | XVDL4M5 | Main | mounting diameter | 70 mm
14133 | XVDL4M5 | Main | component name | XVD
14134 | XVDL4M5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14135 | XVDL4M5 | Main | light source | Bulb not included, orange
14136 | XVDL4M5 | Main | bulb type | Incandescent with BA 15d base Protected LED
14137 | XVDL4M5 | Main | [Us] rated supply voltage | 48...230 V AC
14138 | XVDL4M5 | Main | maximum power dissipation in W | 10 W
14139 | XVDL4M5 | Complementary | assembly style | Customer assembly
14140 | XVDL4M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14141 | XVDL4M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14142 | XVDL4M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14143 | XVDL4M5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
14144 | XVDL4M5 | Complementary | flashing frequency | 1 Hz
14145 | XVDL4M5 | Complementary | CAD overall width | 70 mm
14146 | XVDL4M5 | Complementary | CAD overall height | 133 mm
14147 | XVDL4M5 | Complementary | CAD overall depth | 70 mm
14148 | XVDL4M5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
14149 | XVDL4M5 | Complementary | net weight | 0.275 kg
14150 | XVDL4M5 | Environment | pollution degree | 2
14151 | XVDL4M5 | Environment | product certifications | CSA UL GOST
14152 | XVDL4M5 | Environment | standards | EN/IEC 60947-5-1
14153 | XVDL4M5 | Environment | protective treatment | TC
14154 | XVDL4M5 | Environment | ambient air temperature for operation | -25…40 °C: incandescent -25…50 °C: LED
14155 | XVDL4M5 | Environment | ambient air temperature for storage | -40…70 °C
14156 | XVDL4M5 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14157 | XVDL4M5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14158 | XVDL4M5 | Contractual warranty | Warranty | 18 months
14159 | XVDL4M6 | Main | range of product | Harmony XVD Application
14160 | XVDL4M6 | Main | product or component type | Beacon
14161 | XVDL4M6 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14162 | XVDL4M6 | Main | signalling type | Flashing
14163 | XVDL4M6 | Main | mounting diameter | 70 mm
14164 | XVDL4M6 | Main | component name | XVD
14165 | XVDL4M6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14166 | XVDL4M6 | Main | light source | Bulb not included, blue
14167 | XVDL4M6 | Main | bulb type | Incandescent with BA 15d base Protected LED
14168 | XVDL4M6 | Main | [Us] rated supply voltage | 48...230 V AC
14169 | XVDL4M6 | Main | maximum power dissipation in W | 10 W
14170 | XVDL4M6 | Complementary | assembly style | Customer assembly
14171 | XVDL4M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14172 | XVDL4M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14173 | XVDL4M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14174 | XVDL4M6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
14175 | XVDL4M6 | Complementary | flashing frequency | 1 Hz
14176 | XVDL4M6 | Complementary | CAD overall width | 70 mm
14177 | XVDL4M6 | Complementary | CAD overall height | 133 mm
14178 | XVDL4M6 | Complementary | CAD overall depth | 70 mm
14179 | XVDL4M6 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
14180 | XVDL4M6 | Complementary | net weight | 0.275 kg
14181 | XVDL4M6 | Environment | pollution degree | 2
14182 | XVDL4M6 | Environment | product certifications | CSA UL GOST
14183 | XVDL4M6 | Environment | standards | EN/IEC 60947-5-1
14184 | XVDL4M6 | Environment | protective treatment | TC
14185 | XVDL4M6 | Environment | ambient air temperature for operation | -25…40 °C: incandescent -25…50 °C: LED
14186 | XVDL4M6 | Environment | ambient air temperature for storage | -40…70 °C
14187 | XVDL4M6 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14188 | XVDL4M6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14189 | XVDL4M6 | Contractual warranty | Warranty | 18 months
14190 | XVDL4M7 | Main | range of product | Harmony XVD Application
14191 | XVDL4M7 | Main | product or component type | Beacon
14192 | XVDL4M7 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14193 | XVDL4M7 | Main | signalling type | Flashing
14194 | XVDL4M7 | Main | mounting diameter | 70 mm
14195 | XVDL4M7 | Main | component name | XVD
14196 | XVDL4M7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14197 | XVDL4M7 | Main | light source | Bulb not included, clear
14198 | XVDL4M7 | Main | bulb type | Incandescent with BA 15d base Protected LED
14199 | XVDL4M7 | Main | [Us] rated supply voltage | 48...230 V AC
14200 | XVDL4M7 | Main | maximum power dissipation in W | 10 W
14201 | XVDL4M7 | Complementary | assembly style | Customer assembly
14202 | XVDL4M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14203 | XVDL4M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14204 | XVDL4M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14205 | XVDL4M7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14206 | XVDL4M7 | Complementary | flashing frequency | 1 Hz
14207 | XVDL4M7 | Complementary | CAD overall width | 70 mm
14208 | XVDL4M7 | Complementary | CAD overall height | 133 mm
14209 | XVDL4M7 | Complementary | CAD overall depth | 70 mm
14210 | XVDL4M7 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
14211 | XVDL4M7 | Complementary | net weight | 0.275 kg
14212 | XVDL4M7 | Environment | pollution degree | 2
14213 | XVDL4M7 | Environment | product certifications | UL CSA GOST
14214 | XVDL4M7 | Environment | standards | EN/IEC 60947-5-1
14215 | XVDL4M7 | Environment | protective treatment | TC
14216 | XVDL4M7 | Environment | ambient air temperature for operation | -25…40 °C: incandescent -25…50 °C: LED
14217 | XVDL4M7 | Environment | ambient air temperature for storage | -40…70 °C
14218 | XVDL4M7 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14219 | XVDL4M7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14220 | XVDL4M7 | Contractual warranty | Warranty | 18 months
14221 | XVDL4M8 | Main | range of product | Harmony XVD Application
14222 | XVDL4M8 | Main | product or component type | Beacon
14223 | XVDL4M8 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14224 | XVDL4M8 | Main | signalling type | Flashing
14225 | XVDL4M8 | Main | mounting diameter | 70 mm
14226 | XVDL4M8 | Main | component name | XVD
14227 | XVDL4M8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14228 | XVDL4M8 | Main | light source | Bulb not included, yellow
14229 | XVDL4M8 | Main | bulb type | Incandescent with BA 15d base Protected LED
14230 | XVDL4M8 | Main | [Us] rated supply voltage | 48...230 V AC
14231 | XVDL4M8 | Main | maximum power dissipation in W | 10 W
14232 | XVDL4M8 | Complementary | assembly style | Customer assembly
14233 | XVDL4M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14234 | XVDL4M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14235 | XVDL4M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14236 | XVDL4M8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
14237 | XVDL4M8 | Complementary | flashing frequency | 1 Hz
14238 | XVDL4M8 | Complementary | CAD overall width | 70 mm
14239 | XVDL4M8 | Complementary | CAD overall height | 133 mm
14240 | XVDL4M8 | Complementary | CAD overall depth | 70 mm
14241 | XVDL4M8 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
14242 | XVDL4M8 | Complementary | net weight | 0.275 kg
14243 | XVDL4M8 | Environment | pollution degree | 2
14244 | XVDL4M8 | Environment | product certifications | UL GOST CSA
14245 | XVDL4M8 | Environment | standards | EN/IEC 60947-5-1
14246 | XVDL4M8 | Environment | protective treatment | TC
14247 | XVDL4M8 | Environment | ambient air temperature for operation | -25…40 °C: incandescent -25…50 °C: LED
14248 | XVDL4M8 | Environment | ambient air temperature for storage | -40…70 °C
14249 | XVDL4M8 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14250 | XVDL4M8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14251 | XVDL4M8 | Contractual warranty | Warranty | 18 months
14252 | XVDL6B3 | Main | range of product | Harmony XVD Application
14253 | XVDL6B3 | Main | product or component type | Beacon
14254 | XVDL6B3 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14255 | XVDL6B3 | Main | signalling type | Flashing
14256 | XVDL6B3 | Main | mounting diameter | 70 mm
14257 | XVDL6B3 | Main | component name | XVD
14258 | XVDL6B3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14259 | XVDL6B3 | Main | light source | Integral flash discharge tube, green
14260 | XVDL6B3 | Main | bulb type | Flash discharge tube
14261 | XVDL6B3 | Main | [Us] rated supply voltage | 24 V AC/DC
14262 | XVDL6B3 | Complementary | assembly style | Customer assembly
14263 | XVDL6B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14264 | XVDL6B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14265 | XVDL6B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14266 | XVDL6B3 | Complementary | current consumption | < 350 mA DC < 550 mA AC
14267 | XVDL6B3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
14268 | XVDL6B3 | Complementary | flash energy | 5 J
14269 | XVDL6B3 | Complementary | flashing frequency | 1 Hz
14270 | XVDL6B3 | Complementary | CAD overall width | 70 mm
14271 | XVDL6B3 | Complementary | CAD overall height | 245 mm
14272 | XVDL6B3 | Complementary | CAD overall depth | 70 mm
14273 | XVDL6B3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
14274 | XVDL6B3 | Complementary | net weight | 0.48 kg
14275 | XVDL6B3 | Environment | product certifications | GOST CSA UL
14276 | XVDL6B3 | Environment | standards | EN/IEC 60947-5-1
14277 | XVDL6B3 | Environment | protective treatment | TC
14278 | XVDL6B3 | Environment | ambient air temperature for storage | -40…70 °C
14279 | XVDL6B3 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14280 | XVDL6B3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14281 | XVDL6B3 | Contractual warranty | Warranty | 18 months
14282 | XVDL6B4 | Main | range of product | Harmony XVD Application
14283 | XVDL6B4 | Main | product or component type | Beacon
14284 | XVDL6B4 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14285 | XVDL6B4 | Main | signalling type | Flashing
14286 | XVDL6B4 | Main | mounting diameter | 70 mm
14287 | XVDL6B4 | Main | component name | XVD
14288 | XVDL6B4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14289 | XVDL6B4 | Main | light source | Integral flash discharge tube, red
14290 | XVDL6B4 | Main | bulb type | Flash discharge tube
14291 | XVDL6B4 | Main | [Us] rated supply voltage | 24 V AC/DC
14292 | XVDL6B4 | Complementary | assembly style | Customer assembly
14293 | XVDL6B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14294 | XVDL6B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14295 | XVDL6B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14296 | XVDL6B4 | Complementary | current consumption | < 350 mA DC < 550 mA AC
14297 | XVDL6B4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14298 | XVDL6B4 | Complementary | flash energy | 5 J
14299 | XVDL6B4 | Complementary | flashing frequency | 1 Hz
14300 | XVDL6B4 | Complementary | CAD overall width | 70 mm
14301 | XVDL6B4 | Complementary | CAD overall height | 245 mm
14302 | XVDL6B4 | Complementary | CAD overall depth | 70 mm
14303 | XVDL6B4 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
14304 | XVDL6B4 | Complementary | net weight | 0.48 kg
14305 | XVDL6B4 | Environment | product certifications | GOST CSA UL
14306 | XVDL6B4 | Environment | standards | EN/IEC 60947-5-1
14307 | XVDL6B4 | Environment | protective treatment | TC
14308 | XVDL6B4 | Environment | ambient air temperature for storage | -40…70 °C
14309 | XVDL6B4 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14310 | XVDL6B4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14311 | XVDL6B4 | Contractual warranty | Warranty | 18 months
14312 | XVDL6B5 | Main | range of product | Harmony XVD Application
14313 | XVDL6B5 | Main | product or component type | Beacon
14314 | XVDL6B5 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14315 | XVDL6B5 | Main | signalling type | Flashing
14316 | XVDL6B5 | Main | mounting diameter | 70 mm
14317 | XVDL6B5 | Main | component name | XVD
14318 | XVDL6B5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14319 | XVDL6B5 | Main | light source | Integral flash discharge tube, orange
14320 | XVDL6B5 | Main | bulb type | Flash discharge tube
14321 | XVDL6B5 | Main | [Us] rated supply voltage | 24 V AC/DC
14322 | XVDL6B5 | Complementary | assembly style | Customer assembly
14323 | XVDL6B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14324 | XVDL6B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14325 | XVDL6B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14326 | XVDL6B5 | Complementary | current consumption | < 350 mA DC < 550 mA AC
14327 | XVDL6B5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14328 | XVDL6B5 | Complementary | flash energy | 5 J
14329 | XVDL6B5 | Complementary | flashing frequency | 1 Hz
14330 | XVDL6B5 | Complementary | CAD overall width | 70 mm
14331 | XVDL6B5 | Complementary | CAD overall height | 245 mm
14332 | XVDL6B5 | Complementary | CAD overall depth | 70 mm
14333 | XVDL6B5 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
14334 | XVDL6B5 | Complementary | net weight | 0.48 kg
14335 | XVDL6B5 | Environment | product certifications | UL CSA GOST
14336 | XVDL6B5 | Environment | standards | EN/IEC 60947-5-1
14337 | XVDL6B5 | Environment | protective treatment | TC
14338 | XVDL6B5 | Environment | ambient air temperature for storage | -40…70 °C
14339 | XVDL6B5 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14340 | XVDL6B5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14341 | XVDL6B5 | Contractual warranty | Warranty | 18 months
14342 | XVDL6B6 | Main | range of product | Harmony XVD Application
14343 | XVDL6B6 | Main | product or component type | Beacon
14344 | XVDL6B6 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14345 | XVDL6B6 | Main | signalling type | Flashing
14346 | XVDL6B6 | Main | mounting diameter | 70 mm
14347 | XVDL6B6 | Main | component name | XVD
14348 | XVDL6B6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14349 | XVDL6B6 | Main | light source | Integral flash discharge tube, blue
14350 | XVDL6B6 | Main | bulb type | Flash discharge tube
14351 | XVDL6B6 | Main | [Us] rated supply voltage | 24 V AC/DC
14352 | XVDL6B6 | Complementary | assembly style | Customer assembly
14353 | XVDL6B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14354 | XVDL6B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14355 | XVDL6B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14356 | XVDL6B6 | Complementary | current consumption | < 350 mA DC < 550 mA AC
14357 | XVDL6B6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14358 | XVDL6B6 | Complementary | flash energy | 5 J
14359 | XVDL6B6 | Complementary | flashing frequency | 1 Hz
14360 | XVDL6B6 | Complementary | CAD overall width | 70 mm
14361 | XVDL6B6 | Complementary | CAD overall height | 245 mm
14362 | XVDL6B6 | Complementary | CAD overall depth | 70 mm
14363 | XVDL6B6 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
14364 | XVDL6B6 | Complementary | net weight | 0.48 kg
14365 | XVDL6B6 | Environment | product certifications | CSA UL GOST
14366 | XVDL6B6 | Environment | standards | EN/IEC 60947-5-1
14367 | XVDL6B6 | Environment | protective treatment | TC
14368 | XVDL6B6 | Environment | ambient air temperature for storage | -40…70 °C
14369 | XVDL6B6 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14370 | XVDL6B6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14371 | XVDL6B6 | Contractual warranty | Warranty | 18 months
14372 | XVDL6B7 | Main | range of product | Harmony XVD Application
14373 | XVDL6B7 | Main | product or component type | Beacon
14374 | XVDL6B7 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14375 | XVDL6B7 | Main | signalling type | Flashing
14376 | XVDL6B7 | Main | mounting diameter | 70 mm
14377 | XVDL6B7 | Main | component name | XVD
14378 | XVDL6B7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14379 | XVDL6B7 | Main | light source | Integral flash discharge tube, clear
14380 | XVDL6B7 | Main | bulb type | Flash discharge tube
14381 | XVDL6B7 | Main | [Us] rated supply voltage | 24 V AC/DC
14382 | XVDL6B7 | Complementary | assembly style | Customer assembly
14383 | XVDL6B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14384 | XVDL6B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14385 | XVDL6B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14386 | XVDL6B7 | Complementary | current consumption | < 350 mA DC < 550 mA AC
14387 | XVDL6B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
14388 | XVDL6B7 | Complementary | flash energy | 5 J
14389 | XVDL6B7 | Complementary | flashing frequency | 1 Hz
14390 | XVDL6B7 | Complementary | illuminating intensity | 13 cd
14391 | XVDL6B7 | Complementary | CAD overall width | 70 mm
14392 | XVDL6B7 | Complementary | CAD overall height | 245 mm
14393 | XVDL6B7 | Complementary | CAD overall depth | 70 mm
14394 | XVDL6B7 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
14395 | XVDL6B7 | Complementary | net weight | 0.48 kg
14396 | XVDL6B7 | Environment | product certifications | UL CSA GOST
14397 | XVDL6B7 | Environment | standards | EN/IEC 60947-5-1
14398 | XVDL6B7 | Environment | protective treatment | TC
14399 | XVDL6B7 | Environment | ambient air temperature for storage | -40…70 °C
14400 | XVDL6B7 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14401 | XVDL6B7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14402 | XVDL6B7 | Contractual warranty | Warranty | 18 months
14403 | XVDL6B8 | Main | range of product | Harmony XVD Application
14404 | XVDL6B8 | Main | product or component type | Beacon
14405 | XVDL6B8 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14406 | XVDL6B8 | Main | signalling type | Flashing
14407 | XVDL6B8 | Main | mounting diameter | 70 mm
14408 | XVDL6B8 | Main | component name | XVD
14409 | XVDL6B8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14410 | XVDL6B8 | Main | light source | Integral flash discharge tube, yellow
14411 | XVDL6B8 | Main | bulb type | Flash discharge tube
14412 | XVDL6B8 | Main | [Us] rated supply voltage | 24 V AC/DC
14413 | XVDL6B8 | Complementary | assembly style | Customer assembly
14414 | XVDL6B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14415 | XVDL6B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14416 | XVDL6B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14417 | XVDL6B8 | Complementary | current consumption | < 350 mA DC < 550 mA AC
14418 | XVDL6B8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14419 | XVDL6B8 | Complementary | flash energy | 5 J
14420 | XVDL6B8 | Complementary | flashing frequency | 1 Hz
14421 | XVDL6B8 | Complementary | CAD overall width | 70 mm
14422 | XVDL6B8 | Complementary | CAD overall height | 245 mm
14423 | XVDL6B8 | Complementary | CAD overall depth | 70 mm
14424 | XVDL6B8 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
14425 | XVDL6B8 | Complementary | net weight | 0.48 kg
14426 | XVDL6B8 | Environment | product certifications | GOST UL CSA
14427 | XVDL6B8 | Environment | standards | EN/IEC 60947-5-1
14428 | XVDL6B8 | Environment | protective treatment | TC
14429 | XVDL6B8 | Environment | ambient air temperature for storage | -40…70 °C
14430 | XVDL6B8 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14431 | XVDL6B8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14432 | XVDL6B8 | Contractual warranty | Warranty | 18 months
14433 | XVDL6M3 | Main | range of product | Harmony XVD Application
14434 | XVDL6M3 | Main | product or component type | Beacon
14435 | XVDL6M3 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14436 | XVDL6M3 | Main | signalling type | Flashing
14437 | XVDL6M3 | Main | mounting diameter | 70 mm
14438 | XVDL6M3 | Main | component name | XVD
14439 | XVDL6M3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14440 | XVDL6M3 | Main | light source | Integral flash discharge tube, green
14441 | XVDL6M3 | Main | bulb type | Flash discharge tube
14442 | XVDL6M3 | Main | [Us] rated supply voltage | 230 V AC
14443 | XVDL6M3 | Complementary | assembly style | Customer assembly
14444 | XVDL6M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14445 | XVDL6M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14446 | XVDL6M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14447 | XVDL6M3 | Complementary | current consumption | < 105 mA AC
14448 | XVDL6M3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
14449 | XVDL6M3 | Complementary | flash energy | 5 J
14450 | XVDL6M3 | Complementary | flashing frequency | 1 Hz
14451 | XVDL6M3 | Complementary | CAD overall width | 70 mm
14452 | XVDL6M3 | Complementary | CAD overall height | 245 mm
14453 | XVDL6M3 | Complementary | CAD overall depth | 70 mm
14454 | XVDL6M3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
14455 | XVDL6M3 | Complementary | net weight | 0.475 kg
14456 | XVDL6M3 | Environment | product certifications | GOST UL CSA
14457 | XVDL6M3 | Environment | standards | EN/IEC 60947-5-1
14458 | XVDL6M3 | Environment | protective treatment | TC
14459 | XVDL6M3 | Environment | ambient air temperature for storage | -40…70 °C
14460 | XVDL6M3 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14461 | XVDL6M3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14462 | XVDL6M3 | Contractual warranty | Warranty | 18 months
14463 | XVDL6M4 | Main | range of product | Harmony XVD Application
14464 | XVDL6M4 | Main | product or component type | Beacon
14465 | XVDL6M4 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14466 | XVDL6M4 | Main | signalling type | Flashing
14467 | XVDL6M4 | Main | mounting diameter | 70 mm
14468 | XVDL6M4 | Main | component name | XVD
14469 | XVDL6M4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14470 | XVDL6M4 | Main | light source | Integral flash discharge tube, red
14471 | XVDL6M4 | Main | bulb type | Flash discharge tube
14472 | XVDL6M4 | Main | [Us] rated supply voltage | 230 V AC
14473 | XVDL6M4 | Complementary | assembly style | Customer assembly
14474 | XVDL6M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14475 | XVDL6M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14476 | XVDL6M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14477 | XVDL6M4 | Complementary | current consumption | < 105 mA AC
14478 | XVDL6M4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14479 | XVDL6M4 | Complementary | flash energy | 5 J
14480 | XVDL6M4 | Complementary | flashing frequency | 1 Hz
14481 | XVDL6M4 | Complementary | CAD overall width | 70 mm
14482 | XVDL6M4 | Complementary | CAD overall height | 245 mm
14483 | XVDL6M4 | Complementary | CAD overall depth | 70 mm
14484 | XVDL6M4 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
14485 | XVDL6M4 | Complementary | net weight | 0.475 kg
14486 | XVDL6M4 | Environment | product certifications | UL CSA GOST
14487 | XVDL6M4 | Environment | standards | EN/IEC 60947-5-1
14488 | XVDL6M4 | Environment | protective treatment | TC
14489 | XVDL6M4 | Environment | ambient air temperature for storage | -40…70 °C
14490 | XVDL6M4 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14491 | XVDL6M4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14492 | XVDL6M4 | Contractual warranty | Warranty | 18 months
14493 | XVDL6M5 | Main | range of product | Harmony XVD Application
14494 | XVDL6M5 | Main | product or component type | Beacon
14495 | XVDL6M5 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14496 | XVDL6M5 | Main | signalling type | Flashing
14497 | XVDL6M5 | Main | mounting diameter | 70 mm
14498 | XVDL6M5 | Main | component name | XVD
14499 | XVDL6M5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14500 | XVDL6M5 | Main | light source | Integral flash discharge tube, orange
14501 | XVDL6M5 | Main | bulb type | Flash discharge tube
14502 | XVDL6M5 | Main | [Us] rated supply voltage | 230 V AC
14503 | XVDL6M5 | Complementary | assembly style | Customer assembly
14504 | XVDL6M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14505 | XVDL6M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14506 | XVDL6M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14507 | XVDL6M5 | Complementary | current consumption | < 105 mA AC
14508 | XVDL6M5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
14509 | XVDL6M5 | Complementary | flash energy | 5 J
14510 | XVDL6M5 | Complementary | flashing frequency | 1 Hz
14511 | XVDL6M5 | Complementary | CAD overall width | 70 mm
14512 | XVDL6M5 | Complementary | CAD overall height | 245 mm
14513 | XVDL6M5 | Complementary | CAD overall depth | 70 mm
14514 | XVDL6M5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
14515 | XVDL6M5 | Complementary | net weight | 0.475 kg
14516 | XVDL6M5 | Environment | product certifications | UL GOST CSA
14517 | XVDL6M5 | Environment | standards | EN/IEC 60947-5-1
14518 | XVDL6M5 | Environment | protective treatment | TC
14519 | XVDL6M5 | Environment | ambient air temperature for operation | -25…50 °C
14520 | XVDL6M5 | Environment | ambient air temperature for storage | -40…70 °C
14521 | XVDL6M5 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14522 | XVDL6M5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14523 | XVDL6M5 | Contractual warranty | Warranty | 18 months
14524 | XVDL6M6 | Main | range of product | Harmony XVD Application
14525 | XVDL6M6 | Main | product or component type | Beacon
14526 | XVDL6M6 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14527 | XVDL6M6 | Main | signalling type | Flashing
14528 | XVDL6M6 | Main | mounting diameter | 70 mm
14529 | XVDL6M6 | Main | component name | XVD
14530 | XVDL6M6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14531 | XVDL6M6 | Main | light source | Integral flash discharge tube, blue
14532 | XVDL6M6 | Main | bulb type | Flash discharge tube
14533 | XVDL6M6 | Main | [Us] rated supply voltage | 230 V AC
14534 | XVDL6M6 | Complementary | assembly style | Customer assembly
14535 | XVDL6M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14536 | XVDL6M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14537 | XVDL6M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14538 | XVDL6M6 | Complementary | current consumption | < 105 mA AC
14539 | XVDL6M6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14540 | XVDL6M6 | Complementary | flash energy | 5 J
14541 | XVDL6M6 | Complementary | flashing frequency | 1 Hz
14542 | XVDL6M6 | Complementary | CAD overall width | 70 mm
14543 | XVDL6M6 | Complementary | CAD overall height | 245 mm
14544 | XVDL6M6 | Complementary | CAD overall depth | 70 mm
14545 | XVDL6M6 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
14546 | XVDL6M6 | Complementary | net weight | 0.475 kg
14547 | XVDL6M6 | Environment | product certifications | CSA UL GOST
14548 | XVDL6M6 | Environment | standards | EN/IEC 60947-5-1
14549 | XVDL6M6 | Environment | protective treatment | TC
14550 | XVDL6M6 | Environment | ambient air temperature for operation | -25…50 °C
14551 | XVDL6M6 | Environment | ambient air temperature for storage | -40…70 °C
14552 | XVDL6M6 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14553 | XVDL6M6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14554 | XVDL6M6 | Contractual warranty | Warranty | 18 months
14555 | XVDL6M7 | Main | range of product | Harmony XVD Application
14556 | XVDL6M7 | Main | product or component type | Beacon
14557 | XVDL6M7 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14558 | XVDL6M7 | Main | signalling type | Flashing
14559 | XVDL6M7 | Main | mounting diameter | 70 mm
14560 | XVDL6M7 | Main | component name | XVD
14561 | XVDL6M7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14562 | XVDL6M7 | Main | light source | Integral flash discharge tube, clear
14563 | XVDL6M7 | Main | bulb type | Flash discharge tube
14564 | XVDL6M7 | Main | [Us] rated supply voltage | 230 V AC
14565 | XVDL6M7 | Complementary | assembly style | Customer assembly
14566 | XVDL6M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14567 | XVDL6M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14568 | XVDL6M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14569 | XVDL6M7 | Complementary | current consumption | < 105 mA AC
14570 | XVDL6M7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14571 | XVDL6M7 | Complementary | flash energy | 5 J
14572 | XVDL6M7 | Complementary | flashing frequency | 1 Hz
14573 | XVDL6M7 | Complementary | illuminating intensity | 13 cd
14574 | XVDL6M7 | Complementary | CAD overall width | 70 mm
14575 | XVDL6M7 | Complementary | CAD overall height | 245 mm
14576 | XVDL6M7 | Complementary | CAD overall depth | 70 mm
14577 | XVDL6M7 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
14578 | XVDL6M7 | Complementary | net weight | 0.475 kg
14579 | XVDL6M7 | Environment | product certifications | CSA GOST UL
14580 | XVDL6M7 | Environment | standards | EN/IEC 60947-5-1
14581 | XVDL6M7 | Environment | protective treatment | TC
14582 | XVDL6M7 | Environment | ambient air temperature for operation | -25…50 °C
14583 | XVDL6M7 | Environment | ambient air temperature for storage | -40…70 °C
14584 | XVDL6M7 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14585 | XVDL6M7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14586 | XVDL6M7 | Contractual warranty | Warranty | 18 months
14587 | XVDL6M8 | Main | range of product | Harmony XVD Application
14588 | XVDL6M8 | Main | product or component type | Beacon
14589 | XVDL6M8 | Main | beacon or indicator bank unit type | Base unit Illuminated unit
14590 | XVDL6M8 | Main | signalling type | Flashing
14591 | XVDL6M8 | Main | mounting diameter | 70 mm
14592 | XVDL6M8 | Main | component name | XVD
14593 | XVDL6M8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
14594 | XVDL6M8 | Main | light source | Integral flash discharge tube, yellow
14595 | XVDL6M8 | Main | bulb type | Flash discharge tube
14596 | XVDL6M8 | Main | [Us] rated supply voltage | 230 V AC
14597 | XVDL6M8 | Complementary | assembly style | Customer assembly
14598 | XVDL6M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
14599 | XVDL6M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14600 | XVDL6M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14601 | XVDL6M8 | Complementary | current consumption | < 105 mA AC
14602 | XVDL6M8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14603 | XVDL6M8 | Complementary | flash energy | 5 J
14604 | XVDL6M8 | Complementary | flashing frequency | 1 Hz
14605 | XVDL6M8 | Complementary | CAD overall width | 70 mm
14606 | XVDL6M8 | Complementary | CAD overall height | 245 mm
14607 | XVDL6M8 | Complementary | CAD overall depth | 70 mm
14608 | XVDL6M8 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
14609 | XVDL6M8 | Complementary | net weight | 0.475 kg
14610 | XVDL6M8 | Environment | product certifications | GOST CSA UL
14611 | XVDL6M8 | Environment | standards | EN/IEC 60947-5-1
14612 | XVDL6M8 | Environment | protective treatment | TC
14613 | XVDL6M8 | Environment | ambient air temperature for operation | -25…50 °C
14614 | XVDL6M8 | Environment | ambient air temperature for storage | -40…70 °C
14615 | XVDL6M8 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536
14616 | XVDL6M8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
14617 | XVDL6M8 | Contractual warranty | Warranty | 18 months
14618 | XVMB1RA | Main | range of product | Harmony XVM
14619 | XVMB1RA | Main | product or component type | Pre-assembled and pre-cabled indicator bank
14620 | XVMB1RA | Main | beacon or indicator bank unit type | 2 illuminated units
14621 | XVMB1RA | Main | component name | XVM
14622 | XVMB1RA | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
14623 | XVMB1RA | Main | light block color | Red/orange
14624 | XVMB1RA | Main | [Us] rated supply voltage | 24 V AC/DC
14625 | XVMB1RA | Main | indicator bank base type | Base without buzzer
14626 | XVMB1RA | Main | mounting mode | Vertical
14627 | XVMB1RA | Complementary | kit composition | Plastic fixing plate Aluminium support tube Cover Base unit
14628 | XVMB1RA | Complementary | mounting diameter | 45 mm
14629 | XVMB1RA | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
14630 | XVMB1RA | Complementary | marking | CE
14631 | XVMB1RA | Complementary | mounting support | Aluminium tube
14632 | XVMB1RA | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14633 | XVMB1RA | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14634 | XVMB1RA | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14635 | XVMB1RA | Complementary | net weight | 0.392 kg
14636 | XVMB1RA | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
14637 | XVMB1RA | Environment | product certifications | CCC
14638 | XVMB1RA | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
14639 | XVMB1RA | Environment | ambient air temperature for storage | -25…70 °C
14640 | XVMB1RA | Environment | ambient air temperature for operation | -10…50 °C
14641 | XVMB1RA | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
14642 | XVMB1RA | Environment | protective treatment | TC
14643 | XVMB1RA | Packing Units | Package 1 Weight | 0.393 kg
14644 | XVMB1RA | Offer Sustainability | Sustainable offer status | Green Premium product
14645 | XVMB1RA | Offer Sustainability | REACh Regulation | REACh Declaration
14646 | XVMB1RA | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
14647 | XVMB1RA | Offer Sustainability | Mercury free | Yes
14648 | XVMB1RA | Offer Sustainability | RoHS exemption information | Yes
14649 | XVMB1RA | Offer Sustainability | China RoHS Regulation | China RoHS declaration
14650 | XVMB1RA | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
14651 | XVMB1RA | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
14652 | XVMB1RA | Contractual warranty | Warranty | 18 months
14653 | XVMB1RG | Main | range of product | Harmony XVM
14654 | XVMB1RG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
14655 | XVMB1RG | Main | beacon or indicator bank unit type | 2 illuminated units
14656 | XVMB1RG | Main | component name | XVM
14657 | XVMB1RG | Main | light source | Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
14658 | XVMB1RG | Main | light block color | Red/green
14659 | XVMB1RG | Main | [Us] rated supply voltage | 24 V AC/DC
14660 | XVMB1RG | Main | indicator bank base type | Base without buzzer
14661 | XVMB1RG | Main | mounting mode | Vertical
14662 | XVMB1RG | Complementary | kit composition | Base unit Aluminium support tube Cover Plastic fixing plate
14663 | XVMB1RG | Complementary | mounting diameter | 45 mm
14664 | XVMB1RG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
14665 | XVMB1RG | Complementary | marking | CE
14666 | XVMB1RG | Complementary | mounting support | Aluminium tube
14667 | XVMB1RG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14668 | XVMB1RG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14669 | XVMB1RG | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14670 | XVMB1RG | Complementary | net weight | 0.392 kg
14671 | XVMB1RG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
14672 | XVMB1RG | Environment | product certifications | CCC
14673 | XVMB1RG | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
14674 | XVMB1RG | Environment | ambient air temperature for storage | -25…70 °C
14675 | XVMB1RG | Environment | ambient air temperature for operation | -10…50 °C
14676 | XVMB1RG | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
14677 | XVMB1RG | Environment | protective treatment | TC
14678 | XVMB1RG | Packing Units | Package 1 Weight | 498 g
14679 | XVMB1RG | Packing Units | Package 2 Weight | 11.194 kg
14680 | XVMB1RG | Offer Sustainability | Sustainable offer status | Green Premium product
14681 | XVMB1RG | Offer Sustainability | REACh Regulation | REACh Declaration
14682 | XVMB1RG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
14683 | XVMB1RG | Offer Sustainability | Mercury free | Yes
14684 | XVMB1RG | Offer Sustainability | RoHS exemption information | Yes
14685 | XVMB1RG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
14686 | XVMB1RG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
14687 | XVMB1RG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
14688 | XVMB1RG | Contractual warranty | Warranty | 18 months
14689 | XVMG1RA | Main | range of product | Harmony XVM
14690 | XVMG1RA | Main | product or component type | Pre-assembled and pre-cabled indicator bank
14691 | XVMG1RA | Main | beacon or indicator bank unit type | 2 illuminated units
14692 | XVMG1RA | Main | component name | XVM
14693 | XVMG1RA | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
14694 | XVMG1RA | Main | light block color | Red/orange
14695 | XVMG1RA | Main | [Us] rated supply voltage | 120 V AC/DC
14696 | XVMG1RA | Main | indicator bank base type | Base without buzzer
14697 | XVMG1RA | Main | mounting mode | Vertical
14698 | XVMG1RA | Complementary | kit composition | Cover Aluminium support tube Plastic fixing plate Base unit
14699 | XVMG1RA | Complementary | mounting diameter | 45 mm
14700 | XVMG1RA | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
14701 | XVMG1RA | Complementary | marking | CE
14702 | XVMG1RA | Complementary | mounting support | Aluminium tube
14703 | XVMG1RA | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14704 | XVMG1RA | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14705 | XVMG1RA | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
14706 | XVMG1RA | Complementary | net weight | 0.392 kg
14707 | XVMG1RA | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
14708 | XVMG1RA | Environment | product certifications | CCC
14709 | XVMG1RA | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
14710 | XVMG1RA | Environment | ambient air temperature for storage | -25…70 °C
14711 | XVMG1RA | Environment | ambient air temperature for operation | -10…50 °C
14712 | XVMG1RA | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
14713 | XVMG1RA | Environment | protective treatment | TC
14714 | XVMG1RA | Contractual warranty | Warranty | 18 months
14715 | XVMG1RG | Main | range of product | Harmony XVM
14716 | XVMG1RG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
14717 | XVMG1RG | Main | beacon or indicator bank unit type | 2 illuminated units
14718 | XVMG1RG | Main | component name | XVM
14719 | XVMG1RG | Main | light source | Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
14720 | XVMG1RG | Main | light block color | Red/green
14721 | XVMG1RG | Main | [Us] rated supply voltage | 120 V AC/DC
14722 | XVMG1RG | Main | indicator bank base type | Base without buzzer
14723 | XVMG1RG | Main | mounting mode | Vertical
14724 | XVMG1RG | Complementary | kit composition | Cover Aluminium support tube Base unit Plastic fixing plate
14725 | XVMG1RG | Complementary | mounting diameter | 45 mm
14726 | XVMG1RG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
14727 | XVMG1RG | Complementary | marking | CE
14728 | XVMG1RG | Complementary | mounting support | Aluminium tube
14729 | XVMG1RG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14730 | XVMG1RG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14731 | XVMG1RG | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
14732 | XVMG1RG | Complementary | net weight | 0.392 kg
14733 | XVMG1RG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
14734 | XVMG1RG | Environment | product certifications | CCC
14735 | XVMG1RG | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
14736 | XVMG1RG | Environment | ambient air temperature for storage | -25…70 °C
14737 | XVMG1RG | Environment | ambient air temperature for operation | -10…50 °C
14738 | XVMG1RG | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
14739 | XVMG1RG | Environment | protective treatment | TC
14740 | XVMG1RG | Offer Sustainability | Sustainable offer status | Green Premium product
14741 | XVMG1RG | Offer Sustainability | REACh Regulation | REACh Declaration
14742 | XVMG1RG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
14743 | XVMG1RG | Offer Sustainability | Mercury free | Yes
14744 | XVMG1RG | Offer Sustainability | RoHS exemption information | Yes
14745 | XVMG1RG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
14746 | XVMG1RG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
14747 | XVMG1RG | Contractual warranty | Warranty | 18 months
14748 | XVMM1RA | Main | range of product | Harmony XVM
14749 | XVMM1RA | Main | product or component type | Pre-assembled and pre-cabled indicator bank
14750 | XVMM1RA | Main | beacon or indicator bank unit type | 2 illuminated units
14751 | XVMM1RA | Main | component name | XVM
14752 | XVMM1RA | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
14753 | XVMM1RA | Main | light block color | Red/orange
14754 | XVMM1RA | Main | [Us] rated supply voltage | 230 V AC/DC
14755 | XVMM1RA | Main | indicator bank base type | Base without buzzer
14756 | XVMM1RA | Main | mounting mode | Vertical
14757 | XVMM1RA | Complementary | kit composition | Aluminium support tube Plastic fixing plate Cover Base unit
14758 | XVMM1RA | Complementary | mounting diameter | 45 mm
14759 | XVMM1RA | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
14760 | XVMM1RA | Complementary | marking | CE
14761 | XVMM1RA | Complementary | mounting support | Aluminium tube
14762 | XVMM1RA | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14763 | XVMM1RA | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14764 | XVMM1RA | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14765 | XVMM1RA | Complementary | net weight | 0.392 kg
14766 | XVMM1RA | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
14767 | XVMM1RA | Environment | product certifications | CCC
14768 | XVMM1RA | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
14769 | XVMM1RA | Environment | ambient air temperature for storage | -25…70 °C
14770 | XVMM1RA | Environment | ambient air temperature for operation | -10…50 °C
14771 | XVMM1RA | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
14772 | XVMM1RA | Environment | protective treatment | TC
14773 | XVMM1RA | Offer Sustainability | Sustainable offer status | Green Premium product
14774 | XVMM1RA | Offer Sustainability | REACh Regulation | REACh Declaration
14775 | XVMM1RA | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
14776 | XVMM1RA | Offer Sustainability | Mercury free | Yes
14777 | XVMM1RA | Offer Sustainability | RoHS exemption information | Yes
14778 | XVMM1RA | Offer Sustainability | China RoHS Regulation | China RoHS declaration
14779 | XVMM1RA | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
14780 | XVMM1RA | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
14781 | XVMM1RA | Contractual warranty | Warranty | 18 months
14782 | XVMM1RG | Main | range of product | Harmony XVM
14783 | XVMM1RG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
14784 | XVMM1RG | Main | beacon or indicator bank unit type | 2 illuminated units
14785 | XVMM1RG | Main | component name | XVM
14786 | XVMM1RG | Main | light source | Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
14787 | XVMM1RG | Main | light block color | Red/green
14788 | XVMM1RG | Main | [Us] rated supply voltage | 230 V AC/DC
14789 | XVMM1RG | Main | indicator bank base type | Base without buzzer
14790 | XVMM1RG | Main | mounting mode | Vertical
14791 | XVMM1RG | Complementary | kit composition | Plastic fixing plate Cover Base unit Aluminium support tube
14792 | XVMM1RG | Complementary | mounting diameter | 45 mm
14793 | XVMM1RG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
14794 | XVMM1RG | Complementary | marking | CE
14795 | XVMM1RG | Complementary | mounting support | Aluminium tube
14796 | XVMM1RG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14797 | XVMM1RG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14798 | XVMM1RG | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14799 | XVMM1RG | Complementary | net weight | 0.392 kg
14800 | XVMM1RG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
14801 | XVMM1RG | Environment | product certifications | CCC
14802 | XVMM1RG | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
14803 | XVMM1RG | Environment | ambient air temperature for storage | -25…70 °C
14804 | XVMM1RG | Environment | ambient air temperature for operation | -10…50 °C
14805 | XVMM1RG | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
14806 | XVMM1RG | Environment | protective treatment | TC
14807 | XVMM1RG | Packing Units | Package 1 Weight | 500 g
14808 | XVMM1RG | Packing Units | Package 2 Weight | 11.064 kg
14809 | XVMM1RG | Offer Sustainability | Sustainable offer status | Green Premium product
14810 | XVMM1RG | Offer Sustainability | REACh Regulation | REACh Declaration
14811 | XVMM1RG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
14812 | XVMM1RG | Offer Sustainability | Mercury free | Yes
14813 | XVMM1RG | Offer Sustainability | RoHS exemption information | Yes
14814 | XVMM1RG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
14815 | XVMM1RG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
14816 | XVMM1RG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
14817 | XVMM1RG | Contractual warranty | Warranty | 18 months
14818 | XVMB1RAS | Main | range of product | Harmony XVM
14819 | XVMB1RAS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
14820 | XVMB1RAS | Main | beacon or indicator bank unit type | 2 illuminated units
14821 | XVMB1RAS | Main | component name | XVM
14822 | XVMB1RAS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
14823 | XVMB1RAS | Main | light block color | Red/orange
14824 | XVMB1RAS | Main | [Us] rated supply voltage | 24 V AC/DC
14825 | XVMB1RAS | Main | indicator bank base type | Base with integrated buzzer
14826 | XVMB1RAS | Main | mounting mode | Vertical
14827 | XVMB1RAS | Complementary | kit composition | Cover Plastic fixing plate Aluminium support tube Base unit
14828 | XVMB1RAS | Complementary | mounting diameter | 45 mm
14829 | XVMB1RAS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
14830 | XVMB1RAS | Complementary | marking | CE
14831 | XVMB1RAS | Complementary | mounting support | Aluminium tube
14832 | XVMB1RAS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14833 | XVMB1RAS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14834 | XVMB1RAS | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14835 | XVMB1RAS | Complementary | fundamental frequency | 4 kHz
14836 | XVMB1RAS | Complementary | net weight | 0.402 kg
14837 | XVMB1RAS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
14838 | XVMB1RAS | Environment | product certifications | CCC
14839 | XVMB1RAS | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
14840 | XVMB1RAS | Environment | ambient air temperature for storage | -25…70 °C
14841 | XVMB1RAS | Environment | ambient air temperature for operation | -10…50 °C
14842 | XVMB1RAS | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
14843 | XVMB1RAS | Environment | protective treatment | TC
14844 | XVMB1RAS | Environment | noise level | 0…80 dB at 1 m
14845 | XVMB1RAS | Contractual warranty | Warranty | 18 months
14846 | XVMB1RGS | Main | range of product | Harmony XVM
14847 | XVMB1RGS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
14848 | XVMB1RGS | Main | beacon or indicator bank unit type | 2 illuminated units
14849 | XVMB1RGS | Main | component name | XVM
14850 | XVMB1RGS | Main | light source | Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
14851 | XVMB1RGS | Main | light block color | Red/green
14852 | XVMB1RGS | Main | [Us] rated supply voltage | 24 V AC/DC
14853 | XVMB1RGS | Main | indicator bank base type | Base with integrated buzzer
14854 | XVMB1RGS | Main | mounting mode | Vertical
14855 | XVMB1RGS | Complementary | kit composition | Plastic fixing plate Aluminium support tube Cover Base unit
14856 | XVMB1RGS | Complementary | mounting diameter | 45 mm
14857 | XVMB1RGS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
14858 | XVMB1RGS | Complementary | marking | CE
14859 | XVMB1RGS | Complementary | mounting support | Aluminium tube
14860 | XVMB1RGS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14861 | XVMB1RGS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14862 | XVMB1RGS | Complementary | current consumption | 15 mA on base unit
14863 | XVMB1RGS | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14864 | XVMB1RGS | Complementary | fundamental frequency | 4 kHz
14865 | XVMB1RGS | Complementary | net weight | 0.402 kg
14866 | XVMB1RGS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
14867 | XVMB1RGS | Environment | product certifications | CCC
14868 | XVMB1RGS | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
14869 | XVMB1RGS | Environment | ambient air temperature for storage | -25…70 °C
14870 | XVMB1RGS | Environment | ambient air temperature for operation | -10…50 °C
14871 | XVMB1RGS | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
14872 | XVMB1RGS | Environment | protective treatment | TC
14873 | XVMB1RGS | Environment | noise level | 0…80 dB at 1 m
14874 | XVMB1RGS | Packing Units | Package 1 Weight | 512 g
14875 | XVMB1RGS | Packing Units | Package 2 Weight | 11.476 kg
14876 | XVMB1RGS | Offer Sustainability | Sustainable offer status | Green Premium product
14877 | XVMB1RGS | Offer Sustainability | REACh Regulation | REACh Declaration
14878 | XVMB1RGS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
14879 | XVMB1RGS | Offer Sustainability | Mercury free | Yes
14880 | XVMB1RGS | Offer Sustainability | RoHS exemption information | Yes
14881 | XVMB1RGS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
14882 | XVMB1RGS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
14883 | XVMB1RGS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
14884 | XVMB1RGS | Contractual warranty | Warranty | 18 months
14885 | XVMG1RAS | Main | range of product | Harmony XVM
14886 | XVMG1RAS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
14887 | XVMG1RAS | Main | beacon or indicator bank unit type | 2 illuminated units
14888 | XVMG1RAS | Main | component name | XVM
14889 | XVMG1RAS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
14890 | XVMG1RAS | Main | light block color | Red/orange
14891 | XVMG1RAS | Main | [Us] rated supply voltage | 120 V AC
14892 | XVMG1RAS | Main | indicator bank base type | Base with integrated buzzer
14893 | XVMG1RAS | Main | mounting mode | Vertical
14894 | XVMG1RAS | Complementary | kit composition | Plastic fixing plate Aluminium support tube Cover Base unit
14895 | XVMG1RAS | Complementary | mounting diameter | 45 mm
14896 | XVMG1RAS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
14897 | XVMG1RAS | Complementary | marking | CE
14898 | XVMG1RAS | Complementary | mounting support | Aluminium tube
14899 | XVMG1RAS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14900 | XVMG1RAS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14901 | XVMG1RAS | Complementary | current consumption | 18 mA on base unit
14902 | XVMG1RAS | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14903 | XVMG1RAS | Complementary | fundamental frequency | 4 kHz
14904 | XVMG1RAS | Complementary | net weight | 0.402 kg
14905 | XVMG1RAS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
14906 | XVMG1RAS | Environment | product certifications | CCC
14907 | XVMG1RAS | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
14908 | XVMG1RAS | Environment | ambient air temperature for storage | -25…70 °C
14909 | XVMG1RAS | Environment | ambient air temperature for operation | -10…50 °C
14910 | XVMG1RAS | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
14911 | XVMG1RAS | Environment | protective treatment | TC
14912 | XVMG1RAS | Environment | noise level | 0…80 dB at 1 m
14913 | XVMG1RAS | Contractual warranty | Warranty | 18 months
14914 | XVMM1RAS | Main | range of product | Harmony XVM
14915 | XVMM1RAS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
14916 | XVMM1RAS | Main | beacon or indicator bank unit type | 2 illuminated units
14917 | XVMM1RAS | Main | component name | XVM
14918 | XVMM1RAS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
14919 | XVMM1RAS | Main | light block color | Red/orange
14920 | XVMM1RAS | Main | [Us] rated supply voltage | 230 V AC
14921 | XVMM1RAS | Main | indicator bank base type | Base with integrated buzzer
14922 | XVMM1RAS | Main | mounting mode | Vertical
14923 | XVMM1RAS | Complementary | kit composition | Plastic fixing plate Cover Base unit Aluminium support tube
14924 | XVMM1RAS | Complementary | mounting diameter | 45 mm
14925 | XVMM1RAS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
14926 | XVMM1RAS | Complementary | marking | CE
14927 | XVMM1RAS | Complementary | mounting support | Aluminium tube
14928 | XVMM1RAS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14929 | XVMM1RAS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14930 | XVMM1RAS | Complementary | current consumption | 18 mA on base unit
14931 | XVMM1RAS | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14932 | XVMM1RAS | Complementary | fundamental frequency | 4 kHz
14933 | XVMM1RAS | Complementary | net weight | 0.402 kg
14934 | XVMM1RAS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
14935 | XVMM1RAS | Environment | product certifications | CCC
14936 | XVMM1RAS | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
14937 | XVMM1RAS | Environment | ambient air temperature for storage | -25…70 °C
14938 | XVMM1RAS | Environment | ambient air temperature for operation | -10…50 °C
14939 | XVMM1RAS | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
14940 | XVMM1RAS | Environment | protective treatment | TC
14941 | XVMM1RAS | Environment | noise level | 0…80 dB at 1 m
14942 | XVMM1RAS | Contractual warranty | Warranty | 18 months
14943 | XVMM1RGS | Main | range of product | Harmony XVM
14944 | XVMM1RGS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
14945 | XVMM1RGS | Main | beacon or indicator bank unit type | 2 illuminated units
14946 | XVMM1RGS | Main | component name | XVM
14947 | XVMM1RGS | Main | light source | Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
14948 | XVMM1RGS | Main | light block color | Red/green
14949 | XVMM1RGS | Main | [Us] rated supply voltage | 230 V AC
14950 | XVMM1RGS | Main | indicator bank base type | Base with integrated buzzer
14951 | XVMM1RGS | Main | mounting mode | Vertical
14952 | XVMM1RGS | Complementary | kit composition | Cover Aluminium support tube Plastic fixing plate Base unit
14953 | XVMM1RGS | Complementary | mounting diameter | 45 mm
14954 | XVMM1RGS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
14955 | XVMM1RGS | Complementary | marking | CE
14956 | XVMM1RGS | Complementary | mounting support | Aluminium tube
14957 | XVMM1RGS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14958 | XVMM1RGS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14959 | XVMM1RGS | Complementary | current consumption | 18 mA on base unit
14960 | XVMM1RGS | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
14961 | XVMM1RGS | Complementary | fundamental frequency | 4 kHz
14962 | XVMM1RGS | Complementary | net weight | 0.402 kg
14963 | XVMM1RGS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
14964 | XVMM1RGS | Environment | product certifications | CCC
14965 | XVMM1RGS | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
14966 | XVMM1RGS | Environment | ambient air temperature for storage | -25…70 °C
14967 | XVMM1RGS | Environment | ambient air temperature for operation | -10…50 °C
14968 | XVMM1RGS | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
14969 | XVMM1RGS | Environment | protective treatment | TC
14970 | XVMM1RGS | Environment | noise level | 0…80 dB at 1 m
14971 | XVMM1RGS | Packing Units | Package 1 Weight | 512 g
14972 | XVMM1RGS | Packing Units | Package 2 Weight | 11.494 kg
14973 | XVMM1RGS | Offer Sustainability | Sustainable offer status | Green Premium product
14974 | XVMM1RGS | Offer Sustainability | REACh Regulation | REACh Declaration
14975 | XVMM1RGS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
14976 | XVMM1RGS | Offer Sustainability | Mercury free | Yes
14977 | XVMM1RGS | Offer Sustainability | RoHS exemption information | Yes
14978 | XVMM1RGS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
14979 | XVMM1RGS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
14980 | XVMM1RGS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
14981 | XVMM1RGS | Contractual warranty | Warranty | 18 months
14982 | XVMB1RAG | Main | range of product | Harmony XVM
14983 | XVMB1RAG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
14984 | XVMB1RAG | Main | beacon or indicator bank unit type | 3 illuminated units
14985 | XVMB1RAG | Main | component name | XVM
14986 | XVMB1RAG | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
14987 | XVMB1RAG | Main | light block color | Red/orange/green
14988 | XVMB1RAG | Main | [Us] rated supply voltage | 24 V AC/DC
14989 | XVMB1RAG | Main | indicator bank base type | Base without buzzer
14990 | XVMB1RAG | Main | mounting mode | Vertical
14991 | XVMB1RAG | Complementary | kit composition | Plastic fixing plate Base unit Aluminium support tube Cover
14992 | XVMB1RAG | Complementary | mounting diameter | 45 mm
14993 | XVMB1RAG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
14994 | XVMB1RAG | Complementary | marking | CE
14995 | XVMB1RAG | Complementary | mounting support | Aluminium tube
14996 | XVMB1RAG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
14997 | XVMB1RAG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
14998 | XVMB1RAG | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
14999 | XVMB1RAG | Complementary | net weight | 0.493 kg
15000 | XVMB1RAG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
15001 | XVMB1RAG | Environment | product certifications | CCC
15002 | XVMB1RAG | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15003 | XVMB1RAG | Environment | ambient air temperature for storage | -25…70 °C
15004 | XVMB1RAG | Environment | ambient air temperature for operation | -10…50 °C
15005 | XVMB1RAG | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15006 | XVMB1RAG | Environment | protective treatment | TC
15007 | XVMB1RAG | Packing Units | Package 1 Weight | 0.555 kg
15008 | XVMB1RAG | Offer Sustainability | Sustainable offer status | Green Premium product
15009 | XVMB1RAG | Offer Sustainability | REACh Regulation | REACh Declaration
15010 | XVMB1RAG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
15011 | XVMB1RAG | Offer Sustainability | Mercury free | Yes
15012 | XVMB1RAG | Offer Sustainability | RoHS exemption information | Yes
15013 | XVMB1RAG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
15014 | XVMB1RAG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
15015 | XVMB1RAG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
15016 | XVMB1RAG | Contractual warranty | Warranty | 18 months
15017 | XVMB1R6AG | Main | range of product | Harmony XVM
15018 | XVMB1R6AG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
15019 | XVMB1R6AG | Main | beacon or indicator bank unit type | 3 illuminated units
15020 | XVMB1R6AG | Main | component name | XVM
15021 | XVMB1R6AG | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Red flash discharge tubeflashing signalling Green incandescent bulb with BA 15d base steady signalling <5 W
15022 | XVMB1R6AG | Main | light block color | Orange/green/red (flashing)
15023 | XVMB1R6AG | Main | [Us] rated supply voltage | 24 V AC/DC
15024 | XVMB1R6AG | Main | indicator bank base type | Base without buzzer
15025 | XVMB1R6AG | Main | mounting mode | Vertical
15026 | XVMB1R6AG | Complementary | kit composition | Cover Plastic fixing plate Aluminium support tube Base unit
15027 | XVMB1R6AG | Complementary | mounting diameter | 45 mm
15028 | XVMB1R6AG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
15029 | XVMB1R6AG | Complementary | marking | CE
15030 | XVMB1R6AG | Complementary | mounting support | Aluminium tube
15031 | XVMB1R6AG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15032 | XVMB1R6AG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15033 | XVMB1R6AG | Complementary | current consumption | 140 mA on flash discharge tube unit AC 98 mA on flash discharge tube unit DC
15034 | XVMB1R6AG | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
15035 | XVMB1R6AG | Complementary | luminance | 650 cd/m² for incandescent bulb unit
15036 | XVMB1R6AG | Complementary | flashing frequency | 0.8 Hz with flash discharge tube unit
15037 | XVMB1R6AG | Complementary | net weight | 0.454 kg
15038 | XVMB1R6AG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
15039 | XVMB1R6AG | Environment | product certifications | CCC
15040 | XVMB1R6AG | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
15041 | XVMB1R6AG | Environment | ambient air temperature for storage | -25…70 °C
15042 | XVMB1R6AG | Environment | ambient air temperature for operation | -10…50 °C
15043 | XVMB1R6AG | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15044 | XVMB1R6AG | Environment | protective treatment | TC
15045 | XVMB1R6AG | Packing Units | Package 1 Weight | 0.571 kg
15046 | XVMB1R6AG | Offer Sustainability | Sustainable offer status | Green Premium product
15047 | XVMB1R6AG | Offer Sustainability | REACh Regulation | REACh Declaration
15048 | XVMB1R6AG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
15049 | XVMB1R6AG | Offer Sustainability | Mercury free | Yes
15050 | XVMB1R6AG | Offer Sustainability | RoHS exemption information | Yes
15051 | XVMB1R6AG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
15052 | XVMB1R6AG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
15053 | XVMB1R6AG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
15054 | XVMB1R6AG | Contractual warranty | Warranty | 18 months
15055 | XVMG1RAG | Main | range of product | Harmony XVM
15056 | XVMG1RAG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
15057 | XVMG1RAG | Main | beacon or indicator bank unit type | 3 illuminated units
15058 | XVMG1RAG | Main | component name | XVM
15059 | XVMG1RAG | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
15060 | XVMG1RAG | Main | light block color | Red/orange/green
15061 | XVMG1RAG | Main | [Us] rated supply voltage | 120 V AC/DC
15062 | XVMG1RAG | Main | indicator bank base type | Base without buzzer
15063 | XVMG1RAG | Main | mounting mode | Vertical
15064 | XVMG1RAG | Complementary | kit composition | Cover Base unit Plastic fixing plate Aluminium support tube
15065 | XVMG1RAG | Complementary | mounting diameter | 45 mm
15066 | XVMG1RAG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
15067 | XVMG1RAG | Complementary | marking | CE
15068 | XVMG1RAG | Complementary | mounting support | Aluminium tube
15069 | XVMG1RAG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15070 | XVMG1RAG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15071 | XVMG1RAG | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
15072 | XVMG1RAG | Complementary | net weight | 0.493 kg
15073 | XVMG1RAG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
15074 | XVMG1RAG | Environment | product certifications | CCC
15075 | XVMG1RAG | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15076 | XVMG1RAG | Environment | ambient air temperature for storage | -25…70 °C
15077 | XVMG1RAG | Environment | ambient air temperature for operation | -10…50 °C
15078 | XVMG1RAG | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15079 | XVMG1RAG | Environment | protective treatment | TC
15080 | XVMG1RAG | Packing Units | Package 1 Weight | 0.493 kg
15081 | XVMG1RAG | Offer Sustainability | Sustainable offer status | Green Premium product
15082 | XVMG1RAG | Offer Sustainability | REACh Regulation | REACh Declaration
15083 | XVMG1RAG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
15084 | XVMG1RAG | Offer Sustainability | Mercury free | Yes
15085 | XVMG1RAG | Offer Sustainability | RoHS exemption information | Yes
15086 | XVMG1RAG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
15087 | XVMG1RAG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
15088 | XVMG1RAG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
15089 | XVMG1RAG | Contractual warranty | Warranty | 18 months
15090 | XVMG1R6AG | Main | range of product | Harmony XVM
15091 | XVMG1R6AG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
15092 | XVMG1R6AG | Main | beacon or indicator bank unit type | 3 illuminated units
15093 | XVMG1R6AG | Main | component name | XVM
15094 | XVMG1R6AG | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Red flash discharge tubeflashing signalling Green incandescent bulb with BA 15d base steady signalling <5 W
15095 | XVMG1R6AG | Main | light block color | Orange/green/red (flashing)
15096 | XVMG1R6AG | Main | [Us] rated supply voltage | 120 V AC/DC
15097 | XVMG1R6AG | Main | indicator bank base type | Base without buzzer
15098 | XVMG1R6AG | Main | mounting mode | Vertical
15099 | XVMG1R6AG | Complementary | kit composition | Aluminium support tube Cover Plastic fixing plate Base unit
15100 | XVMG1R6AG | Complementary | mounting diameter | 45 mm
15101 | XVMG1R6AG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
15102 | XVMG1R6AG | Complementary | marking | CE
15103 | XVMG1R6AG | Complementary | mounting support | Aluminium tube
15104 | XVMG1R6AG | Complementary | short-circuit protection | 0.2 A
15105 | XVMG1R6AG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15106 | XVMG1R6AG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15107 | XVMG1R6AG | Complementary | current consumption | 33 mA on flash discharge tube unit
15108 | XVMG1R6AG | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15109 | XVMG1R6AG | Complementary | luminance | 650 cd/m² for incandescent bulb unit
15110 | XVMG1R6AG | Complementary | flashing frequency | 0.8 Hz with flash discharge tube unit
15111 | XVMG1R6AG | Complementary | net weight | 0.454 kg
15112 | XVMG1R6AG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
15113 | XVMG1R6AG | Environment | product certifications | CCC
15114 | XVMG1R6AG | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15115 | XVMG1R6AG | Environment | ambient air temperature for storage | -25…70 °C
15116 | XVMG1R6AG | Environment | ambient air temperature for operation | -10…50 °C
15117 | XVMG1R6AG | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15118 | XVMG1R6AG | Environment | protective treatment | TC
15119 | XVMG1R6AG | Contractual warranty | Warranty | 18 months
15120 | XVMM1RAG | Main | range of product | Harmony XVM
15121 | XVMM1RAG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
15122 | XVMM1RAG | Main | beacon or indicator bank unit type | 3 illuminated units
15123 | XVMM1RAG | Main | component name | XVM
15124 | XVMM1RAG | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
15125 | XVMM1RAG | Main | light block color | Red/orange/green
15126 | XVMM1RAG | Main | [Us] rated supply voltage | 230 V AC/DC
15127 | XVMM1RAG | Main | indicator bank base type | Base without buzzer
15128 | XVMM1RAG | Main | mounting mode | Vertical
15129 | XVMM1RAG | Complementary | kit composition | Base unit Aluminium support tube Cover Plastic fixing plate
15130 | XVMM1RAG | Complementary | mounting diameter | 45 mm
15131 | XVMM1RAG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
15132 | XVMM1RAG | Complementary | marking | CE
15133 | XVMM1RAG | Complementary | mounting support | Aluminium tube
15134 | XVMM1RAG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15135 | XVMM1RAG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15136 | XVMM1RAG | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
15137 | XVMM1RAG | Complementary | net weight | 0.493 kg
15138 | XVMM1RAG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
15139 | XVMM1RAG | Environment | product certifications | CCC
15140 | XVMM1RAG | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15141 | XVMM1RAG | Environment | ambient air temperature for storage | -25…70 °C
15142 | XVMM1RAG | Environment | ambient air temperature for operation | -10…50 °C
15143 | XVMM1RAG | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15144 | XVMM1RAG | Environment | protective treatment | TC
15145 | XVMM1RAG | Packing Units | Package 1 Weight | 0.545 kg
15146 | XVMM1RAG | Offer Sustainability | Sustainable offer status | Green Premium product
15147 | XVMM1RAG | Offer Sustainability | REACh Regulation | REACh Declaration
15148 | XVMM1RAG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
15149 | XVMM1RAG | Offer Sustainability | Mercury free | Yes
15150 | XVMM1RAG | Offer Sustainability | RoHS exemption information | Yes
15151 | XVMM1RAG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
15152 | XVMM1RAG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
15153 | XVMM1RAG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
15154 | XVMM1RAG | Contractual warranty | Warranty | 18 months
15155 | XVMM1R6AG | Main | range of product | Harmony XVM
15156 | XVMM1R6AG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
15157 | XVMM1R6AG | Main | beacon or indicator bank unit type | 3 illuminated units
15158 | XVMM1R6AG | Main | component name | XVM
15159 | XVMM1R6AG | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Red flash discharge tubeflashing signalling Green incandescent bulb with BA 15d base steady signalling <5 W
15160 | XVMM1R6AG | Main | light block color | Orange/green/red (flashing)
15161 | XVMM1R6AG | Main | [Us] rated supply voltage | 230 V AC/DC
15162 | XVMM1R6AG | Main | indicator bank base type | Base without buzzer
15163 | XVMM1R6AG | Main | mounting mode | Vertical
15164 | XVMM1R6AG | Complementary | kit composition | Base unit Plastic fixing plate Cover Aluminium support tube
15165 | XVMM1R6AG | Complementary | mounting diameter | 45 mm
15166 | XVMM1R6AG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
15167 | XVMM1R6AG | Complementary | marking | CE
15168 | XVMM1R6AG | Complementary | mounting support | Aluminium tube
15169 | XVMM1R6AG | Complementary | short-circuit protection | 0.2 A
15170 | XVMM1R6AG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15171 | XVMM1R6AG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15172 | XVMM1R6AG | Complementary | current consumption | 20 mA on flash discharge tube unit
15173 | XVMM1R6AG | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
15174 | XVMM1R6AG | Complementary | luminance | 650 cd/m² for incandescent bulb unit
15175 | XVMM1R6AG | Complementary | flashing frequency | 0.8 Hz with flash discharge tube unit
15176 | XVMM1R6AG | Complementary | net weight | 0.454 kg
15177 | XVMM1R6AG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
15178 | XVMM1R6AG | Environment | product certifications | CCC
15179 | XVMM1R6AG | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15180 | XVMM1R6AG | Environment | ambient air temperature for storage | -25…70 °C
15181 | XVMM1R6AG | Environment | ambient air temperature for operation | -10…50 °C
15182 | XVMM1R6AG | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15183 | XVMM1R6AG | Environment | protective treatment | TC
15184 | XVMM1R6AG | Contractual warranty | Warranty | 18 months
15185 | XVMB1RAGS | Main | range of product | Harmony XVM
15186 | XVMB1RAGS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
15187 | XVMB1RAGS | Main | beacon or indicator bank unit type | 3 illuminated units
15188 | XVMB1RAGS | Main | component name | XVM
15189 | XVMB1RAGS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
15190 | XVMB1RAGS | Main | light block color | Red/orange/green
15191 | XVMB1RAGS | Main | [Us] rated supply voltage | 24 V AC/DC
15192 | XVMB1RAGS | Main | indicator bank base type | Base with integrated buzzer
15193 | XVMB1RAGS | Main | mounting mode | Vertical
15194 | XVMB1RAGS | Complementary | kit composition | Cover Plastic fixing plate Aluminium support tube Base unit
15195 | XVMB1RAGS | Complementary | mounting diameter | 45 mm
15196 | XVMB1RAGS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
15197 | XVMB1RAGS | Complementary | marking | CE
15198 | XVMB1RAGS | Complementary | mounting support | Aluminium tube
15199 | XVMB1RAGS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15200 | XVMB1RAGS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15201 | XVMB1RAGS | Complementary | current consumption | 15 mA on base unit
15202 | XVMB1RAGS | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
15203 | XVMB1RAGS | Complementary | fundamental frequency | 4 kHz
15204 | XVMB1RAGS | Complementary | net weight | 0.449 kg
15205 | XVMB1RAGS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
15206 | XVMB1RAGS | Environment | product certifications | CCC
15207 | XVMB1RAGS | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
15208 | XVMB1RAGS | Environment | ambient air temperature for storage | -25…70 °C
15209 | XVMB1RAGS | Environment | ambient air temperature for operation | -10…50 °C
15210 | XVMB1RAGS | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15211 | XVMB1RAGS | Environment | protective treatment | TC
15212 | XVMB1RAGS | Environment | noise level | 0…80 dB at 1 m
15213 | XVMB1RAGS | Packing Units | Package 1 Weight | 560 g
15214 | XVMB1RAGS | Packing Units | Package 2 Weight | 12.502 kg
15215 | XVMB1RAGS | Offer Sustainability | Sustainable offer status | Green Premium product
15216 | XVMB1RAGS | Offer Sustainability | REACh Regulation | REACh Declaration
15217 | XVMB1RAGS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
15218 | XVMB1RAGS | Offer Sustainability | Mercury free | Yes
15219 | XVMB1RAGS | Offer Sustainability | RoHS exemption information | Yes
15220 | XVMB1RAGS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
15221 | XVMB1RAGS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
15222 | XVMB1RAGS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
15223 | XVMB1RAGS | Contractual warranty | Warranty | 18 months
15224 | XVMB1R6AGS | Main | range of product | Harmony XVM
15225 | XVMB1R6AGS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
15226 | XVMB1R6AGS | Main | beacon or indicator bank unit type | 3 illuminated units
15227 | XVMB1R6AGS | Main | component name | XVM
15228 | XVMB1R6AGS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Red flash discharge tubeflashing signalling Green incandescent bulb with BA 15d base steady signalling <5 W
15229 | XVMB1R6AGS | Main | light block color | Orange/green/red (flashing)
15230 | XVMB1R6AGS | Main | [Us] rated supply voltage | 24 V AC/DC
15231 | XVMB1R6AGS | Main | indicator bank base type | Base with integrated buzzer
15232 | XVMB1R6AGS | Main | mounting mode | Vertical
15233 | XVMB1R6AGS | Complementary | kit composition | Aluminium support tube Cover Plastic fixing plate Base unit
15234 | XVMB1R6AGS | Complementary | mounting diameter | 45 mm
15235 | XVMB1R6AGS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
15236 | XVMB1R6AGS | Complementary | marking | CE
15237 | XVMB1R6AGS | Complementary | mounting support | Aluminium tube
15238 | XVMB1R6AGS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15239 | XVMB1R6AGS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15240 | XVMB1R6AGS | Complementary | current consumption | 140 mA on flash discharge tube unit AC 98 mA on flash discharge tube unit DC 15 mA on base unit
15241 | XVMB1R6AGS | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15242 | XVMB1R6AGS | Complementary | luminance | 650 cd/m² for incandescent bulb unit
15243 | XVMB1R6AGS | Complementary | flashing frequency | 0.8 Hz with flash discharge tube unit
15244 | XVMB1R6AGS | Complementary | fundamental frequency | 4 kHz
15245 | XVMB1R6AGS | Complementary | net weight | 0.463 kg
15246 | XVMB1R6AGS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
15247 | XVMB1R6AGS | Environment | product certifications | CCC
15248 | XVMB1R6AGS | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
15249 | XVMB1R6AGS | Environment | ambient air temperature for storage | -25…70 °C
15250 | XVMB1R6AGS | Environment | ambient air temperature for operation | -10…50 °C
15251 | XVMB1R6AGS | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15252 | XVMB1R6AGS | Environment | protective treatment | TC
15253 | XVMB1R6AGS | Environment | noise level | 0…80 dB at 1 m
15254 | XVMB1R6AGS | Packing Units | Package 1 Weight | 0.463 kg
15255 | XVMB1R6AGS | Offer Sustainability | Sustainable offer status | Green Premium product
15256 | XVMB1R6AGS | Offer Sustainability | REACh Regulation | REACh Declaration
15257 | XVMB1R6AGS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
15258 | XVMB1R6AGS | Offer Sustainability | Mercury free | Yes
15259 | XVMB1R6AGS | Offer Sustainability | RoHS exemption information | Yes
15260 | XVMB1R6AGS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
15261 | XVMB1R6AGS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
15262 | XVMB1R6AGS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
15263 | XVMB1R6AGS | Contractual warranty | Warranty | 18 months
15264 | XVMG1RAGS | Main | range of product | Harmony XVM
15265 | XVMG1RAGS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
15266 | XVMG1RAGS | Main | beacon or indicator bank unit type | 3 illuminated units
15267 | XVMG1RAGS | Main | component name | XVM
15268 | XVMG1RAGS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
15269 | XVMG1RAGS | Main | light block color | Red/orange/green
15270 | XVMG1RAGS | Main | [Us] rated supply voltage | 120 V AC
15271 | XVMG1RAGS | Main | indicator bank base type | Base with integrated buzzer
15272 | XVMG1RAGS | Main | mounting mode | Vertical
15273 | XVMG1RAGS | Complementary | kit composition | Aluminium support tube Base unit Cover Plastic fixing plate
15274 | XVMG1RAGS | Complementary | mounting diameter | 45 mm
15275 | XVMG1RAGS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
15276 | XVMG1RAGS | Complementary | marking | CE
15277 | XVMG1RAGS | Complementary | mounting support | Aluminium tube
15278 | XVMG1RAGS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15279 | XVMG1RAGS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15280 | XVMG1RAGS | Complementary | current consumption | 18 mA on base unit
15281 | XVMG1RAGS | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15282 | XVMG1RAGS | Complementary | fundamental frequency | 4 kHz
15283 | XVMG1RAGS | Complementary | net weight | 0.449 kg
15284 | XVMG1RAGS | Environment | IP degree of protection | IP54 vertical position conforming to IEC 60529
15285 | XVMG1RAGS | Environment | product certifications | CCC
15286 | XVMG1RAGS | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
15287 | XVMG1RAGS | Environment | ambient air temperature for storage | -25…70 °C
15288 | XVMG1RAGS | Environment | ambient air temperature for operation | -10…50 °C
15289 | XVMG1RAGS | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15290 | XVMG1RAGS | Environment | protective treatment | TC
15291 | XVMG1RAGS | Environment | noise level | 0…80 dB at 1 m
15292 | XVMG1RAGS | Offer Sustainability | Sustainable offer status | Green Premium product
15293 | XVMG1RAGS | Offer Sustainability | REACh Regulation | REACh Declaration
15294 | XVMG1RAGS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
15295 | XVMG1RAGS | Offer Sustainability | Mercury free | Yes
15296 | XVMG1RAGS | Offer Sustainability | RoHS exemption information | Yes
15297 | XVMG1RAGS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
15298 | XVMG1RAGS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
15299 | XVMG1RAGS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
15300 | XVMG1RAGS | Contractual warranty | Warranty | 18 months
15301 | XVMG1R6AGS | Main | range of product | Harmony XVM
15302 | XVMG1R6AGS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
15303 | XVMG1R6AGS | Main | beacon or indicator bank unit type | 3 illuminated units
15304 | XVMG1R6AGS | Main | component name | XVM
15305 | XVMG1R6AGS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Red flash discharge tubeflashing signalling Green incandescent bulb with BA 15d base steady signalling <5 W
15306 | XVMG1R6AGS | Main | light block color | Orange/green/red (flashing)
15307 | XVMG1R6AGS | Main | [Us] rated supply voltage | 120 V AC
15308 | XVMG1R6AGS | Main | indicator bank base type | Base with integrated buzzer
15309 | XVMG1R6AGS | Main | mounting mode | Vertical
15310 | XVMG1R6AGS | Complementary | kit composition | Plastic fixing plate Aluminium support tube Cover Base unit
15311 | XVMG1R6AGS | Complementary | mounting diameter | 45 mm
15312 | XVMG1R6AGS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
15313 | XVMG1R6AGS | Complementary | marking | CE
15314 | XVMG1R6AGS | Complementary | mounting support | Aluminium tube
15315 | XVMG1R6AGS | Complementary | short-circuit protection | 0.2 A
15316 | XVMG1R6AGS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15317 | XVMG1R6AGS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15318 | XVMG1R6AGS | Complementary | current consumption | 18 mA on base unit 33 mA on flash discharge tube unit
15319 | XVMG1R6AGS | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15320 | XVMG1R6AGS | Complementary | luminance | 650 cd/m² for incandescent bulb unit
15321 | XVMG1R6AGS | Complementary | flashing frequency | 0.8 Hz with flash discharge tube unit
15322 | XVMG1R6AGS | Complementary | fundamental frequency | 4 kHz
15323 | XVMG1R6AGS | Complementary | net weight | 0.463 kg
15324 | XVMG1R6AGS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
15325 | XVMG1R6AGS | Environment | product certifications | CCC
15326 | XVMG1R6AGS | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15327 | XVMG1R6AGS | Environment | ambient air temperature for storage | -25…70 °C
15328 | XVMG1R6AGS | Environment | ambient air temperature for operation | -10…50 °C
15329 | XVMG1R6AGS | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15330 | XVMG1R6AGS | Environment | protective treatment | TC
15331 | XVMG1R6AGS | Environment | noise level | 0…80 dB at 1 m
15332 | XVMG1R6AGS | Contractual warranty | Warranty | 18 months
15333 | XVMM1RAGS | Main | range of product | Harmony XVM
15334 | XVMM1RAGS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
15335 | XVMM1RAGS | Main | beacon or indicator bank unit type | 3 illuminated units
15336 | XVMM1RAGS | Main | component name | XVM
15337 | XVMM1RAGS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W
15338 | XVMM1RAGS | Main | light block color | Red/orange/green
15339 | XVMM1RAGS | Main | [Us] rated supply voltage | 230 V AC
15340 | XVMM1RAGS | Main | indicator bank base type | Base with integrated buzzer
15341 | XVMM1RAGS | Main | mounting mode | Vertical
15342 | XVMM1RAGS | Complementary | kit composition | Base unit Cover Aluminium support tube Plastic fixing plate
15343 | XVMM1RAGS | Complementary | mounting diameter | 45 mm
15344 | XVMM1RAGS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
15345 | XVMM1RAGS | Complementary | marking | CE
15346 | XVMM1RAGS | Complementary | mounting support | Aluminium tube
15347 | XVMM1RAGS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15348 | XVMM1RAGS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15349 | XVMM1RAGS | Complementary | current consumption | 18 mA on base unit
15350 | XVMM1RAGS | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15351 | XVMM1RAGS | Complementary | fundamental frequency | 4 kHz
15352 | XVMM1RAGS | Complementary | net weight | 0.449 kg
15353 | XVMM1RAGS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
15354 | XVMM1RAGS | Environment | product certifications | CCC
15355 | XVMM1RAGS | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
15356 | XVMM1RAGS | Environment | ambient air temperature for storage | -25…70 °C
15357 | XVMM1RAGS | Environment | ambient air temperature for operation | -10…50 °C
15358 | XVMM1RAGS | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15359 | XVMM1RAGS | Environment | protective treatment | TC
15360 | XVMM1RAGS | Environment | noise level | 0…80 dB at 1 m
15361 | XVMM1RAGS | Packing Units | Package 1 Weight | 0.561 kg
15362 | XVMM1RAGS | Offer Sustainability | Sustainable offer status | Green Premium product
15363 | XVMM1RAGS | Offer Sustainability | REACh Regulation | REACh Declaration
15364 | XVMM1RAGS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
15365 | XVMM1RAGS | Offer Sustainability | Mercury free | Yes
15366 | XVMM1RAGS | Offer Sustainability | RoHS exemption information | Yes
15367 | XVMM1RAGS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
15368 | XVMM1RAGS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
15369 | XVMM1RAGS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
15370 | XVMM1RAGS | Contractual warranty | Warranty | 18 months
15371 | XVMB1RAGB | Main | range of product | Harmony XVM
15372 | XVMB1RAGB | Main | product or component type | Pre-assembled and pre-cabled indicator bank
15373 | XVMB1RAGB | Main | beacon or indicator bank unit type | 4 illuminated units
15374 | XVMB1RAGB | Main | component name | XVM
15375 | XVMB1RAGB | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W Blue incandescent bulb with BA 15d base steady signalling <5 W
15376 | XVMB1RAGB | Main | light block color | Red/orange/green/blue
15377 | XVMB1RAGB | Main | [Us] rated supply voltage | 24 V AC/DC
15378 | XVMB1RAGB | Main | indicator bank base type | Base without buzzer
15379 | XVMB1RAGB | Main | mounting mode | Vertical
15380 | XVMB1RAGB | Complementary | kit composition | Plastic fixing plate Aluminium support tube Cover Base unit
15381 | XVMB1RAGB | Complementary | mounting diameter | 45 mm
15382 | XVMB1RAGB | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
15383 | XVMB1RAGB | Complementary | marking | CE
15384 | XVMB1RAGB | Complementary | mounting support | Aluminium tube
15385 | XVMB1RAGB | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15386 | XVMB1RAGB | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15387 | XVMB1RAGB | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
15388 | XVMB1RAGB | Complementary | net weight | 0.486 kg
15389 | XVMB1RAGB | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
15390 | XVMB1RAGB | Environment | product certifications | CCC
15391 | XVMB1RAGB | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
15392 | XVMB1RAGB | Environment | ambient air temperature for storage | -25…70 °C
15393 | XVMB1RAGB | Environment | ambient air temperature for operation | -10…50 °C
15394 | XVMB1RAGB | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15395 | XVMB1RAGB | Environment | protective treatment | TC
15396 | XVMB1RAGB | Packing Units | Package 1 Weight | 0.486 kg
15397 | XVMB1RAGB | Offer Sustainability | Sustainable offer status | Green Premium product
15398 | XVMB1RAGB | Offer Sustainability | REACh Regulation | REACh Declaration
15399 | XVMB1RAGB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
15400 | XVMB1RAGB | Offer Sustainability | Mercury free | Yes
15401 | XVMB1RAGB | Offer Sustainability | RoHS exemption information | Yes
15402 | XVMB1RAGB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
15403 | XVMB1RAGB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
15404 | XVMB1RAGB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
15405 | XVMB1RAGB | Contractual warranty | Warranty | 18 months
15406 | XVMG1RAGB | Main | range of product | Harmony XVM
15407 | XVMG1RAGB | Main | product or component type | Pre-assembled and pre-cabled indicator bank
15408 | XVMG1RAGB | Main | beacon or indicator bank unit type | 4 illuminated units
15409 | XVMG1RAGB | Main | component name | XVM
15410 | XVMG1RAGB | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W Blue incandescent bulb with BA 15d base steady signalling <5 W
15411 | XVMG1RAGB | Main | light block color | Red/orange/green/blue
15412 | XVMG1RAGB | Main | [Us] rated supply voltage | 120 V AC/DC
15413 | XVMG1RAGB | Main | indicator bank base type | Base without buzzer
15414 | XVMG1RAGB | Main | mounting mode | Vertical
15415 | XVMG1RAGB | Complementary | kit composition | Aluminium support tube Base unit Plastic fixing plate Cover
15416 | XVMG1RAGB | Complementary | mounting diameter | 45 mm
15417 | XVMG1RAGB | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
15418 | XVMG1RAGB | Complementary | marking | CE
15419 | XVMG1RAGB | Complementary | mounting support | Aluminium tube
15420 | XVMG1RAGB | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15421 | XVMG1RAGB | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15422 | XVMG1RAGB | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15423 | XVMG1RAGB | Complementary | net weight | 0.486 kg
15424 | XVMG1RAGB | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
15425 | XVMG1RAGB | Environment | product certifications | CCC
15426 | XVMG1RAGB | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
15427 | XVMG1RAGB | Environment | ambient air temperature for storage | -25…70 °C
15428 | XVMG1RAGB | Environment | ambient air temperature for operation | -10…50 °C
15429 | XVMG1RAGB | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15430 | XVMG1RAGB | Environment | protective treatment | TC
15431 | XVMG1RAGB | Packing Units | Package 1 Weight | 0.486 kg
15432 | XVMG1RAGB | Offer Sustainability | Sustainable offer status | Green Premium product
15433 | XVMG1RAGB | Offer Sustainability | REACh Regulation | REACh Declaration
15434 | XVMG1RAGB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
15435 | XVMG1RAGB | Offer Sustainability | Mercury free | Yes
15436 | XVMG1RAGB | Offer Sustainability | RoHS exemption information | Yes
15437 | XVMG1RAGB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
15438 | XVMG1RAGB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
15439 | XVMG1RAGB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
15440 | XVMG1RAGB | Contractual warranty | Warranty | 18 months
15441 | XVMM1RAGB | Main | range of product | Harmony XVM
15442 | XVMM1RAGB | Main | product or component type | Pre-assembled and pre-cabled indicator bank
15443 | XVMM1RAGB | Main | beacon or indicator bank unit type | 4 illuminated units
15444 | XVMM1RAGB | Main | component name | XVM
15445 | XVMM1RAGB | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W Blue incandescent bulb with BA 15d base steady signalling <5 W
15446 | XVMM1RAGB | Main | light block color | Red/orange/green/blue
15447 | XVMM1RAGB | Main | [Us] rated supply voltage | 230 V AC/DC
15448 | XVMM1RAGB | Main | indicator bank base type | Base without buzzer
15449 | XVMM1RAGB | Main | mounting mode | Vertical
15450 | XVMM1RAGB | Complementary | kit composition | Cover Base unit Plastic fixing plate Aluminium support tube
15451 | XVMM1RAGB | Complementary | mounting diameter | 45 mm
15452 | XVMM1RAGB | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
15453 | XVMM1RAGB | Complementary | marking | CE
15454 | XVMM1RAGB | Complementary | mounting support | Aluminium tube
15455 | XVMM1RAGB | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15456 | XVMM1RAGB | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15457 | XVMM1RAGB | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
15458 | XVMM1RAGB | Complementary | net weight | 0.486 kg
15459 | XVMM1RAGB | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
15460 | XVMM1RAGB | Environment | product certifications | CCC
15461 | XVMM1RAGB | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15462 | XVMM1RAGB | Environment | ambient air temperature for storage | -25…70 °C
15463 | XVMM1RAGB | Environment | ambient air temperature for operation | -10…50 °C
15464 | XVMM1RAGB | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15465 | XVMM1RAGB | Environment | protective treatment | TC
15466 | XVMM1RAGB | Packing Units | Package 1 Weight | 0.486 kg
15467 | XVMM1RAGB | Offer Sustainability | Sustainable offer status | Green Premium product
15468 | XVMM1RAGB | Offer Sustainability | REACh Regulation | REACh Declaration
15469 | XVMM1RAGB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
15470 | XVMM1RAGB | Offer Sustainability | Mercury free | Yes
15471 | XVMM1RAGB | Offer Sustainability | RoHS exemption information | Yes
15472 | XVMM1RAGB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
15473 | XVMM1RAGB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
15474 | XVMM1RAGB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
15475 | XVMM1RAGB | Contractual warranty | Warranty | 18 months
15476 | XVMB1RAGBS | Main | range of product | Harmony XVM
15477 | XVMB1RAGBS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
15478 | XVMB1RAGBS | Main | beacon or indicator bank unit type | 4 illuminated units
15479 | XVMB1RAGBS | Main | component name | XVM
15480 | XVMB1RAGBS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W Blue incandescent bulb with BA 15d base steady signalling <5 W
15481 | XVMB1RAGBS | Main | light block color | Red/orange/green/blue
15482 | XVMB1RAGBS | Main | [Us] rated supply voltage | 24 V AC/DC
15483 | XVMB1RAGBS | Main | indicator bank base type | Base with integrated buzzer
15484 | XVMB1RAGBS | Main | mounting mode | Vertical
15485 | XVMB1RAGBS | Complementary | kit composition | Plastic fixing plate Cover Aluminium support tube Base unit
15486 | XVMB1RAGBS | Complementary | mounting diameter | 45 mm
15487 | XVMB1RAGBS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
15488 | XVMB1RAGBS | Complementary | marking | CE
15489 | XVMB1RAGBS | Complementary | mounting support | Aluminium tube
15490 | XVMB1RAGBS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15491 | XVMB1RAGBS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15492 | XVMB1RAGBS | Complementary | current consumption | 15 mA on base unit
15493 | XVMB1RAGBS | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15494 | XVMB1RAGBS | Complementary | fundamental frequency | 4 kHz
15495 | XVMB1RAGBS | Complementary | net weight | 0.496 kg
15496 | XVMB1RAGBS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
15497 | XVMB1RAGBS | Environment | product certifications | CCC
15498 | XVMB1RAGBS | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15499 | XVMB1RAGBS | Environment | ambient air temperature for storage | -25…70 °C
15500 | XVMB1RAGBS | Environment | ambient air temperature for operation | -10…50 °C
15501 | XVMB1RAGBS | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15502 | XVMB1RAGBS | Environment | protective treatment | TC
15503 | XVMB1RAGBS | Environment | noise level | 0…80 dB at 1 m
15504 | XVMB1RAGBS | Packing Units | Package 1 Weight | 0.496 kg
15505 | XVMB1RAGBS | Offer Sustainability | Sustainable offer status | Green Premium product
15506 | XVMB1RAGBS | Offer Sustainability | REACh Regulation | REACh Declaration
15507 | XVMB1RAGBS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
15508 | XVMB1RAGBS | Offer Sustainability | Mercury free | Yes
15509 | XVMB1RAGBS | Offer Sustainability | RoHS exemption information | Yes
15510 | XVMB1RAGBS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
15511 | XVMB1RAGBS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
15512 | XVMB1RAGBS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
15513 | XVMB1RAGBS | Contractual warranty | Warranty | 18 months
15514 | XVMG1RAGBS | Main | range of product | Harmony XVM
15515 | XVMG1RAGBS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
15516 | XVMG1RAGBS | Main | beacon or indicator bank unit type | 4 illuminated units
15517 | XVMG1RAGBS | Main | component name | XVM
15518 | XVMG1RAGBS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W Blue incandescent bulb with BA 15d base steady signalling <5 W
15519 | XVMG1RAGBS | Main | light block color | Red/orange/green/blue
15520 | XVMG1RAGBS | Main | [Us] rated supply voltage | 120 V AC
15521 | XVMG1RAGBS | Main | indicator bank base type | Base with integrated buzzer
15522 | XVMG1RAGBS | Main | mounting mode | Vertical
15523 | XVMG1RAGBS | Complementary | kit composition | Aluminium support tube Base unit Plastic fixing plate Cover
15524 | XVMG1RAGBS | Complementary | mounting diameter | 45 mm
15525 | XVMG1RAGBS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
15526 | XVMG1RAGBS | Complementary | marking | CE
15527 | XVMG1RAGBS | Complementary | mounting support | Aluminium tube
15528 | XVMG1RAGBS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15529 | XVMG1RAGBS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15530 | XVMG1RAGBS | Complementary | current consumption | 18 mA on base unit
15531 | XVMG1RAGBS | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15532 | XVMG1RAGBS | Complementary | fundamental frequency | 4 kHz
15533 | XVMG1RAGBS | Complementary | net weight | 0.496 kg
15534 | XVMG1RAGBS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
15535 | XVMG1RAGBS | Environment | product certifications | CCC
15536 | XVMG1RAGBS | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
15537 | XVMG1RAGBS | Environment | ambient air temperature for storage | -25…70 °C
15538 | XVMG1RAGBS | Environment | ambient air temperature for operation | -10…50 °C
15539 | XVMG1RAGBS | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15540 | XVMG1RAGBS | Environment | protective treatment | TC
15541 | XVMG1RAGBS | Environment | noise level | 0…80 dB at 1 m
15542 | XVMG1RAGBS | Contractual warranty | Warranty | 18 months
15543 | XVMM1RAGBS | Main | range of product | Harmony XVM
15544 | XVMM1RAGBS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
15545 | XVMM1RAGBS | Main | beacon or indicator bank unit type | 4 illuminated units
15546 | XVMM1RAGBS | Main | component name | XVM
15547 | XVMM1RAGBS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W Blue incandescent bulb with BA 15d base steady signalling <5 W
15548 | XVMM1RAGBS | Main | light block color | Red/orange/green/blue
15549 | XVMM1RAGBS | Main | [Us] rated supply voltage | 230 V AC
15550 | XVMM1RAGBS | Main | indicator bank base type | Base with integrated buzzer
15551 | XVMM1RAGBS | Main | mounting mode | Vertical
15552 | XVMM1RAGBS | Complementary | kit composition | Cover Aluminium support tube Plastic fixing plate Base unit
15553 | XVMM1RAGBS | Complementary | mounting diameter | 45 mm
15554 | XVMM1RAGBS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
15555 | XVMM1RAGBS | Complementary | marking | CE
15556 | XVMM1RAGBS | Complementary | mounting support | Aluminium tube
15557 | XVMM1RAGBS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15558 | XVMM1RAGBS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15559 | XVMM1RAGBS | Complementary | current consumption | 18 mA on base unit
15560 | XVMM1RAGBS | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
15561 | XVMM1RAGBS | Complementary | fundamental frequency | 4 kHz
15562 | XVMM1RAGBS | Complementary | net weight | 0.496 kg
15563 | XVMM1RAGBS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
15564 | XVMM1RAGBS | Environment | product certifications | CCC
15565 | XVMM1RAGBS | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15566 | XVMM1RAGBS | Environment | ambient air temperature for storage | -25…70 °C
15567 | XVMM1RAGBS | Environment | ambient air temperature for operation | -10…50 °C
15568 | XVMM1RAGBS | Environment | overvoltage category | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140
15569 | XVMM1RAGBS | Environment | protective treatment | TC
15570 | XVMM1RAGBS | Environment | noise level | 0…80 dB at 1 m
15571 | XVMM1RAGBS | Packing Units | Package 1 Weight | 0.496 kg
15572 | XVMM1RAGBS | Contractual warranty | Warranty | 18 months
15573 | XVEL33 | Main | range of product | Harmony XVE Optimum
15574 | XVEL33 | Main | product or component type | Complete illuminated beacon
15575 | XVEL33 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
15576 | XVEL33 | Main | signalling type | Steady
15577 | XVEL33 | Main | component name | XVE
15578 | XVEL33 | Main | light source | Bulb not included, green
15579 | XVEL33 | Main | bulb type | Incandescent with BA 15d base
15580 | XVEL33 | Main | [Us] rated supply voltage | <= 240 V AC/DC
15581 | XVEL33 | Complementary | mounting diameter | 70 mm
15582 | XVEL33 | Complementary | maximum power dissipation in W | 5 W
15583 | XVEL33 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
15584 | XVEL33 | Complementary | marking | CE
15585 | XVEL33 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15586 | XVEL33 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15587 | XVEL33 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15588 | XVEL33 | Complementary | luminance | 640 cd/m²
15589 | XVEL33 | Complementary | CAD overall width | 70 mm
15590 | XVEL33 | Complementary | CAD overall height | 129 mm
15591 | XVEL33 | Complementary | CAD overall depth | 70 mm
15592 | XVEL33 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
15593 | XVEL33 | Complementary | net weight | 0.245 kg
15594 | XVEL33 | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15595 | XVEL33 | Environment | product certifications | CSA UL CCC
15596 | XVEL33 | Environment | ambient air temperature for storage | -40…70 °C
15597 | XVEL33 | Environment | ambient air temperature for operation | -25…55 °C
15598 | XVEL33 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
15599 | XVEL33 | Environment | protective treatment | TC
15600 | XVEL33 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
15601 | XVEL33 | Contractual warranty | Warranty | 18 months
15602 | XVEL34 | Main | range of product | Harmony XVE Optimum
15603 | XVEL34 | Main | product or component type | Complete illuminated beacon
15604 | XVEL34 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
15605 | XVEL34 | Main | signalling type | Steady
15606 | XVEL34 | Main | component name | XVE
15607 | XVEL34 | Main | light source | Bulb not included, red
15608 | XVEL34 | Main | bulb type | Incandescent with BA 15d base
15609 | XVEL34 | Main | [Us] rated supply voltage | <= 240 V AC/DC
15610 | XVEL34 | Complementary | mounting diameter | 70 mm
15611 | XVEL34 | Complementary | maximum power dissipation in W | 5 W
15612 | XVEL34 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
15613 | XVEL34 | Complementary | marking | CE
15614 | XVEL34 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15615 | XVEL34 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15616 | XVEL34 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15617 | XVEL34 | Complementary | luminance | 640 cd/m²
15618 | XVEL34 | Complementary | CAD overall width | 70 mm
15619 | XVEL34 | Complementary | CAD overall height | 129 mm
15620 | XVEL34 | Complementary | CAD overall depth | 70 mm
15621 | XVEL34 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
15622 | XVEL34 | Complementary | net weight | 0.245 kg
15623 | XVEL34 | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15624 | XVEL34 | Environment | product certifications | UL CSA CCC
15625 | XVEL34 | Environment | ambient air temperature for storage | -40…70 °C
15626 | XVEL34 | Environment | ambient air temperature for operation | -25…55 °C
15627 | XVEL34 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
15628 | XVEL34 | Environment | protective treatment | TC
15629 | XVEL34 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
15630 | XVEL34 | Contractual warranty | Warranty | 18 months
15631 | XVEL35 | Main | range of product | Harmony XVE Optimum
15632 | XVEL35 | Main | product or component type | Complete illuminated beacon
15633 | XVEL35 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
15634 | XVEL35 | Main | signalling type | Steady
15635 | XVEL35 | Main | component name | XVE
15636 | XVEL35 | Main | light source | Bulb not included, orange
15637 | XVEL35 | Main | bulb type | Incandescent with BA 15d base
15638 | XVEL35 | Main | [Us] rated supply voltage | <= 240 V AC/DC
15639 | XVEL35 | Complementary | mounting diameter | 70 mm
15640 | XVEL35 | Complementary | maximum power dissipation in W | 5 W
15641 | XVEL35 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
15642 | XVEL35 | Complementary | marking | CE
15643 | XVEL35 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15644 | XVEL35 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15645 | XVEL35 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15646 | XVEL35 | Complementary | luminance | 640 cd/m²
15647 | XVEL35 | Complementary | CAD overall width | 70 mm
15648 | XVEL35 | Complementary | CAD overall height | 129 mm
15649 | XVEL35 | Complementary | CAD overall depth | 70 mm
15650 | XVEL35 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
15651 | XVEL35 | Complementary | net weight | 0.245 kg
15652 | XVEL35 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
15653 | XVEL35 | Environment | product certifications | CCC CSA UL
15654 | XVEL35 | Environment | ambient air temperature for storage | -40…70 °C
15655 | XVEL35 | Environment | ambient air temperature for operation | -25…55 °C
15656 | XVEL35 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
15657 | XVEL35 | Environment | protective treatment | TC
15658 | XVEL35 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
15659 | XVEL35 | Contractual warranty | Warranty | 18 months
15660 | XVEL36 | Main | range of product | Harmony XVE Optimum
15661 | XVEL36 | Main | product or component type | Complete illuminated beacon
15662 | XVEL36 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
15663 | XVEL36 | Main | signalling type | Steady
15664 | XVEL36 | Main | component name | XVE
15665 | XVEL36 | Main | light source | Bulb not included, blue
15666 | XVEL36 | Main | bulb type | Incandescent with BA 15d base
15667 | XVEL36 | Main | [Us] rated supply voltage | <= 240 V AC/DC
15668 | XVEL36 | Complementary | mounting diameter | 70 mm
15669 | XVEL36 | Complementary | maximum power dissipation in W | 5 W
15670 | XVEL36 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
15671 | XVEL36 | Complementary | marking | CE
15672 | XVEL36 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15673 | XVEL36 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15674 | XVEL36 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15675 | XVEL36 | Complementary | luminance | 640 cd/m²
15676 | XVEL36 | Complementary | CAD overall width | 70 mm
15677 | XVEL36 | Complementary | CAD overall height | 129 mm
15678 | XVEL36 | Complementary | CAD overall depth | 70 mm
15679 | XVEL36 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
15680 | XVEL36 | Complementary | net weight | 0.245 kg
15681 | XVEL36 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
15682 | XVEL36 | Environment | product certifications | CCC CSA UL
15683 | XVEL36 | Environment | ambient air temperature for storage | -40…70 °C
15684 | XVEL36 | Environment | ambient air temperature for operation | -25…55 °C
15685 | XVEL36 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
15686 | XVEL36 | Environment | protective treatment | TC
15687 | XVEL36 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
15688 | XVEL36 | Contractual warranty | Warranty | 18 months
15689 | XVEL37 | Main | range of product | Harmony XVE Optimum
15690 | XVEL37 | Main | product or component type | Complete illuminated beacon
15691 | XVEL37 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
15692 | XVEL37 | Main | signalling type | Steady
15693 | XVEL37 | Main | component name | XVE
15694 | XVEL37 | Main | light source | Bulb not included, clear
15695 | XVEL37 | Main | bulb type | Incandescent with BA 15d base
15696 | XVEL37 | Main | [Us] rated supply voltage | <= 240 V AC/DC
15697 | XVEL37 | Complementary | mounting diameter | 70 mm
15698 | XVEL37 | Complementary | maximum power dissipation in W | 5 W
15699 | XVEL37 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
15700 | XVEL37 | Complementary | marking | CE
15701 | XVEL37 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15702 | XVEL37 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15703 | XVEL37 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15704 | XVEL37 | Complementary | luminance | 640 cd/m²
15705 | XVEL37 | Complementary | CAD overall width | 70 mm
15706 | XVEL37 | Complementary | CAD overall height | 129 mm
15707 | XVEL37 | Complementary | CAD overall depth | 70 mm
15708 | XVEL37 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
15709 | XVEL37 | Complementary | net weight | 0.245 kg
15710 | XVEL37 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
15711 | XVEL37 | Environment | product certifications | UL CCC CSA
15712 | XVEL37 | Environment | ambient air temperature for storage | -40…70 °C
15713 | XVEL37 | Environment | ambient air temperature for operation | -25…55 °C
15714 | XVEL37 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
15715 | XVEL37 | Environment | protective treatment | TC
15716 | XVEL37 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
15717 | XVEL37 | Contractual warranty | Warranty | 18 months
15718 | XVEL2B3 | Main | range of product | Harmony XVE Optimum
15719 | XVEL2B3 | Main | product or component type | Complete illuminated beacon
15720 | XVEL2B3 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
15721 | XVEL2B3 | Main | signalling type | Steady
15722 | XVEL2B3 | Main | component name | XVE
15723 | XVEL2B3 | Main | light source | Integral LED, green
15724 | XVEL2B3 | Main | bulb type | LED
15725 | XVEL2B3 | Main | [Us] rated supply voltage | 24 V AC/DC
15726 | XVEL2B3 | Complementary | mounting diameter | 70 mm
15727 | XVEL2B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
15728 | XVEL2B3 | Complementary | marking | CE
15729 | XVEL2B3 | Complementary | short-circuit protection | 0.63 A
15730 | XVEL2B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15731 | XVEL2B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15732 | XVEL2B3 | Complementary | current consumption | < 25 mA
15733 | XVEL2B3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15734 | XVEL2B3 | Complementary | luminance | 800 cd/m²
15735 | XVEL2B3 | Complementary | CAD overall width | 70 mm
15736 | XVEL2B3 | Complementary | CAD overall height | 129 mm
15737 | XVEL2B3 | Complementary | CAD overall depth | 70 mm
15738 | XVEL2B3 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
15739 | XVEL2B3 | Complementary | net weight | 0.25 kg
15740 | XVEL2B3 | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15741 | XVEL2B3 | Environment | product certifications | CSA CCC UL
15742 | XVEL2B3 | Environment | ambient air temperature for storage | -40…70 °C
15743 | XVEL2B3 | Environment | ambient air temperature for operation | -25…55 °C
15744 | XVEL2B3 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
15745 | XVEL2B3 | Environment | protective treatment | TC
15746 | XVEL2B3 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
15747 | XVEL2B3 | Packing Units | Package 1 Weight | 0.232 kg
15748 | XVEL2B3 | Contractual warranty | Warranty | 18 months
15749 | XVEL2B4 | Main | range of product | Harmony XVE Optimum
15750 | XVEL2B4 | Main | product or component type | Complete illuminated beacon
15751 | XVEL2B4 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
15752 | XVEL2B4 | Main | signalling type | Steady
15753 | XVEL2B4 | Main | component name | XVE
15754 | XVEL2B4 | Main | light source | Integral LED, red
15755 | XVEL2B4 | Main | bulb type | LED
15756 | XVEL2B4 | Main | [Us] rated supply voltage | 24 V AC/DC
15757 | XVEL2B4 | Complementary | mounting diameter | 70 mm
15758 | XVEL2B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
15759 | XVEL2B4 | Complementary | marking | CE
15760 | XVEL2B4 | Complementary | short-circuit protection | 0.63 A
15761 | XVEL2B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15762 | XVEL2B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15763 | XVEL2B4 | Complementary | current consumption | < 25 mA
15764 | XVEL2B4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15765 | XVEL2B4 | Complementary | luminance | 800 cd/m²
15766 | XVEL2B4 | Complementary | CAD overall width | 70 mm
15767 | XVEL2B4 | Complementary | CAD overall height | 129 mm
15768 | XVEL2B4 | Complementary | CAD overall depth | 70 mm
15769 | XVEL2B4 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
15770 | XVEL2B4 | Complementary | net weight | 0.25 kg
15771 | XVEL2B4 | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15772 | XVEL2B4 | Environment | product certifications | UL CCC CSA
15773 | XVEL2B4 | Environment | ambient air temperature for storage | -40…70 °C
15774 | XVEL2B4 | Environment | ambient air temperature for operation | -25…55 °C
15775 | XVEL2B4 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
15776 | XVEL2B4 | Environment | protective treatment | TC
15777 | XVEL2B4 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
15778 | XVEL2B4 | Packing Units | Package 1 Weight | 0.231 kg
15779 | XVEL2B4 | Contractual warranty | Warranty | 18 months
15780 | XVEL2B5 | Main | range of product | Harmony XVE Optimum
15781 | XVEL2B5 | Main | product or component type | Complete illuminated beacon
15782 | XVEL2B5 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
15783 | XVEL2B5 | Main | signalling type | Steady
15784 | XVEL2B5 | Main | component name | XVE
15785 | XVEL2B5 | Main | light source | Integral LED, orange
15786 | XVEL2B5 | Main | bulb type | LED
15787 | XVEL2B5 | Main | [Us] rated supply voltage | 24 V AC/DC
15788 | XVEL2B5 | Complementary | mounting diameter | 70 mm
15789 | XVEL2B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
15790 | XVEL2B5 | Complementary | marking | CE
15791 | XVEL2B5 | Complementary | short-circuit protection | 0.63 A
15792 | XVEL2B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15793 | XVEL2B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15794 | XVEL2B5 | Complementary | current consumption | < 25 mA
15795 | XVEL2B5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15796 | XVEL2B5 | Complementary | luminance | 800 cd/m²
15797 | XVEL2B5 | Complementary | CAD overall width | 70 mm
15798 | XVEL2B5 | Complementary | CAD overall height | 129 mm
15799 | XVEL2B5 | Complementary | CAD overall depth | 70 mm
15800 | XVEL2B5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
15801 | XVEL2B5 | Complementary | net weight | 0.25 kg
15802 | XVEL2B5 | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15803 | XVEL2B5 | Environment | product certifications | CCC CSA UL
15804 | XVEL2B5 | Environment | ambient air temperature for storage | -40…70 °C
15805 | XVEL2B5 | Environment | ambient air temperature for operation | -25…55 °C
15806 | XVEL2B5 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
15807 | XVEL2B5 | Environment | protective treatment | TC
15808 | XVEL2B5 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
15809 | XVEL2B5 | Packing Units | Package 1 Weight | 0.231 kg
15810 | XVEL2B5 | Contractual warranty | Warranty | 18 months
15811 | XVEL2B6 | Main | range of product | Harmony XVE Optimum
15812 | XVEL2B6 | Main | product or component type | Complete illuminated beacon
15813 | XVEL2B6 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
15814 | XVEL2B6 | Main | signalling type | Steady
15815 | XVEL2B6 | Main | component name | XVE
15816 | XVEL2B6 | Main | light source | Integral LED, blue
15817 | XVEL2B6 | Main | bulb type | LED
15818 | XVEL2B6 | Main | [Us] rated supply voltage | 24 V AC/DC
15819 | XVEL2B6 | Complementary | mounting diameter | 70 mm
15820 | XVEL2B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
15821 | XVEL2B6 | Complementary | marking | CE
15822 | XVEL2B6 | Complementary | short-circuit protection | 0.63 A
15823 | XVEL2B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15824 | XVEL2B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15825 | XVEL2B6 | Complementary | current consumption | < 25 mA
15826 | XVEL2B6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
15827 | XVEL2B6 | Complementary | luminance | 800 cd/m²
15828 | XVEL2B6 | Complementary | CAD overall width | 70 mm
15829 | XVEL2B6 | Complementary | CAD overall height | 129 mm
15830 | XVEL2B6 | Complementary | CAD overall depth | 70 mm
15831 | XVEL2B6 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
15832 | XVEL2B6 | Complementary | net weight | 0.25 kg
15833 | XVEL2B6 | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15834 | XVEL2B6 | Environment | product certifications | CCC CSA UL
15835 | XVEL2B6 | Environment | ambient air temperature for storage | -40…70 °C
15836 | XVEL2B6 | Environment | ambient air temperature for operation | -25…55 °C
15837 | XVEL2B6 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
15838 | XVEL2B6 | Environment | protective treatment | TC
15839 | XVEL2B6 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
15840 | XVEL2B6 | Contractual warranty | Warranty | 18 months
15841 | XVEL2B7 | Main | range of product | Harmony XVE Optimum
15842 | XVEL2B7 | Main | product or component type | Complete illuminated beacon
15843 | XVEL2B7 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
15844 | XVEL2B7 | Main | signalling type | Steady
15845 | XVEL2B7 | Main | component name | XVE
15846 | XVEL2B7 | Main | light source | Integral LED, clear
15847 | XVEL2B7 | Main | bulb type | LED
15848 | XVEL2B7 | Main | [Us] rated supply voltage | 24 V AC/DC
15849 | XVEL2B7 | Complementary | mounting diameter | 70 mm
15850 | XVEL2B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
15851 | XVEL2B7 | Complementary | marking | CE
15852 | XVEL2B7 | Complementary | short-circuit protection | 0.63 A
15853 | XVEL2B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15854 | XVEL2B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15855 | XVEL2B7 | Complementary | current consumption | < 25 mA
15856 | XVEL2B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
15857 | XVEL2B7 | Complementary | luminance | 800 cd/m²
15858 | XVEL2B7 | Complementary | CAD overall width | 70 mm
15859 | XVEL2B7 | Complementary | CAD overall height | 129 mm
15860 | XVEL2B7 | Complementary | CAD overall depth | 70 mm
15861 | XVEL2B7 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
15862 | XVEL2B7 | Complementary | net weight | 0.25 kg
15863 | XVEL2B7 | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15864 | XVEL2B7 | Environment | product certifications | CCC UL CSA
15865 | XVEL2B7 | Environment | ambient air temperature for storage | -40…70 °C
15866 | XVEL2B7 | Environment | ambient air temperature for operation | -25…55 °C
15867 | XVEL2B7 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
15868 | XVEL2B7 | Environment | protective treatment | TC
15869 | XVEL2B7 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
15870 | XVEL2B7 | Contractual warranty | Warranty | 18 months
15871 | XVEL2G3 | Main | range of product | Harmony XVE Optimum
15872 | XVEL2G3 | Main | product or component type | Complete illuminated beacon
15873 | XVEL2G3 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
15874 | XVEL2G3 | Main | signalling type | Steady
15875 | XVEL2G3 | Main | component name | XVE
15876 | XVEL2G3 | Main | light source | Integral LED, green
15877 | XVEL2G3 | Main | bulb type | LED
15878 | XVEL2G3 | Main | [Us] rated supply voltage | 120 V AC
15879 | XVEL2G3 | Complementary | mounting diameter | 70 mm
15880 | XVEL2G3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
15881 | XVEL2G3 | Complementary | marking | CE
15882 | XVEL2G3 | Complementary | short-circuit protection | 0.16 A
15883 | XVEL2G3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15884 | XVEL2G3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15885 | XVEL2G3 | Complementary | current consumption | < 25 mA
15886 | XVEL2G3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
15887 | XVEL2G3 | Complementary | luminance | 800 cd/m²
15888 | XVEL2G3 | Complementary | CAD overall width | 70 mm
15889 | XVEL2G3 | Complementary | CAD overall height | 129 mm
15890 | XVEL2G3 | Complementary | CAD overall depth | 70 mm
15891 | XVEL2G3 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
15892 | XVEL2G3 | Complementary | net weight | 0.25 kg
15893 | XVEL2G3 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
15894 | XVEL2G3 | Environment | product certifications | UL CCC CSA
15895 | XVEL2G3 | Environment | ambient air temperature for storage | -40…70 °C
15896 | XVEL2G3 | Environment | ambient air temperature for operation | -25…55 °C
15897 | XVEL2G3 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
15898 | XVEL2G3 | Environment | protective treatment | TC
15899 | XVEL2G3 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
15900 | XVEL2G3 | Contractual warranty | Warranty | 18 months
15901 | XVEL2G4 | Main | range of product | Harmony XVE Optimum
15902 | XVEL2G4 | Main | product or component type | Complete illuminated beacon
15903 | XVEL2G4 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
15904 | XVEL2G4 | Main | signalling type | Steady
15905 | XVEL2G4 | Main | component name | XVE
15906 | XVEL2G4 | Main | light source | Integral LED, red
15907 | XVEL2G4 | Main | bulb type | LED
15908 | XVEL2G4 | Main | [Us] rated supply voltage | 120 V AC
15909 | XVEL2G4 | Complementary | mounting diameter | 70 mm
15910 | XVEL2G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
15911 | XVEL2G4 | Complementary | marking | CE
15912 | XVEL2G4 | Complementary | short-circuit protection | 0.16 A
15913 | XVEL2G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15914 | XVEL2G4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15915 | XVEL2G4 | Complementary | current consumption | < 25 mA
15916 | XVEL2G4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
15917 | XVEL2G4 | Complementary | luminance | 800 cd/m²
15918 | XVEL2G4 | Complementary | CAD overall width | 70 mm
15919 | XVEL2G4 | Complementary | CAD overall height | 129 mm
15920 | XVEL2G4 | Complementary | CAD overall depth | 70 mm
15921 | XVEL2G4 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
15922 | XVEL2G4 | Complementary | net weight | 0.25 kg
15923 | XVEL2G4 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
15924 | XVEL2G4 | Environment | product certifications | CCC CSA UL
15925 | XVEL2G4 | Environment | ambient air temperature for storage | -40…70 °C
15926 | XVEL2G4 | Environment | ambient air temperature for operation | -25…55 °C
15927 | XVEL2G4 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
15928 | XVEL2G4 | Environment | protective treatment | TC
15929 | XVEL2G4 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
15930 | XVEL2G4 | Contractual warranty | Warranty | 18 months
15931 | XVEL2G5 | Main | range of product | Harmony XVE Optimum
15932 | XVEL2G5 | Main | product or component type | Complete illuminated beacon
15933 | XVEL2G5 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
15934 | XVEL2G5 | Main | signalling type | Steady
15935 | XVEL2G5 | Main | component name | XVE
15936 | XVEL2G5 | Main | light source | Integral LED, orange
15937 | XVEL2G5 | Main | bulb type | LED
15938 | XVEL2G5 | Main | [Us] rated supply voltage | 120 V AC
15939 | XVEL2G5 | Complementary | mounting diameter | 70 mm
15940 | XVEL2G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
15941 | XVEL2G5 | Complementary | marking | CE
15942 | XVEL2G5 | Complementary | short-circuit protection | 0.16 A
15943 | XVEL2G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15944 | XVEL2G5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15945 | XVEL2G5 | Complementary | current consumption | < 25 mA
15946 | XVEL2G5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
15947 | XVEL2G5 | Complementary | luminance | 800 cd/m²
15948 | XVEL2G5 | Complementary | CAD overall width | 70 mm
15949 | XVEL2G5 | Complementary | CAD overall height | 129 mm
15950 | XVEL2G5 | Complementary | CAD overall depth | 70 mm
15951 | XVEL2G5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
15952 | XVEL2G5 | Complementary | net weight | 0.25 kg
15953 | XVEL2G5 | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15954 | XVEL2G5 | Environment | product certifications | CCC UL CSA
15955 | XVEL2G5 | Environment | ambient air temperature for storage | -40…70 °C
15956 | XVEL2G5 | Environment | ambient air temperature for operation | -25…55 °C
15957 | XVEL2G5 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
15958 | XVEL2G5 | Environment | protective treatment | TC
15959 | XVEL2G5 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
15960 | XVEL2G5 | Contractual warranty | Warranty | 18 months
15961 | XVEL2G6 | Main | range of product | Harmony XVE Optimum
15962 | XVEL2G6 | Main | product or component type | Complete illuminated beacon
15963 | XVEL2G6 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
15964 | XVEL2G6 | Main | signalling type | Steady
15965 | XVEL2G6 | Main | component name | XVE
15966 | XVEL2G6 | Main | light source | Integral LED, blue
15967 | XVEL2G6 | Main | bulb type | LED
15968 | XVEL2G6 | Main | [Us] rated supply voltage | 120 V AC
15969 | XVEL2G6 | Complementary | mounting diameter | 70 mm
15970 | XVEL2G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
15971 | XVEL2G6 | Complementary | marking | CE
15972 | XVEL2G6 | Complementary | short-circuit protection | 0.16 A
15973 | XVEL2G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
15974 | XVEL2G6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
15975 | XVEL2G6 | Complementary | current consumption | < 25 mA
15976 | XVEL2G6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
15977 | XVEL2G6 | Complementary | luminance | 800 cd/m²
15978 | XVEL2G6 | Complementary | CAD overall width | 70 mm
15979 | XVEL2G6 | Complementary | CAD overall height | 129 mm
15980 | XVEL2G6 | Complementary | CAD overall depth | 70 mm
15981 | XVEL2G6 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
15982 | XVEL2G6 | Complementary | net weight | 0.25 kg
15983 | XVEL2G6 | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
15984 | XVEL2G6 | Environment | product certifications | CCC UL CSA
15985 | XVEL2G6 | Environment | ambient air temperature for storage | -40…70 °C
15986 | XVEL2G6 | Environment | ambient air temperature for operation | -25…55 °C
15987 | XVEL2G6 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
15988 | XVEL2G6 | Environment | protective treatment | TC
15989 | XVEL2G6 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
15990 | XVEL2G6 | Contractual warranty | Warranty | 18 months
15991 | XVEL2G7 | Main | range of product | Harmony XVE Optimum
15992 | XVEL2G7 | Main | product or component type | Complete illuminated beacon
15993 | XVEL2G7 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
15994 | XVEL2G7 | Main | signalling type | Steady
15995 | XVEL2G7 | Main | component name | XVE
15996 | XVEL2G7 | Main | light source | Integral LED, clear
15997 | XVEL2G7 | Main | bulb type | LED
15998 | XVEL2G7 | Main | [Us] rated supply voltage | 120 V AC
15999 | XVEL2G7 | Complementary | mounting diameter | 70 mm
16000 | XVEL2G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16001 | XVEL2G7 | Complementary | marking | CE
16002 | XVEL2G7 | Complementary | short-circuit protection | 0.16 A
16003 | XVEL2G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16004 | XVEL2G7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16005 | XVEL2G7 | Complementary | current consumption | < 25 mA
16006 | XVEL2G7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16007 | XVEL2G7 | Complementary | luminance | 800 cd/m²
16008 | XVEL2G7 | Complementary | CAD overall width | 70 mm
16009 | XVEL2G7 | Complementary | CAD overall height | 129 mm
16010 | XVEL2G7 | Complementary | CAD overall depth | 70 mm
16011 | XVEL2G7 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
16012 | XVEL2G7 | Complementary | net weight | 0.25 kg
16013 | XVEL2G7 | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
16014 | XVEL2G7 | Environment | product certifications | UL CSA CCC
16015 | XVEL2G7 | Environment | ambient air temperature for storage | -40…70 °C
16016 | XVEL2G7 | Environment | ambient air temperature for operation | -25…55 °C
16017 | XVEL2G7 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16018 | XVEL2G7 | Environment | protective treatment | TC
16019 | XVEL2G7 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16020 | XVEL2G7 | Contractual warranty | Warranty | 18 months
16021 | XVEL2M3 | Main | range of product | Harmony XVE Optimum
16022 | XVEL2M3 | Main | product or component type | Complete illuminated beacon
16023 | XVEL2M3 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16024 | XVEL2M3 | Main | signalling type | Steady
16025 | XVEL2M3 | Main | component name | XVE
16026 | XVEL2M3 | Main | light source | Integral LED, green
16027 | XVEL2M3 | Main | bulb type | LED
16028 | XVEL2M3 | Main | [Us] rated supply voltage | 230...240 V AC
16029 | XVEL2M3 | Complementary | mounting diameter | 70 mm
16030 | XVEL2M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16031 | XVEL2M3 | Complementary | marking | CE
16032 | XVEL2M3 | Complementary | short-circuit protection | 0.16 A
16033 | XVEL2M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16034 | XVEL2M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16035 | XVEL2M3 | Complementary | current consumption | < 25 mA
16036 | XVEL2M3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16037 | XVEL2M3 | Complementary | luminance | 800 cd/m²
16038 | XVEL2M3 | Complementary | CAD overall width | 70 mm
16039 | XVEL2M3 | Complementary | CAD overall height | 129 mm
16040 | XVEL2M3 | Complementary | CAD overall depth | 70 mm
16041 | XVEL2M3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
16042 | XVEL2M3 | Complementary | net weight | 0.25 kg
16043 | XVEL2M3 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
16044 | XVEL2M3 | Environment | product certifications | UL CCC CSA
16045 | XVEL2M3 | Environment | ambient air temperature for storage | -40…70 °C
16046 | XVEL2M3 | Environment | ambient air temperature for operation | -25…55 °C
16047 | XVEL2M3 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16048 | XVEL2M3 | Environment | protective treatment | TC
16049 | XVEL2M3 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16050 | XVEL2M3 | Contractual warranty | Warranty | 18 months
16051 | XVEL2M4 | Main | range of product | Harmony XVE Optimum
16052 | XVEL2M4 | Main | product or component type | Complete illuminated beacon
16053 | XVEL2M4 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16054 | XVEL2M4 | Main | signalling type | Steady
16055 | XVEL2M4 | Main | component name | XVE
16056 | XVEL2M4 | Main | light source | Integral LED, red
16057 | XVEL2M4 | Main | bulb type | LED
16058 | XVEL2M4 | Main | [Us] rated supply voltage | 230...240 V AC
16059 | XVEL2M4 | Complementary | mounting diameter | 70 mm
16060 | XVEL2M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16061 | XVEL2M4 | Complementary | marking | CE
16062 | XVEL2M4 | Complementary | short-circuit protection | 0.16 A
16063 | XVEL2M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16064 | XVEL2M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16065 | XVEL2M4 | Complementary | current consumption | < 25 mA
16066 | XVEL2M4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
16067 | XVEL2M4 | Complementary | luminance | 800 cd/m²
16068 | XVEL2M4 | Complementary | CAD overall width | 70 mm
16069 | XVEL2M4 | Complementary | CAD overall height | 129 mm
16070 | XVEL2M4 | Complementary | CAD overall depth | 70 mm
16071 | XVEL2M4 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
16072 | XVEL2M4 | Complementary | net weight | 0.25 kg
16073 | XVEL2M4 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
16074 | XVEL2M4 | Environment | product certifications | UL CCC CSA
16075 | XVEL2M4 | Environment | ambient air temperature for storage | -40…70 °C
16076 | XVEL2M4 | Environment | ambient air temperature for operation | -25…55 °C
16077 | XVEL2M4 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16078 | XVEL2M4 | Environment | protective treatment | TC
16079 | XVEL2M4 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16080 | XVEL2M4 | Packing Units | Package 1 Weight | 0.231 kg
16081 | XVEL2M4 | Contractual warranty | Warranty | 18 months
16082 | XVEL2M5 | Main | range of product | Harmony XVE Optimum
16083 | XVEL2M5 | Main | product or component type | Complete illuminated beacon
16084 | XVEL2M5 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16085 | XVEL2M5 | Main | signalling type | Steady
16086 | XVEL2M5 | Main | component name | XVE
16087 | XVEL2M5 | Main | light source | Integral LED, orange
16088 | XVEL2M5 | Main | bulb type | LED
16089 | XVEL2M5 | Main | [Us] rated supply voltage | 230...240 V AC
16090 | XVEL2M5 | Complementary | mounting diameter | 70 mm
16091 | XVEL2M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16092 | XVEL2M5 | Complementary | marking | CE
16093 | XVEL2M5 | Complementary | short-circuit protection | 0.16 A
16094 | XVEL2M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16095 | XVEL2M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16096 | XVEL2M5 | Complementary | current consumption | < 25 mA
16097 | XVEL2M5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
16098 | XVEL2M5 | Complementary | luminance | 800 cd/m²
16099 | XVEL2M5 | Complementary | CAD overall width | 70 mm
16100 | XVEL2M5 | Complementary | CAD overall height | 129 mm
16101 | XVEL2M5 | Complementary | CAD overall depth | 70 mm
16102 | XVEL2M5 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16103 | XVEL2M5 | Complementary | net weight | 0.25 kg
16104 | XVEL2M5 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
16105 | XVEL2M5 | Environment | product certifications | UL CSA CCC
16106 | XVEL2M5 | Environment | ambient air temperature for storage | -40…70 °C
16107 | XVEL2M5 | Environment | ambient air temperature for operation | -25…55 °C
16108 | XVEL2M5 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16109 | XVEL2M5 | Environment | protective treatment | TC
16110 | XVEL2M5 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16111 | XVEL2M5 | Contractual warranty | Warranty | 18 months
16112 | XVEL2M6 | Main | range of product | Harmony XVE Optimum
16113 | XVEL2M6 | Main | product or component type | Complete illuminated beacon
16114 | XVEL2M6 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16115 | XVEL2M6 | Main | signalling type | Steady
16116 | XVEL2M6 | Main | component name | XVE
16117 | XVEL2M6 | Main | light source | Integral LED, blue
16118 | XVEL2M6 | Main | bulb type | LED
16119 | XVEL2M6 | Main | [Us] rated supply voltage | 230...240 V AC
16120 | XVEL2M6 | Complementary | mounting diameter | 70 mm
16121 | XVEL2M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16122 | XVEL2M6 | Complementary | marking | CE
16123 | XVEL2M6 | Complementary | short-circuit protection | 0.16 A
16124 | XVEL2M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16125 | XVEL2M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16126 | XVEL2M6 | Complementary | current consumption | < 25 mA
16127 | XVEL2M6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16128 | XVEL2M6 | Complementary | luminance | 800 cd/m²
16129 | XVEL2M6 | Complementary | CAD overall width | 70 mm
16130 | XVEL2M6 | Complementary | CAD overall height | 129 mm
16131 | XVEL2M6 | Complementary | CAD overall depth | 70 mm
16132 | XVEL2M6 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
16133 | XVEL2M6 | Complementary | net weight | 0.25 kg
16134 | XVEL2M6 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
16135 | XVEL2M6 | Environment | product certifications | UL CSA CCC
16136 | XVEL2M6 | Environment | ambient air temperature for storage | -40…70 °C
16137 | XVEL2M6 | Environment | ambient air temperature for operation | -25…55 °C
16138 | XVEL2M6 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16139 | XVEL2M6 | Environment | protective treatment | TC
16140 | XVEL2M6 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16141 | XVEL2M6 | Contractual warranty | Warranty | 18 months
16142 | XVEL2M7 | Main | range of product | Harmony XVE Optimum
16143 | XVEL2M7 | Main | product or component type | Complete illuminated beacon
16144 | XVEL2M7 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16145 | XVEL2M7 | Main | signalling type | Steady
16146 | XVEL2M7 | Main | component name | XVE
16147 | XVEL2M7 | Main | light source | Integral LED, clear
16148 | XVEL2M7 | Main | bulb type | LED
16149 | XVEL2M7 | Main | [Us] rated supply voltage | 230...240 V AC
16150 | XVEL2M7 | Complementary | mounting diameter | 70 mm
16151 | XVEL2M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16152 | XVEL2M7 | Complementary | marking | CE
16153 | XVEL2M7 | Complementary | short-circuit protection | 0.16 A
16154 | XVEL2M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16155 | XVEL2M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16156 | XVEL2M7 | Complementary | current consumption | < 25 mA
16157 | XVEL2M7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
16158 | XVEL2M7 | Complementary | luminance | 800 cd/m²
16159 | XVEL2M7 | Complementary | CAD overall width | 70 mm
16160 | XVEL2M7 | Complementary | CAD overall height | 129 mm
16161 | XVEL2M7 | Complementary | CAD overall depth | 70 mm
16162 | XVEL2M7 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16163 | XVEL2M7 | Complementary | net weight | 0.25 kg
16164 | XVEL2M7 | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
16165 | XVEL2M7 | Environment | product certifications | CCC UL CSA
16166 | XVEL2M7 | Environment | ambient air temperature for storage | -40…70 °C
16167 | XVEL2M7 | Environment | ambient air temperature for operation | -25…55 °C
16168 | XVEL2M7 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16169 | XVEL2M7 | Environment | protective treatment | TC
16170 | XVEL2M7 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16171 | XVEL2M7 | Contractual warranty | Warranty | 18 months
16172 | XVEL6B3 | Main | range of product | Harmony XVE Optimum
16173 | XVEL6B3 | Main | product or component type | Complete illuminated beacon
16174 | XVEL6B3 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16175 | XVEL6B3 | Main | signalling type | Flashing
16176 | XVEL6B3 | Main | component name | XVE
16177 | XVEL6B3 | Main | light source | Integral flash discharge tube, green
16178 | XVEL6B3 | Main | bulb type | Flash discharge tube
16179 | XVEL6B3 | Main | [Us] rated supply voltage | 24 V AC/DC
16180 | XVEL6B3 | Complementary | mounting diameter | 70 mm
16181 | XVEL6B3 | Complementary | flash energy | 1 J
16182 | XVEL6B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16183 | XVEL6B3 | Complementary | marking | CE
16184 | XVEL6B3 | Complementary | short-circuit protection | 0.63 A
16185 | XVEL6B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16186 | XVEL6B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16187 | XVEL6B3 | Complementary | current consumption | < 145 mA AC < 85 mA DC
16188 | XVEL6B3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
16189 | XVEL6B3 | Complementary | flashing frequency | 1 Hz
16190 | XVEL6B3 | Complementary | CAD overall width | 70 mm
16191 | XVEL6B3 | Complementary | CAD overall height | 129 mm
16192 | XVEL6B3 | Complementary | CAD overall depth | 70 mm
16193 | XVEL6B3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
16194 | XVEL6B3 | Complementary | net weight | 0.27 kg
16195 | XVEL6B3 | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
16196 | XVEL6B3 | Environment | product certifications | CSA CCC UL
16197 | XVEL6B3 | Environment | ambient air temperature for storage | -40…70 °C
16198 | XVEL6B3 | Environment | ambient air temperature for operation | -25…55 °C
16199 | XVEL6B3 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16200 | XVEL6B3 | Environment | protective treatment | TC
16201 | XVEL6B3 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16202 | XVEL6B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16203 | XVEL6B3 | Offer Sustainability | Mercury free | Yes
16204 | XVEL6B3 | Offer Sustainability | RoHS exemption information | Yes
16205 | XVEL6B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16206 | XVEL6B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16207 | XVEL6B3 | Contractual warranty | Warranty | 18 months
16208 | XVEL6B4 | Main | range of product | Harmony XVE Optimum
16209 | XVEL6B4 | Main | product or component type | Complete illuminated beacon
16210 | XVEL6B4 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16211 | XVEL6B4 | Main | signalling type | Flashing
16212 | XVEL6B4 | Main | component name | XVE
16213 | XVEL6B4 | Main | light source | Integral flash discharge tube, red
16214 | XVEL6B4 | Main | bulb type | Flash discharge tube
16215 | XVEL6B4 | Main | [Us] rated supply voltage | 24 V AC/DC
16216 | XVEL6B4 | Complementary | mounting diameter | 70 mm
16217 | XVEL6B4 | Complementary | flash energy | 1 J
16218 | XVEL6B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16219 | XVEL6B4 | Complementary | marking | CE
16220 | XVEL6B4 | Complementary | short-circuit protection | 0.63 A
16221 | XVEL6B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16222 | XVEL6B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16223 | XVEL6B4 | Complementary | current consumption | < 145 mA AC < 85 mA DC
16224 | XVEL6B4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16225 | XVEL6B4 | Complementary | flashing frequency | 1 Hz
16226 | XVEL6B4 | Complementary | CAD overall width | 70 mm
16227 | XVEL6B4 | Complementary | CAD overall height | 129 mm
16228 | XVEL6B4 | Complementary | CAD overall depth | 70 mm
16229 | XVEL6B4 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16230 | XVEL6B4 | Complementary | net weight | 0.27 kg
16231 | XVEL6B4 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
16232 | XVEL6B4 | Environment | product certifications | UL CCC CSA
16233 | XVEL6B4 | Environment | ambient air temperature for storage | -40…70 °C
16234 | XVEL6B4 | Environment | ambient air temperature for operation | -25…55 °C
16235 | XVEL6B4 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16236 | XVEL6B4 | Environment | protective treatment | TC
16237 | XVEL6B4 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16238 | XVEL6B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16239 | XVEL6B4 | Offer Sustainability | Mercury free | Yes
16240 | XVEL6B4 | Offer Sustainability | RoHS exemption information | Yes
16241 | XVEL6B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16242 | XVEL6B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16243 | XVEL6B4 | Contractual warranty | Warranty | 18 months
16244 | XVEL6B5 | Main | range of product | Harmony XVE Optimum
16245 | XVEL6B5 | Main | product or component type | Complete illuminated beacon
16246 | XVEL6B5 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16247 | XVEL6B5 | Main | signalling type | Flashing
16248 | XVEL6B5 | Main | component name | XVE
16249 | XVEL6B5 | Main | light source | Integral flash discharge tube, orange
16250 | XVEL6B5 | Main | bulb type | Flash discharge tube
16251 | XVEL6B5 | Main | [Us] rated supply voltage | 24 V AC/DC
16252 | XVEL6B5 | Complementary | mounting diameter | 70 mm
16253 | XVEL6B5 | Complementary | flash energy | 1 J
16254 | XVEL6B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16255 | XVEL6B5 | Complementary | marking | CE
16256 | XVEL6B5 | Complementary | short-circuit protection | 0.63 A
16257 | XVEL6B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16258 | XVEL6B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16259 | XVEL6B5 | Complementary | current consumption | < 145 mA AC < 85 mA DC
16260 | XVEL6B5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
16261 | XVEL6B5 | Complementary | flashing frequency | 1 Hz
16262 | XVEL6B5 | Complementary | CAD overall width | 70 mm
16263 | XVEL6B5 | Complementary | CAD overall height | 129 mm
16264 | XVEL6B5 | Complementary | CAD overall depth | 70 mm
16265 | XVEL6B5 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16266 | XVEL6B5 | Complementary | net weight | 0.27 kg
16267 | XVEL6B5 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
16268 | XVEL6B5 | Environment | product certifications | UL CSA CCC
16269 | XVEL6B5 | Environment | ambient air temperature for storage | -40…70 °C
16270 | XVEL6B5 | Environment | ambient air temperature for operation | -25…55 °C
16271 | XVEL6B5 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16272 | XVEL6B5 | Environment | protective treatment | TC
16273 | XVEL6B5 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16274 | XVEL6B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16275 | XVEL6B5 | Offer Sustainability | Mercury free | Yes
16276 | XVEL6B5 | Offer Sustainability | RoHS exemption information | Yes
16277 | XVEL6B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16278 | XVEL6B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16279 | XVEL6B5 | Contractual warranty | Warranty | 18 months
16280 | XVEL6B6 | Main | range of product | Harmony XVE Optimum
16281 | XVEL6B6 | Main | product or component type | Complete illuminated beacon
16282 | XVEL6B6 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16283 | XVEL6B6 | Main | signalling type | Flashing
16284 | XVEL6B6 | Main | component name | XVE
16285 | XVEL6B6 | Main | light source | Integral flash discharge tube, blue
16286 | XVEL6B6 | Main | bulb type | Flash discharge tube
16287 | XVEL6B6 | Main | [Us] rated supply voltage | 24 V AC/DC
16288 | XVEL6B6 | Complementary | mounting diameter | 70 mm
16289 | XVEL6B6 | Complementary | flash energy | 1 J
16290 | XVEL6B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16291 | XVEL6B6 | Complementary | marking | CE
16292 | XVEL6B6 | Complementary | short-circuit protection | 0.63 A
16293 | XVEL6B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16294 | XVEL6B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16295 | XVEL6B6 | Complementary | current consumption | < 145 mA AC < 85 mA DC
16296 | XVEL6B6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16297 | XVEL6B6 | Complementary | flashing frequency | 1 Hz
16298 | XVEL6B6 | Complementary | CAD overall width | 70 mm
16299 | XVEL6B6 | Complementary | CAD overall height | 129 mm
16300 | XVEL6B6 | Complementary | CAD overall depth | 70 mm
16301 | XVEL6B6 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16302 | XVEL6B6 | Complementary | net weight | 0.27 kg
16303 | XVEL6B6 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
16304 | XVEL6B6 | Environment | product certifications | CCC CSA UL
16305 | XVEL6B6 | Environment | ambient air temperature for storage | -40…70 °C
16306 | XVEL6B6 | Environment | ambient air temperature for operation | -25…55 °C
16307 | XVEL6B6 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16308 | XVEL6B6 | Environment | protective treatment | TC
16309 | XVEL6B6 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16310 | XVEL6B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16311 | XVEL6B6 | Offer Sustainability | Mercury free | Yes
16312 | XVEL6B6 | Offer Sustainability | RoHS exemption information | Yes
16313 | XVEL6B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16314 | XVEL6B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16315 | XVEL6B6 | Contractual warranty | Warranty | 18 months
16316 | XVEL6B7 | Main | range of product | Harmony XVE Optimum
16317 | XVEL6B7 | Main | product or component type | Complete illuminated beacon
16318 | XVEL6B7 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16319 | XVEL6B7 | Main | signalling type | Flashing
16320 | XVEL6B7 | Main | component name | XVE
16321 | XVEL6B7 | Main | light source | Integral flash discharge tube, clear
16322 | XVEL6B7 | Main | bulb type | Flash discharge tube
16323 | XVEL6B7 | Main | [Us] rated supply voltage | 24 V AC/DC
16324 | XVEL6B7 | Complementary | mounting diameter | 70 mm
16325 | XVEL6B7 | Complementary | flash energy | 1 J
16326 | XVEL6B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16327 | XVEL6B7 | Complementary | marking | CE
16328 | XVEL6B7 | Complementary | short-circuit protection | 0.63 A
16329 | XVEL6B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16330 | XVEL6B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16331 | XVEL6B7 | Complementary | current consumption | < 145 mA AC < 85 mA DC
16332 | XVEL6B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16333 | XVEL6B7 | Complementary | flashing frequency | 1 Hz
16334 | XVEL6B7 | Complementary | CAD overall width | 70 mm
16335 | XVEL6B7 | Complementary | CAD overall height | 129 mm
16336 | XVEL6B7 | Complementary | CAD overall depth | 70 mm
16337 | XVEL6B7 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16338 | XVEL6B7 | Complementary | net weight | 0.27 kg
16339 | XVEL6B7 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
16340 | XVEL6B7 | Environment | product certifications | CSA UL CCC
16341 | XVEL6B7 | Environment | ambient air temperature for storage | -40…70 °C
16342 | XVEL6B7 | Environment | ambient air temperature for operation | -25…55 °C
16343 | XVEL6B7 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16344 | XVEL6B7 | Environment | protective treatment | TC
16345 | XVEL6B7 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16346 | XVEL6B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16347 | XVEL6B7 | Offer Sustainability | Mercury free | Yes
16348 | XVEL6B7 | Offer Sustainability | RoHS exemption information | Yes
16349 | XVEL6B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16350 | XVEL6B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16351 | XVEL6B7 | Contractual warranty | Warranty | 18 months
16352 | XVEL6G3 | Main | range of product | Harmony XVE Optimum
16353 | XVEL6G3 | Main | product or component type | Complete illuminated beacon
16354 | XVEL6G3 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16355 | XVEL6G3 | Main | signalling type | Flashing
16356 | XVEL6G3 | Main | component name | XVE
16357 | XVEL6G3 | Main | light source | Integral flash discharge tube, green
16358 | XVEL6G3 | Main | bulb type | Flash discharge tube
16359 | XVEL6G3 | Main | [Us] rated supply voltage | 120 V AC
16360 | XVEL6G3 | Complementary | mounting diameter | 70 mm
16361 | XVEL6G3 | Complementary | flash energy | 1 J
16362 | XVEL6G3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16363 | XVEL6G3 | Complementary | marking | CE
16364 | XVEL6G3 | Complementary | short-circuit protection | 0.16 A
16365 | XVEL6G3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16366 | XVEL6G3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16367 | XVEL6G3 | Complementary | current consumption | < 35 mA
16368 | XVEL6G3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16369 | XVEL6G3 | Complementary | flashing frequency | 1 Hz
16370 | XVEL6G3 | Complementary | CAD overall width | 70 mm
16371 | XVEL6G3 | Complementary | CAD overall height | 129 mm
16372 | XVEL6G3 | Complementary | CAD overall depth | 70 mm
16373 | XVEL6G3 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16374 | XVEL6G3 | Complementary | net weight | 0.27 kg
16375 | XVEL6G3 | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
16376 | XVEL6G3 | Environment | product certifications | CSA CCC UL
16377 | XVEL6G3 | Environment | ambient air temperature for storage | -40…70 °C
16378 | XVEL6G3 | Environment | ambient air temperature for operation | -25…55 °C
16379 | XVEL6G3 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16380 | XVEL6G3 | Environment | protective treatment | TC
16381 | XVEL6G3 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16382 | XVEL6G3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16383 | XVEL6G3 | Offer Sustainability | Mercury free | Yes
16384 | XVEL6G3 | Offer Sustainability | RoHS exemption information | Yes
16385 | XVEL6G3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16386 | XVEL6G3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16387 | XVEL6G3 | Contractual warranty | Warranty | 18 months
16388 | XVEL6G4 | Main | range of product | Harmony XVE Optimum
16389 | XVEL6G4 | Main | product or component type | Complete illuminated beacon
16390 | XVEL6G4 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16391 | XVEL6G4 | Main | signalling type | Flashing
16392 | XVEL6G4 | Main | component name | XVE
16393 | XVEL6G4 | Main | light source | Integral flash discharge tube, red
16394 | XVEL6G4 | Main | bulb type | Flash discharge tube
16395 | XVEL6G4 | Main | [Us] rated supply voltage | 120 V AC
16396 | XVEL6G4 | Complementary | mounting diameter | 70 mm
16397 | XVEL6G4 | Complementary | flash energy | 1 J
16398 | XVEL6G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16399 | XVEL6G4 | Complementary | marking | CE
16400 | XVEL6G4 | Complementary | short-circuit protection | 0.16 A
16401 | XVEL6G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16402 | XVEL6G4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16403 | XVEL6G4 | Complementary | current consumption | < 35 mA
16404 | XVEL6G4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16405 | XVEL6G4 | Complementary | flashing frequency | 1 Hz
16406 | XVEL6G4 | Complementary | CAD overall width | 70 mm
16407 | XVEL6G4 | Complementary | CAD overall height | 129 mm
16408 | XVEL6G4 | Complementary | CAD overall depth | 70 mm
16409 | XVEL6G4 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16410 | XVEL6G4 | Complementary | net weight | 0.27 kg
16411 | XVEL6G4 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
16412 | XVEL6G4 | Environment | product certifications | CCC CSA UL
16413 | XVEL6G4 | Environment | ambient air temperature for storage | -40…70 °C
16414 | XVEL6G4 | Environment | ambient air temperature for operation | -25…55 °C
16415 | XVEL6G4 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16416 | XVEL6G4 | Environment | protective treatment | TC
16417 | XVEL6G4 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16418 | XVEL6G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16419 | XVEL6G4 | Offer Sustainability | Mercury free | Yes
16420 | XVEL6G4 | Offer Sustainability | RoHS exemption information | Yes
16421 | XVEL6G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16422 | XVEL6G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16423 | XVEL6G4 | Contractual warranty | Warranty | 18 months
16424 | XVEL6G5 | Main | range of product | Harmony XVE Optimum
16425 | XVEL6G5 | Main | product or component type | Complete illuminated beacon
16426 | XVEL6G5 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16427 | XVEL6G5 | Main | signalling type | Flashing
16428 | XVEL6G5 | Main | component name | XVE
16429 | XVEL6G5 | Main | light source | Integral flash discharge tube, orange
16430 | XVEL6G5 | Main | bulb type | Flash discharge tube
16431 | XVEL6G5 | Main | [Us] rated supply voltage | 120 V AC
16432 | XVEL6G5 | Complementary | mounting diameter | 70 mm
16433 | XVEL6G5 | Complementary | flash energy | 1 J
16434 | XVEL6G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16435 | XVEL6G5 | Complementary | marking | CE
16436 | XVEL6G5 | Complementary | short-circuit protection | 0.16 A
16437 | XVEL6G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16438 | XVEL6G5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16439 | XVEL6G5 | Complementary | current consumption | < 35 mA
16440 | XVEL6G5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16441 | XVEL6G5 | Complementary | flashing frequency | 1 Hz
16442 | XVEL6G5 | Complementary | CAD overall width | 70 mm
16443 | XVEL6G5 | Complementary | CAD overall height | 129 mm
16444 | XVEL6G5 | Complementary | CAD overall depth | 70 mm
16445 | XVEL6G5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
16446 | XVEL6G5 | Complementary | net weight | 0.27 kg
16447 | XVEL6G5 | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
16448 | XVEL6G5 | Environment | product certifications | CSA CCC UL
16449 | XVEL6G5 | Environment | ambient air temperature for storage | -40…70 °C
16450 | XVEL6G5 | Environment | ambient air temperature for operation | -25…55 °C
16451 | XVEL6G5 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16452 | XVEL6G5 | Environment | protective treatment | TC
16453 | XVEL6G5 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16454 | XVEL6G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16455 | XVEL6G5 | Offer Sustainability | Mercury free | Yes
16456 | XVEL6G5 | Offer Sustainability | RoHS exemption information | Yes
16457 | XVEL6G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16458 | XVEL6G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16459 | XVEL6G5 | Contractual warranty | Warranty | 18 months
16460 | XVEL6G6 | Main | range of product | Harmony XVE Optimum
16461 | XVEL6G6 | Main | product or component type | Complete illuminated beacon
16462 | XVEL6G6 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16463 | XVEL6G6 | Main | signalling type | Flashing
16464 | XVEL6G6 | Main | component name | XVE
16465 | XVEL6G6 | Main | light source | Integral flash discharge tube, blue
16466 | XVEL6G6 | Main | bulb type | Flash discharge tube
16467 | XVEL6G6 | Main | [Us] rated supply voltage | 120 V AC
16468 | XVEL6G6 | Complementary | mounting diameter | 70 mm
16469 | XVEL6G6 | Complementary | flash energy | 1 J
16470 | XVEL6G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16471 | XVEL6G6 | Complementary | marking | CE
16472 | XVEL6G6 | Complementary | short-circuit protection | 0.16 A
16473 | XVEL6G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16474 | XVEL6G6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16475 | XVEL6G6 | Complementary | current consumption | < 35 mA
16476 | XVEL6G6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16477 | XVEL6G6 | Complementary | flashing frequency | 1 Hz
16478 | XVEL6G6 | Complementary | CAD overall width | 70 mm
16479 | XVEL6G6 | Complementary | CAD overall height | 129 mm
16480 | XVEL6G6 | Complementary | CAD overall depth | 70 mm
16481 | XVEL6G6 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16482 | XVEL6G6 | Complementary | net weight | 0.27 kg
16483 | XVEL6G6 | Environment | standards | EN/IEC 60947-1 EN/IEC 60947-5-1
16484 | XVEL6G6 | Environment | product certifications | CCC CSA UL
16485 | XVEL6G6 | Environment | ambient air temperature for storage | -40…70 °C
16486 | XVEL6G6 | Environment | ambient air temperature for operation | -25…55 °C
16487 | XVEL6G6 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16488 | XVEL6G6 | Environment | protective treatment | TC
16489 | XVEL6G6 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16490 | XVEL6G6 | Contractual warranty | Warranty | 18 months
16491 | XVEL6G7 | Main | range of product | Harmony XVE Optimum
16492 | XVEL6G7 | Main | product or component type | Complete illuminated beacon
16493 | XVEL6G7 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16494 | XVEL6G7 | Main | signalling type | Flashing
16495 | XVEL6G7 | Main | component name | XVE
16496 | XVEL6G7 | Main | light source | Integral flash discharge tube, clear
16497 | XVEL6G7 | Main | bulb type | Flash discharge tube
16498 | XVEL6G7 | Main | [Us] rated supply voltage | 120 V AC
16499 | XVEL6G7 | Complementary | mounting diameter | 70 mm
16500 | XVEL6G7 | Complementary | flash energy | 1 J
16501 | XVEL6G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16502 | XVEL6G7 | Complementary | marking | CE
16503 | XVEL6G7 | Complementary | short-circuit protection | 0.16 A
16504 | XVEL6G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16505 | XVEL6G7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16506 | XVEL6G7 | Complementary | current consumption | < 35 mA
16507 | XVEL6G7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16508 | XVEL6G7 | Complementary | flashing frequency | 1 Hz
16509 | XVEL6G7 | Complementary | CAD overall width | 70 mm
16510 | XVEL6G7 | Complementary | CAD overall height | 129 mm
16511 | XVEL6G7 | Complementary | CAD overall depth | 70 mm
16512 | XVEL6G7 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16513 | XVEL6G7 | Complementary | net weight | 0.27 kg
16514 | XVEL6G7 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
16515 | XVEL6G7 | Environment | product certifications | CCC CSA UL
16516 | XVEL6G7 | Environment | ambient air temperature for storage | -40…70 °C
16517 | XVEL6G7 | Environment | ambient air temperature for operation | -25…55 °C
16518 | XVEL6G7 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16519 | XVEL6G7 | Environment | protective treatment | TC
16520 | XVEL6G7 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16521 | XVEL6G7 | Contractual warranty | Warranty | 18 months
16522 | XVEL6M3 | Main | range of product | Harmony XVE Optimum
16523 | XVEL6M3 | Main | product or component type | Complete illuminated beacon
16524 | XVEL6M3 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16525 | XVEL6M3 | Main | signalling type | Flashing
16526 | XVEL6M3 | Main | component name | XVE
16527 | XVEL6M3 | Main | light source | Integral flash discharge tube, green
16528 | XVEL6M3 | Main | bulb type | Flash discharge tube
16529 | XVEL6M3 | Main | [Us] rated supply voltage | 230...240 V AC
16530 | XVEL6M3 | Complementary | mounting diameter | 70 mm
16531 | XVEL6M3 | Complementary | flash energy | 1 J
16532 | XVEL6M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16533 | XVEL6M3 | Complementary | marking | CE
16534 | XVEL6M3 | Complementary | short-circuit protection | 0.16 A
16535 | XVEL6M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16536 | XVEL6M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16537 | XVEL6M3 | Complementary | current consumption | < 25 mA
16538 | XVEL6M3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
16539 | XVEL6M3 | Complementary | flashing frequency | 1 Hz
16540 | XVEL6M3 | Complementary | CAD overall width | 70 mm
16541 | XVEL6M3 | Complementary | CAD overall height | 129 mm
16542 | XVEL6M3 | Complementary | CAD overall depth | 70 mm
16543 | XVEL6M3 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16544 | XVEL6M3 | Complementary | net weight | 0.27 kg
16545 | XVEL6M3 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
16546 | XVEL6M3 | Environment | product certifications | CSA UL CCC
16547 | XVEL6M3 | Environment | ambient air temperature for storage | -40…70 °C
16548 | XVEL6M3 | Environment | ambient air temperature for operation | -25…55 °C
16549 | XVEL6M3 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16550 | XVEL6M3 | Environment | protective treatment | TC
16551 | XVEL6M3 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16552 | XVEL6M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16553 | XVEL6M3 | Offer Sustainability | Mercury free | Yes
16554 | XVEL6M3 | Offer Sustainability | RoHS exemption information | Yes
16555 | XVEL6M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16556 | XVEL6M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16557 | XVEL6M3 | Contractual warranty | Warranty | 18 months
16558 | XVEL6M4 | Main | range of product | Harmony XVE Optimum
16559 | XVEL6M4 | Main | product or component type | Complete illuminated beacon
16560 | XVEL6M4 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16561 | XVEL6M4 | Main | signalling type | Flashing
16562 | XVEL6M4 | Main | component name | XVE
16563 | XVEL6M4 | Main | light source | Integral flash discharge tube, red
16564 | XVEL6M4 | Main | bulb type | Flash discharge tube
16565 | XVEL6M4 | Main | [Us] rated supply voltage | 230...240 V AC
16566 | XVEL6M4 | Complementary | mounting diameter | 70 mm
16567 | XVEL6M4 | Complementary | flash energy | 1 J
16568 | XVEL6M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16569 | XVEL6M4 | Complementary | marking | CE
16570 | XVEL6M4 | Complementary | short-circuit protection | 0.16 A
16571 | XVEL6M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16572 | XVEL6M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16573 | XVEL6M4 | Complementary | current consumption | < 25 mA
16574 | XVEL6M4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
16575 | XVEL6M4 | Complementary | flashing frequency | 1 Hz
16576 | XVEL6M4 | Complementary | CAD overall width | 70 mm
16577 | XVEL6M4 | Complementary | CAD overall height | 129 mm
16578 | XVEL6M4 | Complementary | CAD overall depth | 70 mm
16579 | XVEL6M4 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16580 | XVEL6M4 | Complementary | net weight | 0.27 kg
16581 | XVEL6M4 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
16582 | XVEL6M4 | Environment | product certifications | CCC UL CSA
16583 | XVEL6M4 | Environment | ambient air temperature for storage | -40…70 °C
16584 | XVEL6M4 | Environment | ambient air temperature for operation | -25…55 °C
16585 | XVEL6M4 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16586 | XVEL6M4 | Environment | protective treatment | TC
16587 | XVEL6M4 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16588 | XVEL6M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16589 | XVEL6M4 | Offer Sustainability | Mercury free | Yes
16590 | XVEL6M4 | Offer Sustainability | RoHS exemption information | Yes
16591 | XVEL6M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16592 | XVEL6M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16593 | XVEL6M4 | Contractual warranty | Warranty | 18 months
16594 | XVEL6M5 | Main | range of product | Harmony XVE Optimum
16595 | XVEL6M5 | Main | product or component type | Complete illuminated beacon
16596 | XVEL6M5 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16597 | XVEL6M5 | Main | signalling type | Flashing
16598 | XVEL6M5 | Main | component name | XVE
16599 | XVEL6M5 | Main | light source | Integral flash discharge tube, orange
16600 | XVEL6M5 | Main | bulb type | Flash discharge tube
16601 | XVEL6M5 | Main | [Us] rated supply voltage | 230...240 V AC
16602 | XVEL6M5 | Complementary | mounting diameter | 70 mm
16603 | XVEL6M5 | Complementary | flash energy | 1 J
16604 | XVEL6M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16605 | XVEL6M5 | Complementary | marking | CE
16606 | XVEL6M5 | Complementary | short-circuit protection | 0.16 A
16607 | XVEL6M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16608 | XVEL6M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16609 | XVEL6M5 | Complementary | current consumption | < 25 mA
16610 | XVEL6M5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16611 | XVEL6M5 | Complementary | flashing frequency | 1 Hz
16612 | XVEL6M5 | Complementary | CAD overall width | 70 mm
16613 | XVEL6M5 | Complementary | CAD overall height | 129 mm
16614 | XVEL6M5 | Complementary | CAD overall depth | 70 mm
16615 | XVEL6M5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
16616 | XVEL6M5 | Complementary | net weight | 0.27 kg
16617 | XVEL6M5 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
16618 | XVEL6M5 | Environment | product certifications | CCC UL CSA
16619 | XVEL6M5 | Environment | ambient air temperature for storage | -40…70 °C
16620 | XVEL6M5 | Environment | ambient air temperature for operation | -25…55 °C
16621 | XVEL6M5 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16622 | XVEL6M5 | Environment | protective treatment | TC
16623 | XVEL6M5 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16624 | XVEL6M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16625 | XVEL6M5 | Offer Sustainability | Mercury free | Yes
16626 | XVEL6M5 | Offer Sustainability | RoHS exemption information | Yes
16627 | XVEL6M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16628 | XVEL6M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16629 | XVEL6M5 | Contractual warranty | Warranty | 18 months
16630 | XVEL6M6 | Main | range of product | Harmony XVE Optimum
16631 | XVEL6M6 | Main | product or component type | Complete illuminated beacon
16632 | XVEL6M6 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16633 | XVEL6M6 | Main | signalling type | Flashing
16634 | XVEL6M6 | Main | component name | XVE
16635 | XVEL6M6 | Main | light source | Integral flash discharge tube, blue
16636 | XVEL6M6 | Main | bulb type | Flash discharge tube
16637 | XVEL6M6 | Main | [Us] rated supply voltage | 230...240 V AC
16638 | XVEL6M6 | Complementary | mounting diameter | 70 mm
16639 | XVEL6M6 | Complementary | flash energy | 1 J
16640 | XVEL6M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16641 | XVEL6M6 | Complementary | marking | CE
16642 | XVEL6M6 | Complementary | short-circuit protection | 0.16 A
16643 | XVEL6M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16644 | XVEL6M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16645 | XVEL6M6 | Complementary | current consumption | < 25 mA
16646 | XVEL6M6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
16647 | XVEL6M6 | Complementary | flashing frequency | 1 Hz
16648 | XVEL6M6 | Complementary | CAD overall width | 70 mm
16649 | XVEL6M6 | Complementary | CAD overall height | 129 mm
16650 | XVEL6M6 | Complementary | CAD overall depth | 70 mm
16651 | XVEL6M6 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16652 | XVEL6M6 | Complementary | net weight | 0.27 kg
16653 | XVEL6M6 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
16654 | XVEL6M6 | Environment | product certifications | UL CCC CSA
16655 | XVEL6M6 | Environment | ambient air temperature for storage | -40…70 °C
16656 | XVEL6M6 | Environment | ambient air temperature for operation | -25…55 °C
16657 | XVEL6M6 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16658 | XVEL6M6 | Environment | protective treatment | TC
16659 | XVEL6M6 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16660 | XVEL6M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16661 | XVEL6M6 | Offer Sustainability | Mercury free | Yes
16662 | XVEL6M6 | Offer Sustainability | RoHS exemption information | Yes
16663 | XVEL6M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16664 | XVEL6M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16665 | XVEL6M6 | Contractual warranty | Warranty | 18 months
16666 | XVEL6M7 | Main | range of product | Harmony XVE Optimum
16667 | XVEL6M7 | Main | product or component type | Complete illuminated beacon
16668 | XVEL6M7 | Main | beacon or indicator bank unit type | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base
16669 | XVEL6M7 | Main | signalling type | Flashing
16670 | XVEL6M7 | Main | component name | XVE
16671 | XVEL6M7 | Main | light source | Integral flash discharge tube, clear
16672 | XVEL6M7 | Main | bulb type | Flash discharge tube
16673 | XVEL6M7 | Main | [Us] rated supply voltage | 230...240 V AC
16674 | XVEL6M7 | Complementary | mounting diameter | 70 mm
16675 | XVEL6M7 | Complementary | flash energy | 1 J
16676 | XVEL6M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16677 | XVEL6M7 | Complementary | marking | CE
16678 | XVEL6M7 | Complementary | short-circuit protection | 0.16 A
16679 | XVEL6M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16680 | XVEL6M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16681 | XVEL6M7 | Complementary | current consumption | < 25 mA
16682 | XVEL6M7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16683 | XVEL6M7 | Complementary | flashing frequency | 1 Hz
16684 | XVEL6M7 | Complementary | CAD overall width | 70 mm
16685 | XVEL6M7 | Complementary | CAD overall height | 129 mm
16686 | XVEL6M7 | Complementary | CAD overall depth | 70 mm
16687 | XVEL6M7 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
16688 | XVEL6M7 | Complementary | net weight | 0.27 kg
16689 | XVEL6M7 | Environment | standards | EN/IEC 60947-5-1 EN/IEC 60947-1
16690 | XVEL6M7 | Environment | product certifications | CSA UL CCC
16691 | XVEL6M7 | Environment | ambient air temperature for storage | -40…70 °C
16692 | XVEL6M7 | Environment | ambient air temperature for operation | -25…55 °C
16693 | XVEL6M7 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140
16694 | XVEL6M7 | Environment | protective treatment | TC
16695 | XVEL6M7 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529
16696 | XVEL6M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16697 | XVEL6M7 | Offer Sustainability | Mercury free | Yes
16698 | XVEL6M7 | Offer Sustainability | RoHS exemption information | Yes
16699 | XVEL6M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16700 | XVEL6M7 | Contractual warranty | Warranty | 18 months
16701 | XVBL33 | Main | range of product | Harmony XVB Universal
16702 | XVBL33 | Main | product or component type | Complete beacon
16703 | XVBL33 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
16704 | XVBL33 | Main | signalling type | Steady
16705 | XVBL33 | Main | mounting diameter | 70 mm
16706 | XVBL33 | Main | component name | XVBL
16707 | XVBL33 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
16708 | XVBL33 | Main | light source | Bulb not included, green
16709 | XVBL33 | Main | bulb type | Incandescent with BA 15d base Protected LED
16710 | XVBL33 | Main | [Us] rated supply voltage | <= 250 V
16711 | XVBL33 | Main | maximum power dissipation in W | 7 W
16712 | XVBL33 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16713 | XVBL33 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16714 | XVBL33 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16715 | XVBL33 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
16716 | XVBL33 | Complementary | CAD overall width | 70 mm
16717 | XVBL33 | Complementary | CAD overall height | 139 mm
16718 | XVBL33 | Complementary | CAD overall depth | 70 mm
16719 | XVBL33 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
16720 | XVBL33 | Complementary | net weight | 0.26 kg
16721 | XVBL33 | Environment | pollution degree | 2
16722 | XVBL33 | Environment | product certifications | GOST CCC UL 508 CSA C22-2 No 14
16723 | XVBL33 | Environment | standards | EN/IEC 60947-5-1
16724 | XVBL33 | Environment | protective treatment | TC
16725 | XVBL33 | Environment | ambient air temperature for operation | -25…50 °C: LED -25…70 °C: incandescent
16726 | XVBL33 | Environment | ambient air temperature for storage | -40…70 °C
16727 | XVBL33 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
16728 | XVBL33 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
16729 | XVBL33 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
16730 | XVBL33 | Packing Units | Package 1 Weight | 266 g
16731 | XVBL33 | Packing Units | Package 2 Weight | 5.189 kg
16732 | XVBL33 | Offer Sustainability | Sustainable offer status | Green Premium product
16733 | XVBL33 | Offer Sustainability | REACh Regulation | REACh Declaration
16734 | XVBL33 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16735 | XVBL33 | Offer Sustainability | Mercury free | Yes
16736 | XVBL33 | Offer Sustainability | RoHS exemption information | Yes
16737 | XVBL33 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16738 | XVBL33 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
16739 | XVBL33 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16740 | XVBL33 | Contractual warranty | Warranty | 18 months
16741 | XVBL34 | Main | range of product | Harmony XVB Universal
16742 | XVBL34 | Main | product or component type | Complete beacon
16743 | XVBL34 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
16744 | XVBL34 | Main | signalling type | Steady
16745 | XVBL34 | Main | mounting diameter | 70 mm
16746 | XVBL34 | Main | component name | XVBL
16747 | XVBL34 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
16748 | XVBL34 | Main | light source | Bulb not included, red
16749 | XVBL34 | Main | bulb type | Incandescent with BA 15d base Protected LED
16750 | XVBL34 | Main | [Us] rated supply voltage | <= 250 V
16751 | XVBL34 | Main | maximum power dissipation in W | 7 W
16752 | XVBL34 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16753 | XVBL34 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16754 | XVBL34 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16755 | XVBL34 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16756 | XVBL34 | Complementary | CAD overall width | 70 mm
16757 | XVBL34 | Complementary | CAD overall height | 139 mm
16758 | XVBL34 | Complementary | CAD overall depth | 70 mm
16759 | XVBL34 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16760 | XVBL34 | Complementary | net weight | 0.26 kg
16761 | XVBL34 | Environment | pollution degree | 2
16762 | XVBL34 | Environment | product certifications | CCC CSA C22-2 No 14 UL 508 GOST
16763 | XVBL34 | Environment | standards | EN/IEC 60947-5-1
16764 | XVBL34 | Environment | protective treatment | TC
16765 | XVBL34 | Environment | ambient air temperature for operation | -25…50 °C: LED -25…70 °C: incandescent
16766 | XVBL34 | Environment | ambient air temperature for storage | -40…70 °C
16767 | XVBL34 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
16768 | XVBL34 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
16769 | XVBL34 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
16770 | XVBL34 | Packing Units | Package 1 Weight | 261 g
16771 | XVBL34 | Packing Units | Package 2 Weight | 5.166 kg
16772 | XVBL34 | Offer Sustainability | Sustainable offer status | Green Premium product
16773 | XVBL34 | Offer Sustainability | REACh Regulation | REACh Declaration
16774 | XVBL34 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16775 | XVBL34 | Offer Sustainability | Mercury free | Yes
16776 | XVBL34 | Offer Sustainability | RoHS exemption information | Yes
16777 | XVBL34 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16778 | XVBL34 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
16779 | XVBL34 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16780 | XVBL34 | Contractual warranty | Warranty | 18 months
16781 | XVBL35 | Main | range of product | Harmony XVB Universal
16782 | XVBL35 | Main | product or component type | Complete beacon
16783 | XVBL35 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
16784 | XVBL35 | Main | signalling type | Steady
16785 | XVBL35 | Main | mounting diameter | 70 mm
16786 | XVBL35 | Main | component name | XVBL
16787 | XVBL35 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
16788 | XVBL35 | Main | light source | Bulb not included, orange
16789 | XVBL35 | Main | bulb type | Incandescent with BA 15d base Protected LED
16790 | XVBL35 | Main | [Us] rated supply voltage | <= 250 V
16791 | XVBL35 | Main | maximum power dissipation in W | 7 W
16792 | XVBL35 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16793 | XVBL35 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16794 | XVBL35 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16795 | XVBL35 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
16796 | XVBL35 | Complementary | CAD overall width | 70 mm
16797 | XVBL35 | Complementary | CAD overall height | 139 mm
16798 | XVBL35 | Complementary | CAD overall depth | 70 mm
16799 | XVBL35 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16800 | XVBL35 | Complementary | net weight | 0.26 kg
16801 | XVBL35 | Environment | pollution degree | 2
16802 | XVBL35 | Environment | product certifications | CCC GOST UL 508 CSA C22-2 No 14
16803 | XVBL35 | Environment | standards | EN/IEC 60947-5-1
16804 | XVBL35 | Environment | protective treatment | TC
16805 | XVBL35 | Environment | ambient air temperature for operation | -25…50 °C: LED -25…70 °C: incandescent
16806 | XVBL35 | Environment | ambient air temperature for storage | -40…70 °C
16807 | XVBL35 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
16808 | XVBL35 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
16809 | XVBL35 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
16810 | XVBL35 | Packing Units | Package 1 Weight | 264 g
16811 | XVBL35 | Offer Sustainability | Sustainable offer status | Green Premium product
16812 | XVBL35 | Offer Sustainability | REACh Regulation | REACh Declaration
16813 | XVBL35 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16814 | XVBL35 | Offer Sustainability | Mercury free | Yes
16815 | XVBL35 | Offer Sustainability | RoHS exemption information | Yes
16816 | XVBL35 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16817 | XVBL35 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
16818 | XVBL35 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16819 | XVBL35 | Contractual warranty | Warranty | 18 months
16820 | XVBL36 | Main | range of product | Harmony XVB Universal
16821 | XVBL36 | Main | product or component type | Complete beacon
16822 | XVBL36 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
16823 | XVBL36 | Main | signalling type | Steady
16824 | XVBL36 | Main | mounting diameter | 70 mm
16825 | XVBL36 | Main | component name | XVBL
16826 | XVBL36 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
16827 | XVBL36 | Main | light source | Bulb not included, blue
16828 | XVBL36 | Main | bulb type | Incandescent with BA 15d base Protected LED
16829 | XVBL36 | Main | [Us] rated supply voltage | <= 250 V
16830 | XVBL36 | Main | maximum power dissipation in W | 7 W
16831 | XVBL36 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16832 | XVBL36 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16833 | XVBL36 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16834 | XVBL36 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16835 | XVBL36 | Complementary | CAD overall width | 70 mm
16836 | XVBL36 | Complementary | CAD overall height | 139 mm
16837 | XVBL36 | Complementary | CAD overall depth | 70 mm
16838 | XVBL36 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16839 | XVBL36 | Complementary | net weight | 0.26 kg
16840 | XVBL36 | Environment | pollution degree | 2
16841 | XVBL36 | Environment | product certifications | CSA C22-2 No 14 GOST CCC UL 508
16842 | XVBL36 | Environment | standards | EN/IEC 60947-5-1
16843 | XVBL36 | Environment | protective treatment | TC
16844 | XVBL36 | Environment | ambient air temperature for operation | -25…50 °C: LED -25…70 °C: incandescent
16845 | XVBL36 | Environment | ambient air temperature for storage | -40…70 °C
16846 | XVBL36 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
16847 | XVBL36 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
16848 | XVBL36 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
16849 | XVBL36 | Packing Units | Package 1 Weight | 266 g
16850 | XVBL36 | Packing Units | Package 2 Weight | 5.201 kg
16851 | XVBL36 | Offer Sustainability | Sustainable offer status | Green Premium product
16852 | XVBL36 | Offer Sustainability | REACh Regulation | REACh Declaration
16853 | XVBL36 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16854 | XVBL36 | Offer Sustainability | Mercury free | Yes
16855 | XVBL36 | Offer Sustainability | RoHS exemption information | Yes
16856 | XVBL36 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16857 | XVBL36 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
16858 | XVBL36 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16859 | XVBL36 | Contractual warranty | Warranty | 18 months
16860 | XVBL37 | Main | range of product | Harmony XVB Universal
16861 | XVBL37 | Main | product or component type | Complete beacon
16862 | XVBL37 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
16863 | XVBL37 | Main | signalling type | Steady
16864 | XVBL37 | Main | mounting diameter | 70 mm
16865 | XVBL37 | Main | component name | XVBL
16866 | XVBL37 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
16867 | XVBL37 | Main | light source | Bulb not included, clear
16868 | XVBL37 | Main | bulb type | Incandescent with BA 15d base Protected LED
16869 | XVBL37 | Main | [Us] rated supply voltage | <= 250 V
16870 | XVBL37 | Main | maximum power dissipation in W | 7 W
16871 | XVBL37 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16872 | XVBL37 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16873 | XVBL37 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16874 | XVBL37 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
16875 | XVBL37 | Complementary | CAD overall width | 70 mm
16876 | XVBL37 | Complementary | CAD overall height | 139 mm
16877 | XVBL37 | Complementary | CAD overall depth | 70 mm
16878 | XVBL37 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
16879 | XVBL37 | Complementary | net weight | 0.26 kg
16880 | XVBL37 | Environment | pollution degree | 2
16881 | XVBL37 | Environment | product certifications | CCC CSA C22-2 No 14 UL 508 GOST
16882 | XVBL37 | Environment | standards | EN/IEC 60947-5-1
16883 | XVBL37 | Environment | protective treatment | TC
16884 | XVBL37 | Environment | ambient air temperature for operation | -25…50 °C: LED -25…70 °C: incandescent
16885 | XVBL37 | Environment | ambient air temperature for storage | -40…70 °C
16886 | XVBL37 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
16887 | XVBL37 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
16888 | XVBL37 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
16889 | XVBL37 | Packing Units | Package 1 Weight | 266 g
16890 | XVBL37 | Packing Units | Package 2 Weight | 5.195 kg
16891 | XVBL37 | Offer Sustainability | Sustainable offer status | Green Premium product
16892 | XVBL37 | Offer Sustainability | REACh Regulation | REACh Declaration
16893 | XVBL37 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16894 | XVBL37 | Offer Sustainability | Mercury free | Yes
16895 | XVBL37 | Offer Sustainability | RoHS exemption information | Yes
16896 | XVBL37 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16897 | XVBL37 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
16898 | XVBL37 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16899 | XVBL37 | Contractual warranty | Warranty | 18 months
16900 | XVBL38 | Main | range of product | Harmony XVB Universal
16901 | XVBL38 | Main | product or component type | Complete beacon
16902 | XVBL38 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
16903 | XVBL38 | Main | signalling type | Steady
16904 | XVBL38 | Main | mounting diameter | 70 mm
16905 | XVBL38 | Main | component name | XVBL
16906 | XVBL38 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
16907 | XVBL38 | Main | light source | Bulb not included, yellow
16908 | XVBL38 | Main | bulb type | Incandescent with BA 15d base Protected LED
16909 | XVBL38 | Main | [Us] rated supply voltage | <= 250 V
16910 | XVBL38 | Main | maximum power dissipation in W | 7 W
16911 | XVBL38 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16912 | XVBL38 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16913 | XVBL38 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16914 | XVBL38 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16915 | XVBL38 | Complementary | CAD overall width | 70 mm
16916 | XVBL38 | Complementary | CAD overall height | 139 mm
16917 | XVBL38 | Complementary | CAD overall depth | 70 mm
16918 | XVBL38 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
16919 | XVBL38 | Complementary | net weight | 0.26 kg
16920 | XVBL38 | Environment | pollution degree | 2
16921 | XVBL38 | Environment | product certifications | UL 508 CCC GOST CSA C22-2 No 14
16922 | XVBL38 | Environment | standards | EN/IEC 60947-5-1
16923 | XVBL38 | Environment | protective treatment | TC
16924 | XVBL38 | Environment | ambient air temperature for operation | -25…50 °C: LED -25…70 °C: incandescent
16925 | XVBL38 | Environment | ambient air temperature for storage | -40…70 °C
16926 | XVBL38 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
16927 | XVBL38 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
16928 | XVBL38 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
16929 | XVBL38 | Packing Units | Package 1 Weight | 261 g
16930 | XVBL38 | Packing Units | Package 2 Weight | 5.171 kg
16931 | XVBL38 | Offer Sustainability | Sustainable offer status | Green Premium product
16932 | XVBL38 | Offer Sustainability | REACh Regulation | REACh Declaration
16933 | XVBL38 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16934 | XVBL38 | Offer Sustainability | Mercury free | Yes
16935 | XVBL38 | Offer Sustainability | RoHS exemption information | Yes
16936 | XVBL38 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16937 | XVBL38 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
16938 | XVBL38 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16939 | XVBL38 | Contractual warranty | Warranty | 18 months
16940 | XVBL4B3 | Main | range of product | Harmony XVB Universal
16941 | XVBL4B3 | Main | product or component type | Complete beacon
16942 | XVBL4B3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
16943 | XVBL4B3 | Main | signalling type | Flashing
16944 | XVBL4B3 | Main | mounting diameter | 70 mm
16945 | XVBL4B3 | Main | component name | XVBL
16946 | XVBL4B3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
16947 | XVBL4B3 | Main | light source | Bulb not included, green
16948 | XVBL4B3 | Main | bulb type | Incandescent Incandescent with BA 15d base Protected LED
16949 | XVBL4B3 | Main | [Us] rated supply voltage | 24 V AC 24...48 V DC
16950 | XVBL4B3 | Main | maximum power dissipation in W | 7 W
16951 | XVBL4B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16952 | XVBL4B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16953 | XVBL4B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16954 | XVBL4B3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
16955 | XVBL4B3 | Complementary | flashing frequency | 1 Hz
16956 | XVBL4B3 | Complementary | CAD overall width | 70 mm
16957 | XVBL4B3 | Complementary | CAD overall height | 139 mm
16958 | XVBL4B3 | Complementary | CAD overall depth | 70 mm
16959 | XVBL4B3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
16960 | XVBL4B3 | Complementary | net weight | 0.28 kg
16961 | XVBL4B3 | Environment | pollution degree | 2
16962 | XVBL4B3 | Environment | product certifications | UL 508 CCC GOST CSA C22-2 No 14
16963 | XVBL4B3 | Environment | standards | EN/IEC 60947-5-1
16964 | XVBL4B3 | Environment | protective treatment | TC
16965 | XVBL4B3 | Environment | ambient air temperature for storage | -40…70 °C
16966 | XVBL4B3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
16967 | XVBL4B3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
16968 | XVBL4B3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
16969 | XVBL4B3 | Packing Units | Package 1 Weight | 280 g
16970 | XVBL4B3 | Offer Sustainability | Sustainable offer status | Green Premium product
16971 | XVBL4B3 | Offer Sustainability | REACh Regulation | REACh Declaration
16972 | XVBL4B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
16973 | XVBL4B3 | Offer Sustainability | Mercury free | Yes
16974 | XVBL4B3 | Offer Sustainability | RoHS exemption information | Yes
16975 | XVBL4B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
16976 | XVBL4B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
16977 | XVBL4B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
16978 | XVBL4B3 | Contractual warranty | Warranty | 18 months
16979 | XVBL4B4 | Main | range of product | Harmony XVB Universal
16980 | XVBL4B4 | Main | product or component type | Complete beacon
16981 | XVBL4B4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
16982 | XVBL4B4 | Main | signalling type | Flashing
16983 | XVBL4B4 | Main | mounting diameter | 70 mm
16984 | XVBL4B4 | Main | component name | XVBL
16985 | XVBL4B4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
16986 | XVBL4B4 | Main | light source | Bulb not included, red
16987 | XVBL4B4 | Main | bulb type | Incandescent Incandescent with BA 15d base Protected LED
16988 | XVBL4B4 | Main | [Us] rated supply voltage | 24 V AC 24...48 V DC
16989 | XVBL4B4 | Main | maximum power dissipation in W | 7 W
16990 | XVBL4B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
16991 | XVBL4B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
16992 | XVBL4B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
16993 | XVBL4B4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
16994 | XVBL4B4 | Complementary | flashing frequency | 1 Hz
16995 | XVBL4B4 | Complementary | CAD overall width | 70 mm
16996 | XVBL4B4 | Complementary | CAD overall height | 139 mm
16997 | XVBL4B4 | Complementary | CAD overall depth | 70 mm
16998 | XVBL4B4 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
16999 | XVBL4B4 | Complementary | net weight | 0.28 kg
17000 | XVBL4B4 | Environment | pollution degree | 2
17001 | XVBL4B4 | Environment | product certifications | UL 508 CSA C22-2 No 14 GOST CCC
17002 | XVBL4B4 | Environment | standards | EN/IEC 60947-5-1
17003 | XVBL4B4 | Environment | protective treatment | TC
17004 | XVBL4B4 | Environment | ambient air temperature for storage | -40…70 °C
17005 | XVBL4B4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17006 | XVBL4B4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17007 | XVBL4B4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17008 | XVBL4B4 | Packing Units | Package 1 Weight | 275 g
17009 | XVBL4B4 | Packing Units | Package 2 Weight | 5.421 kg
17010 | XVBL4B4 | Offer Sustainability | Sustainable offer status | Green Premium product
17011 | XVBL4B4 | Offer Sustainability | REACh Regulation | REACh Declaration
17012 | XVBL4B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17013 | XVBL4B4 | Offer Sustainability | Mercury free | Yes
17014 | XVBL4B4 | Offer Sustainability | RoHS exemption information | Yes
17015 | XVBL4B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17016 | XVBL4B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17017 | XVBL4B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17018 | XVBL4B4 | Contractual warranty | Warranty | 18 months
17019 | XVBL4B5 | Main | range of product | Harmony XVB Universal
17020 | XVBL4B5 | Main | product or component type | Complete beacon
17021 | XVBL4B5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17022 | XVBL4B5 | Main | signalling type | Flashing
17023 | XVBL4B5 | Main | mounting diameter | 70 mm
17024 | XVBL4B5 | Main | component name | XVBL
17025 | XVBL4B5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17026 | XVBL4B5 | Main | light source | Bulb not included, orange
17027 | XVBL4B5 | Main | bulb type | Incandescent Incandescent with BA 15d base Protected LED
17028 | XVBL4B5 | Main | [Us] rated supply voltage | 24 V AC 24...48 V DC
17029 | XVBL4B5 | Main | maximum power dissipation in W | 7 W
17030 | XVBL4B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17031 | XVBL4B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17032 | XVBL4B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17033 | XVBL4B5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
17034 | XVBL4B5 | Complementary | flashing frequency | 1 Hz
17035 | XVBL4B5 | Complementary | CAD overall width | 70 mm
17036 | XVBL4B5 | Complementary | CAD overall height | 139 mm
17037 | XVBL4B5 | Complementary | CAD overall depth | 70 mm
17038 | XVBL4B5 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
17039 | XVBL4B5 | Complementary | net weight | 0.28 kg
17040 | XVBL4B5 | Environment | pollution degree | 2
17041 | XVBL4B5 | Environment | product certifications | CSA C22-2 No 14 GOST CCC UL 508
17042 | XVBL4B5 | Environment | standards | EN/IEC 60947-5-1
17043 | XVBL4B5 | Environment | protective treatment | TC
17044 | XVBL4B5 | Environment | ambient air temperature for storage | -40…70 °C
17045 | XVBL4B5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17046 | XVBL4B5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17047 | XVBL4B5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17048 | XVBL4B5 | Packing Units | Package 1 Weight | 280 g
17049 | XVBL4B5 | Packing Units | Package 2 Weight | 5.419 kg
17050 | XVBL4B5 | Offer Sustainability | Sustainable offer status | Green Premium product
17051 | XVBL4B5 | Offer Sustainability | REACh Regulation | REACh Declaration
17052 | XVBL4B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17053 | XVBL4B5 | Offer Sustainability | Mercury free | Yes
17054 | XVBL4B5 | Offer Sustainability | RoHS exemption information | Yes
17055 | XVBL4B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17056 | XVBL4B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17057 | XVBL4B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17058 | XVBL4B5 | Contractual warranty | Warranty | 18 months
17059 | XVBL4B6 | Main | range of product | Harmony XVB Universal
17060 | XVBL4B6 | Main | product or component type | Complete beacon
17061 | XVBL4B6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17062 | XVBL4B6 | Main | signalling type | Flashing
17063 | XVBL4B6 | Main | mounting diameter | 70 mm
17064 | XVBL4B6 | Main | component name | XVBL
17065 | XVBL4B6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17066 | XVBL4B6 | Main | light source | Bulb not included, blue
17067 | XVBL4B6 | Main | bulb type | Incandescent Incandescent with BA 15d base Protected LED
17068 | XVBL4B6 | Main | [Us] rated supply voltage | 24 V AC 24...48 V DC
17069 | XVBL4B6 | Main | maximum power dissipation in W | 7 W
17070 | XVBL4B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17071 | XVBL4B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17072 | XVBL4B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17073 | XVBL4B6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
17074 | XVBL4B6 | Complementary | flashing frequency | 1 Hz
17075 | XVBL4B6 | Complementary | CAD overall width | 70 mm
17076 | XVBL4B6 | Complementary | CAD overall height | 139 mm
17077 | XVBL4B6 | Complementary | CAD overall depth | 70 mm
17078 | XVBL4B6 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
17079 | XVBL4B6 | Complementary | net weight | 0.28 kg
17080 | XVBL4B6 | Environment | pollution degree | 2
17081 | XVBL4B6 | Environment | product certifications | CCC GOST CSA C22-2 No 14 UL 508
17082 | XVBL4B6 | Environment | standards | EN/IEC 60947-5-1
17083 | XVBL4B6 | Environment | protective treatment | TC
17084 | XVBL4B6 | Environment | ambient air temperature for storage | -40…70 °C
17085 | XVBL4B6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17086 | XVBL4B6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17087 | XVBL4B6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17088 | XVBL4B6 | Packing Units | Package 1 Weight | 280 g
17089 | XVBL4B6 | Offer Sustainability | Sustainable offer status | Green Premium product
17090 | XVBL4B6 | Offer Sustainability | REACh Regulation | REACh Declaration
17091 | XVBL4B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17092 | XVBL4B6 | Offer Sustainability | Mercury free | Yes
17093 | XVBL4B6 | Offer Sustainability | RoHS exemption information | Yes
17094 | XVBL4B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17095 | XVBL4B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17096 | XVBL4B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17097 | XVBL4B6 | Contractual warranty | Warranty | 18 months
17098 | XVBL4B7 | Main | range of product | Harmony XVB Universal
17099 | XVBL4B7 | Main | product or component type | Complete beacon
17100 | XVBL4B7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17101 | XVBL4B7 | Main | signalling type | Flashing
17102 | XVBL4B7 | Main | mounting diameter | 70 mm
17103 | XVBL4B7 | Main | component name | XVBL
17104 | XVBL4B7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17105 | XVBL4B7 | Main | light source | Bulb not included, clear
17106 | XVBL4B7 | Main | bulb type | Incandescent Incandescent with BA 15d base Protected LED
17107 | XVBL4B7 | Main | [Us] rated supply voltage | 24 V AC 24...48 V DC
17108 | XVBL4B7 | Main | maximum power dissipation in W | 7 W
17109 | XVBL4B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17110 | XVBL4B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17111 | XVBL4B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17112 | XVBL4B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
17113 | XVBL4B7 | Complementary | flashing frequency | 1 Hz
17114 | XVBL4B7 | Complementary | CAD overall width | 70 mm
17115 | XVBL4B7 | Complementary | CAD overall height | 139 mm
17116 | XVBL4B7 | Complementary | CAD overall depth | 70 mm
17117 | XVBL4B7 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
17118 | XVBL4B7 | Complementary | net weight | 0.28 kg
17119 | XVBL4B7 | Environment | pollution degree | 2
17120 | XVBL4B7 | Environment | product certifications | CCC GOST CSA C22-2 No 14 UL 508
17121 | XVBL4B7 | Environment | standards | EN/IEC 60947-5-1
17122 | XVBL4B7 | Environment | protective treatment | TC
17123 | XVBL4B7 | Environment | ambient air temperature for storage | -40…70 °C
17124 | XVBL4B7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17125 | XVBL4B7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17126 | XVBL4B7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17127 | XVBL4B7 | Packing Units | Package 1 Weight | 280 g
17128 | XVBL4B7 | Offer Sustainability | Sustainable offer status | Green Premium product
17129 | XVBL4B7 | Offer Sustainability | REACh Regulation | REACh Declaration
17130 | XVBL4B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17131 | XVBL4B7 | Offer Sustainability | Mercury free | Yes
17132 | XVBL4B7 | Offer Sustainability | RoHS exemption information | Yes
17133 | XVBL4B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17134 | XVBL4B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17135 | XVBL4B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17136 | XVBL4B7 | Contractual warranty | Warranty | 18 months
17137 | XVBL4B8 | Main | range of product | Harmony XVB Universal
17138 | XVBL4B8 | Main | product or component type | Complete beacon
17139 | XVBL4B8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17140 | XVBL4B8 | Main | signalling type | Flashing
17141 | XVBL4B8 | Main | mounting diameter | 70 mm
17142 | XVBL4B8 | Main | component name | XVBL
17143 | XVBL4B8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17144 | XVBL4B8 | Main | light source | Bulb not included, yellow
17145 | XVBL4B8 | Main | bulb type | Incandescent Incandescent with BA 15d base Protected LED
17146 | XVBL4B8 | Main | [Us] rated supply voltage | 24 V AC 24...48 V DC
17147 | XVBL4B8 | Main | maximum power dissipation in W | 7 W
17148 | XVBL4B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17149 | XVBL4B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17150 | XVBL4B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17151 | XVBL4B8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
17152 | XVBL4B8 | Complementary | flashing frequency | 1 Hz
17153 | XVBL4B8 | Complementary | CAD overall width | 70 mm
17154 | XVBL4B8 | Complementary | CAD overall height | 139 mm
17155 | XVBL4B8 | Complementary | CAD overall depth | 70 mm
17156 | XVBL4B8 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
17157 | XVBL4B8 | Complementary | net weight | 0.28 kg
17158 | XVBL4B8 | Environment | pollution degree | 2
17159 | XVBL4B8 | Environment | product certifications | CCC UL 508 GOST CSA C22-2 No 14
17160 | XVBL4B8 | Environment | standards | EN/IEC 60947-5-1
17161 | XVBL4B8 | Environment | protective treatment | TC
17162 | XVBL4B8 | Environment | ambient air temperature for storage | -40…70 °C
17163 | XVBL4B8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17164 | XVBL4B8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17165 | XVBL4B8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17166 | XVBL4B8 | Packing Units | Package 1 Weight | 274 g
17167 | XVBL4B8 | Packing Units | Package 2 Weight | 5.4 kg
17168 | XVBL4B8 | Offer Sustainability | Sustainable offer status | Green Premium product
17169 | XVBL4B8 | Offer Sustainability | REACh Regulation | REACh Declaration
17170 | XVBL4B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17171 | XVBL4B8 | Offer Sustainability | Mercury free | Yes
17172 | XVBL4B8 | Offer Sustainability | RoHS exemption information | Yes
17173 | XVBL4B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17174 | XVBL4B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17175 | XVBL4B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17176 | XVBL4B8 | Contractual warranty | Warranty | 18 months
17177 | XVBL4M3 | Main | range of product | Harmony XVB Universal
17178 | XVBL4M3 | Main | product or component type | Complete beacon
17179 | XVBL4M3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17180 | XVBL4M3 | Main | signalling type | Flashing
17181 | XVBL4M3 | Main | mounting diameter | 70 mm
17182 | XVBL4M3 | Main | component name | XVBL
17183 | XVBL4M3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17184 | XVBL4M3 | Main | light source | Bulb not included, green
17185 | XVBL4M3 | Main | bulb type | Incandescent with BA 15d base Protected LED
17186 | XVBL4M3 | Main | [Us] rated supply voltage | 48...230 V AC
17187 | XVBL4M3 | Main | maximum power dissipation in W | 7 W
17188 | XVBL4M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17189 | XVBL4M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17190 | XVBL4M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17191 | XVBL4M3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
17192 | XVBL4M3 | Complementary | flashing frequency | 1 Hz
17193 | XVBL4M3 | Complementary | CAD overall width | 70 mm
17194 | XVBL4M3 | Complementary | CAD overall height | 139 mm
17195 | XVBL4M3 | Complementary | CAD overall depth | 70 mm
17196 | XVBL4M3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
17197 | XVBL4M3 | Complementary | net weight | 0.28 kg
17198 | XVBL4M3 | Environment | pollution degree | 2
17199 | XVBL4M3 | Environment | product certifications | CCC UL 508 CSA C22-2 No 14 GOST
17200 | XVBL4M3 | Environment | standards | EN/IEC 60947-5-1
17201 | XVBL4M3 | Environment | protective treatment | TC
17202 | XVBL4M3 | Environment | ambient air temperature for storage | -40…70 °C
17203 | XVBL4M3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17204 | XVBL4M3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17205 | XVBL4M3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17206 | XVBL4M3 | Packing Units | Package 1 Weight | 280 g
17207 | XVBL4M3 | Offer Sustainability | Sustainable offer status | Green Premium product
17208 | XVBL4M3 | Offer Sustainability | REACh Regulation | REACh Declaration
17209 | XVBL4M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17210 | XVBL4M3 | Offer Sustainability | Mercury free | Yes
17211 | XVBL4M3 | Offer Sustainability | RoHS exemption information | Yes
17212 | XVBL4M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17213 | XVBL4M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17214 | XVBL4M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17215 | XVBL4M3 | Contractual warranty | Warranty | 18 months
17216 | XVBL4M4 | Main | range of product | Harmony XVB Universal
17217 | XVBL4M4 | Main | product or component type | Complete beacon
17218 | XVBL4M4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17219 | XVBL4M4 | Main | signalling type | Flashing
17220 | XVBL4M4 | Main | mounting diameter | 70 mm
17221 | XVBL4M4 | Main | component name | XVBL
17222 | XVBL4M4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17223 | XVBL4M4 | Main | light source | Bulb not included, red
17224 | XVBL4M4 | Main | bulb type | Incandescent with BA 15d base Protected LED
17225 | XVBL4M4 | Main | [Us] rated supply voltage | 48...230 V AC
17226 | XVBL4M4 | Main | maximum power dissipation in W | 7 W
17227 | XVBL4M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17228 | XVBL4M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17229 | XVBL4M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17230 | XVBL4M4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
17231 | XVBL4M4 | Complementary | flashing frequency | 1 Hz
17232 | XVBL4M4 | Complementary | CAD overall width | 70 mm
17233 | XVBL4M4 | Complementary | CAD overall height | 139 mm
17234 | XVBL4M4 | Complementary | CAD overall depth | 70 mm
17235 | XVBL4M4 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
17236 | XVBL4M4 | Complementary | net weight | 0.28 kg
17237 | XVBL4M4 | Environment | pollution degree | 2
17238 | XVBL4M4 | Environment | product certifications | UL 508 GOST CCC CSA C22-2 No 14
17239 | XVBL4M4 | Environment | standards | EN/IEC 60947-5-1
17240 | XVBL4M4 | Environment | protective treatment | TC
17241 | XVBL4M4 | Environment | ambient air temperature for storage | -40…70 °C
17242 | XVBL4M4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17243 | XVBL4M4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17244 | XVBL4M4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17245 | XVBL4M4 | Packing Units | Package 1 Weight | 280 g
17246 | XVBL4M4 | Packing Units | Package 2 Weight | 5.383 kg
17247 | XVBL4M4 | Offer Sustainability | Sustainable offer status | Green Premium product
17248 | XVBL4M4 | Offer Sustainability | REACh Regulation | REACh Declaration
17249 | XVBL4M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17250 | XVBL4M4 | Offer Sustainability | Mercury free | Yes
17251 | XVBL4M4 | Offer Sustainability | RoHS exemption information | Yes
17252 | XVBL4M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17253 | XVBL4M4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17254 | XVBL4M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17255 | XVBL4M4 | Contractual warranty | Warranty | 18 months
17256 | XVBL4M5 | Main | range of product | Harmony XVB Universal
17257 | XVBL4M5 | Main | product or component type | Complete beacon
17258 | XVBL4M5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17259 | XVBL4M5 | Main | signalling type | Flashing
17260 | XVBL4M5 | Main | mounting diameter | 70 mm
17261 | XVBL4M5 | Main | component name | XVBL
17262 | XVBL4M5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17263 | XVBL4M5 | Main | light source | Bulb not included, orange
17264 | XVBL4M5 | Main | bulb type | Incandescent with BA 15d base Protected LED
17265 | XVBL4M5 | Main | [Us] rated supply voltage | 48...230 V AC
17266 | XVBL4M5 | Main | maximum power dissipation in W | 7 W
17267 | XVBL4M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17268 | XVBL4M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17269 | XVBL4M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17270 | XVBL4M5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
17271 | XVBL4M5 | Complementary | flashing frequency | 1 Hz
17272 | XVBL4M5 | Complementary | CAD overall width | 70 mm
17273 | XVBL4M5 | Complementary | CAD overall height | 139 mm
17274 | XVBL4M5 | Complementary | CAD overall depth | 70 mm
17275 | XVBL4M5 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
17276 | XVBL4M5 | Complementary | net weight | 0.28 kg
17277 | XVBL4M5 | Environment | pollution degree | 2
17278 | XVBL4M5 | Environment | product certifications | CSA C22-2 No 14 UL 508 CCC GOST
17279 | XVBL4M5 | Environment | standards | EN/IEC 60947-5-1
17280 | XVBL4M5 | Environment | protective treatment | TC
17281 | XVBL4M5 | Environment | ambient air temperature for storage | -40…70 °C
17282 | XVBL4M5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17283 | XVBL4M5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17284 | XVBL4M5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17285 | XVBL4M5 | Packing Units | Package 1 Weight | 275 g
17286 | XVBL4M5 | Packing Units | Package 2 Weight | 5.439 kg
17287 | XVBL4M5 | Offer Sustainability | Sustainable offer status | Green Premium product
17288 | XVBL4M5 | Offer Sustainability | REACh Regulation | REACh Declaration
17289 | XVBL4M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17290 | XVBL4M5 | Offer Sustainability | Mercury free | Yes
17291 | XVBL4M5 | Offer Sustainability | RoHS exemption information | Yes
17292 | XVBL4M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17293 | XVBL4M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17294 | XVBL4M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17295 | XVBL4M5 | Contractual warranty | Warranty | 18 months
17296 | XVBL4M6 | Main | range of product | Harmony XVB Universal
17297 | XVBL4M6 | Main | product or component type | Complete beacon
17298 | XVBL4M6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17299 | XVBL4M6 | Main | signalling type | Flashing
17300 | XVBL4M6 | Main | mounting diameter | 70 mm
17301 | XVBL4M6 | Main | component name | XVBL
17302 | XVBL4M6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17303 | XVBL4M6 | Main | light source | Bulb not included, blue
17304 | XVBL4M6 | Main | bulb type | Incandescent with BA 15d base Protected LED
17305 | XVBL4M6 | Main | [Us] rated supply voltage | 48...230 V AC
17306 | XVBL4M6 | Main | maximum power dissipation in W | 7 W
17307 | XVBL4M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17308 | XVBL4M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17309 | XVBL4M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17310 | XVBL4M6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
17311 | XVBL4M6 | Complementary | flashing frequency | 1 Hz
17312 | XVBL4M6 | Complementary | CAD overall width | 70 mm
17313 | XVBL4M6 | Complementary | CAD overall height | 139 mm
17314 | XVBL4M6 | Complementary | CAD overall depth | 70 mm
17315 | XVBL4M6 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
17316 | XVBL4M6 | Complementary | net weight | 0.28 kg
17317 | XVBL4M6 | Environment | pollution degree | 2
17318 | XVBL4M6 | Environment | product certifications | CSA C22-2 No 14 CCC GOST UL 508
17319 | XVBL4M6 | Environment | standards | EN/IEC 60947-5-1
17320 | XVBL4M6 | Environment | protective treatment | TC
17321 | XVBL4M6 | Environment | ambient air temperature for storage | -40…70 °C
17322 | XVBL4M6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17323 | XVBL4M6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17324 | XVBL4M6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17325 | XVBL4M6 | Packing Units | Package 1 Weight | 280 g
17326 | XVBL4M6 | Offer Sustainability | Sustainable offer status | Green Premium product
17327 | XVBL4M6 | Offer Sustainability | REACh Regulation | REACh Declaration
17328 | XVBL4M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17329 | XVBL4M6 | Offer Sustainability | Mercury free | Yes
17330 | XVBL4M6 | Offer Sustainability | RoHS exemption information | Yes
17331 | XVBL4M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17332 | XVBL4M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17333 | XVBL4M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17334 | XVBL4M6 | Contractual warranty | Warranty | 18 months
17335 | XVBL4M7 | Main | range of product | Harmony XVB Universal
17336 | XVBL4M7 | Main | product or component type | Complete beacon
17337 | XVBL4M7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17338 | XVBL4M7 | Main | signalling type | Flashing
17339 | XVBL4M7 | Main | mounting diameter | 70 mm
17340 | XVBL4M7 | Main | component name | XVBL
17341 | XVBL4M7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17342 | XVBL4M7 | Main | light source | Bulb not included, clear
17343 | XVBL4M7 | Main | bulb type | Incandescent with BA 15d base Protected LED
17344 | XVBL4M7 | Main | [Us] rated supply voltage | 48...230 V AC
17345 | XVBL4M7 | Main | maximum power dissipation in W | 7 W
17346 | XVBL4M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17347 | XVBL4M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17348 | XVBL4M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17349 | XVBL4M7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
17350 | XVBL4M7 | Complementary | flashing frequency | 1 Hz
17351 | XVBL4M7 | Complementary | CAD overall width | 70 mm
17352 | XVBL4M7 | Complementary | CAD overall height | 139 mm
17353 | XVBL4M7 | Complementary | CAD overall depth | 70 mm
17354 | XVBL4M7 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
17355 | XVBL4M7 | Complementary | net weight | 0.28 kg
17356 | XVBL4M7 | Environment | pollution degree | 2
17357 | XVBL4M7 | Environment | product certifications | CCC GOST CSA C22-2 No 14 UL 508
17358 | XVBL4M7 | Environment | standards | EN/IEC 60947-5-1
17359 | XVBL4M7 | Environment | protective treatment | TC
17360 | XVBL4M7 | Environment | ambient air temperature for storage | -40…70 °C
17361 | XVBL4M7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17362 | XVBL4M7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17363 | XVBL4M7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17364 | XVBL4M7 | Packing Units | Package 1 Weight | 280 g
17365 | XVBL4M7 | Offer Sustainability | Sustainable offer status | Green Premium product
17366 | XVBL4M7 | Offer Sustainability | REACh Regulation | REACh Declaration
17367 | XVBL4M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17368 | XVBL4M7 | Offer Sustainability | Mercury free | Yes
17369 | XVBL4M7 | Offer Sustainability | RoHS exemption information | Yes
17370 | XVBL4M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17371 | XVBL4M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17372 | XVBL4M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17373 | XVBL4M7 | Contractual warranty | Warranty | 18 months
17374 | XVBL4M8 | Main | range of product | Harmony XVB Universal
17375 | XVBL4M8 | Main | product or component type | Complete beacon
17376 | XVBL4M8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17377 | XVBL4M8 | Main | signalling type | Flashing
17378 | XVBL4M8 | Main | mounting diameter | 70 mm
17379 | XVBL4M8 | Main | component name | XVBL
17380 | XVBL4M8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17381 | XVBL4M8 | Main | light source | Bulb not included, yellow
17382 | XVBL4M8 | Main | bulb type | Incandescent with BA 15d base Protected LED
17383 | XVBL4M8 | Main | [Us] rated supply voltage | 48...230 V AC
17384 | XVBL4M8 | Main | maximum power dissipation in W | 7 W
17385 | XVBL4M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17386 | XVBL4M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17387 | XVBL4M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17388 | XVBL4M8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
17389 | XVBL4M8 | Complementary | flashing frequency | 1 Hz
17390 | XVBL4M8 | Complementary | CAD overall width | 70 mm
17391 | XVBL4M8 | Complementary | CAD overall height | 139 mm
17392 | XVBL4M8 | Complementary | CAD overall depth | 70 mm
17393 | XVBL4M8 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
17394 | XVBL4M8 | Complementary | net weight | 0.28 kg
17395 | XVBL4M8 | Environment | pollution degree | 2
17396 | XVBL4M8 | Environment | product certifications | UL 508 GOST CSA C22-2 No 14 CCC
17397 | XVBL4M8 | Environment | standards | EN/IEC 60947-5-1
17398 | XVBL4M8 | Environment | protective treatment | TC
17399 | XVBL4M8 | Environment | ambient air temperature for storage | -40…70 °C
17400 | XVBL4M8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17401 | XVBL4M8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17402 | XVBL4M8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17403 | XVBL4M8 | Packing Units | Package 1 Weight | 280 g
17404 | XVBL4M8 | Offer Sustainability | Sustainable offer status | Green Premium product
17405 | XVBL4M8 | Offer Sustainability | REACh Regulation | REACh Declaration
17406 | XVBL4M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17407 | XVBL4M8 | Offer Sustainability | Mercury free | Yes
17408 | XVBL4M8 | Offer Sustainability | RoHS exemption information | Yes
17409 | XVBL4M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17410 | XVBL4M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17411 | XVBL4M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17412 | XVBL4M8 | Contractual warranty | Warranty | 18 months
17413 | XVBL0B3 | Main | range of product | Harmony XVB Universal
17414 | XVBL0B3 | Main | product or component type | Complete beacon
17415 | XVBL0B3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17416 | XVBL0B3 | Main | signalling type | Steady
17417 | XVBL0B3 | Main | mounting diameter | 70 mm
17418 | XVBL0B3 | Main | component name | XVBL
17419 | XVBL0B3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17420 | XVBL0B3 | Main | light source | Integral LED, green
17421 | XVBL0B3 | Main | bulb type | Protected LED
17422 | XVBL0B3 | Main | [Us] rated supply voltage | 24 V AC/DC
17423 | XVBL0B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17424 | XVBL0B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17425 | XVBL0B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17426 | XVBL0B3 | Complementary | current consumption | < 47 mA AC/DC
17427 | XVBL0B3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
17428 | XVBL0B3 | Complementary | CAD overall width | 70 mm
17429 | XVBL0B3 | Complementary | CAD overall height | 139 mm
17430 | XVBL0B3 | Complementary | CAD overall depth | 70 mm
17431 | XVBL0B3 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
17432 | XVBL0B3 | Complementary | net weight | 0.27 kg
17433 | XVBL0B3 | Environment | pollution degree | 2
17434 | XVBL0B3 | Environment | product certifications | GOST UL 508 CCC CSA C22-2 No 14
17435 | XVBL0B3 | Environment | standards | EN/IEC 60947-5-1
17436 | XVBL0B3 | Environment | protective treatment | TC
17437 | XVBL0B3 | Environment | ambient air temperature for storage | -40…70 °C
17438 | XVBL0B3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17439 | XVBL0B3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17440 | XVBL0B3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17441 | XVBL0B3 | Packing Units | Package 1 Weight | 269 g
17442 | XVBL0B3 | Packing Units | Package 2 Weight | 3.684 kg
17443 | XVBL0B3 | Offer Sustainability | Sustainable offer status | Green Premium product
17444 | XVBL0B3 | Offer Sustainability | REACh Regulation | REACh Declaration
17445 | XVBL0B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17446 | XVBL0B3 | Offer Sustainability | Mercury free | Yes
17447 | XVBL0B3 | Offer Sustainability | RoHS exemption information | Yes
17448 | XVBL0B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17449 | XVBL0B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17450 | XVBL0B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17451 | XVBL0B3 | Contractual warranty | Warranty | 18 months
17452 | XVBL0B4 | Main | range of product | Harmony XVB Universal
17453 | XVBL0B4 | Main | product or component type | Complete beacon
17454 | XVBL0B4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17455 | XVBL0B4 | Main | signalling type | Steady
17456 | XVBL0B4 | Main | mounting diameter | 70 mm
17457 | XVBL0B4 | Main | component name | XVBL
17458 | XVBL0B4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17459 | XVBL0B4 | Main | light source | Integral LED, red
17460 | XVBL0B4 | Main | bulb type | Protected LED
17461 | XVBL0B4 | Main | [Us] rated supply voltage | 24 V AC/DC
17462 | XVBL0B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17463 | XVBL0B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17464 | XVBL0B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17465 | XVBL0B4 | Complementary | current consumption | < 47 mA AC/DC
17466 | XVBL0B4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
17467 | XVBL0B4 | Complementary | CAD overall width | 70 mm
17468 | XVBL0B4 | Complementary | CAD overall height | 139 mm
17469 | XVBL0B4 | Complementary | CAD overall depth | 70 mm
17470 | XVBL0B4 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
17471 | XVBL0B4 | Complementary | net weight | 0.27 kg
17472 | XVBL0B4 | Environment | pollution degree | 2
17473 | XVBL0B4 | Environment | product certifications | CSA C22-2 No 14 UL 508 GOST CCC
17474 | XVBL0B4 | Environment | standards | EN/IEC 60947-5-1
17475 | XVBL0B4 | Environment | protective treatment | TC
17476 | XVBL0B4 | Environment | ambient air temperature for storage | -40…70 °C
17477 | XVBL0B4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17478 | XVBL0B4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17479 | XVBL0B4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17480 | XVBL0B4 | Packing Units | Package 1 Weight | 272 g
17481 | XVBL0B4 | Packing Units | Package 2 Weight | 3.79 kg
17482 | XVBL0B4 | Offer Sustainability | Sustainable offer status | Green Premium product
17483 | XVBL0B4 | Offer Sustainability | REACh Regulation | REACh Declaration
17484 | XVBL0B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17485 | XVBL0B4 | Offer Sustainability | Mercury free | Yes
17486 | XVBL0B4 | Offer Sustainability | RoHS exemption information | Yes
17487 | XVBL0B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17488 | XVBL0B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17489 | XVBL0B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17490 | XVBL0B4 | Contractual warranty | Warranty | 18 months
17491 | XVBL0B5 | Main | range of product | Harmony XVB Universal
17492 | XVBL0B5 | Main | product or component type | Complete beacon
17493 | XVBL0B5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17494 | XVBL0B5 | Main | signalling type | Steady
17495 | XVBL0B5 | Main | mounting diameter | 70 mm
17496 | XVBL0B5 | Main | component name | XVBL
17497 | XVBL0B5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17498 | XVBL0B5 | Main | light source | Integral LED, orange
17499 | XVBL0B5 | Main | bulb type | Protected LED
17500 | XVBL0B5 | Main | [Us] rated supply voltage | 24 V AC/DC
17501 | XVBL0B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17502 | XVBL0B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17503 | XVBL0B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17504 | XVBL0B5 | Complementary | current consumption | < 47 mA AC/DC
17505 | XVBL0B5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
17506 | XVBL0B5 | Complementary | CAD overall width | 70 mm
17507 | XVBL0B5 | Complementary | CAD overall height | 139 mm
17508 | XVBL0B5 | Complementary | CAD overall depth | 70 mm
17509 | XVBL0B5 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
17510 | XVBL0B5 | Complementary | net weight | 0.27 kg
17511 | XVBL0B5 | Environment | pollution degree | 2
17512 | XVBL0B5 | Environment | product certifications | GOST UL 508 CSA C22-2 No 14 CCC
17513 | XVBL0B5 | Environment | standards | EN/IEC 60947-5-1
17514 | XVBL0B5 | Environment | protective treatment | TC
17515 | XVBL0B5 | Environment | ambient air temperature for storage | -40…70 °C
17516 | XVBL0B5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17517 | XVBL0B5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17518 | XVBL0B5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17519 | XVBL0B5 | Packing Units | Package 1 Weight | 266 g
17520 | XVBL0B5 | Packing Units | Package 2 Weight | 3.664 kg
17521 | XVBL0B5 | Offer Sustainability | Sustainable offer status | Green Premium product
17522 | XVBL0B5 | Offer Sustainability | REACh Regulation | REACh Declaration
17523 | XVBL0B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17524 | XVBL0B5 | Offer Sustainability | Mercury free | Yes
17525 | XVBL0B5 | Offer Sustainability | RoHS exemption information | Yes
17526 | XVBL0B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17527 | XVBL0B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17528 | XVBL0B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17529 | XVBL0B5 | Contractual warranty | Warranty | 18 months
17530 | XVBL0B6 | Main | range of product | Harmony XVB Universal
17531 | XVBL0B6 | Main | product or component type | Complete beacon
17532 | XVBL0B6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17533 | XVBL0B6 | Main | signalling type | Steady
17534 | XVBL0B6 | Main | mounting diameter | 70 mm
17535 | XVBL0B6 | Main | component name | XVBL
17536 | XVBL0B6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17537 | XVBL0B6 | Main | light source | Integral LED, blue
17538 | XVBL0B6 | Main | bulb type | Protected LED
17539 | XVBL0B6 | Main | [Us] rated supply voltage | 24 V AC/DC
17540 | XVBL0B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17541 | XVBL0B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17542 | XVBL0B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17543 | XVBL0B6 | Complementary | current consumption | < 47 mA AC/DC
17544 | XVBL0B6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
17545 | XVBL0B6 | Complementary | CAD overall width | 70 mm
17546 | XVBL0B6 | Complementary | CAD overall height | 139 mm
17547 | XVBL0B6 | Complementary | CAD overall depth | 70 mm
17548 | XVBL0B6 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
17549 | XVBL0B6 | Complementary | net weight | 0.27 kg
17550 | XVBL0B6 | Environment | pollution degree | 2
17551 | XVBL0B6 | Environment | product certifications | CSA C22-2 No 14 CCC GOST UL 508
17552 | XVBL0B6 | Environment | standards | EN/IEC 60947-5-1
17553 | XVBL0B6 | Environment | protective treatment | TC
17554 | XVBL0B6 | Environment | ambient air temperature for storage | -40…70 °C
17555 | XVBL0B6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17556 | XVBL0B6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17557 | XVBL0B6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17558 | XVBL0B6 | Packing Units | Package 1 Weight | 272 g
17559 | XVBL0B6 | Packing Units | Package 2 Weight | 3.697 kg
17560 | XVBL0B6 | Offer Sustainability | Sustainable offer status | Green Premium product
17561 | XVBL0B6 | Offer Sustainability | REACh Regulation | REACh Declaration
17562 | XVBL0B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17563 | XVBL0B6 | Offer Sustainability | Mercury free | Yes
17564 | XVBL0B6 | Offer Sustainability | RoHS exemption information | Yes
17565 | XVBL0B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17566 | XVBL0B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17567 | XVBL0B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17568 | XVBL0B6 | Contractual warranty | Warranty | 18 months
17569 | XVBL0B7 | Main | range of product | Harmony XVB Universal
17570 | XVBL0B7 | Main | product or component type | Complete beacon
17571 | XVBL0B7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17572 | XVBL0B7 | Main | signalling type | Steady
17573 | XVBL0B7 | Main | mounting diameter | 70 mm
17574 | XVBL0B7 | Main | component name | XVBL
17575 | XVBL0B7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17576 | XVBL0B7 | Main | light source | Integral LED, clear
17577 | XVBL0B7 | Main | bulb type | Protected LED
17578 | XVBL0B7 | Main | [Us] rated supply voltage | 24 V AC/DC
17579 | XVBL0B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17580 | XVBL0B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17581 | XVBL0B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17582 | XVBL0B7 | Complementary | current consumption | < 47 mA AC/DC
17583 | XVBL0B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
17584 | XVBL0B7 | Complementary | CAD overall width | 70 mm
17585 | XVBL0B7 | Complementary | CAD overall height | 139 mm
17586 | XVBL0B7 | Complementary | CAD overall depth | 70 mm
17587 | XVBL0B7 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
17588 | XVBL0B7 | Complementary | net weight | 0.27 kg
17589 | XVBL0B7 | Environment | pollution degree | 2
17590 | XVBL0B7 | Environment | product certifications | CSA C22-2 No 14 GOST CCC UL 508
17591 | XVBL0B7 | Environment | standards | EN/IEC 60947-5-1
17592 | XVBL0B7 | Environment | protective treatment | TC
17593 | XVBL0B7 | Environment | ambient air temperature for storage | -40…70 °C
17594 | XVBL0B7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17595 | XVBL0B7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17596 | XVBL0B7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17597 | XVBL0B7 | Packing Units | Package 1 Weight | 268 g
17598 | XVBL0B7 | Packing Units | Package 2 Weight | 3.697 kg
17599 | XVBL0B7 | Offer Sustainability | Sustainable offer status | Green Premium product
17600 | XVBL0B7 | Offer Sustainability | REACh Regulation | REACh Declaration
17601 | XVBL0B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17602 | XVBL0B7 | Offer Sustainability | Mercury free | Yes
17603 | XVBL0B7 | Offer Sustainability | RoHS exemption information | Yes
17604 | XVBL0B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17605 | XVBL0B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17606 | XVBL0B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17607 | XVBL0B7 | Contractual warranty | Warranty | 18 months
17608 | XVBL0B8 | Main | range of product | Harmony XVB Universal
17609 | XVBL0B8 | Main | product or component type | Complete beacon
17610 | XVBL0B8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17611 | XVBL0B8 | Main | signalling type | Steady
17612 | XVBL0B8 | Main | mounting diameter | 70 mm
17613 | XVBL0B8 | Main | component name | XVBL
17614 | XVBL0B8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17615 | XVBL0B8 | Main | light source | Integral LED, yellow
17616 | XVBL0B8 | Main | bulb type | Protected LED
17617 | XVBL0B8 | Main | [Us] rated supply voltage | 24 V AC/DC
17618 | XVBL0B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17619 | XVBL0B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17620 | XVBL0B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17621 | XVBL0B8 | Complementary | current consumption | < 47 mA AC/DC
17622 | XVBL0B8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
17623 | XVBL0B8 | Complementary | CAD overall width | 70 mm
17624 | XVBL0B8 | Complementary | CAD overall height | 139 mm
17625 | XVBL0B8 | Complementary | CAD overall depth | 70 mm
17626 | XVBL0B8 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
17627 | XVBL0B8 | Complementary | net weight | 0.27 kg
17628 | XVBL0B8 | Environment | pollution degree | 2
17629 | XVBL0B8 | Environment | product certifications | GOST UL 508 CSA C22-2 No 14 CCC
17630 | XVBL0B8 | Environment | standards | EN/IEC 60947-5-1
17631 | XVBL0B8 | Environment | protective treatment | TC
17632 | XVBL0B8 | Environment | ambient air temperature for storage | -40…70 °C
17633 | XVBL0B8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17634 | XVBL0B8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17635 | XVBL0B8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17636 | XVBL0B8 | Packing Units | Package 1 Weight | 260 g
17637 | XVBL0B8 | Packing Units | Package 2 Weight | 3.569 kg
17638 | XVBL0B8 | Offer Sustainability | Sustainable offer status | Green Premium product
17639 | XVBL0B8 | Offer Sustainability | REACh Regulation | REACh Declaration
17640 | XVBL0B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17641 | XVBL0B8 | Offer Sustainability | Mercury free | Yes
17642 | XVBL0B8 | Offer Sustainability | RoHS exemption information | Yes
17643 | XVBL0B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17644 | XVBL0B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17645 | XVBL0B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17646 | XVBL0B8 | Contractual warranty | Warranty | 18 months
17647 | XVBL0G3 | Main | range of product | Harmony XVB Universal
17648 | XVBL0G3 | Main | product or component type | Complete beacon
17649 | XVBL0G3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17650 | XVBL0G3 | Main | signalling type | Steady
17651 | XVBL0G3 | Main | mounting diameter | 70 mm
17652 | XVBL0G3 | Main | component name | XVBL
17653 | XVBL0G3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17654 | XVBL0G3 | Main | light source | Integral LED, green
17655 | XVBL0G3 | Main | bulb type | Protected LED
17656 | XVBL0G3 | Main | [Us] rated supply voltage | 120 V AC
17657 | XVBL0G3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17658 | XVBL0G3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17659 | XVBL0G3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17660 | XVBL0G3 | Complementary | current consumption | < 17 mA AC
17661 | XVBL0G3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
17662 | XVBL0G3 | Complementary | CAD overall width | 70 mm
17663 | XVBL0G3 | Complementary | CAD overall height | 139 mm
17664 | XVBL0G3 | Complementary | CAD overall depth | 70 mm
17665 | XVBL0G3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
17666 | XVBL0G3 | Complementary | net weight | 0.27 kg
17667 | XVBL0G3 | Environment | pollution degree | 2
17668 | XVBL0G3 | Environment | product certifications | UL 508 CCC CSA C22-2 No 14 GOST
17669 | XVBL0G3 | Environment | standards | EN/IEC 60947-5-1
17670 | XVBL0G3 | Environment | protective treatment | TC
17671 | XVBL0G3 | Environment | ambient air temperature for storage | -40…70 °C
17672 | XVBL0G3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17673 | XVBL0G3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17674 | XVBL0G3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17675 | XVBL0G3 | Packing Units | Package 1 Weight | 267 g
17676 | XVBL0G3 | Offer Sustainability | Sustainable offer status | Green Premium product
17677 | XVBL0G3 | Offer Sustainability | REACh Regulation | REACh Declaration
17678 | XVBL0G3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17679 | XVBL0G3 | Offer Sustainability | Mercury free | Yes
17680 | XVBL0G3 | Offer Sustainability | RoHS exemption information | Yes
17681 | XVBL0G3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17682 | XVBL0G3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17683 | XVBL0G3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17684 | XVBL0G3 | Contractual warranty | Warranty | 18 months
17685 | XVBL0G4 | Main | range of product | Harmony XVB Universal
17686 | XVBL0G4 | Main | product or component type | Complete beacon
17687 | XVBL0G4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17688 | XVBL0G4 | Main | signalling type | Steady
17689 | XVBL0G4 | Main | mounting diameter | 70 mm
17690 | XVBL0G4 | Main | component name | XVBL
17691 | XVBL0G4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17692 | XVBL0G4 | Main | light source | Integral LED, red
17693 | XVBL0G4 | Main | bulb type | Protected LED
17694 | XVBL0G4 | Main | [Us] rated supply voltage | 120 V AC
17695 | XVBL0G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17696 | XVBL0G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17697 | XVBL0G4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17698 | XVBL0G4 | Complementary | current consumption | < 17 mA AC
17699 | XVBL0G4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
17700 | XVBL0G4 | Complementary | CAD overall width | 70 mm
17701 | XVBL0G4 | Complementary | CAD overall height | 139 mm
17702 | XVBL0G4 | Complementary | CAD overall depth | 70 mm
17703 | XVBL0G4 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
17704 | XVBL0G4 | Complementary | net weight | 0.27 kg
17705 | XVBL0G4 | Environment | pollution degree | 2
17706 | XVBL0G4 | Environment | product certifications | CSA C22-2 No 14 UL 508 GOST CCC
17707 | XVBL0G4 | Environment | standards | EN/IEC 60947-5-1
17708 | XVBL0G4 | Environment | protective treatment | TC
17709 | XVBL0G4 | Environment | ambient air temperature for storage | -40…70 °C
17710 | XVBL0G4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17711 | XVBL0G4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17712 | XVBL0G4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17713 | XVBL0G4 | Packing Units | Package 1 Weight | 268 g
17714 | XVBL0G4 | Packing Units | Package 2 Weight | 5.294 kg
17715 | XVBL0G4 | Offer Sustainability | Sustainable offer status | Green Premium product
17716 | XVBL0G4 | Offer Sustainability | REACh Regulation | REACh Declaration
17717 | XVBL0G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17718 | XVBL0G4 | Offer Sustainability | Mercury free | Yes
17719 | XVBL0G4 | Offer Sustainability | RoHS exemption information | Yes
17720 | XVBL0G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17721 | XVBL0G4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17722 | XVBL0G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17723 | XVBL0G4 | Contractual warranty | Warranty | 18 months
17724 | XVBL0G5 | Main | range of product | Harmony XVB Universal
17725 | XVBL0G5 | Main | product or component type | Complete beacon
17726 | XVBL0G5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17727 | XVBL0G5 | Main | signalling type | Steady
17728 | XVBL0G5 | Main | mounting diameter | 70 mm
17729 | XVBL0G5 | Main | component name | XVBL
17730 | XVBL0G5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17731 | XVBL0G5 | Main | light source | Integral LED, orange
17732 | XVBL0G5 | Main | bulb type | Protected LED
17733 | XVBL0G5 | Main | [Us] rated supply voltage | 120 V AC
17734 | XVBL0G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17735 | XVBL0G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17736 | XVBL0G5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17737 | XVBL0G5 | Complementary | current consumption | < 17 mA AC
17738 | XVBL0G5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
17739 | XVBL0G5 | Complementary | CAD overall width | 70 mm
17740 | XVBL0G5 | Complementary | CAD overall height | 139 mm
17741 | XVBL0G5 | Complementary | CAD overall depth | 70 mm
17742 | XVBL0G5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
17743 | XVBL0G5 | Complementary | net weight | 0.27 kg
17744 | XVBL0G5 | Environment | pollution degree | 2
17745 | XVBL0G5 | Environment | product certifications | UL 508 CCC CSA C22-2 No 14 GOST
17746 | XVBL0G5 | Environment | standards | EN/IEC 60947-5-1
17747 | XVBL0G5 | Environment | protective treatment | TC
17748 | XVBL0G5 | Environment | ambient air temperature for storage | -40…70 °C
17749 | XVBL0G5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17750 | XVBL0G5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17751 | XVBL0G5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17752 | XVBL0G5 | Packing Units | Package 1 Weight | 270 g
17753 | XVBL0G5 | Offer Sustainability | Sustainable offer status | Green Premium product
17754 | XVBL0G5 | Offer Sustainability | REACh Regulation | REACh Declaration
17755 | XVBL0G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17756 | XVBL0G5 | Offer Sustainability | Mercury free | Yes
17757 | XVBL0G5 | Offer Sustainability | RoHS exemption information | Yes
17758 | XVBL0G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17759 | XVBL0G5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17760 | XVBL0G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17761 | XVBL0G5 | Contractual warranty | Warranty | 18 months
17762 | XVBL0G6 | Main | range of product | Harmony XVB Universal
17763 | XVBL0G6 | Main | product or component type | Complete beacon
17764 | XVBL0G6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17765 | XVBL0G6 | Main | signalling type | Steady
17766 | XVBL0G6 | Main | mounting diameter | 70 mm
17767 | XVBL0G6 | Main | component name | XVBL
17768 | XVBL0G6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17769 | XVBL0G6 | Main | light source | Integral LED, blue
17770 | XVBL0G6 | Main | bulb type | Protected LED
17771 | XVBL0G6 | Main | [Us] rated supply voltage | 120 V AC
17772 | XVBL0G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17773 | XVBL0G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17774 | XVBL0G6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17775 | XVBL0G6 | Complementary | current consumption | < 17 mA AC
17776 | XVBL0G6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
17777 | XVBL0G6 | Complementary | CAD overall width | 70 mm
17778 | XVBL0G6 | Complementary | CAD overall height | 139 mm
17779 | XVBL0G6 | Complementary | CAD overall depth | 70 mm
17780 | XVBL0G6 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
17781 | XVBL0G6 | Complementary | net weight | 0.27 kg
17782 | XVBL0G6 | Environment | pollution degree | 2
17783 | XVBL0G6 | Environment | product certifications | GOST CSA C22-2 No 14 UL 508 CCC
17784 | XVBL0G6 | Environment | standards | EN/IEC 60947-5-1
17785 | XVBL0G6 | Environment | protective treatment | TC
17786 | XVBL0G6 | Environment | ambient air temperature for storage | -40…70 °C
17787 | XVBL0G6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17788 | XVBL0G6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17789 | XVBL0G6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17790 | XVBL0G6 | Packing Units | Package 1 Weight | 0.268 kg
17791 | XVBL0G6 | Offer Sustainability | Sustainable offer status | Green Premium product
17792 | XVBL0G6 | Offer Sustainability | REACh Regulation | REACh Declaration
17793 | XVBL0G6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17794 | XVBL0G6 | Offer Sustainability | Mercury free | Yes
17795 | XVBL0G6 | Offer Sustainability | RoHS exemption information | Yes
17796 | XVBL0G6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17797 | XVBL0G6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17798 | XVBL0G6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17799 | XVBL0G6 | Contractual warranty | Warranty | 18 months
17800 | XVBL0G7 | Main | range of product | Harmony XVB Universal
17801 | XVBL0G7 | Main | product or component type | Complete beacon
17802 | XVBL0G7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17803 | XVBL0G7 | Main | signalling type | Steady
17804 | XVBL0G7 | Main | mounting diameter | 70 mm
17805 | XVBL0G7 | Main | component name | XVBL
17806 | XVBL0G7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17807 | XVBL0G7 | Main | light source | Integral LED, clear
17808 | XVBL0G7 | Main | bulb type | Protected LED
17809 | XVBL0G7 | Main | [Us] rated supply voltage | 120 V AC
17810 | XVBL0G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17811 | XVBL0G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17812 | XVBL0G7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17813 | XVBL0G7 | Complementary | current consumption | < 17 mA AC
17814 | XVBL0G7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
17815 | XVBL0G7 | Complementary | CAD overall width | 70 mm
17816 | XVBL0G7 | Complementary | CAD overall height | 139 mm
17817 | XVBL0G7 | Complementary | CAD overall depth | 70 mm
17818 | XVBL0G7 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
17819 | XVBL0G7 | Complementary | net weight | 0.27 kg
17820 | XVBL0G7 | Environment | pollution degree | 2
17821 | XVBL0G7 | Environment | product certifications | CSA C22-2 No 14 GOST UL 508 CCC
17822 | XVBL0G7 | Environment | standards | EN/IEC 60947-5-1
17823 | XVBL0G7 | Environment | protective treatment | TC
17824 | XVBL0G7 | Environment | ambient air temperature for storage | -40…70 °C
17825 | XVBL0G7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17826 | XVBL0G7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17827 | XVBL0G7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17828 | XVBL0G7 | Packing Units | Package 1 Weight | 267 g
17829 | XVBL0G7 | Offer Sustainability | Sustainable offer status | Green Premium product
17830 | XVBL0G7 | Offer Sustainability | REACh Regulation | REACh Declaration
17831 | XVBL0G7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17832 | XVBL0G7 | Offer Sustainability | Mercury free | Yes
17833 | XVBL0G7 | Offer Sustainability | RoHS exemption information | Yes
17834 | XVBL0G7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17835 | XVBL0G7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17836 | XVBL0G7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17837 | XVBL0G7 | Contractual warranty | Warranty | 18 months
17838 | XVBL0G8 | Main | range of product | Harmony XVB Universal
17839 | XVBL0G8 | Main | product or component type | Complete beacon
17840 | XVBL0G8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17841 | XVBL0G8 | Main | signalling type | Steady
17842 | XVBL0G8 | Main | mounting diameter | 70 mm
17843 | XVBL0G8 | Main | component name | XVBL
17844 | XVBL0G8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17845 | XVBL0G8 | Main | light source | Integral LED, yellow
17846 | XVBL0G8 | Main | bulb type | Protected LED
17847 | XVBL0G8 | Main | [Us] rated supply voltage | 120 V AC
17848 | XVBL0G8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17849 | XVBL0G8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17850 | XVBL0G8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17851 | XVBL0G8 | Complementary | current consumption | < 17 mA AC
17852 | XVBL0G8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
17853 | XVBL0G8 | Complementary | CAD overall width | 70 mm
17854 | XVBL0G8 | Complementary | CAD overall height | 139 mm
17855 | XVBL0G8 | Complementary | CAD overall depth | 70 mm
17856 | XVBL0G8 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
17857 | XVBL0G8 | Complementary | net weight | 0.27 kg
17858 | XVBL0G8 | Environment | pollution degree | 2
17859 | XVBL0G8 | Environment | product certifications | CCC UL 508 GOST CSA C22-2 No 14
17860 | XVBL0G8 | Environment | standards | EN/IEC 60947-5-1
17861 | XVBL0G8 | Environment | protective treatment | TC
17862 | XVBL0G8 | Environment | ambient air temperature for storage | -40…70 °C
17863 | XVBL0G8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17864 | XVBL0G8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17865 | XVBL0G8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17866 | XVBL0G8 | Packing Units | Package 1 Weight | 275 g
17867 | XVBL0G8 | Offer Sustainability | Sustainable offer status | Green Premium product
17868 | XVBL0G8 | Offer Sustainability | REACh Regulation | REACh Declaration
17869 | XVBL0G8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17870 | XVBL0G8 | Offer Sustainability | Mercury free | Yes
17871 | XVBL0G8 | Offer Sustainability | RoHS exemption information | Yes
17872 | XVBL0G8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17873 | XVBL0G8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17874 | XVBL0G8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17875 | XVBL0G8 | Contractual warranty | Warranty | 18 months
17876 | XVBL0M3 | Main | range of product | Harmony XVB Universal
17877 | XVBL0M3 | Main | product or component type | Complete beacon
17878 | XVBL0M3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17879 | XVBL0M3 | Main | signalling type | Steady
17880 | XVBL0M3 | Main | mounting diameter | 70 mm
17881 | XVBL0M3 | Main | component name | XVBL
17882 | XVBL0M3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17883 | XVBL0M3 | Main | light source | Integral LED, green
17884 | XVBL0M3 | Main | bulb type | Protected LED
17885 | XVBL0M3 | Main | [Us] rated supply voltage | 230 V AC
17886 | XVBL0M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17887 | XVBL0M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17888 | XVBL0M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17889 | XVBL0M3 | Complementary | current consumption | < 17 mA AC
17890 | XVBL0M3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
17891 | XVBL0M3 | Complementary | CAD overall width | 70 mm
17892 | XVBL0M3 | Complementary | CAD overall height | 139 mm
17893 | XVBL0M3 | Complementary | CAD overall depth | 70 mm
17894 | XVBL0M3 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
17895 | XVBL0M3 | Complementary | net weight | 0.27 kg
17896 | XVBL0M3 | Environment | pollution degree | 2
17897 | XVBL0M3 | Environment | product certifications | CCC GOST CSA C22-2 No 14 UL 508
17898 | XVBL0M3 | Environment | standards | EN/IEC 60947-5-1
17899 | XVBL0M3 | Environment | protective treatment | TC
17900 | XVBL0M3 | Environment | ambient air temperature for storage | -40…70 °C
17901 | XVBL0M3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17902 | XVBL0M3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17903 | XVBL0M3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17904 | XVBL0M3 | Packing Units | Package 1 Weight | 267 g
17905 | XVBL0M3 | Packing Units | Package 2 Weight | 3.692 kg
17906 | XVBL0M3 | Offer Sustainability | Sustainable offer status | Green Premium product
17907 | XVBL0M3 | Offer Sustainability | REACh Regulation | REACh Declaration
17908 | XVBL0M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17909 | XVBL0M3 | Offer Sustainability | Mercury free | Yes
17910 | XVBL0M3 | Offer Sustainability | RoHS exemption information | Yes
17911 | XVBL0M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17912 | XVBL0M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17913 | XVBL0M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17914 | XVBL0M3 | Contractual warranty | Warranty | 18 months
17915 | XVBL0M4 | Main | range of product | Harmony XVB Universal
17916 | XVBL0M4 | Main | product or component type | Complete beacon
17917 | XVBL0M4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17918 | XVBL0M4 | Main | signalling type | Steady
17919 | XVBL0M4 | Main | mounting diameter | 70 mm
17920 | XVBL0M4 | Main | component name | XVBL
17921 | XVBL0M4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17922 | XVBL0M4 | Main | light source | Integral LED, red
17923 | XVBL0M4 | Main | bulb type | Protected LED
17924 | XVBL0M4 | Main | [Us] rated supply voltage | 230 V AC
17925 | XVBL0M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17926 | XVBL0M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17927 | XVBL0M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17928 | XVBL0M4 | Complementary | current consumption | < 17 mA AC
17929 | XVBL0M4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
17930 | XVBL0M4 | Complementary | CAD overall width | 70 mm
17931 | XVBL0M4 | Complementary | CAD overall height | 139 mm
17932 | XVBL0M4 | Complementary | CAD overall depth | 70 mm
17933 | XVBL0M4 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
17934 | XVBL0M4 | Complementary | net weight | 0.27 kg
17935 | XVBL0M4 | Environment | pollution degree | 2
17936 | XVBL0M4 | Environment | product certifications | UL 508 CCC GOST CSA C22-2 No 14
17937 | XVBL0M4 | Environment | standards | EN/IEC 60947-5-1
17938 | XVBL0M4 | Environment | protective treatment | TC
17939 | XVBL0M4 | Environment | ambient air temperature for storage | -40…70 °C
17940 | XVBL0M4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17941 | XVBL0M4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17942 | XVBL0M4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17943 | XVBL0M4 | Packing Units | Package 1 Weight | 268 g
17944 | XVBL0M4 | Packing Units | Package 2 Weight | 3.668 kg
17945 | XVBL0M4 | Offer Sustainability | Sustainable offer status | Green Premium product
17946 | XVBL0M4 | Offer Sustainability | REACh Regulation | REACh Declaration
17947 | XVBL0M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17948 | XVBL0M4 | Offer Sustainability | Mercury free | Yes
17949 | XVBL0M4 | Offer Sustainability | RoHS exemption information | Yes
17950 | XVBL0M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17951 | XVBL0M4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17952 | XVBL0M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17953 | XVBL0M4 | Contractual warranty | Warranty | 18 months
17954 | XVBL0M5 | Main | range of product | Harmony XVB Universal
17955 | XVBL0M5 | Main | product or component type | Complete beacon
17956 | XVBL0M5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17957 | XVBL0M5 | Main | signalling type | Steady
17958 | XVBL0M5 | Main | mounting diameter | 70 mm
17959 | XVBL0M5 | Main | component name | XVBL
17960 | XVBL0M5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
17961 | XVBL0M5 | Main | light source | Integral LED, orange
17962 | XVBL0M5 | Main | bulb type | Protected LED
17963 | XVBL0M5 | Main | [Us] rated supply voltage | 230 V AC
17964 | XVBL0M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
17965 | XVBL0M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
17966 | XVBL0M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
17967 | XVBL0M5 | Complementary | current consumption | < 17 mA AC
17968 | XVBL0M5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
17969 | XVBL0M5 | Complementary | CAD overall width | 70 mm
17970 | XVBL0M5 | Complementary | CAD overall height | 139 mm
17971 | XVBL0M5 | Complementary | CAD overall depth | 70 mm
17972 | XVBL0M5 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
17973 | XVBL0M5 | Complementary | net weight | 0.27 kg
17974 | XVBL0M5 | Environment | pollution degree | 2
17975 | XVBL0M5 | Environment | product certifications | CCC UL 508 GOST CSA C22-2 No 14
17976 | XVBL0M5 | Environment | standards | EN/IEC 60947-5-1
17977 | XVBL0M5 | Environment | protective treatment | TC
17978 | XVBL0M5 | Environment | ambient air temperature for storage | -40…70 °C
17979 | XVBL0M5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
17980 | XVBL0M5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
17981 | XVBL0M5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
17982 | XVBL0M5 | Packing Units | Package 1 Weight | 269 g
17983 | XVBL0M5 | Packing Units | Package 2 Weight | 3.713 kg
17984 | XVBL0M5 | Offer Sustainability | Sustainable offer status | Green Premium product
17985 | XVBL0M5 | Offer Sustainability | REACh Regulation | REACh Declaration
17986 | XVBL0M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
17987 | XVBL0M5 | Offer Sustainability | Mercury free | Yes
17988 | XVBL0M5 | Offer Sustainability | RoHS exemption information | Yes
17989 | XVBL0M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
17990 | XVBL0M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
17991 | XVBL0M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
17992 | XVBL0M5 | Contractual warranty | Warranty | 18 months
17993 | XVBL0M6 | Main | range of product | Harmony XVB Universal
17994 | XVBL0M6 | Main | product or component type | Complete beacon
17995 | XVBL0M6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
17996 | XVBL0M6 | Main | signalling type | Steady
17997 | XVBL0M6 | Main | mounting diameter | 70 mm
17998 | XVBL0M6 | Main | component name | XVBL
17999 | XVBL0M6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18000 | XVBL0M6 | Main | light source | Integral LED, blue
18001 | XVBL0M6 | Main | bulb type | Protected LED
18002 | XVBL0M6 | Main | [Us] rated supply voltage | 230 V AC
18003 | XVBL0M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18004 | XVBL0M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18005 | XVBL0M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18006 | XVBL0M6 | Complementary | current consumption | < 17 mA AC
18007 | XVBL0M6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
18008 | XVBL0M6 | Complementary | CAD overall width | 70 mm
18009 | XVBL0M6 | Complementary | CAD overall height | 139 mm
18010 | XVBL0M6 | Complementary | CAD overall depth | 70 mm
18011 | XVBL0M6 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
18012 | XVBL0M6 | Complementary | net weight | 0.27 kg
18013 | XVBL0M6 | Environment | pollution degree | 2
18014 | XVBL0M6 | Environment | product certifications | GOST CCC UL 508 CSA C22-2 No 14
18015 | XVBL0M6 | Environment | standards | EN/IEC 60947-5-1
18016 | XVBL0M6 | Environment | protective treatment | TC
18017 | XVBL0M6 | Environment | ambient air temperature for storage | -40…70 °C
18018 | XVBL0M6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18019 | XVBL0M6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18020 | XVBL0M6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18021 | XVBL0M6 | Packing Units | Package 1 Weight | 0.270 kg
18022 | XVBL0M6 | Offer Sustainability | Sustainable offer status | Green Premium product
18023 | XVBL0M6 | Offer Sustainability | REACh Regulation | REACh Declaration
18024 | XVBL0M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18025 | XVBL0M6 | Offer Sustainability | Mercury free | Yes
18026 | XVBL0M6 | Offer Sustainability | RoHS exemption information | Yes
18027 | XVBL0M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18028 | XVBL0M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18029 | XVBL0M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18030 | XVBL0M6 | Contractual warranty | Warranty | 18 months
18031 | XVBL0M7 | Main | range of product | Harmony XVB Universal
18032 | XVBL0M7 | Main | product or component type | Complete beacon
18033 | XVBL0M7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18034 | XVBL0M7 | Main | signalling type | Steady
18035 | XVBL0M7 | Main | mounting diameter | 70 mm
18036 | XVBL0M7 | Main | component name | XVBL
18037 | XVBL0M7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18038 | XVBL0M7 | Main | light source | Integral LED, clear
18039 | XVBL0M7 | Main | bulb type | Protected LED
18040 | XVBL0M7 | Main | [Us] rated supply voltage | 230 V AC
18041 | XVBL0M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18042 | XVBL0M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18043 | XVBL0M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18044 | XVBL0M7 | Complementary | current consumption | < 17 mA AC
18045 | XVBL0M7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
18046 | XVBL0M7 | Complementary | CAD overall width | 70 mm
18047 | XVBL0M7 | Complementary | CAD overall height | 139 mm
18048 | XVBL0M7 | Complementary | CAD overall depth | 70 mm
18049 | XVBL0M7 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
18050 | XVBL0M7 | Complementary | net weight | 0.27 kg
18051 | XVBL0M7 | Environment | pollution degree | 2
18052 | XVBL0M7 | Environment | product certifications | CSA C22-2 No 14 CCC GOST UL 508
18053 | XVBL0M7 | Environment | standards | EN/IEC 60947-5-1
18054 | XVBL0M7 | Environment | protective treatment | TC
18055 | XVBL0M7 | Environment | ambient air temperature for storage | -40…70 °C
18056 | XVBL0M7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18057 | XVBL0M7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18058 | XVBL0M7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18059 | XVBL0M7 | Packing Units | Package 1 Weight | 268 g
18060 | XVBL0M7 | Offer Sustainability | Sustainable offer status | Green Premium product
18061 | XVBL0M7 | Offer Sustainability | REACh Regulation | REACh Declaration
18062 | XVBL0M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18063 | XVBL0M7 | Offer Sustainability | Mercury free | Yes
18064 | XVBL0M7 | Offer Sustainability | RoHS exemption information | Yes
18065 | XVBL0M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18066 | XVBL0M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18067 | XVBL0M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18068 | XVBL0M7 | Contractual warranty | Warranty | 18 months
18069 | XVBL0M8 | Main | range of product | Harmony XVB Universal
18070 | XVBL0M8 | Main | product or component type | Complete beacon
18071 | XVBL0M8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18072 | XVBL0M8 | Main | signalling type | Steady
18073 | XVBL0M8 | Main | mounting diameter | 70 mm
18074 | XVBL0M8 | Main | component name | XVBL
18075 | XVBL0M8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18076 | XVBL0M8 | Main | light source | Integral LED, yellow
18077 | XVBL0M8 | Main | bulb type | Protected LED
18078 | XVBL0M8 | Main | [Us] rated supply voltage | 230 V AC
18079 | XVBL0M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18080 | XVBL0M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18081 | XVBL0M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18082 | XVBL0M8 | Complementary | current consumption | < 17 mA AC
18083 | XVBL0M8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
18084 | XVBL0M8 | Complementary | CAD overall width | 70 mm
18085 | XVBL0M8 | Complementary | CAD overall height | 139 mm
18086 | XVBL0M8 | Complementary | CAD overall depth | 70 mm
18087 | XVBL0M8 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
18088 | XVBL0M8 | Complementary | net weight | 0.27 kg
18089 | XVBL0M8 | Environment | pollution degree | 2
18090 | XVBL0M8 | Environment | product certifications | CCC GOST UL 508 CSA C22-2 No 14
18091 | XVBL0M8 | Environment | standards | EN/IEC 60947-5-1
18092 | XVBL0M8 | Environment | protective treatment | TC
18093 | XVBL0M8 | Environment | ambient air temperature for storage | -40…70 °C
18094 | XVBL0M8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18095 | XVBL0M8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18096 | XVBL0M8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18097 | XVBL0M8 | Packing Units | Package 1 Weight | 267 g
18098 | XVBL0M8 | Offer Sustainability | Sustainable offer status | Green Premium product
18099 | XVBL0M8 | Offer Sustainability | REACh Regulation | REACh Declaration
18100 | XVBL0M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18101 | XVBL0M8 | Offer Sustainability | Mercury free | Yes
18102 | XVBL0M8 | Offer Sustainability | RoHS exemption information | Yes
18103 | XVBL0M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18104 | XVBL0M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18105 | XVBL0M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18106 | XVBL0M8 | Contractual warranty | Warranty | 18 months
18107 | XVBL1B3 | Main | range of product | Harmony XVB Universal
18108 | XVBL1B3 | Main | product or component type | Complete beacon
18109 | XVBL1B3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18110 | XVBL1B3 | Main | signalling type | Flashing
18111 | XVBL1B3 | Main | mounting diameter | 70 mm
18112 | XVBL1B3 | Main | component name | XVBL
18113 | XVBL1B3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18114 | XVBL1B3 | Main | light source | Integral LED, green
18115 | XVBL1B3 | Main | bulb type | Protected LED
18116 | XVBL1B3 | Main | [Us] rated supply voltage | 24 V AC/DC
18117 | XVBL1B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18118 | XVBL1B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18119 | XVBL1B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18120 | XVBL1B3 | Complementary | current consumption | < 47 mA AC/DC
18121 | XVBL1B3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
18122 | XVBL1B3 | Complementary | flashing frequency | 1 Hz
18123 | XVBL1B3 | Complementary | CAD overall width | 70 mm
18124 | XVBL1B3 | Complementary | CAD overall height | 139 mm
18125 | XVBL1B3 | Complementary | CAD overall depth | 70 mm
18126 | XVBL1B3 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
18127 | XVBL1B3 | Complementary | net weight | 0.28 kg
18128 | XVBL1B3 | Environment | pollution degree | 2
18129 | XVBL1B3 | Environment | product certifications | CCC UL 508 CSA C22-2 No 14 GOST
18130 | XVBL1B3 | Environment | standards | EN/IEC 60947-5-1
18131 | XVBL1B3 | Environment | protective treatment | TC
18132 | XVBL1B3 | Environment | ambient air temperature for storage | -40…70 °C
18133 | XVBL1B3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18134 | XVBL1B3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18135 | XVBL1B3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18136 | XVBL1B3 | Packing Units | Package 1 Weight | 0.271 kg
18137 | XVBL1B3 | Offer Sustainability | Sustainable offer status | Green Premium product
18138 | XVBL1B3 | Offer Sustainability | REACh Regulation | REACh Declaration
18139 | XVBL1B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18140 | XVBL1B3 | Offer Sustainability | Mercury free | Yes
18141 | XVBL1B3 | Offer Sustainability | RoHS exemption information | Yes
18142 | XVBL1B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18143 | XVBL1B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18144 | XVBL1B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18145 | XVBL1B3 | Contractual warranty | Warranty | 18 months
18146 | XVBL1B4 | Main | range of product | Harmony XVB Universal
18147 | XVBL1B4 | Main | product or component type | Complete beacon
18148 | XVBL1B4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18149 | XVBL1B4 | Main | signalling type | Flashing
18150 | XVBL1B4 | Main | mounting diameter | 70 mm
18151 | XVBL1B4 | Main | component name | XVBL
18152 | XVBL1B4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18153 | XVBL1B4 | Main | light source | Integral LED, red
18154 | XVBL1B4 | Main | bulb type | Protected LED
18155 | XVBL1B4 | Main | [Us] rated supply voltage | 24 V AC/DC
18156 | XVBL1B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18157 | XVBL1B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18158 | XVBL1B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18159 | XVBL1B4 | Complementary | current consumption | < 47 mA AC/DC
18160 | XVBL1B4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
18161 | XVBL1B4 | Complementary | flashing frequency | 1 Hz
18162 | XVBL1B4 | Complementary | CAD overall width | 70 mm
18163 | XVBL1B4 | Complementary | CAD overall height | 139 mm
18164 | XVBL1B4 | Complementary | CAD overall depth | 70 mm
18165 | XVBL1B4 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
18166 | XVBL1B4 | Complementary | net weight | 0.28 kg
18167 | XVBL1B4 | Environment | pollution degree | 2
18168 | XVBL1B4 | Environment | product certifications | UL 508 GOST CCC CSA C22-2 No 14
18169 | XVBL1B4 | Environment | standards | EN/IEC 60947-5-1
18170 | XVBL1B4 | Environment | protective treatment | TC
18171 | XVBL1B4 | Environment | ambient air temperature for storage | -40…70 °C
18172 | XVBL1B4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18173 | XVBL1B4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18174 | XVBL1B4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18175 | XVBL1B4 | Packing Units | Package 1 Weight | 284 g
18176 | XVBL1B4 | Packing Units | Package 2 Weight | 3.817 kg
18177 | XVBL1B4 | Offer Sustainability | Sustainable offer status | Green Premium product
18178 | XVBL1B4 | Offer Sustainability | REACh Regulation | REACh Declaration
18179 | XVBL1B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18180 | XVBL1B4 | Offer Sustainability | Mercury free | Yes
18181 | XVBL1B4 | Offer Sustainability | RoHS exemption information | Yes
18182 | XVBL1B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18183 | XVBL1B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18184 | XVBL1B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18185 | XVBL1B4 | Contractual warranty | Warranty | 18 months
18186 | XVBL1B5 | Main | range of product | Harmony XVB Universal
18187 | XVBL1B5 | Main | product or component type | Complete beacon
18188 | XVBL1B5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18189 | XVBL1B5 | Main | signalling type | Flashing
18190 | XVBL1B5 | Main | mounting diameter | 70 mm
18191 | XVBL1B5 | Main | component name | XVBL
18192 | XVBL1B5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18193 | XVBL1B5 | Main | light source | Integral LED, orange
18194 | XVBL1B5 | Main | bulb type | Protected LED
18195 | XVBL1B5 | Main | [Us] rated supply voltage | 24 V AC/DC
18196 | XVBL1B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18197 | XVBL1B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18198 | XVBL1B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18199 | XVBL1B5 | Complementary | current consumption | < 47 mA AC/DC
18200 | XVBL1B5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
18201 | XVBL1B5 | Complementary | flashing frequency | 1 Hz
18202 | XVBL1B5 | Complementary | CAD overall width | 70 mm
18203 | XVBL1B5 | Complementary | CAD overall height | 139 mm
18204 | XVBL1B5 | Complementary | CAD overall depth | 70 mm
18205 | XVBL1B5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
18206 | XVBL1B5 | Complementary | net weight | 0.28 kg
18207 | XVBL1B5 | Environment | pollution degree | 2
18208 | XVBL1B5 | Environment | product certifications | GOST CSA C22-2 No 14 CCC UL 508
18209 | XVBL1B5 | Environment | standards | EN/IEC 60947-5-1
18210 | XVBL1B5 | Environment | protective treatment | TC
18211 | XVBL1B5 | Environment | ambient air temperature for storage | -40…70 °C
18212 | XVBL1B5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18213 | XVBL1B5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18214 | XVBL1B5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18215 | XVBL1B5 | Packing Units | Package 1 Weight | 286 g
18216 | XVBL1B5 | Packing Units | Package 2 Weight | 3.865 kg
18217 | XVBL1B5 | Offer Sustainability | Sustainable offer status | Green Premium product
18218 | XVBL1B5 | Offer Sustainability | REACh Regulation | REACh Declaration
18219 | XVBL1B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18220 | XVBL1B5 | Offer Sustainability | Mercury free | Yes
18221 | XVBL1B5 | Offer Sustainability | RoHS exemption information | Yes
18222 | XVBL1B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18223 | XVBL1B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18224 | XVBL1B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18225 | XVBL1B5 | Contractual warranty | Warranty | 18 months
18226 | XVBL1B6 | Main | range of product | Harmony XVB Universal
18227 | XVBL1B6 | Main | product or component type | Complete beacon
18228 | XVBL1B6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18229 | XVBL1B6 | Main | signalling type | Flashing
18230 | XVBL1B6 | Main | mounting diameter | 70 mm
18231 | XVBL1B6 | Main | component name | XVBL
18232 | XVBL1B6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18233 | XVBL1B6 | Main | light source | Integral LED, blue
18234 | XVBL1B6 | Main | bulb type | Protected LED
18235 | XVBL1B6 | Main | [Us] rated supply voltage | 24 V AC/DC
18236 | XVBL1B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18237 | XVBL1B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18238 | XVBL1B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18239 | XVBL1B6 | Complementary | current consumption | < 47 mA AC/DC
18240 | XVBL1B6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
18241 | XVBL1B6 | Complementary | flashing frequency | 1 Hz
18242 | XVBL1B6 | Complementary | CAD overall width | 70 mm
18243 | XVBL1B6 | Complementary | CAD overall height | 139 mm
18244 | XVBL1B6 | Complementary | CAD overall depth | 70 mm
18245 | XVBL1B6 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
18246 | XVBL1B6 | Complementary | net weight | 0.28 kg
18247 | XVBL1B6 | Environment | pollution degree | 2
18248 | XVBL1B6 | Environment | product certifications | CCC GOST CSA C22-2 No 14 UL 508
18249 | XVBL1B6 | Environment | standards | EN/IEC 60947-5-1
18250 | XVBL1B6 | Environment | protective treatment | TC
18251 | XVBL1B6 | Environment | ambient air temperature for storage | -40…70 °C
18252 | XVBL1B6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18253 | XVBL1B6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18254 | XVBL1B6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18255 | XVBL1B6 | Packing Units | Package 1 Weight | 280 g
18256 | XVBL1B6 | Packing Units | Package 2 Weight | 5.5 kg
18257 | XVBL1B6 | Offer Sustainability | Sustainable offer status | Green Premium product
18258 | XVBL1B6 | Offer Sustainability | REACh Regulation | REACh Declaration
18259 | XVBL1B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18260 | XVBL1B6 | Offer Sustainability | Mercury free | Yes
18261 | XVBL1B6 | Offer Sustainability | RoHS exemption information | Yes
18262 | XVBL1B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18263 | XVBL1B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18264 | XVBL1B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18265 | XVBL1B6 | Contractual warranty | Warranty | 18 months
18266 | XVBL1B7 | Main | range of product | Harmony XVB Universal
18267 | XVBL1B7 | Main | product or component type | Complete beacon
18268 | XVBL1B7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18269 | XVBL1B7 | Main | signalling type | Flashing
18270 | XVBL1B7 | Main | mounting diameter | 70 mm
18271 | XVBL1B7 | Main | component name | XVBL
18272 | XVBL1B7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18273 | XVBL1B7 | Main | light source | Integral LED, clear
18274 | XVBL1B7 | Main | bulb type | Protected LED
18275 | XVBL1B7 | Main | [Us] rated supply voltage | 24 V AC/DC
18276 | XVBL1B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18277 | XVBL1B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18278 | XVBL1B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18279 | XVBL1B7 | Complementary | current consumption | < 47 mA AC/DC
18280 | XVBL1B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
18281 | XVBL1B7 | Complementary | flashing frequency | 1 Hz
18282 | XVBL1B7 | Complementary | CAD overall width | 70 mm
18283 | XVBL1B7 | Complementary | CAD overall height | 139 mm
18284 | XVBL1B7 | Complementary | CAD overall depth | 70 mm
18285 | XVBL1B7 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
18286 | XVBL1B7 | Complementary | net weight | 0.28 kg
18287 | XVBL1B7 | Environment | pollution degree | 2
18288 | XVBL1B7 | Environment | product certifications | CCC UL 508 GOST CSA C22-2 No 14
18289 | XVBL1B7 | Environment | standards | EN/IEC 60947-5-1
18290 | XVBL1B7 | Environment | protective treatment | TC
18291 | XVBL1B7 | Environment | ambient air temperature for storage | -40…70 °C
18292 | XVBL1B7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18293 | XVBL1B7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18294 | XVBL1B7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18295 | XVBL1B7 | Packing Units | Package 1 Weight | 276 g
18296 | XVBL1B7 | Offer Sustainability | Sustainable offer status | Green Premium product
18297 | XVBL1B7 | Offer Sustainability | REACh Regulation | REACh Declaration
18298 | XVBL1B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18299 | XVBL1B7 | Offer Sustainability | Mercury free | Yes
18300 | XVBL1B7 | Offer Sustainability | RoHS exemption information | Yes
18301 | XVBL1B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18302 | XVBL1B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18303 | XVBL1B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18304 | XVBL1B7 | Contractual warranty | Warranty | 18 months
18305 | XVBL1B8 | Main | range of product | Harmony XVB Universal
18306 | XVBL1B8 | Main | product or component type | Complete beacon
18307 | XVBL1B8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18308 | XVBL1B8 | Main | signalling type | Flashing
18309 | XVBL1B8 | Main | mounting diameter | 70 mm
18310 | XVBL1B8 | Main | component name | XVBL
18311 | XVBL1B8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18312 | XVBL1B8 | Main | light source | Integral LED, yellow
18313 | XVBL1B8 | Main | bulb type | Protected LED
18314 | XVBL1B8 | Main | [Us] rated supply voltage | 24 V AC/DC
18315 | XVBL1B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18316 | XVBL1B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18317 | XVBL1B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18318 | XVBL1B8 | Complementary | current consumption | < 47 mA AC/DC
18319 | XVBL1B8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
18320 | XVBL1B8 | Complementary | flashing frequency | 1 Hz
18321 | XVBL1B8 | Complementary | CAD overall width | 70 mm
18322 | XVBL1B8 | Complementary | CAD overall height | 139 mm
18323 | XVBL1B8 | Complementary | CAD overall depth | 70 mm
18324 | XVBL1B8 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
18325 | XVBL1B8 | Complementary | net weight | 0.28 kg
18326 | XVBL1B8 | Environment | pollution degree | 2
18327 | XVBL1B8 | Environment | product certifications | CCC UL 508 GOST CSA C22-2 No 14
18328 | XVBL1B8 | Environment | standards | EN/IEC 60947-5-1
18329 | XVBL1B8 | Environment | protective treatment | TC
18330 | XVBL1B8 | Environment | ambient air temperature for storage | -40…70 °C
18331 | XVBL1B8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18332 | XVBL1B8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18333 | XVBL1B8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18334 | XVBL1B8 | Packing Units | Package 1 Weight | 0.284 kg
18335 | XVBL1B8 | Offer Sustainability | Sustainable offer status | Green Premium product
18336 | XVBL1B8 | Offer Sustainability | REACh Regulation | REACh Declaration
18337 | XVBL1B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18338 | XVBL1B8 | Offer Sustainability | Mercury free | Yes
18339 | XVBL1B8 | Offer Sustainability | RoHS exemption information | Yes
18340 | XVBL1B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18341 | XVBL1B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18342 | XVBL1B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18343 | XVBL1B8 | Contractual warranty | Warranty | 18 months
18344 | XVBL1G3 | Main | range of product | Harmony XVB Universal
18345 | XVBL1G3 | Main | product or component type | Complete beacon
18346 | XVBL1G3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18347 | XVBL1G3 | Main | signalling type | Flashing
18348 | XVBL1G3 | Main | mounting diameter | 70 mm
18349 | XVBL1G3 | Main | component name | XVBL
18350 | XVBL1G3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18351 | XVBL1G3 | Main | light source | Integral LED, green
18352 | XVBL1G3 | Main | bulb type | Protected LED
18353 | XVBL1G3 | Main | [Us] rated supply voltage | 120 V AC
18354 | XVBL1G3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18355 | XVBL1G3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18356 | XVBL1G3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18357 | XVBL1G3 | Complementary | current consumption | < 17 mA AC
18358 | XVBL1G3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
18359 | XVBL1G3 | Complementary | flashing frequency | 1 Hz
18360 | XVBL1G3 | Complementary | CAD overall width | 70 mm
18361 | XVBL1G3 | Complementary | CAD overall height | 139 mm
18362 | XVBL1G3 | Complementary | CAD overall depth | 70 mm
18363 | XVBL1G3 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
18364 | XVBL1G3 | Complementary | net weight | 0.28 kg
18365 | XVBL1G3 | Environment | pollution degree | 2
18366 | XVBL1G3 | Environment | product certifications | CCC CSA C22-2 No 14 UL 508 GOST
18367 | XVBL1G3 | Environment | standards | EN/IEC 60947-5-1
18368 | XVBL1G3 | Environment | protective treatment | TC
18369 | XVBL1G3 | Environment | ambient air temperature for storage | -40…70 °C
18370 | XVBL1G3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18371 | XVBL1G3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18372 | XVBL1G3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18373 | XVBL1G3 | Packing Units | Package 1 Weight | 0.281 kg
18374 | XVBL1G3 | Offer Sustainability | Sustainable offer status | Green Premium product
18375 | XVBL1G3 | Offer Sustainability | REACh Regulation | REACh Declaration
18376 | XVBL1G3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18377 | XVBL1G3 | Offer Sustainability | Mercury free | Yes
18378 | XVBL1G3 | Offer Sustainability | RoHS exemption information | Yes
18379 | XVBL1G3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18380 | XVBL1G3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18381 | XVBL1G3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18382 | XVBL1G3 | Contractual warranty | Warranty | 18 months
18383 | XVBL1G4 | Main | range of product | Harmony XVB Universal
18384 | XVBL1G4 | Main | product or component type | Complete beacon
18385 | XVBL1G4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18386 | XVBL1G4 | Main | signalling type | Flashing
18387 | XVBL1G4 | Main | mounting diameter | 70 mm
18388 | XVBL1G4 | Main | component name | XVBL
18389 | XVBL1G4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18390 | XVBL1G4 | Main | light source | Integral LED, red
18391 | XVBL1G4 | Main | bulb type | Protected LED
18392 | XVBL1G4 | Main | [Us] rated supply voltage | 120 V AC
18393 | XVBL1G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18394 | XVBL1G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18395 | XVBL1G4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18396 | XVBL1G4 | Complementary | current consumption | < 17 mA AC
18397 | XVBL1G4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
18398 | XVBL1G4 | Complementary | flashing frequency | 1 Hz
18399 | XVBL1G4 | Complementary | CAD overall width | 70 mm
18400 | XVBL1G4 | Complementary | CAD overall height | 139 mm
18401 | XVBL1G4 | Complementary | CAD overall depth | 70 mm
18402 | XVBL1G4 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
18403 | XVBL1G4 | Complementary | net weight | 0.28 kg
18404 | XVBL1G4 | Environment | pollution degree | 2
18405 | XVBL1G4 | Environment | product certifications | CCC CSA C22-2 No 14 UL 508 GOST
18406 | XVBL1G4 | Environment | standards | EN/IEC 60947-5-1
18407 | XVBL1G4 | Environment | protective treatment | TC
18408 | XVBL1G4 | Environment | ambient air temperature for storage | -40…70 °C
18409 | XVBL1G4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18410 | XVBL1G4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18411 | XVBL1G4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18412 | XVBL1G4 | Packing Units | Package 1 Weight | 0.280 kg
18413 | XVBL1G4 | Offer Sustainability | Sustainable offer status | Green Premium product
18414 | XVBL1G4 | Offer Sustainability | REACh Regulation | REACh Declaration
18415 | XVBL1G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18416 | XVBL1G4 | Offer Sustainability | Mercury free | Yes
18417 | XVBL1G4 | Offer Sustainability | RoHS exemption information | Yes
18418 | XVBL1G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18419 | XVBL1G4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18420 | XVBL1G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18421 | XVBL1G4 | Contractual warranty | Warranty | 18 months
18422 | XVBL1G5 | Main | range of product | Harmony XVB Universal
18423 | XVBL1G5 | Main | product or component type | Complete beacon
18424 | XVBL1G5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18425 | XVBL1G5 | Main | signalling type | Flashing
18426 | XVBL1G5 | Main | mounting diameter | 70 mm
18427 | XVBL1G5 | Main | component name | XVBL
18428 | XVBL1G5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18429 | XVBL1G5 | Main | light source | Integral LED, orange
18430 | XVBL1G5 | Main | bulb type | Protected LED
18431 | XVBL1G5 | Main | [Us] rated supply voltage | 120 V AC
18432 | XVBL1G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18433 | XVBL1G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18434 | XVBL1G5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18435 | XVBL1G5 | Complementary | current consumption | < 17 mA AC
18436 | XVBL1G5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
18437 | XVBL1G5 | Complementary | flashing frequency | 1 Hz
18438 | XVBL1G5 | Complementary | CAD overall width | 70 mm
18439 | XVBL1G5 | Complementary | CAD overall height | 139 mm
18440 | XVBL1G5 | Complementary | CAD overall depth | 70 mm
18441 | XVBL1G5 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
18442 | XVBL1G5 | Complementary | net weight | 0.28 kg
18443 | XVBL1G5 | Environment | pollution degree | 2
18444 | XVBL1G5 | Environment | product certifications | CCC GOST UL 508 CSA C22-2 No 14
18445 | XVBL1G5 | Environment | standards | EN/IEC 60947-5-1
18446 | XVBL1G5 | Environment | protective treatment | TC
18447 | XVBL1G5 | Environment | ambient air temperature for storage | -40…70 °C
18448 | XVBL1G5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18449 | XVBL1G5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18450 | XVBL1G5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18451 | XVBL1G5 | Packing Units | Package 1 Weight | 275 g
18452 | XVBL1G5 | Packing Units | Package 2 Weight | 5.412 kg
18453 | XVBL1G5 | Offer Sustainability | Sustainable offer status | Green Premium product
18454 | XVBL1G5 | Offer Sustainability | REACh Regulation | REACh Declaration
18455 | XVBL1G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18456 | XVBL1G5 | Offer Sustainability | Mercury free | Yes
18457 | XVBL1G5 | Offer Sustainability | RoHS exemption information | Yes
18458 | XVBL1G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18459 | XVBL1G5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18460 | XVBL1G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18461 | XVBL1G5 | Contractual warranty | Warranty | 18 months
18462 | XVBL1G6 | Main | range of product | Harmony XVB Universal
18463 | XVBL1G6 | Main | product or component type | Complete beacon
18464 | XVBL1G6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18465 | XVBL1G6 | Main | signalling type | Flashing
18466 | XVBL1G6 | Main | mounting diameter | 70 mm
18467 | XVBL1G6 | Main | component name | XVBL
18468 | XVBL1G6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18469 | XVBL1G6 | Main | light source | Integral LED, blue
18470 | XVBL1G6 | Main | bulb type | Protected LED
18471 | XVBL1G6 | Main | [Us] rated supply voltage | 120 V AC
18472 | XVBL1G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18473 | XVBL1G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18474 | XVBL1G6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18475 | XVBL1G6 | Complementary | current consumption | < 17 mA AC
18476 | XVBL1G6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
18477 | XVBL1G6 | Complementary | flashing frequency | 1 Hz
18478 | XVBL1G6 | Complementary | CAD overall width | 70 mm
18479 | XVBL1G6 | Complementary | CAD overall height | 139 mm
18480 | XVBL1G6 | Complementary | CAD overall depth | 70 mm
18481 | XVBL1G6 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
18482 | XVBL1G6 | Complementary | net weight | 0.28 kg
18483 | XVBL1G6 | Environment | pollution degree | 2
18484 | XVBL1G6 | Environment | product certifications | CCC UL 508 GOST CSA C22-2 No 14
18485 | XVBL1G6 | Environment | standards | EN/IEC 60947-5-1
18486 | XVBL1G6 | Environment | protective treatment | TC
18487 | XVBL1G6 | Environment | ambient air temperature for storage | -40…70 °C
18488 | XVBL1G6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18489 | XVBL1G6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18490 | XVBL1G6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18491 | XVBL1G6 | Packing Units | Package 1 Weight | 0.275 kg
18492 | XVBL1G6 | Offer Sustainability | Sustainable offer status | Green Premium product
18493 | XVBL1G6 | Offer Sustainability | REACh Regulation | REACh Declaration
18494 | XVBL1G6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18495 | XVBL1G6 | Offer Sustainability | Mercury free | Yes
18496 | XVBL1G6 | Offer Sustainability | RoHS exemption information | Yes
18497 | XVBL1G6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18498 | XVBL1G6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18499 | XVBL1G6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18500 | XVBL1G6 | Contractual warranty | Warranty | 18 months
18501 | XVBL1G7 | Main | range of product | Harmony XVB Universal
18502 | XVBL1G7 | Main | product or component type | Complete beacon
18503 | XVBL1G7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18504 | XVBL1G7 | Main | signalling type | Flashing
18505 | XVBL1G7 | Main | mounting diameter | 70 mm
18506 | XVBL1G7 | Main | component name | XVBL
18507 | XVBL1G7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18508 | XVBL1G7 | Main | light source | Integral LED, clear
18509 | XVBL1G7 | Main | bulb type | Protected LED
18510 | XVBL1G7 | Main | [Us] rated supply voltage | 120 V AC
18511 | XVBL1G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18512 | XVBL1G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18513 | XVBL1G7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18514 | XVBL1G7 | Complementary | current consumption | < 17 mA AC
18515 | XVBL1G7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
18516 | XVBL1G7 | Complementary | flashing frequency | 1 Hz
18517 | XVBL1G7 | Complementary | CAD overall width | 70 mm
18518 | XVBL1G7 | Complementary | CAD overall height | 139 mm
18519 | XVBL1G7 | Complementary | CAD overall depth | 70 mm
18520 | XVBL1G7 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
18521 | XVBL1G7 | Complementary | net weight | 0.28 kg
18522 | XVBL1G7 | Environment | pollution degree | 2
18523 | XVBL1G7 | Environment | product certifications | CSA C22-2 No 14 GOST CCC UL 508
18524 | XVBL1G7 | Environment | standards | EN/IEC 60947-5-1
18525 | XVBL1G7 | Environment | protective treatment | TC
18526 | XVBL1G7 | Environment | ambient air temperature for storage | -40…70 °C
18527 | XVBL1G7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18528 | XVBL1G7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18529 | XVBL1G7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18530 | XVBL1G7 | Packing Units | Package 1 Weight | 0.287 kg
18531 | XVBL1G7 | Contractual warranty | Warranty | 18 months
18532 | XVBL1G8 | Main | range of product | Harmony XVB Universal
18533 | XVBL1G8 | Main | product or component type | Complete beacon
18534 | XVBL1G8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18535 | XVBL1G8 | Main | signalling type | Flashing
18536 | XVBL1G8 | Main | mounting diameter | 70 mm
18537 | XVBL1G8 | Main | component name | XVBL
18538 | XVBL1G8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18539 | XVBL1G8 | Main | light source | Integral LED, yellow
18540 | XVBL1G8 | Main | bulb type | Protected LED
18541 | XVBL1G8 | Main | [Us] rated supply voltage | 120 V AC
18542 | XVBL1G8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18543 | XVBL1G8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18544 | XVBL1G8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18545 | XVBL1G8 | Complementary | current consumption | < 17 mA AC
18546 | XVBL1G8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
18547 | XVBL1G8 | Complementary | flashing frequency | 1 Hz
18548 | XVBL1G8 | Complementary | CAD overall width | 70 mm
18549 | XVBL1G8 | Complementary | CAD overall height | 139 mm
18550 | XVBL1G8 | Complementary | CAD overall depth | 70 mm
18551 | XVBL1G8 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
18552 | XVBL1G8 | Complementary | net weight | 0.28 kg
18553 | XVBL1G8 | Environment | pollution degree | 2
18554 | XVBL1G8 | Environment | product certifications | CSA C22-2 No 14 CCC GOST UL 508
18555 | XVBL1G8 | Environment | standards | EN/IEC 60947-5-1
18556 | XVBL1G8 | Environment | protective treatment | TC
18557 | XVBL1G8 | Environment | ambient air temperature for storage | -40…70 °C
18558 | XVBL1G8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18559 | XVBL1G8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18560 | XVBL1G8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18561 | XVBL1G8 | Packing Units | Package 1 Weight | 276 g
18562 | XVBL1G8 | Offer Sustainability | Sustainable offer status | Green Premium product
18563 | XVBL1G8 | Offer Sustainability | REACh Regulation | REACh Declaration
18564 | XVBL1G8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18565 | XVBL1G8 | Offer Sustainability | Mercury free | Yes
18566 | XVBL1G8 | Offer Sustainability | RoHS exemption information | Yes
18567 | XVBL1G8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18568 | XVBL1G8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18569 | XVBL1G8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18570 | XVBL1G8 | Contractual warranty | Warranty | 18 months
18571 | XVBL1M3 | Main | range of product | Harmony XVB Universal
18572 | XVBL1M3 | Main | product or component type | Complete beacon
18573 | XVBL1M3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18574 | XVBL1M3 | Main | signalling type | Flashing
18575 | XVBL1M3 | Main | mounting diameter | 70 mm
18576 | XVBL1M3 | Main | component name | XVBL
18577 | XVBL1M3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18578 | XVBL1M3 | Main | light source | Integral LED, green
18579 | XVBL1M3 | Main | bulb type | Protected LED
18580 | XVBL1M3 | Main | [Us] rated supply voltage | 230 V AC
18581 | XVBL1M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18582 | XVBL1M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18583 | XVBL1M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18584 | XVBL1M3 | Complementary | current consumption | < 17 mA AC
18585 | XVBL1M3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
18586 | XVBL1M3 | Complementary | flashing frequency | 1 Hz
18587 | XVBL1M3 | Complementary | CAD overall width | 70 mm
18588 | XVBL1M3 | Complementary | CAD overall height | 139 mm
18589 | XVBL1M3 | Complementary | CAD overall depth | 70 mm
18590 | XVBL1M3 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
18591 | XVBL1M3 | Complementary | net weight | 0.28 kg
18592 | XVBL1M3 | Environment | pollution degree | 2
18593 | XVBL1M3 | Environment | product certifications | CCC UL 508 GOST CSA C22-2 No 14
18594 | XVBL1M3 | Environment | standards | EN/IEC 60947-5-1
18595 | XVBL1M3 | Environment | protective treatment | TC
18596 | XVBL1M3 | Environment | ambient air temperature for storage | -40…70 °C
18597 | XVBL1M3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18598 | XVBL1M3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18599 | XVBL1M3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18600 | XVBL1M3 | Packing Units | Package 1 Weight | 0.273 kg
18601 | XVBL1M3 | Offer Sustainability | Sustainable offer status | Green Premium product
18602 | XVBL1M3 | Offer Sustainability | REACh Regulation | REACh Declaration
18603 | XVBL1M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18604 | XVBL1M3 | Offer Sustainability | Mercury free | Yes
18605 | XVBL1M3 | Offer Sustainability | RoHS exemption information | Yes
18606 | XVBL1M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18607 | XVBL1M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18608 | XVBL1M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18609 | XVBL1M3 | Contractual warranty | Warranty | 18 months
18610 | XVBL1M4 | Main | range of product | Harmony XVB Universal
18611 | XVBL1M4 | Main | product or component type | Complete beacon
18612 | XVBL1M4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18613 | XVBL1M4 | Main | signalling type | Flashing
18614 | XVBL1M4 | Main | mounting diameter | 70 mm
18615 | XVBL1M4 | Main | component name | XVBL
18616 | XVBL1M4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18617 | XVBL1M4 | Main | light source | Integral LED, red
18618 | XVBL1M4 | Main | bulb type | Protected LED
18619 | XVBL1M4 | Main | [Us] rated supply voltage | 230 V AC
18620 | XVBL1M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18621 | XVBL1M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18622 | XVBL1M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18623 | XVBL1M4 | Complementary | current consumption | < 17 mA AC
18624 | XVBL1M4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
18625 | XVBL1M4 | Complementary | flashing frequency | 1 Hz
18626 | XVBL1M4 | Complementary | CAD overall width | 70 mm
18627 | XVBL1M4 | Complementary | CAD overall height | 139 mm
18628 | XVBL1M4 | Complementary | CAD overall depth | 70 mm
18629 | XVBL1M4 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
18630 | XVBL1M4 | Complementary | net weight | 0.28 kg
18631 | XVBL1M4 | Environment | pollution degree | 2
18632 | XVBL1M4 | Environment | product certifications | CSA C22-2 No 14 GOST UL 508 CCC
18633 | XVBL1M4 | Environment | standards | EN/IEC 60947-5-1
18634 | XVBL1M4 | Environment | protective treatment | TC
18635 | XVBL1M4 | Environment | ambient air temperature for storage | -40…70 °C
18636 | XVBL1M4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18637 | XVBL1M4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18638 | XVBL1M4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18639 | XVBL1M4 | Packing Units | Package 1 Weight | 286 g
18640 | XVBL1M4 | Packing Units | Package 2 Weight | 3.838 kg
18641 | XVBL1M4 | Offer Sustainability | Sustainable offer status | Green Premium product
18642 | XVBL1M4 | Offer Sustainability | REACh Regulation | REACh Declaration
18643 | XVBL1M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18644 | XVBL1M4 | Offer Sustainability | Mercury free | Yes
18645 | XVBL1M4 | Offer Sustainability | RoHS exemption information | Yes
18646 | XVBL1M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18647 | XVBL1M4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18648 | XVBL1M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18649 | XVBL1M4 | Contractual warranty | Warranty | 18 months
18650 | XVBL1M5 | Main | range of product | Harmony XVB Universal
18651 | XVBL1M5 | Main | product or component type | Complete beacon
18652 | XVBL1M5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18653 | XVBL1M5 | Main | signalling type | Flashing
18654 | XVBL1M5 | Main | mounting diameter | 70 mm
18655 | XVBL1M5 | Main | component name | XVBL
18656 | XVBL1M5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18657 | XVBL1M5 | Main | light source | Integral LED, orange
18658 | XVBL1M5 | Main | bulb type | Protected LED
18659 | XVBL1M5 | Main | [Us] rated supply voltage | 230 V AC
18660 | XVBL1M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18661 | XVBL1M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18662 | XVBL1M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18663 | XVBL1M5 | Complementary | current consumption | < 17 mA AC
18664 | XVBL1M5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
18665 | XVBL1M5 | Complementary | flashing frequency | 1 Hz
18666 | XVBL1M5 | Complementary | CAD overall width | 70 mm
18667 | XVBL1M5 | Complementary | CAD overall height | 139 mm
18668 | XVBL1M5 | Complementary | CAD overall depth | 70 mm
18669 | XVBL1M5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
18670 | XVBL1M5 | Complementary | net weight | 0.28 kg
18671 | XVBL1M5 | Environment | pollution degree | 2
18672 | XVBL1M5 | Environment | product certifications | GOST CSA C22-2 No 14 UL 508 CCC
18673 | XVBL1M5 | Environment | standards | EN/IEC 60947-5-1
18674 | XVBL1M5 | Environment | protective treatment | TC
18675 | XVBL1M5 | Environment | ambient air temperature for storage | -40…70 °C
18676 | XVBL1M5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18677 | XVBL1M5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18678 | XVBL1M5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18679 | XVBL1M5 | Packing Units | Package 1 Weight | 274 g
18680 | XVBL1M5 | Packing Units | Package 2 Weight | 3.838 kg
18681 | XVBL1M5 | Offer Sustainability | Sustainable offer status | Green Premium product
18682 | XVBL1M5 | Offer Sustainability | REACh Regulation | REACh Declaration
18683 | XVBL1M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18684 | XVBL1M5 | Offer Sustainability | Mercury free | Yes
18685 | XVBL1M5 | Offer Sustainability | RoHS exemption information | Yes
18686 | XVBL1M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18687 | XVBL1M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18688 | XVBL1M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18689 | XVBL1M5 | Contractual warranty | Warranty | 18 months
18690 | XVBL1M6 | Main | range of product | Harmony XVB Universal
18691 | XVBL1M6 | Main | product or component type | Complete beacon
18692 | XVBL1M6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18693 | XVBL1M6 | Main | signalling type | Flashing
18694 | XVBL1M6 | Main | mounting diameter | 70 mm
18695 | XVBL1M6 | Main | component name | XVBL
18696 | XVBL1M6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18697 | XVBL1M6 | Main | light source | Integral LED, blue
18698 | XVBL1M6 | Main | bulb type | Protected LED
18699 | XVBL1M6 | Main | [Us] rated supply voltage | 230 V AC
18700 | XVBL1M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18701 | XVBL1M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18702 | XVBL1M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18703 | XVBL1M6 | Complementary | current consumption | < 17 mA AC
18704 | XVBL1M6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
18705 | XVBL1M6 | Complementary | flashing frequency | 1 Hz
18706 | XVBL1M6 | Complementary | CAD overall width | 70 mm
18707 | XVBL1M6 | Complementary | CAD overall height | 139 mm
18708 | XVBL1M6 | Complementary | CAD overall depth | 70 mm
18709 | XVBL1M6 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
18710 | XVBL1M6 | Complementary | net weight | 0.28 kg
18711 | XVBL1M6 | Environment | pollution degree | 2
18712 | XVBL1M6 | Environment | product certifications | CCC GOST CSA C22-2 No 14 UL 508
18713 | XVBL1M6 | Environment | standards | EN/IEC 60947-5-1
18714 | XVBL1M6 | Environment | protective treatment | TC
18715 | XVBL1M6 | Environment | ambient air temperature for storage | -40…70 °C
18716 | XVBL1M6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18717 | XVBL1M6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18718 | XVBL1M6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18719 | XVBL1M6 | Packing Units | Package 1 Weight | 280 g
18720 | XVBL1M6 | Offer Sustainability | Sustainable offer status | Green Premium product
18721 | XVBL1M6 | Offer Sustainability | REACh Regulation | REACh Declaration
18722 | XVBL1M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18723 | XVBL1M6 | Offer Sustainability | Mercury free | Yes
18724 | XVBL1M6 | Offer Sustainability | RoHS exemption information | Yes
18725 | XVBL1M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18726 | XVBL1M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18727 | XVBL1M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18728 | XVBL1M6 | Contractual warranty | Warranty | 18 months
18729 | XVBL1M7 | Main | range of product | Harmony XVB Universal
18730 | XVBL1M7 | Main | product or component type | Complete beacon
18731 | XVBL1M7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18732 | XVBL1M7 | Main | signalling type | Flashing
18733 | XVBL1M7 | Main | mounting diameter | 70 mm
18734 | XVBL1M7 | Main | component name | XVBL
18735 | XVBL1M7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18736 | XVBL1M7 | Main | light source | Integral LED, clear
18737 | XVBL1M7 | Main | bulb type | Protected LED
18738 | XVBL1M7 | Main | [Us] rated supply voltage | 230 V AC
18739 | XVBL1M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18740 | XVBL1M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18741 | XVBL1M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18742 | XVBL1M7 | Complementary | current consumption | < 17 mA AC
18743 | XVBL1M7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
18744 | XVBL1M7 | Complementary | flashing frequency | 1 Hz
18745 | XVBL1M7 | Complementary | CAD overall width | 70 mm
18746 | XVBL1M7 | Complementary | CAD overall height | 139 mm
18747 | XVBL1M7 | Complementary | CAD overall depth | 70 mm
18748 | XVBL1M7 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
18749 | XVBL1M7 | Complementary | net weight | 0.28 kg
18750 | XVBL1M7 | Environment | pollution degree | 2
18751 | XVBL1M7 | Environment | product certifications | CCC GOST UL 508 CSA C22-2 No 14
18752 | XVBL1M7 | Environment | standards | EN/IEC 60947-5-1
18753 | XVBL1M7 | Environment | protective treatment | TC
18754 | XVBL1M7 | Environment | ambient air temperature for storage | -40…70 °C
18755 | XVBL1M7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18756 | XVBL1M7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18757 | XVBL1M7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18758 | XVBL1M7 | Packing Units | Package 1 Weight | 275 g
18759 | XVBL1M7 | Offer Sustainability | Sustainable offer status | Green Premium product
18760 | XVBL1M7 | Offer Sustainability | REACh Regulation | REACh Declaration
18761 | XVBL1M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18762 | XVBL1M7 | Offer Sustainability | Mercury free | Yes
18763 | XVBL1M7 | Offer Sustainability | RoHS exemption information | Yes
18764 | XVBL1M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18765 | XVBL1M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18766 | XVBL1M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18767 | XVBL1M7 | Contractual warranty | Warranty | 18 months
18768 | XVBL1M8 | Main | range of product | Harmony XVB Universal
18769 | XVBL1M8 | Main | product or component type | Complete beacon
18770 | XVBL1M8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18771 | XVBL1M8 | Main | signalling type | Flashing
18772 | XVBL1M8 | Main | mounting diameter | 70 mm
18773 | XVBL1M8 | Main | component name | XVBL
18774 | XVBL1M8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18775 | XVBL1M8 | Main | light source | Integral LED, yellow
18776 | XVBL1M8 | Main | bulb type | Protected LED
18777 | XVBL1M8 | Main | [Us] rated supply voltage | 230 V AC
18778 | XVBL1M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18779 | XVBL1M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18780 | XVBL1M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18781 | XVBL1M8 | Complementary | current consumption | < 17 mA AC
18782 | XVBL1M8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
18783 | XVBL1M8 | Complementary | flashing frequency | 1 Hz
18784 | XVBL1M8 | Complementary | CAD overall width | 70 mm
18785 | XVBL1M8 | Complementary | CAD overall height | 139 mm
18786 | XVBL1M8 | Complementary | CAD overall depth | 70 mm
18787 | XVBL1M8 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
18788 | XVBL1M8 | Complementary | net weight | 0.28 kg
18789 | XVBL1M8 | Environment | pollution degree | 2
18790 | XVBL1M8 | Environment | product certifications | UL 508 GOST CSA C22-2 No 14 CCC
18791 | XVBL1M8 | Environment | standards | EN/IEC 60947-5-1
18792 | XVBL1M8 | Environment | protective treatment | TC
18793 | XVBL1M8 | Environment | ambient air temperature for storage | -40…70 °C
18794 | XVBL1M8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18795 | XVBL1M8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18796 | XVBL1M8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18797 | XVBL1M8 | Packing Units | Package 1 Weight | 0.282 kg
18798 | XVBL1M8 | Offer Sustainability | Sustainable offer status | Green Premium product
18799 | XVBL1M8 | Offer Sustainability | REACh Regulation | REACh Declaration
18800 | XVBL1M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18801 | XVBL1M8 | Offer Sustainability | Mercury free | Yes
18802 | XVBL1M8 | Offer Sustainability | RoHS exemption information | Yes
18803 | XVBL1M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18804 | XVBL1M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18805 | XVBL1M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18806 | XVBL1M8 | Contractual warranty | Warranty | 18 months
18807 | XVBL6B3 | Main | range of product | Harmony XVB Universal
18808 | XVBL6B3 | Main | product or component type | Complete beacon
18809 | XVBL6B3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18810 | XVBL6B3 | Main | signalling type | Flashing
18811 | XVBL6B3 | Main | mounting diameter | 70 mm
18812 | XVBL6B3 | Main | component name | XVBL
18813 | XVBL6B3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18814 | XVBL6B3 | Main | light source | Integral flash discharge tube, green
18815 | XVBL6B3 | Main | bulb type | Flash discharge tube
18816 | XVBL6B3 | Main | [Us] rated supply voltage | 24 V AC/DC
18817 | XVBL6B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18818 | XVBL6B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18819 | XVBL6B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18820 | XVBL6B3 | Complementary | current consumption | < 350 mA DC < 550 mA AC
18821 | XVBL6B3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
18822 | XVBL6B3 | Complementary | flash energy | 5 J
18823 | XVBL6B3 | Complementary | flashing frequency | 1 Hz
18824 | XVBL6B3 | Complementary | CAD overall width | 70 mm
18825 | XVBL6B3 | Complementary | CAD overall height | 232 mm
18826 | XVBL6B3 | Complementary | CAD overall depth | 70 mm
18827 | XVBL6B3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
18828 | XVBL6B3 | Complementary | net weight | 0.44 kg
18829 | XVBL6B3 | Environment | product certifications | UL 508 CSA C22-2 No 14 GOST CCC
18830 | XVBL6B3 | Environment | standards | EN/IEC 60947-5-1
18831 | XVBL6B3 | Environment | protective treatment | TC
18832 | XVBL6B3 | Environment | ambient air temperature for storage | -40…70 °C
18833 | XVBL6B3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18834 | XVBL6B3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18835 | XVBL6B3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18836 | XVBL6B3 | Packing Units | Package 1 Weight | 0.440 kg
18837 | XVBL6B3 | Offer Sustainability | Sustainable offer status | Green Premium product
18838 | XVBL6B3 | Offer Sustainability | REACh Regulation | REACh Declaration
18839 | XVBL6B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18840 | XVBL6B3 | Offer Sustainability | Mercury free | Yes
18841 | XVBL6B3 | Offer Sustainability | RoHS exemption information | Yes
18842 | XVBL6B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18843 | XVBL6B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18844 | XVBL6B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18845 | XVBL6B3 | Contractual warranty | Warranty | 18 months
18846 | XVBL6B4 | Main | range of product | Harmony XVB Universal
18847 | XVBL6B4 | Main | product or component type | Complete beacon
18848 | XVBL6B4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18849 | XVBL6B4 | Main | signalling type | Flashing
18850 | XVBL6B4 | Main | mounting diameter | 70 mm
18851 | XVBL6B4 | Main | component name | XVBL
18852 | XVBL6B4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18853 | XVBL6B4 | Main | light source | Integral flash discharge tube, red
18854 | XVBL6B4 | Main | bulb type | Flash discharge tube
18855 | XVBL6B4 | Main | [Us] rated supply voltage | 24 V AC/DC
18856 | XVBL6B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18857 | XVBL6B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18858 | XVBL6B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18859 | XVBL6B4 | Complementary | current consumption | < 350 mA DC < 550 mA AC
18860 | XVBL6B4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
18861 | XVBL6B4 | Complementary | flash energy | 5 J
18862 | XVBL6B4 | Complementary | flashing frequency | 1 Hz
18863 | XVBL6B4 | Complementary | CAD overall width | 70 mm
18864 | XVBL6B4 | Complementary | CAD overall height | 232 mm
18865 | XVBL6B4 | Complementary | CAD overall depth | 70 mm
18866 | XVBL6B4 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
18867 | XVBL6B4 | Complementary | net weight | 0.44 kg
18868 | XVBL6B4 | Environment | product certifications | CCC UL 508 GOST CSA C22-2 No 14
18869 | XVBL6B4 | Environment | standards | EN/IEC 60947-5-1
18870 | XVBL6B4 | Environment | protective treatment | TC
18871 | XVBL6B4 | Environment | ambient air temperature for storage | -40…70 °C
18872 | XVBL6B4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18873 | XVBL6B4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18874 | XVBL6B4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18875 | XVBL6B4 | Packing Units | Package 1 Weight | 438 g
18876 | XVBL6B4 | Packing Units | Package 2 Weight | 5.724 kg
18877 | XVBL6B4 | Offer Sustainability | Sustainable offer status | Green Premium product
18878 | XVBL6B4 | Offer Sustainability | REACh Regulation | REACh Declaration
18879 | XVBL6B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18880 | XVBL6B4 | Offer Sustainability | Mercury free | Yes
18881 | XVBL6B4 | Offer Sustainability | RoHS exemption information | Yes
18882 | XVBL6B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18883 | XVBL6B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18884 | XVBL6B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18885 | XVBL6B4 | Contractual warranty | Warranty | 18 months
18886 | XVBL6B5 | Main | range of product | Harmony XVB Universal
18887 | XVBL6B5 | Main | product or component type | Complete beacon
18888 | XVBL6B5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18889 | XVBL6B5 | Main | signalling type | Flashing
18890 | XVBL6B5 | Main | mounting diameter | 70 mm
18891 | XVBL6B5 | Main | component name | XVBL
18892 | XVBL6B5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18893 | XVBL6B5 | Main | light source | Integral flash discharge tube, orange
18894 | XVBL6B5 | Main | bulb type | Flash discharge tube
18895 | XVBL6B5 | Main | [Us] rated supply voltage | 24 V AC/DC
18896 | XVBL6B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18897 | XVBL6B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18898 | XVBL6B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18899 | XVBL6B5 | Complementary | current consumption | < 350 mA DC < 550 mA AC
18900 | XVBL6B5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
18901 | XVBL6B5 | Complementary | flash energy | 5 J
18902 | XVBL6B5 | Complementary | flashing frequency | 1 Hz
18903 | XVBL6B5 | Complementary | CAD overall width | 70 mm
18904 | XVBL6B5 | Complementary | CAD overall height | 232 mm
18905 | XVBL6B5 | Complementary | CAD overall depth | 70 mm
18906 | XVBL6B5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
18907 | XVBL6B5 | Complementary | net weight | 0.44 kg
18908 | XVBL6B5 | Environment | product certifications | UL 508 CSA C22-2 No 14 CCC GOST
18909 | XVBL6B5 | Environment | standards | EN/IEC 60947-5-1
18910 | XVBL6B5 | Environment | protective treatment | TC
18911 | XVBL6B5 | Environment | ambient air temperature for storage | -40…70 °C
18912 | XVBL6B5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18913 | XVBL6B5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18914 | XVBL6B5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18915 | XVBL6B5 | Packing Units | Package 1 Weight | 440 g
18916 | XVBL6B5 | Packing Units | Package 2 Weight | 5.68 kg
18917 | XVBL6B5 | Offer Sustainability | Sustainable offer status | Green Premium product
18918 | XVBL6B5 | Offer Sustainability | REACh Regulation | REACh Declaration
18919 | XVBL6B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18920 | XVBL6B5 | Offer Sustainability | Mercury free | Yes
18921 | XVBL6B5 | Offer Sustainability | RoHS exemption information | Yes
18922 | XVBL6B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18923 | XVBL6B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18924 | XVBL6B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18925 | XVBL6B5 | Contractual warranty | Warranty | 18 months
18926 | XVBL6B6 | Main | range of product | Harmony XVB Universal
18927 | XVBL6B6 | Main | product or component type | Complete beacon
18928 | XVBL6B6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18929 | XVBL6B6 | Main | signalling type | Flashing
18930 | XVBL6B6 | Main | mounting diameter | 70 mm
18931 | XVBL6B6 | Main | component name | XVBL
18932 | XVBL6B6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18933 | XVBL6B6 | Main | light source | Integral flash discharge tube, blue
18934 | XVBL6B6 | Main | bulb type | Flash discharge tube
18935 | XVBL6B6 | Main | [Us] rated supply voltage | 24 V AC/DC
18936 | XVBL6B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18937 | XVBL6B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18938 | XVBL6B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18939 | XVBL6B6 | Complementary | current consumption | < 350 mA DC < 550 mA AC
18940 | XVBL6B6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
18941 | XVBL6B6 | Complementary | flash energy | 5 J
18942 | XVBL6B6 | Complementary | flashing frequency | 1 Hz
18943 | XVBL6B6 | Complementary | CAD overall width | 70 mm
18944 | XVBL6B6 | Complementary | CAD overall height | 232 mm
18945 | XVBL6B6 | Complementary | CAD overall depth | 70 mm
18946 | XVBL6B6 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
18947 | XVBL6B6 | Complementary | net weight | 0.44 kg
18948 | XVBL6B6 | Environment | product certifications | UL 508 GOST CSA C22-2 No 14 CCC
18949 | XVBL6B6 | Environment | standards | EN/IEC 60947-5-1
18950 | XVBL6B6 | Environment | protective treatment | TC
18951 | XVBL6B6 | Environment | ambient air temperature for storage | -40…70 °C
18952 | XVBL6B6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18953 | XVBL6B6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18954 | XVBL6B6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18955 | XVBL6B6 | Packing Units | Package 1 Weight | 432 g
18956 | XVBL6B6 | Packing Units | Package 2 Weight | 5.7 kg
18957 | XVBL6B6 | Offer Sustainability | Sustainable offer status | Green Premium product
18958 | XVBL6B6 | Offer Sustainability | REACh Regulation | REACh Declaration
18959 | XVBL6B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
18960 | XVBL6B6 | Offer Sustainability | Mercury free | Yes
18961 | XVBL6B6 | Offer Sustainability | RoHS exemption information | Yes
18962 | XVBL6B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
18963 | XVBL6B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
18964 | XVBL6B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
18965 | XVBL6B6 | Contractual warranty | Warranty | 18 months
18966 | XVBL6B7 | Main | range of product | Harmony XVB Universal
18967 | XVBL6B7 | Main | product or component type | Complete beacon
18968 | XVBL6B7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
18969 | XVBL6B7 | Main | signalling type | Flashing
18970 | XVBL6B7 | Main | mounting diameter | 70 mm
18971 | XVBL6B7 | Main | component name | XVBL
18972 | XVBL6B7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
18973 | XVBL6B7 | Main | light source | Integral flash discharge tube, clear
18974 | XVBL6B7 | Main | bulb type | Flash discharge tube
18975 | XVBL6B7 | Main | [Us] rated supply voltage | 24 V AC/DC
18976 | XVBL6B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
18977 | XVBL6B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
18978 | XVBL6B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
18979 | XVBL6B7 | Complementary | current consumption | < 350 mA DC < 550 mA AC
18980 | XVBL6B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
18981 | XVBL6B7 | Complementary | flash energy | 5 J
18982 | XVBL6B7 | Complementary | flashing frequency | 1 Hz
18983 | XVBL6B7 | Complementary | illuminating intensity | 13 cd
18984 | XVBL6B7 | Complementary | CAD overall width | 70 mm
18985 | XVBL6B7 | Complementary | CAD overall height | 232 mm
18986 | XVBL6B7 | Complementary | CAD overall depth | 70 mm
18987 | XVBL6B7 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
18988 | XVBL6B7 | Complementary | net weight | 0.44 kg
18989 | XVBL6B7 | Environment | product certifications | GOST CSA C22-2 No 14 CCC UL 508
18990 | XVBL6B7 | Environment | standards | EN/IEC 60947-5-1
18991 | XVBL6B7 | Environment | protective treatment | TC
18992 | XVBL6B7 | Environment | ambient air temperature for storage | -40…70 °C
18993 | XVBL6B7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
18994 | XVBL6B7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
18995 | XVBL6B7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
18996 | XVBL6B7 | Packing Units | Package 1 Weight | 0.440 kg
18997 | XVBL6B7 | Offer Sustainability | Sustainable offer status | Green Premium product
18998 | XVBL6B7 | Offer Sustainability | REACh Regulation | REACh Declaration
18999 | XVBL6B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19000 | XVBL6B7 | Offer Sustainability | Mercury free | Yes
19001 | XVBL6B7 | Offer Sustainability | RoHS exemption information | Yes
19002 | XVBL6B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19003 | XVBL6B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19004 | XVBL6B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19005 | XVBL6B7 | Contractual warranty | Warranty | 18 months
19006 | XVBL6B8 | Main | range of product | Harmony XVB Universal
19007 | XVBL6B8 | Main | product or component type | Complete beacon
19008 | XVBL6B8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19009 | XVBL6B8 | Main | signalling type | Flashing
19010 | XVBL6B8 | Main | mounting diameter | 70 mm
19011 | XVBL6B8 | Main | component name | XVBL
19012 | XVBL6B8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19013 | XVBL6B8 | Main | light source | Integral flash discharge tube, yellow
19014 | XVBL6B8 | Main | bulb type | Flash discharge tube
19015 | XVBL6B8 | Main | [Us] rated supply voltage | 24 V AC/DC
19016 | XVBL6B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19017 | XVBL6B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19018 | XVBL6B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19019 | XVBL6B8 | Complementary | current consumption | < 350 mA DC < 550 mA AC
19020 | XVBL6B8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
19021 | XVBL6B8 | Complementary | flash energy | 5 J
19022 | XVBL6B8 | Complementary | flashing frequency | 1 Hz
19023 | XVBL6B8 | Complementary | CAD overall width | 70 mm
19024 | XVBL6B8 | Complementary | CAD overall height | 232 mm
19025 | XVBL6B8 | Complementary | CAD overall depth | 70 mm
19026 | XVBL6B8 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19027 | XVBL6B8 | Complementary | net weight | 0.44 kg
19028 | XVBL6B8 | Environment | product certifications | UL 508 GOST CSA C22-2 No 14 CCC
19029 | XVBL6B8 | Environment | standards | EN/IEC 60947-5-1
19030 | XVBL6B8 | Environment | protective treatment | TC
19031 | XVBL6B8 | Environment | ambient air temperature for storage | -40…70 °C
19032 | XVBL6B8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19033 | XVBL6B8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19034 | XVBL6B8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19035 | XVBL6B8 | Packing Units | Package 1 Weight | 0.440 kg
19036 | XVBL6B8 | Offer Sustainability | Sustainable offer status | Green Premium product
19037 | XVBL6B8 | Offer Sustainability | REACh Regulation | REACh Declaration
19038 | XVBL6B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19039 | XVBL6B8 | Offer Sustainability | Mercury free | Yes
19040 | XVBL6B8 | Offer Sustainability | RoHS exemption information | Yes
19041 | XVBL6B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19042 | XVBL6B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19043 | XVBL6B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19044 | XVBL6B8 | Contractual warranty | Warranty | 18 months
19045 | XVBL6G3 | Main | range of product | Harmony XVB Universal
19046 | XVBL6G3 | Main | product or component type | Complete beacon
19047 | XVBL6G3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19048 | XVBL6G3 | Main | signalling type | Flashing
19049 | XVBL6G3 | Main | mounting diameter | 70 mm
19050 | XVBL6G3 | Main | component name | XVBL
19051 | XVBL6G3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19052 | XVBL6G3 | Main | light source | Integral flash discharge tube, green
19053 | XVBL6G3 | Main | bulb type | Flash discharge tube
19054 | XVBL6G3 | Main | [Us] rated supply voltage | 120 V AC
19055 | XVBL6G3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19056 | XVBL6G3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19057 | XVBL6G3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19058 | XVBL6G3 | Complementary | current consumption | < 140 mA AC
19059 | XVBL6G3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19060 | XVBL6G3 | Complementary | flash energy | 5 J
19061 | XVBL6G3 | Complementary | flashing frequency | 1 Hz
19062 | XVBL6G3 | Complementary | CAD overall width | 70 mm
19063 | XVBL6G3 | Complementary | CAD overall height | 232 mm
19064 | XVBL6G3 | Complementary | CAD overall depth | 70 mm
19065 | XVBL6G3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19066 | XVBL6G3 | Complementary | net weight | 0.425 kg
19067 | XVBL6G3 | Environment | product certifications | UL 508 GOST CCC CSA C22-2 No 14
19068 | XVBL6G3 | Environment | standards | EN/IEC 60947-5-1
19069 | XVBL6G3 | Environment | protective treatment | TC
19070 | XVBL6G3 | Environment | ambient air temperature for storage | -40…70 °C
19071 | XVBL6G3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19072 | XVBL6G3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19073 | XVBL6G3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19074 | XVBL6G3 | Packing Units | Package 1 Weight | 425 g
19075 | XVBL6G3 | Offer Sustainability | Sustainable offer status | Green Premium product
19076 | XVBL6G3 | Offer Sustainability | REACh Regulation | REACh Declaration
19077 | XVBL6G3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19078 | XVBL6G3 | Offer Sustainability | Mercury free | Yes
19079 | XVBL6G3 | Offer Sustainability | RoHS exemption information | Yes
19080 | XVBL6G3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19081 | XVBL6G3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19082 | XVBL6G3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19083 | XVBL6G3 | Contractual warranty | Warranty | 18 months
19084 | XVBL6G4 | Main | range of product | Harmony XVB Universal
19085 | XVBL6G4 | Main | product or component type | Complete beacon
19086 | XVBL6G4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19087 | XVBL6G4 | Main | signalling type | Flashing
19088 | XVBL6G4 | Main | mounting diameter | 70 mm
19089 | XVBL6G4 | Main | component name | XVBL
19090 | XVBL6G4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19091 | XVBL6G4 | Main | light source | Integral flash discharge tube, red
19092 | XVBL6G4 | Main | bulb type | Flash discharge tube
19093 | XVBL6G4 | Main | [Us] rated supply voltage | 120 V AC
19094 | XVBL6G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19095 | XVBL6G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19096 | XVBL6G4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19097 | XVBL6G4 | Complementary | current consumption | < 140 mA AC
19098 | XVBL6G4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
19099 | XVBL6G4 | Complementary | flash energy | 5 J
19100 | XVBL6G4 | Complementary | flashing frequency | 1 Hz
19101 | XVBL6G4 | Complementary | CAD overall width | 70 mm
19102 | XVBL6G4 | Complementary | CAD overall height | 232 mm
19103 | XVBL6G4 | Complementary | CAD overall depth | 70 mm
19104 | XVBL6G4 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19105 | XVBL6G4 | Complementary | net weight | 0.425 kg
19106 | XVBL6G4 | Environment | product certifications | GOST UL 508 CCC CSA C22-2 No 14
19107 | XVBL6G4 | Environment | standards | EN/IEC 60947-5-1
19108 | XVBL6G4 | Environment | protective treatment | TC
19109 | XVBL6G4 | Environment | ambient air temperature for storage | -40…70 °C
19110 | XVBL6G4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19111 | XVBL6G4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19112 | XVBL6G4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19113 | XVBL6G4 | Packing Units | Package 1 Weight | 417 g
19114 | XVBL6G4 | Packing Units | Package 2 Weight | 5.479 kg
19115 | XVBL6G4 | Offer Sustainability | Sustainable offer status | Green Premium product
19116 | XVBL6G4 | Offer Sustainability | REACh Regulation | REACh Declaration
19117 | XVBL6G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19118 | XVBL6G4 | Offer Sustainability | Mercury free | Yes
19119 | XVBL6G4 | Offer Sustainability | RoHS exemption information | Yes
19120 | XVBL6G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19121 | XVBL6G4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19122 | XVBL6G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19123 | XVBL6G4 | Contractual warranty | Warranty | 18 months
19124 | XVBL6G5 | Main | range of product | Harmony XVB Universal
19125 | XVBL6G5 | Main | product or component type | Complete beacon
19126 | XVBL6G5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19127 | XVBL6G5 | Main | signalling type | Flashing
19128 | XVBL6G5 | Main | mounting diameter | 70 mm
19129 | XVBL6G5 | Main | component name | XVBL
19130 | XVBL6G5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19131 | XVBL6G5 | Main | light source | Integral flash discharge tube, orange
19132 | XVBL6G5 | Main | bulb type | Flash discharge tube
19133 | XVBL6G5 | Main | [Us] rated supply voltage | 120 V AC
19134 | XVBL6G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19135 | XVBL6G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19136 | XVBL6G5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19137 | XVBL6G5 | Complementary | current consumption | < 140 mA AC
19138 | XVBL6G5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
19139 | XVBL6G5 | Complementary | flash energy | 5 J
19140 | XVBL6G5 | Complementary | flashing frequency | 1 Hz
19141 | XVBL6G5 | Complementary | CAD overall width | 70 mm
19142 | XVBL6G5 | Complementary | CAD overall height | 232 mm
19143 | XVBL6G5 | Complementary | CAD overall depth | 70 mm
19144 | XVBL6G5 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
19145 | XVBL6G5 | Complementary | net weight | 0.425 kg
19146 | XVBL6G5 | Environment | product certifications | CCC CSA C22-2 No 14 GOST UL 508
19147 | XVBL6G5 | Environment | standards | EN/IEC 60947-5-1
19148 | XVBL6G5 | Environment | protective treatment | TC
19149 | XVBL6G5 | Environment | ambient air temperature for storage | -40…70 °C
19150 | XVBL6G5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19151 | XVBL6G5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19152 | XVBL6G5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19153 | XVBL6G5 | Packing Units | Package 1 Weight | 417 g
19154 | XVBL6G5 | Packing Units | Package 2 Weight | 5.476 kg
19155 | XVBL6G5 | Offer Sustainability | Sustainable offer status | Green Premium product
19156 | XVBL6G5 | Offer Sustainability | REACh Regulation | REACh Declaration
19157 | XVBL6G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19158 | XVBL6G5 | Offer Sustainability | Mercury free | Yes
19159 | XVBL6G5 | Offer Sustainability | RoHS exemption information | Yes
19160 | XVBL6G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19161 | XVBL6G5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19162 | XVBL6G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19163 | XVBL6G5 | Contractual warranty | Warranty | 18 months
19164 | XVBL6G6 | Main | range of product | Harmony XVB Universal
19165 | XVBL6G6 | Main | product or component type | Complete beacon
19166 | XVBL6G6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19167 | XVBL6G6 | Main | signalling type | Flashing
19168 | XVBL6G6 | Main | mounting diameter | 70 mm
19169 | XVBL6G6 | Main | component name | XVBL
19170 | XVBL6G6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19171 | XVBL6G6 | Main | light source | Integral flash discharge tube, blue
19172 | XVBL6G6 | Main | bulb type | Flash discharge tube
19173 | XVBL6G6 | Main | [Us] rated supply voltage | 120 V AC
19174 | XVBL6G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19175 | XVBL6G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19176 | XVBL6G6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19177 | XVBL6G6 | Complementary | current consumption | < 140 mA AC
19178 | XVBL6G6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
19179 | XVBL6G6 | Complementary | flash energy | 5 J
19180 | XVBL6G6 | Complementary | flashing frequency | 1 Hz
19181 | XVBL6G6 | Complementary | CAD overall width | 70 mm
19182 | XVBL6G6 | Complementary | CAD overall height | 232 mm
19183 | XVBL6G6 | Complementary | CAD overall depth | 70 mm
19184 | XVBL6G6 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
19185 | XVBL6G6 | Complementary | net weight | 0.425 kg
19186 | XVBL6G6 | Environment | product certifications | CSA C22-2 No 14 UL 508 CCC GOST
19187 | XVBL6G6 | Environment | standards | EN/IEC 60947-5-1
19188 | XVBL6G6 | Environment | protective treatment | TC
19189 | XVBL6G6 | Environment | ambient air temperature for storage | -40…70 °C
19190 | XVBL6G6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19191 | XVBL6G6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19192 | XVBL6G6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19193 | XVBL6G6 | Packing Units | Package 1 Weight | 425 g
19194 | XVBL6G6 | Offer Sustainability | Sustainable offer status | Green Premium product
19195 | XVBL6G6 | Offer Sustainability | REACh Regulation | REACh Declaration
19196 | XVBL6G6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19197 | XVBL6G6 | Offer Sustainability | Mercury free | Yes
19198 | XVBL6G6 | Offer Sustainability | RoHS exemption information | Yes
19199 | XVBL6G6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19200 | XVBL6G6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19201 | XVBL6G6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19202 | XVBL6G6 | Contractual warranty | Warranty | 18 months
19203 | XVBL6G7 | Main | range of product | Harmony XVB Universal
19204 | XVBL6G7 | Main | product or component type | Complete beacon
19205 | XVBL6G7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19206 | XVBL6G7 | Main | signalling type | Flashing
19207 | XVBL6G7 | Main | mounting diameter | 70 mm
19208 | XVBL6G7 | Main | component name | XVBL
19209 | XVBL6G7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19210 | XVBL6G7 | Main | light source | Integral flash discharge tube, clear
19211 | XVBL6G7 | Main | bulb type | Flash discharge tube
19212 | XVBL6G7 | Main | [Us] rated supply voltage | 120 V AC
19213 | XVBL6G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19214 | XVBL6G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19215 | XVBL6G7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19216 | XVBL6G7 | Complementary | current consumption | < 140 mA AC
19217 | XVBL6G7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19218 | XVBL6G7 | Complementary | flash energy | 5 J
19219 | XVBL6G7 | Complementary | flashing frequency | 1 Hz
19220 | XVBL6G7 | Complementary | illuminating intensity | 13 cd
19221 | XVBL6G7 | Complementary | CAD overall width | 70 mm
19222 | XVBL6G7 | Complementary | CAD overall height | 232 mm
19223 | XVBL6G7 | Complementary | CAD overall depth | 70 mm
19224 | XVBL6G7 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19225 | XVBL6G7 | Complementary | net weight | 0.425 kg
19226 | XVBL6G7 | Environment | product certifications | UL 508 CCC GOST CSA C22-2 No 14
19227 | XVBL6G7 | Environment | standards | EN/IEC 60947-5-1
19228 | XVBL6G7 | Environment | protective treatment | TC
19229 | XVBL6G7 | Environment | ambient air temperature for storage | -40…70 °C
19230 | XVBL6G7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19231 | XVBL6G7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19232 | XVBL6G7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19233 | XVBL6G7 | Packing Units | Package 1 Weight | 425 g
19234 | XVBL6G7 | Offer Sustainability | Sustainable offer status | Green Premium product
19235 | XVBL6G7 | Offer Sustainability | REACh Regulation | REACh Declaration
19236 | XVBL6G7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19237 | XVBL6G7 | Offer Sustainability | Mercury free | Yes
19238 | XVBL6G7 | Offer Sustainability | RoHS exemption information | Yes
19239 | XVBL6G7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19240 | XVBL6G7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19241 | XVBL6G7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19242 | XVBL6G7 | Contractual warranty | Warranty | 18 months
19243 | XVBL6G8 | Main | range of product | Harmony XVB Universal
19244 | XVBL6G8 | Main | product or component type | Complete beacon
19245 | XVBL6G8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19246 | XVBL6G8 | Main | signalling type | Flashing
19247 | XVBL6G8 | Main | mounting diameter | 70 mm
19248 | XVBL6G8 | Main | component name | XVBL
19249 | XVBL6G8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19250 | XVBL6G8 | Main | light source | Integral flash discharge tube, yellow
19251 | XVBL6G8 | Main | bulb type | Flash discharge tube
19252 | XVBL6G8 | Main | [Us] rated supply voltage | 120 V AC
19253 | XVBL6G8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19254 | XVBL6G8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19255 | XVBL6G8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19256 | XVBL6G8 | Complementary | current consumption | < 140 mA AC
19257 | XVBL6G8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
19258 | XVBL6G8 | Complementary | flash energy | 5 J
19259 | XVBL6G8 | Complementary | flashing frequency | 1 Hz
19260 | XVBL6G8 | Complementary | CAD overall width | 70 mm
19261 | XVBL6G8 | Complementary | CAD overall height | 232 mm
19262 | XVBL6G8 | Complementary | CAD overall depth | 70 mm
19263 | XVBL6G8 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
19264 | XVBL6G8 | Complementary | net weight | 0.425 kg
19265 | XVBL6G8 | Environment | product certifications | CSA C22-2 No 14 UL 508 CCC GOST
19266 | XVBL6G8 | Environment | standards | EN/IEC 60947-5-1
19267 | XVBL6G8 | Environment | protective treatment | TC
19268 | XVBL6G8 | Environment | ambient air temperature for storage | -40…70 °C
19269 | XVBL6G8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19270 | XVBL6G8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19271 | XVBL6G8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19272 | XVBL6G8 | Packing Units | Package 1 Weight | 425 g
19273 | XVBL6G8 | Offer Sustainability | Sustainable offer status | Green Premium product
19274 | XVBL6G8 | Offer Sustainability | REACh Regulation | REACh Declaration
19275 | XVBL6G8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19276 | XVBL6G8 | Offer Sustainability | Mercury free | Yes
19277 | XVBL6G8 | Offer Sustainability | RoHS exemption information | Yes
19278 | XVBL6G8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19279 | XVBL6G8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19280 | XVBL6G8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19281 | XVBL6G8 | Contractual warranty | Warranty | 18 months
19282 | XVBL6M3 | Main | range of product | Harmony XVB Universal
19283 | XVBL6M3 | Main | product or component type | Complete beacon
19284 | XVBL6M3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19285 | XVBL6M3 | Main | signalling type | Flashing
19286 | XVBL6M3 | Main | mounting diameter | 70 mm
19287 | XVBL6M3 | Main | component name | XVBL
19288 | XVBL6M3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19289 | XVBL6M3 | Main | light source | Integral flash discharge tube, green
19290 | XVBL6M3 | Main | bulb type | Flash discharge tube
19291 | XVBL6M3 | Main | [Us] rated supply voltage | 230 V AC
19292 | XVBL6M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19293 | XVBL6M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19294 | XVBL6M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19295 | XVBL6M3 | Complementary | current consumption | < 105 mA AC
19296 | XVBL6M3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19297 | XVBL6M3 | Complementary | flash energy | 5 J
19298 | XVBL6M3 | Complementary | flashing frequency | 1 Hz
19299 | XVBL6M3 | Complementary | CAD overall width | 70 mm
19300 | XVBL6M3 | Complementary | CAD overall height | 232 mm
19301 | XVBL6M3 | Complementary | CAD overall depth | 70 mm
19302 | XVBL6M3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19303 | XVBL6M3 | Complementary | net weight | 0.435 kg
19304 | XVBL6M3 | Environment | product certifications | CCC CSA C22-2 No 14 GOST UL 508
19305 | XVBL6M3 | Environment | standards | EN/IEC 60947-5-1
19306 | XVBL6M3 | Environment | protective treatment | TC
19307 | XVBL6M3 | Environment | ambient air temperature for storage | -40…70 °C
19308 | XVBL6M3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19309 | XVBL6M3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19310 | XVBL6M3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19311 | XVBL6M3 | Packing Units | Package 1 Weight | 435 g
19312 | XVBL6M3 | Offer Sustainability | Sustainable offer status | Green Premium product
19313 | XVBL6M3 | Offer Sustainability | REACh Regulation | REACh Declaration
19314 | XVBL6M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19315 | XVBL6M3 | Offer Sustainability | Mercury free | Yes
19316 | XVBL6M3 | Offer Sustainability | RoHS exemption information | Yes
19317 | XVBL6M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19318 | XVBL6M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19319 | XVBL6M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19320 | XVBL6M3 | Contractual warranty | Warranty | 18 months
19321 | XVBL6M4 | Main | range of product | Harmony XVB Universal
19322 | XVBL6M4 | Main | product or component type | Complete beacon
19323 | XVBL6M4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19324 | XVBL6M4 | Main | signalling type | Flashing
19325 | XVBL6M4 | Main | mounting diameter | 70 mm
19326 | XVBL6M4 | Main | component name | XVBL
19327 | XVBL6M4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19328 | XVBL6M4 | Main | light source | Integral flash discharge tube, red
19329 | XVBL6M4 | Main | bulb type | Flash discharge tube
19330 | XVBL6M4 | Main | [Us] rated supply voltage | 230 V AC
19331 | XVBL6M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19332 | XVBL6M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19333 | XVBL6M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19334 | XVBL6M4 | Complementary | current consumption | < 105 mA AC
19335 | XVBL6M4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
19336 | XVBL6M4 | Complementary | flash energy | 5 J
19337 | XVBL6M4 | Complementary | flashing frequency | 1 Hz
19338 | XVBL6M4 | Complementary | CAD overall width | 70 mm
19339 | XVBL6M4 | Complementary | CAD overall height | 232 mm
19340 | XVBL6M4 | Complementary | CAD overall depth | 70 mm
19341 | XVBL6M4 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
19342 | XVBL6M4 | Complementary | net weight | 0.435 kg
19343 | XVBL6M4 | Environment | product certifications | CSA C22-2 No 14 GOST UL 508 CCC
19344 | XVBL6M4 | Environment | standards | EN/IEC 60947-5-1
19345 | XVBL6M4 | Environment | protective treatment | TC
19346 | XVBL6M4 | Environment | ambient air temperature for storage | -40…70 °C
19347 | XVBL6M4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19348 | XVBL6M4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19349 | XVBL6M4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19350 | XVBL6M4 | Packing Units | Package 1 Weight | 427 g
19351 | XVBL6M4 | Packing Units | Package 2 Weight | 5.589 kg
19352 | XVBL6M4 | Offer Sustainability | Sustainable offer status | Green Premium product
19353 | XVBL6M4 | Offer Sustainability | REACh Regulation | REACh Declaration
19354 | XVBL6M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19355 | XVBL6M4 | Offer Sustainability | Mercury free | Yes
19356 | XVBL6M4 | Offer Sustainability | RoHS exemption information | Yes
19357 | XVBL6M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19358 | XVBL6M4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19359 | XVBL6M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19360 | XVBL6M4 | Contractual warranty | Warranty | 18 months
19361 | XVBL6M5 | Main | range of product | Harmony XVB Universal
19362 | XVBL6M5 | Main | product or component type | Complete beacon
19363 | XVBL6M5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19364 | XVBL6M5 | Main | signalling type | Flashing
19365 | XVBL6M5 | Main | mounting diameter | 70 mm
19366 | XVBL6M5 | Main | component name | XVBL
19367 | XVBL6M5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19368 | XVBL6M5 | Main | light source | Integral flash discharge tube, orange
19369 | XVBL6M5 | Main | bulb type | Flash discharge tube
19370 | XVBL6M5 | Main | [Us] rated supply voltage | 230 V AC
19371 | XVBL6M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19372 | XVBL6M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19373 | XVBL6M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19374 | XVBL6M5 | Complementary | current consumption | < 105 mA AC
19375 | XVBL6M5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19376 | XVBL6M5 | Complementary | flash energy | 5 J
19377 | XVBL6M5 | Complementary | flashing frequency | 1 Hz
19378 | XVBL6M5 | Complementary | CAD overall width | 70 mm
19379 | XVBL6M5 | Complementary | CAD overall height | 232 mm
19380 | XVBL6M5 | Complementary | CAD overall depth | 70 mm
19381 | XVBL6M5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19382 | XVBL6M5 | Complementary | net weight | 0.435 kg
19383 | XVBL6M5 | Environment | product certifications | UL 508 CCC CSA C22-2 No 14 GOST
19384 | XVBL6M5 | Environment | standards | EN/IEC 60947-5-1
19385 | XVBL6M5 | Environment | protective treatment | TC
19386 | XVBL6M5 | Environment | ambient air temperature for storage | -40…70 °C
19387 | XVBL6M5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19388 | XVBL6M5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19389 | XVBL6M5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19390 | XVBL6M5 | Packing Units | Package 1 Weight | 434 g
19391 | XVBL6M5 | Packing Units | Package 2 Weight | 5.591 kg
19392 | XVBL6M5 | Offer Sustainability | Sustainable offer status | Green Premium product
19393 | XVBL6M5 | Offer Sustainability | REACh Regulation | REACh Declaration
19394 | XVBL6M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19395 | XVBL6M5 | Offer Sustainability | Mercury free | Yes
19396 | XVBL6M5 | Offer Sustainability | RoHS exemption information | Yes
19397 | XVBL6M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19398 | XVBL6M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19399 | XVBL6M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19400 | XVBL6M5 | Contractual warranty | Warranty | 18 months
19401 | XVBL6M6 | Main | range of product | Harmony XVB Universal
19402 | XVBL6M6 | Main | product or component type | Complete beacon
19403 | XVBL6M6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19404 | XVBL6M6 | Main | signalling type | Flashing
19405 | XVBL6M6 | Main | mounting diameter | 70 mm
19406 | XVBL6M6 | Main | component name | XVBL
19407 | XVBL6M6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19408 | XVBL6M6 | Main | light source | Integral flash discharge tube, blue
19409 | XVBL6M6 | Main | bulb type | Flash discharge tube
19410 | XVBL6M6 | Main | [Us] rated supply voltage | 230 V AC
19411 | XVBL6M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19412 | XVBL6M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19413 | XVBL6M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19414 | XVBL6M6 | Complementary | current consumption | < 105 mA AC
19415 | XVBL6M6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19416 | XVBL6M6 | Complementary | flash energy | 5 J
19417 | XVBL6M6 | Complementary | flashing frequency | 1 Hz
19418 | XVBL6M6 | Complementary | CAD overall width | 70 mm
19419 | XVBL6M6 | Complementary | CAD overall height | 232 mm
19420 | XVBL6M6 | Complementary | CAD overall depth | 70 mm
19421 | XVBL6M6 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19422 | XVBL6M6 | Complementary | net weight | 0.435 kg
19423 | XVBL6M6 | Environment | product certifications | UL 508 GOST CCC CSA C22-2 No 14
19424 | XVBL6M6 | Environment | standards | EN/IEC 60947-5-1
19425 | XVBL6M6 | Environment | protective treatment | TC
19426 | XVBL6M6 | Environment | ambient air temperature for storage | -40…70 °C
19427 | XVBL6M6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19428 | XVBL6M6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19429 | XVBL6M6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19430 | XVBL6M6 | Packing Units | Package 1 Weight | 435 g
19431 | XVBL6M6 | Offer Sustainability | Sustainable offer status | Green Premium product
19432 | XVBL6M6 | Offer Sustainability | REACh Regulation | REACh Declaration
19433 | XVBL6M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19434 | XVBL6M6 | Offer Sustainability | Mercury free | Yes
19435 | XVBL6M6 | Offer Sustainability | RoHS exemption information | Yes
19436 | XVBL6M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19437 | XVBL6M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19438 | XVBL6M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19439 | XVBL6M6 | Contractual warranty | Warranty | 18 months
19440 | XVBL6M7 | Main | range of product | Harmony XVB Universal
19441 | XVBL6M7 | Main | product or component type | Complete beacon
19442 | XVBL6M7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19443 | XVBL6M7 | Main | signalling type | Flashing
19444 | XVBL6M7 | Main | mounting diameter | 70 mm
19445 | XVBL6M7 | Main | component name | XVBL
19446 | XVBL6M7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19447 | XVBL6M7 | Main | light source | Integral flash discharge tube, clear
19448 | XVBL6M7 | Main | bulb type | Flash discharge tube
19449 | XVBL6M7 | Main | [Us] rated supply voltage | 230 V AC
19450 | XVBL6M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19451 | XVBL6M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19452 | XVBL6M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19453 | XVBL6M7 | Complementary | current consumption | < 105 mA AC
19454 | XVBL6M7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19455 | XVBL6M7 | Complementary | flash energy | 5 J
19456 | XVBL6M7 | Complementary | flashing frequency | 1 Hz
19457 | XVBL6M7 | Complementary | illuminating intensity | 13 cd
19458 | XVBL6M7 | Complementary | CAD overall width | 70 mm
19459 | XVBL6M7 | Complementary | CAD overall height | 232 mm
19460 | XVBL6M7 | Complementary | CAD overall depth | 70 mm
19461 | XVBL6M7 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19462 | XVBL6M7 | Complementary | net weight | 0.435 kg
19463 | XVBL6M7 | Environment | product certifications | GOST UL 508 CSA C22-2 No 14 CCC
19464 | XVBL6M7 | Environment | standards | EN/IEC 60947-5-1
19465 | XVBL6M7 | Environment | protective treatment | TC
19466 | XVBL6M7 | Environment | ambient air temperature for storage | -40…70 °C
19467 | XVBL6M7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19468 | XVBL6M7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19469 | XVBL6M7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19470 | XVBL6M7 | Packing Units | Package 1 Weight | 435 g
19471 | XVBL6M7 | Offer Sustainability | Sustainable offer status | Green Premium product
19472 | XVBL6M7 | Offer Sustainability | REACh Regulation | REACh Declaration
19473 | XVBL6M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19474 | XVBL6M7 | Offer Sustainability | Mercury free | Yes
19475 | XVBL6M7 | Offer Sustainability | RoHS exemption information | Yes
19476 | XVBL6M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19477 | XVBL6M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19478 | XVBL6M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19479 | XVBL6M7 | Contractual warranty | Warranty | 18 months
19480 | XVBL6M8 | Main | range of product | Harmony XVB Universal
19481 | XVBL6M8 | Main | product or component type | Complete beacon
19482 | XVBL6M8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19483 | XVBL6M8 | Main | signalling type | Flashing
19484 | XVBL6M8 | Main | mounting diameter | 70 mm
19485 | XVBL6M8 | Main | component name | XVBL
19486 | XVBL6M8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19487 | XVBL6M8 | Main | light source | Integral flash discharge tube, yellow
19488 | XVBL6M8 | Main | bulb type | Flash discharge tube
19489 | XVBL6M8 | Main | [Us] rated supply voltage | 230 V AC
19490 | XVBL6M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19491 | XVBL6M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19492 | XVBL6M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19493 | XVBL6M8 | Complementary | current consumption | < 105 mA AC
19494 | XVBL6M8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19495 | XVBL6M8 | Complementary | flash energy | 5 J
19496 | XVBL6M8 | Complementary | flashing frequency | 1 Hz
19497 | XVBL6M8 | Complementary | CAD overall width | 70 mm
19498 | XVBL6M8 | Complementary | CAD overall height | 232 mm
19499 | XVBL6M8 | Complementary | CAD overall depth | 70 mm
19500 | XVBL6M8 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19501 | XVBL6M8 | Complementary | net weight | 0.435 kg
19502 | XVBL6M8 | Environment | product certifications | UL 508 GOST CSA C22-2 No 14 CCC
19503 | XVBL6M8 | Environment | standards | EN/IEC 60947-5-1
19504 | XVBL6M8 | Environment | protective treatment | TC
19505 | XVBL6M8 | Environment | ambient air temperature for storage | -40…70 °C
19506 | XVBL6M8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19507 | XVBL6M8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19508 | XVBL6M8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19509 | XVBL6M8 | Packing Units | Package 1 Weight | 435 g
19510 | XVBL6M8 | Offer Sustainability | Sustainable offer status | Green Premium product
19511 | XVBL6M8 | Offer Sustainability | REACh Regulation | REACh Declaration
19512 | XVBL6M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19513 | XVBL6M8 | Offer Sustainability | Mercury free | Yes
19514 | XVBL6M8 | Offer Sustainability | RoHS exemption information | Yes
19515 | XVBL6M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19516 | XVBL6M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19517 | XVBL6M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19518 | XVBL6M8 | Contractual warranty | Warranty | 18 months
19519 | XVBL8B3 | Main | range of product | Harmony XVB Universal
19520 | XVBL8B3 | Main | product or component type | Complete beacon
19521 | XVBL8B3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19522 | XVBL8B3 | Main | signalling type | Flashing
19523 | XVBL8B3 | Main | mounting diameter | 70 mm
19524 | XVBL8B3 | Main | component name | XVBL
19525 | XVBL8B3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19526 | XVBL8B3 | Main | light source | Integral flash discharge tube, green
19527 | XVBL8B3 | Main | bulb type | Flash discharge tube
19528 | XVBL8B3 | Main | [Us] rated supply voltage | 24 V AC/DC
19529 | XVBL8B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19530 | XVBL8B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19531 | XVBL8B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19532 | XVBL8B3 | Complementary | current consumption | < 1300 mA AC < 850 mA DC
19533 | XVBL8B3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19534 | XVBL8B3 | Complementary | flash energy | 10 J
19535 | XVBL8B3 | Complementary | flashing frequency | 1 Hz
19536 | XVBL8B3 | Complementary | CAD overall width | 70 mm
19537 | XVBL8B3 | Complementary | CAD overall height | 232 mm
19538 | XVBL8B3 | Complementary | CAD overall depth | 70 mm
19539 | XVBL8B3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19540 | XVBL8B3 | Complementary | net weight | 0.45 kg
19541 | XVBL8B3 | Environment | product certifications | UL 508 CSA C22-2 No 14 GOST CCC
19542 | XVBL8B3 | Environment | standards | EN/IEC 60947-5-1
19543 | XVBL8B3 | Environment | protective treatment | TC
19544 | XVBL8B3 | Environment | ambient air temperature for storage | -40…70 °C
19545 | XVBL8B3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19546 | XVBL8B3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19547 | XVBL8B3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19548 | XVBL8B3 | Packing Units | Package 1 Weight | 450 g
19549 | XVBL8B3 | Offer Sustainability | Sustainable offer status | Green Premium product
19550 | XVBL8B3 | Offer Sustainability | REACh Regulation | REACh Declaration
19551 | XVBL8B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19552 | XVBL8B3 | Offer Sustainability | Mercury free | Yes
19553 | XVBL8B3 | Offer Sustainability | RoHS exemption information | Yes
19554 | XVBL8B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19555 | XVBL8B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19556 | XVBL8B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19557 | XVBL8B3 | Contractual warranty | Warranty | 18 months
19558 | XVBL8B4 | Main | range of product | Harmony XVB Universal
19559 | XVBL8B4 | Main | product or component type | Complete beacon
19560 | XVBL8B4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19561 | XVBL8B4 | Main | signalling type | Flashing
19562 | XVBL8B4 | Main | mounting diameter | 70 mm
19563 | XVBL8B4 | Main | component name | XVBL
19564 | XVBL8B4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19565 | XVBL8B4 | Main | light source | Integral flash discharge tube, red
19566 | XVBL8B4 | Main | bulb type | Flash discharge tube
19567 | XVBL8B4 | Main | [Us] rated supply voltage | 24 V AC/DC
19568 | XVBL8B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19569 | XVBL8B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19570 | XVBL8B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19571 | XVBL8B4 | Complementary | current consumption | < 1300 mA AC < 850 mA DC
19572 | XVBL8B4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19573 | XVBL8B4 | Complementary | flash energy | 10 J
19574 | XVBL8B4 | Complementary | flashing frequency | 1 Hz
19575 | XVBL8B4 | Complementary | CAD overall width | 70 mm
19576 | XVBL8B4 | Complementary | CAD overall height | 232 mm
19577 | XVBL8B4 | Complementary | CAD overall depth | 70 mm
19578 | XVBL8B4 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19579 | XVBL8B4 | Complementary | net weight | 0.45 kg
19580 | XVBL8B4 | Environment | product certifications | UL 508 CCC CSA C22-2 No 14 GOST
19581 | XVBL8B4 | Environment | standards | EN/IEC 60947-5-1
19582 | XVBL8B4 | Environment | protective treatment | TC
19583 | XVBL8B4 | Environment | ambient air temperature for storage | -40…70 °C
19584 | XVBL8B4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19585 | XVBL8B4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19586 | XVBL8B4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19587 | XVBL8B4 | Packing Units | Package 1 Weight | 464 g
19588 | XVBL8B4 | Packing Units | Package 2 Weight | 5.976 kg
19589 | XVBL8B4 | Offer Sustainability | Sustainable offer status | Green Premium product
19590 | XVBL8B4 | Offer Sustainability | REACh Regulation | REACh Declaration
19591 | XVBL8B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19592 | XVBL8B4 | Offer Sustainability | Mercury free | Yes
19593 | XVBL8B4 | Offer Sustainability | RoHS exemption information | Yes
19594 | XVBL8B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19595 | XVBL8B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19596 | XVBL8B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19597 | XVBL8B4 | Contractual warranty | Warranty | 18 months
19598 | XVBL8B5 | Main | range of product | Harmony XVB Universal
19599 | XVBL8B5 | Main | product or component type | Complete beacon
19600 | XVBL8B5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19601 | XVBL8B5 | Main | signalling type | Flashing
19602 | XVBL8B5 | Main | mounting diameter | 70 mm
19603 | XVBL8B5 | Main | component name | XVBL
19604 | XVBL8B5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19605 | XVBL8B5 | Main | light source | Integral flash discharge tube, orange
19606 | XVBL8B5 | Main | bulb type | Flash discharge tube
19607 | XVBL8B5 | Main | [Us] rated supply voltage | 24 V AC/DC
19608 | XVBL8B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19609 | XVBL8B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19610 | XVBL8B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19611 | XVBL8B5 | Complementary | current consumption | < 1300 mA AC < 850 mA DC
19612 | XVBL8B5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19613 | XVBL8B5 | Complementary | flash energy | 10 J
19614 | XVBL8B5 | Complementary | flashing frequency | 1 Hz
19615 | XVBL8B5 | Complementary | CAD overall width | 70 mm
19616 | XVBL8B5 | Complementary | CAD overall height | 232 mm
19617 | XVBL8B5 | Complementary | CAD overall depth | 70 mm
19618 | XVBL8B5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19619 | XVBL8B5 | Complementary | net weight | 0.45 kg
19620 | XVBL8B5 | Environment | product certifications | UL 508 CCC CSA C22-2 No 14 GOST
19621 | XVBL8B5 | Environment | standards | EN/IEC 60947-5-1
19622 | XVBL8B5 | Environment | protective treatment | TC
19623 | XVBL8B5 | Environment | ambient air temperature for storage | -40…70 °C
19624 | XVBL8B5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19625 | XVBL8B5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19626 | XVBL8B5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19627 | XVBL8B5 | Packing Units | Package 1 Weight | 466 g
19628 | XVBL8B5 | Packing Units | Package 2 Weight | 6.025 kg
19629 | XVBL8B5 | Offer Sustainability | Sustainable offer status | Green Premium product
19630 | XVBL8B5 | Offer Sustainability | REACh Regulation | REACh Declaration
19631 | XVBL8B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19632 | XVBL8B5 | Offer Sustainability | Mercury free | Yes
19633 | XVBL8B5 | Offer Sustainability | RoHS exemption information | Yes
19634 | XVBL8B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19635 | XVBL8B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19636 | XVBL8B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19637 | XVBL8B5 | Contractual warranty | Warranty | 18 months
19638 | XVBL8B6 | Main | range of product | Harmony XVB Universal
19639 | XVBL8B6 | Main | product or component type | Complete beacon
19640 | XVBL8B6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19641 | XVBL8B6 | Main | signalling type | Flashing
19642 | XVBL8B6 | Main | mounting diameter | 70 mm
19643 | XVBL8B6 | Main | component name | XVBL
19644 | XVBL8B6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19645 | XVBL8B6 | Main | light source | Integral flash discharge tube, blue
19646 | XVBL8B6 | Main | bulb type | Flash discharge tube
19647 | XVBL8B6 | Main | [Us] rated supply voltage | 24 V AC/DC
19648 | XVBL8B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19649 | XVBL8B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19650 | XVBL8B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19651 | XVBL8B6 | Complementary | current consumption | < 1300 mA AC < 850 mA DC
19652 | XVBL8B6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19653 | XVBL8B6 | Complementary | flash energy | 10 J
19654 | XVBL8B6 | Complementary | flashing frequency | 1 Hz
19655 | XVBL8B6 | Complementary | CAD overall width | 70 mm
19656 | XVBL8B6 | Complementary | CAD overall height | 232 mm
19657 | XVBL8B6 | Complementary | CAD overall depth | 70 mm
19658 | XVBL8B6 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19659 | XVBL8B6 | Complementary | net weight | 0.45 kg
19660 | XVBL8B6 | Environment | product certifications | CSA C22-2 No 14 UL 508 CCC GOST
19661 | XVBL8B6 | Environment | standards | EN/IEC 60947-5-1
19662 | XVBL8B6 | Environment | protective treatment | TC
19663 | XVBL8B6 | Environment | ambient air temperature for storage | -40…70 °C
19664 | XVBL8B6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19665 | XVBL8B6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19666 | XVBL8B6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19667 | XVBL8B6 | Packing Units | Package 1 Weight | 450 g
19668 | XVBL8B6 | Offer Sustainability | Sustainable offer status | Green Premium product
19669 | XVBL8B6 | Offer Sustainability | REACh Regulation | REACh Declaration
19670 | XVBL8B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19671 | XVBL8B6 | Offer Sustainability | Mercury free | Yes
19672 | XVBL8B6 | Offer Sustainability | RoHS exemption information | Yes
19673 | XVBL8B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19674 | XVBL8B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19675 | XVBL8B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19676 | XVBL8B6 | Contractual warranty | Warranty | 18 months
19677 | XVBL8B7 | Main | range of product | Harmony XVB Universal
19678 | XVBL8B7 | Main | product or component type | Complete beacon
19679 | XVBL8B7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19680 | XVBL8B7 | Main | signalling type | Flashing
19681 | XVBL8B7 | Main | mounting diameter | 70 mm
19682 | XVBL8B7 | Main | component name | XVBL
19683 | XVBL8B7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19684 | XVBL8B7 | Main | light source | Integral flash discharge tube, clear
19685 | XVBL8B7 | Main | bulb type | Flash discharge tube
19686 | XVBL8B7 | Main | [Us] rated supply voltage | 24 V AC/DC
19687 | XVBL8B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19688 | XVBL8B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19689 | XVBL8B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19690 | XVBL8B7 | Complementary | current consumption | < 1300 mA AC < 850 mA DC
19691 | XVBL8B7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19692 | XVBL8B7 | Complementary | flash energy | 10 J
19693 | XVBL8B7 | Complementary | flashing frequency | 1 Hz
19694 | XVBL8B7 | Complementary | illuminating intensity | 26 cd
19695 | XVBL8B7 | Complementary | CAD overall width | 70 mm
19696 | XVBL8B7 | Complementary | CAD overall height | 232 mm
19697 | XVBL8B7 | Complementary | CAD overall depth | 70 mm
19698 | XVBL8B7 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
19699 | XVBL8B7 | Complementary | net weight | 0.45 kg
19700 | XVBL8B7 | Environment | product certifications | GOST CCC UL 508 CSA C22-2 No 14
19701 | XVBL8B7 | Environment | standards | EN/IEC 60947-5-1
19702 | XVBL8B7 | Environment | protective treatment | TC
19703 | XVBL8B7 | Environment | ambient air temperature for storage | -40…70 °C
19704 | XVBL8B7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19705 | XVBL8B7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19706 | XVBL8B7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19707 | XVBL8B7 | Packing Units | Package 1 Weight | 450 g
19708 | XVBL8B7 | Offer Sustainability | Sustainable offer status | Green Premium product
19709 | XVBL8B7 | Offer Sustainability | REACh Regulation | REACh Declaration
19710 | XVBL8B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19711 | XVBL8B7 | Offer Sustainability | Mercury free | Yes
19712 | XVBL8B7 | Offer Sustainability | RoHS exemption information | Yes
19713 | XVBL8B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19714 | XVBL8B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19715 | XVBL8B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19716 | XVBL8B7 | Contractual warranty | Warranty | 18 months
19717 | XVBL8B8 | Main | range of product | Harmony XVB Universal
19718 | XVBL8B8 | Main | product or component type | Complete beacon
19719 | XVBL8B8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19720 | XVBL8B8 | Main | signalling type | Flashing
19721 | XVBL8B8 | Main | mounting diameter | 70 mm
19722 | XVBL8B8 | Main | component name | XVBL
19723 | XVBL8B8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19724 | XVBL8B8 | Main | light source | Integral flash discharge tube, yellow
19725 | XVBL8B8 | Main | bulb type | Flash discharge tube
19726 | XVBL8B8 | Main | [Us] rated supply voltage | 24 V AC/DC
19727 | XVBL8B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19728 | XVBL8B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19729 | XVBL8B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19730 | XVBL8B8 | Complementary | current consumption | < 1300 mA AC < 850 mA DC
19731 | XVBL8B8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19732 | XVBL8B8 | Complementary | flash energy | 10 J
19733 | XVBL8B8 | Complementary | flashing frequency | 1 Hz
19734 | XVBL8B8 | Complementary | CAD overall width | 70 mm
19735 | XVBL8B8 | Complementary | CAD overall height | 232 mm
19736 | XVBL8B8 | Complementary | CAD overall depth | 70 mm
19737 | XVBL8B8 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19738 | XVBL8B8 | Complementary | net weight | 0.45 kg
19739 | XVBL8B8 | Environment | product certifications | GOST CSA C22-2 No 14 UL 508 CCC
19740 | XVBL8B8 | Environment | standards | EN/IEC 60947-5-1
19741 | XVBL8B8 | Environment | protective treatment | TC
19742 | XVBL8B8 | Environment | ambient air temperature for storage | -40…70 °C
19743 | XVBL8B8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19744 | XVBL8B8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19745 | XVBL8B8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19746 | XVBL8B8 | Packing Units | Package 1 Weight | 450 g
19747 | XVBL8B8 | Offer Sustainability | Sustainable offer status | Green Premium product
19748 | XVBL8B8 | Offer Sustainability | REACh Regulation | REACh Declaration
19749 | XVBL8B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19750 | XVBL8B8 | Offer Sustainability | Mercury free | Yes
19751 | XVBL8B8 | Offer Sustainability | RoHS exemption information | Yes
19752 | XVBL8B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19753 | XVBL8B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19754 | XVBL8B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19755 | XVBL8B8 | Contractual warranty | Warranty | 18 months
19756 | XVBL8G3 | Main | range of product | Harmony XVB Universal
19757 | XVBL8G3 | Main | product or component type | Complete beacon
19758 | XVBL8G3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19759 | XVBL8G3 | Main | signalling type | Flashing
19760 | XVBL8G3 | Main | mounting diameter | 70 mm
19761 | XVBL8G3 | Main | component name | XVBL
19762 | XVBL8G3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19763 | XVBL8G3 | Main | light source | Integral flash discharge tube, green
19764 | XVBL8G3 | Main | bulb type | Flash discharge tube
19765 | XVBL8G3 | Main | [Us] rated supply voltage | 120 V AC
19766 | XVBL8G3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19767 | XVBL8G3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19768 | XVBL8G3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19769 | XVBL8G3 | Complementary | current consumption | < 290 mA AC
19770 | XVBL8G3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19771 | XVBL8G3 | Complementary | flash energy | 10 J
19772 | XVBL8G3 | Complementary | flashing frequency | 1 Hz
19773 | XVBL8G3 | Complementary | CAD overall width | 70 mm
19774 | XVBL8G3 | Complementary | CAD overall height | 232 mm
19775 | XVBL8G3 | Complementary | CAD overall depth | 70 mm
19776 | XVBL8G3 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19777 | XVBL8G3 | Complementary | net weight | 0.46 kg
19778 | XVBL8G3 | Environment | product certifications | GOST CSA C22-2 No 14 CCC UL 508
19779 | XVBL8G3 | Environment | standards | EN/IEC 60947-5-1
19780 | XVBL8G3 | Environment | protective treatment | TC
19781 | XVBL8G3 | Environment | ambient air temperature for storage | -40…70 °C
19782 | XVBL8G3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19783 | XVBL8G3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19784 | XVBL8G3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19785 | XVBL8G3 | Packing Units | Package 1 Weight | 460 g
19786 | XVBL8G3 | Offer Sustainability | Sustainable offer status | Green Premium product
19787 | XVBL8G3 | Offer Sustainability | REACh Regulation | REACh Declaration
19788 | XVBL8G3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19789 | XVBL8G3 | Offer Sustainability | Mercury free | Yes
19790 | XVBL8G3 | Offer Sustainability | RoHS exemption information | Yes
19791 | XVBL8G3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19792 | XVBL8G3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19793 | XVBL8G3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19794 | XVBL8G3 | Contractual warranty | Warranty | 18 months
19795 | XVBL8G4 | Main | range of product | Harmony XVB Universal
19796 | XVBL8G4 | Main | product or component type | Complete beacon
19797 | XVBL8G4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19798 | XVBL8G4 | Main | signalling type | Flashing
19799 | XVBL8G4 | Main | mounting diameter | 70 mm
19800 | XVBL8G4 | Main | component name | XVBL
19801 | XVBL8G4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19802 | XVBL8G4 | Main | light source | Integral flash discharge tube, red
19803 | XVBL8G4 | Main | bulb type | Flash discharge tube
19804 | XVBL8G4 | Main | [Us] rated supply voltage | 120 V AC
19805 | XVBL8G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19806 | XVBL8G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19807 | XVBL8G4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19808 | XVBL8G4 | Complementary | current consumption | < 290 mA AC
19809 | XVBL8G4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19810 | XVBL8G4 | Complementary | flash energy | 10 J
19811 | XVBL8G4 | Complementary | flashing frequency | 1 Hz
19812 | XVBL8G4 | Complementary | CAD overall width | 70 mm
19813 | XVBL8G4 | Complementary | CAD overall height | 232 mm
19814 | XVBL8G4 | Complementary | CAD overall depth | 70 mm
19815 | XVBL8G4 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19816 | XVBL8G4 | Complementary | net weight | 0.46 kg
19817 | XVBL8G4 | Environment | product certifications | CCC UL 508 GOST CSA C22-2 No 14
19818 | XVBL8G4 | Environment | standards | EN/IEC 60947-5-1
19819 | XVBL8G4 | Environment | protective treatment | TC
19820 | XVBL8G4 | Environment | ambient air temperature for storage | -40…70 °C
19821 | XVBL8G4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19822 | XVBL8G4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19823 | XVBL8G4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19824 | XVBL8G4 | Packing Units | Package 1 Weight | 460 g
19825 | XVBL8G4 | Offer Sustainability | Sustainable offer status | Green Premium product
19826 | XVBL8G4 | Offer Sustainability | REACh Regulation | REACh Declaration
19827 | XVBL8G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19828 | XVBL8G4 | Offer Sustainability | Mercury free | Yes
19829 | XVBL8G4 | Offer Sustainability | RoHS exemption information | Yes
19830 | XVBL8G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19831 | XVBL8G4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19832 | XVBL8G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19833 | XVBL8G4 | Contractual warranty | Warranty | 18 months
19834 | XVBL8G5 | Main | range of product | Harmony XVB Universal
19835 | XVBL8G5 | Main | product or component type | Complete beacon
19836 | XVBL8G5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19837 | XVBL8G5 | Main | signalling type | Flashing
19838 | XVBL8G5 | Main | mounting diameter | 70 mm
19839 | XVBL8G5 | Main | component name | XVBL
19840 | XVBL8G5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19841 | XVBL8G5 | Main | light source | Integral flash discharge tube, orange
19842 | XVBL8G5 | Main | bulb type | Flash discharge tube
19843 | XVBL8G5 | Main | [Us] rated supply voltage | 120 V AC
19844 | XVBL8G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19845 | XVBL8G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19846 | XVBL8G5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19847 | XVBL8G5 | Complementary | current consumption | < 290 mA AC
19848 | XVBL8G5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19849 | XVBL8G5 | Complementary | flash energy | 10 J
19850 | XVBL8G5 | Complementary | flashing frequency | 1 Hz
19851 | XVBL8G5 | Complementary | CAD overall width | 70 mm
19852 | XVBL8G5 | Complementary | CAD overall height | 232 mm
19853 | XVBL8G5 | Complementary | CAD overall depth | 70 mm
19854 | XVBL8G5 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
19855 | XVBL8G5 | Complementary | net weight | 0.46 kg
19856 | XVBL8G5 | Environment | product certifications | CSA C22-2 No 14 GOST UL 508 CCC
19857 | XVBL8G5 | Environment | standards | EN/IEC 60947-5-1
19858 | XVBL8G5 | Environment | protective treatment | TC
19859 | XVBL8G5 | Environment | ambient air temperature for storage | -40…70 °C
19860 | XVBL8G5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19861 | XVBL8G5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19862 | XVBL8G5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19863 | XVBL8G5 | Packing Units | Package 1 Weight | 460 g
19864 | XVBL8G5 | Offer Sustainability | Sustainable offer status | Green Premium product
19865 | XVBL8G5 | Offer Sustainability | REACh Regulation | REACh Declaration
19866 | XVBL8G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19867 | XVBL8G5 | Offer Sustainability | Mercury free | Yes
19868 | XVBL8G5 | Offer Sustainability | RoHS exemption information | Yes
19869 | XVBL8G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19870 | XVBL8G5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19871 | XVBL8G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19872 | XVBL8G5 | Contractual warranty | Warranty | 18 months
19873 | XVBL8G6 | Main | range of product | Harmony XVB Universal
19874 | XVBL8G6 | Main | product or component type | Complete beacon
19875 | XVBL8G6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19876 | XVBL8G6 | Main | signalling type | Flashing
19877 | XVBL8G6 | Main | mounting diameter | 70 mm
19878 | XVBL8G6 | Main | component name | XVBL
19879 | XVBL8G6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19880 | XVBL8G6 | Main | light source | Integral flash discharge tube, blue
19881 | XVBL8G6 | Main | bulb type | Flash discharge tube
19882 | XVBL8G6 | Main | [Us] rated supply voltage | 120 V AC
19883 | XVBL8G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19884 | XVBL8G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19885 | XVBL8G6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19886 | XVBL8G6 | Complementary | current consumption | < 290 mA AC
19887 | XVBL8G6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19888 | XVBL8G6 | Complementary | flash energy | 10 J
19889 | XVBL8G6 | Complementary | flashing frequency | 1 Hz
19890 | XVBL8G6 | Complementary | CAD overall width | 70 mm
19891 | XVBL8G6 | Complementary | CAD overall height | 232 mm
19892 | XVBL8G6 | Complementary | CAD overall depth | 70 mm
19893 | XVBL8G6 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
19894 | XVBL8G6 | Complementary | net weight | 0.46 kg
19895 | XVBL8G6 | Environment | product certifications | CSA C22-2 No 14 CCC UL 508 GOST
19896 | XVBL8G6 | Environment | standards | EN/IEC 60947-5-1
19897 | XVBL8G6 | Environment | protective treatment | TC
19898 | XVBL8G6 | Environment | ambient air temperature for storage | -40…70 °C
19899 | XVBL8G6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19900 | XVBL8G6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19901 | XVBL8G6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19902 | XVBL8G6 | Packing Units | Package 1 Weight | 460 g
19903 | XVBL8G6 | Offer Sustainability | Sustainable offer status | Green Premium product
19904 | XVBL8G6 | Offer Sustainability | REACh Regulation | REACh Declaration
19905 | XVBL8G6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19906 | XVBL8G6 | Offer Sustainability | Mercury free | Yes
19907 | XVBL8G6 | Offer Sustainability | RoHS exemption information | Yes
19908 | XVBL8G6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19909 | XVBL8G6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19910 | XVBL8G6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19911 | XVBL8G6 | Contractual warranty | Warranty | 18 months
19912 | XVBL8G7 | Main | range of product | Harmony XVB Universal
19913 | XVBL8G7 | Main | product or component type | Complete beacon
19914 | XVBL8G7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19915 | XVBL8G7 | Main | signalling type | Flashing
19916 | XVBL8G7 | Main | mounting diameter | 70 mm
19917 | XVBL8G7 | Main | component name | XVBL
19918 | XVBL8G7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19919 | XVBL8G7 | Main | light source | Integral flash discharge tube, clear
19920 | XVBL8G7 | Main | bulb type | Flash discharge tube
19921 | XVBL8G7 | Main | [Us] rated supply voltage | 120 V AC
19922 | XVBL8G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19923 | XVBL8G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19924 | XVBL8G7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19925 | XVBL8G7 | Complementary | current consumption | < 290 mA AC
19926 | XVBL8G7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19927 | XVBL8G7 | Complementary | flash energy | 10 J
19928 | XVBL8G7 | Complementary | flashing frequency | 1 Hz
19929 | XVBL8G7 | Complementary | illuminating intensity | 26 cd
19930 | XVBL8G7 | Complementary | CAD overall width | 70 mm
19931 | XVBL8G7 | Complementary | CAD overall height | 232 mm
19932 | XVBL8G7 | Complementary | CAD overall depth | 70 mm
19933 | XVBL8G7 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
19934 | XVBL8G7 | Complementary | net weight | 0.46 kg
19935 | XVBL8G7 | Environment | product certifications | CCC UL 508 GOST CSA C22-2 No 14
19936 | XVBL8G7 | Environment | standards | EN/IEC 60947-5-1
19937 | XVBL8G7 | Environment | protective treatment | TC
19938 | XVBL8G7 | Environment | ambient air temperature for storage | -40…70 °C
19939 | XVBL8G7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19940 | XVBL8G7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19941 | XVBL8G7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19942 | XVBL8G7 | Packing Units | Package 1 Weight | 460 g
19943 | XVBL8G7 | Offer Sustainability | Sustainable offer status | Green Premium product
19944 | XVBL8G7 | Offer Sustainability | REACh Regulation | REACh Declaration
19945 | XVBL8G7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19946 | XVBL8G7 | Offer Sustainability | Mercury free | Yes
19947 | XVBL8G7 | Offer Sustainability | RoHS exemption information | Yes
19948 | XVBL8G7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19949 | XVBL8G7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19950 | XVBL8G7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19951 | XVBL8G7 | Contractual warranty | Warranty | 18 months
19952 | XVBL8G8 | Main | range of product | Harmony XVB Universal
19953 | XVBL8G8 | Main | product or component type | Complete beacon
19954 | XVBL8G8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19955 | XVBL8G8 | Main | signalling type | Flashing
19956 | XVBL8G8 | Main | mounting diameter | 70 mm
19957 | XVBL8G8 | Main | component name | XVBL
19958 | XVBL8G8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19959 | XVBL8G8 | Main | light source | Integral flash discharge tube, yellow
19960 | XVBL8G8 | Main | bulb type | Flash discharge tube
19961 | XVBL8G8 | Main | [Us] rated supply voltage | 120 V AC
19962 | XVBL8G8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
19963 | XVBL8G8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
19964 | XVBL8G8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
19965 | XVBL8G8 | Complementary | current consumption | < 290 mA AC
19966 | XVBL8G8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
19967 | XVBL8G8 | Complementary | flash energy | 10 J
19968 | XVBL8G8 | Complementary | flashing frequency | 1 Hz
19969 | XVBL8G8 | Complementary | CAD overall width | 70 mm
19970 | XVBL8G8 | Complementary | CAD overall height | 232 mm
19971 | XVBL8G8 | Complementary | CAD overall depth | 70 mm
19972 | XVBL8G8 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
19973 | XVBL8G8 | Complementary | net weight | 0.46 kg
19974 | XVBL8G8 | Environment | product certifications | GOST CSA C22-2 No 14 CCC UL 508
19975 | XVBL8G8 | Environment | standards | EN/IEC 60947-5-1
19976 | XVBL8G8 | Environment | protective treatment | TC
19977 | XVBL8G8 | Environment | ambient air temperature for storage | -40…70 °C
19978 | XVBL8G8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
19979 | XVBL8G8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
19980 | XVBL8G8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
19981 | XVBL8G8 | Packing Units | Package 1 Weight | 460 g
19982 | XVBL8G8 | Offer Sustainability | Sustainable offer status | Green Premium product
19983 | XVBL8G8 | Offer Sustainability | REACh Regulation | REACh Declaration
19984 | XVBL8G8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
19985 | XVBL8G8 | Offer Sustainability | Mercury free | Yes
19986 | XVBL8G8 | Offer Sustainability | RoHS exemption information | Yes
19987 | XVBL8G8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
19988 | XVBL8G8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
19989 | XVBL8G8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
19990 | XVBL8G8 | Contractual warranty | Warranty | 18 months
19991 | XVBL8M3 | Main | range of product | Harmony XVB Universal
19992 | XVBL8M3 | Main | product or component type | Complete beacon
19993 | XVBL8M3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
19994 | XVBL8M3 | Main | signalling type | Flashing
19995 | XVBL8M3 | Main | mounting diameter | 70 mm
19996 | XVBL8M3 | Main | component name | XVBL
19997 | XVBL8M3 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
19998 | XVBL8M3 | Main | light source | Integral flash discharge tube, green
19999 | XVBL8M3 | Main | bulb type | Flash discharge tube
20000 | XVBL8M3 | Main | [Us] rated supply voltage | 230 V AC
20001 | XVBL8M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20002 | XVBL8M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20003 | XVBL8M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20004 | XVBL8M3 | Complementary | current consumption | < 280 mA AC
20005 | XVBL8M3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20006 | XVBL8M3 | Complementary | flash energy | 10 J
20007 | XVBL8M3 | Complementary | flashing frequency | 1 Hz
20008 | XVBL8M3 | Complementary | CAD overall width | 70 mm
20009 | XVBL8M3 | Complementary | CAD overall height | 232 mm
20010 | XVBL8M3 | Complementary | CAD overall depth | 70 mm
20011 | XVBL8M3 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
20012 | XVBL8M3 | Complementary | net weight | 0.46 kg
20013 | XVBL8M3 | Environment | product certifications | GOST UL 508 CCC CSA C22-2 No 14
20014 | XVBL8M3 | Environment | standards | EN/IEC 60947-5-1
20015 | XVBL8M3 | Environment | protective treatment | TC
20016 | XVBL8M3 | Environment | ambient air temperature for storage | -40…70 °C
20017 | XVBL8M3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20018 | XVBL8M3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20019 | XVBL8M3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20020 | XVBL8M3 | Packing Units | Package 1 Weight | 460 g
20021 | XVBL8M3 | Offer Sustainability | Sustainable offer status | Green Premium product
20022 | XVBL8M3 | Offer Sustainability | REACh Regulation | REACh Declaration
20023 | XVBL8M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20024 | XVBL8M3 | Offer Sustainability | Mercury free | Yes
20025 | XVBL8M3 | Offer Sustainability | RoHS exemption information | Yes
20026 | XVBL8M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20027 | XVBL8M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20028 | XVBL8M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20029 | XVBL8M3 | Contractual warranty | Warranty | 18 months
20030 | XVBL8M4 | Main | range of product | Harmony XVB Universal
20031 | XVBL8M4 | Main | product or component type | Complete beacon
20032 | XVBL8M4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
20033 | XVBL8M4 | Main | signalling type | Flashing
20034 | XVBL8M4 | Main | mounting diameter | 70 mm
20035 | XVBL8M4 | Main | component name | XVBL
20036 | XVBL8M4 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
20037 | XVBL8M4 | Main | light source | Integral flash discharge tube, red
20038 | XVBL8M4 | Main | bulb type | Flash discharge tube
20039 | XVBL8M4 | Main | [Us] rated supply voltage | 230 V AC
20040 | XVBL8M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20041 | XVBL8M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20042 | XVBL8M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20043 | XVBL8M4 | Complementary | current consumption | < 280 mA AC
20044 | XVBL8M4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20045 | XVBL8M4 | Complementary | flash energy | 10 J
20046 | XVBL8M4 | Complementary | flashing frequency | 1 Hz
20047 | XVBL8M4 | Complementary | CAD overall width | 70 mm
20048 | XVBL8M4 | Complementary | CAD overall height | 232 mm
20049 | XVBL8M4 | Complementary | CAD overall depth | 70 mm
20050 | XVBL8M4 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
20051 | XVBL8M4 | Complementary | net weight | 0.46 kg
20052 | XVBL8M4 | Environment | product certifications | GOST UL 508 CCC CSA C22-2 No 14
20053 | XVBL8M4 | Environment | standards | EN/IEC 60947-5-1
20054 | XVBL8M4 | Environment | protective treatment | TC
20055 | XVBL8M4 | Environment | ambient air temperature for storage | -40…70 °C
20056 | XVBL8M4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20057 | XVBL8M4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20058 | XVBL8M4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20059 | XVBL8M4 | Packing Units | Package 1 Weight | 480 g
20060 | XVBL8M4 | Packing Units | Package 2 Weight | 6.176 kg
20061 | XVBL8M4 | Offer Sustainability | Sustainable offer status | Green Premium product
20062 | XVBL8M4 | Offer Sustainability | REACh Regulation | REACh Declaration
20063 | XVBL8M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20064 | XVBL8M4 | Offer Sustainability | Mercury free | Yes
20065 | XVBL8M4 | Offer Sustainability | RoHS exemption information | Yes
20066 | XVBL8M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20067 | XVBL8M4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20068 | XVBL8M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20069 | XVBL8M4 | Contractual warranty | Warranty | 18 months
20070 | XVBL8M5 | Main | range of product | Harmony XVB Universal
20071 | XVBL8M5 | Main | product or component type | Complete beacon
20072 | XVBL8M5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
20073 | XVBL8M5 | Main | signalling type | Flashing
20074 | XVBL8M5 | Main | mounting diameter | 70 mm
20075 | XVBL8M5 | Main | component name | XVBL
20076 | XVBL8M5 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
20077 | XVBL8M5 | Main | light source | Integral flash discharge tube, orange
20078 | XVBL8M5 | Main | bulb type | Flash discharge tube
20079 | XVBL8M5 | Main | [Us] rated supply voltage | 230 V AC
20080 | XVBL8M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20081 | XVBL8M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20082 | XVBL8M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20083 | XVBL8M5 | Complementary | current consumption | < 280 mA AC
20084 | XVBL8M5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20085 | XVBL8M5 | Complementary | flash energy | 10 J
20086 | XVBL8M5 | Complementary | flashing frequency | 1 Hz
20087 | XVBL8M5 | Complementary | CAD overall width | 70 mm
20088 | XVBL8M5 | Complementary | CAD overall height | 232 mm
20089 | XVBL8M5 | Complementary | CAD overall depth | 70 mm
20090 | XVBL8M5 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
20091 | XVBL8M5 | Complementary | net weight | 0.46 kg
20092 | XVBL8M5 | Environment | product certifications | CSA C22-2 No 14 UL 508 GOST CCC
20093 | XVBL8M5 | Environment | standards | EN/IEC 60947-5-1
20094 | XVBL8M5 | Environment | protective treatment | TC
20095 | XVBL8M5 | Environment | ambient air temperature for storage | -40…70 °C
20096 | XVBL8M5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20097 | XVBL8M5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20098 | XVBL8M5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20099 | XVBL8M5 | Packing Units | Package 1 Weight | 0.473 kg
20100 | XVBL8M5 | Offer Sustainability | Sustainable offer status | Green Premium product
20101 | XVBL8M5 | Offer Sustainability | REACh Regulation | REACh Declaration
20102 | XVBL8M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20103 | XVBL8M5 | Offer Sustainability | Mercury free | Yes
20104 | XVBL8M5 | Offer Sustainability | RoHS exemption information | Yes
20105 | XVBL8M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20106 | XVBL8M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20107 | XVBL8M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20108 | XVBL8M5 | Contractual warranty | Warranty | 18 months
20109 | XVBL8M6 | Main | range of product | Harmony XVB Universal
20110 | XVBL8M6 | Main | product or component type | Complete beacon
20111 | XVBL8M6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
20112 | XVBL8M6 | Main | signalling type | Flashing
20113 | XVBL8M6 | Main | mounting diameter | 70 mm
20114 | XVBL8M6 | Main | component name | XVBL
20115 | XVBL8M6 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
20116 | XVBL8M6 | Main | light source | Integral flash discharge tube, blue
20117 | XVBL8M6 | Main | bulb type | Flash discharge tube
20118 | XVBL8M6 | Main | [Us] rated supply voltage | 230 V AC
20119 | XVBL8M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20120 | XVBL8M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20121 | XVBL8M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20122 | XVBL8M6 | Complementary | current consumption | < 280 mA AC
20123 | XVBL8M6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20124 | XVBL8M6 | Complementary | flash energy | 10 J
20125 | XVBL8M6 | Complementary | flashing frequency | 1 Hz
20126 | XVBL8M6 | Complementary | CAD overall width | 70 mm
20127 | XVBL8M6 | Complementary | CAD overall height | 232 mm
20128 | XVBL8M6 | Complementary | CAD overall depth | 70 mm
20129 | XVBL8M6 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
20130 | XVBL8M6 | Complementary | net weight | 0.46 kg
20131 | XVBL8M6 | Environment | product certifications | GOST UL 508 CSA C22-2 No 14 CCC
20132 | XVBL8M6 | Environment | standards | EN/IEC 60947-5-1
20133 | XVBL8M6 | Environment | protective treatment | TC
20134 | XVBL8M6 | Environment | ambient air temperature for storage | -40…70 °C
20135 | XVBL8M6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20136 | XVBL8M6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20137 | XVBL8M6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20138 | XVBL8M6 | Packing Units | Package 1 Weight | 460 g
20139 | XVBL8M6 | Offer Sustainability | Sustainable offer status | Green Premium product
20140 | XVBL8M6 | Offer Sustainability | REACh Regulation | REACh Declaration
20141 | XVBL8M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20142 | XVBL8M6 | Offer Sustainability | Mercury free | Yes
20143 | XVBL8M6 | Offer Sustainability | RoHS exemption information | Yes
20144 | XVBL8M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20145 | XVBL8M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20146 | XVBL8M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20147 | XVBL8M6 | Contractual warranty | Warranty | 18 months
20148 | XVBL8M7 | Main | range of product | Harmony XVB Universal
20149 | XVBL8M7 | Main | product or component type | Complete beacon
20150 | XVBL8M7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
20151 | XVBL8M7 | Main | signalling type | Flashing
20152 | XVBL8M7 | Main | mounting diameter | 70 mm
20153 | XVBL8M7 | Main | component name | XVBL
20154 | XVBL8M7 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
20155 | XVBL8M7 | Main | light source | Integral flash discharge tube, clear
20156 | XVBL8M7 | Main | bulb type | Flash discharge tube
20157 | XVBL8M7 | Main | [Us] rated supply voltage | 230 V AC
20158 | XVBL8M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20159 | XVBL8M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20160 | XVBL8M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20161 | XVBL8M7 | Complementary | current consumption | < 280 mA AC
20162 | XVBL8M7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20163 | XVBL8M7 | Complementary | flash energy | 10 J
20164 | XVBL8M7 | Complementary | flashing frequency | 1 Hz
20165 | XVBL8M7 | Complementary | illuminating intensity | 26 cd
20166 | XVBL8M7 | Complementary | CAD overall width | 70 mm
20167 | XVBL8M7 | Complementary | CAD overall height | 232 mm
20168 | XVBL8M7 | Complementary | CAD overall depth | 70 mm
20169 | XVBL8M7 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
20170 | XVBL8M7 | Complementary | net weight | 0.46 kg
20171 | XVBL8M7 | Environment | product certifications | CSA C22-2 No 14 CCC GOST UL 508
20172 | XVBL8M7 | Environment | standards | EN/IEC 60947-5-1
20173 | XVBL8M7 | Environment | protective treatment | TC
20174 | XVBL8M7 | Environment | ambient air temperature for storage | -40…70 °C
20175 | XVBL8M7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20176 | XVBL8M7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20177 | XVBL8M7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20178 | XVBL8M7 | Packing Units | Package 1 Weight | 460 g
20179 | XVBL8M7 | Offer Sustainability | Sustainable offer status | Green Premium product
20180 | XVBL8M7 | Offer Sustainability | REACh Regulation | REACh Declaration
20181 | XVBL8M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20182 | XVBL8M7 | Offer Sustainability | Mercury free | Yes
20183 | XVBL8M7 | Offer Sustainability | RoHS exemption information | Yes
20184 | XVBL8M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20185 | XVBL8M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20186 | XVBL8M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20187 | XVBL8M7 | Contractual warranty | Warranty | 18 months
20188 | XVBL8M8 | Main | range of product | Harmony XVB Universal
20189 | XVBL8M8 | Main | product or component type | Complete beacon
20190 | XVBL8M8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing Illuminated unit
20191 | XVBL8M8 | Main | signalling type | Flashing
20192 | XVBL8M8 | Main | mounting diameter | 70 mm
20193 | XVBL8M8 | Main | component name | XVBL
20194 | XVBL8M8 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
20195 | XVBL8M8 | Main | light source | Integral flash discharge tube, yellow
20196 | XVBL8M8 | Main | bulb type | Flash discharge tube
20197 | XVBL8M8 | Main | [Us] rated supply voltage | 230 V AC
20198 | XVBL8M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20199 | XVBL8M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20200 | XVBL8M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20201 | XVBL8M8 | Complementary | current consumption | < 280 mA AC
20202 | XVBL8M8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20203 | XVBL8M8 | Complementary | flash energy | 10 J
20204 | XVBL8M8 | Complementary | flashing frequency | 1 Hz
20205 | XVBL8M8 | Complementary | CAD overall width | 70 mm
20206 | XVBL8M8 | Complementary | CAD overall height | 232 mm
20207 | XVBL8M8 | Complementary | CAD overall depth | 70 mm
20208 | XVBL8M8 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
20209 | XVBL8M8 | Complementary | net weight | 0.46 kg
20210 | XVBL8M8 | Environment | product certifications | CCC GOST CSA C22-2 No 14 UL 508
20211 | XVBL8M8 | Environment | standards | EN/IEC 60947-5-1
20212 | XVBL8M8 | Environment | protective treatment | TC
20213 | XVBL8M8 | Environment | ambient air temperature for storage | -40…70 °C
20214 | XVBL8M8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20215 | XVBL8M8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20216 | XVBL8M8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20217 | XVBL8M8 | Packing Units | Package 1 Weight | 460 g
20218 | XVBL8M8 | Offer Sustainability | Sustainable offer status | Green Premium product
20219 | XVBL8M8 | Offer Sustainability | REACh Regulation | REACh Declaration
20220 | XVBL8M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20221 | XVBL8M8 | Offer Sustainability | Mercury free | Yes
20222 | XVBL8M8 | Offer Sustainability | RoHS exemption information | Yes
20223 | XVBL8M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20224 | XVBL8M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20225 | XVBL8M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20226 | XVBL8M8 | Contractual warranty | Warranty | 18 months
20227 | XVBC6B3 | Main | range of product | Harmony XVB Universal
20228 | XVBC6B3 | Main | product or component type | Indicator bank
20229 | XVBC6B3 | Main | beacon or indicator bank unit type | Illuminated unit
20230 | XVBC6B3 | Main | signalling type | Flashing
20231 | XVBC6B3 | Main | mounting diameter | 70 mm
20232 | XVBC6B3 | Main | component name | XVBC
20233 | XVBC6B3 | Main | material | Polycarbonate
20234 | XVBC6B3 | Main | light source | Integral flash discharge tube, green
20235 | XVBC6B3 | Main | bulb type | Flash discharge tube
20236 | XVBC6B3 | Main | [Us] rated supply voltage | 24 V AC/DC
20237 | XVBC6B3 | Main | flash energy | 5 J
20238 | XVBC6B3 | Complementary | assembly style | Customer assembly, up to 5 units
20239 | XVBC6B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20240 | XVBC6B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20241 | XVBC6B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20242 | XVBC6B3 | Complementary | current consumption | < 350 mA DC < 550 mA AC
20243 | XVBC6B3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
20244 | XVBC6B3 | Complementary | flashing frequency | 1 Hz
20245 | XVBC6B3 | Complementary | CAD overall width | 70 mm
20246 | XVBC6B3 | Complementary | CAD overall height | 157 mm
20247 | XVBC6B3 | Complementary | CAD overall depth | 70 mm
20248 | XVBC6B3 | Complementary | net weight | 0.295 kg
20249 | XVBC6B3 | Environment | product certifications | UL 508 CSA C22-2 No 14 CCC GOST
20250 | XVBC6B3 | Environment | standards | EN/IEC 60947-5-1
20251 | XVBC6B3 | Environment | protective treatment | TC
20252 | XVBC6B3 | Environment | ambient air temperature for storage | -40…70 °C
20253 | XVBC6B3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20254 | XVBC6B3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20255 | XVBC6B3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20256 | XVBC6B3 | Packing Units | Package 1 Weight | 298.000 g
20257 | XVBC6B3 | Offer Sustainability | Sustainable offer status | Green Premium product
20258 | XVBC6B3 | Offer Sustainability | REACh Regulation | REACh Declaration
20259 | XVBC6B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20260 | XVBC6B3 | Offer Sustainability | Mercury free | Yes
20261 | XVBC6B3 | Offer Sustainability | RoHS exemption information | Yes
20262 | XVBC6B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20263 | XVBC6B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20264 | XVBC6B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20265 | XVBC6B3 | Contractual warranty | Warranty | 18 months
20266 | XVBC6B4 | Main | range of product | Harmony XVB Universal
20267 | XVBC6B4 | Main | product or component type | Indicator bank
20268 | XVBC6B4 | Main | beacon or indicator bank unit type | Illuminated unit
20269 | XVBC6B4 | Main | signalling type | Flashing
20270 | XVBC6B4 | Main | mounting diameter | 70 mm
20271 | XVBC6B4 | Main | component name | XVBC
20272 | XVBC6B4 | Main | material | Polycarbonate
20273 | XVBC6B4 | Main | light source | Integral flash discharge tube, red
20274 | XVBC6B4 | Main | bulb type | Flash discharge tube
20275 | XVBC6B4 | Main | [Us] rated supply voltage | 24 V AC/DC
20276 | XVBC6B4 | Main | flash energy | 5 J
20277 | XVBC6B4 | Complementary | assembly style | Customer assembly, up to 5 units
20278 | XVBC6B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20279 | XVBC6B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20280 | XVBC6B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20281 | XVBC6B4 | Complementary | current consumption | < 350 mA DC < 550 mA AC
20282 | XVBC6B4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
20283 | XVBC6B4 | Complementary | flashing frequency | 1 Hz
20284 | XVBC6B4 | Complementary | CAD overall width | 70 mm
20285 | XVBC6B4 | Complementary | CAD overall height | 157 mm
20286 | XVBC6B4 | Complementary | CAD overall depth | 70 mm
20287 | XVBC6B4 | Complementary | net weight | 0.295 kg
20288 | XVBC6B4 | Environment | product certifications | UL 508 CCC GOST CSA C22-2 No 14
20289 | XVBC6B4 | Environment | standards | EN/IEC 60947-5-1
20290 | XVBC6B4 | Environment | protective treatment | TC
20291 | XVBC6B4 | Environment | ambient air temperature for storage | -40…70 °C
20292 | XVBC6B4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20293 | XVBC6B4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20294 | XVBC6B4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20295 | XVBC6B4 | Packing Units | Package 1 Weight | 298.000 g
20296 | XVBC6B4 | Offer Sustainability | Sustainable offer status | Green Premium product
20297 | XVBC6B4 | Offer Sustainability | REACh Regulation | REACh Declaration
20298 | XVBC6B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20299 | XVBC6B4 | Offer Sustainability | Mercury free | Yes
20300 | XVBC6B4 | Offer Sustainability | RoHS exemption information | Yes
20301 | XVBC6B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20302 | XVBC6B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20303 | XVBC6B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20304 | XVBC6B4 | Contractual warranty | Warranty | 18 months
20305 | XVBC6B5 | Main | range of product | Harmony XVB Universal
20306 | XVBC6B5 | Main | product or component type | Indicator bank
20307 | XVBC6B5 | Main | beacon or indicator bank unit type | Illuminated unit
20308 | XVBC6B5 | Main | signalling type | Flashing
20309 | XVBC6B5 | Main | mounting diameter | 70 mm
20310 | XVBC6B5 | Main | component name | XVBC
20311 | XVBC6B5 | Main | material | Polycarbonate
20312 | XVBC6B5 | Main | light source | Integral flash discharge tube, orange
20313 | XVBC6B5 | Main | bulb type | Flash discharge tube
20314 | XVBC6B5 | Main | [Us] rated supply voltage | 24 V AC/DC
20315 | XVBC6B5 | Main | flash energy | 5 J
20316 | XVBC6B5 | Complementary | assembly style | Customer assembly, up to 5 units
20317 | XVBC6B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20318 | XVBC6B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20319 | XVBC6B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20320 | XVBC6B5 | Complementary | current consumption | < 350 mA DC < 550 mA AC
20321 | XVBC6B5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20322 | XVBC6B5 | Complementary | flashing frequency | 1 Hz
20323 | XVBC6B5 | Complementary | CAD overall width | 70 mm
20324 | XVBC6B5 | Complementary | CAD overall height | 157 mm
20325 | XVBC6B5 | Complementary | CAD overall depth | 70 mm
20326 | XVBC6B5 | Complementary | net weight | 0.295 kg
20327 | XVBC6B5 | Environment | product certifications | CSA C22-2 No 14 CCC GOST UL 508
20328 | XVBC6B5 | Environment | standards | EN/IEC 60947-5-1
20329 | XVBC6B5 | Environment | protective treatment | TC
20330 | XVBC6B5 | Environment | ambient air temperature for storage | -40…70 °C
20331 | XVBC6B5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20332 | XVBC6B5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20333 | XVBC6B5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20334 | XVBC6B5 | Packing Units | Package 1 Weight | 298.000 g
20335 | XVBC6B5 | Offer Sustainability | Sustainable offer status | Green Premium product
20336 | XVBC6B5 | Offer Sustainability | REACh Regulation | REACh Declaration
20337 | XVBC6B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20338 | XVBC6B5 | Offer Sustainability | Mercury free | Yes
20339 | XVBC6B5 | Offer Sustainability | RoHS exemption information | Yes
20340 | XVBC6B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20341 | XVBC6B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20342 | XVBC6B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20343 | XVBC6B5 | Contractual warranty | Warranty | 18 months
20344 | XVBC6B6 | Main | range of product | Harmony XVB Universal
20345 | XVBC6B6 | Main | product or component type | Indicator bank
20346 | XVBC6B6 | Main | beacon or indicator bank unit type | Illuminated unit
20347 | XVBC6B6 | Main | signalling type | Flashing
20348 | XVBC6B6 | Main | mounting diameter | 70 mm
20349 | XVBC6B6 | Main | component name | XVBC
20350 | XVBC6B6 | Main | material | Polycarbonate
20351 | XVBC6B6 | Main | light source | Integral flash discharge tube, blue
20352 | XVBC6B6 | Main | bulb type | Flash discharge tube
20353 | XVBC6B6 | Main | [Us] rated supply voltage | 24 V AC/DC
20354 | XVBC6B6 | Main | flash energy | 5 J
20355 | XVBC6B6 | Complementary | assembly style | Customer assembly, up to 5 units
20356 | XVBC6B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20357 | XVBC6B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20358 | XVBC6B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20359 | XVBC6B6 | Complementary | current consumption | < 350 mA DC < 550 mA AC
20360 | XVBC6B6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
20361 | XVBC6B6 | Complementary | flashing frequency | 1 Hz
20362 | XVBC6B6 | Complementary | CAD overall width | 70 mm
20363 | XVBC6B6 | Complementary | CAD overall height | 157 mm
20364 | XVBC6B6 | Complementary | CAD overall depth | 70 mm
20365 | XVBC6B6 | Complementary | net weight | 0.295 kg
20366 | XVBC6B6 | Environment | product certifications | CCC UL 508 CSA C22-2 No 14 GOST
20367 | XVBC6B6 | Environment | standards | EN/IEC 60947-5-1
20368 | XVBC6B6 | Environment | protective treatment | TC
20369 | XVBC6B6 | Environment | ambient air temperature for storage | -40…70 °C
20370 | XVBC6B6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20371 | XVBC6B6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20372 | XVBC6B6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20373 | XVBC6B6 | Packing Units | Package 1 Weight | 296 g
20374 | XVBC6B6 | Packing Units | Package 2 Weight | 4.032 kg
20375 | XVBC6B6 | Offer Sustainability | Sustainable offer status | Green Premium product
20376 | XVBC6B6 | Offer Sustainability | REACh Regulation | REACh Declaration
20377 | XVBC6B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20378 | XVBC6B6 | Offer Sustainability | Mercury free | Yes
20379 | XVBC6B6 | Offer Sustainability | RoHS exemption information | Yes
20380 | XVBC6B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20381 | XVBC6B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20382 | XVBC6B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20383 | XVBC6B6 | Contractual warranty | Warranty | 18 months
20384 | XVBC6B7 | Main | range of product | Harmony XVB Universal
20385 | XVBC6B7 | Main | product or component type | Indicator bank
20386 | XVBC6B7 | Main | beacon or indicator bank unit type | Illuminated unit
20387 | XVBC6B7 | Main | signalling type | Flashing
20388 | XVBC6B7 | Main | mounting diameter | 70 mm
20389 | XVBC6B7 | Main | component name | XVBC
20390 | XVBC6B7 | Main | material | Polycarbonate
20391 | XVBC6B7 | Main | light source | Integral flash discharge tube, clear
20392 | XVBC6B7 | Main | bulb type | Flash discharge tube
20393 | XVBC6B7 | Main | [Us] rated supply voltage | 24 V AC/DC
20394 | XVBC6B7 | Main | flash energy | 5 J
20395 | XVBC6B7 | Complementary | assembly style | Customer assembly, up to 5 units
20396 | XVBC6B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20397 | XVBC6B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20398 | XVBC6B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20399 | XVBC6B7 | Complementary | current consumption | < 350 mA DC < 550 mA AC
20400 | XVBC6B7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20401 | XVBC6B7 | Complementary | flashing frequency | 1 Hz
20402 | XVBC6B7 | Complementary | illuminating intensity | 13 cd
20403 | XVBC6B7 | Complementary | CAD overall width | 70 mm
20404 | XVBC6B7 | Complementary | CAD overall height | 157 mm
20405 | XVBC6B7 | Complementary | CAD overall depth | 70 mm
20406 | XVBC6B7 | Complementary | net weight | 0.295 kg
20407 | XVBC6B7 | Environment | product certifications | CSA C22-2 No 14 UL 508 GOST CCC
20408 | XVBC6B7 | Environment | standards | EN/IEC 60947-5-1
20409 | XVBC6B7 | Environment | protective treatment | TC
20410 | XVBC6B7 | Environment | ambient air temperature for storage | -40…70 °C
20411 | XVBC6B7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20412 | XVBC6B7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20413 | XVBC6B7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20414 | XVBC6B7 | Packing Units | Package 1 Weight | 298 g
20415 | XVBC6B7 | Packing Units | Package 2 Weight | 3.992 kg
20416 | XVBC6B7 | Offer Sustainability | Sustainable offer status | Green Premium product
20417 | XVBC6B7 | Offer Sustainability | REACh Regulation | REACh Declaration
20418 | XVBC6B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20419 | XVBC6B7 | Offer Sustainability | Mercury free | Yes
20420 | XVBC6B7 | Offer Sustainability | RoHS exemption information | Yes
20421 | XVBC6B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20422 | XVBC6B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20423 | XVBC6B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20424 | XVBC6B7 | Contractual warranty | Warranty | 18 months
20425 | XVBC6B8 | Main | range of product | Harmony XVB Universal
20426 | XVBC6B8 | Main | product or component type | Indicator bank
20427 | XVBC6B8 | Main | beacon or indicator bank unit type | Illuminated unit
20428 | XVBC6B8 | Main | signalling type | Flashing
20429 | XVBC6B8 | Main | mounting diameter | 70 mm
20430 | XVBC6B8 | Main | component name | XVBC
20431 | XVBC6B8 | Main | material | Polycarbonate
20432 | XVBC6B8 | Main | light source | Integral flash discharge tube, yellow
20433 | XVBC6B8 | Main | bulb type | Flash discharge tube
20434 | XVBC6B8 | Main | [Us] rated supply voltage | 24 V AC/DC
20435 | XVBC6B8 | Main | flash energy | 5 J
20436 | XVBC6B8 | Complementary | assembly style | Customer assembly, up to 5 units
20437 | XVBC6B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20438 | XVBC6B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20439 | XVBC6B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20440 | XVBC6B8 | Complementary | current consumption | < 350 mA DC < 550 mA AC
20441 | XVBC6B8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
20442 | XVBC6B8 | Complementary | flashing frequency | 1 Hz
20443 | XVBC6B8 | Complementary | CAD overall width | 70 mm
20444 | XVBC6B8 | Complementary | CAD overall height | 157 mm
20445 | XVBC6B8 | Complementary | CAD overall depth | 70 mm
20446 | XVBC6B8 | Complementary | net weight | 0.295 kg
20447 | XVBC6B8 | Environment | product certifications | CCC GOST CSA C22-2 No 14 UL 508
20448 | XVBC6B8 | Environment | standards | EN/IEC 60947-5-1
20449 | XVBC6B8 | Environment | protective treatment | TC
20450 | XVBC6B8 | Environment | ambient air temperature for storage | -40…70 °C
20451 | XVBC6B8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20452 | XVBC6B8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20453 | XVBC6B8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20454 | XVBC6B8 | Packing Units | Package 1 Weight | 300 g
20455 | XVBC6B8 | Offer Sustainability | Sustainable offer status | Green Premium product
20456 | XVBC6B8 | Offer Sustainability | REACh Regulation | REACh Declaration
20457 | XVBC6B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20458 | XVBC6B8 | Offer Sustainability | Mercury free | Yes
20459 | XVBC6B8 | Offer Sustainability | RoHS exemption information | Yes
20460 | XVBC6B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20461 | XVBC6B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20462 | XVBC6B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20463 | XVBC6B8 | Contractual warranty | Warranty | 18 months
20464 | XVBC6G3 | Main | range of product | Harmony XVB Universal
20465 | XVBC6G3 | Main | product or component type | Indicator bank
20466 | XVBC6G3 | Main | beacon or indicator bank unit type | Illuminated unit
20467 | XVBC6G3 | Main | signalling type | Flashing
20468 | XVBC6G3 | Main | mounting diameter | 70 mm
20469 | XVBC6G3 | Main | component name | XVBC
20470 | XVBC6G3 | Main | material | Polycarbonate
20471 | XVBC6G3 | Main | light source | Integral flash discharge tube, green
20472 | XVBC6G3 | Main | bulb type | Flash discharge tube
20473 | XVBC6G3 | Main | [Us] rated supply voltage | 120 V AC
20474 | XVBC6G3 | Main | flash energy | 5 J
20475 | XVBC6G3 | Complementary | assembly style | Customer assembly, up to 5 units
20476 | XVBC6G3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20477 | XVBC6G3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20478 | XVBC6G3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20479 | XVBC6G3 | Complementary | current consumption | < 140 mA AC
20480 | XVBC6G3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20481 | XVBC6G3 | Complementary | flashing frequency | 1 Hz
20482 | XVBC6G3 | Complementary | CAD overall width | 70 mm
20483 | XVBC6G3 | Complementary | CAD overall height | 157 mm
20484 | XVBC6G3 | Complementary | CAD overall depth | 70 mm
20485 | XVBC6G3 | Complementary | net weight | 0.28 kg
20486 | XVBC6G3 | Environment | product certifications | CCC UL 508 CSA C22-2 No 14 GOST
20487 | XVBC6G3 | Environment | standards | EN/IEC 60947-5-1
20488 | XVBC6G3 | Environment | protective treatment | TC
20489 | XVBC6G3 | Environment | ambient air temperature for storage | -40…70 °C
20490 | XVBC6G3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20491 | XVBC6G3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20492 | XVBC6G3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20493 | XVBC6G3 | Packing Units | Package 1 Weight | 275 g
20494 | XVBC6G3 | Offer Sustainability | Sustainable offer status | Green Premium product
20495 | XVBC6G3 | Offer Sustainability | REACh Regulation | REACh Declaration
20496 | XVBC6G3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20497 | XVBC6G3 | Offer Sustainability | Mercury free | Yes
20498 | XVBC6G3 | Offer Sustainability | RoHS exemption information | Yes
20499 | XVBC6G3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20500 | XVBC6G3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20501 | XVBC6G3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20502 | XVBC6G3 | Contractual warranty | Warranty | 18 months
20503 | XVBC6G4 | Main | range of product | Harmony XVB Universal
20504 | XVBC6G4 | Main | product or component type | Indicator bank
20505 | XVBC6G4 | Main | beacon or indicator bank unit type | Illuminated unit
20506 | XVBC6G4 | Main | signalling type | Flashing
20507 | XVBC6G4 | Main | mounting diameter | 70 mm
20508 | XVBC6G4 | Main | component name | XVBC
20509 | XVBC6G4 | Main | material | Polycarbonate
20510 | XVBC6G4 | Main | light source | Integral flash discharge tube, red
20511 | XVBC6G4 | Main | bulb type | Flash discharge tube
20512 | XVBC6G4 | Main | [Us] rated supply voltage | 120 V AC
20513 | XVBC6G4 | Main | flash energy | 5 J
20514 | XVBC6G4 | Complementary | assembly style | Customer assembly, up to 5 units
20515 | XVBC6G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20516 | XVBC6G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20517 | XVBC6G4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20518 | XVBC6G4 | Complementary | current consumption | < 140 mA AC
20519 | XVBC6G4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
20520 | XVBC6G4 | Complementary | flashing frequency | 1 Hz
20521 | XVBC6G4 | Complementary | CAD overall width | 70 mm
20522 | XVBC6G4 | Complementary | CAD overall height | 157 mm
20523 | XVBC6G4 | Complementary | CAD overall depth | 70 mm
20524 | XVBC6G4 | Complementary | net weight | 0.28 kg
20525 | XVBC6G4 | Environment | product certifications | CCC GOST CSA C22-2 No 14 UL 508
20526 | XVBC6G4 | Environment | standards | EN/IEC 60947-5-1
20527 | XVBC6G4 | Environment | protective treatment | TC
20528 | XVBC6G4 | Environment | ambient air temperature for storage | -40…70 °C
20529 | XVBC6G4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20530 | XVBC6G4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20531 | XVBC6G4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20532 | XVBC6G4 | Packing Units | Package 1 Weight | 276 g
20533 | XVBC6G4 | Packing Units | Package 2 Weight | 3.772 kg
20534 | XVBC6G4 | Offer Sustainability | Sustainable offer status | Green Premium product
20535 | XVBC6G4 | Offer Sustainability | REACh Regulation | REACh Declaration
20536 | XVBC6G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20537 | XVBC6G4 | Offer Sustainability | Mercury free | Yes
20538 | XVBC6G4 | Offer Sustainability | RoHS exemption information | Yes
20539 | XVBC6G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20540 | XVBC6G4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20541 | XVBC6G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20542 | XVBC6G4 | Contractual warranty | Warranty | 18 months
20543 | XVBC6G5 | Main | range of product | Harmony XVB Universal
20544 | XVBC6G5 | Main | product or component type | Indicator bank
20545 | XVBC6G5 | Main | beacon or indicator bank unit type | Illuminated unit
20546 | XVBC6G5 | Main | signalling type | Flashing
20547 | XVBC6G5 | Main | mounting diameter | 70 mm
20548 | XVBC6G5 | Main | component name | XVBC
20549 | XVBC6G5 | Main | material | Polycarbonate
20550 | XVBC6G5 | Main | light source | Integral flash discharge tube, orange
20551 | XVBC6G5 | Main | bulb type | Flash discharge tube
20552 | XVBC6G5 | Main | [Us] rated supply voltage | 120 V AC
20553 | XVBC6G5 | Main | flash energy | 5 J
20554 | XVBC6G5 | Complementary | assembly style | Customer assembly, up to 5 units
20555 | XVBC6G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20556 | XVBC6G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20557 | XVBC6G5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20558 | XVBC6G5 | Complementary | current consumption | < 140 mA AC
20559 | XVBC6G5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20560 | XVBC6G5 | Complementary | flashing frequency | 1 Hz
20561 | XVBC6G5 | Complementary | CAD overall width | 70 mm
20562 | XVBC6G5 | Complementary | CAD overall height | 157 mm
20563 | XVBC6G5 | Complementary | CAD overall depth | 70 mm
20564 | XVBC6G5 | Complementary | net weight | 0.28 kg
20565 | XVBC6G5 | Environment | product certifications | CSA C22-2 No 14 CCC UL 508 GOST
20566 | XVBC6G5 | Environment | standards | EN/IEC 60947-5-1
20567 | XVBC6G5 | Environment | protective treatment | TC
20568 | XVBC6G5 | Environment | ambient air temperature for storage | -40…70 °C
20569 | XVBC6G5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20570 | XVBC6G5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20571 | XVBC6G5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20572 | XVBC6G5 | Packing Units | Package 1 Weight | 0.276 kg
20573 | XVBC6G5 | Offer Sustainability | Sustainable offer status | Green Premium product
20574 | XVBC6G5 | Offer Sustainability | REACh Regulation | REACh Declaration
20575 | XVBC6G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20576 | XVBC6G5 | Offer Sustainability | Mercury free | Yes
20577 | XVBC6G5 | Offer Sustainability | RoHS exemption information | Yes
20578 | XVBC6G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20579 | XVBC6G5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20580 | XVBC6G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20581 | XVBC6G5 | Contractual warranty | Warranty | 18 months
20582 | XVBC6G6 | Main | range of product | Harmony XVB Universal
20583 | XVBC6G6 | Main | product or component type | Indicator bank
20584 | XVBC6G6 | Main | beacon or indicator bank unit type | Illuminated unit
20585 | XVBC6G6 | Main | signalling type | Flashing
20586 | XVBC6G6 | Main | mounting diameter | 70 mm
20587 | XVBC6G6 | Main | component name | XVBC
20588 | XVBC6G6 | Main | material | Polycarbonate
20589 | XVBC6G6 | Main | light source | Integral flash discharge tube, blue
20590 | XVBC6G6 | Main | bulb type | Flash discharge tube
20591 | XVBC6G6 | Main | [Us] rated supply voltage | 120 V AC
20592 | XVBC6G6 | Main | flash energy | 5 J
20593 | XVBC6G6 | Complementary | assembly style | Customer assembly, up to 5 units
20594 | XVBC6G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20595 | XVBC6G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20596 | XVBC6G6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20597 | XVBC6G6 | Complementary | current consumption | < 140 mA AC
20598 | XVBC6G6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
20599 | XVBC6G6 | Complementary | flashing frequency | 1 Hz
20600 | XVBC6G6 | Complementary | CAD overall width | 70 mm
20601 | XVBC6G6 | Complementary | CAD overall height | 157 mm
20602 | XVBC6G6 | Complementary | CAD overall depth | 70 mm
20603 | XVBC6G6 | Complementary | net weight | 0.28 kg
20604 | XVBC6G6 | Environment | product certifications | CSA C22-2 No 14 CCC UL 508 GOST
20605 | XVBC6G6 | Environment | standards | EN/IEC 60947-5-1
20606 | XVBC6G6 | Environment | protective treatment | TC
20607 | XVBC6G6 | Environment | ambient air temperature for storage | -40…70 °C
20608 | XVBC6G6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20609 | XVBC6G6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20610 | XVBC6G6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20611 | XVBC6G6 | Packing Units | Package 1 Weight | 273 g
20612 | XVBC6G6 | Offer Sustainability | Sustainable offer status | Green Premium product
20613 | XVBC6G6 | Offer Sustainability | REACh Regulation | REACh Declaration
20614 | XVBC6G6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20615 | XVBC6G6 | Offer Sustainability | Mercury free | Yes
20616 | XVBC6G6 | Offer Sustainability | RoHS exemption information | Yes
20617 | XVBC6G6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20618 | XVBC6G6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20619 | XVBC6G6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20620 | XVBC6G6 | Contractual warranty | Warranty | 18 months
20621 | XVBC6G7 | Main | range of product | Harmony XVB Universal
20622 | XVBC6G7 | Main | product or component type | Indicator bank
20623 | XVBC6G7 | Main | beacon or indicator bank unit type | Illuminated unit
20624 | XVBC6G7 | Main | signalling type | Flashing
20625 | XVBC6G7 | Main | mounting diameter | 70 mm
20626 | XVBC6G7 | Main | component name | XVBC
20627 | XVBC6G7 | Main | material | Polycarbonate
20628 | XVBC6G7 | Main | light source | Integral flash discharge tube, clear
20629 | XVBC6G7 | Main | bulb type | Flash discharge tube
20630 | XVBC6G7 | Main | [Us] rated supply voltage | 120 V AC
20631 | XVBC6G7 | Main | flash energy | 5 J
20632 | XVBC6G7 | Complementary | assembly style | Customer assembly, up to 5 units
20633 | XVBC6G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20634 | XVBC6G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20635 | XVBC6G7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20636 | XVBC6G7 | Complementary | current consumption | < 140 mA AC
20637 | XVBC6G7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20638 | XVBC6G7 | Complementary | flashing frequency | 1 Hz
20639 | XVBC6G7 | Complementary | illuminating intensity | 13 cd
20640 | XVBC6G7 | Complementary | CAD overall width | 70 mm
20641 | XVBC6G7 | Complementary | CAD overall height | 157 mm
20642 | XVBC6G7 | Complementary | CAD overall depth | 70 mm
20643 | XVBC6G7 | Complementary | net weight | 0.28 kg
20644 | XVBC6G7 | Environment | product certifications | CCC GOST CSA C22-2 No 14 UL 508
20645 | XVBC6G7 | Environment | standards | EN/IEC 60947-5-1
20646 | XVBC6G7 | Environment | protective treatment | TC
20647 | XVBC6G7 | Environment | ambient air temperature for storage | -40…70 °C
20648 | XVBC6G7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20649 | XVBC6G7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20650 | XVBC6G7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20651 | XVBC6G7 | Packing Units | Package 1 Weight | 0.273 kg
20652 | XVBC6G7 | Offer Sustainability | Sustainable offer status | Green Premium product
20653 | XVBC6G7 | Offer Sustainability | REACh Regulation | REACh Declaration
20654 | XVBC6G7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20655 | XVBC6G7 | Offer Sustainability | Mercury free | Yes
20656 | XVBC6G7 | Offer Sustainability | RoHS exemption information | Yes
20657 | XVBC6G7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20658 | XVBC6G7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20659 | XVBC6G7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20660 | XVBC6G7 | Contractual warranty | Warranty | 18 months
20661 | XVBC6G8 | Main | range of product | Harmony XVB Universal
20662 | XVBC6G8 | Main | product or component type | Indicator bank
20663 | XVBC6G8 | Main | beacon or indicator bank unit type | Illuminated unit
20664 | XVBC6G8 | Main | signalling type | Flashing
20665 | XVBC6G8 | Main | mounting diameter | 70 mm
20666 | XVBC6G8 | Main | component name | XVBC
20667 | XVBC6G8 | Main | material | Polycarbonate
20668 | XVBC6G8 | Main | light source | Integral flash discharge tube, yellow
20669 | XVBC6G8 | Main | bulb type | Flash discharge tube
20670 | XVBC6G8 | Main | [Us] rated supply voltage | 120 V AC
20671 | XVBC6G8 | Main | flash energy | 5 J
20672 | XVBC6G8 | Complementary | assembly style | Customer assembly, up to 5 units
20673 | XVBC6G8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20674 | XVBC6G8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20675 | XVBC6G8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20676 | XVBC6G8 | Complementary | current consumption | < 140 mA AC
20677 | XVBC6G8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
20678 | XVBC6G8 | Complementary | flashing frequency | 1 Hz
20679 | XVBC6G8 | Complementary | CAD overall width | 70 mm
20680 | XVBC6G8 | Complementary | CAD overall height | 157 mm
20681 | XVBC6G8 | Complementary | CAD overall depth | 70 mm
20682 | XVBC6G8 | Complementary | net weight | 0.28 kg
20683 | XVBC6G8 | Environment | product certifications | CSA C22-2 No 14 UL 508 GOST CCC
20684 | XVBC6G8 | Environment | standards | EN/IEC 60947-5-1
20685 | XVBC6G8 | Environment | protective treatment | TC
20686 | XVBC6G8 | Environment | ambient air temperature for storage | -40…70 °C
20687 | XVBC6G8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20688 | XVBC6G8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20689 | XVBC6G8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20690 | XVBC6G8 | Packing Units | Package 1 Weight | 280 g
20691 | XVBC6G8 | Offer Sustainability | Sustainable offer status | Green Premium product
20692 | XVBC6G8 | Offer Sustainability | REACh Regulation | REACh Declaration
20693 | XVBC6G8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20694 | XVBC6G8 | Offer Sustainability | Mercury free | Yes
20695 | XVBC6G8 | Offer Sustainability | RoHS exemption information | Yes
20696 | XVBC6G8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20697 | XVBC6G8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20698 | XVBC6G8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20699 | XVBC6G8 | Contractual warranty | Warranty | 18 months
20700 | XVBC6M3 | Main | range of product | Harmony XVB Universal
20701 | XVBC6M3 | Main | product or component type | Indicator bank
20702 | XVBC6M3 | Main | beacon or indicator bank unit type | Illuminated unit
20703 | XVBC6M3 | Main | signalling type | Flashing
20704 | XVBC6M3 | Main | mounting diameter | 70 mm
20705 | XVBC6M3 | Main | component name | XVBC
20706 | XVBC6M3 | Main | material | Polycarbonate
20707 | XVBC6M3 | Main | light source | Integral flash discharge tube, green
20708 | XVBC6M3 | Main | bulb type | Flash discharge tube
20709 | XVBC6M3 | Main | [Us] rated supply voltage | 230 V AC
20710 | XVBC6M3 | Main | flash energy | 5 J
20711 | XVBC6M3 | Complementary | assembly style | Customer assembly, up to 5 units
20712 | XVBC6M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20713 | XVBC6M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20714 | XVBC6M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20715 | XVBC6M3 | Complementary | current consumption | < 105 mA AC
20716 | XVBC6M3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20717 | XVBC6M3 | Complementary | flashing frequency | 1 Hz
20718 | XVBC6M3 | Complementary | CAD overall width | 70 mm
20719 | XVBC6M3 | Complementary | CAD overall height | 157 mm
20720 | XVBC6M3 | Complementary | CAD overall depth | 70 mm
20721 | XVBC6M3 | Environment | product certifications | GOST CSA C22-2 No 14 UL 508 CCC
20722 | XVBC6M3 | Environment | standards | EN/IEC 60947-5-1
20723 | XVBC6M3 | Environment | protective treatment | TC
20724 | XVBC6M3 | Environment | ambient air temperature for storage | -40…70 °C
20725 | XVBC6M3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20726 | XVBC6M3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20727 | XVBC6M3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20728 | XVBC6M3 | Packing Units | Package 1 Weight | 281 g
20729 | XVBC6M3 | Packing Units | Package 2 Weight | 3.838 kg
20730 | XVBC6M3 | Offer Sustainability | Sustainable offer status | Green Premium product
20731 | XVBC6M3 | Offer Sustainability | REACh Regulation | REACh Declaration
20732 | XVBC6M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20733 | XVBC6M3 | Offer Sustainability | Mercury free | Yes
20734 | XVBC6M3 | Offer Sustainability | RoHS exemption information | Yes
20735 | XVBC6M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20736 | XVBC6M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20737 | XVBC6M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20738 | XVBC6M3 | Contractual warranty | Warranty | 18 months
20739 | XVBC6M4 | Main | range of product | Harmony XVB Universal
20740 | XVBC6M4 | Main | product or component type | Indicator bank
20741 | XVBC6M4 | Main | beacon or indicator bank unit type | Illuminated unit
20742 | XVBC6M4 | Main | signalling type | Flashing
20743 | XVBC6M4 | Main | mounting diameter | 70 mm
20744 | XVBC6M4 | Main | component name | XVBC
20745 | XVBC6M4 | Main | material | Polycarbonate
20746 | XVBC6M4 | Main | light source | Integral flash discharge tube, red
20747 | XVBC6M4 | Main | bulb type | Flash discharge tube
20748 | XVBC6M4 | Main | [Us] rated supply voltage | 230 V AC
20749 | XVBC6M4 | Main | flash energy | 5 J
20750 | XVBC6M4 | Complementary | assembly style | Customer assembly, up to 5 units
20751 | XVBC6M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20752 | XVBC6M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20753 | XVBC6M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20754 | XVBC6M4 | Complementary | current consumption | < 105 mA AC
20755 | XVBC6M4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
20756 | XVBC6M4 | Complementary | flashing frequency | 1 Hz
20757 | XVBC6M4 | Complementary | CAD overall width | 70 mm
20758 | XVBC6M4 | Complementary | CAD overall height | 157 mm
20759 | XVBC6M4 | Complementary | CAD overall depth | 70 mm
20760 | XVBC6M4 | Environment | product certifications | UL 508 CCC CSA C22-2 No 14 GOST
20761 | XVBC6M4 | Environment | standards | EN/IEC 60947-5-1
20762 | XVBC6M4 | Environment | protective treatment | TC
20763 | XVBC6M4 | Environment | ambient air temperature for storage | -40…70 °C
20764 | XVBC6M4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20765 | XVBC6M4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20766 | XVBC6M4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20767 | XVBC6M4 | Packing Units | Package 1 Weight | 281 g
20768 | XVBC6M4 | Packing Units | Package 2 Weight | 3.883 kg
20769 | XVBC6M4 | Offer Sustainability | Sustainable offer status | Green Premium product
20770 | XVBC6M4 | Offer Sustainability | REACh Regulation | REACh Declaration
20771 | XVBC6M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20772 | XVBC6M4 | Offer Sustainability | Mercury free | Yes
20773 | XVBC6M4 | Offer Sustainability | RoHS exemption information | Yes
20774 | XVBC6M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20775 | XVBC6M4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20776 | XVBC6M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20777 | XVBC6M4 | Contractual warranty | Warranty | 18 months
20778 | XVBC6M5 | Main | range of product | Harmony XVB Universal
20779 | XVBC6M5 | Main | product or component type | Indicator bank
20780 | XVBC6M5 | Main | beacon or indicator bank unit type | Illuminated unit
20781 | XVBC6M5 | Main | signalling type | Flashing
20782 | XVBC6M5 | Main | mounting diameter | 70 mm
20783 | XVBC6M5 | Main | component name | XVBC
20784 | XVBC6M5 | Main | material | Polycarbonate
20785 | XVBC6M5 | Main | light source | Integral flash discharge tube, orange
20786 | XVBC6M5 | Main | bulb type | Flash discharge tube
20787 | XVBC6M5 | Main | [Us] rated supply voltage | 230 V AC
20788 | XVBC6M5 | Main | flash energy | 5 J
20789 | XVBC6M5 | Complementary | assembly style | Customer assembly, up to 5 units
20790 | XVBC6M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20791 | XVBC6M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20792 | XVBC6M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20793 | XVBC6M5 | Complementary | current consumption | < 105 mA AC
20794 | XVBC6M5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20795 | XVBC6M5 | Complementary | flashing frequency | 1 Hz
20796 | XVBC6M5 | Complementary | CAD overall width | 70 mm
20797 | XVBC6M5 | Complementary | CAD overall height | 157 mm
20798 | XVBC6M5 | Complementary | CAD overall depth | 70 mm
20799 | XVBC6M5 | Environment | product certifications | CCC CSA C22-2 No 14 UL 508 GOST
20800 | XVBC6M5 | Environment | standards | EN/IEC 60947-5-1
20801 | XVBC6M5 | Environment | protective treatment | TC
20802 | XVBC6M5 | Environment | ambient air temperature for storage | -40…70 °C
20803 | XVBC6M5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20804 | XVBC6M5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20805 | XVBC6M5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20806 | XVBC6M5 | Packing Units | Package 1 Weight | 285.9 g
20807 | XVBC6M5 | Offer Sustainability | Sustainable offer status | Green Premium product
20808 | XVBC6M5 | Offer Sustainability | REACh Regulation | REACh Declaration
20809 | XVBC6M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20810 | XVBC6M5 | Offer Sustainability | Mercury free | Yes
20811 | XVBC6M5 | Offer Sustainability | RoHS exemption information | Yes
20812 | XVBC6M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20813 | XVBC6M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20814 | XVBC6M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20815 | XVBC6M5 | Contractual warranty | Warranty | 18 months
20816 | XVBC6M6 | Main | range of product | Harmony XVB Universal
20817 | XVBC6M6 | Main | product or component type | Indicator bank
20818 | XVBC6M6 | Main | beacon or indicator bank unit type | Illuminated unit
20819 | XVBC6M6 | Main | signalling type | Flashing
20820 | XVBC6M6 | Main | mounting diameter | 70 mm
20821 | XVBC6M6 | Main | component name | XVBC
20822 | XVBC6M6 | Main | material | Polycarbonate
20823 | XVBC6M6 | Main | light source | Integral flash discharge tube, blue
20824 | XVBC6M6 | Main | bulb type | Flash discharge tube
20825 | XVBC6M6 | Main | [Us] rated supply voltage | 230 V AC
20826 | XVBC6M6 | Main | flash energy | 5 J
20827 | XVBC6M6 | Complementary | assembly style | Customer assembly, up to 5 units
20828 | XVBC6M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20829 | XVBC6M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20830 | XVBC6M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20831 | XVBC6M6 | Complementary | current consumption | < 105 mA AC
20832 | XVBC6M6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20833 | XVBC6M6 | Complementary | flashing frequency | 1 Hz
20834 | XVBC6M6 | Complementary | CAD overall width | 70 mm
20835 | XVBC6M6 | Complementary | CAD overall height | 157 mm
20836 | XVBC6M6 | Complementary | CAD overall depth | 70 mm
20837 | XVBC6M6 | Environment | product certifications | UL 508 GOST CCC CSA C22-2 No 14
20838 | XVBC6M6 | Environment | standards | EN/IEC 60947-5-1
20839 | XVBC6M6 | Environment | protective treatment | TC
20840 | XVBC6M6 | Environment | ambient air temperature for storage | -40…70 °C
20841 | XVBC6M6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20842 | XVBC6M6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20843 | XVBC6M6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20844 | XVBC6M6 | Packing Units | Package 1 Weight | 0.283 kg
20845 | XVBC6M6 | Offer Sustainability | Sustainable offer status | Green Premium product
20846 | XVBC6M6 | Offer Sustainability | REACh Regulation | REACh Declaration
20847 | XVBC6M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20848 | XVBC6M6 | Offer Sustainability | Mercury free | Yes
20849 | XVBC6M6 | Offer Sustainability | RoHS exemption information | Yes
20850 | XVBC6M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20851 | XVBC6M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20852 | XVBC6M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20853 | XVBC6M6 | Contractual warranty | Warranty | 18 months
20854 | XVBC6M7 | Main | range of product | Harmony XVB Universal
20855 | XVBC6M7 | Main | product or component type | Indicator bank
20856 | XVBC6M7 | Main | beacon or indicator bank unit type | Illuminated unit
20857 | XVBC6M7 | Main | signalling type | Flashing
20858 | XVBC6M7 | Main | mounting diameter | 70 mm
20859 | XVBC6M7 | Main | component name | XVBC
20860 | XVBC6M7 | Main | material | Polycarbonate
20861 | XVBC6M7 | Main | light source | Integral flash discharge tube, clear
20862 | XVBC6M7 | Main | bulb type | Flash discharge tube
20863 | XVBC6M7 | Main | [Us] rated supply voltage | 230 V AC
20864 | XVBC6M7 | Main | flash energy | 5 J
20865 | XVBC6M7 | Complementary | assembly style | Customer assembly, up to 5 units
20866 | XVBC6M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20867 | XVBC6M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20868 | XVBC6M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20869 | XVBC6M7 | Complementary | current consumption | < 105 mA AC
20870 | XVBC6M7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20871 | XVBC6M7 | Complementary | flashing frequency | 1 Hz
20872 | XVBC6M7 | Complementary | illuminating intensity | 13 cd
20873 | XVBC6M7 | Complementary | CAD overall width | 70 mm
20874 | XVBC6M7 | Complementary | CAD overall height | 157 mm
20875 | XVBC6M7 | Complementary | CAD overall depth | 70 mm
20876 | XVBC6M7 | Environment | product certifications | CSA C22-2 No 14 GOST UL 508 CCC
20877 | XVBC6M7 | Environment | standards | EN/IEC 60947-5-1
20878 | XVBC6M7 | Environment | protective treatment | TC
20879 | XVBC6M7 | Environment | ambient air temperature for storage | -40…70 °C
20880 | XVBC6M7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20881 | XVBC6M7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20882 | XVBC6M7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20883 | XVBC6M7 | Packing Units | Package 1 Weight | 283.9 g
20884 | XVBC6M7 | Offer Sustainability | Sustainable offer status | Green Premium product
20885 | XVBC6M7 | Offer Sustainability | REACh Regulation | REACh Declaration
20886 | XVBC6M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20887 | XVBC6M7 | Offer Sustainability | Mercury free | Yes
20888 | XVBC6M7 | Offer Sustainability | RoHS exemption information | Yes
20889 | XVBC6M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20890 | XVBC6M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20891 | XVBC6M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20892 | XVBC6M7 | Contractual warranty | Warranty | 18 months
20893 | XVBC6M8 | Main | range of product | Harmony XVB Universal
20894 | XVBC6M8 | Main | product or component type | Indicator bank
20895 | XVBC6M8 | Main | beacon or indicator bank unit type | Illuminated unit
20896 | XVBC6M8 | Main | signalling type | Flashing
20897 | XVBC6M8 | Main | mounting diameter | 70 mm
20898 | XVBC6M8 | Main | component name | XVBC
20899 | XVBC6M8 | Main | material | Polycarbonate
20900 | XVBC6M8 | Main | light source | Integral flash discharge tube, yellow
20901 | XVBC6M8 | Main | bulb type | Flash discharge tube
20902 | XVBC6M8 | Main | [Us] rated supply voltage | 230 V AC
20903 | XVBC6M8 | Main | flash energy | 5 J
20904 | XVBC6M8 | Complementary | assembly style | Customer assembly, up to 5 units
20905 | XVBC6M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20906 | XVBC6M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20907 | XVBC6M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20908 | XVBC6M8 | Complementary | current consumption | < 105 mA AC
20909 | XVBC6M8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
20910 | XVBC6M8 | Complementary | flashing frequency | 1 Hz
20911 | XVBC6M8 | Complementary | CAD overall width | 70 mm
20912 | XVBC6M8 | Complementary | CAD overall height | 157 mm
20913 | XVBC6M8 | Complementary | CAD overall depth | 70 mm
20914 | XVBC6M8 | Environment | product certifications | UL 508 CSA C22-2 No 14 GOST CCC
20915 | XVBC6M8 | Environment | standards | EN/IEC 60947-5-1
20916 | XVBC6M8 | Environment | protective treatment | TC
20917 | XVBC6M8 | Environment | ambient air temperature for storage | -40…70 °C
20918 | XVBC6M8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20919 | XVBC6M8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20920 | XVBC6M8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20921 | XVBC6M8 | Packing Units | Package 1 Weight | 282.9 g
20922 | XVBC6M8 | Offer Sustainability | Sustainable offer status | Green Premium product
20923 | XVBC6M8 | Offer Sustainability | REACh Regulation | REACh Declaration
20924 | XVBC6M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20925 | XVBC6M8 | Offer Sustainability | Mercury free | Yes
20926 | XVBC6M8 | Offer Sustainability | RoHS exemption information | Yes
20927 | XVBC6M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20928 | XVBC6M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20929 | XVBC6M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20930 | XVBC6M8 | Contractual warranty | Warranty | 18 months
20931 | XVBC8B3 | Main | range of product | Harmony XVB Universal
20932 | XVBC8B3 | Main | product or component type | Indicator bank
20933 | XVBC8B3 | Main | beacon or indicator bank unit type | Illuminated unit
20934 | XVBC8B3 | Main | signalling type | Flashing
20935 | XVBC8B3 | Main | mounting diameter | 70 mm
20936 | XVBC8B3 | Main | component name | XVBC
20937 | XVBC8B3 | Main | material | Polycarbonate
20938 | XVBC8B3 | Main | light source | Integral flash discharge tube, green
20939 | XVBC8B3 | Main | bulb type | Flash discharge tube
20940 | XVBC8B3 | Main | [Us] rated supply voltage | 24 V AC/DC
20941 | XVBC8B3 | Main | flash energy | 10 J
20942 | XVBC8B3 | Complementary | assembly style | Customer assembly, up to 5 units
20943 | XVBC8B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20944 | XVBC8B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20945 | XVBC8B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20946 | XVBC8B3 | Complementary | current consumption | < 1300 mA AC < 850 mA DC
20947 | XVBC8B3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20948 | XVBC8B3 | Complementary | flashing frequency | 1 Hz
20949 | XVBC8B3 | Complementary | CAD overall width | 70 mm
20950 | XVBC8B3 | Complementary | CAD overall height | 157 mm
20951 | XVBC8B3 | Complementary | CAD overall depth | 70 mm
20952 | XVBC8B3 | Complementary | net weight | 0.305 kg
20953 | XVBC8B3 | Environment | product certifications | UL 508 CCC CSA C22-2 No 14 GOST
20954 | XVBC8B3 | Environment | standards | EN/IEC 60947-5-1
20955 | XVBC8B3 | Environment | protective treatment | TC
20956 | XVBC8B3 | Environment | ambient air temperature for storage | -40…70 °C
20957 | XVBC8B3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20958 | XVBC8B3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20959 | XVBC8B3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20960 | XVBC8B3 | Packing Units | Package 1 Weight | 0.317 kg
20961 | XVBC8B3 | Offer Sustainability | Sustainable offer status | Green Premium product
20962 | XVBC8B3 | Offer Sustainability | REACh Regulation | REACh Declaration
20963 | XVBC8B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
20964 | XVBC8B3 | Offer Sustainability | Mercury free | Yes
20965 | XVBC8B3 | Offer Sustainability | RoHS exemption information | Yes
20966 | XVBC8B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
20967 | XVBC8B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
20968 | XVBC8B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
20969 | XVBC8B3 | Contractual warranty | Warranty | 18 months
20970 | XVBC8B4 | Main | range of product | Harmony XVB Universal
20971 | XVBC8B4 | Main | product or component type | Indicator bank
20972 | XVBC8B4 | Main | beacon or indicator bank unit type | Illuminated unit
20973 | XVBC8B4 | Main | signalling type | Flashing
20974 | XVBC8B4 | Main | mounting diameter | 70 mm
20975 | XVBC8B4 | Main | component name | XVBC
20976 | XVBC8B4 | Main | material | Polycarbonate
20977 | XVBC8B4 | Main | light source | Integral flash discharge tube, red
20978 | XVBC8B4 | Main | bulb type | Flash discharge tube
20979 | XVBC8B4 | Main | [Us] rated supply voltage | 24 V AC/DC
20980 | XVBC8B4 | Main | flash energy | 10 J
20981 | XVBC8B4 | Complementary | assembly style | Customer assembly, up to 5 units
20982 | XVBC8B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
20983 | XVBC8B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
20984 | XVBC8B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
20985 | XVBC8B4 | Complementary | current consumption | < 1300 mA AC < 850 mA DC
20986 | XVBC8B4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
20987 | XVBC8B4 | Complementary | flashing frequency | 1 Hz
20988 | XVBC8B4 | Complementary | CAD overall width | 70 mm
20989 | XVBC8B4 | Complementary | CAD overall height | 157 mm
20990 | XVBC8B4 | Complementary | CAD overall depth | 70 mm
20991 | XVBC8B4 | Complementary | net weight | 0.305 kg
20992 | XVBC8B4 | Environment | product certifications | CSA C22-2 No 14 CCC GOST UL 508
20993 | XVBC8B4 | Environment | standards | EN/IEC 60947-5-1
20994 | XVBC8B4 | Environment | protective treatment | TC
20995 | XVBC8B4 | Environment | ambient air temperature for storage | -40…70 °C
20996 | XVBC8B4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
20997 | XVBC8B4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
20998 | XVBC8B4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
20999 | XVBC8B4 | Packing Units | Package 1 Weight | 322 g
21000 | XVBC8B4 | Packing Units | Package 2 Weight | 4.286 kg
21001 | XVBC8B4 | Offer Sustainability | Sustainable offer status | Green Premium product
21002 | XVBC8B4 | Offer Sustainability | REACh Regulation | REACh Declaration
21003 | XVBC8B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21004 | XVBC8B4 | Offer Sustainability | Mercury free | Yes
21005 | XVBC8B4 | Offer Sustainability | RoHS exemption information | Yes
21006 | XVBC8B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21007 | XVBC8B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21008 | XVBC8B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21009 | XVBC8B4 | Contractual warranty | Warranty | 18 months
21010 | XVBC8B5 | Main | range of product | Harmony XVB Universal
21011 | XVBC8B5 | Main | product or component type | Indicator bank
21012 | XVBC8B5 | Main | beacon or indicator bank unit type | Illuminated unit
21013 | XVBC8B5 | Main | signalling type | Flashing
21014 | XVBC8B5 | Main | mounting diameter | 70 mm
21015 | XVBC8B5 | Main | component name | XVBC
21016 | XVBC8B5 | Main | material | Polycarbonate
21017 | XVBC8B5 | Main | light source | Integral flash discharge tube, orange
21018 | XVBC8B5 | Main | bulb type | Flash discharge tube
21019 | XVBC8B5 | Main | [Us] rated supply voltage | 24 V AC/DC
21020 | XVBC8B5 | Main | flash energy | 10 J
21021 | XVBC8B5 | Complementary | assembly style | Customer assembly, up to 5 units
21022 | XVBC8B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21023 | XVBC8B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21024 | XVBC8B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21025 | XVBC8B5 | Complementary | current consumption | < 1300 mA AC < 850 mA DC
21026 | XVBC8B5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
21027 | XVBC8B5 | Complementary | flashing frequency | 1 Hz
21028 | XVBC8B5 | Complementary | CAD overall width | 70 mm
21029 | XVBC8B5 | Complementary | CAD overall height | 157 mm
21030 | XVBC8B5 | Complementary | CAD overall depth | 70 mm
21031 | XVBC8B5 | Complementary | net weight | 0.305 kg
21032 | XVBC8B5 | Environment | product certifications | UL 508 GOST CCC CSA C22-2 No 14
21033 | XVBC8B5 | Environment | standards | EN/IEC 60947-5-1
21034 | XVBC8B5 | Environment | protective treatment | TC
21035 | XVBC8B5 | Environment | ambient air temperature for storage | -40…70 °C
21036 | XVBC8B5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21037 | XVBC8B5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21038 | XVBC8B5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21039 | XVBC8B5 | Packing Units | Package 1 Weight | 320 g
21040 | XVBC8B5 | Packing Units | Package 2 Weight | 4.322 kg
21041 | XVBC8B5 | Offer Sustainability | Sustainable offer status | Green Premium product
21042 | XVBC8B5 | Offer Sustainability | REACh Regulation | REACh Declaration
21043 | XVBC8B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21044 | XVBC8B5 | Offer Sustainability | Mercury free | Yes
21045 | XVBC8B5 | Offer Sustainability | RoHS exemption information | Yes
21046 | XVBC8B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21047 | XVBC8B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21048 | XVBC8B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21049 | XVBC8B5 | Contractual warranty | Warranty | 18 months
21050 | XVBC8B6 | Main | range of product | Harmony XVB Universal
21051 | XVBC8B6 | Main | product or component type | Indicator bank
21052 | XVBC8B6 | Main | beacon or indicator bank unit type | Illuminated unit
21053 | XVBC8B6 | Main | signalling type | Flashing
21054 | XVBC8B6 | Main | mounting diameter | 70 mm
21055 | XVBC8B6 | Main | component name | XVBC
21056 | XVBC8B6 | Main | material | Polycarbonate
21057 | XVBC8B6 | Main | light source | Integral flash discharge tube, blue
21058 | XVBC8B6 | Main | bulb type | Flash discharge tube
21059 | XVBC8B6 | Main | [Us] rated supply voltage | 24 V AC/DC
21060 | XVBC8B6 | Main | flash energy | 10 J
21061 | XVBC8B6 | Complementary | assembly style | Customer assembly, up to 5 units
21062 | XVBC8B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21063 | XVBC8B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21064 | XVBC8B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21065 | XVBC8B6 | Complementary | current consumption | < 1300 mA AC < 850 mA DC
21066 | XVBC8B6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
21067 | XVBC8B6 | Complementary | flashing frequency | 1 Hz
21068 | XVBC8B6 | Complementary | CAD overall width | 70 mm
21069 | XVBC8B6 | Complementary | CAD overall height | 157 mm
21070 | XVBC8B6 | Complementary | CAD overall depth | 70 mm
21071 | XVBC8B6 | Complementary | net weight | 0.305 kg
21072 | XVBC8B6 | Environment | product certifications | UL 508 GOST CCC CSA C22-2 No 14
21073 | XVBC8B6 | Environment | standards | EN/IEC 60947-5-1
21074 | XVBC8B6 | Environment | protective treatment | TC
21075 | XVBC8B6 | Environment | ambient air temperature for storage | -40…70 °C
21076 | XVBC8B6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21077 | XVBC8B6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21078 | XVBC8B6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21079 | XVBC8B6 | Packing Units | Package 1 Weight | 0.320 kg
21080 | XVBC8B6 | Offer Sustainability | Sustainable offer status | Green Premium product
21081 | XVBC8B6 | Offer Sustainability | REACh Regulation | REACh Declaration
21082 | XVBC8B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21083 | XVBC8B6 | Offer Sustainability | Mercury free | Yes
21084 | XVBC8B6 | Offer Sustainability | RoHS exemption information | Yes
21085 | XVBC8B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21086 | XVBC8B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21087 | XVBC8B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21088 | XVBC8B6 | Contractual warranty | Warranty | 18 months
21089 | XVBC8B7 | Main | range of product | Harmony XVB Universal
21090 | XVBC8B7 | Main | product or component type | Indicator bank
21091 | XVBC8B7 | Main | beacon or indicator bank unit type | Illuminated unit
21092 | XVBC8B7 | Main | signalling type | Flashing
21093 | XVBC8B7 | Main | mounting diameter | 70 mm
21094 | XVBC8B7 | Main | component name | XVBC
21095 | XVBC8B7 | Main | material | Polycarbonate
21096 | XVBC8B7 | Main | light source | Integral flash discharge tube, clear
21097 | XVBC8B7 | Main | bulb type | Flash discharge tube
21098 | XVBC8B7 | Main | [Us] rated supply voltage | 24 V AC/DC
21099 | XVBC8B7 | Main | flash energy | 10 J
21100 | XVBC8B7 | Complementary | assembly style | Customer assembly, up to 5 units
21101 | XVBC8B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21102 | XVBC8B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21103 | XVBC8B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21104 | XVBC8B7 | Complementary | current consumption | < 1300 mA AC < 850 mA DC
21105 | XVBC8B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
21106 | XVBC8B7 | Complementary | flashing frequency | 1 Hz
21107 | XVBC8B7 | Complementary | illuminating intensity | 26 cd
21108 | XVBC8B7 | Complementary | CAD overall width | 70 mm
21109 | XVBC8B7 | Complementary | CAD overall height | 157 mm
21110 | XVBC8B7 | Complementary | CAD overall depth | 70 mm
21111 | XVBC8B7 | Complementary | net weight | 0.305 kg
21112 | XVBC8B7 | Environment | product certifications | CCC CSA C22-2 No 14 UL 508 GOST
21113 | XVBC8B7 | Environment | standards | EN/IEC 60947-5-1
21114 | XVBC8B7 | Environment | protective treatment | TC
21115 | XVBC8B7 | Environment | ambient air temperature for storage | -40…70 °C
21116 | XVBC8B7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21117 | XVBC8B7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21118 | XVBC8B7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21119 | XVBC8B7 | Packing Units | Package 1 Weight | 317 g
21120 | XVBC8B7 | Packing Units | Package 2 Weight | 4.28 kg
21121 | XVBC8B7 | Offer Sustainability | Sustainable offer status | Green Premium product
21122 | XVBC8B7 | Offer Sustainability | REACh Regulation | REACh Declaration
21123 | XVBC8B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21124 | XVBC8B7 | Offer Sustainability | Mercury free | Yes
21125 | XVBC8B7 | Offer Sustainability | RoHS exemption information | Yes
21126 | XVBC8B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21127 | XVBC8B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21128 | XVBC8B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21129 | XVBC8B7 | Contractual warranty | Warranty | 18 months
21130 | XVBC8B8 | Main | range of product | Harmony XVB Universal
21131 | XVBC8B8 | Main | product or component type | Indicator bank
21132 | XVBC8B8 | Main | beacon or indicator bank unit type | Illuminated unit
21133 | XVBC8B8 | Main | signalling type | Flashing
21134 | XVBC8B8 | Main | mounting diameter | 70 mm
21135 | XVBC8B8 | Main | component name | XVBC
21136 | XVBC8B8 | Main | material | Polycarbonate
21137 | XVBC8B8 | Main | light source | Integral flash discharge tube, yellow
21138 | XVBC8B8 | Main | bulb type | Flash discharge tube
21139 | XVBC8B8 | Main | [Us] rated supply voltage | 24 V AC/DC
21140 | XVBC8B8 | Main | flash energy | 10 J
21141 | XVBC8B8 | Complementary | assembly style | Customer assembly, up to 5 units
21142 | XVBC8B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21143 | XVBC8B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21144 | XVBC8B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21145 | XVBC8B8 | Complementary | current consumption | < 1300 mA AC < 850 mA DC
21146 | XVBC8B8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
21147 | XVBC8B8 | Complementary | flashing frequency | 1 Hz
21148 | XVBC8B8 | Complementary | CAD overall width | 70 mm
21149 | XVBC8B8 | Complementary | CAD overall height | 157 mm
21150 | XVBC8B8 | Complementary | CAD overall depth | 70 mm
21151 | XVBC8B8 | Complementary | net weight | 0.305 kg
21152 | XVBC8B8 | Environment | product certifications | CSA C22-2 No 14 GOST UL 508 CCC
21153 | XVBC8B8 | Environment | standards | EN/IEC 60947-5-1
21154 | XVBC8B8 | Environment | protective treatment | TC
21155 | XVBC8B8 | Environment | ambient air temperature for storage | -40…70 °C
21156 | XVBC8B8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21157 | XVBC8B8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21158 | XVBC8B8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21159 | XVBC8B8 | Packing Units | Package 1 Weight | 314 g
21160 | XVBC8B8 | Offer Sustainability | Sustainable offer status | Green Premium product
21161 | XVBC8B8 | Offer Sustainability | REACh Regulation | REACh Declaration
21162 | XVBC8B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21163 | XVBC8B8 | Offer Sustainability | Mercury free | Yes
21164 | XVBC8B8 | Offer Sustainability | RoHS exemption information | Yes
21165 | XVBC8B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21166 | XVBC8B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21167 | XVBC8B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21168 | XVBC8B8 | Contractual warranty | Warranty | 18 months
21169 | XVBC8E5 | Main | range of product | Harmony XVB Universal
21170 | XVBC8E5 | Main | product or component type | Indicator bank
21171 | XVBC8E5 | Main | beacon or indicator bank unit type | Illuminated unit
21172 | XVBC8E5 | Main | signalling type | Flashing
21173 | XVBC8E5 | Main | mounting diameter | 70 mm
21174 | XVBC8E5 | Main | component name | XVBC
21175 | XVBC8E5 | Main | material | Polycarbonate
21176 | XVBC8E5 | Main | light source | Integral flash discharge tube, orange
21177 | XVBC8E5 | Main | bulb type | Flash discharge tube
21178 | XVBC8E5 | Main | [Us] rated supply voltage | 48 V AC/DC
21179 | XVBC8E5 | Main | flash energy | 10 J
21180 | XVBC8E5 | Complementary | assembly style | Customer assembly, up to 5 units
21181 | XVBC8E5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21182 | XVBC8E5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21183 | XVBC8E5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21184 | XVBC8E5 | Complementary | current consumption | < 400 mA DC < 650 mA AC
21185 | XVBC8E5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
21186 | XVBC8E5 | Complementary | flashing frequency | 1 Hz
21187 | XVBC8E5 | Complementary | net weight | 0.315 kg
21188 | XVBC8E5 | Environment | product certifications | CCC CSA C22-2 No 14 UL 508 GOST
21189 | XVBC8E5 | Environment | standards | EN/IEC 60947-5-1
21190 | XVBC8E5 | Environment | protective treatment | TC
21191 | XVBC8E5 | Environment | ambient air temperature for storage | -40…70 °C
21192 | XVBC8E5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21193 | XVBC8E5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21194 | XVBC8E5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21195 | XVBC8E5 | Packing Units | Package 1 Weight | 322 g
21196 | XVBC8E5 | Offer Sustainability | Sustainable offer status | Green Premium product
21197 | XVBC8E5 | Offer Sustainability | REACh Regulation | REACh Declaration
21198 | XVBC8E5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21199 | XVBC8E5 | Offer Sustainability | Mercury free | Yes
21200 | XVBC8E5 | Offer Sustainability | RoHS exemption information | Yes
21201 | XVBC8E5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21202 | XVBC8E5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21203 | XVBC8E5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21204 | XVBC8E5 | Contractual warranty | Warranty | 18 months
21205 | XVBC8G3 | Main | range of product | Harmony XVB Universal
21206 | XVBC8G3 | Main | product or component type | Indicator bank
21207 | XVBC8G3 | Main | beacon or indicator bank unit type | Illuminated unit
21208 | XVBC8G3 | Main | signalling type | Flashing
21209 | XVBC8G3 | Main | mounting diameter | 70 mm
21210 | XVBC8G3 | Main | component name | XVBC
21211 | XVBC8G3 | Main | material | Polycarbonate
21212 | XVBC8G3 | Main | light source | Integral flash discharge tube, green
21213 | XVBC8G3 | Main | bulb type | Flash discharge tube
21214 | XVBC8G3 | Main | [Us] rated supply voltage | 120 V AC
21215 | XVBC8G3 | Main | flash energy | 10 J
21216 | XVBC8G3 | Complementary | assembly style | Customer assembly, up to 5 units
21217 | XVBC8G3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21218 | XVBC8G3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21219 | XVBC8G3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21220 | XVBC8G3 | Complementary | current consumption | < 290 mA AC
21221 | XVBC8G3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
21222 | XVBC8G3 | Complementary | flashing frequency | 1 Hz
21223 | XVBC8G3 | Complementary | CAD overall width | 70 mm
21224 | XVBC8G3 | Complementary | CAD overall height | 157 mm
21225 | XVBC8G3 | Complementary | CAD overall depth | 70 mm
21226 | XVBC8G3 | Complementary | net weight | 0.315 kg
21227 | XVBC8G3 | Environment | product certifications | CCC CSA C22-2 No 14 GOST UL 508
21228 | XVBC8G3 | Environment | standards | EN/IEC 60947-5-1
21229 | XVBC8G3 | Environment | protective treatment | TC
21230 | XVBC8G3 | Environment | ambient air temperature for storage | -40…70 °C
21231 | XVBC8G3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21232 | XVBC8G3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21233 | XVBC8G3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21234 | XVBC8G3 | Packing Units | Package 1 Weight | 315 g
21235 | XVBC8G3 | Offer Sustainability | Sustainable offer status | Green Premium product
21236 | XVBC8G3 | Offer Sustainability | REACh Regulation | REACh Declaration
21237 | XVBC8G3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21238 | XVBC8G3 | Offer Sustainability | Mercury free | Yes
21239 | XVBC8G3 | Offer Sustainability | RoHS exemption information | Yes
21240 | XVBC8G3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21241 | XVBC8G3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21242 | XVBC8G3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21243 | XVBC8G3 | Contractual warranty | Warranty | 18 months
21244 | XVBC8G4 | Main | range of product | Harmony XVB Universal
21245 | XVBC8G4 | Main | product or component type | Indicator bank
21246 | XVBC8G4 | Main | beacon or indicator bank unit type | Illuminated unit
21247 | XVBC8G4 | Main | signalling type | Flashing
21248 | XVBC8G4 | Main | mounting diameter | 70 mm
21249 | XVBC8G4 | Main | component name | XVBC
21250 | XVBC8G4 | Main | material | Polycarbonate
21251 | XVBC8G4 | Main | light source | Integral flash discharge tube, red
21252 | XVBC8G4 | Main | bulb type | Flash discharge tube
21253 | XVBC8G4 | Main | [Us] rated supply voltage | 120 V AC
21254 | XVBC8G4 | Main | flash energy | 10 J
21255 | XVBC8G4 | Complementary | assembly style | Customer assembly, up to 5 units
21256 | XVBC8G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21257 | XVBC8G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21258 | XVBC8G4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21259 | XVBC8G4 | Complementary | current consumption | < 290 mA AC
21260 | XVBC8G4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
21261 | XVBC8G4 | Complementary | flashing frequency | 1 Hz
21262 | XVBC8G4 | Complementary | CAD overall width | 70 mm
21263 | XVBC8G4 | Complementary | CAD overall height | 157 mm
21264 | XVBC8G4 | Complementary | CAD overall depth | 70 mm
21265 | XVBC8G4 | Complementary | net weight | 0.315 kg
21266 | XVBC8G4 | Environment | product certifications | CCC GOST CSA C22-2 No 14 UL 508
21267 | XVBC8G4 | Environment | standards | EN/IEC 60947-5-1
21268 | XVBC8G4 | Environment | protective treatment | TC
21269 | XVBC8G4 | Environment | ambient air temperature for storage | -40…70 °C
21270 | XVBC8G4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21271 | XVBC8G4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21272 | XVBC8G4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21273 | XVBC8G4 | Packing Units | Package 1 Weight | 315 g
21274 | XVBC8G4 | Offer Sustainability | Sustainable offer status | Green Premium product
21275 | XVBC8G4 | Offer Sustainability | REACh Regulation | REACh Declaration
21276 | XVBC8G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21277 | XVBC8G4 | Offer Sustainability | Mercury free | Yes
21278 | XVBC8G4 | Offer Sustainability | RoHS exemption information | Yes
21279 | XVBC8G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21280 | XVBC8G4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21281 | XVBC8G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21282 | XVBC8G4 | Contractual warranty | Warranty | 18 months
21283 | XVBC8G5 | Main | range of product | Harmony XVB Universal
21284 | XVBC8G5 | Main | product or component type | Indicator bank
21285 | XVBC8G5 | Main | beacon or indicator bank unit type | Illuminated unit
21286 | XVBC8G5 | Main | signalling type | Flashing
21287 | XVBC8G5 | Main | mounting diameter | 70 mm
21288 | XVBC8G5 | Main | component name | XVBC
21289 | XVBC8G5 | Main | material | Polycarbonate
21290 | XVBC8G5 | Main | light source | Integral flash discharge tube, orange
21291 | XVBC8G5 | Main | bulb type | Flash discharge tube
21292 | XVBC8G5 | Main | [Us] rated supply voltage | 120 V AC
21293 | XVBC8G5 | Main | flash energy | 10 J
21294 | XVBC8G5 | Complementary | assembly style | Customer assembly, up to 5 units
21295 | XVBC8G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21296 | XVBC8G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21297 | XVBC8G5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21298 | XVBC8G5 | Complementary | current consumption | < 290 mA AC
21299 | XVBC8G5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
21300 | XVBC8G5 | Complementary | flashing frequency | 1 Hz
21301 | XVBC8G5 | Complementary | CAD overall width | 70 mm
21302 | XVBC8G5 | Complementary | CAD overall height | 157 mm
21303 | XVBC8G5 | Complementary | CAD overall depth | 70 mm
21304 | XVBC8G5 | Complementary | net weight | 0.315 kg
21305 | XVBC8G5 | Environment | product certifications | GOST CSA C22-2 No 14 CCC UL 508
21306 | XVBC8G5 | Environment | standards | EN/IEC 60947-5-1
21307 | XVBC8G5 | Environment | protective treatment | TC
21308 | XVBC8G5 | Environment | ambient air temperature for storage | -40…70 °C
21309 | XVBC8G5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21310 | XVBC8G5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21311 | XVBC8G5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21312 | XVBC8G5 | Packing Units | Package 1 Weight | 315 g
21313 | XVBC8G5 | Packing Units | Package 2 Weight | 4.493 kg
21314 | XVBC8G5 | Offer Sustainability | Sustainable offer status | Green Premium product
21315 | XVBC8G5 | Offer Sustainability | REACh Regulation | REACh Declaration
21316 | XVBC8G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21317 | XVBC8G5 | Offer Sustainability | Mercury free | Yes
21318 | XVBC8G5 | Offer Sustainability | RoHS exemption information | Yes
21319 | XVBC8G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21320 | XVBC8G5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21321 | XVBC8G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21322 | XVBC8G5 | Contractual warranty | Warranty | 18 months
21323 | XVBC8G6 | Main | range of product | Harmony XVB Universal
21324 | XVBC8G6 | Main | product or component type | Indicator bank
21325 | XVBC8G6 | Main | beacon or indicator bank unit type | Illuminated unit
21326 | XVBC8G6 | Main | signalling type | Flashing
21327 | XVBC8G6 | Main | mounting diameter | 70 mm
21328 | XVBC8G6 | Main | component name | XVBC
21329 | XVBC8G6 | Main | material | Polycarbonate
21330 | XVBC8G6 | Main | light source | Integral flash discharge tube, blue
21331 | XVBC8G6 | Main | bulb type | Flash discharge tube
21332 | XVBC8G6 | Main | [Us] rated supply voltage | 120 V AC
21333 | XVBC8G6 | Main | flash energy | 10 J
21334 | XVBC8G6 | Complementary | assembly style | Customer assembly, up to 5 units
21335 | XVBC8G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21336 | XVBC8G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21337 | XVBC8G6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21338 | XVBC8G6 | Complementary | current consumption | < 290 mA AC
21339 | XVBC8G6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
21340 | XVBC8G6 | Complementary | flashing frequency | 1 Hz
21341 | XVBC8G6 | Complementary | CAD overall width | 70 mm
21342 | XVBC8G6 | Complementary | CAD overall height | 157 mm
21343 | XVBC8G6 | Complementary | CAD overall depth | 70 mm
21344 | XVBC8G6 | Complementary | net weight | 0.315 kg
21345 | XVBC8G6 | Environment | product certifications | UL 508 CCC GOST CSA C22-2 No 14
21346 | XVBC8G6 | Environment | standards | EN/IEC 60947-5-1
21347 | XVBC8G6 | Environment | protective treatment | TC
21348 | XVBC8G6 | Environment | ambient air temperature for storage | -40…70 °C
21349 | XVBC8G6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21350 | XVBC8G6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21351 | XVBC8G6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21352 | XVBC8G6 | Packing Units | Package 1 Weight | 315 g
21353 | XVBC8G6 | Offer Sustainability | Sustainable offer status | Green Premium product
21354 | XVBC8G6 | Offer Sustainability | REACh Regulation | REACh Declaration
21355 | XVBC8G6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21356 | XVBC8G6 | Offer Sustainability | Mercury free | Yes
21357 | XVBC8G6 | Offer Sustainability | RoHS exemption information | Yes
21358 | XVBC8G6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21359 | XVBC8G6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21360 | XVBC8G6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21361 | XVBC8G6 | Contractual warranty | Warranty | 18 months
21362 | XVBC8G7 | Main | range of product | Harmony XVB Universal
21363 | XVBC8G7 | Main | product or component type | Indicator bank
21364 | XVBC8G7 | Main | beacon or indicator bank unit type | Illuminated unit
21365 | XVBC8G7 | Main | signalling type | Flashing
21366 | XVBC8G7 | Main | mounting diameter | 70 mm
21367 | XVBC8G7 | Main | component name | XVBC
21368 | XVBC8G7 | Main | material | Polycarbonate
21369 | XVBC8G7 | Main | light source | Integral flash discharge tube, clear
21370 | XVBC8G7 | Main | bulb type | Flash discharge tube
21371 | XVBC8G7 | Main | [Us] rated supply voltage | 120 V AC
21372 | XVBC8G7 | Main | flash energy | 10 J
21373 | XVBC8G7 | Complementary | assembly style | Customer assembly, up to 5 units
21374 | XVBC8G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21375 | XVBC8G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21376 | XVBC8G7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21377 | XVBC8G7 | Complementary | current consumption | < 290 mA AC
21378 | XVBC8G7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
21379 | XVBC8G7 | Complementary | flashing frequency | 1 Hz
21380 | XVBC8G7 | Complementary | illuminating intensity | 26 cd
21381 | XVBC8G7 | Complementary | CAD overall width | 70 mm
21382 | XVBC8G7 | Complementary | CAD overall height | 157 mm
21383 | XVBC8G7 | Complementary | CAD overall depth | 70 mm
21384 | XVBC8G7 | Complementary | net weight | 0.315 kg
21385 | XVBC8G7 | Environment | product certifications | GOST CSA C22-2 No 14 CCC UL 508
21386 | XVBC8G7 | Environment | standards | EN/IEC 60947-5-1
21387 | XVBC8G7 | Environment | protective treatment | TC
21388 | XVBC8G7 | Environment | ambient air temperature for storage | -40…70 °C
21389 | XVBC8G7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21390 | XVBC8G7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21391 | XVBC8G7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21392 | XVBC8G7 | Packing Units | Package 1 Weight | 315 g
21393 | XVBC8G7 | Offer Sustainability | Sustainable offer status | Green Premium product
21394 | XVBC8G7 | Offer Sustainability | REACh Regulation | REACh Declaration
21395 | XVBC8G7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21396 | XVBC8G7 | Offer Sustainability | Mercury free | Yes
21397 | XVBC8G7 | Offer Sustainability | RoHS exemption information | Yes
21398 | XVBC8G7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21399 | XVBC8G7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21400 | XVBC8G7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21401 | XVBC8G7 | Contractual warranty | Warranty | 18 months
21402 | XVBC8G8 | Main | range of product | Harmony XVB Universal
21403 | XVBC8G8 | Main | product or component type | Indicator bank
21404 | XVBC8G8 | Main | beacon or indicator bank unit type | Illuminated unit
21405 | XVBC8G8 | Main | signalling type | Flashing
21406 | XVBC8G8 | Main | mounting diameter | 70 mm
21407 | XVBC8G8 | Main | component name | XVBC
21408 | XVBC8G8 | Main | material | Polycarbonate
21409 | XVBC8G8 | Main | light source | Integral flash discharge tube, yellow
21410 | XVBC8G8 | Main | bulb type | Flash discharge tube
21411 | XVBC8G8 | Main | [Us] rated supply voltage | 120 V AC
21412 | XVBC8G8 | Main | flash energy | 10 J
21413 | XVBC8G8 | Complementary | assembly style | Customer assembly, up to 5 units
21414 | XVBC8G8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21415 | XVBC8G8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21416 | XVBC8G8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21417 | XVBC8G8 | Complementary | current consumption | < 290 mA AC
21418 | XVBC8G8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
21419 | XVBC8G8 | Complementary | flashing frequency | 1 Hz
21420 | XVBC8G8 | Complementary | CAD overall width | 70 mm
21421 | XVBC8G8 | Complementary | CAD overall height | 157 mm
21422 | XVBC8G8 | Complementary | CAD overall depth | 70 mm
21423 | XVBC8G8 | Complementary | net weight | 0.315 kg
21424 | XVBC8G8 | Environment | product certifications | GOST CSA C22-2 No 14 UL 508 CCC
21425 | XVBC8G8 | Environment | standards | EN/IEC 60947-5-1
21426 | XVBC8G8 | Environment | protective treatment | TC
21427 | XVBC8G8 | Environment | ambient air temperature for storage | -40…70 °C
21428 | XVBC8G8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21429 | XVBC8G8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21430 | XVBC8G8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21431 | XVBC8G8 | Packing Units | Package 1 Weight | 315 g
21432 | XVBC8G8 | Offer Sustainability | Sustainable offer status | Green Premium product
21433 | XVBC8G8 | Offer Sustainability | REACh Regulation | REACh Declaration
21434 | XVBC8G8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21435 | XVBC8G8 | Offer Sustainability | Mercury free | Yes
21436 | XVBC8G8 | Offer Sustainability | RoHS exemption information | Yes
21437 | XVBC8G8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21438 | XVBC8G8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21439 | XVBC8G8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21440 | XVBC8G8 | Contractual warranty | Warranty | 18 months
21441 | XVBC8M3 | Main | range of product | Harmony XVB Universal
21442 | XVBC8M3 | Main | product or component type | Indicator bank
21443 | XVBC8M3 | Main | beacon or indicator bank unit type | Illuminated unit
21444 | XVBC8M3 | Main | signalling type | Flashing
21445 | XVBC8M3 | Main | mounting diameter | 70 mm
21446 | XVBC8M3 | Main | component name | XVBC
21447 | XVBC8M3 | Main | material | Polycarbonate
21448 | XVBC8M3 | Main | light source | Integral flash discharge tube, green
21449 | XVBC8M3 | Main | bulb type | Flash discharge tube
21450 | XVBC8M3 | Main | [Us] rated supply voltage | 230 V AC
21451 | XVBC8M3 | Main | flash energy | 10 J
21452 | XVBC8M3 | Complementary | assembly style | Customer assembly, up to 5 units
21453 | XVBC8M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21454 | XVBC8M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21455 | XVBC8M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21456 | XVBC8M3 | Complementary | current consumption | < 280 mA AC
21457 | XVBC8M3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
21458 | XVBC8M3 | Complementary | flashing frequency | 1 Hz
21459 | XVBC8M3 | Complementary | CAD overall width | 70 mm
21460 | XVBC8M3 | Complementary | CAD overall height | 157 mm
21461 | XVBC8M3 | Complementary | CAD overall depth | 70 mm
21462 | XVBC8M3 | Complementary | net weight | 0.315 kg
21463 | XVBC8M3 | Environment | product certifications | CSA C22-2 No 14 CCC UL 508 GOST
21464 | XVBC8M3 | Environment | standards | EN/IEC 60947-5-1
21465 | XVBC8M3 | Environment | protective treatment | TC
21466 | XVBC8M3 | Environment | ambient air temperature for storage | -40…70 °C
21467 | XVBC8M3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21468 | XVBC8M3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21469 | XVBC8M3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21470 | XVBC8M3 | Packing Units | Package 1 Weight | 0.329 kg
21471 | XVBC8M3 | Offer Sustainability | Sustainable offer status | Green Premium product
21472 | XVBC8M3 | Offer Sustainability | REACh Regulation | REACh Declaration
21473 | XVBC8M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21474 | XVBC8M3 | Offer Sustainability | Mercury free | Yes
21475 | XVBC8M3 | Offer Sustainability | RoHS exemption information | Yes
21476 | XVBC8M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21477 | XVBC8M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21478 | XVBC8M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21479 | XVBC8M3 | Contractual warranty | Warranty | 18 months
21480 | XVBC8M4 | Main | range of product | Harmony XVB Universal
21481 | XVBC8M4 | Main | product or component type | Indicator bank
21482 | XVBC8M4 | Main | beacon or indicator bank unit type | Illuminated unit
21483 | XVBC8M4 | Main | signalling type | Flashing
21484 | XVBC8M4 | Main | mounting diameter | 70 mm
21485 | XVBC8M4 | Main | component name | XVBC
21486 | XVBC8M4 | Main | material | Polycarbonate
21487 | XVBC8M4 | Main | light source | Integral flash discharge tube, red
21488 | XVBC8M4 | Main | bulb type | Flash discharge tube
21489 | XVBC8M4 | Main | [Us] rated supply voltage | 230 V AC
21490 | XVBC8M4 | Main | flash energy | 10 J
21491 | XVBC8M4 | Complementary | assembly style | Customer assembly, up to 5 units
21492 | XVBC8M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21493 | XVBC8M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21494 | XVBC8M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21495 | XVBC8M4 | Complementary | current consumption | < 280 mA AC
21496 | XVBC8M4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
21497 | XVBC8M4 | Complementary | flashing frequency | 1 Hz
21498 | XVBC8M4 | Complementary | CAD overall width | 70 mm
21499 | XVBC8M4 | Complementary | CAD overall height | 157 mm
21500 | XVBC8M4 | Complementary | CAD overall depth | 70 mm
21501 | XVBC8M4 | Complementary | net weight | 0.315 kg
21502 | XVBC8M4 | Environment | product certifications | UL 508 CCC CSA C22-2 No 14 GOST
21503 | XVBC8M4 | Environment | standards | EN/IEC 60947-5-1
21504 | XVBC8M4 | Environment | protective treatment | TC
21505 | XVBC8M4 | Environment | ambient air temperature for storage | -40…70 °C
21506 | XVBC8M4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21507 | XVBC8M4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21508 | XVBC8M4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21509 | XVBC8M4 | Packing Units | Package 1 Weight | 340 g
21510 | XVBC8M4 | Packing Units | Package 2 Weight | 4.416 kg
21511 | XVBC8M4 | Offer Sustainability | Sustainable offer status | Green Premium product
21512 | XVBC8M4 | Offer Sustainability | REACh Regulation | REACh Declaration
21513 | XVBC8M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21514 | XVBC8M4 | Offer Sustainability | Mercury free | Yes
21515 | XVBC8M4 | Offer Sustainability | RoHS exemption information | Yes
21516 | XVBC8M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21517 | XVBC8M4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21518 | XVBC8M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21519 | XVBC8M4 | Contractual warranty | Warranty | 18 months
21520 | XVBC8M5 | Main | range of product | Harmony XVB Universal
21521 | XVBC8M5 | Main | product or component type | Indicator bank
21522 | XVBC8M5 | Main | beacon or indicator bank unit type | Illuminated unit
21523 | XVBC8M5 | Main | signalling type | Flashing
21524 | XVBC8M5 | Main | mounting diameter | 70 mm
21525 | XVBC8M5 | Main | component name | XVBC
21526 | XVBC8M5 | Main | material | Polycarbonate
21527 | XVBC8M5 | Main | light source | Integral flash discharge tube, orange
21528 | XVBC8M5 | Main | bulb type | Flash discharge tube
21529 | XVBC8M5 | Main | [Us] rated supply voltage | 230 V AC
21530 | XVBC8M5 | Main | flash energy | 10 J
21531 | XVBC8M5 | Complementary | assembly style | Customer assembly, up to 5 units
21532 | XVBC8M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21533 | XVBC8M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21534 | XVBC8M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21535 | XVBC8M5 | Complementary | current consumption | < 280 mA AC
21536 | XVBC8M5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
21537 | XVBC8M5 | Complementary | flashing frequency | 1 Hz
21538 | XVBC8M5 | Complementary | CAD overall width | 70 mm
21539 | XVBC8M5 | Complementary | CAD overall height | 157 mm
21540 | XVBC8M5 | Complementary | CAD overall depth | 70 mm
21541 | XVBC8M5 | Complementary | net weight | 0.315 kg
21542 | XVBC8M5 | Environment | product certifications | CSA C22-2 No 14 UL 508 CCC GOST
21543 | XVBC8M5 | Environment | standards | EN/IEC 60947-5-1
21544 | XVBC8M5 | Environment | protective treatment | TC
21545 | XVBC8M5 | Environment | ambient air temperature for storage | -40…70 °C
21546 | XVBC8M5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21547 | XVBC8M5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21548 | XVBC8M5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21549 | XVBC8M5 | Packing Units | Package 1 Weight | 333 g
21550 | XVBC8M5 | Packing Units | Package 2 Weight | 4.477 kg
21551 | XVBC8M5 | Offer Sustainability | Sustainable offer status | Green Premium product
21552 | XVBC8M5 | Offer Sustainability | REACh Regulation | REACh Declaration
21553 | XVBC8M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21554 | XVBC8M5 | Offer Sustainability | Mercury free | Yes
21555 | XVBC8M5 | Offer Sustainability | RoHS exemption information | Yes
21556 | XVBC8M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21557 | XVBC8M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21558 | XVBC8M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21559 | XVBC8M5 | Contractual warranty | Warranty | 18 months
21560 | XVBC8M6 | Main | range of product | Harmony XVB Universal
21561 | XVBC8M6 | Main | product or component type | Indicator bank
21562 | XVBC8M6 | Main | beacon or indicator bank unit type | Illuminated unit
21563 | XVBC8M6 | Main | signalling type | Flashing
21564 | XVBC8M6 | Main | mounting diameter | 70 mm
21565 | XVBC8M6 | Main | component name | XVBC
21566 | XVBC8M6 | Main | material | Polycarbonate
21567 | XVBC8M6 | Main | light source | Integral flash discharge tube, blue
21568 | XVBC8M6 | Main | bulb type | Flash discharge tube
21569 | XVBC8M6 | Main | [Us] rated supply voltage | 230 V AC
21570 | XVBC8M6 | Main | flash energy | 10 J
21571 | XVBC8M6 | Complementary | assembly style | Customer assembly, up to 5 units
21572 | XVBC8M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21573 | XVBC8M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21574 | XVBC8M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21575 | XVBC8M6 | Complementary | current consumption | < 280 mA AC
21576 | XVBC8M6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
21577 | XVBC8M6 | Complementary | flashing frequency | 1 Hz
21578 | XVBC8M6 | Complementary | CAD overall width | 70 mm
21579 | XVBC8M6 | Complementary | CAD overall height | 157 mm
21580 | XVBC8M6 | Complementary | CAD overall depth | 70 mm
21581 | XVBC8M6 | Complementary | net weight | 0.315 kg
21582 | XVBC8M6 | Environment | product certifications | CCC CSA C22-2 No 14 GOST UL 508
21583 | XVBC8M6 | Environment | standards | EN/IEC 60947-5-1
21584 | XVBC8M6 | Environment | protective treatment | TC
21585 | XVBC8M6 | Environment | ambient air temperature for storage | -40…70 °C
21586 | XVBC8M6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21587 | XVBC8M6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21588 | XVBC8M6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21589 | XVBC8M6 | Packing Units | Package 1 Weight | 0.329 kg
21590 | XVBC8M6 | Offer Sustainability | Sustainable offer status | Green Premium product
21591 | XVBC8M6 | Offer Sustainability | REACh Regulation | REACh Declaration
21592 | XVBC8M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21593 | XVBC8M6 | Offer Sustainability | Mercury free | Yes
21594 | XVBC8M6 | Offer Sustainability | RoHS exemption information | Yes
21595 | XVBC8M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21596 | XVBC8M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21597 | XVBC8M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21598 | XVBC8M6 | Contractual warranty | Warranty | 18 months
21599 | XVBC8M7 | Main | range of product | Harmony XVB Universal
21600 | XVBC8M7 | Main | product or component type | Indicator bank
21601 | XVBC8M7 | Main | beacon or indicator bank unit type | Illuminated unit
21602 | XVBC8M7 | Main | signalling type | Flashing
21603 | XVBC8M7 | Main | mounting diameter | 70 mm
21604 | XVBC8M7 | Main | component name | XVBC
21605 | XVBC8M7 | Main | material | Polycarbonate
21606 | XVBC8M7 | Main | light source | Integral flash discharge tube, clear
21607 | XVBC8M7 | Main | bulb type | Flash discharge tube
21608 | XVBC8M7 | Main | [Us] rated supply voltage | 230 V AC
21609 | XVBC8M7 | Main | flash energy | 10 J
21610 | XVBC8M7 | Complementary | assembly style | Customer assembly, up to 5 units
21611 | XVBC8M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21612 | XVBC8M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21613 | XVBC8M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21614 | XVBC8M7 | Complementary | current consumption | < 280 mA AC
21615 | XVBC8M7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
21616 | XVBC8M7 | Complementary | flashing frequency | 1 Hz
21617 | XVBC8M7 | Complementary | illuminating intensity | 26 cd
21618 | XVBC8M7 | Complementary | CAD overall width | 70 mm
21619 | XVBC8M7 | Complementary | CAD overall height | 157 mm
21620 | XVBC8M7 | Complementary | CAD overall depth | 70 mm
21621 | XVBC8M7 | Complementary | net weight | 0.315 kg
21622 | XVBC8M7 | Environment | product certifications | CCC GOST CSA C22-2 No 14 UL 508
21623 | XVBC8M7 | Environment | standards | EN/IEC 60947-5-1
21624 | XVBC8M7 | Environment | protective treatment | TC
21625 | XVBC8M7 | Environment | ambient air temperature for storage | -40…70 °C
21626 | XVBC8M7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21627 | XVBC8M7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21628 | XVBC8M7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21629 | XVBC8M7 | Packing Units | Package 1 Weight | 0.329 kg
21630 | XVBC8M7 | Offer Sustainability | Sustainable offer status | Green Premium product
21631 | XVBC8M7 | Offer Sustainability | REACh Regulation | REACh Declaration
21632 | XVBC8M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21633 | XVBC8M7 | Offer Sustainability | Mercury free | Yes
21634 | XVBC8M7 | Offer Sustainability | RoHS exemption information | Yes
21635 | XVBC8M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21636 | XVBC8M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21637 | XVBC8M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21638 | XVBC8M7 | Contractual warranty | Warranty | 18 months
21639 | XVBC8M8 | Main | range of product | Harmony XVB Universal
21640 | XVBC8M8 | Main | product or component type | Indicator bank
21641 | XVBC8M8 | Main | beacon or indicator bank unit type | Illuminated unit
21642 | XVBC8M8 | Main | signalling type | Flashing
21643 | XVBC8M8 | Main | mounting diameter | 70 mm
21644 | XVBC8M8 | Main | component name | XVBC
21645 | XVBC8M8 | Main | material | Polycarbonate
21646 | XVBC8M8 | Main | light source | Integral flash discharge tube, yellow
21647 | XVBC8M8 | Main | bulb type | Flash discharge tube
21648 | XVBC8M8 | Main | [Us] rated supply voltage | 230 V AC
21649 | XVBC8M8 | Main | flash energy | 10 J
21650 | XVBC8M8 | Complementary | assembly style | Customer assembly, up to 5 units
21651 | XVBC8M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
21652 | XVBC8M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
21653 | XVBC8M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
21654 | XVBC8M8 | Complementary | current consumption | < 280 mA AC
21655 | XVBC8M8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
21656 | XVBC8M8 | Complementary | flashing frequency | 1 Hz
21657 | XVBC8M8 | Complementary | CAD overall width | 70 mm
21658 | XVBC8M8 | Complementary | CAD overall height | 157 mm
21659 | XVBC8M8 | Complementary | CAD overall depth | 70 mm
21660 | XVBC8M8 | Complementary | net weight | 0.315 kg
21661 | XVBC8M8 | Environment | product certifications | UL 508 CCC CSA C22-2 No 14 GOST
21662 | XVBC8M8 | Environment | standards | EN/IEC 60947-5-1
21663 | XVBC8M8 | Environment | protective treatment | TC
21664 | XVBC8M8 | Environment | ambient air temperature for storage | -40…70 °C
21665 | XVBC8M8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140
21666 | XVBC8M8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529
21667 | XVBC8M8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
21668 | XVBC8M8 | Packing Units | Package 1 Weight | 0.329 kg
21669 | XVBC8M8 | Offer Sustainability | Sustainable offer status | Green Premium product
21670 | XVBC8M8 | Offer Sustainability | REACh Regulation | REACh Declaration
21671 | XVBC8M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
21672 | XVBC8M8 | Offer Sustainability | Mercury free | Yes
21673 | XVBC8M8 | Offer Sustainability | RoHS exemption information | Yes
21674 | XVBC8M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
21675 | XVBC8M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
21676 | XVBC8M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
21677 | XVBC8M8 | Contractual warranty | Warranty | 18 months
21678 | RHR4138J | Main | range of product | Zelio Relay
21679 | RHR4138J | Main | product or component type | Plug-in relay Timing relay
21680 | RHR4138J | Main | device short name | RHR
21681 | RHR4138J | Main | contacts type and composition | 4 C/O
21682 | RHR4138J | Main | contact operation | Standard
21683 | RHR4138J | Main | [Uc] control circuit voltage | 12 V AC/DC 50/60 Hz
21684 | RHR4138J | Main | time delay type | Off-delay
21685 | RHR4138J | Main | time delay range | 1.25...24 s 2...40 min 12.5...240 s
21686 | RHR4138J | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
21687 | RHR4138J | Main | status LED | With
21688 | RHR4138J | Main | control type | Selector switch
21689 | RHR4138J | Main | coil interference suppression | With
21690 | RHR4138J | Complementary | [Ui] rated insulation voltage | 250 V
21691 | RHR4138J | Complementary | operating position | Any position
21692 | RHR4138J | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
21693 | RHR4138J | Complementary | contact bounce time | <= 10 ms
21694 | RHR4138J | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
21695 | RHR4138J | Complementary | average resistance | 30 mOhm at 20 °C
21696 | RHR4138J | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
21697 | RHR4138J | Complementary | average coil consumption | 2.5 W at 20 °C
21698 | RHR4138J | Complementary | average coil consumption in VA | 2.9 at 20 °C
21699 | RHR4138J | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
21700 | RHR4138J | Complementary | mechanical durability | 20000000 cycles
21701 | RHR4138J | Complementary | repeat accuracy | +/- 1 %
21702 | RHR4138J | Complementary | setting accuracy of time delay | +/- 15 % of full scale
21703 | RHR4138J | Complementary | reset time | 100 ms
21704 | RHR4138J | Complementary | CAD overall width | 33 mm
21705 | RHR4138J | Complementary | CAD overall height | 43 mm
21706 | RHR4138J | Complementary | CAD overall depth | 108 mm
21707 | RHR4138J | Complementary | terminals description ISO n°1 | (31-32-34)OC (21-22-24)OC (41-42-44)OC (B1-A2-B2)CO (11-12-14)OC
21708 | RHR4138J | Complementary | net weight | 0.13 kg
21709 | RHR4138J | Environment | standards | IEC 60255 VDE 0435 NF C 45-250
21710 | RHR4138J | Environment | product certifications | USSR CSA BV ASE EDF
21711 | RHR4138J | Environment | protective treatment | TC
21712 | RHR4138J | Environment | dielectric strength | 2500 V
21713 | RHR4138J | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
21714 | RHR4138J | Environment | ambient air temperature for storage | -40…70 °C
21715 | RHR4138J | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
21716 | RHR4138J | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
21717 | RHR4138J | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
21718 | RHR4138J | Contractual warranty | Warranty | 18 months
21719 | RHR418J | Main | range of product | Zelio Relay
21720 | RHR418J | Main | product or component type | Timing relay Plug-in relay
21721 | RHR418J | Main | device short name | RHR
21722 | RHR418J | Main | contacts type and composition | 4 C/O
21723 | RHR418J | Main | contact operation | Standard
21724 | RHR418J | Main | [Uc] control circuit voltage | 12 V AC/DC 50/60 Hz
21725 | RHR418J | Main | time delay type | Off-delay
21726 | RHR418J | Main | time delay range | 0.2...3 s 15...300 s 1.5...30 s
21727 | RHR418J | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
21728 | RHR418J | Main | status LED | With
21729 | RHR418J | Main | control type | Selector switch
21730 | RHR418J | Main | coil interference suppression | With
21731 | RHR418J | Complementary | [Ui] rated insulation voltage | 250 V
21732 | RHR418J | Complementary | operating position | Any position
21733 | RHR418J | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
21734 | RHR418J | Complementary | contact bounce time | <= 10 ms
21735 | RHR418J | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
21736 | RHR418J | Complementary | average resistance | 30 mOhm at 20 °C
21737 | RHR418J | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
21738 | RHR418J | Complementary | average coil consumption | 2.5 W at 20 °C
21739 | RHR418J | Complementary | average coil consumption in VA | 2.9 at 20 °C
21740 | RHR418J | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
21741 | RHR418J | Complementary | mechanical durability | 20000000 cycles
21742 | RHR418J | Complementary | repeat accuracy | +/- 1 %
21743 | RHR418J | Complementary | setting accuracy of time delay | +/- 15 % of full scale
21744 | RHR418J | Complementary | reset time | 100 ms
21745 | RHR418J | Complementary | CAD overall width | 33 mm
21746 | RHR418J | Complementary | CAD overall height | 43 mm
21747 | RHR418J | Complementary | CAD overall depth | 108 mm
21748 | RHR418J | Complementary | terminals description ISO n°1 | (31-32-34)OC (11-12-14)OC (B1-A2-B2)CO (21-22-24)OC (41-42-44)OC
21749 | RHR418J | Complementary | net weight | 0.13 kg
21750 | RHR418J | Environment | standards | IEC 60255 NF C 45-250 VDE 0435
21751 | RHR418J | Environment | product certifications | ASE USSR BV EDF CSA
21752 | RHR418J | Environment | protective treatment | TC
21753 | RHR418J | Environment | dielectric strength | 2500 V
21754 | RHR418J | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
21755 | RHR418J | Environment | ambient air temperature for storage | -40…70 °C
21756 | RHR418J | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
21757 | RHR418J | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
21758 | RHR418J | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
21759 | RHR418J | Contractual warranty | Warranty | 18 months
21760 | RHT4138J | Main | range of product | Zelio Relay
21761 | RHT4138J | Main | product or component type | Plug-in relay Timing relay
21762 | RHT4138J | Main | device short name | RHT
21763 | RHT4138J | Main | contacts type and composition | 4 C/O
21764 | RHT4138J | Main | contact operation | Standard
21765 | RHT4138J | Main | [Uc] control circuit voltage | 12 V AC/DC 50/60 Hz
21766 | RHT4138J | Main | time delay type | On-delay
21767 | RHT4138J | Main | time delay range | 1.25...24 s 12.5...240 s 2...40 min
21768 | RHT4138J | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
21769 | RHT4138J | Main | status LED | With
21770 | RHT4138J | Main | control type | Selector switch
21771 | RHT4138J | Main | coil interference suppression | With
21772 | RHT4138J | Complementary | [Ui] rated insulation voltage | 250 V
21773 | RHT4138J | Complementary | operating position | Any position
21774 | RHT4138J | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
21775 | RHT4138J | Complementary | contact bounce time | <= 10 ms
21776 | RHT4138J | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
21777 | RHT4138J | Complementary | average resistance | 30 mOhm at 20 °C
21778 | RHT4138J | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
21779 | RHT4138J | Complementary | average coil consumption | 2.5 W at 20 °C
21780 | RHT4138J | Complementary | average coil consumption in VA | 2.9 at 20 °C
21781 | RHT4138J | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
21782 | RHT4138J | Complementary | mechanical durability | 20000000 cycles
21783 | RHT4138J | Complementary | repeat accuracy | +/- 1 %
21784 | RHT4138J | Complementary | setting accuracy of time delay | +/- 20 % of full scale
21785 | RHT4138J | Complementary | reset time | 100 ms
21786 | RHT4138J | Complementary | CAD overall width | 33 mm
21787 | RHT4138J | Complementary | CAD overall height | 43 mm
21788 | RHT4138J | Complementary | CAD overall depth | 108 mm
21789 | RHT4138J | Complementary | terminals description ISO n°1 | (A1-A2)CO (11-12-14)OC (41-42-44)OC (31-32-34)OC (21-22-24)OC
21790 | RHT4138J | Complementary | net weight | 0.13 kg
21791 | RHT4138J | Environment | standards | IEC 60255 NF C 45-250 VDE 0435
21792 | RHT4138J | Environment | product certifications | ASE USSR EDF BV CSA
21793 | RHT4138J | Environment | protective treatment | TC
21794 | RHT4138J | Environment | dielectric strength | 2500 V
21795 | RHT4138J | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
21796 | RHT4138J | Environment | ambient air temperature for storage | -40…70 °C
21797 | RHT4138J | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
21798 | RHT4138J | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
21799 | RHT4138J | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
21800 | RHT4138J | Contractual warranty | Warranty | 18 months
21801 | RHT418J | Main | range of product | Zelio Relay
21802 | RHT418J | Main | product or component type | Plug-in relay Timing relay
21803 | RHT418J | Main | device short name | RHT
21804 | RHT418J | Main | contacts type and composition | 4 C/O
21805 | RHT418J | Main | contact operation | Standard
21806 | RHT418J | Main | [Uc] control circuit voltage | 12 V AC/DC 50/60 Hz
21807 | RHT418J | Main | time delay type | On-delay
21808 | RHT418J | Main | time delay range | 15...300 s 0.2...3 s 1.5...30 s
21809 | RHT418J | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
21810 | RHT418J | Main | status LED | With
21811 | RHT418J | Main | control type | Selector switch
21812 | RHT418J | Main | coil interference suppression | With
21813 | RHT418J | Complementary | [Ui] rated insulation voltage | 250 V
21814 | RHT418J | Complementary | operating position | Any position
21815 | RHT418J | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
21816 | RHT418J | Complementary | contact bounce time | <= 10 ms
21817 | RHT418J | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
21818 | RHT418J | Complementary | average resistance | 30 mOhm at 20 °C
21819 | RHT418J | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
21820 | RHT418J | Complementary | average coil consumption | 2.5 W at 20 °C
21821 | RHT418J | Complementary | average coil consumption in VA | 2.9 at 20 °C
21822 | RHT418J | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
21823 | RHT418J | Complementary | mechanical durability | 20000000 cycles
21824 | RHT418J | Complementary | repeat accuracy | +/- 1 %
21825 | RHT418J | Complementary | setting accuracy of time delay | +/- 15 % of full scale
21826 | RHT418J | Complementary | reset time | 100 ms
21827 | RHT418J | Complementary | CAD overall width | 33 mm
21828 | RHT418J | Complementary | CAD overall height | 43 mm
21829 | RHT418J | Complementary | CAD overall depth | 108 mm
21830 | RHT418J | Complementary | terminals description ISO n°1 | (41-42-44)OC (A1-A2)CO (21-22-24)OC (11-12-14)OC (31-32-34)OC
21831 | RHT418J | Complementary | net weight | 0.13 kg
21832 | RHT418J | Environment | standards | IEC 60255 VDE 0435 NF C 45-250
21833 | RHT418J | Environment | product certifications | ASE BV USSR CSA EDF
21834 | RHT418J | Environment | protective treatment | TC
21835 | RHT418J | Environment | dielectric strength | 2500 V
21836 | RHT418J | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
21837 | RHT418J | Environment | ambient air temperature for storage | -40…70 °C
21838 | RHT418J | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
21839 | RHT418J | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
21840 | RHT418J | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
21841 | RHT418J | Contractual warranty | Warranty | 18 months
21842 | RHR4138F | Main | range of product | Zelio Relay
21843 | RHR4138F | Main | product or component type | Timing relay Plug-in relay
21844 | RHR4138F | Main | device short name | RHR
21845 | RHR4138F | Main | contacts type and composition | 4 C/O
21846 | RHR4138F | Main | contact operation | Standard
21847 | RHR4138F | Main | [Uc] control circuit voltage | 110 V AC/DC 50/60 Hz
21848 | RHR4138F | Main | time delay type | Off-delay
21849 | RHR4138F | Main | time delay range | 12.5...240 s 2...40 min 1.25...24 s
21850 | RHR4138F | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
21851 | RHR4138F | Main | status LED | With
21852 | RHR4138F | Main | control type | Selector switch
21853 | RHR4138F | Main | coil interference suppression | With
21854 | RHR4138F | Complementary | [Ui] rated insulation voltage | 250 V
21855 | RHR4138F | Complementary | operating position | Any position
21856 | RHR4138F | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
21857 | RHR4138F | Complementary | contact bounce time | <= 10 ms
21858 | RHR4138F | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
21859 | RHR4138F | Complementary | average resistance | 30 mOhm at 20 °C
21860 | RHR4138F | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
21861 | RHR4138F | Complementary | average coil consumption | 2.5 W at 20 °C
21862 | RHR4138F | Complementary | average coil consumption in VA | 2.9 at 20 °C
21863 | RHR4138F | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
21864 | RHR4138F | Complementary | mechanical durability | 20000000 cycles
21865 | RHR4138F | Complementary | repeat accuracy | +/- 1 %
21866 | RHR4138F | Complementary | setting accuracy of time delay | +/- 15 % of full scale
21867 | RHR4138F | Complementary | reset time | 100 ms
21868 | RHR4138F | Complementary | CAD overall width | 33 mm
21869 | RHR4138F | Complementary | CAD overall height | 43 mm
21870 | RHR4138F | Complementary | CAD overall depth | 108 mm
21871 | RHR4138F | Complementary | terminals description ISO n°1 | (11-12-14)OC (31-32-34)OC (21-22-24)OC (41-42-44)OC (B1-A2-B2)CO
21872 | RHR4138F | Complementary | net weight | 0.13 kg
21873 | RHR4138F | Environment | standards | IEC 60255 VDE 0435 NF C 45-250
21874 | RHR4138F | Environment | product certifications | EDF USSR ASE CSA BV
21875 | RHR4138F | Environment | protective treatment | TC
21876 | RHR4138F | Environment | dielectric strength | 2500 V
21877 | RHR4138F | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
21878 | RHR4138F | Environment | ambient air temperature for storage | -40…70 °C
21879 | RHR4138F | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
21880 | RHR4138F | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
21881 | RHR4138F | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
21882 | RHR4138F | Contractual warranty | Warranty | 18 months
21883 | RHR4138G | Main | range of product | Zelio Relay
21884 | RHR4138G | Main | product or component type | Timing relay Plug-in relay
21885 | RHR4138G | Main | device short name | RHR
21886 | RHR4138G | Main | contacts type and composition | 4 C/O
21887 | RHR4138G | Main | contact operation | Standard
21888 | RHR4138G | Main | [Uc] control circuit voltage | 127 V AC/DC 50/60 Hz
21889 | RHR4138G | Main | time delay type | Off-delay
21890 | RHR4138G | Main | time delay range | 1.25...24 s 2...40 min 12.5...240 s
21891 | RHR4138G | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
21892 | RHR4138G | Main | status LED | With
21893 | RHR4138G | Main | control type | Selector switch
21894 | RHR4138G | Main | coil interference suppression | With
21895 | RHR4138G | Complementary | [Ui] rated insulation voltage | 250 V
21896 | RHR4138G | Complementary | operating position | Any position
21897 | RHR4138G | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
21898 | RHR4138G | Complementary | contact bounce time | <= 10 ms
21899 | RHR4138G | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
21900 | RHR4138G | Complementary | average resistance | 30 mOhm at 20 °C
21901 | RHR4138G | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
21902 | RHR4138G | Complementary | average coil consumption | 2.5 W at 20 °C
21903 | RHR4138G | Complementary | average coil consumption in VA | 2.9 at 20 °C
21904 | RHR4138G | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
21905 | RHR4138G | Complementary | mechanical durability | 20000000 cycles
21906 | RHR4138G | Complementary | repeat accuracy | +/- 1 %
21907 | RHR4138G | Complementary | setting accuracy of time delay | +/- 15 % of full scale
21908 | RHR4138G | Complementary | reset time | 100 ms
21909 | RHR4138G | Complementary | CAD overall width | 33 mm
21910 | RHR4138G | Complementary | CAD overall height | 43 mm
21911 | RHR4138G | Complementary | CAD overall depth | 108 mm
21912 | RHR4138G | Complementary | terminals description ISO n°1 | (41-42-44)OC (11-12-14)OC (B1-A2-B2)CO (21-22-24)OC (31-32-34)OC
21913 | RHR4138G | Complementary | net weight | 0.13 kg
21914 | RHR4138G | Environment | standards | NF C 45-250 VDE 0435 IEC 60255
21915 | RHR4138G | Environment | product certifications | USSR EDF ASE CSA BV
21916 | RHR4138G | Environment | protective treatment | TC
21917 | RHR4138G | Environment | dielectric strength | 2500 V
21918 | RHR4138G | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
21919 | RHR4138G | Environment | ambient air temperature for storage | -40…70 °C
21920 | RHR4138G | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
21921 | RHR4138G | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
21922 | RHR4138G | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
21923 | RHR4138G | Contractual warranty | Warranty | 18 months
21924 | RHR4131M | Main | range of product | Zelio Relay
21925 | RHR4131M | Main | product or component type | Plug-in relay Timing relay
21926 | RHR4131M | Main | device short name | RHR
21927 | RHR4131M | Main | contacts type and composition | 4 C/O
21928 | RHR4131M | Main | contact operation | Standard
21929 | RHR4131M | Main | [Uc] control circuit voltage | 220 V AC 50/60 Hz
21930 | RHR4131M | Main | time delay type | Off-delay
21931 | RHR4131M | Main | time delay range | 12.5...240 s 1.25...24 s 2...40 min
21932 | RHR4131M | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
21933 | RHR4131M | Main | status LED | With
21934 | RHR4131M | Main | control type | Selector switch
21935 | RHR4131M | Main | coil interference suppression | With
21936 | RHR4131M | Complementary | [Ui] rated insulation voltage | 250 V
21937 | RHR4131M | Complementary | operating position | Any position
21938 | RHR4131M | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
21939 | RHR4131M | Complementary | contact bounce time | <= 10 ms
21940 | RHR4131M | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
21941 | RHR4131M | Complementary | average resistance | 30 mOhm at 20 °C
21942 | RHR4131M | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation
21943 | RHR4131M | Complementary | average coil consumption in VA | 3.5 at 20 °C
21944 | RHR4131M | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
21945 | RHR4131M | Complementary | mechanical durability | 20000000 cycles
21946 | RHR4131M | Complementary | repeat accuracy | +/- 1 %
21947 | RHR4131M | Complementary | setting accuracy of time delay | +/- 15 % of full scale
21948 | RHR4131M | Complementary | reset time | 100 ms
21949 | RHR4131M | Complementary | CAD overall width | 33 mm
21950 | RHR4131M | Complementary | CAD overall height | 43 mm
21951 | RHR4131M | Complementary | CAD overall depth | 108 mm
21952 | RHR4131M | Complementary | terminals description ISO n°1 | (41-42-44)OC (B1-A2-B2)CO (21-22-24)OC (31-32-34)OC (11-12-14)OC
21953 | RHR4131M | Complementary | net weight | 0.13 kg
21954 | RHR4131M | Environment | standards | NF C 45-250 IEC 60255 VDE 0435
21955 | RHR4131M | Environment | product certifications | ASE EDF USSR BV CSA
21956 | RHR4131M | Environment | protective treatment | TC
21957 | RHR4131M | Environment | dielectric strength | 2500 V
21958 | RHR4131M | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
21959 | RHR4131M | Environment | ambient air temperature for storage | -40…70 °C
21960 | RHR4131M | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
21961 | RHR4131M | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
21962 | RHR4131M | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
21963 | RHR4131M | Contractual warranty | Warranty | 18 months
21964 | RHR4138B | Main | range of product | Zelio Relay
21965 | RHR4138B | Main | product or component type | Plug-in relay Timing relay
21966 | RHR4138B | Main | device short name | RHR
21967 | RHR4138B | Main | contacts type and composition | 4 C/O
21968 | RHR4138B | Main | contact operation | Standard
21969 | RHR4138B | Main | [Uc] control circuit voltage | 24 V AC/DC 50/60 Hz
21970 | RHR4138B | Main | time delay type | Off-delay
21971 | RHR4138B | Main | time delay range | 1.25...24 s 12.5...240 s 2...40 min
21972 | RHR4138B | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
21973 | RHR4138B | Main | status LED | With
21974 | RHR4138B | Main | control type | Selector switch
21975 | RHR4138B | Main | coil interference suppression | With
21976 | RHR4138B | Complementary | [Ui] rated insulation voltage | 250 V
21977 | RHR4138B | Complementary | operating position | Any position
21978 | RHR4138B | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
21979 | RHR4138B | Complementary | contact bounce time | <= 10 ms
21980 | RHR4138B | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
21981 | RHR4138B | Complementary | average resistance | 30 mOhm at 20 °C
21982 | RHR4138B | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
21983 | RHR4138B | Complementary | average coil consumption | 2.5 W at 20 °C
21984 | RHR4138B | Complementary | average coil consumption in VA | 2.9 at 20 °C
21985 | RHR4138B | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
21986 | RHR4138B | Complementary | mechanical durability | 20000000 cycles
21987 | RHR4138B | Complementary | repeat accuracy | +/- 1 %
21988 | RHR4138B | Complementary | setting accuracy of time delay | +/- 15 % of full scale
21989 | RHR4138B | Complementary | reset time | 100 ms
21990 | RHR4138B | Complementary | CAD overall width | 33 mm
21991 | RHR4138B | Complementary | CAD overall height | 43 mm
21992 | RHR4138B | Complementary | CAD overall depth | 108 mm
21993 | RHR4138B | Complementary | terminals description ISO n°1 | (B1-A2-B2)CO (41-42-44)OC (31-32-34)OC (11-12-14)OC (21-22-24)OC
21994 | RHR4138B | Complementary | net weight | 0.13 kg
21995 | RHR4138B | Environment | standards | NF C 45-250 VDE 0435 IEC 60255
21996 | RHR4138B | Environment | product certifications | ASE EDF BV CSA USSR
21997 | RHR4138B | Environment | protective treatment | TC
21998 | RHR4138B | Environment | dielectric strength | 2500 V
21999 | RHR4138B | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22000 | RHR4138B | Environment | ambient air temperature for storage | -40…70 °C
22001 | RHR4138B | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22002 | RHR4138B | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22003 | RHR4138B | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22004 | RHR4138B | Packing Units | Package 1 Weight | 0.146 kg
22005 | RHR4138B | Contractual warranty | Warranty | 18 months
22006 | RHR4138BE | Main | range of product | Zelio Relay
22007 | RHR4138BE | Main | product or component type | Timing relay Plug-in relay
22008 | RHR4138BE | Main | device short name | RHR
22009 | RHR4138BE | Main | contacts type and composition | 4 C/O
22010 | RHR4138BE | Main | contact operation | Standard
22011 | RHR4138BE | Main | [Uc] control circuit voltage | 27 V AC/DC 50/60 Hz
22012 | RHR4138BE | Main | time delay type | Off-delay
22013 | RHR4138BE | Main | time delay range | 1.25...24 s 12.5...240 s 2...40 min
22014 | RHR4138BE | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22015 | RHR4138BE | Main | status LED | With
22016 | RHR4138BE | Main | control type | Selector switch
22017 | RHR4138BE | Main | coil interference suppression | With
22018 | RHR4138BE | Complementary | [Ui] rated insulation voltage | 250 V
22019 | RHR4138BE | Complementary | operating position | Any position
22020 | RHR4138BE | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
22021 | RHR4138BE | Complementary | contact bounce time | <= 10 ms
22022 | RHR4138BE | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22023 | RHR4138BE | Complementary | average resistance | 30 mOhm at 20 °C
22024 | RHR4138BE | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22025 | RHR4138BE | Complementary | average coil consumption | 2.5 W at 20 °C
22026 | RHR4138BE | Complementary | average coil consumption in VA | 2.9 at 20 °C
22027 | RHR4138BE | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22028 | RHR4138BE | Complementary | mechanical durability | 20000000 cycles
22029 | RHR4138BE | Complementary | repeat accuracy | +/- 1 %
22030 | RHR4138BE | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22031 | RHR4138BE | Complementary | reset time | 100 ms
22032 | RHR4138BE | Complementary | CAD overall width | 33 mm
22033 | RHR4138BE | Complementary | CAD overall height | 43 mm
22034 | RHR4138BE | Complementary | CAD overall depth | 108 mm
22035 | RHR4138BE | Complementary | terminals description ISO n°1 | (B1-A2-B2)CO (11-12-14)OC (21-22-24)OC (41-42-44)OC (31-32-34)OC
22036 | RHR4138BE | Complementary | net weight | 0.13 kg
22037 | RHR4138BE | Environment | standards | NF C 45-250 IEC 60255 VDE 0435
22038 | RHR4138BE | Environment | product certifications | ASE CSA USSR EDF BV
22039 | RHR4138BE | Environment | protective treatment | TC
22040 | RHR4138BE | Environment | dielectric strength | 2500 V
22041 | RHR4138BE | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22042 | RHR4138BE | Environment | ambient air temperature for storage | -40…70 °C
22043 | RHR4138BE | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22044 | RHR4138BE | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22045 | RHR4138BE | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22046 | RHR4138BE | Contractual warranty | Warranty | 18 months
22047 | RHR428F | Main | range of product | Zelio Relay
22048 | RHR428F | Main | product or component type | Timing relay Plug-in relay
22049 | RHR428F | Main | device short name | RHR
22050 | RHR428F | Main | contacts type and composition | 4 C/O
22051 | RHR428F | Main | contact operation | Low level
22052 | RHR428F | Main | [Uc] control circuit voltage | 127 V AC/DC 50/60 Hz
22053 | RHR428F | Main | time delay type | Off-delay
22054 | RHR428F | Main | time delay range | 0.2...3 s 1.5...30 s 15...300 s
22055 | RHR428F | Main | [Ithe] conventional enclosed thermal current | 1 A 40 °C
22056 | RHR428F | Main | status LED | With
22057 | RHR428F | Main | control type | Selector switch
22058 | RHR428F | Main | coil interference suppression | With
22059 | RHR428F | Complementary | [Ui] rated insulation voltage | 250 V
22060 | RHR428F | Complementary | operating position | Any position
22061 | RHR428F | Complementary | minimum switching capacity | 50 mVA at 1 mA, 1 V
22062 | RHR428F | Complementary | contact bounce time | <= 10 ms
22063 | RHR428F | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22064 | RHR428F | Complementary | average resistance | 30 mOhm at 20 °C
22065 | RHR428F | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22066 | RHR428F | Complementary | average coil consumption | 2.5 W at 20 °C
22067 | RHR428F | Complementary | average coil consumption in VA | 2.9 at 20 °C
22068 | RHR428F | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22069 | RHR428F | Complementary | mechanical durability | 20000000 cycles
22070 | RHR428F | Complementary | repeat accuracy | +/- 1 %
22071 | RHR428F | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22072 | RHR428F | Complementary | reset time | 100 ms
22073 | RHR428F | Complementary | CAD overall width | 33 mm
22074 | RHR428F | Complementary | CAD overall height | 43 mm
22075 | RHR428F | Complementary | CAD overall depth | 108 mm
22076 | RHR428F | Complementary | terminals description ISO n°1 | (11-12-14)OC (41-42-44)OC (21-22-24)OC (31-32-34)OC (B1-A2-B2)CO
22077 | RHR428F | Complementary | net weight | 0.13 kg
22078 | RHR428F | Environment | standards | NF C 45-250 VDE 0435 IEC 60255
22079 | RHR428F | Environment | product certifications | ASE USSR BV CSA EDF
22080 | RHR428F | Environment | protective treatment | TC
22081 | RHR428F | Environment | dielectric strength | 2500 V
22082 | RHR428F | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22083 | RHR428F | Environment | ambient air temperature for storage | -40…70 °C
22084 | RHR428F | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22085 | RHR428F | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22086 | RHR428F | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22087 | RHR428F | Contractual warranty | Warranty | 18 months
22088 | RHR421M | Main | range of product | Zelio Relay
22089 | RHR421M | Main | product or component type | Plug-in relay Timing relay
22090 | RHR421M | Main | device short name | RHR
22091 | RHR421M | Main | contacts type and composition | 4 C/O
22092 | RHR421M | Main | contact operation | Low level
22093 | RHR421M | Main | [Uc] control circuit voltage | 220 V AC 50/60 Hz
22094 | RHR421M | Main | time delay type | Off-delay
22095 | RHR421M | Main | time delay range | 1.5...30 s 15...300 s 0.2...3 s
22096 | RHR421M | Main | [Ithe] conventional enclosed thermal current | 1 A 40 °C
22097 | RHR421M | Main | status LED | With
22098 | RHR421M | Main | control type | Selector switch
22099 | RHR421M | Main | coil interference suppression | With
22100 | RHR421M | Complementary | [Ui] rated insulation voltage | 250 V
22101 | RHR421M | Complementary | operating position | Any position
22102 | RHR421M | Complementary | minimum switching capacity | 50 mVA at 1 mA, 1 V
22103 | RHR421M | Complementary | contact bounce time | <= 10 ms
22104 | RHR421M | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22105 | RHR421M | Complementary | average resistance | 30 mOhm at 20 °C
22106 | RHR421M | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation
22107 | RHR421M | Complementary | average coil consumption in VA | 3.5 at 20 °C
22108 | RHR421M | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22109 | RHR421M | Complementary | mechanical durability | 20000000 cycles
22110 | RHR421M | Complementary | repeat accuracy | +/- 1 %
22111 | RHR421M | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22112 | RHR421M | Complementary | reset time | 100 ms
22113 | RHR421M | Complementary | CAD overall width | 33 mm
22114 | RHR421M | Complementary | CAD overall height | 43 mm
22115 | RHR421M | Complementary | CAD overall depth | 108 mm
22116 | RHR421M | Complementary | terminals description ISO n°1 | (31-32-34)OC (21-22-24)OC (41-42-44)OC (11-12-14)OC (B1-A2-B2)CO
22117 | RHR421M | Complementary | net weight | 0.13 kg
22118 | RHR421M | Environment | standards | VDE 0435 NF C 45-250 IEC 60255
22119 | RHR421M | Environment | product certifications | USSR ASE BV EDF CSA
22120 | RHR421M | Environment | protective treatment | TC
22121 | RHR421M | Environment | dielectric strength | 2500 V
22122 | RHR421M | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22123 | RHR421M | Environment | ambient air temperature for storage | -40…70 °C
22124 | RHR421M | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22125 | RHR421M | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22126 | RHR421M | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22127 | RHR421M | Contractual warranty | Warranty | 18 months
22128 | RHR428B | Main | range of product | Zelio Relay
22129 | RHR428B | Main | product or component type | Plug-in relay Timing relay
22130 | RHR428B | Main | device short name | RHR
22131 | RHR428B | Main | contacts type and composition | 4 C/O
22132 | RHR428B | Main | contact operation | Low level
22133 | RHR428B | Main | [Uc] control circuit voltage | 24 V AC/DC 50/60 Hz
22134 | RHR428B | Main | time delay type | Off-delay
22135 | RHR428B | Main | time delay range | 0.2...3 s 1.5...30 s 15...300 s
22136 | RHR428B | Main | [Ithe] conventional enclosed thermal current | 1 A 40 °C
22137 | RHR428B | Main | status LED | With
22138 | RHR428B | Main | control type | Selector switch
22139 | RHR428B | Main | coil interference suppression | With
22140 | RHR428B | Complementary | [Ui] rated insulation voltage | 250 V
22141 | RHR428B | Complementary | operating position | Any position
22142 | RHR428B | Complementary | minimum switching capacity | 50 mVA at 1 mA, 1 V
22143 | RHR428B | Complementary | contact bounce time | <= 10 ms
22144 | RHR428B | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22145 | RHR428B | Complementary | average resistance | 30 mOhm at 20 °C
22146 | RHR428B | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22147 | RHR428B | Complementary | average coil consumption | 2.5 W at 20 °C
22148 | RHR428B | Complementary | average coil consumption in VA | 2.9 at 20 °C
22149 | RHR428B | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22150 | RHR428B | Complementary | mechanical durability | 20000000 cycles
22151 | RHR428B | Complementary | repeat accuracy | +/- 1 %
22152 | RHR428B | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22153 | RHR428B | Complementary | reset time | 100 ms
22154 | RHR428B | Complementary | CAD overall width | 33 mm
22155 | RHR428B | Complementary | CAD overall height | 43 mm
22156 | RHR428B | Complementary | CAD overall depth | 108 mm
22157 | RHR428B | Complementary | terminals description ISO n°1 | (B1-A2-B2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC
22158 | RHR428B | Complementary | net weight | 0.13 kg
22159 | RHR428B | Environment | standards | IEC 60255 VDE 0435 NF C 45-250
22160 | RHR428B | Environment | product certifications | CSA USSR ASE EDF BV
22161 | RHR428B | Environment | protective treatment | TC
22162 | RHR428B | Environment | dielectric strength | 2500 V
22163 | RHR428B | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22164 | RHR428B | Environment | ambient air temperature for storage | -40…70 °C
22165 | RHR428B | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22166 | RHR428B | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22167 | RHR428B | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22168 | RHR428B | Contractual warranty | Warranty | 18 months
22169 | RHR428E | Main | range of product | Zelio Relay
22170 | RHR428E | Main | product or component type | Plug-in relay Timing relay
22171 | RHR428E | Main | device short name | RHR
22172 | RHR428E | Main | contacts type and composition | 4 C/O
22173 | RHR428E | Main | contact operation | Low level
22174 | RHR428E | Main | [Uc] control circuit voltage | 48 V AC/DC 50/60 Hz
22175 | RHR428E | Main | time delay type | Off-delay
22176 | RHR428E | Main | time delay range | 15...300 s 1.5...30 s 0.2...3 s
22177 | RHR428E | Main | [Ithe] conventional enclosed thermal current | 1 A 40 °C
22178 | RHR428E | Main | status LED | With
22179 | RHR428E | Main | control type | Selector switch
22180 | RHR428E | Main | coil interference suppression | With
22181 | RHR428E | Complementary | [Ui] rated insulation voltage | 250 V
22182 | RHR428E | Complementary | operating position | Any position
22183 | RHR428E | Complementary | minimum switching capacity | 50 mVA at 1 mA, 1 V
22184 | RHR428E | Complementary | contact bounce time | <= 10 ms
22185 | RHR428E | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22186 | RHR428E | Complementary | average resistance | 30 mOhm at 20 °C
22187 | RHR428E | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22188 | RHR428E | Complementary | average coil consumption | 2.5 W at 20 °C
22189 | RHR428E | Complementary | average coil consumption in VA | 2.9 at 20 °C
22190 | RHR428E | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22191 | RHR428E | Complementary | mechanical durability | 20000000 cycles
22192 | RHR428E | Complementary | repeat accuracy | +/- 1 %
22193 | RHR428E | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22194 | RHR428E | Complementary | reset time | 100 ms
22195 | RHR428E | Complementary | CAD overall width | 33 mm
22196 | RHR428E | Complementary | CAD overall height | 43 mm
22197 | RHR428E | Complementary | CAD overall depth | 108 mm
22198 | RHR428E | Complementary | terminals description ISO n°1 | (B1-A2-B2)CO (21-22-24)OC (41-42-44)OC (31-32-34)OC (11-12-14)OC
22199 | RHR428E | Complementary | net weight | 0.13 kg
22200 | RHR428E | Environment | standards | NF C 45-250 IEC 60255 VDE 0435
22201 | RHR428E | Environment | product certifications | ASE USSR BV EDF CSA
22202 | RHR428E | Environment | protective treatment | TC
22203 | RHR428E | Environment | dielectric strength | 2500 V
22204 | RHR428E | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22205 | RHR428E | Environment | ambient air temperature for storage | -40…70 °C
22206 | RHR428E | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22207 | RHR428E | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22208 | RHR428E | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22209 | RHR428E | Contractual warranty | Warranty | 18 months
22210 | RHR418F | Main | range of product | Zelio Relay
22211 | RHR418F | Main | product or component type | Timing relay Plug-in relay
22212 | RHR418F | Main | device short name | RHR
22213 | RHR418F | Main | contacts type and composition | 4 C/O
22214 | RHR418F | Main | contact operation | Standard
22215 | RHR418F | Main | [Uc] control circuit voltage | 110 V AC/DC 50/60 Hz
22216 | RHR418F | Main | time delay type | Off-delay
22217 | RHR418F | Main | time delay range | 0.2...3 s 1.5...30 s 15...300 s
22218 | RHR418F | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22219 | RHR418F | Main | status LED | With
22220 | RHR418F | Main | control type | Selector switch
22221 | RHR418F | Main | coil interference suppression | With
22222 | RHR418F | Complementary | [Ui] rated insulation voltage | 250 V
22223 | RHR418F | Complementary | operating position | Any position
22224 | RHR418F | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
22225 | RHR418F | Complementary | contact bounce time | <= 10 ms
22226 | RHR418F | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22227 | RHR418F | Complementary | average resistance | 30 mOhm at 20 °C
22228 | RHR418F | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22229 | RHR418F | Complementary | average coil consumption | 2.5 W at 20 °C
22230 | RHR418F | Complementary | average coil consumption in VA | 2.9 at 20 °C
22231 | RHR418F | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22232 | RHR418F | Complementary | mechanical durability | 20000000 cycles
22233 | RHR418F | Complementary | repeat accuracy | +/- 1 %
22234 | RHR418F | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22235 | RHR418F | Complementary | reset time | 100 ms
22236 | RHR418F | Complementary | CAD overall width | 33 mm
22237 | RHR418F | Complementary | CAD overall height | 43 mm
22238 | RHR418F | Complementary | CAD overall depth | 108 mm
22239 | RHR418F | Complementary | terminals description ISO n°1 | (B1-A2-B2)CO (11-12-14)OC (31-32-34)OC (21-22-24)OC (41-42-44)OC
22240 | RHR418F | Complementary | net weight | 0.13 kg
22241 | RHR418F | Environment | standards | IEC 60255 VDE 0435 NF C 45-250
22242 | RHR418F | Environment | product certifications | ASE CSA BV USSR EDF
22243 | RHR418F | Environment | protective treatment | TC
22244 | RHR418F | Environment | dielectric strength | 2500 V
22245 | RHR418F | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22246 | RHR418F | Environment | ambient air temperature for storage | -40…70 °C
22247 | RHR418F | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22248 | RHR418F | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22249 | RHR418F | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22250 | RHR418F | Contractual warranty | Warranty | 18 months
22251 | RHR418G | Main | range of product | Zelio Relay
22252 | RHR418G | Main | product or component type | Timing relay Plug-in relay
22253 | RHR418G | Main | device short name | RHR
22254 | RHR418G | Main | contacts type and composition | 4 C/O
22255 | RHR418G | Main | contact operation | Standard
22256 | RHR418G | Main | [Uc] control circuit voltage | 127 V AC/DC 50/60 Hz
22257 | RHR418G | Main | time delay type | Off-delay
22258 | RHR418G | Main | time delay range | 15...300 s 1.5...30 s 0.2...3 s
22259 | RHR418G | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22260 | RHR418G | Main | status LED | With
22261 | RHR418G | Main | control type | Selector switch
22262 | RHR418G | Main | coil interference suppression | With
22263 | RHR418G | Complementary | [Ui] rated insulation voltage | 250 V
22264 | RHR418G | Complementary | operating position | Any position
22265 | RHR418G | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
22266 | RHR418G | Complementary | contact bounce time | <= 10 ms
22267 | RHR418G | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22268 | RHR418G | Complementary | average resistance | 30 mOhm at 20 °C
22269 | RHR418G | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22270 | RHR418G | Complementary | average coil consumption | 2.5 W at 20 °C
22271 | RHR418G | Complementary | average coil consumption in VA | 2.9 at 20 °C
22272 | RHR418G | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22273 | RHR418G | Complementary | mechanical durability | 20000000 cycles
22274 | RHR418G | Complementary | repeat accuracy | +/- 1 %
22275 | RHR418G | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22276 | RHR418G | Complementary | reset time | 100 ms
22277 | RHR418G | Complementary | CAD overall width | 33 mm
22278 | RHR418G | Complementary | CAD overall height | 43 mm
22279 | RHR418G | Complementary | CAD overall depth | 108 mm
22280 | RHR418G | Complementary | terminals description ISO n°1 | (41-42-44)OC (31-32-34)OC (B1-A2-B2)CO (11-12-14)OC (21-22-24)OC
22281 | RHR418G | Complementary | net weight | 0.13 kg
22282 | RHR418G | Environment | standards | VDE 0435 IEC 60255 NF C 45-250
22283 | RHR418G | Environment | product certifications | USSR EDF CSA BV ASE
22284 | RHR418G | Environment | protective treatment | TC
22285 | RHR418G | Environment | dielectric strength | 2500 V
22286 | RHR418G | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22287 | RHR418G | Environment | ambient air temperature for storage | -40…70 °C
22288 | RHR418G | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22289 | RHR418G | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22290 | RHR418G | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22291 | RHR418G | Contractual warranty | Warranty | 18 months
22292 | RHR411M | Main | range of product | Zelio Relay
22293 | RHR411M | Main | product or component type | Timing relay Plug-in relay
22294 | RHR411M | Main | device short name | RHR
22295 | RHR411M | Main | contacts type and composition | 4 C/O
22296 | RHR411M | Main | contact operation | Standard
22297 | RHR411M | Main | [Uc] control circuit voltage | 220 V AC 50/60 Hz
22298 | RHR411M | Main | time delay type | Off-delay
22299 | RHR411M | Main | time delay range | 15...300 s 0.2...3 s 1.5...30 s
22300 | RHR411M | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22301 | RHR411M | Main | status LED | With
22302 | RHR411M | Main | control type | Selector switch
22303 | RHR411M | Main | coil interference suppression | With
22304 | RHR411M | Complementary | [Ui] rated insulation voltage | 250 V
22305 | RHR411M | Complementary | operating position | Any position
22306 | RHR411M | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
22307 | RHR411M | Complementary | contact bounce time | <= 10 ms
22308 | RHR411M | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22309 | RHR411M | Complementary | average resistance | 30 mOhm at 20 °C
22310 | RHR411M | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation
22311 | RHR411M | Complementary | average coil consumption in VA | 3.5 at 20 °C
22312 | RHR411M | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22313 | RHR411M | Complementary | mechanical durability | 20000000 cycles
22314 | RHR411M | Complementary | repeat accuracy | +/- 1 %
22315 | RHR411M | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22316 | RHR411M | Complementary | reset time | 100 ms
22317 | RHR411M | Complementary | CAD overall width | 33 mm
22318 | RHR411M | Complementary | CAD overall height | 43 mm
22319 | RHR411M | Complementary | CAD overall depth | 108 mm
22320 | RHR411M | Complementary | terminals description ISO n°1 | (31-32-34)OC (41-42-44)OC (21-22-24)OC (11-12-14)OC (B1-A2-B2)CO
22321 | RHR411M | Complementary | net weight | 0.13 kg
22322 | RHR411M | Environment | standards | NF C 45-250 IEC 60255 VDE 0435
22323 | RHR411M | Environment | product certifications | USSR EDF BV ASE CSA
22324 | RHR411M | Environment | protective treatment | TC
22325 | RHR411M | Environment | dielectric strength | 2500 V
22326 | RHR411M | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22327 | RHR411M | Environment | ambient air temperature for storage | -40…70 °C
22328 | RHR411M | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22329 | RHR411M | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22330 | RHR411M | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22331 | RHR411M | Contractual warranty | Warranty | 18 months
22332 | RHR411U | Main | range of product | Zelio Relay
22333 | RHR411U | Main | product or component type | Timing relay Plug-in relay
22334 | RHR411U | Main | device short name | RHR
22335 | RHR411U | Main | contacts type and composition | 4 C/O
22336 | RHR411U | Main | contact operation | Standard
22337 | RHR411U | Main | [Uc] control circuit voltage | 240 V AC 50/60 Hz
22338 | RHR411U | Main | time delay type | Off-delay
22339 | RHR411U | Main | time delay range | 0.2...3 s 1.5...30 s 15...300 s
22340 | RHR411U | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22341 | RHR411U | Main | status LED | With
22342 | RHR411U | Main | control type | Selector switch
22343 | RHR411U | Main | coil interference suppression | With
22344 | RHR411U | Complementary | [Ui] rated insulation voltage | 250 V
22345 | RHR411U | Complementary | operating position | Any position
22346 | RHR411U | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
22347 | RHR411U | Complementary | contact bounce time | <= 10 ms
22348 | RHR411U | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22349 | RHR411U | Complementary | average resistance | 30 mOhm at 20 °C
22350 | RHR411U | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation
22351 | RHR411U | Complementary | average coil consumption in VA | 3.5 at 20 °C
22352 | RHR411U | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22353 | RHR411U | Complementary | mechanical durability | 20000000 cycles
22354 | RHR411U | Complementary | repeat accuracy | +/- 1 %
22355 | RHR411U | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22356 | RHR411U | Complementary | reset time | 100 ms
22357 | RHR411U | Complementary | CAD overall width | 33 mm
22358 | RHR411U | Complementary | CAD overall height | 43 mm
22359 | RHR411U | Complementary | CAD overall depth | 108 mm
22360 | RHR411U | Complementary | terminals description ISO n°1 | (41-42-44)OC (21-22-24)OC (B1-A2-B2)CO (11-12-14)OC (31-32-34)OC
22361 | RHR411U | Complementary | net weight | 0.13 kg
22362 | RHR411U | Environment | standards | IEC 60255 NF C 45-250 VDE 0435
22363 | RHR411U | Environment | product certifications | USSR BV ASE EDF CSA
22364 | RHR411U | Environment | protective treatment | TC
22365 | RHR411U | Environment | dielectric strength | 2500 V
22366 | RHR411U | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22367 | RHR411U | Environment | ambient air temperature for storage | -40…70 °C
22368 | RHR411U | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22369 | RHR411U | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22370 | RHR411U | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22371 | RHR411U | Packing Units | Package 1 Weight | 0.143 kg
22372 | RHR411U | Contractual warranty | Warranty | 18 months
22373 | RHR418B | Main | range of product | Zelio Relay
22374 | RHR418B | Main | product or component type | Timing relay Plug-in relay
22375 | RHR418B | Main | device short name | RHR
22376 | RHR418B | Main | contacts type and composition | 4 C/O
22377 | RHR418B | Main | contact operation | Standard
22378 | RHR418B | Main | [Uc] control circuit voltage | 24 V AC/DC 50/60 Hz
22379 | RHR418B | Main | time delay type | Off-delay
22380 | RHR418B | Main | time delay range | 1.5...30 s 0.2...3 s 15...300 s
22381 | RHR418B | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22382 | RHR418B | Main | status LED | With
22383 | RHR418B | Main | control type | Selector switch
22384 | RHR418B | Main | coil interference suppression | With
22385 | RHR418B | Complementary | [Ui] rated insulation voltage | 250 V
22386 | RHR418B | Complementary | operating position | Any position
22387 | RHR418B | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
22388 | RHR418B | Complementary | contact bounce time | <= 10 ms
22389 | RHR418B | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22390 | RHR418B | Complementary | average resistance | 30 mOhm at 20 °C
22391 | RHR418B | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22392 | RHR418B | Complementary | average coil consumption | 2.5 W at 20 °C
22393 | RHR418B | Complementary | average coil consumption in VA | 2.9 at 20 °C
22394 | RHR418B | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22395 | RHR418B | Complementary | mechanical durability | 20000000 cycles
22396 | RHR418B | Complementary | repeat accuracy | +/- 1 %
22397 | RHR418B | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22398 | RHR418B | Complementary | reset time | 100 ms
22399 | RHR418B | Complementary | CAD overall width | 33 mm
22400 | RHR418B | Complementary | CAD overall height | 43 mm
22401 | RHR418B | Complementary | CAD overall depth | 108 mm
22402 | RHR418B | Complementary | terminals description ISO n°1 | (41-42-44)OC (11-12-14)OC (31-32-34)OC (21-22-24)OC (B1-A2-B2)CO
22403 | RHR418B | Complementary | net weight | 0.13 kg
22404 | RHR418B | Environment | standards | VDE 0435 IEC 60255 NF C 45-250
22405 | RHR418B | Environment | product certifications | ASE CSA EDF USSR BV
22406 | RHR418B | Environment | protective treatment | TC
22407 | RHR418B | Environment | dielectric strength | 2500 V
22408 | RHR418B | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22409 | RHR418B | Environment | ambient air temperature for storage | -40…70 °C
22410 | RHR418B | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22411 | RHR418B | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22412 | RHR418B | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22413 | RHR418B | Contractual warranty | Warranty | 18 months
22414 | RHR418BE | Main | range of product | Harmony Relay
22415 | RHR418BE | Main | product or component type | Timing relay Plug-in relay
22416 | RHR418BE | Main | device short name | RHR
22417 | RHR418BE | Main | contacts type and composition | 4 C/O
22418 | RHR418BE | Main | contact operation | Standard
22419 | RHR418BE | Main | [Uc] control circuit voltage | 27 V AC/DC 50/60 Hz
22420 | RHR418BE | Main | time delay type | Off-delay
22421 | RHR418BE | Main | time delay range | 0.2...3 s 15...300 s 1.5...30 s
22422 | RHR418BE | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22423 | RHR418BE | Main | status LED | With
22424 | RHR418BE | Main | control type | Selector switch
22425 | RHR418BE | Main | coil interference suppression | With
22426 | RHR418BE | Complementary | [Ui] rated insulation voltage | 250 V
22427 | RHR418BE | Complementary | operating position | Any position
22428 | RHR418BE | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
22429 | RHR418BE | Complementary | contact bounce time | <= 10 ms
22430 | RHR418BE | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22431 | RHR418BE | Complementary | average resistance | 30 mOhm at 20 °C
22432 | RHR418BE | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22433 | RHR418BE | Complementary | average coil consumption | 2.5 W at 20 °C
22434 | RHR418BE | Complementary | average coil consumption in VA | 2.9 at 20 °C
22435 | RHR418BE | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22436 | RHR418BE | Complementary | mechanical durability | 20000000 cycles
22437 | RHR418BE | Complementary | repeat accuracy | +/- 1 %
22438 | RHR418BE | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22439 | RHR418BE | Complementary | reset time | 100 ms
22440 | RHR418BE | Complementary | CAD overall width | 33 mm
22441 | RHR418BE | Complementary | CAD overall height | 43 mm
22442 | RHR418BE | Complementary | CAD overall depth | 108 mm
22443 | RHR418BE | Complementary | terminals description ISO n°1 | (31-32-34)OC (21-22-24)OC (11-12-14)OC (41-42-44)OC (B1-A2-B2)CO
22444 | RHR418BE | Complementary | net weight | 0.13 kg
22445 | RHR418BE | Environment | standards | NF C 45-250 VDE 0435 IEC 60255
22446 | RHR418BE | Environment | product certifications | EDF BV CSA ASE USSR
22447 | RHR418BE | Environment | protective treatment | TC
22448 | RHR418BE | Environment | dielectric strength | 2500 V
22449 | RHR418BE | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22450 | RHR418BE | Environment | ambient air temperature for storage | -40…70 °C
22451 | RHR418BE | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22452 | RHR418BE | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22453 | RHR418BE | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22454 | RHR418BE | Contractual warranty | Warranty | 18 months
22455 | RHR418E | Main | range of product | Zelio Relay
22456 | RHR418E | Main | product or component type | Plug-in relay Timing relay
22457 | RHR418E | Main | device short name | RHR
22458 | RHR418E | Main | contacts type and composition | 4 C/O
22459 | RHR418E | Main | contact operation | Standard
22460 | RHR418E | Main | [Uc] control circuit voltage | 48 V AC/DC 50/60 Hz
22461 | RHR418E | Main | time delay type | Off-delay
22462 | RHR418E | Main | time delay range | 1.5...30 s 0.2...3 s 15...300 s
22463 | RHR418E | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22464 | RHR418E | Main | status LED | With
22465 | RHR418E | Main | control type | Selector switch
22466 | RHR418E | Main | coil interference suppression | With
22467 | RHR418E | Complementary | [Ui] rated insulation voltage | 250 V
22468 | RHR418E | Complementary | operating position | Any position
22469 | RHR418E | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
22470 | RHR418E | Complementary | contact bounce time | <= 10 ms
22471 | RHR418E | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22472 | RHR418E | Complementary | average resistance | 30 mOhm at 20 °C
22473 | RHR418E | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22474 | RHR418E | Complementary | average coil consumption | 2.5 W at 20 °C
22475 | RHR418E | Complementary | average coil consumption in VA | 2.9 at 20 °C
22476 | RHR418E | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22477 | RHR418E | Complementary | mechanical durability | 20000000 cycles
22478 | RHR418E | Complementary | repeat accuracy | +/- 1 %
22479 | RHR418E | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22480 | RHR418E | Complementary | reset time | 100 ms
22481 | RHR418E | Complementary | CAD overall width | 33 mm
22482 | RHR418E | Complementary | CAD overall height | 43 mm
22483 | RHR418E | Complementary | CAD overall depth | 108 mm
22484 | RHR418E | Complementary | terminals description ISO n°1 | (11-12-14)OC (41-42-44)OC (21-22-24)OC (B1-A2-B2)CO (31-32-34)OC
22485 | RHR418E | Complementary | net weight | 0.13 kg
22486 | RHR418E | Environment | standards | VDE 0435 IEC 60255 NF C 45-250
22487 | RHR418E | Environment | product certifications | EDF CSA ASE BV USSR
22488 | RHR418E | Environment | protective treatment | TC
22489 | RHR418E | Environment | dielectric strength | 2500 V
22490 | RHR418E | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22491 | RHR418E | Environment | ambient air temperature for storage | -40…70 °C
22492 | RHR418E | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22493 | RHR418E | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22494 | RHR418E | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22495 | RHR418E | Contractual warranty | Warranty | 18 months
22496 | RHR418P | Main | range of product | Zelio Relay
22497 | RHR418P | Main | product or component type | Timing relay Plug-in relay
22498 | RHR418P | Main | device short name | RHR
22499 | RHR418P | Main | contacts type and composition | 4 C/O
22500 | RHR418P | Main | contact operation | Standard
22501 | RHR418P | Main | [Uc] control circuit voltage | 60 V AC/DC 50/60 Hz
22502 | RHR418P | Main | time delay type | Off-delay
22503 | RHR418P | Main | time delay range | 0.2...3 s 15...300 s 1.5...30 s
22504 | RHR418P | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22505 | RHR418P | Main | status LED | With
22506 | RHR418P | Main | control type | Selector switch
22507 | RHR418P | Main | coil interference suppression | With
22508 | RHR418P | Complementary | [Ui] rated insulation voltage | 250 V
22509 | RHR418P | Complementary | operating position | Any position
22510 | RHR418P | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
22511 | RHR418P | Complementary | contact bounce time | <= 10 ms
22512 | RHR418P | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22513 | RHR418P | Complementary | average resistance | 30 mOhm at 20 °C
22514 | RHR418P | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22515 | RHR418P | Complementary | average coil consumption | 2.5 W at 20 °C
22516 | RHR418P | Complementary | average coil consumption in VA | 2.9 at 20 °C
22517 | RHR418P | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22518 | RHR418P | Complementary | mechanical durability | 20000000 cycles
22519 | RHR418P | Complementary | repeat accuracy | +/- 1 %
22520 | RHR418P | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22521 | RHR418P | Complementary | reset time | 100 ms
22522 | RHR418P | Complementary | CAD overall width | 33 mm
22523 | RHR418P | Complementary | CAD overall height | 43 mm
22524 | RHR418P | Complementary | CAD overall depth | 108 mm
22525 | RHR418P | Complementary | terminals description ISO n°1 | (31-32-34)OC (B1-A2-B2)CO (21-22-24)OC (41-42-44)OC (11-12-14)OC
22526 | RHR418P | Complementary | net weight | 0.13 kg
22527 | RHR418P | Environment | standards | IEC 60255 VDE 0435 NF C 45-250
22528 | RHR418P | Environment | product certifications | EDF CSA ASE USSR BV
22529 | RHR418P | Environment | protective treatment | TC
22530 | RHR418P | Environment | dielectric strength | 2500 V
22531 | RHR418P | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22532 | RHR418P | Environment | ambient air temperature for storage | -40…70 °C
22533 | RHR418P | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22534 | RHR418P | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22535 | RHR418P | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22536 | RHR418P | Contractual warranty | Warranty | 18 months
22537 | RHR418EN | Main | range of product | Zelio Relay
22538 | RHR418EN | Main | product or component type | Timing relay Plug-in relay
22539 | RHR418EN | Main | device short name | RHR
22540 | RHR418EN | Main | contacts type and composition | 4 C/O
22541 | RHR418EN | Main | contact operation | Standard
22542 | RHR418EN | Main | [Uc] control circuit voltage | 72 V AC/DC 50/60 Hz
22543 | RHR418EN | Main | time delay type | Off-delay
22544 | RHR418EN | Main | time delay range | 15...300 s 1.5...30 s 0.2...3 s
22545 | RHR418EN | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22546 | RHR418EN | Main | status LED | With
22547 | RHR418EN | Main | control type | Selector switch
22548 | RHR418EN | Main | coil interference suppression | With
22549 | RHR418EN | Complementary | [Ui] rated insulation voltage | 250 V
22550 | RHR418EN | Complementary | operating position | Any position
22551 | RHR418EN | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
22552 | RHR418EN | Complementary | contact bounce time | <= 10 ms
22553 | RHR418EN | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22554 | RHR418EN | Complementary | average resistance | 30 mOhm at 20 °C
22555 | RHR418EN | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22556 | RHR418EN | Complementary | average coil consumption | 2.5 W at 20 °C
22557 | RHR418EN | Complementary | average coil consumption in VA | 2.9 at 20 °C
22558 | RHR418EN | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22559 | RHR418EN | Complementary | mechanical durability | 20000000 cycles
22560 | RHR418EN | Complementary | repeat accuracy | +/- 1 %
22561 | RHR418EN | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22562 | RHR418EN | Complementary | reset time | 100 ms
22563 | RHR418EN | Complementary | CAD overall width | 33 mm
22564 | RHR418EN | Complementary | CAD overall height | 43 mm
22565 | RHR418EN | Complementary | CAD overall depth | 108 mm
22566 | RHR418EN | Complementary | terminals description ISO n°1 | (B1-A2-B2)CO (31-32-34)OC (41-42-44)OC (21-22-24)OC (11-12-14)OC
22567 | RHR418EN | Complementary | net weight | 0.13 kg
22568 | RHR418EN | Environment | standards | VDE 0435 NF C 45-250 IEC 60255
22569 | RHR418EN | Environment | product certifications | BV USSR EDF CSA ASE
22570 | RHR418EN | Environment | protective treatment | TC
22571 | RHR418EN | Environment | dielectric strength | 2500 V
22572 | RHR418EN | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22573 | RHR418EN | Environment | ambient air temperature for storage | -40…70 °C
22574 | RHR418EN | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22575 | RHR418EN | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22576 | RHR418EN | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22577 | RHR418EN | Contractual warranty | Warranty | 18 months
22578 | RHT4138F | Main | range of product | Zelio Relay
22579 | RHT4138F | Main | product or component type | Timing relay Plug-in relay
22580 | RHT4138F | Main | device short name | RHT
22581 | RHT4138F | Main | contacts type and composition | 4 C/O
22582 | RHT4138F | Main | contact operation | Standard
22583 | RHT4138F | Main | [Uc] control circuit voltage | 110 V AC/DC 50/60 Hz
22584 | RHT4138F | Main | time delay type | On-delay
22585 | RHT4138F | Main | time delay range | 2...40 min 12.5...240 s 1.25...24 s
22586 | RHT4138F | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22587 | RHT4138F | Main | status LED | With
22588 | RHT4138F | Main | control type | Selector switch
22589 | RHT4138F | Main | coil interference suppression | With
22590 | RHT4138F | Complementary | [Ui] rated insulation voltage | 250 V
22591 | RHT4138F | Complementary | operating position | Any position
22592 | RHT4138F | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
22593 | RHT4138F | Complementary | contact bounce time | <= 10 ms
22594 | RHT4138F | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22595 | RHT4138F | Complementary | average resistance | 30 mOhm at 20 °C
22596 | RHT4138F | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22597 | RHT4138F | Complementary | average coil consumption | 2.5 W at 20 °C
22598 | RHT4138F | Complementary | average coil consumption in VA | 2.9 at 20 °C
22599 | RHT4138F | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22600 | RHT4138F | Complementary | mechanical durability | 20000000 cycles
22601 | RHT4138F | Complementary | repeat accuracy | +/- 1 %
22602 | RHT4138F | Complementary | setting accuracy of time delay | +/- 20 % of full scale
22603 | RHT4138F | Complementary | reset time | 100 ms
22604 | RHT4138F | Complementary | CAD overall width | 33 mm
22605 | RHT4138F | Complementary | CAD overall height | 43 mm
22606 | RHT4138F | Complementary | CAD overall depth | 108 mm
22607 | RHT4138F | Complementary | terminals description ISO n°1 | (A1-A2)CO (31-32-34)OC (11-12-14)OC (21-22-24)OC (41-42-44)OC
22608 | RHT4138F | Complementary | net weight | 0.13 kg
22609 | RHT4138F | Environment | standards | IEC 60255 NF C 45-250 VDE 0435
22610 | RHT4138F | Environment | product certifications | EDF BV CSA USSR ASE
22611 | RHT4138F | Environment | protective treatment | TC
22612 | RHT4138F | Environment | dielectric strength | 2500 V
22613 | RHT4138F | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22614 | RHT4138F | Environment | ambient air temperature for storage | -40…70 °C
22615 | RHT4138F | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22616 | RHT4138F | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22617 | RHT4138F | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22618 | RHT4138F | Contractual warranty | Warranty | 18 months
22619 | RHT4138G | Main | range of product | Zelio Relay
22620 | RHT4138G | Main | product or component type | Plug-in relay Timing relay
22621 | RHT4138G | Main | device short name | RHT
22622 | RHT4138G | Main | contacts type and composition | 4 C/O
22623 | RHT4138G | Main | contact operation | Standard
22624 | RHT4138G | Main | [Uc] control circuit voltage | 125 V AC/DC 50/60 Hz
22625 | RHT4138G | Main | time delay type | On-delay
22626 | RHT4138G | Main | time delay range | 1.25...24 s 12.5...240 s 2...40 min
22627 | RHT4138G | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22628 | RHT4138G | Main | status LED | With
22629 | RHT4138G | Main | control type | Selector switch
22630 | RHT4138G | Main | coil interference suppression | With
22631 | RHT4138G | Complementary | [Ui] rated insulation voltage | 250 V
22632 | RHT4138G | Complementary | operating position | Any position
22633 | RHT4138G | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
22634 | RHT4138G | Complementary | contact bounce time | <= 10 ms
22635 | RHT4138G | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22636 | RHT4138G | Complementary | average resistance | 30 mOhm at 20 °C
22637 | RHT4138G | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22638 | RHT4138G | Complementary | average coil consumption | 2.5 W at 20 °C
22639 | RHT4138G | Complementary | average coil consumption in VA | 2.9 at 20 °C
22640 | RHT4138G | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22641 | RHT4138G | Complementary | mechanical durability | 20000000 cycles
22642 | RHT4138G | Complementary | repeat accuracy | +/- 1 %
22643 | RHT4138G | Complementary | setting accuracy of time delay | +/- 20 % of full scale
22644 | RHT4138G | Complementary | reset time | 100 ms
22645 | RHT4138G | Complementary | CAD overall width | 33 mm
22646 | RHT4138G | Complementary | CAD overall height | 43 mm
22647 | RHT4138G | Complementary | CAD overall depth | 108 mm
22648 | RHT4138G | Complementary | terminals description ISO n°1 | (31-32-34)OC (41-42-44)OC (A1-A2)CO (21-22-24)OC (11-12-14)OC
22649 | RHT4138G | Complementary | net weight | 0.13 kg
22650 | RHT4138G | Environment | standards | NF C 45-250 VDE 0435 IEC 60255
22651 | RHT4138G | Environment | product certifications | BV ASE CSA USSR EDF
22652 | RHT4138G | Environment | protective treatment | TC
22653 | RHT4138G | Environment | dielectric strength | 2500 V
22654 | RHT4138G | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22655 | RHT4138G | Environment | ambient air temperature for storage | -40…70 °C
22656 | RHT4138G | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22657 | RHT4138G | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22658 | RHT4138G | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22659 | RHT4138G | Contractual warranty | Warranty | 18 months
22660 | RHT4131M | Main | range of product | Zelio Relay
22661 | RHT4131M | Main | product or component type | Plug-in relay Timing relay
22662 | RHT4131M | Main | device short name | RHT
22663 | RHT4131M | Main | contacts type and composition | 4 C/O
22664 | RHT4131M | Main | contact operation | Standard
22665 | RHT4131M | Main | [Uc] control circuit voltage | 220 V AC 50/60 Hz
22666 | RHT4131M | Main | time delay type | On-delay
22667 | RHT4131M | Main | time delay range | 2...40 min 12.5...240 s 1.25...24 s
22668 | RHT4131M | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22669 | RHT4131M | Main | status LED | With
22670 | RHT4131M | Main | control type | Selector switch
22671 | RHT4131M | Main | coil interference suppression | With
22672 | RHT4131M | Complementary | [Ui] rated insulation voltage | 250 V
22673 | RHT4131M | Complementary | operating position | Any position
22674 | RHT4131M | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
22675 | RHT4131M | Complementary | contact bounce time | <= 10 ms
22676 | RHT4131M | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22677 | RHT4131M | Complementary | average resistance | 30 mOhm at 20 °C
22678 | RHT4131M | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation
22679 | RHT4131M | Complementary | average coil consumption in VA | 3.5 at 20 °C
22680 | RHT4131M | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22681 | RHT4131M | Complementary | mechanical durability | 20000000 cycles
22682 | RHT4131M | Complementary | repeat accuracy | +/- 1 %
22683 | RHT4131M | Complementary | setting accuracy of time delay | +/- 20 % of full scale
22684 | RHT4131M | Complementary | reset time | 100 ms
22685 | RHT4131M | Complementary | CAD overall width | 33 mm
22686 | RHT4131M | Complementary | CAD overall height | 43 mm
22687 | RHT4131M | Complementary | CAD overall depth | 108 mm
22688 | RHT4131M | Complementary | terminals description ISO n°1 | (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC
22689 | RHT4131M | Complementary | net weight | 0.13 kg
22690 | RHT4131M | Environment | standards | VDE 0435 IEC 60255 NF C 45-250
22691 | RHT4131M | Environment | product certifications | EDF ASE BV CSA USSR
22692 | RHT4131M | Environment | protective treatment | TC
22693 | RHT4131M | Environment | dielectric strength | 2500 V
22694 | RHT4131M | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22695 | RHT4131M | Environment | ambient air temperature for storage | -40…70 °C
22696 | RHT4131M | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22697 | RHT4131M | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22698 | RHT4131M | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22699 | RHT4131M | Contractual warranty | Warranty | 18 months
22700 | RHT4138B | Main | range of product | Zelio Relay
22701 | RHT4138B | Main | product or component type | Plug-in relay Timing relay
22702 | RHT4138B | Main | device short name | RHT
22703 | RHT4138B | Main | contacts type and composition | 4 C/O
22704 | RHT4138B | Main | contact operation | Standard
22705 | RHT4138B | Main | [Uc] control circuit voltage | 24 V AC/DC 50/60 Hz
22706 | RHT4138B | Main | time delay type | On-delay
22707 | RHT4138B | Main | time delay range | 1.25...24 s 2...40 min 12.5...240 s
22708 | RHT4138B | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22709 | RHT4138B | Main | status LED | With
22710 | RHT4138B | Main | control type | Selector switch
22711 | RHT4138B | Main | coil interference suppression | With
22712 | RHT4138B | Complementary | [Ui] rated insulation voltage | 250 V
22713 | RHT4138B | Complementary | operating position | Any position
22714 | RHT4138B | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
22715 | RHT4138B | Complementary | contact bounce time | <= 10 ms
22716 | RHT4138B | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22717 | RHT4138B | Complementary | average resistance | 30 mOhm at 20 °C
22718 | RHT4138B | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22719 | RHT4138B | Complementary | average coil consumption | 2.5 W at 20 °C
22720 | RHT4138B | Complementary | average coil consumption in VA | 2.9 at 20 °C
22721 | RHT4138B | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22722 | RHT4138B | Complementary | mechanical durability | 20000000 cycles
22723 | RHT4138B | Complementary | repeat accuracy | +/- 1 %
22724 | RHT4138B | Complementary | setting accuracy of time delay | +/- 20 % of full scale
22725 | RHT4138B | Complementary | reset time | 100 ms
22726 | RHT4138B | Complementary | CAD overall width | 33 mm
22727 | RHT4138B | Complementary | CAD overall height | 43 mm
22728 | RHT4138B | Complementary | CAD overall depth | 108 mm
22729 | RHT4138B | Complementary | terminals description ISO n°1 | (21-22-24)OC (41-42-44)OC (31-32-34)OC (11-12-14)OC (A1-A2)CO
22730 | RHT4138B | Complementary | net weight | 0.13 kg
22731 | RHT4138B | Environment | standards | VDE 0435 NF C 45-250 IEC 60255
22732 | RHT4138B | Environment | product certifications | ASE EDF USSR BV CSA
22733 | RHT4138B | Environment | protective treatment | TC
22734 | RHT4138B | Environment | dielectric strength | 2500 V
22735 | RHT4138B | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22736 | RHT4138B | Environment | ambient air temperature for storage | -40…70 °C
22737 | RHT4138B | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22738 | RHT4138B | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22739 | RHT4138B | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22740 | RHT4138B | Contractual warranty | Warranty | 18 months
22741 | RHT4138E | Main | range of product | Zelio Relay
22742 | RHT4138E | Main | product or component type | Plug-in relay Timing relay
22743 | RHT4138E | Main | device short name | RHT
22744 | RHT4138E | Main | contacts type and composition | 4 C/O
22745 | RHT4138E | Main | contact operation | Standard
22746 | RHT4138E | Main | [Uc] control circuit voltage | 48 V AC/DC 50/60 Hz
22747 | RHT4138E | Main | time delay type | On-delay
22748 | RHT4138E | Main | time delay range | 12.5...240 s 2...40 min 1.25...24 s
22749 | RHT4138E | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22750 | RHT4138E | Main | status LED | With
22751 | RHT4138E | Main | control type | Selector switch
22752 | RHT4138E | Main | coil interference suppression | With
22753 | RHT4138E | Complementary | [Ui] rated insulation voltage | 250 V
22754 | RHT4138E | Complementary | operating position | Any position
22755 | RHT4138E | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
22756 | RHT4138E | Complementary | contact bounce time | <= 10 ms
22757 | RHT4138E | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22758 | RHT4138E | Complementary | average resistance | 30 mOhm at 20 °C
22759 | RHT4138E | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22760 | RHT4138E | Complementary | average coil consumption | 2.5 W at 20 °C
22761 | RHT4138E | Complementary | average coil consumption in VA | 2.9 at 20 °C
22762 | RHT4138E | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22763 | RHT4138E | Complementary | mechanical durability | 20000000 cycles
22764 | RHT4138E | Complementary | repeat accuracy | +/- 1 %
22765 | RHT4138E | Complementary | setting accuracy of time delay | +/- 20 % of full scale
22766 | RHT4138E | Complementary | reset time | 100 ms
22767 | RHT4138E | Complementary | CAD overall width | 33 mm
22768 | RHT4138E | Complementary | CAD overall height | 43 mm
22769 | RHT4138E | Complementary | CAD overall depth | 108 mm
22770 | RHT4138E | Complementary | terminals description ISO n°1 | (31-32-34)OC (A1-A2)CO (11-12-14)OC (41-42-44)OC (21-22-24)OC
22771 | RHT4138E | Complementary | net weight | 0.13 kg
22772 | RHT4138E | Environment | standards | VDE 0435 IEC 60255 NF C 45-250
22773 | RHT4138E | Environment | product certifications | ASE EDF USSR BV CSA
22774 | RHT4138E | Environment | protective treatment | TC
22775 | RHT4138E | Environment | dielectric strength | 2500 V
22776 | RHT4138E | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22777 | RHT4138E | Environment | ambient air temperature for storage | -40…70 °C
22778 | RHT4138E | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22779 | RHT4138E | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22780 | RHT4138E | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22781 | RHT4138E | Contractual warranty | Warranty | 18 months
22782 | RHT428F | Main | range of product | Zelio Relay
22783 | RHT428F | Main | product or component type | Timing relay Plug-in relay
22784 | RHT428F | Main | device short name | RHT
22785 | RHT428F | Main | contacts type and composition | 4 C/O
22786 | RHT428F | Main | contact operation | Low level
22787 | RHT428F | Main | [Uc] control circuit voltage | 110 V AC/DC 50/60 Hz
22788 | RHT428F | Main | time delay type | On-delay
22789 | RHT428F | Main | time delay range | 15...300 s 0.2...3 s 1.5...30 s
22790 | RHT428F | Main | [Ithe] conventional enclosed thermal current | 1 A 40 °C
22791 | RHT428F | Main | status LED | With
22792 | RHT428F | Main | control type | Selector switch
22793 | RHT428F | Main | coil interference suppression | With
22794 | RHT428F | Complementary | [Ui] rated insulation voltage | 250 V
22795 | RHT428F | Complementary | operating position | Any position
22796 | RHT428F | Complementary | minimum switching capacity | 50 mVA at 1 mA, 1 V
22797 | RHT428F | Complementary | contact bounce time | <= 10 ms
22798 | RHT428F | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22799 | RHT428F | Complementary | average resistance | 30 mOhm at 20 °C
22800 | RHT428F | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22801 | RHT428F | Complementary | average coil consumption | 2.5 W at 20 °C
22802 | RHT428F | Complementary | average coil consumption in VA | 2.9 at 20 °C
22803 | RHT428F | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22804 | RHT428F | Complementary | mechanical durability | 20000000 cycles
22805 | RHT428F | Complementary | repeat accuracy | +/- 1 %
22806 | RHT428F | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22807 | RHT428F | Complementary | reset time | 100 ms
22808 | RHT428F | Complementary | CAD overall width | 33 mm
22809 | RHT428F | Complementary | CAD overall height | 43 mm
22810 | RHT428F | Complementary | CAD overall depth | 108 mm
22811 | RHT428F | Complementary | terminals description ISO n°1 | (A1-A2)CO (41-42-44)OC (11-12-14)OC (31-32-34)OC (21-22-24)OC
22812 | RHT428F | Complementary | net weight | 0.13 kg
22813 | RHT428F | Environment | standards | NF C 45-250 IEC 60255 VDE 0435
22814 | RHT428F | Environment | product certifications | USSR EDF CSA ASE BV
22815 | RHT428F | Environment | protective treatment | TC
22816 | RHT428F | Environment | dielectric strength | 2500 V
22817 | RHT428F | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22818 | RHT428F | Environment | ambient air temperature for storage | -40…70 °C
22819 | RHT428F | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22820 | RHT428F | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22821 | RHT428F | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22822 | RHT428F | Contractual warranty | Warranty | 18 months
22823 | RHT428G | Main | range of product | Zelio Relay
22824 | RHT428G | Main | product or component type | Plug-in relay Timing relay
22825 | RHT428G | Main | device short name | RHT
22826 | RHT428G | Main | contacts type and composition | 4 C/O
22827 | RHT428G | Main | contact operation | Low level
22828 | RHT428G | Main | [Uc] control circuit voltage | 127 V AC/DC 50/60 Hz
22829 | RHT428G | Main | time delay type | On-delay
22830 | RHT428G | Main | time delay range | 1.5...30 s 15...300 s 0.2...3 s
22831 | RHT428G | Main | [Ithe] conventional enclosed thermal current | 1 A 40 °C
22832 | RHT428G | Main | status LED | With
22833 | RHT428G | Main | control type | Selector switch
22834 | RHT428G | Main | coil interference suppression | With
22835 | RHT428G | Complementary | [Ui] rated insulation voltage | 250 V
22836 | RHT428G | Complementary | operating position | Any position
22837 | RHT428G | Complementary | minimum switching capacity | 50 mVA at 1 mA, 1 V
22838 | RHT428G | Complementary | contact bounce time | <= 10 ms
22839 | RHT428G | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22840 | RHT428G | Complementary | average resistance | 30 mOhm at 20 °C
22841 | RHT428G | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22842 | RHT428G | Complementary | average coil consumption | 2.5 W at 20 °C
22843 | RHT428G | Complementary | average coil consumption in VA | 2.9 at 20 °C
22844 | RHT428G | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22845 | RHT428G | Complementary | mechanical durability | 20000000 cycles
22846 | RHT428G | Complementary | repeat accuracy | +/- 1 %
22847 | RHT428G | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22848 | RHT428G | Complementary | reset time | 100 ms
22849 | RHT428G | Complementary | CAD overall width | 33 mm
22850 | RHT428G | Complementary | CAD overall height | 43 mm
22851 | RHT428G | Complementary | CAD overall depth | 108 mm
22852 | RHT428G | Complementary | terminals description ISO n°1 | (A1-A2)CO (41-42-44)OC (11-12-14)OC (21-22-24)OC (31-32-34)OC
22853 | RHT428G | Complementary | net weight | 0.13 kg
22854 | RHT428G | Environment | standards | IEC 60255 VDE 0435 NF C 45-250
22855 | RHT428G | Environment | product certifications | EDF USSR ASE CSA BV
22856 | RHT428G | Environment | protective treatment | TC
22857 | RHT428G | Environment | dielectric strength | 2500 V
22858 | RHT428G | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22859 | RHT428G | Environment | ambient air temperature for storage | -40…70 °C
22860 | RHT428G | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22861 | RHT428G | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22862 | RHT428G | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22863 | RHT428G | Contractual warranty | Warranty | 18 months
22864 | RHT421M | Main | range of product | Zelio Relay
22865 | RHT421M | Main | product or component type | Plug-in relay Timing relay
22866 | RHT421M | Main | device short name | RHT
22867 | RHT421M | Main | contacts type and composition | 4 C/O
22868 | RHT421M | Main | contact operation | Low level
22869 | RHT421M | Main | [Uc] control circuit voltage | 220 V AC 50/60 Hz
22870 | RHT421M | Main | time delay type | On-delay
22871 | RHT421M | Main | time delay range | 0.2...3 s 15...300 s 1.5...30 s
22872 | RHT421M | Main | [Ithe] conventional enclosed thermal current | 1 A 40 °C
22873 | RHT421M | Main | status LED | With
22874 | RHT421M | Main | control type | Selector switch
22875 | RHT421M | Main | coil interference suppression | With
22876 | RHT421M | Complementary | [Ui] rated insulation voltage | 250 V
22877 | RHT421M | Complementary | operating position | Any position
22878 | RHT421M | Complementary | minimum switching capacity | 50 mVA at 1 mA, 1 V
22879 | RHT421M | Complementary | contact bounce time | <= 10 ms
22880 | RHT421M | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22881 | RHT421M | Complementary | average resistance | 30 mOhm at 20 °C
22882 | RHT421M | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation
22883 | RHT421M | Complementary | average coil consumption in VA | 3.5 at 20 °C
22884 | RHT421M | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22885 | RHT421M | Complementary | mechanical durability | 20000000 cycles
22886 | RHT421M | Complementary | repeat accuracy | +/- 1 %
22887 | RHT421M | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22888 | RHT421M | Complementary | reset time | 100 ms
22889 | RHT421M | Complementary | CAD overall width | 33 mm
22890 | RHT421M | Complementary | CAD overall height | 43 mm
22891 | RHT421M | Complementary | CAD overall depth | 108 mm
22892 | RHT421M | Complementary | terminals description ISO n°1 | (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC
22893 | RHT421M | Complementary | net weight | 0.13 kg
22894 | RHT421M | Environment | standards | VDE 0435 IEC 60255 NF C 45-250
22895 | RHT421M | Environment | product certifications | USSR ASE EDF CSA BV
22896 | RHT421M | Environment | protective treatment | TC
22897 | RHT421M | Environment | dielectric strength | 2500 V
22898 | RHT421M | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22899 | RHT421M | Environment | ambient air temperature for storage | -40…70 °C
22900 | RHT421M | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22901 | RHT421M | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22902 | RHT421M | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22903 | RHT421M | Contractual warranty | Warranty | 18 months
22904 | RHT428B | Main | range of product | Zelio Relay
22905 | RHT428B | Main | product or component type | Plug-in relay Timing relay
22906 | RHT428B | Main | device short name | RHT
22907 | RHT428B | Main | contacts type and composition | 4 C/O
22908 | RHT428B | Main | contact operation | Low level
22909 | RHT428B | Main | [Uc] control circuit voltage | 24 V AC/DC 50/60 Hz
22910 | RHT428B | Main | time delay type | On-delay
22911 | RHT428B | Main | time delay range | 15...300 s 0.2...3 s 1.5...30 s
22912 | RHT428B | Main | [Ithe] conventional enclosed thermal current | 1 A 40 °C
22913 | RHT428B | Main | status LED | With
22914 | RHT428B | Main | control type | Selector switch
22915 | RHT428B | Main | coil interference suppression | With
22916 | RHT428B | Complementary | [Ui] rated insulation voltage | 250 V
22917 | RHT428B | Complementary | operating position | Any position
22918 | RHT428B | Complementary | minimum switching capacity | 50 mVA at 1 mA, 1 V
22919 | RHT428B | Complementary | contact bounce time | <= 10 ms
22920 | RHT428B | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22921 | RHT428B | Complementary | average resistance | 30 mOhm at 20 °C
22922 | RHT428B | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22923 | RHT428B | Complementary | average coil consumption | 2.5 W at 20 °C
22924 | RHT428B | Complementary | average coil consumption in VA | 2.9 at 20 °C
22925 | RHT428B | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22926 | RHT428B | Complementary | mechanical durability | 20000000 cycles
22927 | RHT428B | Complementary | repeat accuracy | +/- 1 %
22928 | RHT428B | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22929 | RHT428B | Complementary | reset time | 100 ms
22930 | RHT428B | Complementary | CAD overall width | 33 mm
22931 | RHT428B | Complementary | CAD overall height | 43 mm
22932 | RHT428B | Complementary | CAD overall depth | 108 mm
22933 | RHT428B | Complementary | terminals description ISO n°1 | (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC
22934 | RHT428B | Complementary | net weight | 0.13 kg
22935 | RHT428B | Environment | standards | IEC 60255 NF C 45-250 VDE 0435
22936 | RHT428B | Environment | product certifications | USSR EDF ASE BV CSA
22937 | RHT428B | Environment | protective treatment | TC
22938 | RHT428B | Environment | dielectric strength | 2500 V
22939 | RHT428B | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22940 | RHT428B | Environment | ambient air temperature for storage | -40…70 °C
22941 | RHT428B | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22942 | RHT428B | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22943 | RHT428B | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22944 | RHT428B | Contractual warranty | Warranty | 18 months
22945 | RHT418F | Main | range of product | Zelio Relay
22946 | RHT418F | Main | product or component type | Plug-in relay Timing relay
22947 | RHT418F | Main | device short name | RHT
22948 | RHT418F | Main | contacts type and composition | 4 C/O
22949 | RHT418F | Main | contact operation | Standard
22950 | RHT418F | Main | [Uc] control circuit voltage | 110 V AC/DC 50/60 Hz
22951 | RHT418F | Main | time delay type | On-delay
22952 | RHT418F | Main | time delay range | 0.2...3 s 1.5...30 s 15...300 s
22953 | RHT418F | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22954 | RHT418F | Main | status LED | With
22955 | RHT418F | Main | control type | Selector switch
22956 | RHT418F | Main | coil interference suppression | With
22957 | RHT418F | Complementary | [Ui] rated insulation voltage | 250 V
22958 | RHT418F | Complementary | operating position | Any position
22959 | RHT418F | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
22960 | RHT418F | Complementary | contact bounce time | <= 10 ms
22961 | RHT418F | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
22962 | RHT418F | Complementary | average resistance | 30 mOhm at 20 °C
22963 | RHT418F | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
22964 | RHT418F | Complementary | average coil consumption | 2.5 W at 20 °C
22965 | RHT418F | Complementary | average coil consumption in VA | 2.9 at 20 °C
22966 | RHT418F | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
22967 | RHT418F | Complementary | mechanical durability | 20000000 cycles
22968 | RHT418F | Complementary | repeat accuracy | +/- 1 %
22969 | RHT418F | Complementary | setting accuracy of time delay | +/- 15 % of full scale
22970 | RHT418F | Complementary | reset time | 100 ms
22971 | RHT418F | Complementary | CAD overall width | 33 mm
22972 | RHT418F | Complementary | CAD overall height | 43 mm
22973 | RHT418F | Complementary | CAD overall depth | 108 mm
22974 | RHT418F | Complementary | terminals description ISO n°1 | (41-42-44)OC (A1-A2)CO (11-12-14)OC (21-22-24)OC (31-32-34)OC
22975 | RHT418F | Complementary | net weight | 0.13 kg
22976 | RHT418F | Environment | standards | NF C 45-250 VDE 0435 IEC 60255
22977 | RHT418F | Environment | product certifications | EDF CSA BV USSR ASE
22978 | RHT418F | Environment | protective treatment | TC
22979 | RHT418F | Environment | dielectric strength | 2500 V
22980 | RHT418F | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
22981 | RHT418F | Environment | ambient air temperature for storage | -40…70 °C
22982 | RHT418F | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
22983 | RHT418F | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
22984 | RHT418F | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
22985 | RHT418F | Contractual warranty | Warranty | 18 months
22986 | RHT418G | Main | range of product | Zelio Relay
22987 | RHT418G | Main | product or component type | Timing relay Plug-in relay
22988 | RHT418G | Main | device short name | RHT
22989 | RHT418G | Main | contacts type and composition | 4 C/O
22990 | RHT418G | Main | contact operation | Standard
22991 | RHT418G | Main | [Uc] control circuit voltage | 125 V AC/DC 50/60 Hz
22992 | RHT418G | Main | time delay type | On-delay
22993 | RHT418G | Main | time delay range | 0.2...3 s 1.5...30 s 15...300 s
22994 | RHT418G | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
22995 | RHT418G | Main | status LED | With
22996 | RHT418G | Main | control type | Selector switch
22997 | RHT418G | Main | coil interference suppression | With
22998 | RHT418G | Complementary | [Ui] rated insulation voltage | 250 V
22999 | RHT418G | Complementary | operating position | Any position
23000 | RHT418G | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
23001 | RHT418G | Complementary | contact bounce time | <= 10 ms
23002 | RHT418G | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
23003 | RHT418G | Complementary | average resistance | 30 mOhm at 20 °C
23004 | RHT418G | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
23005 | RHT418G | Complementary | average coil consumption | 2.5 W at 20 °C
23006 | RHT418G | Complementary | average coil consumption in VA | 2.9 at 20 °C
23007 | RHT418G | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
23008 | RHT418G | Complementary | mechanical durability | 20000000 cycles
23009 | RHT418G | Complementary | repeat accuracy | +/- 1 %
23010 | RHT418G | Complementary | setting accuracy of time delay | +/- 15 % of full scale
23011 | RHT418G | Complementary | reset time | 100 ms
23012 | RHT418G | Complementary | CAD overall width | 33 mm
23013 | RHT418G | Complementary | CAD overall height | 43 mm
23014 | RHT418G | Complementary | CAD overall depth | 108 mm
23015 | RHT418G | Complementary | terminals description ISO n°1 | (31-32-34)OC (21-22-24)OC (41-42-44)OC (A1-A2)CO (11-12-14)OC
23016 | RHT418G | Complementary | net weight | 0.13 kg
23017 | RHT418G | Environment | standards | IEC 60255 VDE 0435 NF C 45-250
23018 | RHT418G | Environment | product certifications | BV ASE EDF CSA USSR
23019 | RHT418G | Environment | protective treatment | TC
23020 | RHT418G | Environment | dielectric strength | 2500 V
23021 | RHT418G | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
23022 | RHT418G | Environment | ambient air temperature for storage | -40…70 °C
23023 | RHT418G | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
23024 | RHT418G | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
23025 | RHT418G | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
23026 | RHT418G | Contractual warranty | Warranty | 18 months
23027 | RHT411M | Main | range of product | Zelio Relay
23028 | RHT411M | Main | product or component type | Timing relay Plug-in relay
23029 | RHT411M | Main | device short name | RHT
23030 | RHT411M | Main | contacts type and composition | 4 C/O
23031 | RHT411M | Main | contact operation | Standard
23032 | RHT411M | Main | [Uc] control circuit voltage | 220 V AC 50/60 Hz
23033 | RHT411M | Main | time delay type | On-delay
23034 | RHT411M | Main | time delay range | 0.2...3 s 15...300 s 1.5...30 s
23035 | RHT411M | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
23036 | RHT411M | Main | status LED | With
23037 | RHT411M | Main | control type | Selector switch
23038 | RHT411M | Main | coil interference suppression | With
23039 | RHT411M | Complementary | [Ui] rated insulation voltage | 250 V
23040 | RHT411M | Complementary | operating position | Any position
23041 | RHT411M | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
23042 | RHT411M | Complementary | contact bounce time | <= 10 ms
23043 | RHT411M | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
23044 | RHT411M | Complementary | average resistance | 30 mOhm at 20 °C
23045 | RHT411M | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation
23046 | RHT411M | Complementary | average coil consumption in VA | 3.5 at 20 °C
23047 | RHT411M | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
23048 | RHT411M | Complementary | mechanical durability | 20000000 cycles
23049 | RHT411M | Complementary | repeat accuracy | +/- 1 %
23050 | RHT411M | Complementary | setting accuracy of time delay | +/- 15 % of full scale
23051 | RHT411M | Complementary | reset time | 100 ms
23052 | RHT411M | Complementary | CAD overall width | 33 mm
23053 | RHT411M | Complementary | CAD overall height | 43 mm
23054 | RHT411M | Complementary | CAD overall depth | 108 mm
23055 | RHT411M | Complementary | terminals description ISO n°1 | (31-32-34)OC (A1-A2)CO (11-12-14)OC (21-22-24)OC (41-42-44)OC
23056 | RHT411M | Complementary | net weight | 0.13 kg
23057 | RHT411M | Environment | standards | NF C 45-250 VDE 0435 IEC 60255
23058 | RHT411M | Environment | product certifications | USSR CSA ASE EDF BV
23059 | RHT411M | Environment | protective treatment | TC
23060 | RHT411M | Environment | dielectric strength | 2500 V
23061 | RHT411M | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
23062 | RHT411M | Environment | ambient air temperature for storage | -40…70 °C
23063 | RHT411M | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
23064 | RHT411M | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
23065 | RHT411M | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
23066 | RHT411M | Contractual warranty | Warranty | 18 months
23067 | RHT411U | Main | range of product | Zelio Relay
23068 | RHT411U | Main | product or component type | Plug-in relay Timing relay
23069 | RHT411U | Main | device short name | RHT
23070 | RHT411U | Main | contacts type and composition | 4 C/O
23071 | RHT411U | Main | contact operation | Standard
23072 | RHT411U | Main | [Uc] control circuit voltage | 240 V AC 50/60 Hz
23073 | RHT411U | Main | time delay type | On-delay
23074 | RHT411U | Main | time delay range | 15...300 s 1.5...30 s 0.2...3 s
23075 | RHT411U | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
23076 | RHT411U | Main | status LED | With
23077 | RHT411U | Main | control type | Selector switch
23078 | RHT411U | Main | coil interference suppression | With
23079 | RHT411U | Complementary | [Ui] rated insulation voltage | 250 V
23080 | RHT411U | Complementary | operating position | Any position
23081 | RHT411U | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
23082 | RHT411U | Complementary | contact bounce time | <= 10 ms
23083 | RHT411U | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
23084 | RHT411U | Complementary | average resistance | 30 mOhm at 20 °C
23085 | RHT411U | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation
23086 | RHT411U | Complementary | average coil consumption in VA | 3.5 at 20 °C
23087 | RHT411U | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
23088 | RHT411U | Complementary | mechanical durability | 20000000 cycles
23089 | RHT411U | Complementary | repeat accuracy | +/- 1 %
23090 | RHT411U | Complementary | setting accuracy of time delay | +/- 15 % of full scale
23091 | RHT411U | Complementary | reset time | 100 ms
23092 | RHT411U | Complementary | CAD overall width | 33 mm
23093 | RHT411U | Complementary | CAD overall height | 43 mm
23094 | RHT411U | Complementary | CAD overall depth | 108 mm
23095 | RHT411U | Complementary | terminals description ISO n°1 | (21-22-24)OC (31-32-34)OC (41-42-44)OC (A1-A2)CO (11-12-14)OC
23096 | RHT411U | Complementary | net weight | 0.13 kg
23097 | RHT411U | Environment | standards | VDE 0435 NF C 45-250 IEC 60255
23098 | RHT411U | Environment | product certifications | USSR CSA EDF ASE BV
23099 | RHT411U | Environment | protective treatment | TC
23100 | RHT411U | Environment | dielectric strength | 2500 V
23101 | RHT411U | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
23102 | RHT411U | Environment | ambient air temperature for storage | -40…70 °C
23103 | RHT411U | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
23104 | RHT411U | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
23105 | RHT411U | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
23106 | RHT411U | Contractual warranty | Warranty | 18 months
23107 | RHT418B | Main | range of product | Zelio Relay
23108 | RHT418B | Main | product or component type | Timing relay Plug-in relay
23109 | RHT418B | Main | device short name | RHT
23110 | RHT418B | Main | contacts type and composition | 4 C/O
23111 | RHT418B | Main | contact operation | Standard
23112 | RHT418B | Main | [Uc] control circuit voltage | 24 V AC/DC 50/60 Hz
23113 | RHT418B | Main | time delay type | On-delay
23114 | RHT418B | Main | time delay range | 0.2...3 s 15...300 s 1.5...30 s
23115 | RHT418B | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
23116 | RHT418B | Main | status LED | With
23117 | RHT418B | Main | control type | Selector switch
23118 | RHT418B | Main | coil interference suppression | With
23119 | RHT418B | Complementary | [Ui] rated insulation voltage | 250 V
23120 | RHT418B | Complementary | operating position | Any position
23121 | RHT418B | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
23122 | RHT418B | Complementary | contact bounce time | <= 10 ms
23123 | RHT418B | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
23124 | RHT418B | Complementary | average resistance | 30 mOhm at 20 °C
23125 | RHT418B | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
23126 | RHT418B | Complementary | average coil consumption | 2.5 W at 20 °C
23127 | RHT418B | Complementary | average coil consumption in VA | 2.9 at 20 °C
23128 | RHT418B | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
23129 | RHT418B | Complementary | mechanical durability | 20000000 cycles
23130 | RHT418B | Complementary | repeat accuracy | +/- 1 %
23131 | RHT418B | Complementary | setting accuracy of time delay | +/- 15 % of full scale
23132 | RHT418B | Complementary | reset time | 100 ms
23133 | RHT418B | Complementary | CAD overall width | 33 mm
23134 | RHT418B | Complementary | CAD overall height | 43 mm
23135 | RHT418B | Complementary | CAD overall depth | 108 mm
23136 | RHT418B | Complementary | terminals description ISO n°1 | (31-32-34)OC (21-22-24)OC (11-12-14)OC (A1-A2)CO (41-42-44)OC
23137 | RHT418B | Complementary | net weight | 0.13 kg
23138 | RHT418B | Environment | standards | NF C 45-250 VDE 0435 IEC 60255
23139 | RHT418B | Environment | product certifications | EDF USSR CSA ASE BV
23140 | RHT418B | Environment | protective treatment | TC
23141 | RHT418B | Environment | dielectric strength | 2500 V
23142 | RHT418B | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
23143 | RHT418B | Environment | ambient air temperature for storage | -40…70 °C
23144 | RHT418B | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
23145 | RHT418B | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
23146 | RHT418B | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
23147 | RHT418B | Contractual warranty | Warranty | 18 months
23148 | RHT418BE | Main | range of product | Zelio Relay
23149 | RHT418BE | Main | product or component type | Timing relay Plug-in relay
23150 | RHT418BE | Main | device short name | RHT
23151 | RHT418BE | Main | contacts type and composition | 4 C/O
23152 | RHT418BE | Main | contact operation | Standard
23153 | RHT418BE | Main | [Uc] control circuit voltage | 27 V AC/DC 50/60 Hz
23154 | RHT418BE | Main | time delay type | On-delay
23155 | RHT418BE | Main | time delay range | 0.2...3 s 15...300 s 1.5...30 s
23156 | RHT418BE | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
23157 | RHT418BE | Main | status LED | With
23158 | RHT418BE | Main | control type | Selector switch
23159 | RHT418BE | Main | coil interference suppression | With
23160 | RHT418BE | Complementary | [Ui] rated insulation voltage | 250 V
23161 | RHT418BE | Complementary | operating position | Any position
23162 | RHT418BE | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
23163 | RHT418BE | Complementary | contact bounce time | <= 10 ms
23164 | RHT418BE | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
23165 | RHT418BE | Complementary | average resistance | 30 mOhm at 20 °C
23166 | RHT418BE | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
23167 | RHT418BE | Complementary | average coil consumption | 2.5 W at 20 °C
23168 | RHT418BE | Complementary | average coil consumption in VA | 2.9 at 20 °C
23169 | RHT418BE | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
23170 | RHT418BE | Complementary | mechanical durability | 20000000 cycles
23171 | RHT418BE | Complementary | repeat accuracy | +/- 1 %
23172 | RHT418BE | Complementary | setting accuracy of time delay | +/- 15 % of full scale
23173 | RHT418BE | Complementary | reset time | 100 ms
23174 | RHT418BE | Complementary | CAD overall width | 33 mm
23175 | RHT418BE | Complementary | CAD overall height | 43 mm
23176 | RHT418BE | Complementary | CAD overall depth | 108 mm
23177 | RHT418BE | Complementary | terminals description ISO n°1 | (31-32-34)OC (41-42-44)OC (11-12-14)OC (21-22-24)OC (A1-A2)CO
23178 | RHT418BE | Complementary | net weight | 0.13 kg
23179 | RHT418BE | Environment | standards | IEC 60255 NF C 45-250 VDE 0435
23180 | RHT418BE | Environment | product certifications | ASE EDF USSR BV CSA
23181 | RHT418BE | Environment | protective treatment | TC
23182 | RHT418BE | Environment | dielectric strength | 2500 V
23183 | RHT418BE | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
23184 | RHT418BE | Environment | ambient air temperature for storage | -40…70 °C
23185 | RHT418BE | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
23186 | RHT418BE | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
23187 | RHT418BE | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
23188 | RHT418BE | Contractual warranty | Warranty | 18 months
23189 | RHT418E | Main | range of product | Zelio Relay
23190 | RHT418E | Main | product or component type | Timing relay Plug-in relay
23191 | RHT418E | Main | device short name | RHT
23192 | RHT418E | Main | contacts type and composition | 4 C/O
23193 | RHT418E | Main | contact operation | Standard
23194 | RHT418E | Main | [Uc] control circuit voltage | 48 V AC/DC 50/60 Hz
23195 | RHT418E | Main | time delay type | On-delay
23196 | RHT418E | Main | time delay range | 0.2...3 s 1.5...30 s 15...300 s
23197 | RHT418E | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C
23198 | RHT418E | Main | status LED | With
23199 | RHT418E | Main | control type | Selector switch
23200 | RHT418E | Main | coil interference suppression | With
23201 | RHT418E | Complementary | [Ui] rated insulation voltage | 250 V
23202 | RHT418E | Complementary | operating position | Any position
23203 | RHT418E | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V
23204 | RHT418E | Complementary | contact bounce time | <= 10 ms
23205 | RHT418E | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
23206 | RHT418E | Complementary | average resistance | 30 mOhm at 20 °C
23207 | RHT418E | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
23208 | RHT418E | Complementary | average coil consumption | 2.5 W at 20 °C
23209 | RHT418E | Complementary | average coil consumption in VA | 2.9 at 20 °C
23210 | RHT418E | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
23211 | RHT418E | Complementary | mechanical durability | 20000000 cycles
23212 | RHT418E | Complementary | repeat accuracy | +/- 1 %
23213 | RHT418E | Complementary | setting accuracy of time delay | +/- 15 % of full scale
23214 | RHT418E | Complementary | reset time | 100 ms
23215 | RHT418E | Complementary | CAD overall width | 33 mm
23216 | RHT418E | Complementary | CAD overall height | 43 mm
23217 | RHT418E | Complementary | CAD overall depth | 108 mm
23218 | RHT418E | Complementary | terminals description ISO n°1 | (21-22-24)OC (11-12-14)OC (41-42-44)OC (A1-A2)CO (31-32-34)OC
23219 | RHT418E | Complementary | net weight | 0.13 kg
23220 | RHT418E | Environment | standards | VDE 0435 IEC 60255 NF C 45-250
23221 | RHT418E | Environment | product certifications | CSA EDF ASE BV USSR
23222 | RHT418E | Environment | protective treatment | TC
23223 | RHT418E | Environment | dielectric strength | 2500 V
23224 | RHT418E | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
23225 | RHT418E | Environment | ambient air temperature for storage | -40…70 °C
23226 | RHT418E | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
23227 | RHT418E | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
23228 | RHT418E | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
23229 | RHT418E | Contractual warranty | Warranty | 18 months
23230 | RM4JA01B | Main | range of product | Zelio Control
23231 | RM4JA01B | Main | product or component type | Industrial measurement and control relays
23232 | RM4JA01B | Main | relay type | Current measurement relay
23233 | RM4JA01B | Main | relay name | RM4J
23234 | RM4JA01B | Main | relay monitored parameters | Overcurrent detection
23235 | RM4JA01B | Main | time delay | Without
23236 | RM4JA01B | Main | maximum power consumption in VA | 2 VA AC
23237 | RM4JA01B | Main | measurement range | 0.3...30 mA current AC 50/60 Hz 0.3...30 mA current DC 10...100 mA current AC 50/60 Hz 10...100 mA current DC 100...1000 mA current AC 50/60 Hz 100...1000 mA current DC
23238 | RM4JA01B | Main | contacts type and composition | 1 C/O
23239 | RM4JA01B | Complementary | maximum switching voltage | 440 V AC
23240 | RM4JA01B | Complementary | [Us] rated supply voltage | 24 V AC 50/60 Hz +/- 5 %
23241 | RM4JA01B | Complementary | operating voltage tolerance | 0.85...1.1 Uc
23242 | RM4JA01B | Complementary | output contacts | 1 C/O
23243 | RM4JA01B | Complementary | maximum measuring cycle | 80 ms
23244 | RM4JA01B | Complementary | internal input resistance | 33 Ohm 10 Ohm 1 Ohm
23245 | RM4JA01B | Complementary | permissible continuous overload | 0.15 A 0.05 A 1.5 A
23246 | RM4JA01B | Complementary | permissible non repetitive overload | 5 A 0.2 A 0.5 A
23247 | RM4JA01B | Complementary | setting accuracy of the switching threshold | +/-5 %
23248 | RM4JA01B | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23249 | RM4JA01B | Complementary | setting accuracy of time delay | 10 P
23250 | RM4JA01B | Complementary | hysteresis | 5…30 % adjustable of current threshold setting
23251 | RM4JA01B | Complementary | marking | CE : LVD 73/23/EEC CE : EMC 89/336/EEC
23252 | RM4JA01B | Complementary | overvoltage category | III conforming to IEC 60664-1
23253 | RM4JA01B | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
23254 | RM4JA01B | Complementary | supply disconnection value | > 0.1 Uc
23255 | RM4JA01B | Complementary | operating position | Any position without derating
23256 | RM4JA01B | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
23257 | RM4JA01B | Complementary | tightening torque | 0.6…1.1 N.m
23258 | RM4JA01B | Complementary | mechanical durability | 30000000 cycles
23259 | RM4JA01B | Complementary | [Ith] conventional free air thermal current | 8 A
23260 | RM4JA01B | Complementary | [Ie] rated operational current | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C
23261 | RM4JA01B | Complementary | switching capacity in mA | 10 mA at 12 V
23262 | RM4JA01B | Complementary | switching voltage | 250 V AC
23263 | RM4JA01B | Complementary | contacts material | 90/10 silver nickel contacts
23264 | RM4JA01B | Complementary | number of cables | 2
23265 | RM4JA01B | Complementary | width | 23 mm
23266 | RM4JA01B | Complementary | height | 78 mm
23267 | RM4JA01B | Complementary | depth | 80 mm
23268 | RM4JA01B | Complementary | terminals description ISO n°1 | (C-B1-B2-B3)CO (15-16-18)OC (A1-A2)CO
23269 | RM4JA01B | Complementary | output relay state | Tripped if V measured > V set Tripped if A measured > A set
23270 | RM4JA01B | Complementary | 9 mm pitches | 2.5
23271 | RM4JA01B | Complementary | net weight | 0.172 kg
23272 | RM4JA01B | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
23273 | RM4JA01B | Environment | standards | EN/IEC 60255-6
23274 | RM4JA01B | Environment | product certifications | GL CSA UL
23275 | RM4JA01B | Environment | ambient air temperature for storage | -40…85 °C
23276 | RM4JA01B | Environment | ambient air temperature for operation | -20…65 °C
23277 | RM4JA01B | Environment | environmental characteristic | 3K3
23278 | RM4JA01B | Environment | relative humidity | 15…85 % conforming to IEC 60721-3-3
23279 | RM4JA01B | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
23280 | RM4JA01B | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
23281 | RM4JA01B | Environment | pollution degree | 3 conforming to IEC 60664-1
23282 | RM4JA01B | Environment | dielectric test voltage | 2.5 kV
23283 | RM4JA01B | Environment | non-dissipating shock wave | 4.8 kV
23284 | RM4JA01B | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
23285 | RM4JA01B | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
23286 | RM4JA01B | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
23287 | RM4JA01B | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
23288 | RM4JA01B | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
23289 | RM4JA01B | Contractual warranty | Warranty | 18 months
23290 | RM4JA01F | Main | range of product | Zelio Control
23291 | RM4JA01F | Main | product or component type | Industrial measurement and control relays
23292 | RM4JA01F | Main | relay type | Current measurement relay
23293 | RM4JA01F | Main | relay name | RM4J
23294 | RM4JA01F | Main | relay monitored parameters | Overcurrent detection
23295 | RM4JA01F | Main | time delay | Without
23296 | RM4JA01F | Main | maximum power consumption in VA | 3.3 VA AC
23297 | RM4JA01F | Main | measurement range | 0.3...30 mA current AC 50/60 Hz 0.3...30 mA current DC 10...100 mA current AC 50/60 Hz 10...100 mA current DC 100...1000 mA current AC 50/60 Hz 100...1000 mA current DC
23298 | RM4JA01F | Main | contacts type and composition | 1 C/O
23299 | RM4JA01F | Complementary | maximum switching voltage | 440 V AC
23300 | RM4JA01F | Complementary | [Us] rated supply voltage | 110...130 V AC 50/60 Hz +/- 5 %
23301 | RM4JA01F | Complementary | operating voltage tolerance | 0.85...1.1 Uc
23302 | RM4JA01F | Complementary | output contacts | 1 C/O
23303 | RM4JA01F | Complementary | maximum measuring cycle | 80 ms
23304 | RM4JA01F | Complementary | internal input resistance | 1 Ohm 33 Ohm 10 Ohm
23305 | RM4JA01F | Complementary | permissible continuous overload | 0.05 A 0.15 A 1.5 A
23306 | RM4JA01F | Complementary | permissible non repetitive overload | 5 A 0.2 A 0.5 A
23307 | RM4JA01F | Complementary | setting accuracy of the switching threshold | +/-5 %
23308 | RM4JA01F | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23309 | RM4JA01F | Complementary | setting accuracy of time delay | 10 P
23310 | RM4JA01F | Complementary | hysteresis | 5…30 % adjustable of current threshold setting
23311 | RM4JA01F | Complementary | marking | CE : LVD 73/23/EEC CE : EMC 89/336/EEC
23312 | RM4JA01F | Complementary | overvoltage category | III conforming to IEC 60664-1
23313 | RM4JA01F | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
23314 | RM4JA01F | Complementary | supply disconnection value | > 0.1 Uc
23315 | RM4JA01F | Complementary | operating position | Any position without derating
23316 | RM4JA01F | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
23317 | RM4JA01F | Complementary | tightening torque | 0.6…1.1 N.m
23318 | RM4JA01F | Complementary | mechanical durability | 30000000 cycles
23319 | RM4JA01F | Complementary | [Ith] conventional free air thermal current | 8 A
23320 | RM4JA01F | Complementary | [Ie] rated operational current | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C
23321 | RM4JA01F | Complementary | switching capacity in mA | 10 mA at 12 V
23322 | RM4JA01F | Complementary | switching voltage | 250 V AC
23323 | RM4JA01F | Complementary | contacts material | 90/10 silver nickel contacts
23324 | RM4JA01F | Complementary | number of cables | 2
23325 | RM4JA01F | Complementary | width | 23 mm
23326 | RM4JA01F | Complementary | height | 78 mm
23327 | RM4JA01F | Complementary | depth | 80 mm
23328 | RM4JA01F | Complementary | terminals description ISO n°1 | (A1-A2)CO (15-16-18)OC (C-B1-B2-B3)CO
23329 | RM4JA01F | Complementary | output relay state | Tripped if A measured > A set Tripped if V measured > V set
23330 | RM4JA01F | Complementary | 9 mm pitches | 2.5
23331 | RM4JA01F | Complementary | net weight | 0.172 kg
23332 | RM4JA01F | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
23333 | RM4JA01F | Environment | standards | EN/IEC 60255-6
23334 | RM4JA01F | Environment | product certifications | CSA UL GL
23335 | RM4JA01F | Environment | ambient air temperature for storage | -40…85 °C
23336 | RM4JA01F | Environment | ambient air temperature for operation | -20…65 °C
23337 | RM4JA01F | Environment | environmental characteristic | 3K3
23338 | RM4JA01F | Environment | relative humidity | 15…85 % conforming to IEC 60721-3-3
23339 | RM4JA01F | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
23340 | RM4JA01F | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
23341 | RM4JA01F | Environment | pollution degree | 3 conforming to IEC 60664-1
23342 | RM4JA01F | Environment | dielectric test voltage | 2.5 kV
23343 | RM4JA01F | Environment | non-dissipating shock wave | 4.8 kV
23344 | RM4JA01F | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
23345 | RM4JA01F | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
23346 | RM4JA01F | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
23347 | RM4JA01F | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
23348 | RM4JA01F | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
23349 | RM4JA01F | Contractual warranty | Warranty | 18 months
23350 | RM4JA01M | Main | range of product | Zelio Control
23351 | RM4JA01M | Main | product or component type | Industrial measurement and control relays
23352 | RM4JA01M | Main | relay type | Current measurement relay
23353 | RM4JA01M | Main | relay name | RM4J
23354 | RM4JA01M | Main | relay monitored parameters | Overcurrent detection
23355 | RM4JA01M | Main | time delay | Without
23356 | RM4JA01M | Main | maximum power consumption in VA | 3.5 VA AC
23357 | RM4JA01M | Main | measurement range | 0.3...30 mA current AC 50/60 Hz 0.3...30 mA current DC 10...100 mA current AC 50/60 Hz 10...100 mA current DC 100...1000 mA current AC 50/60 Hz 100...1000 mA current DC
23358 | RM4JA01M | Main | contacts type and composition | 1 C/O
23359 | RM4JA01M | Complementary | maximum switching voltage | 440 V AC
23360 | RM4JA01M | Complementary | [Us] rated supply voltage | 220...240 V AC 50/60 Hz +/- 5 %
23361 | RM4JA01M | Complementary | operating voltage tolerance | 0.85...1.1 Uc
23362 | RM4JA01M | Complementary | output contacts | 1 C/O
23363 | RM4JA01M | Complementary | maximum measuring cycle | 80 ms
23364 | RM4JA01M | Complementary | internal input resistance | 10 Ohm 1 Ohm 33 Ohm
23365 | RM4JA01M | Complementary | permissible continuous overload | 1.5 A 0.15 A 0.05 A
23366 | RM4JA01M | Complementary | permissible non repetitive overload | 5 A 0.2 A 0.5 A
23367 | RM4JA01M | Complementary | setting accuracy of the switching threshold | +/-5 %
23368 | RM4JA01M | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23369 | RM4JA01M | Complementary | setting accuracy of time delay | 10 P
23370 | RM4JA01M | Complementary | hysteresis | 5…30 % adjustable of current threshold setting
23371 | RM4JA01M | Complementary | marking | CE : LVD 73/23/EEC CE : EMC 89/336/EEC
23372 | RM4JA01M | Complementary | overvoltage category | III conforming to IEC 60664-1
23373 | RM4JA01M | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
23374 | RM4JA01M | Complementary | supply disconnection value | > 0.1 Uc
23375 | RM4JA01M | Complementary | operating position | Any position without derating
23376 | RM4JA01M | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
23377 | RM4JA01M | Complementary | tightening torque | 0.6…1.1 N.m
23378 | RM4JA01M | Complementary | mechanical durability | 30000000 cycles
23379 | RM4JA01M | Complementary | [Ith] conventional free air thermal current | 8 A
23380 | RM4JA01M | Complementary | [Ie] rated operational current | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C
23381 | RM4JA01M | Complementary | switching capacity in mA | 10 mA at 12 V
23382 | RM4JA01M | Complementary | switching voltage | 250 V AC
23383 | RM4JA01M | Complementary | contacts material | 90/10 silver nickel contacts
23384 | RM4JA01M | Complementary | number of cables | 2
23385 | RM4JA01M | Complementary | width | 23 mm
23386 | RM4JA01M | Complementary | height | 78 mm
23387 | RM4JA01M | Complementary | depth | 80 mm
23388 | RM4JA01M | Complementary | terminals description ISO n°1 | (15-16-18)OC (C-B1-B2-B3)CO (A1-A2)CO
23389 | RM4JA01M | Complementary | output relay state | Tripped if V measured > V set Tripped if A measured > A set
23390 | RM4JA01M | Complementary | 9 mm pitches | 2.5
23391 | RM4JA01M | Complementary | net weight | 0.172 kg
23392 | RM4JA01M | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
23393 | RM4JA01M | Environment | standards | EN/IEC 60255-6
23394 | RM4JA01M | Environment | product certifications | CSA UL GL
23395 | RM4JA01M | Environment | ambient air temperature for storage | -40…85 °C
23396 | RM4JA01M | Environment | ambient air temperature for operation | -20…65 °C
23397 | RM4JA01M | Environment | environmental characteristic | 3K3
23398 | RM4JA01M | Environment | relative humidity | 15…85 % conforming to IEC 60721-3-3
23399 | RM4JA01M | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
23400 | RM4JA01M | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
23401 | RM4JA01M | Environment | pollution degree | 3 conforming to IEC 60664-1
23402 | RM4JA01M | Environment | dielectric test voltage | 2.5 kV
23403 | RM4JA01M | Environment | non-dissipating shock wave | 4.8 kV
23404 | RM4JA01M | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
23405 | RM4JA01M | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
23406 | RM4JA01M | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
23407 | RM4JA01M | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
23408 | RM4JA01M | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
23409 | RM4JA01M | Contractual warranty | Warranty | 18 months
23410 | RM4JA31F | Main | range of product | Zelio Control
23411 | RM4JA31F | Main | product or component type | Industrial measurement and control relays
23412 | RM4JA31F | Main | relay type | Current measurement relay
23413 | RM4JA31F | Main | relay name | RM4J
23414 | RM4JA31F | Main | relay monitored parameters | Overcurrent or undercurrent detection
23415 | RM4JA31F | Main | time delay | Adjustable 0.05...30 s
23416 | RM4JA31F | Main | maximum power consumption in VA | 3.3 VA AC
23417 | RM4JA31F | Main | measurement range | 0.3...30 mA current AC 50/60 Hz 0.3...30 mA current DC 10...100 mA current AC 50/60 Hz 10...100 mA current DC 100...1000 mA current AC 50/60 Hz 100...1000 mA current DC
23418 | RM4JA31F | Main | contacts type and composition | 2 C/O
23419 | RM4JA31F | Complementary | maximum switching voltage | 440 V AC
23420 | RM4JA31F | Complementary | [Us] rated supply voltage | 110...130 V AC 50/60 Hz +/- 5 %
23421 | RM4JA31F | Complementary | operating voltage tolerance | 0.85...1.1 Uc
23422 | RM4JA31F | Complementary | output contacts | 2 C/O
23423 | RM4JA31F | Complementary | maximum measuring cycle | 80 ms
23424 | RM4JA31F | Complementary | internal input resistance | 33 Ohm 10 Ohm 1 Ohm
23425 | RM4JA31F | Complementary | permissible continuous overload | 1.5 A 0.15 A 0.05 A
23426 | RM4JA31F | Complementary | permissible non repetitive overload | 5 A 0.2 A 0.5 A
23427 | RM4JA31F | Complementary | setting accuracy of the switching threshold | +/-5 %
23428 | RM4JA31F | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23429 | RM4JA31F | Complementary | setting accuracy of time delay | 10 P
23430 | RM4JA31F | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23431 | RM4JA31F | Complementary | hysteresis | 5…30 % adjustable of current threshold setting
23432 | RM4JA31F | Complementary | marking | CE : LVD 73/23/EEC CE : EMC 89/336/EEC
23433 | RM4JA31F | Complementary | overvoltage category | III conforming to IEC 60664-1
23434 | RM4JA31F | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
23435 | RM4JA31F | Complementary | supply disconnection value | > 0.1 Uc
23436 | RM4JA31F | Complementary | operating position | Any position without derating
23437 | RM4JA31F | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
23438 | RM4JA31F | Complementary | tightening torque | 0.6…1.1 N.m
23439 | RM4JA31F | Complementary | mechanical durability | 30000000 cycles
23440 | RM4JA31F | Complementary | [Ith] conventional free air thermal current | 8 A
23441 | RM4JA31F | Complementary | [Ie] rated operational current | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C
23442 | RM4JA31F | Complementary | switching capacity in mA | 10 mA at 12 V
23443 | RM4JA31F | Complementary | switching voltage | 250 V AC
23444 | RM4JA31F | Complementary | contacts material | 90/10 silver nickel contacts
23445 | RM4JA31F | Complementary | number of cables | 2
23446 | RM4JA31F | Complementary | width | 23 mm
23447 | RM4JA31F | Complementary | height | 78 mm
23448 | RM4JA31F | Complementary | depth | 80 mm
23449 | RM4JA31F | Complementary | terminals description ISO n°1 | (25-26-28)OC (C-B1-B2-B3)CO (A1-A2)CO (15-16-18)OC
23450 | RM4JA31F | Complementary | output relay state | Tripped if A measured > A set Tripped if V measured > V set
23451 | RM4JA31F | Complementary | 9 mm pitches | 2.5
23452 | RM4JA31F | Complementary | net weight | 0.172 kg
23453 | RM4JA31F | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
23454 | RM4JA31F | Environment | standards | EN/IEC 60255-6
23455 | RM4JA31F | Environment | product certifications | CSA GL UL
23456 | RM4JA31F | Environment | ambient air temperature for storage | -40…85 °C
23457 | RM4JA31F | Environment | ambient air temperature for operation | -20…65 °C
23458 | RM4JA31F | Environment | environmental characteristic | 3K3
23459 | RM4JA31F | Environment | relative humidity | 15…85 % conforming to IEC 60721-3-3
23460 | RM4JA31F | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
23461 | RM4JA31F | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
23462 | RM4JA31F | Environment | pollution degree | 3 conforming to IEC 60664-1
23463 | RM4JA31F | Environment | dielectric test voltage | 2.5 kV
23464 | RM4JA31F | Environment | non-dissipating shock wave | 4.8 kV
23465 | RM4JA31F | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
23466 | RM4JA31F | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
23467 | RM4JA31F | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
23468 | RM4JA31F | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
23469 | RM4JA31F | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
23470 | RM4JA31F | Contractual warranty | Warranty | 18 months
23471 | RM4JA31M | Main | range of product | Zelio Control
23472 | RM4JA31M | Main | product or component type | Industrial measurement and control relays
23473 | RM4JA31M | Main | relay type | Current measurement relay
23474 | RM4JA31M | Main | relay name | RM4J
23475 | RM4JA31M | Main | relay monitored parameters | Overcurrent or undercurrent detection
23476 | RM4JA31M | Main | time delay | Adjustable 0.05...30 s
23477 | RM4JA31M | Main | maximum power consumption in VA | 3.4 VA AC
23478 | RM4JA31M | Main | measurement range | 0.3...30 mA current DC 10...100 mA current DC 100...1000 mA current DC 0.3...30 mA current AC 10...100 mA current AC 100...1000 mA current AC
23479 | RM4JA31M | Main | contacts type and composition | 2 C/O
23480 | RM4JA31M | Complementary | maximum switching voltage | 440 V AC
23481 | RM4JA31M | Complementary | [Us] rated supply voltage | 220...240 V AC 50/60 Hz +/- 5 %
23482 | RM4JA31M | Complementary | operating voltage tolerance | 0.85...1.1 Uc
23483 | RM4JA31M | Complementary | output contacts | 2 C/O
23484 | RM4JA31M | Complementary | maximum measuring cycle | 80 ms
23485 | RM4JA31M | Complementary | internal input resistance | 1 Ohm 10 Ohm 33 Ohm
23486 | RM4JA31M | Complementary | permissible continuous overload | 0.05 A 1.5 A 0.15 A
23487 | RM4JA31M | Complementary | permissible non repetitive overload | 5 A 0.2 A 0.5 A
23488 | RM4JA31M | Complementary | setting accuracy of the switching threshold | +/-5 %
23489 | RM4JA31M | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23490 | RM4JA31M | Complementary | setting accuracy of time delay | 10 P
23491 | RM4JA31M | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23492 | RM4JA31M | Complementary | hysteresis | 5…30 % adjustable of current threshold setting
23493 | RM4JA31M | Complementary | marking | CE : LVD 73/23/EEC CE : EMC 89/336/EEC
23494 | RM4JA31M | Complementary | overvoltage category | III conforming to IEC 60664-1
23495 | RM4JA31M | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
23496 | RM4JA31M | Complementary | supply disconnection value | > 0.1 Uc
23497 | RM4JA31M | Complementary | operating position | Any position without derating
23498 | RM4JA31M | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
23499 | RM4JA31M | Complementary | tightening torque | 0.6…1.1 N.m
23500 | RM4JA31M | Complementary | mechanical durability | 30000000 cycles
23501 | RM4JA31M | Complementary | [Ith] conventional free air thermal current | 8 A
23502 | RM4JA31M | Complementary | [Ie] rated operational current | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C
23503 | RM4JA31M | Complementary | switching capacity in mA | 10 mA at 12 V
23504 | RM4JA31M | Complementary | switching voltage | 250 V AC
23505 | RM4JA31M | Complementary | contacts material | 90/10 silver nickel contacts
23506 | RM4JA31M | Complementary | number of cables | 2
23507 | RM4JA31M | Complementary | width | 23 mm
23508 | RM4JA31M | Complementary | height | 78 mm
23509 | RM4JA31M | Complementary | depth | 80 mm
23510 | RM4JA31M | Complementary | terminals description ISO n°1 | (C-B1-B2-B3)CO (25-26-28)OC (A1-A2)CO (15-16-18)OC
23511 | RM4JA31M | Complementary | output relay state | Tripped if V measured > V set Tripped if A measured > A set
23512 | RM4JA31M | Complementary | 9 mm pitches | 2.5
23513 | RM4JA31M | Complementary | net weight | 0.172 kg
23514 | RM4JA31M | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
23515 | RM4JA31M | Environment | standards | EN/IEC 60255-6
23516 | RM4JA31M | Environment | product certifications | UL CSA GL
23517 | RM4JA31M | Environment | ambient air temperature for storage | -40…85 °C
23518 | RM4JA31M | Environment | ambient air temperature for operation | -20…65 °C
23519 | RM4JA31M | Environment | environmental characteristic | 3K3
23520 | RM4JA31M | Environment | relative humidity | 15…85 % conforming to IEC 60721-3-3
23521 | RM4JA31M | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
23522 | RM4JA31M | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
23523 | RM4JA31M | Environment | pollution degree | 3 conforming to IEC 60664-1
23524 | RM4JA31M | Environment | dielectric test voltage | 2.5 kV
23525 | RM4JA31M | Environment | non-dissipating shock wave | 4.8 kV
23526 | RM4JA31M | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
23527 | RM4JA31M | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
23528 | RM4JA31M | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
23529 | RM4JA31M | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
23530 | RM4JA31M | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
23531 | RM4JA31M | Contractual warranty | Warranty | 18 months
23532 | RM4JA31MW | Main | range of product | Zelio Control
23533 | RM4JA31MW | Main | product or component type | Industrial measurement and control relays
23534 | RM4JA31MW | Main | relay type | Current measurement relay
23535 | RM4JA31MW | Main | relay name | RM4J
23536 | RM4JA31MW | Main | relay monitored parameters | Overcurrent or undercurrent detection
23537 | RM4JA31MW | Main | time delay | Adjustable 0.05...30 s
23538 | RM4JA31MW | Main | maximum power consumption in VA | 3.3 VA AC
23539 | RM4JA31MW | Main | measurement range | 0.3...30 mA current DC 10...100 mA current DC 100...1000 mA current DC 0.3...30 mA current AC 10...100 mA current AC 100...1000 mA current AC
23540 | RM4JA31MW | Main | contacts type and composition | 2 C/O
23541 | RM4JA31MW | Complementary | maximum switching voltage | 440 V AC
23542 | RM4JA31MW | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz +/- 5 % 24...240 V DC
23543 | RM4JA31MW | Complementary | operating voltage tolerance | 0.85...1.1 Uc
23544 | RM4JA31MW | Complementary | maximum power consumption in W | 1.2 W DC
23545 | RM4JA31MW | Complementary | output contacts | 2 C/O
23546 | RM4JA31MW | Complementary | maximum measuring cycle | 80 ms
23547 | RM4JA31MW | Complementary | internal input resistance | 10 Ohm 33 Ohm 1 Ohm
23548 | RM4JA31MW | Complementary | permissible continuous overload | 0.15 A 1.5 A 0.05 A
23549 | RM4JA31MW | Complementary | permissible non repetitive overload | 5 A 0.2 A 0.5 A
23550 | RM4JA31MW | Complementary | setting accuracy of the switching threshold | +/-5 %
23551 | RM4JA31MW | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23552 | RM4JA31MW | Complementary | setting accuracy of time delay | 10 P
23553 | RM4JA31MW | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23554 | RM4JA31MW | Complementary | hysteresis | 5…30 % adjustable of current threshold setting
23555 | RM4JA31MW | Complementary | marking | CE : EMC 89/336/EEC CE : LVD 73/23/EEC
23556 | RM4JA31MW | Complementary | overvoltage category | III conforming to IEC 60664-1
23557 | RM4JA31MW | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
23558 | RM4JA31MW | Complementary | supply disconnection value | > 0.1 Uc
23559 | RM4JA31MW | Complementary | operating position | Any position without derating
23560 | RM4JA31MW | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
23561 | RM4JA31MW | Complementary | tightening torque | 0.6…1.1 N.m
23562 | RM4JA31MW | Complementary | mechanical durability | 30000000 cycles
23563 | RM4JA31MW | Complementary | [Ith] conventional free air thermal current | 8 A
23564 | RM4JA31MW | Complementary | [Ie] rated operational current | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C
23565 | RM4JA31MW | Complementary | switching capacity in mA | 10 mA at 12 V
23566 | RM4JA31MW | Complementary | switching voltage | 250 V AC
23567 | RM4JA31MW | Complementary | contacts material | 90/10 silver nickel contacts
23568 | RM4JA31MW | Complementary | number of cables | 2
23569 | RM4JA31MW | Complementary | width | 23 mm
23570 | RM4JA31MW | Complementary | height | 78 mm
23571 | RM4JA31MW | Complementary | depth | 80 mm
23572 | RM4JA31MW | Complementary | terminals description ISO n°1 | (25-26-28)OC (C-B1-B2-B3)CO (15-16-18)OC (A1-A2)CO
23573 | RM4JA31MW | Complementary | output relay state | Tripped if A measured > A set Tripped if V measured > V set
23574 | RM4JA31MW | Complementary | 9 mm pitches | 2.5
23575 | RM4JA31MW | Complementary | net weight | 0.172 kg
23576 | RM4JA31MW | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
23577 | RM4JA31MW | Environment | standards | EN/IEC 60255-6
23578 | RM4JA31MW | Environment | product certifications | CSA GL UL
23579 | RM4JA31MW | Environment | ambient air temperature for storage | -40…85 °C
23580 | RM4JA31MW | Environment | ambient air temperature for operation | -20…65 °C
23581 | RM4JA31MW | Environment | environmental characteristic | 3K3
23582 | RM4JA31MW | Environment | relative humidity | 15…85 % conforming to IEC 60721-3-3
23583 | RM4JA31MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
23584 | RM4JA31MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
23585 | RM4JA31MW | Environment | pollution degree | 3 conforming to IEC 60664-1
23586 | RM4JA31MW | Environment | dielectric test voltage | 2.5 kV
23587 | RM4JA31MW | Environment | non-dissipating shock wave | 4.8 kV
23588 | RM4JA31MW | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
23589 | RM4JA31MW | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
23590 | RM4JA31MW | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
23591 | RM4JA31MW | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
23592 | RM4JA31MW | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
23593 | RM4JA31MW | Contractual warranty | Warranty | 18 months
23594 | RM4JA31Q | Main | range of product | Zelio Control
23595 | RM4JA31Q | Main | product or component type | Industrial measurement and control relays
23596 | RM4JA31Q | Main | relay type | Current measurement relay
23597 | RM4JA31Q | Main | relay name | RM4J
23598 | RM4JA31Q | Main | relay monitored parameters | Overcurrent or undercurrent detection
23599 | RM4JA31Q | Main | time delay | Adjustable 0.05...30 s
23600 | RM4JA31Q | Main | maximum power consumption in VA | 3 VA AC
23601 | RM4JA31Q | Main | measurement range | 0.3...30 mA current DC 10...100 mA current DC 100...1000 mA current DC 0.3...30 mA current AC 10...100 mA current AC 100...1000 mA current AC
23602 | RM4JA31Q | Main | contacts type and composition | 2 C/O
23603 | RM4JA31Q | Complementary | maximum switching voltage | 440 V AC
23604 | RM4JA31Q | Complementary | [Us] rated supply voltage | 380...415 V AC 50/60 Hz +/- 5 %
23605 | RM4JA31Q | Complementary | operating voltage tolerance | 0.85...1.1 Uc
23606 | RM4JA31Q | Complementary | output contacts | 2 C/O
23607 | RM4JA31Q | Complementary | maximum measuring cycle | 80 ms
23608 | RM4JA31Q | Complementary | internal input resistance | 1 Ohm 10 Ohm 33 Ohm
23609 | RM4JA31Q | Complementary | permissible continuous overload | 0.15 A 1.5 A 0.05 A
23610 | RM4JA31Q | Complementary | permissible non repetitive overload | 5 A 0.2 A 0.5 A
23611 | RM4JA31Q | Complementary | setting accuracy of the switching threshold | +/-5 %
23612 | RM4JA31Q | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23613 | RM4JA31Q | Complementary | setting accuracy of time delay | 10 P
23614 | RM4JA31Q | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23615 | RM4JA31Q | Complementary | hysteresis | 5…30 % adjustable of current threshold setting
23616 | RM4JA31Q | Complementary | marking | CE : EMC 89/336/EEC CE : LVD 73/23/EEC
23617 | RM4JA31Q | Complementary | overvoltage category | III conforming to IEC 60664-1
23618 | RM4JA31Q | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
23619 | RM4JA31Q | Complementary | supply disconnection value | > 0.1 Uc
23620 | RM4JA31Q | Complementary | operating position | Any position without derating
23621 | RM4JA31Q | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
23622 | RM4JA31Q | Complementary | tightening torque | 0.6…1.1 N.m
23623 | RM4JA31Q | Complementary | mechanical durability | 30000000 cycles
23624 | RM4JA31Q | Complementary | [Ith] conventional free air thermal current | 8 A
23625 | RM4JA31Q | Complementary | [Ie] rated operational current | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C
23626 | RM4JA31Q | Complementary | switching capacity in mA | 10 mA at 12 V
23627 | RM4JA31Q | Complementary | switching voltage | 250 V AC
23628 | RM4JA31Q | Complementary | contacts material | 90/10 silver nickel contacts
23629 | RM4JA31Q | Complementary | number of cables | 2
23630 | RM4JA31Q | Complementary | width | 23 mm
23631 | RM4JA31Q | Complementary | height | 78 mm
23632 | RM4JA31Q | Complementary | depth | 80 mm
23633 | RM4JA31Q | Complementary | terminals description ISO n°1 | (A1-A2)CO (15-16-18)OC (C-B1-B2-B3)CO (25-26-28)OC
23634 | RM4JA31Q | Complementary | output relay state | Tripped if A measured > A set Tripped if V measured > V set
23635 | RM4JA31Q | Complementary | 9 mm pitches | 2.5
23636 | RM4JA31Q | Complementary | net weight | 0.172 kg
23637 | RM4JA31Q | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
23638 | RM4JA31Q | Environment | standards | EN/IEC 60255-6
23639 | RM4JA31Q | Environment | product certifications | UL GL CSA
23640 | RM4JA31Q | Environment | ambient air temperature for storage | -40…85 °C
23641 | RM4JA31Q | Environment | ambient air temperature for operation | -20…65 °C
23642 | RM4JA31Q | Environment | environmental characteristic | 3K3
23643 | RM4JA31Q | Environment | relative humidity | 15…85 % conforming to IEC 60721-3-3
23644 | RM4JA31Q | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
23645 | RM4JA31Q | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
23646 | RM4JA31Q | Environment | pollution degree | 3 conforming to IEC 60664-1
23647 | RM4JA31Q | Environment | dielectric test voltage | 2.5 kV
23648 | RM4JA31Q | Environment | non-dissipating shock wave | 4.8 kV
23649 | RM4JA31Q | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
23650 | RM4JA31Q | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
23651 | RM4JA31Q | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
23652 | RM4JA31Q | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
23653 | RM4JA31Q | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
23654 | RM4JA31Q | Contractual warranty | Warranty | 18 months
23655 | RM4JA32F | Main | range of product | Zelio Control
23656 | RM4JA32F | Main | product or component type | Industrial measurement and control relays
23657 | RM4JA32F | Main | relay type | Current measurement relay
23658 | RM4JA32F | Main | relay name | RM4J
23659 | RM4JA32F | Main | relay monitored parameters | Overcurrent or undercurrent detection
23660 | RM4JA32F | Main | time delay | Adjustable 0.05...30 s
23661 | RM4JA32F | Main | maximum power consumption in VA | 3.3 VA AC
23662 | RM4JA32F | Main | measurement range | 1...5 A current AC 1...5 A current DC 3...15 A current AC 3...15 A current DC 300...1500 mA current AC 300...1500 mA current DC
23663 | RM4JA32F | Main | contacts type and composition | 2 C/O
23664 | RM4JA32F | Complementary | maximum switching voltage | 440 V AC
23665 | RM4JA32F | Complementary | [Us] rated supply voltage | 110...130 V AC 50/60 Hz +/- 5 %
23666 | RM4JA32F | Complementary | operating voltage tolerance | 0.85...1.1 Uc
23667 | RM4JA32F | Complementary | output contacts | 2 C/O
23668 | RM4JA32F | Complementary | maximum measuring cycle | 80 ms
23669 | RM4JA32F | Complementary | internal input resistance | 0.02 Ohm 0.06 Ohm 0.006 Ohm
23670 | RM4JA32F | Complementary | permissible continuous overload | 2 A 20 A 7 A
23671 | RM4JA32F | Complementary | permissible non repetitive overload | 10 A for <= 3 s 100 A 15 A
23672 | RM4JA32F | Complementary | setting accuracy of the switching threshold | +/-5 %
23673 | RM4JA32F | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23674 | RM4JA32F | Complementary | setting accuracy of time delay | 10 P
23675 | RM4JA32F | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23676 | RM4JA32F | Complementary | hysteresis | 5…30 % adjustable of current threshold setting
23677 | RM4JA32F | Complementary | marking | CE : EMC 89/336/EEC CE : LVD 73/23/EEC
23678 | RM4JA32F | Complementary | overvoltage category | III conforming to IEC 60664-1
23679 | RM4JA32F | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
23680 | RM4JA32F | Complementary | supply disconnection value | > 0.1 Uc
23681 | RM4JA32F | Complementary | operating position | Any position without derating
23682 | RM4JA32F | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
23683 | RM4JA32F | Complementary | tightening torque | 0.6…1.1 N.m
23684 | RM4JA32F | Complementary | mechanical durability | 30000000 cycles
23685 | RM4JA32F | Complementary | [Ith] conventional free air thermal current | 8 A
23686 | RM4JA32F | Complementary | [Ie] rated operational current | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C
23687 | RM4JA32F | Complementary | switching capacity in mA | 10 mA at 12 V
23688 | RM4JA32F | Complementary | switching voltage | 250 V AC
23689 | RM4JA32F | Complementary | contacts material | 90/10 silver nickel contacts
23690 | RM4JA32F | Complementary | number of cables | 2
23691 | RM4JA32F | Complementary | width | 45 mm
23692 | RM4JA32F | Complementary | height | 78 mm
23693 | RM4JA32F | Complementary | depth | 80 mm
23694 | RM4JA32F | Complementary | terminals description ISO n°1 | (15-16-18)OC (C-B1-B2-B3)CO (A1-A2)CO (25-26-28)OC
23695 | RM4JA32F | Complementary | output relay state | Tripped if A measured > A set Tripped if V measured > V set
23696 | RM4JA32F | Complementary | 9 mm pitches | 5
23697 | RM4JA32F | Complementary | net weight | 0.204 kg
23698 | RM4JA32F | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
23699 | RM4JA32F | Environment | standards | EN/IEC 60255-6
23700 | RM4JA32F | Environment | product certifications | GL CSA UL
23701 | RM4JA32F | Environment | ambient air temperature for storage | -40…85 °C
23702 | RM4JA32F | Environment | ambient air temperature for operation | -20…65 °C
23703 | RM4JA32F | Environment | environmental characteristic | 3K3
23704 | RM4JA32F | Environment | relative humidity | 15…85 % conforming to IEC 60721-3-3
23705 | RM4JA32F | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
23706 | RM4JA32F | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
23707 | RM4JA32F | Environment | pollution degree | 3 conforming to IEC 60664-1
23708 | RM4JA32F | Environment | dielectric test voltage | 2.5 kV
23709 | RM4JA32F | Environment | non-dissipating shock wave | 4.8 kV
23710 | RM4JA32F | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
23711 | RM4JA32F | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
23712 | RM4JA32F | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
23713 | RM4JA32F | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
23714 | RM4JA32F | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
23715 | RM4JA32F | Contractual warranty | Warranty | 18 months
23716 | RM4JA32M | Main | range of product | Zelio Control
23717 | RM4JA32M | Main | product or component type | Industrial measurement and control relays
23718 | RM4JA32M | Main | relay type | Current measurement relay
23719 | RM4JA32M | Main | relay name | RM4J
23720 | RM4JA32M | Main | relay monitored parameters | Overcurrent or undercurrent detection
23721 | RM4JA32M | Main | time delay | Adjustable 0.05...30 s
23722 | RM4JA32M | Main | maximum power consumption in VA | 3.4 VA AC
23723 | RM4JA32M | Main | measurement range | 1...5 A current AC 1...5 A current DC 3...15 A current AC 3...15 A current DC 300...1500 mA current AC 300...1500 mA current DC
23724 | RM4JA32M | Main | contacts type and composition | 2 C/O
23725 | RM4JA32M | Complementary | maximum switching voltage | 440 V AC
23726 | RM4JA32M | Complementary | [Us] rated supply voltage | 220...240 V AC 50/60 Hz +/- 5 %
23727 | RM4JA32M | Complementary | operating voltage tolerance | 0.85...1.1 Uc
23728 | RM4JA32M | Complementary | output contacts | 2 C/O
23729 | RM4JA32M | Complementary | maximum measuring cycle | 80 ms
23730 | RM4JA32M | Complementary | internal input resistance | 0.02 Ohm 0.06 Ohm 0.006 Ohm
23731 | RM4JA32M | Complementary | permissible continuous overload | 7 A 20 A 2 A
23732 | RM4JA32M | Complementary | permissible non repetitive overload | 10 A for <= 3 s 100 A 15 A
23733 | RM4JA32M | Complementary | setting accuracy of the switching threshold | +/-5 %
23734 | RM4JA32M | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23735 | RM4JA32M | Complementary | setting accuracy of time delay | 10 P
23736 | RM4JA32M | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23737 | RM4JA32M | Complementary | hysteresis | 5…30 % adjustable of current threshold setting
23738 | RM4JA32M | Complementary | marking | CE : LVD 73/23/EEC CE : EMC 89/336/EEC
23739 | RM4JA32M | Complementary | overvoltage category | III conforming to IEC 60664-1
23740 | RM4JA32M | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
23741 | RM4JA32M | Complementary | supply disconnection value | > 0.1 Uc
23742 | RM4JA32M | Complementary | operating position | Any position without derating
23743 | RM4JA32M | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
23744 | RM4JA32M | Complementary | tightening torque | 0.6…1.1 N.m
23745 | RM4JA32M | Complementary | mechanical durability | 30000000 cycles
23746 | RM4JA32M | Complementary | [Ith] conventional free air thermal current | 8 A
23747 | RM4JA32M | Complementary | [Ie] rated operational current | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C
23748 | RM4JA32M | Complementary | switching capacity in mA | 10 mA at 12 V
23749 | RM4JA32M | Complementary | switching voltage | 250 V AC
23750 | RM4JA32M | Complementary | contacts material | 90/10 silver nickel contacts
23751 | RM4JA32M | Complementary | number of cables | 2
23752 | RM4JA32M | Complementary | width | 45 mm
23753 | RM4JA32M | Complementary | height | 78 mm
23754 | RM4JA32M | Complementary | depth | 80 mm
23755 | RM4JA32M | Complementary | terminals description ISO n°1 | (15-16-18)OC (C-B1-B2-B3)CO (25-26-28)OC (A1-A2)CO
23756 | RM4JA32M | Complementary | output relay state | Tripped if A measured > A set Tripped if V measured > V set
23757 | RM4JA32M | Complementary | 9 mm pitches | 5
23758 | RM4JA32M | Complementary | net weight | 0.204 kg
23759 | RM4JA32M | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
23760 | RM4JA32M | Environment | standards | EN/IEC 60255-6
23761 | RM4JA32M | Environment | product certifications | UL GL CSA
23762 | RM4JA32M | Environment | ambient air temperature for storage | -40…85 °C
23763 | RM4JA32M | Environment | ambient air temperature for operation | -20…65 °C
23764 | RM4JA32M | Environment | environmental characteristic | 3K3
23765 | RM4JA32M | Environment | relative humidity | 15…85 % conforming to IEC 60721-3-3
23766 | RM4JA32M | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
23767 | RM4JA32M | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
23768 | RM4JA32M | Environment | pollution degree | 3 conforming to IEC 60664-1
23769 | RM4JA32M | Environment | dielectric test voltage | 2.5 kV
23770 | RM4JA32M | Environment | non-dissipating shock wave | 4.8 kV
23771 | RM4JA32M | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
23772 | RM4JA32M | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
23773 | RM4JA32M | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
23774 | RM4JA32M | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
23775 | RM4JA32M | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
23776 | RM4JA32M | Contractual warranty | Warranty | 18 months
23777 | RM4JA32MW | Main | range of product | Zelio Control
23778 | RM4JA32MW | Main | product or component type | Industrial measurement and control relays
23779 | RM4JA32MW | Main | relay type | Current measurement relay
23780 | RM4JA32MW | Main | relay name | RM4J
23781 | RM4JA32MW | Main | relay monitored parameters | Overcurrent or undercurrent detection
23782 | RM4JA32MW | Main | time delay | Adjustable 0.05...30 s
23783 | RM4JA32MW | Main | maximum power consumption in VA | 3.3 VA AC
23784 | RM4JA32MW | Main | measurement range | 1...5 A current AC 1...5 A current DC 3...15 A current AC 3...15 A current DC 300...1500 mA current AC 300...1500 mA current DC
23785 | RM4JA32MW | Main | contacts type and composition | 2 C/O
23786 | RM4JA32MW | Complementary | maximum switching voltage | 440 V AC
23787 | RM4JA32MW | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz +/- 5 % 24...240 V DC
23788 | RM4JA32MW | Complementary | operating voltage tolerance | 0.85...1.1 Uc
23789 | RM4JA32MW | Complementary | maximum power consumption in W | 1.2 W DC
23790 | RM4JA32MW | Complementary | output contacts | 2 C/O
23791 | RM4JA32MW | Complementary | maximum measuring cycle | 80 ms
23792 | RM4JA32MW | Complementary | internal input resistance | 0.06 Ohm 0.006 Ohm 0.02 Ohm
23793 | RM4JA32MW | Complementary | permissible continuous overload | 7 A 20 A 2 A
23794 | RM4JA32MW | Complementary | permissible non repetitive overload | 10 A for <= 3 s 100 A 15 A
23795 | RM4JA32MW | Complementary | setting accuracy of the switching threshold | +/-5 %
23796 | RM4JA32MW | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23797 | RM4JA32MW | Complementary | setting accuracy of time delay | 10 P
23798 | RM4JA32MW | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23799 | RM4JA32MW | Complementary | hysteresis | 5…30 % adjustable of current threshold setting
23800 | RM4JA32MW | Complementary | marking | CE : EMC 89/336/EEC CE : LVD 73/23/EEC
23801 | RM4JA32MW | Complementary | overvoltage category | III conforming to IEC 60664-1
23802 | RM4JA32MW | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
23803 | RM4JA32MW | Complementary | supply disconnection value | > 0.1 Uc
23804 | RM4JA32MW | Complementary | operating position | Any position without derating
23805 | RM4JA32MW | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
23806 | RM4JA32MW | Complementary | tightening torque | 0.6…1.1 N.m
23807 | RM4JA32MW | Complementary | mechanical durability | 30000000 cycles
23808 | RM4JA32MW | Complementary | [Ith] conventional free air thermal current | 8 A
23809 | RM4JA32MW | Complementary | [Ie] rated operational current | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C
23810 | RM4JA32MW | Complementary | switching capacity in mA | 10 mA at 12 V
23811 | RM4JA32MW | Complementary | switching voltage | 250 V AC
23812 | RM4JA32MW | Complementary | contacts material | 90/10 silver nickel contacts
23813 | RM4JA32MW | Complementary | number of cables | 2
23814 | RM4JA32MW | Complementary | width | 45 mm
23815 | RM4JA32MW | Complementary | depth | 80 mm
23816 | RM4JA32MW | Complementary | terminals description ISO n°1 | (C-B1-B2-B3)CO (25-26-28)OC (A1-A2)CO (15-16-18)OC
23817 | RM4JA32MW | Complementary | output relay state | Tripped if V measured > V set Tripped if A measured > A set
23818 | RM4JA32MW | Complementary | 9 mm pitches | 5
23819 | RM4JA32MW | Complementary | net weight | 0.204 kg
23820 | RM4JA32MW | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
23821 | RM4JA32MW | Environment | standards | EN/IEC 60255-6
23822 | RM4JA32MW | Environment | product certifications | GL UL CSA
23823 | RM4JA32MW | Environment | ambient air temperature for storage | -40…85 °C
23824 | RM4JA32MW | Environment | ambient air temperature for operation | -20…65 °C
23825 | RM4JA32MW | Environment | environmental characteristic | 3K3
23826 | RM4JA32MW | Environment | relative humidity | 15…85 % conforming to IEC 60721-3-3
23827 | RM4JA32MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
23828 | RM4JA32MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
23829 | RM4JA32MW | Environment | pollution degree | 3 conforming to IEC 60664-1
23830 | RM4JA32MW | Environment | dielectric test voltage | 2.5 kV
23831 | RM4JA32MW | Environment | non-dissipating shock wave | 4.8 kV
23832 | RM4JA32MW | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
23833 | RM4JA32MW | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
23834 | RM4JA32MW | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
23835 | RM4JA32MW | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
23836 | RM4JA32MW | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
23837 | RM4JA32MW | Contractual warranty | Warranty | 18 months
23838 | RM4JA32Q | Main | range of product | Zelio Control
23839 | RM4JA32Q | Main | product or component type | Industrial measurement and control relays
23840 | RM4JA32Q | Main | relay type | Current measurement relay
23841 | RM4JA32Q | Main | relay name | RM4J
23842 | RM4JA32Q | Main | relay monitored parameters | Overcurrent or undercurrent detection
23843 | RM4JA32Q | Main | time delay | Adjustable 0.05...30 s
23844 | RM4JA32Q | Main | maximum power consumption in VA | 3 VA AC
23845 | RM4JA32Q | Main | measurement range | 1...5 A current AC 1...5 A current DC 3...15 A current AC 3...15 A current DC 300...1500 mA current AC 300...1500 mA current DC
23846 | RM4JA32Q | Main | contacts type and composition | 2 C/O
23847 | RM4JA32Q | Complementary | maximum switching voltage | 440 V AC
23848 | RM4JA32Q | Complementary | [Us] rated supply voltage | 380...415 V AC 50/60 Hz +/- 5 %
23849 | RM4JA32Q | Complementary | operating voltage tolerance | 0.85...1.1 Uc
23850 | RM4JA32Q | Complementary | output contacts | 2 C/O
23851 | RM4JA32Q | Complementary | maximum measuring cycle | 80 ms
23852 | RM4JA32Q | Complementary | internal input resistance | 0.02 Ohm 0.006 Ohm 0.06 Ohm
23853 | RM4JA32Q | Complementary | permissible continuous overload | 20 A 2 A 7 A
23854 | RM4JA32Q | Complementary | permissible non repetitive overload | 10 A for <= 3 s 100 A 15 A
23855 | RM4JA32Q | Complementary | setting accuracy of the switching threshold | +/-5 %
23856 | RM4JA32Q | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23857 | RM4JA32Q | Complementary | setting accuracy of time delay | 10 P
23858 | RM4JA32Q | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23859 | RM4JA32Q | Complementary | hysteresis | 5…30 % adjustable of current threshold setting
23860 | RM4JA32Q | Complementary | marking | CE : LVD 73/23/EEC CE : EMC 89/336/EEC
23861 | RM4JA32Q | Complementary | overvoltage category | III conforming to IEC 60664-1
23862 | RM4JA32Q | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
23863 | RM4JA32Q | Complementary | supply disconnection value | > 0.1 Uc
23864 | RM4JA32Q | Complementary | operating position | Any position without derating
23865 | RM4JA32Q | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
23866 | RM4JA32Q | Complementary | tightening torque | 0.6…1.1 N.m
23867 | RM4JA32Q | Complementary | mechanical durability | 30000000 cycles
23868 | RM4JA32Q | Complementary | [Ith] conventional free air thermal current | 8 A
23869 | RM4JA32Q | Complementary | [Ie] rated operational current | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C
23870 | RM4JA32Q | Complementary | switching capacity in mA | 10 mA at 12 V
23871 | RM4JA32Q | Complementary | switching voltage | 250 V AC
23872 | RM4JA32Q | Complementary | contacts material | 90/10 silver nickel contacts
23873 | RM4JA32Q | Complementary | number of cables | 2
23874 | RM4JA32Q | Complementary | width | 45 mm
23875 | RM4JA32Q | Complementary | height | 78 mm
23876 | RM4JA32Q | Complementary | depth | 80 mm
23877 | RM4JA32Q | Complementary | terminals description ISO n°1 | (15-16-18)OC (25-26-28)OC (C-B1-B2-B3)CO (A1-A2)CO
23878 | RM4JA32Q | Complementary | output relay state | Tripped if A measured > A set Tripped if V measured > V set
23879 | RM4JA32Q | Complementary | 9 mm pitches | 5
23880 | RM4JA32Q | Complementary | net weight | 0.204 kg
23881 | RM4JA32Q | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
23882 | RM4JA32Q | Environment | standards | EN/IEC 60255-6
23883 | RM4JA32Q | Environment | product certifications | CSA GL UL
23884 | RM4JA32Q | Environment | ambient air temperature for storage | -40…85 °C
23885 | RM4JA32Q | Environment | ambient air temperature for operation | -20…65 °C
23886 | RM4JA32Q | Environment | environmental characteristic | 3K3
23887 | RM4JA32Q | Environment | relative humidity | 15…85 % conforming to IEC 60721-3-3
23888 | RM4JA32Q | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
23889 | RM4JA32Q | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
23890 | RM4JA32Q | Environment | pollution degree | 3 conforming to IEC 60664-1
23891 | RM4JA32Q | Environment | dielectric test voltage | 2.5 kV
23892 | RM4JA32Q | Environment | non-dissipating shock wave | 4.8 kV
23893 | RM4JA32Q | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
23894 | RM4JA32Q | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
23895 | RM4JA32Q | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
23896 | RM4JA32Q | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
23897 | RM4JA32Q | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
23898 | RM4JA32Q | Contractual warranty | Warranty | 18 months
23899 | RM4UA01B | Main | range of product | Zelio Control
23900 | RM4UA01B | Main | product or component type | Industrial measurement and control relays
23901 | RM4UA01B | Main | relay type | Voltage measurement relay
23902 | RM4UA01B | Main | relay name | RM4U
23903 | RM4UA01B | Main | relay monitored parameters | Overvoltage or undervoltage detection
23904 | RM4UA01B | Main | time delay | Without
23905 | RM4UA01B | Main | power consumption in VA | 2 VA AC
23906 | RM4UA01B | Main | measurement range | 0.05...0.5 V voltage AC 50/60 Hz 0.3...3 V voltage AC 50/60 Hz 0.5...5 V voltage AC 50/60 Hz <= 80 ms cycle 0.05...0.5 V voltage DC 0.3...3 V voltage DC 0.5...5 V voltage DC
23907 | RM4UA01B | Main | contacts type and composition | 1 C/O
23908 | RM4UA01B | Complementary | maximum switching voltage | 440 V AC
23909 | RM4UA01B | Complementary | [Us] rated supply voltage | 24 V AC 50/60 Hz +/- 5 %
23910 | RM4UA01B | Complementary | output contacts | 1 C/O
23911 | RM4UA01B | Complementary | internal input resistance | 43000 Ohm 6600 Ohm 71000 Ohm
23912 | RM4UA01B | Complementary | permissible continuous overload | 80 V 20 V 60 V
23913 | RM4UA01B | Complementary | permissible non repetitive overload | 100 A for <= 1 s 25 A for <= 1 s 80 A for <= 1 s
23914 | RM4UA01B | Complementary | setting accuracy of the switching threshold | +/-5 %
23915 | RM4UA01B | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23916 | RM4UA01B | Complementary | setting accuracy of time delay | 10 P
23917 | RM4UA01B | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
23918 | RM4UA01B | Complementary | quality labels | CE
23919 | RM4UA01B | Complementary | overvoltage category | III conforming to IEC 60664-1
23920 | RM4UA01B | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
23921 | RM4UA01B | Complementary | operating voltage tolerance | 0.85...1.1 Uc
23922 | RM4UA01B | Complementary | supply disconnection value | > 0.1 Uc
23923 | RM4UA01B | Complementary | operating position | Any position without derating
23924 | RM4UA01B | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
23925 | RM4UA01B | Complementary | tightening torque | 0.6…1.1 N.m
23926 | RM4UA01B | Complementary | mechanical durability | 30000000 cycles
23927 | RM4UA01B | Complementary | [Ith] conventional free air thermal current | 8 A
23928 | RM4UA01B | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
23929 | RM4UA01B | Complementary | switching capacity in mA | 10 mA at 12 V
23930 | RM4UA01B | Complementary | switching voltage | 250 V AC
23931 | RM4UA01B | Complementary | contacts material | 90/10 silver nickel contacts
23932 | RM4UA01B | Complementary | number of cables | 2
23933 | RM4UA01B | Complementary | height | 78 mm
23934 | RM4UA01B | Complementary | width | 22.5 mm
23935 | RM4UA01B | Complementary | depth | 80 mm
23936 | RM4UA01B | Complementary | terminals description ISO n°1 | (A1-A2)CO (C-B1-B2-B3)CO (15-16-18)OC
23937 | RM4UA01B | Complementary | output relay state | Tripped if A measured > A set
23938 | RM4UA01B | Complementary | 9 mm pitches | 2.5
23939 | RM4UA01B | Complementary | net weight | 0.168 kg
23940 | RM4UA01B | Complementary | compatibility code | RM4
23941 | RM4UA01B | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
23942 | RM4UA01B | Environment | standards | EN/IEC 60255-6
23943 | RM4UA01B | Environment | product certifications | GL UL CSA
23944 | RM4UA01B | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
23945 | RM4UA01B | Environment | ambient air temperature for storage | -40…85 °C
23946 | RM4UA01B | Environment | ambient air temperature for operation | -20…65 °C
23947 | RM4UA01B | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
23948 | RM4UA01B | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
23949 | RM4UA01B | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
23950 | RM4UA01B | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
23951 | RM4UA01B | Environment | pollution degree | 3 conforming to IEC 60664-1
23952 | RM4UA01B | Environment | dielectric test voltage | 2.5 kV
23953 | RM4UA01B | Environment | non-dissipating shock wave | 4.8 kV
23954 | RM4UA01B | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
23955 | RM4UA01B | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
23956 | RM4UA01B | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
23957 | RM4UA01B | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
23958 | RM4UA01B | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
23959 | RM4UA01B | Contractual warranty | Warranty | 18 months
23960 | RM4UA01F | Main | range of product | Zelio Control
23961 | RM4UA01F | Main | product or component type | Industrial measurement and control relays
23962 | RM4UA01F | Main | relay type | Voltage measurement relay
23963 | RM4UA01F | Main | relay name | RM4U
23964 | RM4UA01F | Main | relay monitored parameters | Overvoltage or undervoltage detection
23965 | RM4UA01F | Main | time delay | Without
23966 | RM4UA01F | Main | power consumption in VA | 1.9…3.3 VA AC
23967 | RM4UA01F | Main | measurement range | 0.05...0.5 V voltage AC 50/60 Hz 0.3...3 V voltage AC 50/60 Hz 0.5...5 V voltage AC 50/60 Hz <= 80 ms cycle 0.05...0.5 V voltage DC 0.3...3 V voltage DC 0.5...5 V voltage DC
23968 | RM4UA01F | Main | contacts type and composition | 1 C/O
23969 | RM4UA01F | Complementary | maximum switching voltage | 440 V AC
23970 | RM4UA01F | Complementary | [Us] rated supply voltage | 110...130 V AC 50/60 Hz +/- 5 %
23971 | RM4UA01F | Complementary | output contacts | 1 C/O
23972 | RM4UA01F | Complementary | internal input resistance | 71000 Ohm 6600 Ohm 43000 Ohm
23973 | RM4UA01F | Complementary | permissible continuous overload | 80 V 20 V 60 V
23974 | RM4UA01F | Complementary | permissible non repetitive overload | 100 A for <= 1 s 25 A for <= 1 s 80 A for <= 1 s
23975 | RM4UA01F | Complementary | setting accuracy of the switching threshold | +/-5 %
23976 | RM4UA01F | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
23977 | RM4UA01F | Complementary | setting accuracy of time delay | 10 P
23978 | RM4UA01F | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
23979 | RM4UA01F | Complementary | quality labels | CE
23980 | RM4UA01F | Complementary | overvoltage category | III conforming to IEC 60664-1
23981 | RM4UA01F | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
23982 | RM4UA01F | Complementary | operating voltage tolerance | 0.85...1.1 Uc
23983 | RM4UA01F | Complementary | supply disconnection value | > 0.1 Uc
23984 | RM4UA01F | Complementary | operating position | Any position without derating
23985 | RM4UA01F | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
23986 | RM4UA01F | Complementary | tightening torque | 0.6…1.1 N.m
23987 | RM4UA01F | Complementary | mechanical durability | 30000000 cycles
23988 | RM4UA01F | Complementary | [Ith] conventional free air thermal current | 8 A
23989 | RM4UA01F | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
23990 | RM4UA01F | Complementary | switching capacity in mA | 10 mA at 12 V
23991 | RM4UA01F | Complementary | switching voltage | 250 V AC
23992 | RM4UA01F | Complementary | contacts material | 90/10 silver nickel contacts
23993 | RM4UA01F | Complementary | number of cables | 2
23994 | RM4UA01F | Complementary | height | 78 mm
23995 | RM4UA01F | Complementary | width | 22.5 mm
23996 | RM4UA01F | Complementary | depth | 80 mm
23997 | RM4UA01F | Complementary | terminals description ISO n°1 | (C-B1-B2-B3)CO (15-16-18)OC (A1-A2)CO
23998 | RM4UA01F | Complementary | output relay state | Tripped if A measured > A set
23999 | RM4UA01F | Complementary | 9 mm pitches | 2.5
24000 | RM4UA01F | Complementary | net weight | 0.168 kg
24001 | RM4UA01F | Complementary | compatibility code | RM4
24002 | RM4UA01F | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24003 | RM4UA01F | Environment | standards | EN/IEC 60255-6
24004 | RM4UA01F | Environment | product certifications | GL CSA UL
24005 | RM4UA01F | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
24006 | RM4UA01F | Environment | ambient air temperature for storage | -40…85 °C
24007 | RM4UA01F | Environment | ambient air temperature for operation | -20…65 °C
24008 | RM4UA01F | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24009 | RM4UA01F | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24010 | RM4UA01F | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24011 | RM4UA01F | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24012 | RM4UA01F | Environment | pollution degree | 3 conforming to IEC 60664-1
24013 | RM4UA01F | Environment | dielectric test voltage | 2.5 kV
24014 | RM4UA01F | Environment | non-dissipating shock wave | 4.8 kV
24015 | RM4UA01F | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24016 | RM4UA01F | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24017 | RM4UA01F | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24018 | RM4UA01F | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24019 | RM4UA01F | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
24020 | RM4UA01F | Contractual warranty | Warranty | 18 months
24021 | RM4UA01M | Main | range of product | Zelio Control
24022 | RM4UA01M | Main | product or component type | Industrial measurement and control relays
24023 | RM4UA01M | Main | relay type | Voltage measurement relay
24024 | RM4UA01M | Main | relay name | RM4U
24025 | RM4UA01M | Main | relay monitored parameters | Overvoltage or undervoltage detection
24026 | RM4UA01M | Main | time delay | Without
24027 | RM4UA01M | Main | power consumption in VA | 2.7…3.5 VA AC
24028 | RM4UA01M | Main | measurement range | 0.05...0.5 V voltage AC 50/60 Hz 0.3...3 V voltage AC 50/60 Hz 0.5...5 V voltage AC 50/60 Hz <= 80 ms cycle 0.05...0.5 V voltage DC 0.3...3 V voltage DC 0.5...5 V voltage DC
24029 | RM4UA01M | Main | contacts type and composition | 1 C/O
24030 | RM4UA01M | Complementary | maximum switching voltage | 440 V AC
24031 | RM4UA01M | Complementary | [Us] rated supply voltage | 220...240 V AC 50/60 Hz +/- 5 %
24032 | RM4UA01M | Complementary | output contacts | 1 C/O
24033 | RM4UA01M | Complementary | internal input resistance | 6600 Ohm 43000 Ohm 71000 Ohm
24034 | RM4UA01M | Complementary | permissible continuous overload | 20 V 80 V 60 V
24035 | RM4UA01M | Complementary | permissible non repetitive overload | 100 A for <= 1 s 25 A for <= 1 s 80 A for <= 1 s
24036 | RM4UA01M | Complementary | setting accuracy of the switching threshold | +/-5 %
24037 | RM4UA01M | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24038 | RM4UA01M | Complementary | setting accuracy of time delay | 10 P
24039 | RM4UA01M | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
24040 | RM4UA01M | Complementary | quality labels | CE
24041 | RM4UA01M | Complementary | overvoltage category | III conforming to IEC 60664-1
24042 | RM4UA01M | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
24043 | RM4UA01M | Complementary | operating voltage tolerance | 0.85...1.1 Uc
24044 | RM4UA01M | Complementary | supply disconnection value | > 0.1 Uc
24045 | RM4UA01M | Complementary | operating position | Any position without derating
24046 | RM4UA01M | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
24047 | RM4UA01M | Complementary | tightening torque | 0.6…1.1 N.m
24048 | RM4UA01M | Complementary | mechanical durability | 30000000 cycles
24049 | RM4UA01M | Complementary | [Ith] conventional free air thermal current | 8 A
24050 | RM4UA01M | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
24051 | RM4UA01M | Complementary | switching capacity in mA | 10 mA at 12 V
24052 | RM4UA01M | Complementary | switching voltage | 250 V AC
24053 | RM4UA01M | Complementary | contacts material | 90/10 silver nickel contacts
24054 | RM4UA01M | Complementary | number of cables | 2
24055 | RM4UA01M | Complementary | height | 78 mm
24056 | RM4UA01M | Complementary | width | 22.5 mm
24057 | RM4UA01M | Complementary | depth | 80 mm
24058 | RM4UA01M | Complementary | terminals description ISO n°1 | (15-16-18)OC (A1-A2)CO (C-B1-B2-B3)CO
24059 | RM4UA01M | Complementary | output relay state | Tripped if A measured > A set
24060 | RM4UA01M | Complementary | 9 mm pitches | 2.5
24061 | RM4UA01M | Complementary | net weight | 0.168 kg
24062 | RM4UA01M | Complementary | compatibility code | RM4
24063 | RM4UA01M | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24064 | RM4UA01M | Environment | standards | EN/IEC 60255-6
24065 | RM4UA01M | Environment | product certifications | CSA UL GL
24066 | RM4UA01M | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
24067 | RM4UA01M | Environment | ambient air temperature for storage | -40…85 °C
24068 | RM4UA01M | Environment | ambient air temperature for operation | -20…65 °C
24069 | RM4UA01M | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24070 | RM4UA01M | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24071 | RM4UA01M | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24072 | RM4UA01M | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24073 | RM4UA01M | Environment | pollution degree | 3 conforming to IEC 60664-1
24074 | RM4UA01M | Environment | dielectric test voltage | 2.5 kV
24075 | RM4UA01M | Environment | non-dissipating shock wave | 4.8 kV
24076 | RM4UA01M | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24077 | RM4UA01M | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24078 | RM4UA01M | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24079 | RM4UA01M | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24080 | RM4UA01M | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
24081 | RM4UA01M | Contractual warranty | Warranty | 18 months
24082 | RM4UA02B | Main | range of product | Zelio Control
24083 | RM4UA02B | Main | product or component type | Industrial measurement and control relays
24084 | RM4UA02B | Main | relay type | Voltage measurement relay
24085 | RM4UA02B | Main | relay name | RM4U
24086 | RM4UA02B | Main | relay monitored parameters | Overvoltage or undervoltage detection
24087 | RM4UA02B | Main | time delay | Without
24088 | RM4UA02B | Main | power consumption in VA | 2 VA AC
24089 | RM4UA02B | Main | measurement range | 1...10 V voltage AC 50/60 Hz 10...100 V voltage AC 50/60 Hz 5...50 V voltage AC 50/60 Hz <= 80 ms cycle 1...10 V voltage DC 10...100 V voltage DC 5...50 V voltage DC
24090 | RM4UA02B | Main | contacts type and composition | 1 C/O
24091 | RM4UA02B | Complementary | maximum switching voltage | 440 V AC
24092 | RM4UA02B | Complementary | [Us] rated supply voltage | 24 V AC 50/60 Hz +/- 5 %
24093 | RM4UA02B | Complementary | output contacts | 1 C/O
24094 | RM4UA02B | Complementary | internal input resistance | 23000 Ohm 112000 Ohm 225000 Ohm
24095 | RM4UA02B | Complementary | permissible continuous overload | 150 V 90 V 300 V
24096 | RM4UA02B | Complementary | permissible non repetitive overload | 100 A for <= 1 s 200 A for <= 1 s 400 A for <= 1 s
24097 | RM4UA02B | Complementary | setting accuracy of the switching threshold | +/-5 %
24098 | RM4UA02B | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24099 | RM4UA02B | Complementary | setting accuracy of time delay | 10 P
24100 | RM4UA02B | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
24101 | RM4UA02B | Complementary | quality labels | CE
24102 | RM4UA02B | Complementary | overvoltage category | III conforming to IEC 60664-1
24103 | RM4UA02B | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
24104 | RM4UA02B | Complementary | operating voltage tolerance | 0.85...1.1 Uc
24105 | RM4UA02B | Complementary | supply disconnection value | > 0.1 Uc
24106 | RM4UA02B | Complementary | operating position | Any position without derating
24107 | RM4UA02B | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
24108 | RM4UA02B | Complementary | tightening torque | 0.6…1.1 N.m
24109 | RM4UA02B | Complementary | mechanical durability | 30000000 cycles
24110 | RM4UA02B | Complementary | [Ith] conventional free air thermal current | 8 A
24111 | RM4UA02B | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
24112 | RM4UA02B | Complementary | switching capacity in mA | 10 mA at 12 V
24113 | RM4UA02B | Complementary | switching voltage | 250 V AC
24114 | RM4UA02B | Complementary | contacts material | 90/10 silver nickel contacts
24115 | RM4UA02B | Complementary | number of cables | 2
24116 | RM4UA02B | Complementary | height | 78 mm
24117 | RM4UA02B | Complementary | width | 22.5 mm
24118 | RM4UA02B | Complementary | depth | 80 mm
24119 | RM4UA02B | Complementary | terminals description ISO n°1 | (15-16-18)OC (A1-A2)CO (C-B1-B2-B3)CO
24120 | RM4UA02B | Complementary | output relay state | Tripped if A measured > A set
24121 | RM4UA02B | Complementary | 9 mm pitches | 2.5
24122 | RM4UA02B | Complementary | net weight | 0.168 kg
24123 | RM4UA02B | Complementary | compatibility code | RM4
24124 | RM4UA02B | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24125 | RM4UA02B | Environment | standards | EN/IEC 60255-6
24126 | RM4UA02B | Environment | product certifications | GL UL CSA
24127 | RM4UA02B | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
24128 | RM4UA02B | Environment | ambient air temperature for storage | -40…85 °C
24129 | RM4UA02B | Environment | ambient air temperature for operation | -20…65 °C
24130 | RM4UA02B | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24131 | RM4UA02B | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24132 | RM4UA02B | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24133 | RM4UA02B | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24134 | RM4UA02B | Environment | pollution degree | 3 conforming to IEC 60664-1
24135 | RM4UA02B | Environment | dielectric test voltage | 2.5 kV
24136 | RM4UA02B | Environment | non-dissipating shock wave | 4.8 kV
24137 | RM4UA02B | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24138 | RM4UA02B | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24139 | RM4UA02B | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24140 | RM4UA02B | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24141 | RM4UA02B | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
24142 | RM4UA02B | Contractual warranty | Warranty | 18 months
24143 | RM4UA02F | Main | range of product | Zelio Control
24144 | RM4UA02F | Main | product or component type | Industrial measurement and control relays
24145 | RM4UA02F | Main | relay type | Voltage measurement relay
24146 | RM4UA02F | Main | relay name | RM4U
24147 | RM4UA02F | Main | relay monitored parameters | Overvoltage or undervoltage detection
24148 | RM4UA02F | Main | time delay | Without
24149 | RM4UA02F | Main | power consumption in VA | 1.9…3.3 VA AC
24150 | RM4UA02F | Main | measurement range | 1...10 V voltage AC 50/60 Hz 10...100 V voltage AC 50/60 Hz 5...50 V voltage AC 50/60 Hz <= 80 ms cycle 1...10 V voltage DC 10...100 V voltage DC 5...50 V voltage DC
24151 | RM4UA02F | Main | contacts type and composition | 1 C/O
24152 | RM4UA02F | Complementary | maximum switching voltage | 440 V AC
24153 | RM4UA02F | Complementary | [Us] rated supply voltage | 110...130 V AC 50/60 Hz +/- 5 %
24154 | RM4UA02F | Complementary | output contacts | 1 C/O
24155 | RM4UA02F | Complementary | internal input resistance | 23000 Ohm 112000 Ohm 225000 Ohm
24156 | RM4UA02F | Complementary | permissible continuous overload | 300 V 90 V 150 V
24157 | RM4UA02F | Complementary | permissible non repetitive overload | 100 A for <= 1 s 200 A for <= 1 s 400 A for <= 1 s
24158 | RM4UA02F | Complementary | setting accuracy of the switching threshold | +/-5 %
24159 | RM4UA02F | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24160 | RM4UA02F | Complementary | setting accuracy of time delay | 10 P
24161 | RM4UA02F | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
24162 | RM4UA02F | Complementary | quality labels | CE
24163 | RM4UA02F | Complementary | overvoltage category | III conforming to IEC 60664-1
24164 | RM4UA02F | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
24165 | RM4UA02F | Complementary | operating voltage tolerance | 0.85...1.1 Uc
24166 | RM4UA02F | Complementary | supply disconnection value | > 0.1 Uc
24167 | RM4UA02F | Complementary | operating position | Any position without derating
24168 | RM4UA02F | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
24169 | RM4UA02F | Complementary | tightening torque | 0.6…1.1 N.m
24170 | RM4UA02F | Complementary | mechanical durability | 30000000 cycles
24171 | RM4UA02F | Complementary | [Ith] conventional free air thermal current | 8 A
24172 | RM4UA02F | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
24173 | RM4UA02F | Complementary | switching capacity in mA | 10 mA at 12 V
24174 | RM4UA02F | Complementary | switching voltage | 250 V AC
24175 | RM4UA02F | Complementary | contacts material | 90/10 silver nickel contacts
24176 | RM4UA02F | Complementary | number of cables | 2
24177 | RM4UA02F | Complementary | height | 78 mm
24178 | RM4UA02F | Complementary | width | 22.5 mm
24179 | RM4UA02F | Complementary | depth | 80 mm
24180 | RM4UA02F | Complementary | terminals description ISO n°1 | (C-B1-B2-B3)CO (15-16-18)OC (A1-A2)CO
24181 | RM4UA02F | Complementary | output relay state | Tripped if A measured > A set
24182 | RM4UA02F | Complementary | 9 mm pitches | 2.5
24183 | RM4UA02F | Complementary | net weight | 0.168 kg
24184 | RM4UA02F | Complementary | compatibility code | RM4
24185 | RM4UA02F | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24186 | RM4UA02F | Environment | standards | EN/IEC 60255-6
24187 | RM4UA02F | Environment | product certifications | CSA GL UL
24188 | RM4UA02F | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
24189 | RM4UA02F | Environment | ambient air temperature for storage | -40…85 °C
24190 | RM4UA02F | Environment | ambient air temperature for operation | -20…65 °C
24191 | RM4UA02F | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24192 | RM4UA02F | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24193 | RM4UA02F | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24194 | RM4UA02F | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24195 | RM4UA02F | Environment | pollution degree | 3 conforming to IEC 60664-1
24196 | RM4UA02F | Environment | dielectric test voltage | 2.5 kV
24197 | RM4UA02F | Environment | non-dissipating shock wave | 4.8 kV
24198 | RM4UA02F | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24199 | RM4UA02F | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24200 | RM4UA02F | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24201 | RM4UA02F | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24202 | RM4UA02F | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
24203 | RM4UA02F | Contractual warranty | Warranty | 18 months
24204 | RM4UA02M | Main | range of product | Zelio Control
24205 | RM4UA02M | Main | product or component type | Industrial measurement and control relays
24206 | RM4UA02M | Main | relay type | Voltage measurement relay
24207 | RM4UA02M | Main | relay name | RM4U
24208 | RM4UA02M | Main | relay monitored parameters | Overvoltage or undervoltage detection
24209 | RM4UA02M | Main | time delay | Without
24210 | RM4UA02M | Main | power consumption in VA | 2.7…3.5 VA AC
24211 | RM4UA02M | Main | measurement range | 1...10 V voltage AC 50/60 Hz 10...100 V voltage AC 50/60 Hz 5...50 V voltage AC 50/60 Hz <= 80 ms cycle 1...10 V voltage DC 10...100 V voltage DC 5...50 V voltage DC
24212 | RM4UA02M | Main | contacts type and composition | 1 C/O
24213 | RM4UA02M | Complementary | maximum switching voltage | 440 V AC
24214 | RM4UA02M | Complementary | [Us] rated supply voltage | 220...240 V AC 50/60 Hz +/- 5 %
24215 | RM4UA02M | Complementary | output contacts | 1 C/O
24216 | RM4UA02M | Complementary | internal input resistance | 112000 Ohm 23000 Ohm 225000 Ohm
24217 | RM4UA02M | Complementary | permissible continuous overload | 90 V 150 V 300 V
24218 | RM4UA02M | Complementary | permissible non repetitive overload | 100 A for <= 1 s 200 A for <= 1 s 400 A for <= 1 s
24219 | RM4UA02M | Complementary | setting accuracy of the switching threshold | +/-5 %
24220 | RM4UA02M | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24221 | RM4UA02M | Complementary | setting accuracy of time delay | 10 P
24222 | RM4UA02M | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
24223 | RM4UA02M | Complementary | quality labels | CE
24224 | RM4UA02M | Complementary | overvoltage category | III conforming to IEC 60664-1
24225 | RM4UA02M | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
24226 | RM4UA02M | Complementary | operating voltage tolerance | 0.85...1.1 Uc
24227 | RM4UA02M | Complementary | supply disconnection value | > 0.1 Uc
24228 | RM4UA02M | Complementary | operating position | Any position without derating
24229 | RM4UA02M | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
24230 | RM4UA02M | Complementary | tightening torque | 0.6…1.1 N.m
24231 | RM4UA02M | Complementary | mechanical durability | 30000000 cycles
24232 | RM4UA02M | Complementary | [Ith] conventional free air thermal current | 8 A
24233 | RM4UA02M | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
24234 | RM4UA02M | Complementary | switching capacity in mA | 10 mA at 12 V
24235 | RM4UA02M | Complementary | switching voltage | 250 V AC
24236 | RM4UA02M | Complementary | contacts material | 90/10 silver nickel contacts
24237 | RM4UA02M | Complementary | number of cables | 2
24238 | RM4UA02M | Complementary | height | 78 mm
24239 | RM4UA02M | Complementary | width | 22.5 mm
24240 | RM4UA02M | Complementary | depth | 80 mm
24241 | RM4UA02M | Complementary | terminals description ISO n°1 | (C-B1-B2-B3)CO (15-16-18)OC (A1-A2)CO
24242 | RM4UA02M | Complementary | output relay state | Tripped if A measured > A set
24243 | RM4UA02M | Complementary | 9 mm pitches | 2.5
24244 | RM4UA02M | Complementary | net weight | 0.168 kg
24245 | RM4UA02M | Complementary | compatibility code | RM4
24246 | RM4UA02M | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24247 | RM4UA02M | Environment | standards | EN/IEC 60255-6
24248 | RM4UA02M | Environment | product certifications | CSA GL UL
24249 | RM4UA02M | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
24250 | RM4UA02M | Environment | ambient air temperature for storage | -40…85 °C
24251 | RM4UA02M | Environment | ambient air temperature for operation | -20…65 °C
24252 | RM4UA02M | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24253 | RM4UA02M | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24254 | RM4UA02M | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24255 | RM4UA02M | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24256 | RM4UA02M | Environment | pollution degree | 3 conforming to IEC 60664-1
24257 | RM4UA02M | Environment | dielectric test voltage | 2.5 kV
24258 | RM4UA02M | Environment | non-dissipating shock wave | 4.8 kV
24259 | RM4UA02M | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24260 | RM4UA02M | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24261 | RM4UA02M | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24262 | RM4UA02M | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24263 | RM4UA02M | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
24264 | RM4UA02M | Contractual warranty | Warranty | 18 months
24265 | RM4UA03B | Main | range of product | Zelio Control
24266 | RM4UA03B | Main | product or component type | Industrial measurement and control relays
24267 | RM4UA03B | Main | relay type | Voltage measurement relay
24268 | RM4UA03B | Main | relay name | RM4U
24269 | RM4UA03B | Main | relay monitored parameters | Overvoltage or undervoltage detection
24270 | RM4UA03B | Main | time delay | Without
24271 | RM4UA03B | Main | power consumption in VA | 2 VA AC
24272 | RM4UA03B | Main | measurement range | 30...300 V voltage AC 50/60 Hz 50...500 V voltage AC 50/60 Hz <= 80 ms cycle 30...300 V voltage DC 50...500 V voltage DC
24273 | RM4UA03B | Main | contacts type and composition | 1 C/O
24274 | RM4UA03B | Complementary | maximum switching voltage | 440 V AC
24275 | RM4UA03B | Complementary | [Us] rated supply voltage | 24 V AC 50/60 Hz +/- 5 %
24276 | RM4UA03B | Complementary | output contacts | 1 C/O
24277 | RM4UA03B | Complementary | internal input resistance | 1111000 Ohm 11110000 Ohm 668000 Ohm
24278 | RM4UA03B | Complementary | permissible continuous overload | 550 V 400 V
24279 | RM4UA03B | Complementary | permissible non repetitive overload | 500 A for <= 1 s 550 A for <= 1 s
24280 | RM4UA03B | Complementary | setting accuracy of the switching threshold | +/-5 %
24281 | RM4UA03B | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24282 | RM4UA03B | Complementary | setting accuracy of time delay | 10 P
24283 | RM4UA03B | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
24284 | RM4UA03B | Complementary | quality labels | CE
24285 | RM4UA03B | Complementary | overvoltage category | III conforming to IEC 60664-1
24286 | RM4UA03B | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
24287 | RM4UA03B | Complementary | operating voltage tolerance | 0.85...1.1 Uc
24288 | RM4UA03B | Complementary | supply disconnection value | > 0.1 Uc
24289 | RM4UA03B | Complementary | operating position | Any position without derating
24290 | RM4UA03B | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
24291 | RM4UA03B | Complementary | tightening torque | 0.6…1.1 N.m
24292 | RM4UA03B | Complementary | mechanical durability | 30000000 cycles
24293 | RM4UA03B | Complementary | [Ith] conventional free air thermal current | 8 A
24294 | RM4UA03B | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
24295 | RM4UA03B | Complementary | switching capacity in mA | 10 mA at 12 V
24296 | RM4UA03B | Complementary | switching voltage | 250 V AC
24297 | RM4UA03B | Complementary | contacts material | 90/10 silver nickel contacts
24298 | RM4UA03B | Complementary | number of cables | 2
24299 | RM4UA03B | Complementary | height | 78 mm
24300 | RM4UA03B | Complementary | width | 22.5 mm
24301 | RM4UA03B | Complementary | depth | 80 mm
24302 | RM4UA03B | Complementary | terminals description ISO n°1 | (A1-A2)CO (C-B2-B3)CO (15-16-18)OC
24303 | RM4UA03B | Complementary | output relay state | Tripped if A measured > A set
24304 | RM4UA03B | Complementary | 9 mm pitches | 2.5
24305 | RM4UA03B | Complementary | net weight | 0.168 kg
24306 | RM4UA03B | Complementary | compatibility code | RM4
24307 | RM4UA03B | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24308 | RM4UA03B | Environment | standards | EN/IEC 60255-6
24309 | RM4UA03B | Environment | product certifications | UL GL CSA
24310 | RM4UA03B | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
24311 | RM4UA03B | Environment | ambient air temperature for storage | -40…85 °C
24312 | RM4UA03B | Environment | ambient air temperature for operation | -20…65 °C
24313 | RM4UA03B | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24314 | RM4UA03B | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24315 | RM4UA03B | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24316 | RM4UA03B | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24317 | RM4UA03B | Environment | pollution degree | 3 conforming to IEC 60664-1
24318 | RM4UA03B | Environment | dielectric test voltage | 2.5 kV
24319 | RM4UA03B | Environment | non-dissipating shock wave | 4.8 kV
24320 | RM4UA03B | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24321 | RM4UA03B | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24322 | RM4UA03B | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24323 | RM4UA03B | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24324 | RM4UA03B | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
24325 | RM4UA03B | Contractual warranty | Warranty | 18 months
24326 | RM4UA03F | Main | range of product | Zelio Control
24327 | RM4UA03F | Main | product or component type | Industrial measurement and control relays
24328 | RM4UA03F | Main | relay type | Voltage measurement relay
24329 | RM4UA03F | Main | relay name | RM4U
24330 | RM4UA03F | Main | relay monitored parameters | Overvoltage or undervoltage detection
24331 | RM4UA03F | Main | time delay | Without
24332 | RM4UA03F | Main | power consumption in VA | 1.9…3.3 VA AC
24333 | RM4UA03F | Main | measurement range | 30...300 V voltage AC 50/60 Hz 50...500 V voltage AC 50/60 Hz <= 80 ms cycle 30...300 V voltage DC 50...500 V voltage DC
24334 | RM4UA03F | Main | contacts type and composition | 1 C/O
24335 | RM4UA03F | Complementary | maximum switching voltage | 440 V AC
24336 | RM4UA03F | Complementary | [Us] rated supply voltage | 110...130 V AC 50/60 Hz +/- 5 %
24337 | RM4UA03F | Complementary | output contacts | 1 C/O
24338 | RM4UA03F | Complementary | internal input resistance | 668000 Ohm 1111000 Ohm 11110000 Ohm
24339 | RM4UA03F | Complementary | permissible continuous overload | 550 V 400 V
24340 | RM4UA03F | Complementary | permissible non repetitive overload | 500 A for <= 1 s 550 A for <= 1 s
24341 | RM4UA03F | Complementary | setting accuracy of the switching threshold | +/-5 %
24342 | RM4UA03F | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24343 | RM4UA03F | Complementary | setting accuracy of time delay | 10 P
24344 | RM4UA03F | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
24345 | RM4UA03F | Complementary | quality labels | CE
24346 | RM4UA03F | Complementary | overvoltage category | III conforming to IEC 60664-1
24347 | RM4UA03F | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
24348 | RM4UA03F | Complementary | operating voltage tolerance | 0.85...1.1 Uc
24349 | RM4UA03F | Complementary | supply disconnection value | > 0.1 Uc
24350 | RM4UA03F | Complementary | operating position | Any position without derating
24351 | RM4UA03F | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
24352 | RM4UA03F | Complementary | tightening torque | 0.6…1.1 N.m
24353 | RM4UA03F | Complementary | mechanical durability | 30000000 cycles
24354 | RM4UA03F | Complementary | [Ith] conventional free air thermal current | 8 A
24355 | RM4UA03F | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
24356 | RM4UA03F | Complementary | switching capacity in mA | 10 mA at 12 V
24357 | RM4UA03F | Complementary | switching voltage | 250 V AC
24358 | RM4UA03F | Complementary | contacts material | 90/10 silver nickel contacts
24359 | RM4UA03F | Complementary | number of cables | 2
24360 | RM4UA03F | Complementary | height | 78 mm
24361 | RM4UA03F | Complementary | width | 22.5 mm
24362 | RM4UA03F | Complementary | depth | 80 mm
24363 | RM4UA03F | Complementary | terminals description ISO n°1 | (A1-A2)CO (C-B2-B3)CO (15-16-18)OC
24364 | RM4UA03F | Complementary | output relay state | Tripped if A measured > A set
24365 | RM4UA03F | Complementary | 9 mm pitches | 2.5
24366 | RM4UA03F | Complementary | net weight | 0.168 kg
24367 | RM4UA03F | Complementary | compatibility code | RM4
24368 | RM4UA03F | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24369 | RM4UA03F | Environment | standards | EN/IEC 60255-6
24370 | RM4UA03F | Environment | product certifications | CSA UL GL
24371 | RM4UA03F | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
24372 | RM4UA03F | Environment | ambient air temperature for storage | -40…85 °C
24373 | RM4UA03F | Environment | ambient air temperature for operation | -20…65 °C
24374 | RM4UA03F | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24375 | RM4UA03F | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24376 | RM4UA03F | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24377 | RM4UA03F | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24378 | RM4UA03F | Environment | pollution degree | 3 conforming to IEC 60664-1
24379 | RM4UA03F | Environment | dielectric test voltage | 2.5 kV
24380 | RM4UA03F | Environment | non-dissipating shock wave | 4.8 kV
24381 | RM4UA03F | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24382 | RM4UA03F | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24383 | RM4UA03F | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24384 | RM4UA03F | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24385 | RM4UA03F | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
24386 | RM4UA03F | Contractual warranty | Warranty | 18 months
24387 | RM4UA03M | Main | range of product | Zelio Control
24388 | RM4UA03M | Main | product or component type | Industrial measurement and control relays
24389 | RM4UA03M | Main | relay type | Voltage measurement relay
24390 | RM4UA03M | Main | relay name | RM4U
24391 | RM4UA03M | Main | relay monitored parameters | Overvoltage or undervoltage detection
24392 | RM4UA03M | Main | time delay | Without
24393 | RM4UA03M | Main | power consumption in VA | 2.7…3.5 VA AC
24394 | RM4UA03M | Main | measurement range | 30...300 V voltage AC 50/60 Hz 50...500 V voltage AC 50/60 Hz <= 80 ms cycle 30...300 V voltage DC 50...500 V voltage DC
24395 | RM4UA03M | Main | contacts type and composition | 1 C/O
24396 | RM4UA03M | Complementary | maximum switching voltage | 440 V AC
24397 | RM4UA03M | Complementary | [Us] rated supply voltage | 220...240 V AC 50/60 Hz +/- 5 %
24398 | RM4UA03M | Complementary | output contacts | 1 C/O
24399 | RM4UA03M | Complementary | internal input resistance | 11110000 Ohm 668000 Ohm 1111000 Ohm
24400 | RM4UA03M | Complementary | permissible continuous overload | 550 V 400 V
24401 | RM4UA03M | Complementary | permissible non repetitive overload | 500 A for <= 1 s 550 A for <= 1 s
24402 | RM4UA03M | Complementary | setting accuracy of the switching threshold | +/-5 %
24403 | RM4UA03M | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24404 | RM4UA03M | Complementary | setting accuracy of time delay | 10 P
24405 | RM4UA03M | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
24406 | RM4UA03M | Complementary | quality labels | CE
24407 | RM4UA03M | Complementary | overvoltage category | III conforming to IEC 60664-1
24408 | RM4UA03M | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
24409 | RM4UA03M | Complementary | operating voltage tolerance | 0.85...1.1 Uc
24410 | RM4UA03M | Complementary | supply disconnection value | > 0.1 Uc
24411 | RM4UA03M | Complementary | operating position | Any position without derating
24412 | RM4UA03M | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
24413 | RM4UA03M | Complementary | tightening torque | 0.6…1.1 N.m
24414 | RM4UA03M | Complementary | mechanical durability | 30000000 cycles
24415 | RM4UA03M | Complementary | [Ith] conventional free air thermal current | 8 A
24416 | RM4UA03M | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
24417 | RM4UA03M | Complementary | switching capacity in mA | 10 mA at 12 V
24418 | RM4UA03M | Complementary | switching voltage | 250 V AC
24419 | RM4UA03M | Complementary | contacts material | 90/10 silver nickel contacts
24420 | RM4UA03M | Complementary | number of cables | 2
24421 | RM4UA03M | Complementary | height | 78 mm
24422 | RM4UA03M | Complementary | width | 22.5 mm
24423 | RM4UA03M | Complementary | depth | 80 mm
24424 | RM4UA03M | Complementary | terminals description ISO n°1 | (A1-A2)CO (15-16-18)OC (C-B2-B3)CO
24425 | RM4UA03M | Complementary | output relay state | Tripped if A measured > A set
24426 | RM4UA03M | Complementary | 9 mm pitches | 2.5
24427 | RM4UA03M | Complementary | net weight | 0.168 kg
24428 | RM4UA03M | Complementary | compatibility code | RM4
24429 | RM4UA03M | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24430 | RM4UA03M | Environment | standards | EN/IEC 60255-6
24431 | RM4UA03M | Environment | product certifications | UL GL CSA
24432 | RM4UA03M | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
24433 | RM4UA03M | Environment | ambient air temperature for storage | -40…85 °C
24434 | RM4UA03M | Environment | ambient air temperature for operation | -20…65 °C
24435 | RM4UA03M | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24436 | RM4UA03M | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24437 | RM4UA03M | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24438 | RM4UA03M | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24439 | RM4UA03M | Environment | pollution degree | 3 conforming to IEC 60664-1
24440 | RM4UA03M | Environment | dielectric test voltage | 2.5 kV
24441 | RM4UA03M | Environment | non-dissipating shock wave | 4.8 kV
24442 | RM4UA03M | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24443 | RM4UA03M | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24444 | RM4UA03M | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24445 | RM4UA03M | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24446 | RM4UA03M | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
24447 | RM4UA03M | Contractual warranty | Warranty | 18 months
24448 | RM4UA31F | Main | range of product | Zelio Control
24449 | RM4UA31F | Main | product or component type | Industrial measurement and control relays
24450 | RM4UA31F | Main | relay type | Voltage measurement relay
24451 | RM4UA31F | Main | relay name | RM4U
24452 | RM4UA31F | Main | relay monitored parameters | Overvoltage or undervoltage detection
24453 | RM4UA31F | Main | time delay | Adjustable 0.05...30 s
24454 | RM4UA31F | Main | power consumption in VA | 1.9…3.3 VA AC
24455 | RM4UA31F | Main | measurement range | 0.05...0.5 V voltage AC 50/60 Hz 0.3...3 V voltage AC 50/60 Hz 0.5...5 V voltage AC 50/60 Hz 0.05...0.5 V voltage DC 0.3...3 V voltage DC 0.5...5 V voltage DC
24456 | RM4UA31F | Main | contacts type and composition | 2 C/O
24457 | RM4UA31F | Complementary | maximum switching voltage | 440 V AC
24458 | RM4UA31F | Complementary | [Us] rated supply voltage | 110...130 V AC 50/60 Hz +/- 5 %
24459 | RM4UA31F | Complementary | output contacts | 2 C/O
24460 | RM4UA31F | Complementary | internal input resistance | 43000 Ohm 6600 Ohm 71000 Ohm
24461 | RM4UA31F | Complementary | permissible continuous overload | 80 V 60 V 20 V
24462 | RM4UA31F | Complementary | permissible non repetitive overload | 100 A for <= 1 s 25 A for <= 1 s 80 A for <= 1 s
24463 | RM4UA31F | Complementary | setting accuracy of the switching threshold | +/-5 %
24464 | RM4UA31F | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24465 | RM4UA31F | Complementary | setting accuracy of time delay | 10 P
24466 | RM4UA31F | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24467 | RM4UA31F | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
24468 | RM4UA31F | Complementary | quality labels | CE
24469 | RM4UA31F | Complementary | overvoltage category | III conforming to IEC 60664-1
24470 | RM4UA31F | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
24471 | RM4UA31F | Complementary | operating voltage tolerance | 0.85...1.1 Uc
24472 | RM4UA31F | Complementary | supply disconnection value | > 0.1 Uc
24473 | RM4UA31F | Complementary | operating position | Any position without derating
24474 | RM4UA31F | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
24475 | RM4UA31F | Complementary | tightening torque | 0.6…1.1 N.m
24476 | RM4UA31F | Complementary | mechanical durability | 30000000 cycles
24477 | RM4UA31F | Complementary | [Ith] conventional free air thermal current | 8 A
24478 | RM4UA31F | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
24479 | RM4UA31F | Complementary | switching capacity in mA | 10 mA at 12 V
24480 | RM4UA31F | Complementary | switching voltage | 250 V AC
24481 | RM4UA31F | Complementary | contacts material | 90/10 silver nickel contacts
24482 | RM4UA31F | Complementary | number of cables | 2
24483 | RM4UA31F | Complementary | height | 78 mm
24484 | RM4UA31F | Complementary | width | 22.5 mm
24485 | RM4UA31F | Complementary | depth | 80 mm
24486 | RM4UA31F | Complementary | terminals description ISO n°1 | (15-16-18)OC (A1-A2)CO (C-B1-B2-B3)CO (25-26-28)OC
24487 | RM4UA31F | Complementary | output relay state | Tripped if A measured > A set
24488 | RM4UA31F | Complementary | 9 mm pitches | 2.5
24489 | RM4UA31F | Complementary | net weight | 0.168 kg
24490 | RM4UA31F | Complementary | compatibility code | RM4
24491 | RM4UA31F | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24492 | RM4UA31F | Environment | standards | EN/IEC 60255-6
24493 | RM4UA31F | Environment | product certifications | CSA UL GL
24494 | RM4UA31F | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
24495 | RM4UA31F | Environment | ambient air temperature for storage | -40…85 °C
24496 | RM4UA31F | Environment | ambient air temperature for operation | -20…65 °C
24497 | RM4UA31F | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24498 | RM4UA31F | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24499 | RM4UA31F | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24500 | RM4UA31F | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24501 | RM4UA31F | Environment | pollution degree | 3 conforming to IEC 60664-1
24502 | RM4UA31F | Environment | dielectric test voltage | 2.5 kV
24503 | RM4UA31F | Environment | non-dissipating shock wave | 4.8 kV
24504 | RM4UA31F | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24505 | RM4UA31F | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24506 | RM4UA31F | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24507 | RM4UA31F | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24508 | RM4UA31F | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
24509 | RM4UA31F | Contractual warranty | Warranty | 18 months
24510 | RM4UA31M | Main | range of product | Zelio Control
24511 | RM4UA31M | Main | product or component type | Industrial measurement and control relays
24512 | RM4UA31M | Main | relay type | Voltage measurement relay
24513 | RM4UA31M | Main | relay name | RM4U
24514 | RM4UA31M | Main | relay monitored parameters | Overvoltage or undervoltage detection
24515 | RM4UA31M | Main | time delay | Adjustable 0.05...30 s
24516 | RM4UA31M | Main | power consumption in VA | 2.7…3.4 VA AC
24517 | RM4UA31M | Main | measurement range | 0.05...0.5 V voltage AC 50/60 Hz 0.3...3 V voltage AC 50/60 Hz 0.5...5 V voltage AC 50/60 Hz 0.05...0.5 V voltage DC 0.3...3 V voltage DC 0.5...5 V voltage DC
24518 | RM4UA31M | Main | contacts type and composition | 2 C/O
24519 | RM4UA31M | Complementary | maximum switching voltage | 440 V AC
24520 | RM4UA31M | Complementary | [Us] rated supply voltage | 220...240 V AC 50/60 Hz +/- 5 %
24521 | RM4UA31M | Complementary | output contacts | 2 C/O
24522 | RM4UA31M | Complementary | internal input resistance | 71000 Ohm 43000 Ohm 6600 Ohm
24523 | RM4UA31M | Complementary | permissible continuous overload | 20 V 60 V 80 V
24524 | RM4UA31M | Complementary | permissible non repetitive overload | 100 A for <= 1 s 25 A for <= 1 s 80 A for <= 1 s
24525 | RM4UA31M | Complementary | setting accuracy of the switching threshold | +/-5 %
24526 | RM4UA31M | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24527 | RM4UA31M | Complementary | setting accuracy of time delay | 10 P
24528 | RM4UA31M | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24529 | RM4UA31M | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
24530 | RM4UA31M | Complementary | quality labels | CE
24531 | RM4UA31M | Complementary | overvoltage category | III conforming to IEC 60664-1
24532 | RM4UA31M | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
24533 | RM4UA31M | Complementary | operating voltage tolerance | 0.85...1.1 Uc
24534 | RM4UA31M | Complementary | supply disconnection value | > 0.1 Uc
24535 | RM4UA31M | Complementary | operating position | Any position without derating
24536 | RM4UA31M | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
24537 | RM4UA31M | Complementary | tightening torque | 0.6…1.1 N.m
24538 | RM4UA31M | Complementary | mechanical durability | 30000000 cycles
24539 | RM4UA31M | Complementary | [Ith] conventional free air thermal current | 8 A
24540 | RM4UA31M | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
24541 | RM4UA31M | Complementary | switching capacity in mA | 10 mA at 12 V
24542 | RM4UA31M | Complementary | switching voltage | 250 V AC
24543 | RM4UA31M | Complementary | contacts material | 90/10 silver nickel contacts
24544 | RM4UA31M | Complementary | number of cables | 2
24545 | RM4UA31M | Complementary | height | 78 mm
24546 | RM4UA31M | Complementary | width | 22.5 mm
24547 | RM4UA31M | Complementary | depth | 80 mm
24548 | RM4UA31M | Complementary | terminals description ISO n°1 | (25-26-28)OC (C-B1-B2-B3)CO (A1-A2)CO (15-16-18)OC
24549 | RM4UA31M | Complementary | output relay state | Tripped if A measured > A set
24550 | RM4UA31M | Complementary | 9 mm pitches | 2.5
24551 | RM4UA31M | Complementary | net weight | 0.168 kg
24552 | RM4UA31M | Complementary | compatibility code | RM4
24553 | RM4UA31M | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24554 | RM4UA31M | Environment | standards | EN/IEC 60255-6
24555 | RM4UA31M | Environment | product certifications | GL UL CSA
24556 | RM4UA31M | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
24557 | RM4UA31M | Environment | ambient air temperature for storage | -40…85 °C
24558 | RM4UA31M | Environment | ambient air temperature for operation | -20…65 °C
24559 | RM4UA31M | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24560 | RM4UA31M | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24561 | RM4UA31M | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24562 | RM4UA31M | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24563 | RM4UA31M | Environment | pollution degree | 3 conforming to IEC 60664-1
24564 | RM4UA31M | Environment | dielectric test voltage | 2.5 kV
24565 | RM4UA31M | Environment | non-dissipating shock wave | 4.8 kV
24566 | RM4UA31M | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24567 | RM4UA31M | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24568 | RM4UA31M | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24569 | RM4UA31M | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24570 | RM4UA31M | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
24571 | RM4UA31M | Contractual warranty | Warranty | 18 months
24572 | RM4UA31MW | Main | range of product | Zelio Control
24573 | RM4UA31MW | Main | product or component type | Industrial measurement and control relays
24574 | RM4UA31MW | Main | relay type | Voltage measurement relay
24575 | RM4UA31MW | Main | relay name | RM4U
24576 | RM4UA31MW | Main | relay monitored parameters | Overvoltage or undervoltage detection
24577 | RM4UA31MW | Main | time delay | Adjustable 0.05...30 s
24578 | RM4UA31MW | Main | power consumption in VA | 1.5…3.3 VA AC
24579 | RM4UA31MW | Main | measurement range | 0.05...0.5 V voltage AC 50/60 Hz 0.3...3 V voltage AC 50/60 Hz 0.5...5 V voltage AC 50/60 Hz 0.05...0.5 V voltage DC 0.3...3 V voltage DC 0.5...5 V voltage DC
24580 | RM4UA31MW | Complementary | maximum switching voltage | 440 V AC
24581 | RM4UA31MW | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz +/- 5 % 24...240 V DC
24582 | RM4UA31MW | Complementary | maximum power consumption in W | 1.2 W DC
24583 | RM4UA31MW | Complementary | output contacts | 2 C/O
24584 | RM4UA31MW | Complementary | internal input resistance | 71000 Ohm 43000 Ohm 6600 Ohm
24585 | RM4UA31MW | Complementary | permissible continuous overload | 80 V 20 V 60 V
24586 | RM4UA31MW | Complementary | permissible non repetitive overload | 100 A for <= 1 s 25 A for <= 1 s 80 A for <= 1 s
24587 | RM4UA31MW | Complementary | setting accuracy of the switching threshold | +/-5 %
24588 | RM4UA31MW | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24589 | RM4UA31MW | Complementary | setting accuracy of time delay | 10 P
24590 | RM4UA31MW | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24591 | RM4UA31MW | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
24592 | RM4UA31MW | Complementary | quality labels | CE
24593 | RM4UA31MW | Complementary | overvoltage category | III conforming to IEC 60664-1
24594 | RM4UA31MW | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
24595 | RM4UA31MW | Complementary | operating voltage tolerance | 0.85...1.1 Uc
24596 | RM4UA31MW | Complementary | supply disconnection value | > 0.1 Uc
24597 | RM4UA31MW | Complementary | operating position | Any position without derating
24598 | RM4UA31MW | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
24599 | RM4UA31MW | Complementary | tightening torque | 0.6…1.1 N.m
24600 | RM4UA31MW | Complementary | mechanical durability | 30000000 cycles
24601 | RM4UA31MW | Complementary | [Ith] conventional free air thermal current | 8 A
24602 | RM4UA31MW | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
24603 | RM4UA31MW | Complementary | switching capacity in mA | 10 mA at 12 V
24604 | RM4UA31MW | Complementary | switching voltage | 250 V AC
24605 | RM4UA31MW | Complementary | contacts material | 90/10 silver nickel contacts
24606 | RM4UA31MW | Complementary | width | 22.5 mm
24607 | RM4UA31MW | Complementary | net weight | 0.08 kg
24608 | RM4UA31MW | Complementary | compatibility code | RM4
24609 | RM4UA31MW | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24610 | RM4UA31MW | Environment | standards | EN/IEC 60255-6
24611 | RM4UA31MW | Environment | product certifications | GL UL CSA
24612 | RM4UA31MW | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
24613 | RM4UA31MW | Environment | ambient air temperature for storage | -40…85 °C
24614 | RM4UA31MW | Environment | ambient air temperature for operation | -20…65 °C
24615 | RM4UA31MW | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24616 | RM4UA31MW | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24617 | RM4UA31MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24618 | RM4UA31MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24619 | RM4UA31MW | Environment | pollution degree | 3 conforming to IEC 60664-1
24620 | RM4UA31MW | Environment | dielectric test voltage | 2.5 kV
24621 | RM4UA31MW | Environment | non-dissipating shock wave | 4.8 kV
24622 | RM4UA31MW | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24623 | RM4UA31MW | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24624 | RM4UA31MW | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24625 | RM4UA31MW | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24626 | RM4UA31MW | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
24627 | RM4UA31MW | Contractual warranty | Warranty | 18 months
24628 | RM4UA31Q | Main | range of product | Zelio Control
24629 | RM4UA31Q | Main | product or component type | Industrial measurement and control relays
24630 | RM4UA31Q | Main | relay type | Voltage measurement relay
24631 | RM4UA31Q | Main | relay name | RM4U
24632 | RM4UA31Q | Main | relay monitored parameters | Overvoltage or undervoltage detection
24633 | RM4UA31Q | Main | time delay | Adjustable 0.05...30 s
24634 | RM4UA31Q | Main | power consumption in VA | 2.7…3.4 VA AC
24635 | RM4UA31Q | Main | measurement range | 0.05...0.5 V voltage AC 50/60 Hz 0.3...3 V voltage AC 50/60 Hz 0.5...5 V voltage AC 50/60 Hz 0.05...0.5 V voltage DC 0.3...3 V voltage DC 0.5...5 V voltage DC
24636 | RM4UA31Q | Main | contacts type and composition | 2 C/O
24637 | RM4UA31Q | Complementary | maximum switching voltage | 440 V AC
24638 | RM4UA31Q | Complementary | [Us] rated supply voltage | 380...415 V AC 50/60 Hz +/- 5 %
24639 | RM4UA31Q | Complementary | output contacts | 2 C/O
24640 | RM4UA31Q | Complementary | internal input resistance | 43000 Ohm 71000 Ohm 6600 Ohm
24641 | RM4UA31Q | Complementary | permissible continuous overload | 60 V 80 V 20 V
24642 | RM4UA31Q | Complementary | permissible non repetitive overload | 100 A for <= 1 s 25 A for <= 1 s 80 A for <= 1 s
24643 | RM4UA31Q | Complementary | setting accuracy of the switching threshold | +/-5 %
24644 | RM4UA31Q | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24645 | RM4UA31Q | Complementary | setting accuracy of time delay | 10 P
24646 | RM4UA31Q | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24647 | RM4UA31Q | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
24648 | RM4UA31Q | Complementary | quality labels | CE
24649 | RM4UA31Q | Complementary | overvoltage category | III conforming to IEC 60664-1
24650 | RM4UA31Q | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
24651 | RM4UA31Q | Complementary | operating voltage tolerance | 0.85...1.1 Uc
24652 | RM4UA31Q | Complementary | supply disconnection value | > 0.1 Uc
24653 | RM4UA31Q | Complementary | operating position | Any position without derating
24654 | RM4UA31Q | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
24655 | RM4UA31Q | Complementary | tightening torque | 0.6…1.1 N.m
24656 | RM4UA31Q | Complementary | mechanical durability | 30000000 cycles
24657 | RM4UA31Q | Complementary | [Ith] conventional free air thermal current | 8 A
24658 | RM4UA31Q | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
24659 | RM4UA31Q | Complementary | switching capacity in mA | 10 mA at 12 V
24660 | RM4UA31Q | Complementary | switching voltage | 250 V AC
24661 | RM4UA31Q | Complementary | contacts material | 90/10 silver nickel contacts
24662 | RM4UA31Q | Complementary | number of cables | 2
24663 | RM4UA31Q | Complementary | height | 78 mm
24664 | RM4UA31Q | Complementary | width | 22.5 mm
24665 | RM4UA31Q | Complementary | depth | 80 mm
24666 | RM4UA31Q | Complementary | terminals description ISO n°1 | (A1-A2)CO (25-26-28)OC (C-B1-B2-B3)CO (15-16-18)OC
24667 | RM4UA31Q | Complementary | output relay state | Tripped if A measured > A set
24668 | RM4UA31Q | Complementary | 9 mm pitches | 2.5
24669 | RM4UA31Q | Complementary | net weight | 0.168 kg
24670 | RM4UA31Q | Complementary | compatibility code | RM4
24671 | RM4UA31Q | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24672 | RM4UA31Q | Environment | standards | EN/IEC 60255-6
24673 | RM4UA31Q | Environment | product certifications | CSA GL UL
24674 | RM4UA31Q | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
24675 | RM4UA31Q | Environment | ambient air temperature for storage | -40…85 °C
24676 | RM4UA31Q | Environment | ambient air temperature for operation | -20…65 °C
24677 | RM4UA31Q | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24678 | RM4UA31Q | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24679 | RM4UA31Q | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24680 | RM4UA31Q | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24681 | RM4UA31Q | Environment | pollution degree | 3 conforming to IEC 60664-1
24682 | RM4UA31Q | Environment | dielectric test voltage | 2.5 kV
24683 | RM4UA31Q | Environment | non-dissipating shock wave | 4.8 kV
24684 | RM4UA31Q | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24685 | RM4UA31Q | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24686 | RM4UA31Q | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24687 | RM4UA31Q | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24688 | RM4UA31Q | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
24689 | RM4UA31Q | Contractual warranty | Warranty | 18 months
24690 | RM4UA32F | Main | range of product | Zelio Control
24691 | RM4UA32F | Main | product or component type | Industrial measurement and control relays
24692 | RM4UA32F | Main | relay type | Voltage measurement relay
24693 | RM4UA32F | Main | relay name | RM4U
24694 | RM4UA32F | Main | relay monitored parameters | Overvoltage or undervoltage detection
24695 | RM4UA32F | Main | time delay | Adjustable 0.05...30 s
24696 | RM4UA32F | Main | power consumption in VA | 1.9…3.3 VA AC
24697 | RM4UA32F | Main | measurement range | 1...10 V voltage AC 50/60 Hz 10...100 V voltage AC 50/60 Hz 5...50 V voltage AC 50/60 Hz 1...10 V voltage DC 10...100 V voltage DC 5...50 V voltage DC
24698 | RM4UA32F | Main | contacts type and composition | 2 C/O
24699 | RM4UA32F | Complementary | maximum switching voltage | 440 V AC
24700 | RM4UA32F | Complementary | [Us] rated supply voltage | 110...130 V AC 50/60 Hz +/- 5 %
24701 | RM4UA32F | Complementary | output contacts | 2 C/O
24702 | RM4UA32F | Complementary | internal input resistance | 112000 Ohm 23000 Ohm 225000 Ohm
24703 | RM4UA32F | Complementary | permissible continuous overload | 150 V 90 V 300 V
24704 | RM4UA32F | Complementary | permissible non repetitive overload | 100 A for <= 1 s 200 A for <= 1 s 550 A for <= 1 s
24705 | RM4UA32F | Complementary | setting accuracy of the switching threshold | +/-5 %
24706 | RM4UA32F | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24707 | RM4UA32F | Complementary | setting accuracy of time delay | 10 P
24708 | RM4UA32F | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24709 | RM4UA32F | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
24710 | RM4UA32F | Complementary | quality labels | CE
24711 | RM4UA32F | Complementary | overvoltage category | III conforming to IEC 60664-1
24712 | RM4UA32F | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
24713 | RM4UA32F | Complementary | operating voltage tolerance | 0.85...1.1 Uc
24714 | RM4UA32F | Complementary | supply disconnection value | > 0.1 Uc
24715 | RM4UA32F | Complementary | operating position | Any position without derating
24716 | RM4UA32F | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
24717 | RM4UA32F | Complementary | tightening torque | 0.6…1.1 N.m
24718 | RM4UA32F | Complementary | mechanical durability | 30000000 cycles
24719 | RM4UA32F | Complementary | [Ith] conventional free air thermal current | 8 A
24720 | RM4UA32F | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
24721 | RM4UA32F | Complementary | switching capacity in mA | 10 mA at 12 V
24722 | RM4UA32F | Complementary | switching voltage | 250 V AC
24723 | RM4UA32F | Complementary | contacts material | 90/10 silver nickel contacts
24724 | RM4UA32F | Complementary | number of cables | 2
24725 | RM4UA32F | Complementary | height | 78 mm
24726 | RM4UA32F | Complementary | width | 22.5 mm
24727 | RM4UA32F | Complementary | depth | 80 mm
24728 | RM4UA32F | Complementary | terminals description ISO n°1 | (15-16-18)OC (25-26-28)OC (A1-A2)CO (C-B1-B2-B3)CO
24729 | RM4UA32F | Complementary | output relay state | Tripped if A measured > A set
24730 | RM4UA32F | Complementary | 9 mm pitches | 2.5
24731 | RM4UA32F | Complementary | net weight | 0.168 kg
24732 | RM4UA32F | Complementary | compatibility code | RM4
24733 | RM4UA32F | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24734 | RM4UA32F | Environment | standards | EN/IEC 60255-6
24735 | RM4UA32F | Environment | product certifications | UL CSA GL
24736 | RM4UA32F | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
24737 | RM4UA32F | Environment | ambient air temperature for storage | -40…85 °C
24738 | RM4UA32F | Environment | ambient air temperature for operation | -20…65 °C
24739 | RM4UA32F | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24740 | RM4UA32F | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24741 | RM4UA32F | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24742 | RM4UA32F | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24743 | RM4UA32F | Environment | pollution degree | 3 conforming to IEC 60664-1
24744 | RM4UA32F | Environment | dielectric test voltage | 2.5 kV
24745 | RM4UA32F | Environment | non-dissipating shock wave | 4.8 kV
24746 | RM4UA32F | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24747 | RM4UA32F | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24748 | RM4UA32F | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24749 | RM4UA32F | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24750 | RM4UA32F | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
24751 | RM4UA32F | Contractual warranty | Warranty | 18 months
24752 | RM4UA32M | Main | range of product | Zelio Control
24753 | RM4UA32M | Main | product or component type | Industrial measurement and control relays
24754 | RM4UA32M | Main | relay type | Voltage measurement relay
24755 | RM4UA32M | Main | relay name | RM4U
24756 | RM4UA32M | Main | relay monitored parameters | Overvoltage or undervoltage detection
24757 | RM4UA32M | Main | time delay | Adjustable 0.05...30 s
24758 | RM4UA32M | Main | power consumption in VA | 2.7…3.4 VA AC
24759 | RM4UA32M | Main | measurement range | 1...10 V voltage AC 50/60 Hz 10...100 V voltage AC 50/60 Hz 5...50 V voltage AC 50/60 Hz 1...10 V voltage DC 10...100 V voltage DC 5...50 V voltage DC
24760 | RM4UA32M | Main | contacts type and composition | 2 C/O
24761 | RM4UA32M | Complementary | maximum switching voltage | 440 V AC
24762 | RM4UA32M | Complementary | [Us] rated supply voltage | 220...240 V AC 50/60 Hz +/- 5 %
24763 | RM4UA32M | Complementary | output contacts | 2 C/O
24764 | RM4UA32M | Complementary | internal input resistance | 112000 Ohm 225000 Ohm 23000 Ohm
24765 | RM4UA32M | Complementary | permissible continuous overload | 90 V 150 V 300 V
24766 | RM4UA32M | Complementary | permissible non repetitive overload | 100 A for <= 1 s 200 A for <= 1 s 400 A for <= 1 s
24767 | RM4UA32M | Complementary | setting accuracy of the switching threshold | +/-5 %
24768 | RM4UA32M | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24769 | RM4UA32M | Complementary | setting accuracy of time delay | 10 P
24770 | RM4UA32M | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24771 | RM4UA32M | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
24772 | RM4UA32M | Complementary | quality labels | CE
24773 | RM4UA32M | Complementary | overvoltage category | III conforming to IEC 60664-1
24774 | RM4UA32M | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
24775 | RM4UA32M | Complementary | operating voltage tolerance | 0.85...1.1 Uc
24776 | RM4UA32M | Complementary | supply disconnection value | > 0.1 Uc
24777 | RM4UA32M | Complementary | operating position | Any position without derating
24778 | RM4UA32M | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
24779 | RM4UA32M | Complementary | tightening torque | 0.6…1.1 N.m
24780 | RM4UA32M | Complementary | mechanical durability | 30000000 cycles
24781 | RM4UA32M | Complementary | [Ith] conventional free air thermal current | 8 A
24782 | RM4UA32M | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
24783 | RM4UA32M | Complementary | switching capacity in mA | 10 mA at 12 V
24784 | RM4UA32M | Complementary | switching voltage | 250 V AC
24785 | RM4UA32M | Complementary | contacts material | 90/10 silver nickel contacts
24786 | RM4UA32M | Complementary | number of cables | 2
24787 | RM4UA32M | Complementary | height | 78 mm
24788 | RM4UA32M | Complementary | width | 22.5 mm
24789 | RM4UA32M | Complementary | depth | 80 mm
24790 | RM4UA32M | Complementary | terminals description ISO n°1 | (C-B1-B2-B3)CO (25-26-28)OC (A1-A2)CO (15-16-18)OC
24791 | RM4UA32M | Complementary | output relay state | Tripped if A measured > A set
24792 | RM4UA32M | Complementary | 9 mm pitches | 2.5
24793 | RM4UA32M | Complementary | net weight | 0.168 kg
24794 | RM4UA32M | Complementary | compatibility code | RM4
24795 | RM4UA32M | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24796 | RM4UA32M | Environment | standards | EN/IEC 60255-6
24797 | RM4UA32M | Environment | product certifications | GL CSA UL
24798 | RM4UA32M | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
24799 | RM4UA32M | Environment | ambient air temperature for storage | -40…85 °C
24800 | RM4UA32M | Environment | ambient air temperature for operation | -20…65 °C
24801 | RM4UA32M | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24802 | RM4UA32M | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24803 | RM4UA32M | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24804 | RM4UA32M | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24805 | RM4UA32M | Environment | pollution degree | 3 conforming to IEC 60664-1
24806 | RM4UA32M | Environment | dielectric test voltage | 2.5 kV
24807 | RM4UA32M | Environment | non-dissipating shock wave | 4.8 kV
24808 | RM4UA32M | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24809 | RM4UA32M | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24810 | RM4UA32M | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24811 | RM4UA32M | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24812 | RM4UA32M | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
24813 | RM4UA32M | Contractual warranty | Warranty | 18 months
24814 | RM4UA32MW | Main | range of product | Zelio Control
24815 | RM4UA32MW | Main | product or component type | Industrial measurement and control relays
24816 | RM4UA32MW | Main | relay type | Voltage measurement relay
24817 | RM4UA32MW | Main | relay name | RM4U
24818 | RM4UA32MW | Main | relay monitored parameters | Overvoltage or undervoltage detection
24819 | RM4UA32MW | Main | time delay | Adjustable 0.05...30 s
24820 | RM4UA32MW | Main | power consumption in VA | 1.5…3.3 VA AC
24821 | RM4UA32MW | Main | measurement range | 1...10 V voltage AC 50/60 Hz 10...100 V voltage AC 50/60 Hz 5...50 V voltage AC 50/60 Hz 1...10 V voltage DC 10...100 V voltage DC 5...50 V voltage DC
24822 | RM4UA32MW | Main | contacts type and composition | 2 C/O
24823 | RM4UA32MW | Complementary | maximum switching voltage | 440 V AC
24824 | RM4UA32MW | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz +/- 5 % 24...240 V DC
24825 | RM4UA32MW | Complementary | maximum power consumption in W | 1.2 W DC
24826 | RM4UA32MW | Complementary | output contacts | 2 C/O
24827 | RM4UA32MW | Complementary | internal input resistance | 112000 Ohm 225000 Ohm 23000 Ohm
24828 | RM4UA32MW | Complementary | permissible continuous overload | 300 V 90 V 150 V
24829 | RM4UA32MW | Complementary | permissible non repetitive overload | 100 A for <= 1 s 200 A for <= 1 s 400 A for <= 1 s
24830 | RM4UA32MW | Complementary | setting accuracy of the switching threshold | +/-5 %
24831 | RM4UA32MW | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24832 | RM4UA32MW | Complementary | setting accuracy of time delay | 10 P
24833 | RM4UA32MW | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24834 | RM4UA32MW | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
24835 | RM4UA32MW | Complementary | quality labels | CE
24836 | RM4UA32MW | Complementary | overvoltage category | III conforming to IEC 60664-1
24837 | RM4UA32MW | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
24838 | RM4UA32MW | Complementary | operating voltage tolerance | 0.85...1.1 Uc
24839 | RM4UA32MW | Complementary | supply disconnection value | > 0.1 Uc
24840 | RM4UA32MW | Complementary | operating position | Any position without derating
24841 | RM4UA32MW | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
24842 | RM4UA32MW | Complementary | tightening torque | 0.6…1.1 N.m
24843 | RM4UA32MW | Complementary | mechanical durability | 30000000 cycles
24844 | RM4UA32MW | Complementary | [Ith] conventional free air thermal current | 8 A
24845 | RM4UA32MW | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
24846 | RM4UA32MW | Complementary | switching capacity in mA | 10 mA at 12 V
24847 | RM4UA32MW | Complementary | switching voltage | 250 V AC
24848 | RM4UA32MW | Complementary | contacts material | 90/10 silver nickel contacts
24849 | RM4UA32MW | Complementary | number of cables | 2
24850 | RM4UA32MW | Complementary | height | 78 mm
24851 | RM4UA32MW | Complementary | width | 22.5 mm
24852 | RM4UA32MW | Complementary | depth | 80 mm
24853 | RM4UA32MW | Complementary | terminals description ISO n°1 | (15-16-18)OC (25-26-28)OC (C-B1-B2-B3)CO (A1-A2)CO
24854 | RM4UA32MW | Complementary | output relay state | Tripped if A measured > A set
24855 | RM4UA32MW | Complementary | 9 mm pitches | 2.5
24856 | RM4UA32MW | Complementary | net weight | 0.168 kg
24857 | RM4UA32MW | Complementary | compatibility code | RM4
24858 | RM4UA32MW | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24859 | RM4UA32MW | Environment | standards | EN/IEC 60255-6
24860 | RM4UA32MW | Environment | product certifications | GL CSA UL
24861 | RM4UA32MW | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
24862 | RM4UA32MW | Environment | ambient air temperature for storage | -40…85 °C
24863 | RM4UA32MW | Environment | ambient air temperature for operation | -20…65 °C
24864 | RM4UA32MW | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24865 | RM4UA32MW | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24866 | RM4UA32MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24867 | RM4UA32MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24868 | RM4UA32MW | Environment | pollution degree | 3 conforming to IEC 60664-1
24869 | RM4UA32MW | Environment | dielectric test voltage | 2.5 kV
24870 | RM4UA32MW | Environment | non-dissipating shock wave | 4.8 kV
24871 | RM4UA32MW | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24872 | RM4UA32MW | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24873 | RM4UA32MW | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24874 | RM4UA32MW | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24875 | RM4UA32MW | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
24876 | RM4UA32MW | Contractual warranty | Warranty | 18 months
24877 | RM4UA32Q | Main | range of product | Zelio Control
24878 | RM4UA32Q | Main | product or component type | Industrial measurement and control relays
24879 | RM4UA32Q | Main | relay type | Voltage measurement relay
24880 | RM4UA32Q | Main | relay name | RM4U
24881 | RM4UA32Q | Main | relay monitored parameters | Overvoltage or undervoltage detection
24882 | RM4UA32Q | Main | time delay | Adjustable 0.05...30 s
24883 | RM4UA32Q | Main | power consumption in VA | 2.7…3 VA AC
24884 | RM4UA32Q | Main | measurement range | 1...10 V voltage AC 50/60 Hz 10...100 V voltage AC 50/60 Hz 5...50 V voltage AC 50/60 Hz 1...10 V voltage DC 10...100 V voltage DC 5...50 V voltage DC
24885 | RM4UA32Q | Main | contacts type and composition | 2 C/O
24886 | RM4UA32Q | Complementary | maximum switching voltage | 440 V AC
24887 | RM4UA32Q | Complementary | [Us] rated supply voltage | 380...415 V AC 50/60 Hz +/- 5 %
24888 | RM4UA32Q | Complementary | output contacts | 2 C/O
24889 | RM4UA32Q | Complementary | internal input resistance | 225000 Ohm 112000 Ohm 23000 Ohm
24890 | RM4UA32Q | Complementary | permissible continuous overload | 150 V 300 V 90 V
24891 | RM4UA32Q | Complementary | permissible non repetitive overload | 100 A for <= 1 s 200 A for <= 1 s 400 A for <= 1 s
24892 | RM4UA32Q | Complementary | setting accuracy of the switching threshold | +/-5 %
24893 | RM4UA32Q | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24894 | RM4UA32Q | Complementary | setting accuracy of time delay | 10 P
24895 | RM4UA32Q | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24896 | RM4UA32Q | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
24897 | RM4UA32Q | Complementary | quality labels | CE
24898 | RM4UA32Q | Complementary | overvoltage category | III conforming to IEC 60664-1
24899 | RM4UA32Q | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
24900 | RM4UA32Q | Complementary | operating voltage tolerance | 0.85...1.1 Uc
24901 | RM4UA32Q | Complementary | supply disconnection value | > 0.1 Uc
24902 | RM4UA32Q | Complementary | operating position | Any position without derating
24903 | RM4UA32Q | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
24904 | RM4UA32Q | Complementary | tightening torque | 0.6…1.1 N.m
24905 | RM4UA32Q | Complementary | mechanical durability | 30000000 cycles
24906 | RM4UA32Q | Complementary | [Ith] conventional free air thermal current | 8 A
24907 | RM4UA32Q | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
24908 | RM4UA32Q | Complementary | switching capacity in mA | 10 mA at 12 V
24909 | RM4UA32Q | Complementary | switching voltage | 250 V AC
24910 | RM4UA32Q | Complementary | contacts material | 90/10 silver nickel contacts
24911 | RM4UA32Q | Complementary | number of cables | 2
24912 | RM4UA32Q | Complementary | height | 78 mm
24913 | RM4UA32Q | Complementary | width | 22.5 mm
24914 | RM4UA32Q | Complementary | depth | 80 mm
24915 | RM4UA32Q | Complementary | terminals description ISO n°1 | (C-B1-B2-B3)CO (15-16-18)OC (A1-A2)CO (25-26-28)OC
24916 | RM4UA32Q | Complementary | output relay state | Tripped if A measured > A set
24917 | RM4UA32Q | Complementary | 9 mm pitches | 2.5
24918 | RM4UA32Q | Complementary | net weight | 0.168 kg
24919 | RM4UA32Q | Complementary | compatibility code | RM4
24920 | RM4UA32Q | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24921 | RM4UA32Q | Environment | standards | EN/IEC 60255-6
24922 | RM4UA32Q | Environment | product certifications | CSA UL GL
24923 | RM4UA32Q | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
24924 | RM4UA32Q | Environment | ambient air temperature for storage | -40…85 °C
24925 | RM4UA32Q | Environment | ambient air temperature for operation | -20…65 °C
24926 | RM4UA32Q | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24927 | RM4UA32Q | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24928 | RM4UA32Q | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24929 | RM4UA32Q | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24930 | RM4UA32Q | Environment | pollution degree | 3 conforming to IEC 60664-1
24931 | RM4UA32Q | Environment | dielectric test voltage | 2.5 kV
24932 | RM4UA32Q | Environment | non-dissipating shock wave | 4.8 kV
24933 | RM4UA32Q | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24934 | RM4UA32Q | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24935 | RM4UA32Q | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24936 | RM4UA32Q | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24937 | RM4UA32Q | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
24938 | RM4UA32Q | Contractual warranty | Warranty | 18 months
24939 | RM4UA33F | Main | range of product | Zelio Control
24940 | RM4UA33F | Main | product or component type | Industrial measurement and control relays
24941 | RM4UA33F | Main | relay type | Voltage measurement relay
24942 | RM4UA33F | Main | relay name | RM4U
24943 | RM4UA33F | Main | relay monitored parameters | Overvoltage or undervoltage detection
24944 | RM4UA33F | Main | time delay | Adjustable 0.05...30 s
24945 | RM4UA33F | Main | power consumption in VA | 1.9…3.3 VA AC
24946 | RM4UA33F | Main | measurement range | 30...300 V voltage AC 50/60 Hz 50...500 V voltage AC 50/60 Hz 30...300 V voltage DC 50...500 V voltage DC
24947 | RM4UA33F | Main | contacts type and composition | 2 C/O
24948 | RM4UA33F | Complementary | maximum switching voltage | 440 V AC
24949 | RM4UA33F | Complementary | [Us] rated supply voltage | 110...130 V AC 50/60 Hz +/- 5 %
24950 | RM4UA33F | Complementary | output contacts | 2 C/O
24951 | RM4UA33F | Complementary | internal input resistance | 1111000 Ohm 668000 Ohm 11110000 Ohm
24952 | RM4UA33F | Complementary | permissible continuous overload | 550 V 400 V
24953 | RM4UA33F | Complementary | permissible non repetitive overload | 500 A for <= 1 s 550 A for <= 1 s
24954 | RM4UA33F | Complementary | setting accuracy of the switching threshold | +/-5 %
24955 | RM4UA33F | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24956 | RM4UA33F | Complementary | setting accuracy of time delay | 10 P
24957 | RM4UA33F | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
24958 | RM4UA33F | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
24959 | RM4UA33F | Complementary | quality labels | CE
24960 | RM4UA33F | Complementary | overvoltage category | III conforming to IEC 60664-1
24961 | RM4UA33F | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
24962 | RM4UA33F | Complementary | operating voltage tolerance | 0.85...1.1 Uc
24963 | RM4UA33F | Complementary | supply disconnection value | > 0.1 Uc
24964 | RM4UA33F | Complementary | operating position | Any position without derating
24965 | RM4UA33F | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
24966 | RM4UA33F | Complementary | tightening torque | 0.6…1.1 N.m
24967 | RM4UA33F | Complementary | mechanical durability | 30000000 cycles
24968 | RM4UA33F | Complementary | [Ith] conventional free air thermal current | 8 A
24969 | RM4UA33F | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
24970 | RM4UA33F | Complementary | switching capacity in mA | 10 mA at 12 V
24971 | RM4UA33F | Complementary | switching voltage | 250 V AC
24972 | RM4UA33F | Complementary | contacts material | 90/10 silver nickel contacts
24973 | RM4UA33F | Complementary | number of cables | 2
24974 | RM4UA33F | Complementary | height | 78 mm
24975 | RM4UA33F | Complementary | width | 22.5 mm
24976 | RM4UA33F | Complementary | depth | 80 mm
24977 | RM4UA33F | Complementary | terminals description ISO n°1 | (C-B2-B3)CO (15-16-18)OC (A1-A2)CO (25-26-28)OC
24978 | RM4UA33F | Complementary | output relay state | Tripped if A measured > A set
24979 | RM4UA33F | Complementary | 9 mm pitches | 2.5
24980 | RM4UA33F | Complementary | net weight | 0.168 kg
24981 | RM4UA33F | Complementary | compatibility code | RM4
24982 | RM4UA33F | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
24983 | RM4UA33F | Environment | standards | EN/IEC 60255-6
24984 | RM4UA33F | Environment | product certifications | UL CSA GL
24985 | RM4UA33F | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
24986 | RM4UA33F | Environment | ambient air temperature for storage | -40…85 °C
24987 | RM4UA33F | Environment | ambient air temperature for operation | -20…65 °C
24988 | RM4UA33F | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
24989 | RM4UA33F | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
24990 | RM4UA33F | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
24991 | RM4UA33F | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
24992 | RM4UA33F | Environment | pollution degree | 3 conforming to IEC 60664-1
24993 | RM4UA33F | Environment | dielectric test voltage | 2.5 kV
24994 | RM4UA33F | Environment | non-dissipating shock wave | 4.8 kV
24995 | RM4UA33F | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
24996 | RM4UA33F | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
24997 | RM4UA33F | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
24998 | RM4UA33F | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
24999 | RM4UA33F | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
25000 | RM4UA33F | Contractual warranty | Warranty | 18 months
25001 | RM4UA33M | Main | range of product | Zelio Control
25002 | RM4UA33M | Main | product or component type | Industrial measurement and control relays
25003 | RM4UA33M | Main | relay type | Voltage measurement relay
25004 | RM4UA33M | Main | relay name | RM4U
25005 | RM4UA33M | Main | relay monitored parameters | Overvoltage or undervoltage detection
25006 | RM4UA33M | Main | time delay | Adjustable 0.05...30 s
25007 | RM4UA33M | Main | power consumption in VA | 2.7…3.4 VA AC
25008 | RM4UA33M | Main | measurement range | 30...300 V voltage AC 50/60 Hz 50...500 V voltage AC 50/60 Hz 30...300 V voltage DC 50...500 V voltage DC
25009 | RM4UA33M | Main | contacts type and composition | 2 C/O
25010 | RM4UA33M | Complementary | maximum switching voltage | 440 V AC
25011 | RM4UA33M | Complementary | [Us] rated supply voltage | 220...240 V AC 50/60 Hz +/- 5 %
25012 | RM4UA33M | Complementary | output contacts | 2 C/O
25013 | RM4UA33M | Complementary | internal input resistance | 1111000 Ohm 11110000 Ohm 668000 Ohm
25014 | RM4UA33M | Complementary | permissible continuous overload | 400 V 550 V
25015 | RM4UA33M | Complementary | permissible non repetitive overload | 500 A for <= 1 s 550 A for <= 1 s
25016 | RM4UA33M | Complementary | setting accuracy of the switching threshold | +/-5 %
25017 | RM4UA33M | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
25018 | RM4UA33M | Complementary | setting accuracy of time delay | 10 P
25019 | RM4UA33M | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
25020 | RM4UA33M | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
25021 | RM4UA33M | Complementary | quality labels | CE
25022 | RM4UA33M | Complementary | overvoltage category | III conforming to IEC 60664-1
25023 | RM4UA33M | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25024 | RM4UA33M | Complementary | operating voltage tolerance | 0.85...1.1 Uc
25025 | RM4UA33M | Complementary | supply disconnection value | > 0.1 Uc
25026 | RM4UA33M | Complementary | operating position | Any position without derating
25027 | RM4UA33M | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
25028 | RM4UA33M | Complementary | tightening torque | 0.6…1.1 N.m
25029 | RM4UA33M | Complementary | mechanical durability | 30000000 cycles
25030 | RM4UA33M | Complementary | [Ith] conventional free air thermal current | 8 A
25031 | RM4UA33M | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25032 | RM4UA33M | Complementary | switching capacity in mA | 10 mA at 12 V
25033 | RM4UA33M | Complementary | switching voltage | 250 V AC
25034 | RM4UA33M | Complementary | contacts material | 90/10 silver nickel contacts
25035 | RM4UA33M | Complementary | number of cables | 2
25036 | RM4UA33M | Complementary | height | 78 mm
25037 | RM4UA33M | Complementary | width | 22.5 mm
25038 | RM4UA33M | Complementary | depth | 80 mm
25039 | RM4UA33M | Complementary | terminals description ISO n°1 | (C-B2-B3)CO (15-16-18)OC (25-26-28)OC (A1-A2)CO
25040 | RM4UA33M | Complementary | output relay state | Tripped if A measured > A set
25041 | RM4UA33M | Complementary | 9 mm pitches | 2.5
25042 | RM4UA33M | Complementary | net weight | 0.168 kg
25043 | RM4UA33M | Complementary | compatibility code | RM4
25044 | RM4UA33M | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
25045 | RM4UA33M | Environment | standards | EN/IEC 60255-6
25046 | RM4UA33M | Environment | product certifications | UL GL CSA
25047 | RM4UA33M | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
25048 | RM4UA33M | Environment | ambient air temperature for storage | -40…85 °C
25049 | RM4UA33M | Environment | ambient air temperature for operation | -20…65 °C
25050 | RM4UA33M | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
25051 | RM4UA33M | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
25052 | RM4UA33M | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
25053 | RM4UA33M | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
25054 | RM4UA33M | Environment | pollution degree | 3 conforming to IEC 60664-1
25055 | RM4UA33M | Environment | dielectric test voltage | 2.5 kV
25056 | RM4UA33M | Environment | non-dissipating shock wave | 4.8 kV
25057 | RM4UA33M | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
25058 | RM4UA33M | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
25059 | RM4UA33M | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
25060 | RM4UA33M | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
25061 | RM4UA33M | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
25062 | RM4UA33M | Contractual warranty | Warranty | 18 months
25063 | RM4UA33MW | Main | range of product | Zelio Control
25064 | RM4UA33MW | Main | product or component type | Industrial measurement and control relays
25065 | RM4UA33MW | Main | relay type | Voltage measurement relay
25066 | RM4UA33MW | Main | relay name | RM4U
25067 | RM4UA33MW | Main | relay monitored parameters | Overvoltage or undervoltage detection
25068 | RM4UA33MW | Main | time delay | Adjustable 0.05...30 s
25069 | RM4UA33MW | Main | power consumption in VA | 1.5…3.3 VA AC
25070 | RM4UA33MW | Main | measurement range | 30...300 V voltage AC 50/60 Hz 50...500 V voltage AC 50/60 Hz 30...300 V voltage DC 50...500 V voltage DC
25071 | RM4UA33MW | Main | contacts type and composition | 2 C/O
25072 | RM4UA33MW | Complementary | maximum switching voltage | 440 V AC
25073 | RM4UA33MW | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz +/- 5 % 24...240 V DC
25074 | RM4UA33MW | Complementary | maximum power consumption in W | 1.2 W DC
25075 | RM4UA33MW | Complementary | output contacts | 2 C/O
25076 | RM4UA33MW | Complementary | internal input resistance | 11110000 Ohm 1111000 Ohm 668000 Ohm
25077 | RM4UA33MW | Complementary | permissible continuous overload | 550 V 400 V
25078 | RM4UA33MW | Complementary | permissible non repetitive overload | 500 A for <= 1 s 550 A for <= 1 s
25079 | RM4UA33MW | Complementary | setting accuracy of the switching threshold | +/-5 %
25080 | RM4UA33MW | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
25081 | RM4UA33MW | Complementary | setting accuracy of time delay | 10 P
25082 | RM4UA33MW | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
25083 | RM4UA33MW | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
25084 | RM4UA33MW | Complementary | quality labels | CE
25085 | RM4UA33MW | Complementary | overvoltage category | III conforming to IEC 60664-1
25086 | RM4UA33MW | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25087 | RM4UA33MW | Complementary | operating voltage tolerance | 0.85...1.1 Uc
25088 | RM4UA33MW | Complementary | supply disconnection value | > 0.1 Uc
25089 | RM4UA33MW | Complementary | operating position | Any position without derating
25090 | RM4UA33MW | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
25091 | RM4UA33MW | Complementary | tightening torque | 0.6…1.1 N.m
25092 | RM4UA33MW | Complementary | mechanical durability | 30000000 cycles
25093 | RM4UA33MW | Complementary | [Ith] conventional free air thermal current | 8 A
25094 | RM4UA33MW | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25095 | RM4UA33MW | Complementary | switching capacity in mA | 10 mA at 12 V
25096 | RM4UA33MW | Complementary | switching voltage | 250 V AC
25097 | RM4UA33MW | Complementary | contacts material | 90/10 silver nickel contacts
25098 | RM4UA33MW | Complementary | number of cables | 2
25099 | RM4UA33MW | Complementary | height | 78 mm
25100 | RM4UA33MW | Complementary | width | 22.5 mm
25101 | RM4UA33MW | Complementary | depth | 80 mm
25102 | RM4UA33MW | Complementary | terminals description ISO n°1 | (25-26-28)OC (C-B2-B3)CO (15-16-18)OC (A1-A2)CO
25103 | RM4UA33MW | Complementary | output relay state | Tripped if A measured > A set
25104 | RM4UA33MW | Complementary | 9 mm pitches | 2.5
25105 | RM4UA33MW | Complementary | net weight | 0.168 kg
25106 | RM4UA33MW | Complementary | compatibility code | RM4
25107 | RM4UA33MW | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
25108 | RM4UA33MW | Environment | standards | EN/IEC 60255-6
25109 | RM4UA33MW | Environment | product certifications | GL CSA UL
25110 | RM4UA33MW | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
25111 | RM4UA33MW | Environment | ambient air temperature for storage | -40…85 °C
25112 | RM4UA33MW | Environment | ambient air temperature for operation | -20…65 °C
25113 | RM4UA33MW | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
25114 | RM4UA33MW | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
25115 | RM4UA33MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
25116 | RM4UA33MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
25117 | RM4UA33MW | Environment | pollution degree | 3 conforming to IEC 60664-1
25118 | RM4UA33MW | Environment | dielectric test voltage | 2.5 kV
25119 | RM4UA33MW | Environment | non-dissipating shock wave | 4.8 kV
25120 | RM4UA33MW | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
25121 | RM4UA33MW | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
25122 | RM4UA33MW | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
25123 | RM4UA33MW | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
25124 | RM4UA33MW | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
25125 | RM4UA33MW | Contractual warranty | Warranty | 18 months
25126 | RM4UA33Q | Main | range of product | Zelio Control
25127 | RM4UA33Q | Main | product or component type | Industrial measurement and control relays
25128 | RM4UA33Q | Main | relay type | Voltage measurement relay
25129 | RM4UA33Q | Main | relay name | RM4U
25130 | RM4UA33Q | Main | relay monitored parameters | Overvoltage or undervoltage detection
25131 | RM4UA33Q | Main | time delay | Adjustable 0.05...30 s
25132 | RM4UA33Q | Main | power consumption in VA | 2.7…3 VA AC
25133 | RM4UA33Q | Main | measurement range | 30...300 V voltage AC 50/60 Hz 50...500 V voltage AC 50/60 Hz 30...300 V voltage DC 50...500 V voltage DC
25134 | RM4UA33Q | Main | contacts type and composition | 2 C/O
25135 | RM4UA33Q | Complementary | maximum switching voltage | 440 V AC
25136 | RM4UA33Q | Complementary | [Us] rated supply voltage | 380...415 V AC 50/60 Hz +/- 5 %
25137 | RM4UA33Q | Complementary | output contacts | 2 C/O
25138 | RM4UA33Q | Complementary | internal input resistance | 668000 Ohm 1111000 Ohm 11110000 Ohm
25139 | RM4UA33Q | Complementary | permissible continuous overload | 550 V 400 V
25140 | RM4UA33Q | Complementary | permissible non repetitive overload | 500 A for <= 1 s 550 A for <= 1 s
25141 | RM4UA33Q | Complementary | setting accuracy of the switching threshold | +/-5 %
25142 | RM4UA33Q | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
25143 | RM4UA33Q | Complementary | setting accuracy of time delay | 10 P
25144 | RM4UA33Q | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un)
25145 | RM4UA33Q | Complementary | hysteresis | 5…30 % adjustable of voltage threshold setting
25146 | RM4UA33Q | Complementary | quality labels | CE
25147 | RM4UA33Q | Complementary | overvoltage category | III conforming to IEC 60664-1
25148 | RM4UA33Q | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25149 | RM4UA33Q | Complementary | operating voltage tolerance | 0.85...1.1 Uc
25150 | RM4UA33Q | Complementary | supply disconnection value | > 0.1 Uc
25151 | RM4UA33Q | Complementary | operating position | Any position without derating
25152 | RM4UA33Q | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
25153 | RM4UA33Q | Complementary | tightening torque | 0.6…1.1 N.m
25154 | RM4UA33Q | Complementary | mechanical durability | 30000000 cycles
25155 | RM4UA33Q | Complementary | [Ith] conventional free air thermal current | 8 A
25156 | RM4UA33Q | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25157 | RM4UA33Q | Complementary | switching capacity in mA | 10 mA at 12 V
25158 | RM4UA33Q | Complementary | switching voltage | 250 V AC
25159 | RM4UA33Q | Complementary | contacts material | 90/10 silver nickel contacts
25160 | RM4UA33Q | Complementary | number of cables | 2
25161 | RM4UA33Q | Complementary | height | 78 mm
25162 | RM4UA33Q | Complementary | width | 22.5 mm
25163 | RM4UA33Q | Complementary | depth | 80 mm
25164 | RM4UA33Q | Complementary | terminals description ISO n°1 | (C-B2-B3)CO (A1-A2)CO (25-26-28)OC (15-16-18)OC
25165 | RM4UA33Q | Complementary | output relay state | Tripped if A measured > A set
25166 | RM4UA33Q | Complementary | 9 mm pitches | 2.5
25167 | RM4UA33Q | Complementary | net weight | 0.168 kg
25168 | RM4UA33Q | Complementary | compatibility code | RM4
25169 | RM4UA33Q | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
25170 | RM4UA33Q | Environment | standards | EN/IEC 60255-6
25171 | RM4UA33Q | Environment | product certifications | GL CSA UL
25172 | RM4UA33Q | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
25173 | RM4UA33Q | Environment | ambient air temperature for storage | -40…85 °C
25174 | RM4UA33Q | Environment | ambient air temperature for operation | -20…65 °C
25175 | RM4UA33Q | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
25176 | RM4UA33Q | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
25177 | RM4UA33Q | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
25178 | RM4UA33Q | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
25179 | RM4UA33Q | Environment | pollution degree | 3 conforming to IEC 60664-1
25180 | RM4UA33Q | Environment | dielectric test voltage | 2.5 kV
25181 | RM4UA33Q | Environment | non-dissipating shock wave | 4.8 kV
25182 | RM4UA33Q | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
25183 | RM4UA33Q | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
25184 | RM4UA33Q | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
25185 | RM4UA33Q | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
25186 | RM4UA33Q | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
25187 | RM4UA33Q | Contractual warranty | Warranty | 18 months
25188 | RM4UB34 | Main | range of product | Zelio Control
25189 | RM4UB34 | Main | product or component type | Industrial measurement and control relays
25190 | RM4UB34 | Main | relay type | Voltage control relay
25191 | RM4UB34 | Main | relay name | RM4U
25192 | RM4UB34 | Main | relay monitored parameters | Overvoltage and undervoltage detection Self-powered
25193 | RM4UB34 | Main | time delay range | 0.1...10 s adjustable delay
25194 | RM4UB34 | Main | minimum switching current | 10 mA at 12 V
25195 | RM4UB34 | Main | maximum switching current | 8 A AC at 250 V
25196 | RM4UB34 | Main | electrical connection | 2 conductors cable 1.5 mm² flexible cable with cable end conforming to IEC 60947-1 2 conductors cable 2.5 mm² flexible cable without cable end conforming to IEC 60947-1
25197 | RM4UB34 | Main | contacts type and composition | 2 C/O
25198 | RM4UB34 | Main | poles description | 1P
25199 | RM4UB34 | Complementary | maximum switching voltage | 440 V AC
25200 | RM4UB34 | Complementary | [Us] rated supply voltage | 80...220 V AC/DC
25201 | RM4UB34 | Complementary | supply voltage limits | 60…300 V AC/DC
25202 | RM4UB34 | Complementary | control threshold undervoltage | 80…120 V
25203 | RM4UB34 | Complementary | control threshold overvoltage | 160...220 V
25204 | RM4UB34 | Complementary | output contacts | 2 C/O
25205 | RM4UB34 | Complementary | maximum measuring cycle | 80 ms
25206 | RM4UB34 | Complementary | setting accuracy of the switching threshold | +/-3 %
25207 | RM4UB34 | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range
25208 | RM4UB34 | Complementary | setting accuracy of time delay | 10 P
25209 | RM4UB34 | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range
25210 | RM4UB34 | Complementary | hysteresis | 5 % fixed of de-energisation threshold
25211 | RM4UB34 | Complementary | [Ue] rated operational voltage | >= 60 V
25212 | RM4UB34 | Complementary | maximum permissible voltage | <= 300 V L1 and L3
25213 | RM4UB34 | Complementary | marking | CE : LVD 73/23/EEC CE : EMC 89/336/EEC
25214 | RM4UB34 | Complementary | overvoltage category | III conforming to IEC 60664-1
25215 | RM4UB34 | Complementary | insulation resistance | > 500 MOhm conforming to IEC 60664-1 at 500 V DC
25216 | RM4UB34 | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25217 | RM4UB34 | Complementary | control circuit voltage limits | 0.85...1.1 Uc
25218 | RM4UB34 | Complementary | supply frequency | 50/60 Hz +/- 5 %
25219 | RM4UB34 | Complementary | supply disconnection value | > 0.1 Uc
25220 | RM4UB34 | Complementary | operating position | Any position without derating
25221 | RM4UB34 | Complementary | tightening torque | 0.6…1.1 N.m
25222 | RM4UB34 | Complementary | mechanical durability | 30000000 cycles
25223 | RM4UB34 | Complementary | [Ith] conventional free air thermal current | 8 A
25224 | RM4UB34 | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25225 | RM4UB34 | Complementary | switching voltage | 250 V AC
25226 | RM4UB34 | Complementary | contacts material | 90/10 silver nickel contacts
25227 | RM4UB34 | Complementary | number of cables | 2
25228 | RM4UB34 | Complementary | height | 78 mm
25229 | RM4UB34 | Complementary | width | 22.5 mm
25230 | RM4UB34 | Complementary | depth | 80 mm
25231 | RM4UB34 | Complementary | terminals description ISO n°1 | (15-16-18)OC (L1-L3)CO (25-26-28)OC
25232 | RM4UB34 | Complementary | output relay state | Tripped, fault present
25233 | RM4UB34 | Complementary | 9 mm pitches | 2.5
25234 | RM4UB34 | Complementary | net weight | 0.11 kg
25235 | RM4UB34 | Environment | standards | EN/IEC 60255-6
25236 | RM4UB34 | Environment | product certifications | GL CSA UL
25237 | RM4UB34 | Environment | ambient air temperature for storage | -40…85 °C
25238 | RM4UB34 | Environment | ambient air temperature for operation | -20…65 °C
25239 | RM4UB34 | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
25240 | RM4UB34 | Environment | vibration resistance | 0.35 mm conforming to IEC 60068-2-6 (f = 10…55 Hz)
25241 | RM4UB34 | Environment | shock resistance | 15 gn conforming to IEC 60068-2-27 for 11 ms
25242 | RM4UB34 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
25243 | RM4UB34 | Environment | pollution degree | 3 conforming to IEC 60664-1
25244 | RM4UB34 | Environment | dielectric test voltage | 2.5 kV
25245 | RM4UB34 | Environment | non-dissipating shock wave | 4.8 kV
25246 | RM4UB34 | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
25247 | RM4UB34 | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
25248 | RM4UB34 | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
25249 | RM4UB34 | Environment | protection against electric shocks | 2 kV conforming to IEC 61000-4-5 level 3
25250 | RM4UB34 | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
25251 | RM4UB34 | Contractual warranty | Warranty | 18 months
25252 | RM4UB35 | Main | range of product | Zelio Control
25253 | RM4UB35 | Main | product or component type | Industrial measurement and control relays
25254 | RM4UB35 | Main | relay type | Voltage control relay
25255 | RM4UB35 | Main | relay name | RM4U
25256 | RM4UB35 | Main | relay monitored parameters | Self-powered Overvoltage and undervoltage detection
25257 | RM4UB35 | Main | time delay range | 0.1...10 s adjustable delay
25258 | RM4UB35 | Main | minimum switching current | 10 mA at 12 V
25259 | RM4UB35 | Main | maximum switching current | 8 A AC at 250 V
25260 | RM4UB35 | Main | electrical connection | 2 conductors cable 1.5 mm² flexible cable with cable end conforming to IEC 60947-1 2 conductors cable 2.5 mm² flexible cable without cable end conforming to IEC 60947-1
25261 | RM4UB35 | Main | contacts type and composition | 2 C/O
25262 | RM4UB35 | Main | poles description | 1P
25263 | RM4UB35 | Complementary | maximum switching voltage | 440 V AC
25264 | RM4UB35 | Complementary | [Us] rated supply voltage | 160...300 V AC
25265 | RM4UB35 | Complementary | supply voltage limits | 160…300 V AC
25266 | RM4UB35 | Complementary | control threshold undervoltage | 160…220 V 50/60 Hz
25267 | RM4UB35 | Complementary | control threshold overvoltage | 220...300 V
25268 | RM4UB35 | Complementary | output contacts | 2 C/O
25269 | RM4UB35 | Complementary | maximum measuring cycle | 80 ms
25270 | RM4UB35 | Complementary | setting accuracy of the switching threshold | +/-3 %
25271 | RM4UB35 | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range
25272 | RM4UB35 | Complementary | setting accuracy of time delay | 10 P
25273 | RM4UB35 | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range
25274 | RM4UB35 | Complementary | hysteresis | 5 % fixed of de-energisation threshold
25275 | RM4UB35 | Complementary | [Ue] rated operational voltage | >= 160 V
25276 | RM4UB35 | Complementary | maximum permissible voltage | <= 300 V L1 and L3
25277 | RM4UB35 | Complementary | marking | CE : LVD 73/23/EEC CE : EMC 89/336/EEC
25278 | RM4UB35 | Complementary | overvoltage category | III conforming to IEC 60664-1
25279 | RM4UB35 | Complementary | insulation resistance | > 500 MOhm conforming to IEC 60255-5 at 500 V DC
25280 | RM4UB35 | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25281 | RM4UB35 | Complementary | control circuit voltage limits | 0.85...1.1 Uc
25282 | RM4UB35 | Complementary | supply frequency | 50/60 Hz +/- 5 %
25283 | RM4UB35 | Complementary | supply disconnection value | > 0.1 Uc
25284 | RM4UB35 | Complementary | operating position | Any position without derating
25285 | RM4UB35 | Complementary | tightening torque | 0.6…1.1 N.m
25286 | RM4UB35 | Complementary | mechanical durability | 30000000 cycles
25287 | RM4UB35 | Complementary | [Ith] conventional free air thermal current | 8 A
25288 | RM4UB35 | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25289 | RM4UB35 | Complementary | switching voltage | 250 V AC
25290 | RM4UB35 | Complementary | contacts material | 90/10 silver nickel contacts
25291 | RM4UB35 | Complementary | number of cables | 2
25292 | RM4UB35 | Complementary | height | 78 mm
25293 | RM4UB35 | Complementary | width | 22.5 mm
25294 | RM4UB35 | Complementary | depth | 80 mm
25295 | RM4UB35 | Complementary | terminals description ISO n°1 | (15-16-18)OC
25296 | RM4UB35 | Complementary | output relay state | Tripped, fault present
25297 | RM4UB35 | Complementary | 9 mm pitches | 2.5
25298 | RM4UB35 | Complementary | net weight | 0.11 kg
25299 | RM4UB35 | Environment | standards | EN/IEC 60255-6
25300 | RM4UB35 | Environment | product certifications | UL GL CSA
25301 | RM4UB35 | Environment | ambient air temperature for storage | -40…85 °C
25302 | RM4UB35 | Environment | ambient air temperature for operation | -20…65 °C
25303 | RM4UB35 | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
25304 | RM4UB35 | Environment | vibration resistance | 0.35 mm conforming to IEC 60068-2-6 (f = 10…55 Hz)
25305 | RM4UB35 | Environment | shock resistance | 15 gn conforming to IEC 60068-2-27 for 11 ms
25306 | RM4UB35 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
25307 | RM4UB35 | Environment | pollution degree | 3 conforming to IEC 60664-1
25308 | RM4UB35 | Environment | dielectric test voltage | 2.5 kV
25309 | RM4UB35 | Environment | non-dissipating shock wave | 4.8 kV
25310 | RM4UB35 | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
25311 | RM4UB35 | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
25312 | RM4UB35 | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
25313 | RM4UB35 | Environment | protection against electric shocks | 2 kV conforming to IEC 61000-4-5 level 3
25314 | RM4UB35 | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
25315 | RM4UB35 | Contractual warranty | Warranty | 18 months
25316 | RM4TA02 | Main | range of product | Zelio Control
25317 | RM4TA02 | Main | product or component type | Industrial measurement and control relays
25318 | RM4TA02 | Main | relay type | Control relay
25319 | RM4TA02 | Main | product specific application | For 3-phase supply
25320 | RM4TA02 | Main | relay name | RM4-T
25321 | RM4TA02 | Main | relay monitored parameters | Phase failure detection Phase sequence Asymmetry
25322 | RM4TA02 | Main | time delay | Fixed 0.5 s
25323 | RM4TA02 | Main | measurement range | 290...484 V
25324 | RM4TA02 | Main | contacts type and composition | 1 C/O
25325 | RM4TA02 | Main | poles description | 3P
25326 | RM4TA02 | Complementary | maximum switching voltage | 440 V AC
25327 | RM4TA02 | Complementary | output contacts | 1 C/O
25328 | RM4TA02 | Complementary | setting accuracy of the switching threshold | +/-3 %
25329 | RM4TA02 | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range
25330 | RM4TA02 | Complementary | setting accuracy of time delay | 10 P
25331 | RM4TA02 | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range
25332 | RM4TA02 | Complementary | hysteresis | 50 % fixed of asymmetry percentage
25333 | RM4TA02 | Complementary | delay at power up | 650 ms
25334 | RM4TA02 | Complementary | maximum measuring cycle | 80 ms
25335 | RM4TA02 | Complementary | adjustment of asymmetry threshold | 5...15 %
25336 | RM4TA02 | Complementary | marking | CE
25337 | RM4TA02 | Complementary | overvoltage category | III conforming to IEC 60664-1
25338 | RM4TA02 | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25339 | RM4TA02 | Complementary | supply frequency | 50/60 Hz +/- 5 %
25340 | RM4TA02 | Complementary | operating position | Any position without derating
25341 | RM4TA02 | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
25342 | RM4TA02 | Complementary | tightening torque | 0.6…1.1 N.m
25343 | RM4TA02 | Complementary | mechanical durability | 30000000 cycles
25344 | RM4TA02 | Complementary | [Ith] conventional free air thermal current | 8 A
25345 | RM4TA02 | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25346 | RM4TA02 | Complementary | switching capacity in mA | 10 mA at 12 V
25347 | RM4TA02 | Complementary | switching voltage | 250 V AC
25348 | RM4TA02 | Complementary | contacts material | 90/10 silver nickel contacts
25349 | RM4TA02 | Complementary | number of cables | 2
25350 | RM4TA02 | Complementary | height | 78 mm
25351 | RM4TA02 | Complementary | width | 22.5 mm
25352 | RM4TA02 | Complementary | depth | 80 mm
25353 | RM4TA02 | Complementary | terminals description ISO n°1 | (15-16-18)OC (L1-L2-L3)CO
25354 | RM4TA02 | Complementary | output relay state | Tripped, fault present
25355 | RM4TA02 | Complementary | 9 mm pitches | 2.5
25356 | RM4TA02 | Complementary | net weight | 0.11 kg
25357 | RM4TA02 | Complementary | time delay on de-energisation | 0.5 s
25358 | RM4TA02 | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3
25359 | RM4TA02 | Environment | standards | EN/IEC 60255-6
25360 | RM4TA02 | Environment | product certifications | UL CSA GL
25361 | RM4TA02 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
25362 | RM4TA02 | Environment | ambient air temperature for storage | -40…85 °C
25363 | RM4TA02 | Environment | ambient air temperature for operation | -20…65 °C
25364 | RM4TA02 | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
25365 | RM4TA02 | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
25366 | RM4TA02 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
25367 | RM4TA02 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
25368 | RM4TA02 | Environment | pollution degree | 3 conforming to IEC 60664-1
25369 | RM4TA02 | Environment | dielectric test voltage | 2.5 kV
25370 | RM4TA02 | Environment | non-dissipating shock wave | 4.8 kV
25371 | RM4TA02 | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
25372 | RM4TA02 | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
25373 | RM4TA02 | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
25374 | RM4TA02 | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
25375 | RM4TA02 | Contractual warranty | Warranty | 18 months
25376 | RM4TA32 | Main | range of product | Zelio Control
25377 | RM4TA32 | Main | product or component type | Industrial measurement and control relays
25378 | RM4TA32 | Main | relay type | Control relay
25379 | RM4TA32 | Main | product specific application | For 3-phase supply
25380 | RM4TA32 | Main | relay name | RM4-T
25381 | RM4TA32 | Main | relay monitored parameters | Phase sequence Phase failure detection Asymmetry
25382 | RM4TA32 | Main | time delay | Adjustable 0.1...10 s
25383 | RM4TA32 | Main | measurement range | 290...484 V
25384 | RM4TA32 | Main | contacts type and composition | 2 C/O
25385 | RM4TA32 | Main | poles description | 3P
25386 | RM4TA32 | Complementary | maximum switching voltage | 440 V AC
25387 | RM4TA32 | Complementary | output contacts | 2 C/O
25388 | RM4TA32 | Complementary | setting accuracy of the switching threshold | +/-3 %
25389 | RM4TA32 | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range
25390 | RM4TA32 | Complementary | setting accuracy of time delay | 10 P
25391 | RM4TA32 | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range
25392 | RM4TA32 | Complementary | hysteresis | 50 % fixed of asymmetry percentage
25393 | RM4TA32 | Complementary | delay at power up | 650 ms
25394 | RM4TA32 | Complementary | maximum measuring cycle | 80 ms
25395 | RM4TA32 | Complementary | adjustment of asymmetry threshold | 5...15 %
25396 | RM4TA32 | Complementary | marking | CE
25397 | RM4TA32 | Complementary | overvoltage category | III conforming to IEC 60664-1
25398 | RM4TA32 | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25399 | RM4TA32 | Complementary | supply frequency | 50/60 Hz +/- 5 %
25400 | RM4TA32 | Complementary | operating position | Any position without derating
25401 | RM4TA32 | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
25402 | RM4TA32 | Complementary | tightening torque | 0.6…1.1 N.m
25403 | RM4TA32 | Complementary | mechanical durability | 30000000 cycles
25404 | RM4TA32 | Complementary | [Ith] conventional free air thermal current | 8 A
25405 | RM4TA32 | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25406 | RM4TA32 | Complementary | switching capacity in mA | 10 mA at 12 V
25407 | RM4TA32 | Complementary | switching voltage | 250 V AC
25408 | RM4TA32 | Complementary | contacts material | 90/10 silver nickel contacts
25409 | RM4TA32 | Complementary | number of cables | 2
25410 | RM4TA32 | Complementary | height | 78 mm
25411 | RM4TA32 | Complementary | width | 22.5 mm
25412 | RM4TA32 | Complementary | depth | 80 mm
25413 | RM4TA32 | Complementary | terminals description ISO n°1 | (25-26-28)OC (L1-L2-L3)CO (15-16-18)OC
25414 | RM4TA32 | Complementary | output relay state | Tripped, fault present
25415 | RM4TA32 | Complementary | 9 mm pitches | 2.5
25416 | RM4TA32 | Complementary | net weight | 0.11 kg
25417 | RM4TA32 | Complementary | time delay on de-energisation | 0.1…10 s
25418 | RM4TA32 | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3
25419 | RM4TA32 | Environment | standards | EN/IEC 60255-6
25420 | RM4TA32 | Environment | product certifications | UL CSA GL
25421 | RM4TA32 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
25422 | RM4TA32 | Environment | ambient air temperature for storage | -40…85 °C
25423 | RM4TA32 | Environment | ambient air temperature for operation | -20…65 °C
25424 | RM4TA32 | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
25425 | RM4TA32 | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
25426 | RM4TA32 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
25427 | RM4TA32 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
25428 | RM4TA32 | Environment | pollution degree | 3 conforming to IEC 60664-1
25429 | RM4TA32 | Environment | dielectric test voltage | 2.5 kV
25430 | RM4TA32 | Environment | non-dissipating shock wave | 4.8 kV
25431 | RM4TA32 | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
25432 | RM4TA32 | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
25433 | RM4TA32 | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
25434 | RM4TA32 | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
25435 | RM4TA32 | Contractual warranty | Warranty | 18 months
25436 | RM4TA01 | Main | range of product | Zelio Control
25437 | RM4TA01 | Main | product or component type | Industrial measurement and control relays
25438 | RM4TA01 | Main | relay type | Control relay
25439 | RM4TA01 | Main | product specific application | For 3-phase supply
25440 | RM4TA01 | Main | relay name | RM4-T
25441 | RM4TA01 | Main | relay monitored parameters | Phase sequence Phase failure detection Asymmetry
25442 | RM4TA01 | Main | time delay | Fixed 0.5 s
25443 | RM4TA01 | Main | measurement range | 160...300 V
25444 | RM4TA01 | Main | contacts type and composition | 1 C/O
25445 | RM4TA01 | Main | poles description | 3P
25446 | RM4TA01 | Complementary | maximum switching voltage | 440 V AC
25447 | RM4TA01 | Complementary | output contacts | 1 C/O
25448 | RM4TA01 | Complementary | setting accuracy of the switching threshold | +/-3 %
25449 | RM4TA01 | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range
25450 | RM4TA01 | Complementary | setting accuracy of time delay | 10 P
25451 | RM4TA01 | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range
25452 | RM4TA01 | Complementary | hysteresis | 50 % fixed of asymmetry percentage
25453 | RM4TA01 | Complementary | delay at power up | 650 ms
25454 | RM4TA01 | Complementary | maximum measuring cycle | 80 ms
25455 | RM4TA01 | Complementary | adjustment of asymmetry threshold | 5...15 %
25456 | RM4TA01 | Complementary | marking | CE
25457 | RM4TA01 | Complementary | overvoltage category | III conforming to IEC 60664-1
25458 | RM4TA01 | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25459 | RM4TA01 | Complementary | supply frequency | 50/60 Hz +/- 5 %
25460 | RM4TA01 | Complementary | operating position | Any position without derating
25461 | RM4TA01 | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
25462 | RM4TA01 | Complementary | tightening torque | 0.6…1.1 N.m
25463 | RM4TA01 | Complementary | mechanical durability | 30000000 cycles
25464 | RM4TA01 | Complementary | [Ith] conventional free air thermal current | 8 A
25465 | RM4TA01 | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25466 | RM4TA01 | Complementary | switching capacity in mA | 10 mA at 12 V
25467 | RM4TA01 | Complementary | switching voltage | 250 V AC
25468 | RM4TA01 | Complementary | contacts material | 90/10 silver nickel contacts
25469 | RM4TA01 | Complementary | number of cables | 2
25470 | RM4TA01 | Complementary | height | 78 mm
25471 | RM4TA01 | Complementary | width | 22.5 mm
25472 | RM4TA01 | Complementary | depth | 80 mm
25473 | RM4TA01 | Complementary | terminals description ISO n°1 | (15-16-18)OC (L1-L2-L3)CO
25474 | RM4TA01 | Complementary | output relay state | Tripped, fault present
25475 | RM4TA01 | Complementary | 9 mm pitches | 2.5
25476 | RM4TA01 | Complementary | net weight | 0.11 kg
25477 | RM4TA01 | Complementary | time delay on de-energisation | 0.5 s
25478 | RM4TA01 | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3
25479 | RM4TA01 | Environment | standards | EN/IEC 60255-6
25480 | RM4TA01 | Environment | product certifications | CSA UL GL
25481 | RM4TA01 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
25482 | RM4TA01 | Environment | ambient air temperature for storage | -40…85 °C
25483 | RM4TA01 | Environment | ambient air temperature for operation | -20…65 °C
25484 | RM4TA01 | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
25485 | RM4TA01 | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
25486 | RM4TA01 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
25487 | RM4TA01 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
25488 | RM4TA01 | Environment | pollution degree | 3 conforming to IEC 60664-1
25489 | RM4TA01 | Environment | dielectric test voltage | 2.5 kV
25490 | RM4TA01 | Environment | non-dissipating shock wave | 4.8 kV
25491 | RM4TA01 | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
25492 | RM4TA01 | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
25493 | RM4TA01 | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
25494 | RM4TA01 | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
25495 | RM4TA01 | Contractual warranty | Warranty | 18 months
25496 | RM4TA31 | Main | range of product | Zelio Control
25497 | RM4TA31 | Main | product or component type | Industrial measurement and control relays
25498 | RM4TA31 | Main | relay type | Control relay
25499 | RM4TA31 | Main | product specific application | For 3-phase supply
25500 | RM4TA31 | Main | relay name | RM4-T
25501 | RM4TA31 | Main | relay monitored parameters | Phase sequence Phase failure detection Asymmetry
25502 | RM4TA31 | Main | time delay | Adjustable 0.1...10 s
25503 | RM4TA31 | Main | measurement range | 160...300 V
25504 | RM4TA31 | Main | contacts type and composition | 2 C/O
25505 | RM4TA31 | Main | poles description | 3P
25506 | RM4TA31 | Complementary | maximum switching voltage | 440 V AC
25507 | RM4TA31 | Complementary | output contacts | 2 C/O
25508 | RM4TA31 | Complementary | setting accuracy of the switching threshold | +/-3 %
25509 | RM4TA31 | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range
25510 | RM4TA31 | Complementary | setting accuracy of time delay | 10 P
25511 | RM4TA31 | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range
25512 | RM4TA31 | Complementary | hysteresis | 50 % fixed of asymmetry percentage
25513 | RM4TA31 | Complementary | delay at power up | 650 ms
25514 | RM4TA31 | Complementary | maximum measuring cycle | 80 ms
25515 | RM4TA31 | Complementary | adjustment of asymmetry threshold | 5...15 %
25516 | RM4TA31 | Complementary | marking | CE
25517 | RM4TA31 | Complementary | overvoltage category | III conforming to IEC 60664-1
25518 | RM4TA31 | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25519 | RM4TA31 | Complementary | supply frequency | 50/60 Hz +/- 5 %
25520 | RM4TA31 | Complementary | operating position | Any position without derating
25521 | RM4TA31 | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
25522 | RM4TA31 | Complementary | tightening torque | 0.6…1.1 N.m
25523 | RM4TA31 | Complementary | mechanical durability | 30000000 cycles
25524 | RM4TA31 | Complementary | [Ith] conventional free air thermal current | 8 A
25525 | RM4TA31 | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25526 | RM4TA31 | Complementary | switching capacity in mA | 10 mA at 12 V
25527 | RM4TA31 | Complementary | switching voltage | 250 V AC
25528 | RM4TA31 | Complementary | contacts material | 90/10 silver nickel contacts
25529 | RM4TA31 | Complementary | number of cables | 2
25530 | RM4TA31 | Complementary | height | 78 mm
25531 | RM4TA31 | Complementary | width | 22.5 mm
25532 | RM4TA31 | Complementary | depth | 80 mm
25533 | RM4TA31 | Complementary | terminals description ISO n°1 | (25-26-28)OC (15-16-18)OC (L1-L2-L3)CO
25534 | RM4TA31 | Complementary | output relay state | Tripped, fault present
25535 | RM4TA31 | Complementary | 9 mm pitches | 2.5
25536 | RM4TA31 | Complementary | net weight | 0.11 kg
25537 | RM4TA31 | Complementary | time delay on de-energisation | 0.1…10 s
25538 | RM4TA31 | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3
25539 | RM4TA31 | Environment | standards | EN/IEC 60255-6
25540 | RM4TA31 | Environment | product certifications | GL CSA UL
25541 | RM4TA31 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
25542 | RM4TA31 | Environment | ambient air temperature for storage | -40…85 °C
25543 | RM4TA31 | Environment | ambient air temperature for operation | -20…65 °C
25544 | RM4TA31 | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
25545 | RM4TA31 | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
25546 | RM4TA31 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
25547 | RM4TA31 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
25548 | RM4TA31 | Environment | pollution degree | 3 conforming to IEC 60664-1
25549 | RM4TA31 | Environment | dielectric test voltage | 2.5 kV
25550 | RM4TA31 | Environment | non-dissipating shock wave | 4.8 kV
25551 | RM4TA31 | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
25552 | RM4TA31 | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
25553 | RM4TA31 | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
25554 | RM4TA31 | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
25555 | RM4TA31 | Contractual warranty | Warranty | 18 months
25556 | RM4TG20 | Main | range of product | Zelio Control
25557 | RM4TG20 | Main | product or component type | Industrial measurement and control relays
25558 | RM4TG20 | Main | relay type | Control relay
25559 | RM4TG20 | Main | product specific application | For 3-phase supply
25560 | RM4TG20 | Main | relay name | RM4-T
25561 | RM4TG20 | Main | relay monitored parameters | Phase failure detection Phase sequence
25562 | RM4TG20 | Main | time delay | Without
25563 | RM4TG20 | Main | measurement range | 198...484 V
25564 | RM4TG20 | Main | contacts type and composition | 2 C/O
25565 | RM4TG20 | Main | poles description | 3P
25566 | RM4TG20 | Complementary | maximum switching voltage | 440 V AC
25567 | RM4TG20 | Complementary | output contacts | 2 C/O
25568 | RM4TG20 | Complementary | setting accuracy of time delay | 10 P
25569 | RM4TG20 | Complementary | delay at power up | 650 ms
25570 | RM4TG20 | Complementary | maximum measuring cycle | 80 ms
25571 | RM4TG20 | Complementary | marking | CE
25572 | RM4TG20 | Complementary | overvoltage category | III conforming to IEC 60664-1
25573 | RM4TG20 | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25574 | RM4TG20 | Complementary | supply frequency | 50/60 Hz +/- 5 %
25575 | RM4TG20 | Complementary | operating position | Any position without derating
25576 | RM4TG20 | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
25577 | RM4TG20 | Complementary | tightening torque | 0.6…1.1 N.m
25578 | RM4TG20 | Complementary | mechanical durability | 30000000 cycles
25579 | RM4TG20 | Complementary | [Ith] conventional free air thermal current | 8 A
25580 | RM4TG20 | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25581 | RM4TG20 | Complementary | switching capacity in mA | 10 mA at 12 V
25582 | RM4TG20 | Complementary | switching voltage | 250 V AC
25583 | RM4TG20 | Complementary | contacts material | 90/10 silver nickel contacts
25584 | RM4TG20 | Complementary | number of cables | 2
25585 | RM4TG20 | Complementary | height | 78 mm
25586 | RM4TG20 | Complementary | width | 22.5 mm
25587 | RM4TG20 | Complementary | depth | 80 mm
25588 | RM4TG20 | Complementary | terminals description ISO n°1 | (L1-L2-L3)CO (15-16-18)OC (25-26-28)OC ALT
25589 | RM4TG20 | Complementary | output relay state | Tripped, fault present
25590 | RM4TG20 | Complementary | 9 mm pitches | 2.5
25591 | RM4TG20 | Complementary | net weight | 0.11 kg
25592 | RM4TG20 | Complementary | terminals description ISO n°2 | (11-12-14)OC ALT (L1-L2-L3)CO (21-22-24)OC
25593 | RM4TG20 | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3
25594 | RM4TG20 | Environment | standards | EN/IEC 60255-6
25595 | RM4TG20 | Environment | product certifications | GL UL CSA
25596 | RM4TG20 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
25597 | RM4TG20 | Environment | ambient air temperature for storage | -40…85 °C
25598 | RM4TG20 | Environment | ambient air temperature for operation | -20…65 °C
25599 | RM4TG20 | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
25600 | RM4TG20 | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
25601 | RM4TG20 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
25602 | RM4TG20 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
25603 | RM4TG20 | Environment | pollution degree | 3 conforming to IEC 60664-1
25604 | RM4TG20 | Environment | dielectric test voltage | 2.5 kV
25605 | RM4TG20 | Environment | non-dissipating shock wave | 4.8 kV
25606 | RM4TG20 | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
25607 | RM4TG20 | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
25608 | RM4TG20 | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
25609 | RM4TG20 | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
25610 | RM4TG20 | Packing Units | Package 1 Weight | 0.131 kg
25611 | RM4TG20 | Contractual warranty | Warranty | 18 months
25612 | RM4TR31 | Main | range of product | Zelio Control
25613 | RM4TR31 | Main | product or component type | Industrial measurement and control relays
25614 | RM4TR31 | Main | relay type | Control relay
25615 | RM4TR31 | Main | product specific application | For 3-phase supply
25616 | RM4TR31 | Main | relay name | RM4-T
25617 | RM4TR31 | Main | relay monitored parameters | Overvoltage and undervoltage detection Phase sequence Phase failure detection
25618 | RM4TR31 | Main | time delay | Adjustable 0.1...10 s
25619 | RM4TR31 | Main | measurement range | 160...300 V
25620 | RM4TR31 | Main | contacts type and composition | 2 C/O
25621 | RM4TR31 | Main | poles description | 3P
25622 | RM4TR31 | Complementary | maximum switching voltage | 440 V AC
25623 | RM4TR31 | Complementary | control threshold undervoltage | 160…220 V
25624 | RM4TR31 | Complementary | control threshold overvoltage | 220...300 V
25625 | RM4TR31 | Complementary | output contacts | 2 C/O
25626 | RM4TR31 | Complementary | setting accuracy of the switching threshold | +/-3 %
25627 | RM4TR31 | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range
25628 | RM4TR31 | Complementary | setting accuracy of time delay | 10 P
25629 | RM4TR31 | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range
25630 | RM4TR31 | Complementary | hysteresis | 5 % fixed of de-energisation threshold
25631 | RM4TR31 | Complementary | delay at power up | 650 ms
25632 | RM4TR31 | Complementary | maximum measuring cycle | 80 ms
25633 | RM4TR31 | Complementary | marking | CE
25634 | RM4TR31 | Complementary | overvoltage category | III conforming to IEC 60664-1
25635 | RM4TR31 | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25636 | RM4TR31 | Complementary | supply frequency | 50/60 Hz +/- 5 %
25637 | RM4TR31 | Complementary | operating position | Any position without derating
25638 | RM4TR31 | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
25639 | RM4TR31 | Complementary | tightening torque | 0.6…1.1 N.m
25640 | RM4TR31 | Complementary | mechanical durability | 30000000 cycles
25641 | RM4TR31 | Complementary | [Ith] conventional free air thermal current | 8 A
25642 | RM4TR31 | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25643 | RM4TR31 | Complementary | switching capacity in mA | 10 mA at 12 V
25644 | RM4TR31 | Complementary | switching voltage | 250 V AC
25645 | RM4TR31 | Complementary | contacts material | 90/10 silver nickel contacts
25646 | RM4TR31 | Complementary | number of cables | 2
25647 | RM4TR31 | Complementary | height | 78 mm
25648 | RM4TR31 | Complementary | width | 22.5 mm
25649 | RM4TR31 | Complementary | depth | 80 mm
25650 | RM4TR31 | Complementary | terminals description ISO n°1 | (25-26-28)OC (L1-L2-L3)CO (15-16-18)OC
25651 | RM4TR31 | Complementary | output relay state | Tripped, fault present
25652 | RM4TR31 | Complementary | 9 mm pitches | 2.5
25653 | RM4TR31 | Complementary | net weight | 0.11 kg
25654 | RM4TR31 | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3
25655 | RM4TR31 | Environment | standards | EN/IEC 60255-6
25656 | RM4TR31 | Environment | product certifications | UL GL CSA
25657 | RM4TR31 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
25658 | RM4TR31 | Environment | ambient air temperature for storage | -40…85 °C
25659 | RM4TR31 | Environment | ambient air temperature for operation | -20…65 °C
25660 | RM4TR31 | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
25661 | RM4TR31 | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
25662 | RM4TR31 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
25663 | RM4TR31 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
25664 | RM4TR31 | Environment | pollution degree | 3 conforming to IEC 60664-1
25665 | RM4TR31 | Environment | dielectric test voltage | 2.5 kV
25666 | RM4TR31 | Environment | non-dissipating shock wave | 4.8 kV
25667 | RM4TR31 | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
25668 | RM4TR31 | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
25669 | RM4TR31 | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
25670 | RM4TR31 | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
25671 | RM4TR31 | Contractual warranty | Warranty | 18 months
25672 | RM4TR33 | Main | range of product | Zelio Control
25673 | RM4TR33 | Main | product or component type | Industrial measurement and control relays
25674 | RM4TR33 | Main | relay type | Control relay
25675 | RM4TR33 | Main | product specific application | For 3-phase supply
25676 | RM4TR33 | Main | relay name | RM4-T
25677 | RM4TR33 | Main | relay monitored parameters | Overvoltage and undervoltage detection Phase failure detection Phase sequence
25678 | RM4TR33 | Main | time delay | Adjustable 0.1...10 s
25679 | RM4TR33 | Main | measurement range | 160...300 V
25680 | RM4TR33 | Main | contacts type and composition | 2 C/O
25681 | RM4TR33 | Main | poles description | 3P
25682 | RM4TR33 | Complementary | maximum switching voltage | 440 V AC
25683 | RM4TR33 | Complementary | control threshold undervoltage | 198 V
25684 | RM4TR33 | Complementary | control threshold overvoltage | 242 V
25685 | RM4TR33 | Complementary | output contacts | 2 C/O
25686 | RM4TR33 | Complementary | setting accuracy of the switching threshold | +/-3 %
25687 | RM4TR33 | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range
25688 | RM4TR33 | Complementary | setting accuracy of time delay | 10 P
25689 | RM4TR33 | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range
25690 | RM4TR33 | Complementary | hysteresis | 5 % fixed of de-energisation threshold
25691 | RM4TR33 | Complementary | delay at power up | 650 ms
25692 | RM4TR33 | Complementary | maximum measuring cycle | 80 ms
25693 | RM4TR33 | Complementary | marking | CE
25694 | RM4TR33 | Complementary | overvoltage category | III conforming to IEC 60664-1
25695 | RM4TR33 | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25696 | RM4TR33 | Complementary | supply frequency | 50/60 Hz +/- 5 %
25697 | RM4TR33 | Complementary | operating position | Any position without derating
25698 | RM4TR33 | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
25699 | RM4TR33 | Complementary | tightening torque | 0.6…1.1 N.m
25700 | RM4TR33 | Complementary | mechanical durability | 30000000 cycles
25701 | RM4TR33 | Complementary | [Ith] conventional free air thermal current | 8 A
25702 | RM4TR33 | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25703 | RM4TR33 | Complementary | switching capacity in mA | 10 mA at 12 V
25704 | RM4TR33 | Complementary | switching voltage | 250 V AC
25705 | RM4TR33 | Complementary | contacts material | 90/10 silver nickel contacts
25706 | RM4TR33 | Complementary | number of cables | 2
25707 | RM4TR33 | Complementary | height | 78 mm
25708 | RM4TR33 | Complementary | width | 22.5 mm
25709 | RM4TR33 | Complementary | depth | 80 mm
25710 | RM4TR33 | Complementary | terminals description ISO n°1 | (25-26-28)OC (15-16-18)OC (L1-L2-L3)CO
25711 | RM4TR33 | Complementary | output relay state | Tripped, fault present
25712 | RM4TR33 | Complementary | 9 mm pitches | 2.5
25713 | RM4TR33 | Complementary | net weight | 0.11 kg
25714 | RM4TR33 | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3
25715 | RM4TR33 | Environment | standards | EN/IEC 60255-6
25716 | RM4TR33 | Environment | product certifications | CSA UL GL
25717 | RM4TR33 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
25718 | RM4TR33 | Environment | ambient air temperature for storage | -40…85 °C
25719 | RM4TR33 | Environment | ambient air temperature for operation | -20…65 °C
25720 | RM4TR33 | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
25721 | RM4TR33 | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
25722 | RM4TR33 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
25723 | RM4TR33 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
25724 | RM4TR33 | Environment | pollution degree | 3 conforming to IEC 60664-1
25725 | RM4TR33 | Environment | dielectric test voltage | 2.5 kV
25726 | RM4TR33 | Environment | non-dissipating shock wave | 4.8 kV
25727 | RM4TR33 | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
25728 | RM4TR33 | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
25729 | RM4TR33 | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
25730 | RM4TR33 | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
25731 | RM4TR33 | Contractual warranty | Warranty | 18 months
25732 | RM4TR32 | Main | range of product | Zelio Control
25733 | RM4TR32 | Main | product or component type | Industrial measurement and control relays
25734 | RM4TR32 | Main | relay type | Control relay
25735 | RM4TR32 | Main | product specific application | For 3-phase supply
25736 | RM4TR32 | Main | relay name | RM4-T
25737 | RM4TR32 | Main | relay monitored parameters | Phase failure detection Phase sequence Overvoltage and undervoltage detection
25738 | RM4TR32 | Main | time delay | Adjustable 0.1...10 s
25739 | RM4TR32 | Main | measurement range | 290...484 V
25740 | RM4TR32 | Main | contacts type and composition | 2 C/O
25741 | RM4TR32 | Main | poles description | 3P
25742 | RM4TR32 | Complementary | maximum switching voltage | 440 V AC
25743 | RM4TR32 | Complementary | control threshold undervoltage | 300…430 V
25744 | RM4TR32 | Complementary | control threshold overvoltage | 420...480 V
25745 | RM4TR32 | Complementary | output contacts | 2 C/O
25746 | RM4TR32 | Complementary | setting accuracy of the switching threshold | +/-3 %
25747 | RM4TR32 | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range
25748 | RM4TR32 | Complementary | setting accuracy of time delay | 10 P
25749 | RM4TR32 | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range
25750 | RM4TR32 | Complementary | hysteresis | 5 % fixed of de-energisation threshold
25751 | RM4TR32 | Complementary | delay at power up | 650 ms
25752 | RM4TR32 | Complementary | maximum measuring cycle | 80 ms
25753 | RM4TR32 | Complementary | marking | CE
25754 | RM4TR32 | Complementary | overvoltage category | III conforming to IEC 60664-1
25755 | RM4TR32 | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25756 | RM4TR32 | Complementary | supply frequency | 50/60 Hz +/- 5 %
25757 | RM4TR32 | Complementary | operating position | Any position without derating
25758 | RM4TR32 | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
25759 | RM4TR32 | Complementary | tightening torque | 0.6…1.1 N.m
25760 | RM4TR32 | Complementary | mechanical durability | 30000000 cycles
25761 | RM4TR32 | Complementary | [Ith] conventional free air thermal current | 8 A
25762 | RM4TR32 | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25763 | RM4TR32 | Complementary | switching capacity in mA | 10 mA at 12 V
25764 | RM4TR32 | Complementary | switching voltage | 250 V AC
25765 | RM4TR32 | Complementary | contacts material | 90/10 silver nickel contacts
25766 | RM4TR32 | Complementary | number of cables | 2
25767 | RM4TR32 | Complementary | height | 78 mm
25768 | RM4TR32 | Complementary | width | 22.5 mm
25769 | RM4TR32 | Complementary | depth | 80 mm
25770 | RM4TR32 | Complementary | terminals description ISO n°1 | (15-16-18)OC (L1-L2-L3)CO (25-26-28)OC
25771 | RM4TR32 | Complementary | output relay state | Tripped, fault present
25772 | RM4TR32 | Complementary | 9 mm pitches | 2.5
25773 | RM4TR32 | Complementary | net weight | 0.11 kg
25774 | RM4TR32 | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3
25775 | RM4TR32 | Environment | standards | EN/IEC 60255-6
25776 | RM4TR32 | Environment | product certifications | CSA GL UL
25777 | RM4TR32 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
25778 | RM4TR32 | Environment | ambient air temperature for storage | -40…85 °C
25779 | RM4TR32 | Environment | ambient air temperature for operation | -20…65 °C
25780 | RM4TR32 | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
25781 | RM4TR32 | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
25782 | RM4TR32 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
25783 | RM4TR32 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
25784 | RM4TR32 | Environment | pollution degree | 3 conforming to IEC 60664-1
25785 | RM4TR32 | Environment | dielectric test voltage | 2.5 kV
25786 | RM4TR32 | Environment | non-dissipating shock wave | 4.8 kV
25787 | RM4TR32 | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
25788 | RM4TR32 | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
25789 | RM4TR32 | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
25790 | RM4TR32 | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
25791 | RM4TR32 | Contractual warranty | Warranty | 18 months
25792 | RM4TR34 | Main | range of product | Zelio Control
25793 | RM4TR34 | Main | product or component type | Industrial measurement and control relays
25794 | RM4TR34 | Main | relay type | Control relay
25795 | RM4TR34 | Main | product specific application | For 3-phase supply
25796 | RM4TR34 | Main | relay name | RM4-T
25797 | RM4TR34 | Main | relay monitored parameters | Phase failure detection Overvoltage and undervoltage detection Phase sequence
25798 | RM4TR34 | Main | time delay | Adjustable 0.1...10 s
25799 | RM4TR34 | Main | measurement range | 290...484 V
25800 | RM4TR34 | Main | contacts type and composition | 2 C/O
25801 | RM4TR34 | Main | poles description | 3P
25802 | RM4TR34 | Complementary | maximum switching voltage | 440 V AC
25803 | RM4TR34 | Complementary | control threshold overvoltage | 440 V
25804 | RM4TR34 | Complementary | output contacts | 2 C/O
25805 | RM4TR34 | Complementary | setting accuracy of the switching threshold | +/-3 %
25806 | RM4TR34 | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range
25807 | RM4TR34 | Complementary | setting accuracy of time delay | 10 P
25808 | RM4TR34 | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range
25809 | RM4TR34 | Complementary | hysteresis | 5 % fixed of de-energisation threshold
25810 | RM4TR34 | Complementary | delay at power up | 650 ms
25811 | RM4TR34 | Complementary | maximum measuring cycle | 80 ms
25812 | RM4TR34 | Complementary | marking | CE
25813 | RM4TR34 | Complementary | overvoltage category | III conforming to IEC 60664-1
25814 | RM4TR34 | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25815 | RM4TR34 | Complementary | supply frequency | 50/60 Hz +/- 5 %
25816 | RM4TR34 | Complementary | operating position | Any position without derating
25817 | RM4TR34 | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
25818 | RM4TR34 | Complementary | tightening torque | 0.6…1.1 N.m
25819 | RM4TR34 | Complementary | mechanical durability | 30000000 cycles
25820 | RM4TR34 | Complementary | [Ith] conventional free air thermal current | 8 A
25821 | RM4TR34 | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25822 | RM4TR34 | Complementary | switching capacity in mA | 10 mA at 12 V
25823 | RM4TR34 | Complementary | switching voltage | 250 V AC
25824 | RM4TR34 | Complementary | contacts material | 90/10 silver nickel contacts
25825 | RM4TR34 | Complementary | number of cables | 2
25826 | RM4TR34 | Complementary | height | 78 mm
25827 | RM4TR34 | Complementary | width | 22.5 mm
25828 | RM4TR34 | Complementary | depth | 80 mm
25829 | RM4TR34 | Complementary | terminals description ISO n°1 | (15-16-18)OC (25-26-28)OC (L1-L2-L3)CO
25830 | RM4TR34 | Complementary | output relay state | Tripped, fault present
25831 | RM4TR34 | Complementary | 9 mm pitches | 2.5
25832 | RM4TR34 | Complementary | net weight | 0.11 kg
25833 | RM4TR34 | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3
25834 | RM4TR34 | Environment | standards | EN/IEC 60255-6
25835 | RM4TR34 | Environment | product certifications | UL GL CSA
25836 | RM4TR34 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
25837 | RM4TR34 | Environment | ambient air temperature for storage | -40…85 °C
25838 | RM4TR34 | Environment | ambient air temperature for operation | -20…65 °C
25839 | RM4TR34 | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
25840 | RM4TR34 | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
25841 | RM4TR34 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
25842 | RM4TR34 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
25843 | RM4TR34 | Environment | pollution degree | 3 conforming to IEC 60664-1
25844 | RM4TR34 | Environment | dielectric test voltage | 2.5 kV
25845 | RM4TR34 | Environment | non-dissipating shock wave | 4.8 kV
25846 | RM4TR34 | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
25847 | RM4TR34 | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
25848 | RM4TR34 | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
25849 | RM4TR34 | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
25850 | RM4TR34 | Contractual warranty | Warranty | 18 months
25851 | RM4TR35 | Main | range of product | Zelio Control
25852 | RM4TR35 | Main | product or component type | Industrial measurement and control relays
25853 | RM4TR35 | Main | relay type | Control relay
25854 | RM4TR35 | Main | product specific application | For 3-phase supply
25855 | RM4TR35 | Main | relay name | RM4-T
25856 | RM4TR35 | Main | relay monitored parameters | Phase failure detection Phase sequence Overvoltage and undervoltage detection
25857 | RM4TR35 | Main | time delay | Adjustable 0.1...10 s
25858 | RM4TR35 | Main | contacts type and composition | 2 C/O
25859 | RM4TR35 | Main | poles description | 3P
25860 | RM4TR35 | Complementary | maximum switching voltage | 440 V AC
25861 | RM4TR35 | Complementary | output contacts | 2 C/O
25862 | RM4TR35 | Complementary | setting accuracy of the switching threshold | +/-3 %
25863 | RM4TR35 | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range
25864 | RM4TR35 | Complementary | setting accuracy of time delay | 10 P
25865 | RM4TR35 | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range
25866 | RM4TR35 | Complementary | hysteresis | 5 % fixed of de-energisation threshold
25867 | RM4TR35 | Complementary | delay at power up | 650 ms
25868 | RM4TR35 | Complementary | maximum measuring cycle | 80 ms
25869 | RM4TR35 | Complementary | marking | CE
25870 | RM4TR35 | Complementary | overvoltage category | III conforming to IEC 60664-1
25871 | RM4TR35 | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25872 | RM4TR35 | Complementary | supply frequency | 50/60 Hz +/- 5 %
25873 | RM4TR35 | Complementary | operating position | Any position without derating
25874 | RM4TR35 | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
25875 | RM4TR35 | Complementary | tightening torque | 0.6…1.1 N.m
25876 | RM4TR35 | Complementary | mechanical durability | 30000000 cycles
25877 | RM4TR35 | Complementary | [Ith] conventional free air thermal current | 8 A
25878 | RM4TR35 | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25879 | RM4TR35 | Complementary | switching capacity in mA | 10 mA at 12 V
25880 | RM4TR35 | Complementary | switching voltage | 250 V AC
25881 | RM4TR35 | Complementary | contacts material | 90/10 silver nickel contacts
25882 | RM4TR35 | Complementary | number of cables | 2
25883 | RM4TR35 | Complementary | height | 78 mm
25884 | RM4TR35 | Complementary | width | 22.5 mm
25885 | RM4TR35 | Complementary | depth | 80 mm
25886 | RM4TR35 | Complementary | terminals description ISO n°1 | (L1-L2-L3)CO (25-26-28)OC (15-16-18)OC
25887 | RM4TR35 | Complementary | output relay state | Tripped, fault present
25888 | RM4TR35 | Complementary | 9 mm pitches | 2.5
25889 | RM4TR35 | Complementary | net weight | 0.11 kg
25890 | RM4TR35 | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3
25891 | RM4TR35 | Environment | standards | EN/IEC 60255-6
25892 | RM4TR35 | Environment | product certifications | UL CSA GL
25893 | RM4TR35 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
25894 | RM4TR35 | Environment | ambient air temperature for storage | -40…85 °C
25895 | RM4TR35 | Environment | ambient air temperature for operation | -20…65 °C
25896 | RM4TR35 | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
25897 | RM4TR35 | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
25898 | RM4TR35 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
25899 | RM4TR35 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
25900 | RM4TR35 | Environment | pollution degree | 3 conforming to IEC 60664-1
25901 | RM4TR35 | Environment | dielectric test voltage | 2.5 kV
25902 | RM4TR35 | Environment | non-dissipating shock wave | 4.8 kV
25903 | RM4TR35 | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
25904 | RM4TR35 | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
25905 | RM4TR35 | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
25906 | RM4TR35 | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
25907 | RM4TR35 | Contractual warranty | Warranty | 18 months
25908 | RM4TU01 | Main | range of product | Zelio Control
25909 | RM4TU01 | Main | product or component type | Industrial measurement and control relays
25910 | RM4TU01 | Main | relay type | Control relay
25911 | RM4TU01 | Main | product specific application | For 3-phase supply
25912 | RM4TU01 | Main | relay name | RM4-T
25913 | RM4TU01 | Main | relay monitored parameters | Phase sequence Phase failure detection Undervoltage detection
25914 | RM4TU01 | Main | time delay | Without
25915 | RM4TU01 | Main | measurement range | 160...300 V
25916 | RM4TU01 | Main | contacts type and composition | 2 C/O
25917 | RM4TU01 | Main | poles description | 3P
25918 | RM4TU01 | Complementary | maximum switching voltage | 440 V AC
25919 | RM4TU01 | Complementary | control threshold undervoltage | 160…220 V
25920 | RM4TU01 | Complementary | output contacts | 2 C/O
25921 | RM4TU01 | Complementary | setting accuracy of the switching threshold | +/-3 %
25922 | RM4TU01 | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range
25923 | RM4TU01 | Complementary | setting accuracy of time delay | 10 P
25924 | RM4TU01 | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range
25925 | RM4TU01 | Complementary | hysteresis | 5 % fixed of de-energisation threshold
25926 | RM4TU01 | Complementary | delay at power up | 650 ms
25927 | RM4TU01 | Complementary | maximum measuring cycle | 80 ms
25928 | RM4TU01 | Complementary | marking | CE
25929 | RM4TU01 | Complementary | overvoltage category | III conforming to IEC 60664-1
25930 | RM4TU01 | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25931 | RM4TU01 | Complementary | supply frequency | 50/60 Hz +/- 5 %
25932 | RM4TU01 | Complementary | operating position | Any position without derating
25933 | RM4TU01 | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
25934 | RM4TU01 | Complementary | tightening torque | 0.6…1.1 N.m
25935 | RM4TU01 | Complementary | mechanical durability | 30000000 cycles
25936 | RM4TU01 | Complementary | [Ith] conventional free air thermal current | 8 A
25937 | RM4TU01 | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25938 | RM4TU01 | Complementary | switching capacity in mA | 10 mA at 12 V
25939 | RM4TU01 | Complementary | switching voltage | 250 V AC
25940 | RM4TU01 | Complementary | contacts material | 90/10 silver nickel contacts
25941 | RM4TU01 | Complementary | number of cables | 2
25942 | RM4TU01 | Complementary | height | 78 mm
25943 | RM4TU01 | Complementary | width | 22.5 mm
25944 | RM4TU01 | Complementary | depth | 80 mm
25945 | RM4TU01 | Complementary | terminals description ISO n°1 | ALT (L1-L2-L3)CO (25-26-28)OC (15-16-18)OC
25946 | RM4TU01 | Complementary | output relay state | Tripped, fault present
25947 | RM4TU01 | Complementary | 9 mm pitches | 2.5
25948 | RM4TU01 | Complementary | net weight | 0.11 kg
25949 | RM4TU01 | Complementary | terminals description ISO n°2 | (21-22-24)OC (11-12-14)OC (L1-L2-L3)CO ALT
25950 | RM4TU01 | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3
25951 | RM4TU01 | Environment | standards | EN/IEC 60255-6
25952 | RM4TU01 | Environment | product certifications | GL UL CSA
25953 | RM4TU01 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
25954 | RM4TU01 | Environment | ambient air temperature for storage | -40…85 °C
25955 | RM4TU01 | Environment | ambient air temperature for operation | -20…65 °C
25956 | RM4TU01 | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
25957 | RM4TU01 | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
25958 | RM4TU01 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
25959 | RM4TU01 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
25960 | RM4TU01 | Environment | pollution degree | 3 conforming to IEC 60664-1
25961 | RM4TU01 | Environment | dielectric test voltage | 2.5 kV
25962 | RM4TU01 | Environment | non-dissipating shock wave | 4.8 kV
25963 | RM4TU01 | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
25964 | RM4TU01 | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
25965 | RM4TU01 | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
25966 | RM4TU01 | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
25967 | RM4TU01 | Contractual warranty | Warranty | 18 months
25968 | RM4TU02 | Main | range of product | Zelio Control
25969 | RM4TU02 | Main | product or component type | Industrial measurement and control relays
25970 | RM4TU02 | Main | relay type | Control relay
25971 | RM4TU02 | Main | product specific application | For 3-phase supply
25972 | RM4TU02 | Main | relay name | RM4-T
25973 | RM4TU02 | Main | relay monitored parameters | Phase sequence Undervoltage detection Phase failure detection
25974 | RM4TU02 | Main | time delay | Without
25975 | RM4TU02 | Main | measurement range | 290...484 V
25976 | RM4TU02 | Main | contacts type and composition | 2 C/O
25977 | RM4TU02 | Main | poles description | 3P
25978 | RM4TU02 | Complementary | maximum switching voltage | 440 V AC
25979 | RM4TU02 | Complementary | control threshold undervoltage | 300…430 V
25980 | RM4TU02 | Complementary | output contacts | 2 C/O
25981 | RM4TU02 | Complementary | setting accuracy of the switching threshold | +/-3 %
25982 | RM4TU02 | Complementary | switching threshold drift | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range
25983 | RM4TU02 | Complementary | setting accuracy of time delay | 10 P
25984 | RM4TU02 | Complementary | time delay drift | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range
25985 | RM4TU02 | Complementary | hysteresis | 5 % fixed of de-energisation threshold
25986 | RM4TU02 | Complementary | delay at power up | 650 ms
25987 | RM4TU02 | Complementary | maximum measuring cycle | 80 ms
25988 | RM4TU02 | Complementary | marking | CE
25989 | RM4TU02 | Complementary | overvoltage category | III conforming to IEC 60664-1
25990 | RM4TU02 | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
25991 | RM4TU02 | Complementary | supply frequency | 50/60 Hz +/- 5 %
25992 | RM4TU02 | Complementary | operating position | Any position without derating
25993 | RM4TU02 | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
25994 | RM4TU02 | Complementary | tightening torque | 0.6…1.1 N.m
25995 | RM4TU02 | Complementary | mechanical durability | 30000000 cycles
25996 | RM4TU02 | Complementary | [Ith] conventional free air thermal current | 8 A
25997 | RM4TU02 | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
25998 | RM4TU02 | Complementary | switching capacity in mA | 10 mA at 12 V
25999 | RM4TU02 | Complementary | switching voltage | 250 V AC
26000 | RM4TU02 | Complementary | contacts material | 90/10 silver nickel contacts
26001 | RM4TU02 | Complementary | number of cables | 2
26002 | RM4TU02 | Complementary | height | 78 mm
26003 | RM4TU02 | Complementary | width | 22.5 mm
26004 | RM4TU02 | Complementary | depth | 80 mm
26005 | RM4TU02 | Complementary | terminals description ISO n°1 | ALT (25-26-28)OC (L1-L2-L3)CO (15-16-18)OC
26006 | RM4TU02 | Complementary | output relay state | Tripped, fault present
26007 | RM4TU02 | Complementary | 9 mm pitches | 2.5
26008 | RM4TU02 | Complementary | net weight | 0.11 kg
26009 | RM4TU02 | Complementary | terminals description ISO n°2 | (L1-L2-L3)CO (11-12-14)OC (21-22-24)OC ALT
26010 | RM4TU02 | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3
26011 | RM4TU02 | Environment | standards | EN/IEC 60255-6
26012 | RM4TU02 | Environment | product certifications | CSA GL UL
26013 | RM4TU02 | Environment | directives | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility
26014 | RM4TU02 | Environment | ambient air temperature for storage | -40…85 °C
26015 | RM4TU02 | Environment | ambient air temperature for operation | -20…65 °C
26016 | RM4TU02 | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26017 | RM4TU02 | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
26018 | RM4TU02 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26019 | RM4TU02 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
26020 | RM4TU02 | Environment | pollution degree | 3 conforming to IEC 60664-1
26021 | RM4TU02 | Environment | dielectric test voltage | 2.5 kV
26022 | RM4TU02 | Environment | non-dissipating shock wave | 4.8 kV
26023 | RM4TU02 | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
26024 | RM4TU02 | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26025 | RM4TU02 | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26026 | RM4TU02 | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
26027 | RM4TU02 | Contractual warranty | Warranty | 18 months
26028 | RM4LA32B | Main | range of product | Zelio Control
26029 | RM4LA32B | Main | product or component type | Industrial measurement and control relays
26030 | RM4LA32B | Main | relay type | Liquid level control relay
26031 | RM4LA32B | Main | relay name | RM4-L
26032 | RM4LA32B | Main | relay monitored parameters | Detection by resistive probes
26033 | RM4LA32B | Main | time delay | Adjustable 0.1...10 s
26034 | RM4LA32B | Main | power consumption | 3.1 VA AC
26035 | RM4LA32B | Main | contacts type and composition | 2 C/O
26036 | RM4LA32B | Complementary | maximum switching voltage | 440 V AC
26037 | RM4LA32B | Complementary | [Un] rated nominal voltage | 24 V AC 50/60 Hz +/- 5 %
26038 | RM4LA32B | Complementary | operating voltage tolerance | 0.85...1.1 Uc
26039 | RM4LA32B | Complementary | output contacts | 2 C/O
26040 | RM4LA32B | Complementary | maximum electrode voltage | 24 V AC
26041 | RM4LA32B | Complementary | maximum electrode current | 1 mA
26042 | RM4LA32B | Complementary | maximum cable capacity | 0 mF
26043 | RM4LA32B | Complementary | maximum cable distance between devices | 1000 m
26044 | RM4LA32B | Complementary | sensitivity scale | 0.25...5 kOhm LS (Low Sensitivity) 2.5...50 kOhm St (Standard Sensitivity) 25...500 kOhm HS (High Sensitivity)
26045 | RM4LA32B | Complementary | marking | CE : EMC 89/336/EEC CE : LVD 73/23/EEC
26046 | RM4LA32B | Complementary | overvoltage category | III conforming to IEC 60664-1
26047 | RM4LA32B | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
26048 | RM4LA32B | Complementary | supply disconnection value | > 0.1 Uc
26049 | RM4LA32B | Complementary | operating position | Any position without derating
26050 | RM4LA32B | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
26051 | RM4LA32B | Complementary | tightening torque | 0.6…1.1 N.m
26052 | RM4LA32B | Complementary | mechanical durability | 30000000 cycles
26053 | RM4LA32B | Complementary | [Ith] conventional free air thermal current | 8 A
26054 | RM4LA32B | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
26055 | RM4LA32B | Complementary | switching capacity in mA | 10 mA at 12 V
26056 | RM4LA32B | Complementary | switching voltage | 250 V AC
26057 | RM4LA32B | Complementary | contacts material | 90/10 silver nickel contacts
26058 | RM4LA32B | Complementary | number of cables | 2
26059 | RM4LA32B | Complementary | width | 22.5 mm
26060 | RM4LA32B | Complementary | terminals description ISO n°1 | (B1-B2-B3)CO (A1-A2)CO (15-16-18)OC (25-26-28)OC
26061 | RM4LA32B | Complementary | output relay state | According to chosen function
26062 | RM4LA32B | Complementary | 9 mm pitches | 2.5
26063 | RM4LA32B | Complementary | net weight | 0.165 kg
26064 | RM4LA32B | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
26065 | RM4LA32B | Environment | standards | EN/IEC 60255-6
26066 | RM4LA32B | Environment | product certifications | CSA UL GL
26067 | RM4LA32B | Environment | ambient air temperature for storage | -40…85 °C
26068 | RM4LA32B | Environment | ambient air temperature for operation | -20…65 °C
26069 | RM4LA32B | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26070 | RM4LA32B | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
26071 | RM4LA32B | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26072 | RM4LA32B | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
26073 | RM4LA32B | Environment | pollution degree | 3 conforming to IEC 60664-1
26074 | RM4LA32B | Environment | dielectric test voltage | 2.5 kV
26075 | RM4LA32B | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
26076 | RM4LA32B | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26077 | RM4LA32B | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26078 | RM4LA32B | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
26079 | RM4LA32B | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
26080 | RM4LA32B | Contractual warranty | Warranty | 18 months
26081 | RM4LA32F | Main | range of product | Zelio Control
26082 | RM4LA32F | Main | product or component type | Industrial measurement and control relays
26083 | RM4LA32F | Main | relay type | Liquid level control relay
26084 | RM4LA32F | Main | relay name | RM4-L
26085 | RM4LA32F | Main | relay monitored parameters | Detection by resistive probes
26086 | RM4LA32F | Main | time delay | Adjustable 0.1...10 s
26087 | RM4LA32F | Main | power consumption | 2.7 VA AC
26088 | RM4LA32F | Main | contacts type and composition | 2 C/O
26089 | RM4LA32F | Complementary | maximum switching voltage | 440 V AC
26090 | RM4LA32F | Complementary | [Un] rated nominal voltage | 110...130 V AC 50/60 Hz +/- 5 %
26091 | RM4LA32F | Complementary | operating voltage tolerance | 0.85...1.1 Uc
26092 | RM4LA32F | Complementary | output contacts | 2 C/O
26093 | RM4LA32F | Complementary | maximum electrode voltage | 24 V AC
26094 | RM4LA32F | Complementary | maximum electrode current | 1 mA
26095 | RM4LA32F | Complementary | maximum cable capacity | 0 mF
26096 | RM4LA32F | Complementary | maximum cable distance between devices | 1000 m
26097 | RM4LA32F | Complementary | sensitivity scale | 0.25...5 kOhm LS (Low Sensitivity) 2.5...50 kOhm St (Standard Sensitivity) 25...500 kOhm HS (High Sensitivity)
26098 | RM4LA32F | Complementary | marking | CE : LVD 73/23/EEC CE : EMC 89/336/EEC
26099 | RM4LA32F | Complementary | overvoltage category | III conforming to IEC 60664-1
26100 | RM4LA32F | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
26101 | RM4LA32F | Complementary | supply disconnection value | > 0.1 Uc
26102 | RM4LA32F | Complementary | operating position | Any position without derating
26103 | RM4LA32F | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
26104 | RM4LA32F | Complementary | tightening torque | 0.6…1.1 N.m
26105 | RM4LA32F | Complementary | mechanical durability | 30000000 cycles
26106 | RM4LA32F | Complementary | [Ith] conventional free air thermal current | 8 A
26107 | RM4LA32F | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
26108 | RM4LA32F | Complementary | switching capacity in mA | 10 mA at 12 V
26109 | RM4LA32F | Complementary | switching voltage | 250 V AC
26110 | RM4LA32F | Complementary | contacts material | 90/10 silver nickel contacts
26111 | RM4LA32F | Complementary | number of cables | 2
26112 | RM4LA32F | Complementary | width | 22.5 mm
26113 | RM4LA32F | Complementary | terminals description ISO n°1 | (A1-A2)CO (15-16-18)OC (25-26-28)OC (B1-B2-B3)CO
26114 | RM4LA32F | Complementary | output relay state | According to chosen function
26115 | RM4LA32F | Complementary | 9 mm pitches | 2.5
26116 | RM4LA32F | Complementary | net weight | 0.165 kg
26117 | RM4LA32F | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
26118 | RM4LA32F | Environment | standards | EN/IEC 60255-6
26119 | RM4LA32F | Environment | product certifications | UL GL CSA
26120 | RM4LA32F | Environment | ambient air temperature for storage | -40…85 °C
26121 | RM4LA32F | Environment | ambient air temperature for operation | -20…65 °C
26122 | RM4LA32F | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26123 | RM4LA32F | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
26124 | RM4LA32F | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26125 | RM4LA32F | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
26126 | RM4LA32F | Environment | pollution degree | 3 conforming to IEC 60664-1
26127 | RM4LA32F | Environment | dielectric test voltage | 2.5 kV
26128 | RM4LA32F | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
26129 | RM4LA32F | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26130 | RM4LA32F | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26131 | RM4LA32F | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
26132 | RM4LA32F | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
26133 | RM4LA32F | Contractual warranty | Warranty | 18 months
26134 | RM4LA32M | Main | range of product | Zelio Control
26135 | RM4LA32M | Main | product or component type | Industrial measurement and control relays
26136 | RM4LA32M | Main | relay type | Liquid level control relay
26137 | RM4LA32M | Main | relay name | RM4-L
26138 | RM4LA32M | Main | relay monitored parameters | Detection by resistive probes
26139 | RM4LA32M | Main | time delay | Adjustable 0.1...10 s
26140 | RM4LA32M | Main | power consumption | 2.6 VA AC
26141 | RM4LA32M | Main | contacts type and composition | 2 C/O
26142 | RM4LA32M | Complementary | maximum switching voltage | 440 V AC
26143 | RM4LA32M | Complementary | [Un] rated nominal voltage | 220...240 V AC 50/60 Hz +/- 5 %
26144 | RM4LA32M | Complementary | operating voltage tolerance | 0.85...1.1 Uc
26145 | RM4LA32M | Complementary | output contacts | 2 C/O
26146 | RM4LA32M | Complementary | maximum electrode voltage | 24 V AC
26147 | RM4LA32M | Complementary | maximum electrode current | 1 mA
26148 | RM4LA32M | Complementary | maximum cable capacity | 0 mF
26149 | RM4LA32M | Complementary | maximum cable distance between devices | 1000 m
26150 | RM4LA32M | Complementary | sensitivity scale | 0.25...5 kOhm LS (Low Sensitivity) 2.5...50 kOhm St (Standard Sensitivity) 25...500 kOhm HS (High Sensitivity)
26151 | RM4LA32M | Complementary | marking | CE : EMC 89/336/EEC CE : LVD 73/23/EEC
26152 | RM4LA32M | Complementary | overvoltage category | III conforming to IEC 60664-1
26153 | RM4LA32M | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
26154 | RM4LA32M | Complementary | supply disconnection value | > 0.1 Uc
26155 | RM4LA32M | Complementary | operating position | Any position without derating
26156 | RM4LA32M | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
26157 | RM4LA32M | Complementary | tightening torque | 0.6…1.1 N.m
26158 | RM4LA32M | Complementary | mechanical durability | 30000000 cycles
26159 | RM4LA32M | Complementary | [Ith] conventional free air thermal current | 8 A
26160 | RM4LA32M | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
26161 | RM4LA32M | Complementary | switching capacity in mA | 10 mA at 12 V
26162 | RM4LA32M | Complementary | switching voltage | 250 V AC
26163 | RM4LA32M | Complementary | contacts material | 90/10 silver nickel contacts
26164 | RM4LA32M | Complementary | number of cables | 2
26165 | RM4LA32M | Complementary | width | 22.5 mm
26166 | RM4LA32M | Complementary | terminals description ISO n°1 | (A1-A2)CO (25-26-28)OC (B1-B2-B3)CO (15-16-18)OC
26167 | RM4LA32M | Complementary | output relay state | According to chosen function
26168 | RM4LA32M | Complementary | 9 mm pitches | 2.5
26169 | RM4LA32M | Complementary | net weight | 0.165 kg
26170 | RM4LA32M | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
26171 | RM4LA32M | Environment | standards | EN/IEC 60255-6
26172 | RM4LA32M | Environment | product certifications | CSA UL GL
26173 | RM4LA32M | Environment | ambient air temperature for storage | -40…85 °C
26174 | RM4LA32M | Environment | ambient air temperature for operation | -20…65 °C
26175 | RM4LA32M | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26176 | RM4LA32M | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
26177 | RM4LA32M | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26178 | RM4LA32M | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
26179 | RM4LA32M | Environment | pollution degree | 3 conforming to IEC 60664-1
26180 | RM4LA32M | Environment | dielectric test voltage | 2.5 kV
26181 | RM4LA32M | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
26182 | RM4LA32M | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26183 | RM4LA32M | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26184 | RM4LA32M | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
26185 | RM4LA32M | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
26186 | RM4LA32M | Contractual warranty | Warranty | 18 months
26187 | RM4LA32MW | Main | range of product | Zelio Control
26188 | RM4LA32MW | Main | product or component type | Industrial measurement and control relays
26189 | RM4LA32MW | Main | relay type | Liquid level control relay
26190 | RM4LA32MW | Main | relay name | RM4-L
26191 | RM4LA32MW | Main | relay monitored parameters | Detection by resistive probes
26192 | RM4LA32MW | Main | time delay | Adjustable 0.1...10 s
26193 | RM4LA32MW | Main | power consumption | 2.7 VA AC
26194 | RM4LA32MW | Main | contacts type and composition | 2 C/O
26195 | RM4LA32MW | Complementary | maximum switching voltage | 440 V AC
26196 | RM4LA32MW | Complementary | [Un] rated nominal voltage | 24...240 V DC 24...240 V AC 50/60 Hz +/- 5 %
26197 | RM4LA32MW | Complementary | operating voltage tolerance | 0.85...1.1 Uc
26198 | RM4LA32MW | Complementary | power consumption | 2.4 W DC
26199 | RM4LA32MW | Complementary | output contacts | 2 C/O
26200 | RM4LA32MW | Complementary | maximum electrode voltage | 24 V AC
26201 | RM4LA32MW | Complementary | maximum electrode current | 1 mA
26202 | RM4LA32MW | Complementary | maximum cable capacity | 0 mF
26203 | RM4LA32MW | Complementary | maximum cable distance between devices | 1000 m
26204 | RM4LA32MW | Complementary | sensitivity scale | 0.25...5 kOhm LS (Low Sensitivity) 2.5...50 kOhm St (Standard Sensitivity) 25...500 kOhm HS (High Sensitivity)
26205 | RM4LA32MW | Complementary | marking | CE : LVD 73/23/EEC CE : EMC 89/336/EEC
26206 | RM4LA32MW | Complementary | overvoltage category | III conforming to IEC 60664-1
26207 | RM4LA32MW | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
26208 | RM4LA32MW | Complementary | supply disconnection value | > 0.1 Uc
26209 | RM4LA32MW | Complementary | operating position | Any position without derating
26210 | RM4LA32MW | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
26211 | RM4LA32MW | Complementary | tightening torque | 0.6…1.1 N.m
26212 | RM4LA32MW | Complementary | mechanical durability | 30000000 cycles
26213 | RM4LA32MW | Complementary | [Ith] conventional free air thermal current | 8 A
26214 | RM4LA32MW | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
26215 | RM4LA32MW | Complementary | switching capacity in mA | 10 mA at 12 V
26216 | RM4LA32MW | Complementary | switching voltage | 250 V AC
26217 | RM4LA32MW | Complementary | contacts material | 90/10 silver nickel contacts
26218 | RM4LA32MW | Complementary | number of cables | 2
26219 | RM4LA32MW | Complementary | width | 22.5 mm
26220 | RM4LA32MW | Complementary | terminals description ISO n°1 | (15-16-18)OC (25-26-28)OC (B1-B2-B3)CO (A1-A2)CO
26221 | RM4LA32MW | Complementary | output relay state | According to chosen function
26222 | RM4LA32MW | Complementary | 9 mm pitches | 2.5
26223 | RM4LA32MW | Complementary | net weight | 0.165 kg
26224 | RM4LA32MW | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
26225 | RM4LA32MW | Environment | standards | EN/IEC 60255-6
26226 | RM4LA32MW | Environment | product certifications | UL GL CSA
26227 | RM4LA32MW | Environment | ambient air temperature for storage | -40…85 °C
26228 | RM4LA32MW | Environment | ambient air temperature for operation | -20…65 °C
26229 | RM4LA32MW | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26230 | RM4LA32MW | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
26231 | RM4LA32MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26232 | RM4LA32MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
26233 | RM4LA32MW | Environment | pollution degree | 3 conforming to IEC 60664-1
26234 | RM4LA32MW | Environment | dielectric test voltage | 2.5 kV
26235 | RM4LA32MW | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
26236 | RM4LA32MW | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26237 | RM4LA32MW | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26238 | RM4LA32MW | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
26239 | RM4LA32MW | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
26240 | RM4LA32MW | Contractual warranty | Warranty | 18 months
26241 | RM4LA32Q | Main | range of product | Zelio Control
26242 | RM4LA32Q | Main | product or component type | Industrial measurement and control relays
26243 | RM4LA32Q | Main | relay type | Liquid level control relay
26244 | RM4LA32Q | Main | relay name | RM4-L
26245 | RM4LA32Q | Main | relay monitored parameters | Detection by resistive probes
26246 | RM4LA32Q | Main | time delay | Adjustable 0.1...10 s
26247 | RM4LA32Q | Main | power consumption | 3.4 VA AC
26248 | RM4LA32Q | Main | contacts type and composition | 2 C/O
26249 | RM4LA32Q | Complementary | maximum switching voltage | 440 V AC
26250 | RM4LA32Q | Complementary | [Un] rated nominal voltage | 380...415 V AC 50/60 Hz +/- 5 %
26251 | RM4LA32Q | Complementary | operating voltage tolerance | 0.85...1.1 Uc
26252 | RM4LA32Q | Complementary | output contacts | 2 C/O
26253 | RM4LA32Q | Complementary | maximum electrode voltage | 24 V AC
26254 | RM4LA32Q | Complementary | maximum electrode current | 1 mA
26255 | RM4LA32Q | Complementary | maximum cable capacity | 0 mF
26256 | RM4LA32Q | Complementary | maximum cable distance between devices | 1000 m
26257 | RM4LA32Q | Complementary | sensitivity scale | 0.25...5 kOhm LS (Low Sensitivity) 2.5...50 kOhm St (Standard Sensitivity) 25...500 kOhm HS (High Sensitivity)
26258 | RM4LA32Q | Complementary | marking | CE : EMC 89/336/EEC CE : LVD 73/23/EEC
26259 | RM4LA32Q | Complementary | overvoltage category | III conforming to IEC 60664-1
26260 | RM4LA32Q | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
26261 | RM4LA32Q | Complementary | supply disconnection value | > 0.1 Uc
26262 | RM4LA32Q | Complementary | operating position | Any position without derating
26263 | RM4LA32Q | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
26264 | RM4LA32Q | Complementary | tightening torque | 0.6…1.1 N.m
26265 | RM4LA32Q | Complementary | mechanical durability | 30000000 cycles
26266 | RM4LA32Q | Complementary | [Ith] conventional free air thermal current | 8 A
26267 | RM4LA32Q | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
26268 | RM4LA32Q | Complementary | switching capacity in mA | 10 mA at 12 V
26269 | RM4LA32Q | Complementary | switching voltage | 250 V AC
26270 | RM4LA32Q | Complementary | contacts material | 90/10 silver nickel contacts
26271 | RM4LA32Q | Complementary | number of cables | 2
26272 | RM4LA32Q | Complementary | width | 22.5 mm
26273 | RM4LA32Q | Complementary | terminals description ISO n°1 | (15-16-18)OC (B1-B2-B3)CO (A1-A2)CO (25-26-28)OC
26274 | RM4LA32Q | Complementary | output relay state | According to chosen function
26275 | RM4LA32Q | Complementary | 9 mm pitches | 2.5
26276 | RM4LA32Q | Complementary | net weight | 0.165 kg
26277 | RM4LA32Q | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
26278 | RM4LA32Q | Environment | standards | EN/IEC 60255-6
26279 | RM4LA32Q | Environment | product certifications | CSA UL GL
26280 | RM4LA32Q | Environment | ambient air temperature for storage | -40…85 °C
26281 | RM4LA32Q | Environment | ambient air temperature for operation | -20…65 °C
26282 | RM4LA32Q | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26283 | RM4LA32Q | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
26284 | RM4LA32Q | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26285 | RM4LA32Q | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
26286 | RM4LA32Q | Environment | pollution degree | 3 conforming to IEC 60664-1
26287 | RM4LA32Q | Environment | dielectric test voltage | 2.5 kV
26288 | RM4LA32Q | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
26289 | RM4LA32Q | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26290 | RM4LA32Q | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26291 | RM4LA32Q | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
26292 | RM4LA32Q | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
26293 | RM4LA32Q | Contractual warranty | Warranty | 18 months
26294 | RM4LG01B | Main | range of product | Zelio Control
26295 | RM4LG01B | Main | product or component type | Industrial measurement and control relays
26296 | RM4LG01B | Main | relay type | Liquid level control relay
26297 | RM4LG01B | Main | relay name | RM4-L
26298 | RM4LG01B | Main | relay monitored parameters | Detection by resistive probes
26299 | RM4LG01B | Main | time delay | Without
26300 | RM4LG01B | Main | power consumption | 1.9 VA AC
26301 | RM4LG01B | Main | contacts type and composition | 1 C/O
26302 | RM4LG01B | Complementary | maximum switching voltage | 440 V AC
26303 | RM4LG01B | Complementary | [Un] rated nominal voltage | 24 V AC 50/60 Hz +/- 5 %
26304 | RM4LG01B | Complementary | operating voltage tolerance | 0.85...1.1 Uc
26305 | RM4LG01B | Complementary | output contacts | 1 C/O
26306 | RM4LG01B | Complementary | maximum electrode voltage | 24 V AC
26307 | RM4LG01B | Complementary | maximum electrode current | 1 mA
26308 | RM4LG01B | Complementary | maximum cable capacity | 0 mF
26309 | RM4LG01B | Complementary | maximum cable distance between devices | 100 m
26310 | RM4LG01B | Complementary | sensitivity scale | 5...100 kOhm
26311 | RM4LG01B | Complementary | marking | CE : LVD 73/23/EEC CE : EMC 89/336/EEC
26312 | RM4LG01B | Complementary | overvoltage category | III conforming to IEC 60664-1
26313 | RM4LG01B | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
26314 | RM4LG01B | Complementary | supply disconnection value | > 0.1 Uc
26315 | RM4LG01B | Complementary | operating position | Any position without derating
26316 | RM4LG01B | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
26317 | RM4LG01B | Complementary | tightening torque | 0.6…1.1 N.m
26318 | RM4LG01B | Complementary | mechanical durability | 30000000 cycles
26319 | RM4LG01B | Complementary | [Ith] conventional free air thermal current | 8 A
26320 | RM4LG01B | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
26321 | RM4LG01B | Complementary | switching capacity in mA | 10 mA at 12 V
26322 | RM4LG01B | Complementary | switching voltage | 250 V AC
26323 | RM4LG01B | Complementary | contacts material | 90/10 silver nickel contacts
26324 | RM4LG01B | Complementary | number of cables | 2
26325 | RM4LG01B | Complementary | width | 22.5 mm
26326 | RM4LG01B | Complementary | terminals description ISO n°1 | (15-16-18)OC (A1-A2)CO (B1-B2-B3)CO
26327 | RM4LG01B | Complementary | output relay state | According to chosen function
26328 | RM4LG01B | Complementary | 9 mm pitches | 2.5
26329 | RM4LG01B | Complementary | net weight | 0.165 kg
26330 | RM4LG01B | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
26331 | RM4LG01B | Environment | standards | EN/IEC 60255-6
26332 | RM4LG01B | Environment | product certifications | UL GL CSA
26333 | RM4LG01B | Environment | ambient air temperature for storage | -40…85 °C
26334 | RM4LG01B | Environment | ambient air temperature for operation | -20…65 °C
26335 | RM4LG01B | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26336 | RM4LG01B | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
26337 | RM4LG01B | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26338 | RM4LG01B | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
26339 | RM4LG01B | Environment | pollution degree | 3 conforming to IEC 60664-1
26340 | RM4LG01B | Environment | dielectric test voltage | 2.5 kV
26341 | RM4LG01B | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
26342 | RM4LG01B | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26343 | RM4LG01B | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26344 | RM4LG01B | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
26345 | RM4LG01B | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
26346 | RM4LG01B | Contractual warranty | Warranty | 18 months
26347 | RM4LG01F | Main | range of product | Zelio Control
26348 | RM4LG01F | Main | product or component type | Industrial measurement and control relays
26349 | RM4LG01F | Main | relay type | Liquid level control relay
26350 | RM4LG01F | Main | relay name | RM4-L
26351 | RM4LG01F | Main | relay monitored parameters | Detection by resistive probes
26352 | RM4LG01F | Main | time delay | Without
26353 | RM4LG01F | Main | power consumption | 2.6 VA AC
26354 | RM4LG01F | Main | contacts type and composition | 1 C/O
26355 | RM4LG01F | Complementary | maximum switching voltage | 440 V AC
26356 | RM4LG01F | Complementary | [Un] rated nominal voltage | 110...130 V AC 50/60 Hz +/- 5 %
26357 | RM4LG01F | Complementary | operating voltage tolerance | 0.85...1.1 Uc
26358 | RM4LG01F | Complementary | output contacts | 1 C/O
26359 | RM4LG01F | Complementary | maximum electrode voltage | 24 V AC
26360 | RM4LG01F | Complementary | maximum electrode current | 1 mA
26361 | RM4LG01F | Complementary | maximum cable capacity | 0 mF
26362 | RM4LG01F | Complementary | maximum cable distance between devices | 100 m
26363 | RM4LG01F | Complementary | sensitivity scale | 5...100 kOhm
26364 | RM4LG01F | Complementary | marking | CE : EMC 89/336/EEC CE : LVD 73/23/EEC
26365 | RM4LG01F | Complementary | overvoltage category | III conforming to IEC 60664-1
26366 | RM4LG01F | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
26367 | RM4LG01F | Complementary | supply disconnection value | > 0.1 Uc
26368 | RM4LG01F | Complementary | operating position | Any position without derating
26369 | RM4LG01F | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
26370 | RM4LG01F | Complementary | tightening torque | 0.6…1.1 N.m
26371 | RM4LG01F | Complementary | mechanical durability | 30000000 cycles
26372 | RM4LG01F | Complementary | [Ith] conventional free air thermal current | 8 A
26373 | RM4LG01F | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
26374 | RM4LG01F | Complementary | switching capacity in mA | 10 mA at 12 V
26375 | RM4LG01F | Complementary | switching voltage | 250 V AC
26376 | RM4LG01F | Complementary | contacts material | 90/10 silver nickel contacts
26377 | RM4LG01F | Complementary | number of cables | 2
26378 | RM4LG01F | Complementary | width | 22.5 mm
26379 | RM4LG01F | Complementary | terminals description ISO n°1 | (B1-B2-B3)CO (15-16-18)OC (A1-A2)CO
26380 | RM4LG01F | Complementary | output relay state | According to chosen function
26381 | RM4LG01F | Complementary | 9 mm pitches | 2.5
26382 | RM4LG01F | Complementary | net weight | 0.165 kg
26383 | RM4LG01F | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
26384 | RM4LG01F | Environment | standards | EN/IEC 60255-6
26385 | RM4LG01F | Environment | product certifications | UL CSA GL
26386 | RM4LG01F | Environment | ambient air temperature for storage | -40…85 °C
26387 | RM4LG01F | Environment | ambient air temperature for operation | -20…65 °C
26388 | RM4LG01F | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26389 | RM4LG01F | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
26390 | RM4LG01F | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26391 | RM4LG01F | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
26392 | RM4LG01F | Environment | pollution degree | 3 conforming to IEC 60664-1
26393 | RM4LG01F | Environment | dielectric test voltage | 2.5 kV
26394 | RM4LG01F | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
26395 | RM4LG01F | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26396 | RM4LG01F | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26397 | RM4LG01F | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
26398 | RM4LG01F | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
26399 | RM4LG01F | Contractual warranty | Warranty | 18 months
26400 | RM4LG01M | Main | range of product | Zelio Control
26401 | RM4LG01M | Main | product or component type | Industrial measurement and control relays
26402 | RM4LG01M | Main | relay type | Liquid level control relay
26403 | RM4LG01M | Main | relay name | RM4-L
26404 | RM4LG01M | Main | relay monitored parameters | Detection by resistive probes
26405 | RM4LG01M | Main | time delay | Without
26406 | RM4LG01M | Main | power consumption | 2.4 VA AC
26407 | RM4LG01M | Main | contacts type and composition | 1 C/O
26408 | RM4LG01M | Complementary | maximum switching voltage | 440 V AC
26409 | RM4LG01M | Complementary | [Un] rated nominal voltage | 220...240 V AC 50/60 Hz +/- 5 %
26410 | RM4LG01M | Complementary | operating voltage tolerance | 0.85...1.1 Uc
26411 | RM4LG01M | Complementary | output contacts | 1 C/O
26412 | RM4LG01M | Complementary | maximum electrode voltage | 24 V AC
26413 | RM4LG01M | Complementary | maximum electrode current | 1 mA
26414 | RM4LG01M | Complementary | maximum cable capacity | 0 mF
26415 | RM4LG01M | Complementary | maximum cable distance between devices | 100 m
26416 | RM4LG01M | Complementary | sensitivity scale | 5...100 kOhm
26417 | RM4LG01M | Complementary | marking | CE : EMC 89/336/EEC CE : LVD 73/23/EEC
26418 | RM4LG01M | Complementary | overvoltage category | III conforming to IEC 60664-1
26419 | RM4LG01M | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
26420 | RM4LG01M | Complementary | supply disconnection value | > 0.1 Uc
26421 | RM4LG01M | Complementary | operating position | Any position without derating
26422 | RM4LG01M | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
26423 | RM4LG01M | Complementary | tightening torque | 0.6…1.1 N.m
26424 | RM4LG01M | Complementary | mechanical durability | 30000000 cycles
26425 | RM4LG01M | Complementary | [Ith] conventional free air thermal current | 8 A
26426 | RM4LG01M | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
26427 | RM4LG01M | Complementary | switching capacity in mA | 10 mA at 12 V
26428 | RM4LG01M | Complementary | switching voltage | 250 V AC
26429 | RM4LG01M | Complementary | contacts material | 90/10 silver nickel contacts
26430 | RM4LG01M | Complementary | number of cables | 2
26431 | RM4LG01M | Complementary | width | 22.5 mm
26432 | RM4LG01M | Complementary | terminals description ISO n°1 | (B1-B2-B3)CO (15-16-18)OC (A1-A2)CO
26433 | RM4LG01M | Complementary | output relay state | According to chosen function
26434 | RM4LG01M | Complementary | 9 mm pitches | 2.5
26435 | RM4LG01M | Complementary | net weight | 0.165 kg
26436 | RM4LG01M | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
26437 | RM4LG01M | Environment | standards | EN/IEC 60255-6
26438 | RM4LG01M | Environment | product certifications | GL CSA UL
26439 | RM4LG01M | Environment | ambient air temperature for storage | -40…85 °C
26440 | RM4LG01M | Environment | ambient air temperature for operation | -20…65 °C
26441 | RM4LG01M | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26442 | RM4LG01M | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
26443 | RM4LG01M | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26444 | RM4LG01M | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
26445 | RM4LG01M | Environment | pollution degree | 3 conforming to IEC 60664-1
26446 | RM4LG01M | Environment | dielectric test voltage | 2.5 kV
26447 | RM4LG01M | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
26448 | RM4LG01M | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26449 | RM4LG01M | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26450 | RM4LG01M | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
26451 | RM4LG01M | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
26452 | RM4LG01M | Contractual warranty | Warranty | 18 months
26453 | RM4LG01Q | Main | range of product | Zelio Control
26454 | RM4LG01Q | Main | product or component type | Industrial measurement and control relays
26455 | RM4LG01Q | Main | relay type | Liquid level control relay
26456 | RM4LG01Q | Main | relay name | RM4-L
26457 | RM4LG01Q | Main | relay monitored parameters | Detection by resistive probes
26458 | RM4LG01Q | Main | time delay | Without
26459 | RM4LG01Q | Main | power consumption | 2.9 VA AC
26460 | RM4LG01Q | Main | contacts type and composition | 1 C/O
26461 | RM4LG01Q | Complementary | maximum switching voltage | 440 V AC
26462 | RM4LG01Q | Complementary | [Un] rated nominal voltage | 380...415 V AC 50/60 Hz +/- 5 %
26463 | RM4LG01Q | Complementary | operating voltage tolerance | 0.85...1.1 Uc
26464 | RM4LG01Q | Complementary | output contacts | 1 C/O
26465 | RM4LG01Q | Complementary | maximum electrode voltage | 24 V AC
26466 | RM4LG01Q | Complementary | maximum electrode current | 1 mA
26467 | RM4LG01Q | Complementary | maximum cable capacity | 0 mF
26468 | RM4LG01Q | Complementary | maximum cable distance between devices | 100 m
26469 | RM4LG01Q | Complementary | sensitivity scale | 5...100 kOhm
26470 | RM4LG01Q | Complementary | marking | CE : LVD 73/23/EEC CE : EMC 89/336/EEC
26471 | RM4LG01Q | Complementary | overvoltage category | III conforming to IEC 60664-1
26472 | RM4LG01Q | Complementary | [Ui] rated insulation voltage | 500 V conforming to IEC
26473 | RM4LG01Q | Complementary | supply disconnection value | > 0.1 Uc
26474 | RM4LG01Q | Complementary | operating position | Any position without derating
26475 | RM4LG01Q | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end
26476 | RM4LG01Q | Complementary | tightening torque | 0.6…1.1 N.m
26477 | RM4LG01Q | Complementary | mechanical durability | 30000000 cycles
26478 | RM4LG01Q | Complementary | [Ith] conventional free air thermal current | 8 A
26479 | RM4LG01Q | Complementary | [Ie] rated operational current | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660
26480 | RM4LG01Q | Complementary | switching capacity in mA | 10 mA at 12 V
26481 | RM4LG01Q | Complementary | switching voltage | 250 V AC
26482 | RM4LG01Q | Complementary | contacts material | 90/10 silver nickel contacts
26483 | RM4LG01Q | Complementary | number of cables | 2
26484 | RM4LG01Q | Complementary | width | 22.5 mm
26485 | RM4LG01Q | Complementary | terminals description ISO n°1 | (B1-B2-B3)CO (A1-A2)CO (15-16-18)OC
26486 | RM4LG01Q | Complementary | output relay state | According to chosen function
26487 | RM4LG01Q | Complementary | 9 mm pitches | 2.5
26488 | RM4LG01Q | Complementary | net weight | 0.165 kg
26489 | RM4LG01Q | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
26490 | RM4LG01Q | Environment | standards | EN/IEC 60255-6
26491 | RM4LG01Q | Environment | product certifications | GL CSA UL
26492 | RM4LG01Q | Environment | ambient air temperature for storage | -40…85 °C
26493 | RM4LG01Q | Environment | ambient air temperature for operation | -20…65 °C
26494 | RM4LG01Q | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26495 | RM4LG01Q | Environment | vibration resistance | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6
26496 | RM4LG01Q | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26497 | RM4LG01Q | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529
26498 | RM4LG01Q | Environment | pollution degree | 3 conforming to IEC 60664-1
26499 | RM4LG01Q | Environment | dielectric test voltage | 2.5 kV
26500 | RM4LG01Q | Environment | resistance to electrostatic discharge | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3
26501 | RM4LG01Q | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26502 | RM4LG01Q | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26503 | RM4LG01Q | Environment | protection against electric shocks | 2 kV: level 3 conforming to IEC 61000-4-5
26504 | RM4LG01Q | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
26505 | RM4LG01Q | Contractual warranty | Warranty | 18 months
26506 | RE7TL11BU | Main | range of product | Zelio Time
26507 | RE7TL11BU | Main | product or component type | Industrial timing relay
26508 | RE7TL11BU | Main | component name | RE7
26509 | RE7TL11BU | Main | time delay type | A
26510 | RE7TL11BU | Main | time delay range | 0.05 s...300 h
26511 | RE7TL11BU | Complementary | discrete output type | Relay
26512 | RE7TL11BU | Complementary | contacts material | 90/10 silver nickel contacts
26513 | RE7TL11BU | Complementary | width pitch dimension | 22.5 mm
26514 | RE7TL11BU | Complementary | [Us] rated supply voltage | 110...240 V AC 50/60 Hz 24 V AC/DC 50/60 Hz
26515 | RE7TL11BU | Complementary | voltage range | 0.85...1.1 Us
26516 | RE7TL11BU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end
26517 | RE7TL11BU | Complementary | tightening torque | 0.6…1.1 N.m
26518 | RE7TL11BU | Complementary | setting accuracy of time delay | +/- 10 % of full scale
26519 | RE7TL11BU | Complementary | repeat accuracy | +/- 0.2 %
26520 | RE7TL11BU | Complementary | temperature drift | < 0.07 %/°C
26521 | RE7TL11BU | Complementary | voltage drift | < 0.2 %/V
26522 | RE7TL11BU | Complementary | minimum pulse duration | 20 ms
26523 | RE7TL11BU | Complementary | reset time | 50 ms
26524 | RE7TL11BU | Complementary | maximum switching voltage | 250 V AC/DC
26525 | RE7TL11BU | Complementary | mechanical durability | 20000000 cycles
26526 | RE7TL11BU | Complementary | [Ith] conventional free air thermal current | 8 A
26527 | RE7TL11BU | Complementary | maximum [Ie] rated operational current | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 3 A AC-15 at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660
26528 | RE7TL11BU | Complementary | minimum switching capacity | at 12 V 10 mA
26529 | RE7TL11BU | Complementary | marking | CE
26530 | RE7TL11BU | Complementary | overvoltage category | III conforming to IEC 60664-1
26531 | RE7TL11BU | Complementary | [Ui] rated insulation voltage | 250 V between contact circuit and control inputs IEC certified 250 V between contact circuit and power supply IEC certified 300 V between contact circuit and control inputs CSA certified 300 V between contact circuit and power supply CSA certified
26532 | RE7TL11BU | Complementary | supply disconnection value | > 0.1 Uc
26533 | RE7TL11BU | Complementary | operating position | Any position without derating
26534 | RE7TL11BU | Complementary | surge withstand | 2 kV conforming to IEC 61000-4-5 level 3
26535 | RE7TL11BU | Complementary | power consumption in VA | 0.7 VA at 24 V 1.8 VA at 110 V 8.5 VA at 240 V
26536 | RE7TL11BU | Complementary | maximum power consumption in W | 0.5 W at 24 V
26537 | RE7TL11BU | Complementary | terminal description | (15-16-18)OC_OFF (B1-A2)CO ALT
26538 | RE7TL11BU | Complementary | height | 78 mm
26539 | RE7TL11BU | Complementary | width | 22.5 mm
26540 | RE7TL11BU | Complementary | depth | 80 mm
26541 | RE7TL11BU | Complementary | net weight | 0.15 kg
26542 | RE7TL11BU | Environment | immunity to microbreaks | 3 ms
26543 | RE7TL11BU | Environment | standards | EN/IEC 61812-1
26544 | RE7TL11BU | Environment | product certifications | CSA GL UL
26545 | RE7TL11BU | Environment | ambient air temperature for storage | -40…85 °C
26546 | RE7TL11BU | Environment | ambient air temperature for operation | -20…60 °C
26547 | RE7TL11BU | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26548 | RE7TL11BU | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
26549 | RE7TL11BU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26550 | RE7TL11BU | Environment | IP degree of protection | IP20 (terminals) IP50 (housing)
26551 | RE7TL11BU | Environment | pollution degree | 3 conforming to IEC 60664-1
26552 | RE7TL11BU | Environment | dielectric strength | 2.5 kV
26553 | RE7TL11BU | Environment | non-dissipating shock wave | 4.8 kV
26554 | RE7TL11BU | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to IEC 61000-4-2 level 3 8 kV in air conforming to IEC 61000-4-2 level 3
26555 | RE7TL11BU | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26556 | RE7TL11BU | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26557 | RE7TL11BU | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
26558 | RE7TL11BU | Contractual warranty | Warranty | 18 months
26559 | RE7TP13BU | Main | range of product | Zelio Time
26560 | RE7TP13BU | Main | product or component type | Industrial timing relay
26561 | RE7TP13BU | Main | contacts type and composition | 2 C/O
26562 | RE7TP13BU | Main | component name | RE7
26563 | RE7TP13BU | Main | time delay type | A
26564 | RE7TP13BU | Main | time delay range | 0.05 s...300 h
26565 | RE7TP13BU | Complementary | discrete output type | Relay
26566 | RE7TP13BU | Complementary | contacts material | 90/10 silver nickel contacts
26567 | RE7TP13BU | Complementary | width pitch dimension | 22.5 mm
26568 | RE7TP13BU | Complementary | [Us] rated supply voltage | 110...240 V AC 50/60 Hz 24 V AC/DC 50/60 Hz 42...48 V AC/DC 50/60 Hz
26569 | RE7TP13BU | Complementary | voltage range | 0.85...1.1 Us
26570 | RE7TP13BU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end
26571 | RE7TP13BU | Complementary | tightening torque | 0.6…1.1 N.m
26572 | RE7TP13BU | Complementary | setting accuracy of time delay | +/- 10 % of full scale
26573 | RE7TP13BU | Complementary | repeat accuracy | +/- 0.2 %
26574 | RE7TP13BU | Complementary | temperature drift | < 0.07 %/°C
26575 | RE7TP13BU | Complementary | voltage drift | < 0.2 %/V
26576 | RE7TP13BU | Complementary | minimum pulse duration | 20 ms
26577 | RE7TP13BU | Complementary | reset time | 50 ms
26578 | RE7TP13BU | Complementary | maximum switching voltage | 250 V AC/DC
26579 | RE7TP13BU | Complementary | mechanical durability | 20000000 cycles
26580 | RE7TP13BU | Complementary | [Ith] conventional free air thermal current | 8 A
26581 | RE7TP13BU | Complementary | maximum [Ie] rated operational current | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 3 A AC-15 at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660
26582 | RE7TP13BU | Complementary | minimum switching capacity | at 12 V 10 mA
26583 | RE7TP13BU | Complementary | potentiometer characteristic | Linear 47 kOhm (+/- 20 %), 0.2 W, cable length <25 m Z1Z2 terminal(s)
26584 | RE7TP13BU | Complementary | marking | CE
26585 | RE7TP13BU | Complementary | overvoltage category | III conforming to IEC 60664-1
26586 | RE7TP13BU | Complementary | [Ui] rated insulation voltage | 250 V between contact circuit and control inputs IEC certified 250 V between contact circuit and power supply IEC certified 300 V between contact circuit and control inputs CSA certified 300 V between contact circuit and power supply CSA certified
26587 | RE7TP13BU | Complementary | supply disconnection value | > 0.1 Uc
26588 | RE7TP13BU | Complementary | operating position | Any position without derating
26589 | RE7TP13BU | Complementary | surge withstand | 2 kV conforming to IEC 61000-4-5 level 3
26590 | RE7TP13BU | Complementary | power consumption in VA | 2 VA at 48 V 1.2 VA at 24 V 12.5 VA at 240 V 2.8 VA at 110 V
26591 | RE7TP13BU | Complementary | maximum power consumption in W | 0.8 W at 24 V 1.6 W at 48 V
26592 | RE7TP13BU | Complementary | terminal description | (B1-A2)CO (Z2)UNUSED (15-16-18)OC_OFF (Z1)UNUSED ALT (25-26-28)OC_ON
26593 | RE7TP13BU | Complementary | height | 78 mm
26594 | RE7TP13BU | Complementary | width | 22.5 mm
26595 | RE7TP13BU | Complementary | depth | 80 mm
26596 | RE7TP13BU | Complementary | net weight | 0.15 kg
26597 | RE7TP13BU | Environment | immunity to microbreaks | 3 ms
26598 | RE7TP13BU | Environment | standards | EN/IEC 61812-1
26599 | RE7TP13BU | Environment | product certifications | GL CSA UL
26600 | RE7TP13BU | Environment | ambient air temperature for storage | -40…85 °C
26601 | RE7TP13BU | Environment | ambient air temperature for operation | -20…60 °C
26602 | RE7TP13BU | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26603 | RE7TP13BU | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
26604 | RE7TP13BU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26605 | RE7TP13BU | Environment | IP degree of protection | IP20 (terminals) IP50 (housing)
26606 | RE7TP13BU | Environment | pollution degree | 3 conforming to IEC 60664-1
26607 | RE7TP13BU | Environment | dielectric strength | 2.5 kV
26608 | RE7TP13BU | Environment | non-dissipating shock wave | 4.8 kV
26609 | RE7TP13BU | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to IEC 61000-4-2 level 3 8 kV in air conforming to IEC 61000-4-2 level 3
26610 | RE7TP13BU | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26611 | RE7TP13BU | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26612 | RE7TP13BU | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
26613 | RE7TP13BU | Contractual warranty | Warranty | 18 months
26614 | RE7RB11MW | Main | range of product | Zelio Time
26615 | RE7RB11MW | Main | product or component type | Industrial timing relay
26616 | RE7RB11MW | Main | component name | RE7
26617 | RE7RB11MW | Main | time delay type | K
26618 | RE7RB11MW | Main | time delay range | 0.05 s...10 min
26619 | RE7RB11MW | Complementary | discrete output type | Relay
26620 | RE7RB11MW | Complementary | contacts material | Silver with gold flashed contacts
26621 | RE7RB11MW | Complementary | width pitch dimension | 22.5 mm
26622 | RE7RB11MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
26623 | RE7RB11MW | Complementary | voltage range | 0.85...1.1 Us
26624 | RE7RB11MW | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end
26625 | RE7RB11MW | Complementary | tightening torque | 0.6…1.1 N.m
26626 | RE7RB11MW | Complementary | setting accuracy of time delay | +/- 10 % of full scale
26627 | RE7RB11MW | Complementary | repeat accuracy | +/- 0.2 %
26628 | RE7RB11MW | Complementary | temperature drift | < 0.07 %/°C
26629 | RE7RB11MW | Complementary | voltage drift | < 0.2 %/V
26630 | RE7RB11MW | Complementary | minimum pulse duration | 1 s
26631 | RE7RB11MW | Complementary | reset time | 50 ms
26632 | RE7RB11MW | Complementary | maximum switching voltage | 250 V AC/DC
26633 | RE7RB11MW | Complementary | mechanical durability | 20000000 cycles
26634 | RE7RB11MW | Complementary | [Ith] conventional free air thermal current | 5 A
26635 | RE7RB11MW | Complementary | maximum [Ie] rated operational current | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 3 A AC-15 at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660
26636 | RE7RB11MW | Complementary | minimum switching capacity | at 12 V 10 mA
26637 | RE7RB11MW | Complementary | potentiometer characteristic | Linear 47 kOhm (+/- 20 %), 0.2 W, cable length <25 m Z1Z2 terminal(s)
26638 | RE7RB11MW | Complementary | marking | CE
26639 | RE7RB11MW | Complementary | overvoltage category | III conforming to IEC 60664-1
26640 | RE7RB11MW | Complementary | [Ui] rated insulation voltage | 250 V between contact circuit and control inputs IEC certified 250 V between contact circuit and power supply IEC certified 300 V between contact circuit and control inputs CSA certified 300 V between contact circuit and power supply CSA certified
26641 | RE7RB11MW | Complementary | supply disconnection value | > 0.1 Uc
26642 | RE7RB11MW | Complementary | operating position | Any position without derating
26643 | RE7RB11MW | Complementary | surge withstand | 2 kV conforming to IEC 61000-4-5 level 3
26644 | RE7RB11MW | Complementary | power consumption in VA | 2 VA at 24 V 6 VA at 240 V 2.5 VA at 48 V 3.2 VA at 110 V
26645 | RE7RB11MW | Complementary | maximum power consumption in W | 1 W at 48 V 2 W at 24 V 2 W at 240 V 3.2 W at 110 V
26646 | RE7RB11MW | Complementary | peak current | 0.001 kA for 30 s on energisation
26647 | RE7RB11MW | Complementary | terminal description | (A1-A2)CO (15-16-18)OC_OFF
26648 | RE7RB11MW | Complementary | height | 78 mm
26649 | RE7RB11MW | Complementary | width | 22.5 mm
26650 | RE7RB11MW | Complementary | depth | 80 mm
26651 | RE7RB11MW | Complementary | net weight | 0.15 kg
26652 | RE7RB11MW | Environment | immunity to microbreaks | 3 ms
26653 | RE7RB11MW | Environment | standards | EN/IEC 61812-1
26654 | RE7RB11MW | Environment | product certifications | GL CSA UL
26655 | RE7RB11MW | Environment | ambient air temperature for storage | -40…85 °C
26656 | RE7RB11MW | Environment | ambient air temperature for operation | -20…60 °C
26657 | RE7RB11MW | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26658 | RE7RB11MW | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
26659 | RE7RB11MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26660 | RE7RB11MW | Environment | IP degree of protection | IP20 (terminals) IP50 (housing)
26661 | RE7RB11MW | Environment | pollution degree | 3 conforming to IEC 60664-1
26662 | RE7RB11MW | Environment | dielectric strength | 2.5 kV
26663 | RE7RB11MW | Environment | non-dissipating shock wave | 4.8 kV
26664 | RE7RB11MW | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to IEC 61000-4-2 level 3 8 kV in air conforming to IEC 61000-4-2 level 3
26665 | RE7RB11MW | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26666 | RE7RB11MW | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26667 | RE7RB11MW | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
26668 | RE7RB11MW | Contractual warranty | Warranty | 18 months
26669 | RE7RB13MW | Main | range of product | Zelio Time
26670 | RE7RB13MW | Main | product or component type | Industrial timing relay
26671 | RE7RB13MW | Main | contacts type and composition | 2 C/O
26672 | RE7RB13MW | Main | component name | RE7
26673 | RE7RB13MW | Main | time delay type | K
26674 | RE7RB13MW | Main | time delay range | 0.05 s...10 min
26675 | RE7RB13MW | Complementary | discrete output type | Relay
26676 | RE7RB13MW | Complementary | contacts material | Silver with gold flashed contacts
26677 | RE7RB13MW | Complementary | width pitch dimension | 22.5 mm
26678 | RE7RB13MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
26679 | RE7RB13MW | Complementary | voltage range | 0.85...1.1 Us
26680 | RE7RB13MW | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end
26681 | RE7RB13MW | Complementary | tightening torque | 0.6…1.1 N.m
26682 | RE7RB13MW | Complementary | setting accuracy of time delay | +/- 10 % of full scale
26683 | RE7RB13MW | Complementary | repeat accuracy | +/- 0.2 %
26684 | RE7RB13MW | Complementary | temperature drift | < 0.07 %/°C
26685 | RE7RB13MW | Complementary | voltage drift | < 0.2 %/V
26686 | RE7RB13MW | Complementary | minimum pulse duration | 1 s
26687 | RE7RB13MW | Complementary | reset time | 50 ms
26688 | RE7RB13MW | Complementary | maximum switching voltage | 250 V AC/DC
26689 | RE7RB13MW | Complementary | mechanical durability | 20000000 cycles
26690 | RE7RB13MW | Complementary | [Ith] conventional free air thermal current | 5 A
26691 | RE7RB13MW | Complementary | maximum [Ie] rated operational current | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 3 A AC-15 at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660
26692 | RE7RB13MW | Complementary | minimum switching capacity | at 12 V 10 mA
26693 | RE7RB13MW | Complementary | potentiometer characteristic | Linear 47 kOhm (+/- 20 %), 0.2 W, cable length <25 m Z1Z2 terminal(s)
26694 | RE7RB13MW | Complementary | marking | CE
26695 | RE7RB13MW | Complementary | overvoltage category | III conforming to IEC 60664-1
26696 | RE7RB13MW | Complementary | [Ui] rated insulation voltage | 250 V between contact circuit and control inputs IEC certified 250 V between contact circuit and power supply IEC certified 300 V between contact circuit and control inputs CSA certified 300 V between contact circuit and power supply CSA certified
26697 | RE7RB13MW | Complementary | supply disconnection value | > 0.1 Uc
26698 | RE7RB13MW | Complementary | operating position | Any position without derating
26699 | RE7RB13MW | Complementary | surge withstand | 2 kV conforming to IEC 61000-4-5 level 3
26700 | RE7RB13MW | Complementary | power consumption in VA | 2 VA at 24 V 6 VA at 240 V 2.5 VA at 48 V 3.2 VA at 110 V
26701 | RE7RB13MW | Complementary | maximum power consumption in W | 1 W at 48 V 2 W at 24 V 2 W at 240 V 3.2 W at 110 V
26702 | RE7RB13MW | Complementary | peak current | 0.001 kA for 30 s on energisation
26703 | RE7RB13MW | Complementary | terminal description | (15-16-18)OC_OFF (25-26-28)OC_OFF (Z1)UNUSED (Z2)UNUSED (A1-A2)CO
26704 | RE7RB13MW | Complementary | height | 78 mm
26705 | RE7RB13MW | Complementary | width | 22.5 mm
26706 | RE7RB13MW | Complementary | depth | 80 mm
26707 | RE7RB13MW | Complementary | net weight | 0.15 kg
26708 | RE7RB13MW | Environment | immunity to microbreaks | 3 ms
26709 | RE7RB13MW | Environment | standards | EN/IEC 61812-1
26710 | RE7RB13MW | Environment | product certifications | GL CSA UL
26711 | RE7RB13MW | Environment | ambient air temperature for storage | -40…85 °C
26712 | RE7RB13MW | Environment | ambient air temperature for operation | -20…60 °C
26713 | RE7RB13MW | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26714 | RE7RB13MW | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
26715 | RE7RB13MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26716 | RE7RB13MW | Environment | IP degree of protection | IP20 (terminals) IP50 (housing)
26717 | RE7RB13MW | Environment | pollution degree | 3 conforming to IEC 60664-1
26718 | RE7RB13MW | Environment | dielectric strength | 2.5 kV
26719 | RE7RB13MW | Environment | non-dissipating shock wave | 4.8 kV
26720 | RE7RB13MW | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to IEC 61000-4-2 level 3 8 kV in air conforming to IEC 61000-4-2 level 3
26721 | RE7RB13MW | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26722 | RE7RB13MW | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26723 | RE7RB13MW | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
26724 | RE7RB13MW | Contractual warranty | Warranty | 18 months
26725 | RE7MY13MW | Main | range of product | Zelio Time
26726 | RE7MY13MW | Main | product or component type | Industrial timing relay
26727 | RE7MY13MW | Main | contacts type and composition | 2 C/O
26728 | RE7MY13MW | Main | component name | RE7
26729 | RE7MY13MW | Main | time delay type | D A Di Qt W Qg H C
26730 | RE7MY13MW | Main | time delay range | 0.05 s...300 h
26731 | RE7MY13MW | Complementary | discrete output type | Relay
26732 | RE7MY13MW | Complementary | contacts material | 90/10 silver nickel contacts
26733 | RE7MY13MW | Complementary | width pitch dimension | 22.5 mm
26734 | RE7MY13MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
26735 | RE7MY13MW | Complementary | voltage range | 0.85...1.1 Us
26736 | RE7MY13MW | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end
26737 | RE7MY13MW | Complementary | tightening torque | 0.6…1.1 N.m
26738 | RE7MY13MW | Complementary | setting accuracy of time delay | +/- 10 % of full scale
26739 | RE7MY13MW | Complementary | repeat accuracy | +/- 0.2 %
26740 | RE7MY13MW | Complementary | temperature drift | < 0.07 %/°C
26741 | RE7MY13MW | Complementary | voltage drift | < 0.2 %/V
26742 | RE7MY13MW | Complementary | minimum pulse duration | 20 ms
26743 | RE7MY13MW | Complementary | reset time | 50 ms
26744 | RE7MY13MW | Complementary | maximum switching voltage | 250 V AC/DC
26745 | RE7MY13MW | Complementary | mechanical durability | 20000000 cycles
26746 | RE7MY13MW | Complementary | [Ith] conventional free air thermal current | 8 A
26747 | RE7MY13MW | Complementary | maximum [Ie] rated operational current | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 3 A AC-15 at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660
26748 | RE7MY13MW | Complementary | minimum switching capacity | at 12 V 10 mA
26749 | RE7MY13MW | Complementary | input voltage | < 60 V X1Z2 terminal(s) < 60 V Y1Z2 terminal(s)
26750 | RE7MY13MW | Complementary | maximum switching current | 1 mA (X1Z2) 1 mA (Y1Z2)
26751 | RE7MY13MW | Complementary | input compatibility | 3/4 wires sensors PNP/NPN without internal load <50 m X1Z2 terminal(s) 3/4 wires sensors PNP/NPN without internal load <50 m Y1Z2 terminal(s)
26752 | RE7MY13MW | Complementary | potentiometer characteristic | Linear 47 kOhm (+/- 20 %), 0.2 W, cable length <25 m Z1Z2 terminal(s)
26753 | RE7MY13MW | Complementary | marking | CE
26754 | RE7MY13MW | Complementary | overvoltage category | III conforming to IEC 60664-1
26755 | RE7MY13MW | Complementary | [Ui] rated insulation voltage | 250 V between contact circuit and control inputs IEC certified 250 V between contact circuit and power supply IEC certified 300 V between contact circuit and control inputs CSA certified 300 V between contact circuit and power supply CSA certified
26756 | RE7MY13MW | Complementary | supply disconnection value | > 0.1 Uc
26757 | RE7MY13MW | Complementary | operating position | Any position without derating
26758 | RE7MY13MW | Complementary | surge withstand | 2 kV conforming to IEC 61000-4-5 level 3
26759 | RE7MY13MW | Complementary | power consumption in VA | 2 VA at 24 V 6 VA at 240 V 2.5 VA at 48 V 3.2 VA at 110 V
26760 | RE7MY13MW | Complementary | maximum power consumption in W | 1 W at 48 V 2 W at 24 V 2 W at 240 V 3.2 W at 110 V
26761 | RE7MY13MW | Complementary | peak current | 0.001 kA for 30 s on energisation
26762 | RE7MY13MW | Complementary | terminal description | (25-26-28)OC_OFF (15-16-18)OC_OFF (Z1)UNUSED (X1)UNUSED (Y1)UNUSED (Z2)UNUSED (A1-A2)CO
26763 | RE7MY13MW | Complementary | height | 78 mm
26764 | RE7MY13MW | Complementary | width | 22.5 mm
26765 | RE7MY13MW | Complementary | depth | 80 mm
26766 | RE7MY13MW | Complementary | net weight | 0.15 kg
26767 | RE7MY13MW | Environment | immunity to microbreaks | 3 ms
26768 | RE7MY13MW | Environment | standards | EN/IEC 61812-1
26769 | RE7MY13MW | Environment | product certifications | GL UL CSA
26770 | RE7MY13MW | Environment | ambient air temperature for storage | -40…85 °C
26771 | RE7MY13MW | Environment | ambient air temperature for operation | -20…60 °C
26772 | RE7MY13MW | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26773 | RE7MY13MW | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
26774 | RE7MY13MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26775 | RE7MY13MW | Environment | IP degree of protection | IP20 (terminals) IP50 (housing)
26776 | RE7MY13MW | Environment | pollution degree | 3 conforming to IEC 60664-1
26777 | RE7MY13MW | Environment | dielectric strength | 2.5 kV
26778 | RE7MY13MW | Environment | non-dissipating shock wave | 4.8 kV
26779 | RE7MY13MW | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to IEC 61000-4-2 level 3 8 kV in air conforming to IEC 61000-4-2 level 3
26780 | RE7MY13MW | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26781 | RE7MY13MW | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26782 | RE7MY13MW | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
26783 | RE7MY13MW | Contractual warranty | Warranty | 18 months
26784 | RE7ML11BU | Main | range of product | Zelio Time
26785 | RE7ML11BU | Main | product or component type | Industrial timing relay
26786 | RE7ML11BU | Main | component name | RE7
26787 | RE7ML11BU | Main | time delay type | Di D W C A H
26788 | RE7ML11BU | Main | time delay range | 0.05 s...300 h
26789 | RE7ML11BU | Complementary | discrete output type | Relay
26790 | RE7ML11BU | Complementary | contacts material | 90/10 silver nickel contacts
26791 | RE7ML11BU | Complementary | width pitch dimension | 22.5 mm
26792 | RE7ML11BU | Complementary | [Us] rated supply voltage | 110...240 V AC 50/60 Hz 24 V AC/DC 50/60 Hz 42...48 V AC/DC 50/60 Hz
26793 | RE7ML11BU | Complementary | voltage range | 0.85...1.1 Us
26794 | RE7ML11BU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end
26795 | RE7ML11BU | Complementary | tightening torque | 0.6…1.1 N.m
26796 | RE7ML11BU | Complementary | setting accuracy of time delay | +/- 10 % of full scale
26797 | RE7ML11BU | Complementary | repeat accuracy | +/- 0.2 %
26798 | RE7ML11BU | Complementary | temperature drift | < 0.07 %/°C
26799 | RE7ML11BU | Complementary | voltage drift | < 0.2 %/V
26800 | RE7ML11BU | Complementary | minimum pulse duration | 20 ms
26801 | RE7ML11BU | Complementary | reset time | 50 ms
26802 | RE7ML11BU | Complementary | maximum switching voltage | 250 V AC/DC
26803 | RE7ML11BU | Complementary | mechanical durability | 20000000 cycles
26804 | RE7ML11BU | Complementary | [Ith] conventional free air thermal current | 8 A
26805 | RE7ML11BU | Complementary | maximum [Ie] rated operational current | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 3 A AC-15 at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660
26806 | RE7ML11BU | Complementary | minimum switching capacity | at 12 V 10 mA
26807 | RE7ML11BU | Complementary | input voltage | < 60 V X1Z2 terminal(s) < 60 V Y1Z2 terminal(s)
26808 | RE7ML11BU | Complementary | maximum switching current | 1 mA (X1Z2) 1 mA (Y1Z2)
26809 | RE7ML11BU | Complementary | input compatibility | 3/4 wires sensors PNP/NPN without internal load <50 m X1Z2 terminal(s) 3/4 wires sensors PNP/NPN without internal load <50 m Y1Z2 terminal(s)
26810 | RE7ML11BU | Complementary | potentiometer characteristic | Linear 47 kOhm (+/- 20 %), 0.2 W, cable length <25 m Z1Z2 terminal(s)
26811 | RE7ML11BU | Complementary | marking | CE
26812 | RE7ML11BU | Complementary | overvoltage category | III conforming to IEC 60664-1
26813 | RE7ML11BU | Complementary | [Ui] rated insulation voltage | 250 V between contact circuit and control inputs IEC certified 250 V between contact circuit and power supply IEC certified 300 V between contact circuit and control inputs CSA certified 300 V between contact circuit and power supply CSA certified
26814 | RE7ML11BU | Complementary | supply disconnection value | > 0.1 Uc
26815 | RE7ML11BU | Complementary | operating position | Any position without derating
26816 | RE7ML11BU | Complementary | surge withstand | 2 kV conforming to IEC 61000-4-5 level 3
26817 | RE7ML11BU | Complementary | power consumption in VA | 0.7 VA at 24 V 1.6 VA at 48 V 1.8 VA at 110 V 8.5 VA at 240 V
26818 | RE7ML11BU | Complementary | maximum power consumption in W | 0.5 W at 24 V 1.2 W at 48 V
26819 | RE7ML11BU | Complementary | terminal description | (Y1)UNUSED (15-16-18)OC (Z1)UNUSED (Z2)UNUSED (B1-A2)CO ALT (X1)UNUSED
26820 | RE7ML11BU | Complementary | height | 78 mm
26821 | RE7ML11BU | Complementary | width | 22.5 mm
26822 | RE7ML11BU | Complementary | depth | 80 mm
26823 | RE7ML11BU | Complementary | net weight | 0.15 kg
26824 | RE7ML11BU | Environment | immunity to microbreaks | 3 ms
26825 | RE7ML11BU | Environment | standards | EN/IEC 61812-1
26826 | RE7ML11BU | Environment | product certifications | CSA GL UL
26827 | RE7ML11BU | Environment | ambient air temperature for storage | -40…85 °C
26828 | RE7ML11BU | Environment | ambient air temperature for operation | -20…60 °C
26829 | RE7ML11BU | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26830 | RE7ML11BU | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
26831 | RE7ML11BU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26832 | RE7ML11BU | Environment | IP degree of protection | IP20 (terminals) IP50 (housing)
26833 | RE7ML11BU | Environment | pollution degree | 3 conforming to IEC 60664-1
26834 | RE7ML11BU | Environment | dielectric strength | 2.5 kV
26835 | RE7ML11BU | Environment | non-dissipating shock wave | 4.8 kV
26836 | RE7ML11BU | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to IEC 61000-4-2 level 3 8 kV in air conforming to IEC 61000-4-2 level 3
26837 | RE7ML11BU | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26838 | RE7ML11BU | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26839 | RE7ML11BU | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
26840 | RE7ML11BU | Contractual warranty | Warranty | 18 months
26841 | RE7CV11BU | Main | range of product | Zelio Time
26842 | RE7CV11BU | Main | product or component type | Industrial timing relay
26843 | RE7CV11BU | Main | component name | RE7
26844 | RE7CV11BU | Main | time delay type | L Lt Li
26845 | RE7CV11BU | Main | time delay range | 0.05 s...300 h
26846 | RE7CV11BU | Complementary | discrete output type | Relay
26847 | RE7CV11BU | Complementary | contacts material | 90/10 silver nickel contacts
26848 | RE7CV11BU | Complementary | width pitch dimension | 22.5 mm
26849 | RE7CV11BU | Complementary | [Us] rated supply voltage | 110...240 V AC 50/60 Hz 24 V AC/DC 50/60 Hz 42...48 V AC/DC 50/60 Hz
26850 | RE7CV11BU | Complementary | voltage range | 0.85...1.1 Us
26851 | RE7CV11BU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end
26852 | RE7CV11BU | Complementary | tightening torque | 0.6…1.1 N.m
26853 | RE7CV11BU | Complementary | setting accuracy of time delay | +/- 10 % of full scale
26854 | RE7CV11BU | Complementary | repeat accuracy | +/- 0.2 %
26855 | RE7CV11BU | Complementary | temperature drift | < 0.07 %/°C
26856 | RE7CV11BU | Complementary | voltage drift | < 0.2 %/V
26857 | RE7CV11BU | Complementary | minimum pulse duration | 20 ms
26858 | RE7CV11BU | Complementary | reset time | 50 ms
26859 | RE7CV11BU | Complementary | maximum switching voltage | 250 V AC/DC
26860 | RE7CV11BU | Complementary | mechanical durability | 20000000 cycles
26861 | RE7CV11BU | Complementary | [Ith] conventional free air thermal current | 8 A
26862 | RE7CV11BU | Complementary | maximum [Ie] rated operational current | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 3 A AC-15 at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660
26863 | RE7CV11BU | Complementary | minimum switching capacity | at 12 V 10 mA
26864 | RE7CV11BU | Complementary | input voltage | < 60 V X1Z2 terminal(s) < 60 V X2Z2 terminal(s)
26865 | RE7CV11BU | Complementary | maximum switching current | 1 mA (X1Z2) 1 mA (X2Z2)
26866 | RE7CV11BU | Complementary | input compatibility | 3/4 wires sensors PNP/NPN without internal load <50 m X1Z2 terminal(s) 3/4 wires sensors PNP/NPN without internal load <50 m X2Z2 terminal(s)
26867 | RE7CV11BU | Complementary | potentiometer characteristic | Linear 47 kOhm (+/- 20 %), 0.2 W, cable length <25 m Z1Z2 terminal(s)
26868 | RE7CV11BU | Complementary | marking | CE
26869 | RE7CV11BU | Complementary | overvoltage category | III conforming to IEC 60664-1
26870 | RE7CV11BU | Complementary | [Ui] rated insulation voltage | 250 V between contact circuit and control inputs IEC certified 250 V between contact circuit and power supply IEC certified 300 V between contact circuit and control inputs CSA certified 300 V between contact circuit and power supply CSA certified
26871 | RE7CV11BU | Complementary | supply disconnection value | > 0.1 Uc
26872 | RE7CV11BU | Complementary | operating position | Any position without derating
26873 | RE7CV11BU | Complementary | surge withstand | 2 kV conforming to IEC 61000-4-5 level 3
26874 | RE7CV11BU | Complementary | power consumption in VA | 0.7 VA at 24 V 1.6 VA at 48 V 1.8 VA at 110 V 8.5 VA at 240 V
26875 | RE7CV11BU | Complementary | maximum power consumption in W | 0.5 W at 24 V 1.2 W at 48 V
26876 | RE7CV11BU | Complementary | terminal description | (B1-A2)CO ALT (15-16-18)OC_OFF
26877 | RE7CV11BU | Complementary | height | 78 mm
26878 | RE7CV11BU | Complementary | width | 22.5 mm
26879 | RE7CV11BU | Complementary | depth | 80 mm
26880 | RE7CV11BU | Complementary | net weight | 0.15 kg
26881 | RE7CV11BU | Environment | immunity to microbreaks | 3 ms
26882 | RE7CV11BU | Environment | standards | EN/IEC 61812-1
26883 | RE7CV11BU | Environment | product certifications | UL CSA GL
26884 | RE7CV11BU | Environment | ambient air temperature for storage | -40…85 °C
26885 | RE7CV11BU | Environment | ambient air temperature for operation | -20…60 °C
26886 | RE7CV11BU | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26887 | RE7CV11BU | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
26888 | RE7CV11BU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26889 | RE7CV11BU | Environment | IP degree of protection | IP20 (terminals) IP50 (housing)
26890 | RE7CV11BU | Environment | pollution degree | 3 conforming to IEC 60664-1
26891 | RE7CV11BU | Environment | dielectric strength | 2.5 kV
26892 | RE7CV11BU | Environment | non-dissipating shock wave | 4.8 kV
26893 | RE7CV11BU | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to IEC 61000-4-2 level 3 8 kV in air conforming to IEC 61000-4-2 level 3
26894 | RE7CV11BU | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26895 | RE7CV11BU | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26896 | RE7CV11BU | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
26897 | RE7CV11BU | Contractual warranty | Warranty | 18 months
26898 | RE7YA12BU | Main | range of product | Zelio Time
26899 | RE7YA12BU | Main | product or component type | Industrial timing relay
26900 | RE7YA12BU | Main | contacts type and composition | 2 C/O
26901 | RE7YA12BU | Main | component name | RE7
26902 | RE7YA12BU | Main | time delay type | Qt
26903 | RE7YA12BU | Main | time delay range | 0.05 s...300 h
26904 | RE7YA12BU | Complementary | discrete output type | Relay
26905 | RE7YA12BU | Complementary | contacts material | 90/10 silver nickel contacts
26906 | RE7YA12BU | Complementary | width pitch dimension | 22.5 mm
26907 | RE7YA12BU | Complementary | [Us] rated supply voltage | 110...240 V AC 50/60 Hz 24 V AC/DC 50/60 Hz 42...48 V AC/DC 50/60 Hz
26908 | RE7YA12BU | Complementary | voltage range | 0.85...1.1 Us
26909 | RE7YA12BU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end
26910 | RE7YA12BU | Complementary | tightening torque | 0.6…1.1 N.m
26911 | RE7YA12BU | Complementary | setting accuracy of time delay | +/- 10 % of full scale
26912 | RE7YA12BU | Complementary | repeat accuracy | +/- 0.2 %
26913 | RE7YA12BU | Complementary | temperature drift | < 0.07 %/°C
26914 | RE7YA12BU | Complementary | voltage drift | < 0.2 %/V
26915 | RE7YA12BU | Complementary | minimum pulse duration | 20 ms
26916 | RE7YA12BU | Complementary | reset time | 50 ms
26917 | RE7YA12BU | Complementary | maximum switching voltage | 250 V AC/DC
26918 | RE7YA12BU | Complementary | mechanical durability | 20000000 cycles
26919 | RE7YA12BU | Complementary | [Ith] conventional free air thermal current | 8 A
26920 | RE7YA12BU | Complementary | maximum [Ie] rated operational current | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 3 A AC-15 at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660
26921 | RE7YA12BU | Complementary | minimum switching capacity | at 12 V 10 mA
26922 | RE7YA12BU | Complementary | marking | CE
26923 | RE7YA12BU | Complementary | overvoltage category | III conforming to IEC 60664-1
26924 | RE7YA12BU | Complementary | [Ui] rated insulation voltage | 250 V between contact circuit and control inputs IEC certified 250 V between contact circuit and power supply IEC certified 300 V between contact circuit and control inputs CSA certified 300 V between contact circuit and power supply CSA certified
26925 | RE7YA12BU | Complementary | supply disconnection value | > 0.1 Uc
26926 | RE7YA12BU | Complementary | operating position | Any position without derating
26927 | RE7YA12BU | Complementary | surge withstand | 2 kV conforming to IEC 61000-4-5 level 3
26928 | RE7YA12BU | Complementary | power consumption in VA | 2 VA at 48 V 1.2 VA at 24 V 12.5 VA at 240 V 2.8 VA at 110 V
26929 | RE7YA12BU | Complementary | maximum power consumption in W | 0.8 W at 24 V 1.6 W at 48 V
26930 | RE7YA12BU | Complementary | terminal description | (B1-A2)CO (25-26-28)OC_ON ALT (15-16-18)OC_ON (Z2)UNUSED
26931 | RE7YA12BU | Complementary | height | 78 mm
26932 | RE7YA12BU | Complementary | width | 22.5 mm
26933 | RE7YA12BU | Complementary | depth | 80 mm
26934 | RE7YA12BU | Complementary | net weight | 0.15 kg
26935 | RE7YA12BU | Environment | immunity to microbreaks | 3 ms
26936 | RE7YA12BU | Environment | standards | EN/IEC 61812-1
26937 | RE7YA12BU | Environment | product certifications | GL UL CSA
26938 | RE7YA12BU | Environment | ambient air temperature for storage | -40…85 °C
26939 | RE7YA12BU | Environment | ambient air temperature for operation | -20…60 °C
26940 | RE7YA12BU | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26941 | RE7YA12BU | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
26942 | RE7YA12BU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
26943 | RE7YA12BU | Environment | IP degree of protection | IP20 (terminals) IP50 (housing)
26944 | RE7YA12BU | Environment | pollution degree | 3 conforming to IEC 60664-1
26945 | RE7YA12BU | Environment | dielectric strength | 2.5 kV
26946 | RE7YA12BU | Environment | non-dissipating shock wave | 4.8 kV
26947 | RE7YA12BU | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to IEC 61000-4-2 level 3 8 kV in air conforming to IEC 61000-4-2 level 3
26948 | RE7YA12BU | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
26949 | RE7YA12BU | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
26950 | RE7YA12BU | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
26951 | RE7YA12BU | Contractual warranty | Warranty | 18 months
26952 | RE8TA11BU | Main | range of product | Zelio Time
26953 | RE8TA11BU | Main | product or component type | Optimum industrial timing relay
26954 | RE8TA11BU | Main | component name | RE8
26955 | RE8TA11BU | Main | time delay type | A
26956 | RE8TA11BU | Main | time delay range | 0.1...10 s
26957 | RE8TA11BU | Main | sale per indivisible quantity | 1
26958 | RE8TA11BU | Complementary | discrete output type | Relay
26959 | RE8TA11BU | Complementary | contacts material | Silver nickel contacts
26960 | RE8TA11BU | Complementary | width pitch dimension | 22.5 mm
26961 | RE8TA11BU | Complementary | [Us] rated supply voltage | 110...240 V AC 50/60 Hz 24 V AC/DC 50/60 Hz
26962 | RE8TA11BU | Complementary | voltage range | 0.9...1.1 Us
26963 | RE8TA11BU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end
26964 | RE8TA11BU | Complementary | tightening torque | 0.6…1.1 N.m
26965 | RE8TA11BU | Complementary | setting accuracy of time delay | +/- 20 % of full scale
26966 | RE8TA11BU | Complementary | repeat accuracy | < 1 %
26967 | RE8TA11BU | Complementary | voltage drift | < 2.5 %/V
26968 | RE8TA11BU | Complementary | temperature drift | < 0.2 %/°C
26969 | RE8TA11BU | Complementary | minimum pulse duration | 26 ms
26970 | RE8TA11BU | Complementary | reset time | 50 ms
26971 | RE8TA11BU | Complementary | maximum switching voltage | 250 V
26972 | RE8TA11BU | Complementary | mechanical durability | 20000000 cycles
26973 | RE8TA11BU | Complementary | [Ith] conventional free air thermal current | 8 A
26974 | RE8TA11BU | Complementary | maximum [Ie] rated operational current | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991 2 A DC-13 24 V at 70 °C conforming to VDE 0660 3 A AC-15 24 V at 70 °C conforming to IEC 60947-5-1/1991 3 A AC-15 24 V at 70 °C conforming to VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991 0.1 A DC-13 250 V at 70 °C conforming to VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991 0.2 A DC-13 115 V at 70 °C conforming to VDE 0660
26975 | RE8TA11BU | Complementary | minimum switching capacity | at 12 V 10 mA
26976 | RE8TA11BU | Complementary | marking | CE
26977 | RE8TA11BU | Complementary | overvoltage category | III conforming to IEC 60664-1
26978 | RE8TA11BU | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 300 V conforming to CSA
26979 | RE8TA11BU | Complementary | supply disconnection value | > 0.1 Uc
26980 | RE8TA11BU | Complementary | operating position | Any position without derating
26981 | RE8TA11BU | Complementary | surge withstand | 2 kV conforming to IEC 61000-4-5 level 3
26982 | RE8TA11BU | Complementary | power consumption in VA | 0.7 VA at 24 V 1.8 VA at 110 V 8.5 VA at 240 V
26983 | RE8TA11BU | Complementary | maximum power consumption in W | 0.5 W at 24 V
26984 | RE8TA11BU | Complementary | terminal description | ALT (A1-B1)CO (15-16-18)OC_OFF
26985 | RE8TA11BU | Complementary | height | 78 mm
26986 | RE8TA11BU | Complementary | width | 22.5 mm
26987 | RE8TA11BU | Complementary | depth | 80 mm
26988 | RE8TA11BU | Complementary | net weight | 0.11 kg
26989 | RE8TA11BU | Environment | immunity to microbreaks | 3 ms
26990 | RE8TA11BU | Environment | standards | EN/IEC 61812-1
26991 | RE8TA11BU | Environment | product certifications | CSA UL GL
26992 | RE8TA11BU | Environment | ambient air temperature for storage | -40…85 °C
26993 | RE8TA11BU | Environment | ambient air temperature for operation | -20…60 °C
26994 | RE8TA11BU | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
26995 | RE8TA11BU | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
26996 | RE8TA11BU | Environment | IP degree of protection | IP20 (terminals) IP50 (casing)
26997 | RE8TA11BU | Environment | pollution degree | 3 conforming to IEC 60664-1
26998 | RE8TA11BU | Environment | dielectric test voltage | 2.5 kV
26999 | RE8TA11BU | Environment | non-dissipating shock wave | 4.8 kV
27000 | RE8TA11BU | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
27001 | RE8TA11BU | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
27002 | RE8TA11BU | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
27003 | RE8TA11BU | Contractual warranty | Warranty | 18 months
27004 | RE8TA21BU | Main | range of product | Zelio Time
27005 | RE8TA21BU | Main | product or component type | Optimum industrial timing relay
27006 | RE8TA21BU | Main | component name | RE8
27007 | RE8TA21BU | Main | time delay type | A
27008 | RE8TA21BU | Main | time delay range | 3...300 s
27009 | RE8TA21BU | Main | sale per indivisible quantity | 1
27010 | RE8TA21BU | Complementary | discrete output type | Relay
27011 | RE8TA21BU | Complementary | contacts material | Silver nickel contacts
27012 | RE8TA21BU | Complementary | width pitch dimension | 22.5 mm
27013 | RE8TA21BU | Complementary | [Us] rated supply voltage | 110...240 V AC 50/60 Hz 24 V AC/DC 50/60 Hz
27014 | RE8TA21BU | Complementary | voltage range | 0.9...1.1 Us
27015 | RE8TA21BU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end
27016 | RE8TA21BU | Complementary | tightening torque | 0.6…1.1 N.m
27017 | RE8TA21BU | Complementary | setting accuracy of time delay | +/- 20 % of full scale
27018 | RE8TA21BU | Complementary | repeat accuracy | < 1 %
27019 | RE8TA21BU | Complementary | voltage drift | < 2.5 %/V
27020 | RE8TA21BU | Complementary | temperature drift | < 0.2 %/°C
27021 | RE8TA21BU | Complementary | minimum pulse duration | 26 ms
27022 | RE8TA21BU | Complementary | reset time | 50 ms
27023 | RE8TA21BU | Complementary | maximum switching voltage | 250 V
27024 | RE8TA21BU | Complementary | mechanical durability | 20000000 cycles
27025 | RE8TA21BU | Complementary | [Ith] conventional free air thermal current | 8 A
27026 | RE8TA21BU | Complementary | maximum [Ie] rated operational current | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991 2 A DC-13 24 V at 70 °C conforming to VDE 0660 3 A AC-15 24 V at 70 °C conforming to IEC 60947-5-1/1991 3 A AC-15 24 V at 70 °C conforming to VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991 0.1 A DC-13 250 V at 70 °C conforming to VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991 0.2 A DC-13 115 V at 70 °C conforming to VDE 0660
27027 | RE8TA21BU | Complementary | minimum switching capacity | at 12 V 10 mA
27028 | RE8TA21BU | Complementary | marking | CE
27029 | RE8TA21BU | Complementary | overvoltage category | III conforming to IEC 60664-1
27030 | RE8TA21BU | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 300 V conforming to CSA
27031 | RE8TA21BU | Complementary | supply disconnection value | > 0.1 Uc
27032 | RE8TA21BU | Complementary | operating position | Any position without derating
27033 | RE8TA21BU | Complementary | surge withstand | 2 kV conforming to IEC 61000-4-5 level 3
27034 | RE8TA21BU | Complementary | power consumption in VA | 0.7 VA at 24 V 1.8 VA at 110 V 8.5 VA at 240 V
27035 | RE8TA21BU | Complementary | maximum power consumption in W | 0.5 W at 24 V
27036 | RE8TA21BU | Complementary | terminal description | ALT (A1-B1)CO (15-16-18)OC_OFF
27037 | RE8TA21BU | Complementary | height | 78 mm
27038 | RE8TA21BU | Complementary | width | 22.5 mm
27039 | RE8TA21BU | Complementary | depth | 80 mm
27040 | RE8TA21BU | Complementary | net weight | 0.11 kg
27041 | RE8TA21BU | Environment | immunity to microbreaks | 3 ms
27042 | RE8TA21BU | Environment | standards | EN/IEC 61812-1
27043 | RE8TA21BU | Environment | product certifications | CSA GL UL
27044 | RE8TA21BU | Environment | ambient air temperature for storage | -40…85 °C
27045 | RE8TA21BU | Environment | ambient air temperature for operation | -20…60 °C
27046 | RE8TA21BU | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
27047 | RE8TA21BU | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
27048 | RE8TA21BU | Environment | IP degree of protection | IP20 (terminals) IP50 (casing)
27049 | RE8TA21BU | Environment | pollution degree | 3 conforming to IEC 60664-1
27050 | RE8TA21BU | Environment | dielectric test voltage | 2.5 kV
27051 | RE8TA21BU | Environment | non-dissipating shock wave | 4.8 kV
27052 | RE8TA21BU | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
27053 | RE8TA21BU | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
27054 | RE8TA21BU | Environment | disturbance radiated/conducted | CISPR 11 group 1 - class A CISPR 22 - class A
27055 | RE8TA21BU | Contractual warranty | Warranty | 18 months
27056 | RE8TA31BU | Main | range of product | Zelio Time
27057 | RE8TA31BU | Main | product or component type | Optimum industrial timing relay
27058 | RE8TA31BU | Main | component name | RE8
27059 | RE8TA31BU | Main | time delay type | A
27060 | RE8TA31BU | Main | time delay range | 0.3...30 s
27061 | RE8TA31BU | Main | sale per indivisible quantity | 1
27062 | RE8TA31BU | Complementary | discrete output type | Relay
27063 | RE8TA31BU | Complementary | contacts material | Silver nickel contacts
27064 | RE8TA31BU | Complementary | width pitch dimension | 22.5 mm
27065 | RE8TA31BU | Complementary | [Us] rated supply voltage | 110...240 V AC 50/60 Hz 24 V AC/DC 50/60 Hz
27066 | RE8TA31BU | Complementary | voltage range | 0.9...1.1 Us
27067 | RE8TA31BU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end
27068 | RE8TA31BU | Complementary | tightening torque | 0.6…1.1 N.m
27069 | RE8TA31BU | Complementary | setting accuracy of time delay | +/- 20 % of full scale
27070 | RE8TA31BU | Complementary | repeat accuracy | < 1 %
27071 | RE8TA31BU | Complementary | voltage drift | < 2.5 %/V
27072 | RE8TA31BU | Complementary | temperature drift | < 0.2 %/°C
27073 | RE8TA31BU | Complementary | minimum pulse duration | 26 ms
27074 | RE8TA31BU | Complementary | reset time | 50 ms
27075 | RE8TA31BU | Complementary | maximum switching voltage | 250 V
27076 | RE8TA31BU | Complementary | mechanical durability | 20000000 cycles
27077 | RE8TA31BU | Complementary | [Ith] conventional free air thermal current | 8 A
27078 | RE8TA31BU | Complementary | maximum [Ie] rated operational current | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991 2 A DC-13 24 V at 70 °C conforming to VDE 0660 3 A AC-15 24 V at 70 °C conforming to IEC 60947-5-1/1991 3 A AC-15 24 V at 70 °C conforming to VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991 0.1 A DC-13 250 V at 70 °C conforming to VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991 0.2 A DC-13 115 V at 70 °C conforming to VDE 0660
27079 | RE8TA31BU | Complementary | minimum switching capacity | at 12 V 10 mA
27080 | RE8TA31BU | Complementary | marking | CE
27081 | RE8TA31BU | Complementary | overvoltage category | III conforming to IEC 60664-1
27082 | RE8TA31BU | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 300 V conforming to CSA
27083 | RE8TA31BU | Complementary | supply disconnection value | > 0.1 Uc
27084 | RE8TA31BU | Complementary | operating position | Any position without derating
27085 | RE8TA31BU | Complementary | surge withstand | 2 kV conforming to IEC 61000-4-5 level 3
27086 | RE8TA31BU | Complementary | power consumption in VA | 0.7 VA at 24 V 1.8 VA at 110 V 8.5 VA at 240 V
27087 | RE8TA31BU | Complementary | maximum power consumption in W | 0.5 W at 24 V
27088 | RE8TA31BU | Complementary | terminal description | ALT (A1-B1)CO (15-16-18)OC_OFF
27089 | RE8TA31BU | Complementary | height | 78 mm
27090 | RE8TA31BU | Complementary | width | 22.5 mm
27091 | RE8TA31BU | Complementary | depth | 80 mm
27092 | RE8TA31BU | Complementary | net weight | 0.11 kg
27093 | RE8TA31BU | Environment | immunity to microbreaks | 3 ms
27094 | RE8TA31BU | Environment | standards | EN/IEC 61812-1
27095 | RE8TA31BU | Environment | product certifications | CSA UL GL
27096 | RE8TA31BU | Environment | ambient air temperature for storage | -40…85 °C
27097 | RE8TA31BU | Environment | ambient air temperature for operation | -20…60 °C
27098 | RE8TA31BU | Environment | relative humidity | 15…85 % 3K3 conforming to IEC 60721-3-3
27099 | RE8TA31BU | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
27100 | RE8TA31BU | Environment | IP degree of protection | IP20 (terminals) IP50 (casing)
27101 | RE8TA31BU | Environment | pollution degree | 3 conforming to IEC 60664-1
27102 | RE8TA31BU | Environment | dielectric test voltage | 2.5 kV
27103 | RE8TA31BU | Environment | non-dissipating shock wave | 4.8 kV
27104 | RE8TA31BU | Environment | resistance to electromagnetic fields | 10 V/m conforming to IEC 61000-4-3 level 3
27105 | RE8TA31BU | Environment | resistance to fast transients | 2 kV conforming to IEC 61000-4-4 level 3
27106 | RE8TA31BU | Environment | disturbance radiated/conducted | CISPR 22 - class A CISPR 11 group 1 - class A
27107 | RE8TA31BU | Contractual warranty | Warranty | 18 months
27108 | RSL1AB4BD | Main | range of product | Zelio Relay
27109 | RSL1AB4BD | Main | series name | Slim interface relay
27110 | RSL1AB4BD | Main | product or component type | Plug-in relay
27111 | RSL1AB4BD | Main | device short name | RSL
27112 | RSL1AB4BD | Main | contacts type and composition | 1 C/O
27113 | RSL1AB4BD | Main | contact operation | Standard
27114 | RSL1AB4BD | Main | [Uc] control circuit voltage | 24 V DC
27115 | RSL1AB4BD | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
27116 | RSL1AB4BD | Main | status LED | Without
27117 | RSL1AB4BD | Main | control type | Without push-button
27118 | RSL1AB4BD | Complementary | shape of pin | Flat (PCB type)
27119 | RSL1AB4BD | Complementary | average resistance | 3390 Ohm at 23 °C +/- 15 %
27120 | RSL1AB4BD | Complementary | rated operational voltage limits | 18...33.6 V DC
27121 | RSL1AB4BD | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
27122 | RSL1AB4BD | Complementary | [Uimp] rated impulse withstand voltage | 6 kV IEC
27123 | RSL1AB4BD | Complementary | contacts material | Silver alloy (AgSnO2)
27124 | RSL1AB4BD | Complementary | [Ie] rated operational current | 6 A (AC-1/DC-1) conforming to IEC/UL
27125 | RSL1AB4BD | Complementary | minimum switching current | 10 mA
27126 | RSL1AB4BD | Complementary | maximum switching voltage | 277 V
27127 | RSL1AB4BD | Complementary | Minimum switching voltage | 12 V
27128 | RSL1AB4BD | Complementary | maximum switching capacity | 1500 VA 50 W
27129 | RSL1AB4BD | Complementary | minimum switching capacity | 120 mW
27130 | RSL1AB4BD | Complementary | operating rate | <= 360 cycles/hour under load <= 18000 cycles/hour no-load
27131 | RSL1AB4BD | Complementary | mechanical durability | 10000000 cycles
27132 | RSL1AB4BD | Complementary | electrical durability | 60000 cycles, 6 A at 250 V, AC-1 C/O
27133 | RSL1AB4BD | Complementary | operating time | 5 ms reset 12 ms
27134 | RSL1AB4BD | Complementary | protection category | RT III
27135 | RSL1AB4BD | Complementary | test levels | Level A group mounting
27136 | RSL1AB4BD | Complementary | operating position | Any position
27137 | RSL1AB4BD | Complementary | width | 5 mm
27138 | RSL1AB4BD | Complementary | height | 28 mm
27139 | RSL1AB4BD | Complementary | depth | 18.5 mm
27140 | RSL1AB4BD | Complementary | terminals description ISO n°1 | (11-12-14)OC (A1-A2)CO
27141 | RSL1AB4BD | Complementary | net weight | 0.0054 kg
27142 | RSL1AB4BD | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
27143 | RSL1AB4BD | Complementary | average coil consumption | 0.17 W
27144 | RSL1AB4BD | Complementary | drop-out voltage threshold | >= 0.05 Uc
27145 | RSL1AB4BD | Complementary | safety reliability data | B10d = 60000
27146 | RSL1AB4BD | Complementary | mounting support | Socket or PCB
27147 | RSL1AB4BD | Complementary | device presentation | Complete product
27148 | RSL1AB4BD | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
27149 | RSL1AB4BD | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
27150 | RSL1AB4BD | Environment | product certifications | CSA UL EAC
27151 | RSL1AB4BD | Environment | ambient air temperature for storage | -40…70 °C
27152 | RSL1AB4BD | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
27153 | RSL1AB4BD | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
27154 | RSL1AB4BD | Environment | shock resistance | 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
27155 | RSL1AB4BD | Environment | ambient air temperature for operation | -40…55 °C
27156 | RSL1AB4BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
27157 | RSL1AB4BD | Offer Sustainability | Toxic heavy metal free | Yes
27158 | RSL1AB4BD | Offer Sustainability | Mercury free | Yes
27159 | RSL1AB4BD | Offer Sustainability | RoHS exemption information | Yes
27160 | RSL1AB4BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
27161 | RSL1AB4BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
27162 | RSL1AB4BD | Offer Sustainability | Circularity Profile | End of Life Information
27163 | RSL1AB4BD | Contractual warranty | Warranty | 18 months
27164 | RSL1AB4ED | Main | range of product | Zelio Relay
27165 | RSL1AB4ED | Main | series name | Slim interface relay
27166 | RSL1AB4ED | Main | product or component type | Plug-in relay
27167 | RSL1AB4ED | Main | device short name | RSL
27168 | RSL1AB4ED | Main | contacts type and composition | 1 C/O
27169 | RSL1AB4ED | Main | contact operation | Standard
27170 | RSL1AB4ED | Main | [Uc] control circuit voltage | 48 V DC
27171 | RSL1AB4ED | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
27172 | RSL1AB4ED | Main | status LED | Without
27173 | RSL1AB4ED | Main | control type | Without push-button
27174 | RSL1AB4ED | Complementary | shape of pin | Flat (PCB type)
27175 | RSL1AB4ED | Complementary | average resistance | 10600 Ohm at 23 °C +/- 15 %
27176 | RSL1AB4ED | Complementary | rated operational voltage limits | 36...67.2 V DC
27177 | RSL1AB4ED | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
27178 | RSL1AB4ED | Complementary | [Uimp] rated impulse withstand voltage | IEC 6 kV
27179 | RSL1AB4ED | Complementary | contacts material | Silver alloy (AgSnO2)
27180 | RSL1AB4ED | Complementary | [Ie] rated operational current | 6 A (AC-1/DC-1) conforming to IEC/UL
27181 | RSL1AB4ED | Complementary | minimum switching current | 10 mA
27182 | RSL1AB4ED | Complementary | maximum switching voltage | 277 V
27183 | RSL1AB4ED | Complementary | Minimum switching voltage | 12 V
27184 | RSL1AB4ED | Complementary | maximum switching capacity | 1500 VA 50 W
27185 | RSL1AB4ED | Complementary | minimum switching capacity | 120 mW
27186 | RSL1AB4ED | Complementary | operating rate | <= 360 cycles/hour under load <= 18000 cycles/hour no-load
27187 | RSL1AB4ED | Complementary | mechanical durability | 10000000 cycles
27188 | RSL1AB4ED | Complementary | electrical durability | 60000 cycles, 6 A at 250 V, AC-1 C/O
27189 | RSL1AB4ED | Complementary | operating time | 5 ms reset 12 ms
27190 | RSL1AB4ED | Complementary | protection category | RT III
27191 | RSL1AB4ED | Complementary | test levels | Level A group mounting
27192 | RSL1AB4ED | Complementary | operating position | Any position
27193 | RSL1AB4ED | Complementary | width | 5 mm
27194 | RSL1AB4ED | Complementary | height | 28 mm
27195 | RSL1AB4ED | Complementary | depth | 18.5 mm
27196 | RSL1AB4ED | Complementary | terminals description ISO n°1 | (A1-A2)CO (11-12-14)OC
27197 | RSL1AB4ED | Complementary | net weight | 0.0054 kg
27198 | RSL1AB4ED | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
27199 | RSL1AB4ED | Complementary | average coil consumption | 0.21 W
27200 | RSL1AB4ED | Complementary | drop-out voltage threshold | >= 0.05 Uc
27201 | RSL1AB4ED | Complementary | safety reliability data | B10d = 60000
27202 | RSL1AB4ED | Complementary | mounting support | Socket or PCB
27203 | RSL1AB4ED | Complementary | device presentation | Complete product
27204 | RSL1AB4ED | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
27205 | RSL1AB4ED | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
27206 | RSL1AB4ED | Environment | product certifications | UL EAC CSA
27207 | RSL1AB4ED | Environment | ambient air temperature for storage | -40…70 °C
27208 | RSL1AB4ED | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
27209 | RSL1AB4ED | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
27210 | RSL1AB4ED | Environment | shock resistance | 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
27211 | RSL1AB4ED | Environment | ambient air temperature for operation | -40…55 °C
27212 | RSL1AB4ED | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
27213 | RSL1AB4ED | Offer Sustainability | Toxic heavy metal free | Yes
27214 | RSL1AB4ED | Offer Sustainability | Mercury free | Yes
27215 | RSL1AB4ED | Offer Sustainability | RoHS exemption information | Yes
27216 | RSL1AB4ED | Offer Sustainability | China RoHS Regulation | China RoHS declaration
27217 | RSL1AB4ED | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
27218 | RSL1AB4ED | Offer Sustainability | Circularity Profile | End of Life Information
27219 | RSL1AB4ED | Contractual warranty | Warranty | 18 months
27220 | RSL1AB4JD | Main | range of product | Zelio Relay
27221 | RSL1AB4JD | Main | series name | Slim interface relay
27222 | RSL1AB4JD | Main | product or component type | Plug-in relay
27223 | RSL1AB4JD | Main | device short name | RSL
27224 | RSL1AB4JD | Main | contacts type and composition | 1 C/O
27225 | RSL1AB4JD | Main | contact operation | Standard
27226 | RSL1AB4JD | Main | [Uc] control circuit voltage | 12 V DC
27227 | RSL1AB4JD | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
27228 | RSL1AB4JD | Main | status LED | Without
27229 | RSL1AB4JD | Main | control type | Without push-button
27230 | RSL1AB4JD | Complementary | shape of pin | Flat (PCB type)
27231 | RSL1AB4JD | Complementary | average resistance | 848 Ohm at 23 °C +/- 10 %
27232 | RSL1AB4JD | Complementary | rated operational voltage limits | 9...16.8 V DC
27233 | RSL1AB4JD | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
27234 | RSL1AB4JD | Complementary | [Uimp] rated impulse withstand voltage | 6 kV IEC
27235 | RSL1AB4JD | Complementary | contacts material | Silver alloy (AgSnO2)
27236 | RSL1AB4JD | Complementary | [Ie] rated operational current | 6 A (AC-1/DC-1) conforming to IEC/UL
27237 | RSL1AB4JD | Complementary | minimum switching current | 10 mA
27238 | RSL1AB4JD | Complementary | maximum switching voltage | 277 V
27239 | RSL1AB4JD | Complementary | Minimum switching voltage | 12 V
27240 | RSL1AB4JD | Complementary | maximum switching capacity | 1500 VA 50 W
27241 | RSL1AB4JD | Complementary | minimum switching capacity | 120 mW
27242 | RSL1AB4JD | Complementary | operating rate | <= 360 cycles/hour under load <= 18000 cycles/hour no-load
27243 | RSL1AB4JD | Complementary | mechanical durability | 10000000 cycles
27244 | RSL1AB4JD | Complementary | electrical durability | 60000 cycles, 6 A at 250 V, AC-1 C/O
27245 | RSL1AB4JD | Complementary | operating time | 5 ms reset 12 ms
27246 | RSL1AB4JD | Complementary | protection category | RT III
27247 | RSL1AB4JD | Complementary | test levels | Level A group mounting
27248 | RSL1AB4JD | Complementary | operating position | Any position
27249 | RSL1AB4JD | Complementary | width | 5 mm
27250 | RSL1AB4JD | Complementary | height | 28 mm
27251 | RSL1AB4JD | Complementary | depth | 18.5 mm
27252 | RSL1AB4JD | Complementary | terminals description ISO n°1 | (A1-A2)CO (11-12-14)OC
27253 | RSL1AB4JD | Complementary | net weight | 0.0054 kg
27254 | RSL1AB4JD | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
27255 | RSL1AB4JD | Complementary | average coil consumption | 0.17 W
27256 | RSL1AB4JD | Complementary | drop-out voltage threshold | >= 0.05 Uc
27257 | RSL1AB4JD | Complementary | safety reliability data | B10d = 60000
27258 | RSL1AB4JD | Complementary | mounting support | Socket or PCB
27259 | RSL1AB4JD | Complementary | device presentation | Complete product
27260 | RSL1AB4JD | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
27261 | RSL1AB4JD | Environment | standards | UL 508 EN/IEC 61810-1 CSA C22.2 No 14
27262 | RSL1AB4JD | Environment | product certifications | EAC CSA UL
27263 | RSL1AB4JD | Environment | ambient air temperature for storage | -40…70 °C
27264 | RSL1AB4JD | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
27265 | RSL1AB4JD | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
27266 | RSL1AB4JD | Environment | shock resistance | 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
27267 | RSL1AB4JD | Environment | ambient air temperature for operation | -40…55 °C
27268 | RSL1AB4JD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
27269 | RSL1AB4JD | Offer Sustainability | Toxic heavy metal free | Yes
27270 | RSL1AB4JD | Offer Sustainability | Mercury free | Yes
27271 | RSL1AB4JD | Offer Sustainability | RoHS exemption information | Yes
27272 | RSL1AB4JD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
27273 | RSL1AB4JD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
27274 | RSL1AB4JD | Offer Sustainability | Circularity Profile | End of Life Information
27275 | RSL1AB4JD | Contractual warranty | Warranty | 18 months
27276 | RSL1AB4ND | Main | range of product | Zelio Relay
27277 | RSL1AB4ND | Main | series name | Slim interface relay
27278 | RSL1AB4ND | Main | product or component type | Plug-in relay
27279 | RSL1AB4ND | Main | device short name | RSL
27280 | RSL1AB4ND | Main | contacts type and composition | 1 C/O
27281 | RSL1AB4ND | Main | contact operation | Standard
27282 | RSL1AB4ND | Main | [Uc] control circuit voltage | 60 V DC
27283 | RSL1AB4ND | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
27284 | RSL1AB4ND | Main | status LED | Without
27285 | RSL1AB4ND | Main | control type | Without push-button
27286 | RSL1AB4ND | Complementary | shape of pin | Flat (PCB type)
27287 | RSL1AB4ND | Complementary | average resistance | 16600 Ohm at 23 °C +/- 15 %
27288 | RSL1AB4ND | Complementary | rated operational voltage limits | 45...84 V DC
27289 | RSL1AB4ND | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
27290 | RSL1AB4ND | Complementary | [Uimp] rated impulse withstand voltage | 6 kV IEC
27291 | RSL1AB4ND | Complementary | contacts material | Silver alloy (AgSnO2)
27292 | RSL1AB4ND | Complementary | [Ie] rated operational current | 6 A (AC-1/DC-1) conforming to IEC/UL
27293 | RSL1AB4ND | Complementary | minimum switching current | 10 mA
27294 | RSL1AB4ND | Complementary | maximum switching voltage | 277 V
27295 | RSL1AB4ND | Complementary | Minimum switching voltage | 12 V
27296 | RSL1AB4ND | Complementary | maximum switching capacity | 1500 VA 50 W
27297 | RSL1AB4ND | Complementary | minimum switching capacity | 120 mW
27298 | RSL1AB4ND | Complementary | operating rate | <= 360 cycles/hour under load <= 18000 cycles/hour no-load
27299 | RSL1AB4ND | Complementary | mechanical durability | 10000000 cycles
27300 | RSL1AB4ND | Complementary | electrical durability | 60000 cycles, 6 A at 250 V, AC-1 C/O
27301 | RSL1AB4ND | Complementary | operating time | 5 ms reset 12 ms
27302 | RSL1AB4ND | Complementary | protection category | RT III
27303 | RSL1AB4ND | Complementary | test levels | Level A group mounting
27304 | RSL1AB4ND | Complementary | operating position | Any position
27305 | RSL1AB4ND | Complementary | width | 5 mm
27306 | RSL1AB4ND | Complementary | height | 28 mm
27307 | RSL1AB4ND | Complementary | depth | 18.5 mm
27308 | RSL1AB4ND | Complementary | terminals description ISO n°1 | (11-12-14)OC (A1-A2)CO
27309 | RSL1AB4ND | Complementary | net weight | 0.0054 kg
27310 | RSL1AB4ND | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
27311 | RSL1AB4ND | Complementary | average coil consumption | 0.21 W
27312 | RSL1AB4ND | Complementary | drop-out voltage threshold | >= 0.05 Uc
27313 | RSL1AB4ND | Complementary | safety reliability data | B10d = 60000
27314 | RSL1AB4ND | Complementary | mounting support | Socket or PCB
27315 | RSL1AB4ND | Complementary | device presentation | Complete product
27316 | RSL1AB4ND | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
27317 | RSL1AB4ND | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
27318 | RSL1AB4ND | Environment | product certifications | CSA UL EAC
27319 | RSL1AB4ND | Environment | ambient air temperature for storage | -40…70 °C
27320 | RSL1AB4ND | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
27321 | RSL1AB4ND | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
27322 | RSL1AB4ND | Environment | shock resistance | 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
27323 | RSL1AB4ND | Environment | ambient air temperature for operation | -40…55 °C
27324 | RSL1AB4ND | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
27325 | RSL1AB4ND | Offer Sustainability | Toxic heavy metal free | Yes
27326 | RSL1AB4ND | Offer Sustainability | Mercury free | Yes
27327 | RSL1AB4ND | Offer Sustainability | RoHS exemption information | Yes
27328 | RSL1AB4ND | Offer Sustainability | China RoHS Regulation | China RoHS declaration
27329 | RSL1AB4ND | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
27330 | RSL1AB4ND | Offer Sustainability | Circularity Profile | End of Life Information
27331 | RSL1AB4ND | Contractual warranty | Warranty | 18 months
27332 | RSL1GB4BD | Main | range of product | Zelio Relay
27333 | RSL1GB4BD | Main | series name | Slim interface relay
27334 | RSL1GB4BD | Main | product or component type | Plug-in relay
27335 | RSL1GB4BD | Main | device short name | RSL
27336 | RSL1GB4BD | Main | contacts type and composition | 1 C/O
27337 | RSL1GB4BD | Main | contact operation | Low level
27338 | RSL1GB4BD | Main | [Uc] control circuit voltage | 24 V DC
27339 | RSL1GB4BD | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
27340 | RSL1GB4BD | Main | status LED | Without
27341 | RSL1GB4BD | Main | control type | Without push-button
27342 | RSL1GB4BD | Complementary | shape of pin | Flat (PCB type)
27343 | RSL1GB4BD | Complementary | average resistance | 3390 Ohm at 23 °C +/- 15 %
27344 | RSL1GB4BD | Complementary | rated operational voltage limits | 18...33.6 V DC
27345 | RSL1GB4BD | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
27346 | RSL1GB4BD | Complementary | [Uimp] rated impulse withstand voltage | IEC 6 kV
27347 | RSL1GB4BD | Complementary | contacts material | Silver alloy - gold plated (AgSnO2)
27348 | RSL1GB4BD | Complementary | [Ie] rated operational current | 6 A (AC-1/DC-1) conforming to IEC/UL
27349 | RSL1GB4BD | Complementary | minimum switching current | 1 mA
27350 | RSL1GB4BD | Complementary | maximum switching voltage | 277 V
27351 | RSL1GB4BD | Complementary | Minimum switching voltage | 24 V
27352 | RSL1GB4BD | Complementary | maximum switching capacity | 1500 VA 50 W
27353 | RSL1GB4BD | Complementary | minimum switching capacity | 24 mW
27354 | RSL1GB4BD | Complementary | operating rate | <= 360 cycles/hour under load <= 18000 cycles/hour no-load
27355 | RSL1GB4BD | Complementary | mechanical durability | 10000000 cycles
27356 | RSL1GB4BD | Complementary | electrical durability | 60000 cycles, 6 A at 250 V, AC-1 C/O
27357 | RSL1GB4BD | Complementary | operating time | 5 ms reset 12 ms
27358 | RSL1GB4BD | Complementary | protection category | RT III
27359 | RSL1GB4BD | Complementary | test levels | Level A group mounting
27360 | RSL1GB4BD | Complementary | operating position | Any position
27361 | RSL1GB4BD | Complementary | width | 5 mm
27362 | RSL1GB4BD | Complementary | height | 28 mm
27363 | RSL1GB4BD | Complementary | depth | 18.5 mm
27364 | RSL1GB4BD | Complementary | terminals description ISO n°1 | (A1-A2)CO (11-12-14)OC
27365 | RSL1GB4BD | Complementary | net weight | 0.0054 kg
27366 | RSL1GB4BD | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
27367 | RSL1GB4BD | Complementary | average coil consumption | 0.17 W
27368 | RSL1GB4BD | Complementary | drop-out voltage threshold | >= 0.05 Uc
27369 | RSL1GB4BD | Complementary | safety reliability data | B10d = 60000
27370 | RSL1GB4BD | Complementary | mounting support | Socket or PCB
27371 | RSL1GB4BD | Complementary | device presentation | Complete product
27372 | RSL1GB4BD | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
27373 | RSL1GB4BD | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1
27374 | RSL1GB4BD | Environment | product certifications | EAC CSA UL
27375 | RSL1GB4BD | Environment | ambient air temperature for storage | -40…70 °C
27376 | RSL1GB4BD | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
27377 | RSL1GB4BD | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
27378 | RSL1GB4BD | Environment | shock resistance | 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
27379 | RSL1GB4BD | Environment | ambient air temperature for operation | -40…55 °C
27380 | RSL1GB4BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
27381 | RSL1GB4BD | Offer Sustainability | Toxic heavy metal free | Yes
27382 | RSL1GB4BD | Offer Sustainability | Mercury free | Yes
27383 | RSL1GB4BD | Offer Sustainability | RoHS exemption information | Yes
27384 | RSL1GB4BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
27385 | RSL1GB4BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
27386 | RSL1GB4BD | Offer Sustainability | Circularity Profile | End of Life Information
27387 | RSL1GB4BD | Contractual warranty | Warranty | 18 months
27388 | RSL1GB4ED | Main | range of product | Zelio Relay
27389 | RSL1GB4ED | Main | series name | Slim interface relay
27390 | RSL1GB4ED | Main | product or component type | Plug-in relay
27391 | RSL1GB4ED | Main | device short name | RSL
27392 | RSL1GB4ED | Main | contacts type and composition | 1 C/O
27393 | RSL1GB4ED | Main | contact operation | Low level
27394 | RSL1GB4ED | Main | [Uc] control circuit voltage | 48 V DC
27395 | RSL1GB4ED | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
27396 | RSL1GB4ED | Main | status LED | Without
27397 | RSL1GB4ED | Main | control type | Without push-button
27398 | RSL1GB4ED | Complementary | shape of pin | Flat (PCB type)
27399 | RSL1GB4ED | Complementary | average resistance | 10600 Ohm at 23 °C +/- 15 %
27400 | RSL1GB4ED | Complementary | rated operational voltage limits | 36...67.2 V DC
27401 | RSL1GB4ED | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
27402 | RSL1GB4ED | Complementary | [Uimp] rated impulse withstand voltage | 6 kV IEC
27403 | RSL1GB4ED | Complementary | contacts material | Silver alloy - gold plated (AgSnO2)
27404 | RSL1GB4ED | Complementary | [Ie] rated operational current | 6 A (AC-1/DC-1) conforming to IEC/UL
27405 | RSL1GB4ED | Complementary | minimum switching current | 1 mA
27406 | RSL1GB4ED | Complementary | maximum switching voltage | 277 V
27407 | RSL1GB4ED | Complementary | Minimum switching voltage | 24 V
27408 | RSL1GB4ED | Complementary | maximum switching capacity | 1500 VA 50 W
27409 | RSL1GB4ED | Complementary | minimum switching capacity | 24 mW
27410 | RSL1GB4ED | Complementary | operating rate | <= 360 cycles/hour under load <= 18000 cycles/hour no-load
27411 | RSL1GB4ED | Complementary | mechanical durability | 10000000 cycles
27412 | RSL1GB4ED | Complementary | electrical durability | 60000 cycles, 6 A at 250 V, AC-1 C/O
27413 | RSL1GB4ED | Complementary | operating time | 5 ms reset 12 ms
27414 | RSL1GB4ED | Complementary | protection category | RT III
27415 | RSL1GB4ED | Complementary | test levels | Level A group mounting
27416 | RSL1GB4ED | Complementary | operating position | Any position
27417 | RSL1GB4ED | Complementary | width | 5 mm
27418 | RSL1GB4ED | Complementary | height | 28 mm
27419 | RSL1GB4ED | Complementary | depth | 18.5 mm
27420 | RSL1GB4ED | Complementary | terminals description ISO n°1 | (A1-A2)CO (11-12-14)OC
27421 | RSL1GB4ED | Complementary | net weight | 0.0054 kg
27422 | RSL1GB4ED | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
27423 | RSL1GB4ED | Complementary | average coil consumption | 0.21 W
27424 | RSL1GB4ED | Complementary | drop-out voltage threshold | >= 0.05 Uc
27425 | RSL1GB4ED | Complementary | safety reliability data | B10d = 60000
27426 | RSL1GB4ED | Complementary | mounting support | Socket or PCB
27427 | RSL1GB4ED | Complementary | device presentation | Complete product
27428 | RSL1GB4ED | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
27429 | RSL1GB4ED | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508
27430 | RSL1GB4ED | Environment | product certifications | CSA UL EAC
27431 | RSL1GB4ED | Environment | ambient air temperature for storage | -40…70 °C
27432 | RSL1GB4ED | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
27433 | RSL1GB4ED | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
27434 | RSL1GB4ED | Environment | shock resistance | 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
27435 | RSL1GB4ED | Environment | ambient air temperature for operation | -40…55 °C
27436 | RSL1GB4ED | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
27437 | RSL1GB4ED | Offer Sustainability | Toxic heavy metal free | Yes
27438 | RSL1GB4ED | Offer Sustainability | Mercury free | Yes
27439 | RSL1GB4ED | Offer Sustainability | RoHS exemption information | Yes
27440 | RSL1GB4ED | Offer Sustainability | China RoHS Regulation | China RoHS declaration
27441 | RSL1GB4ED | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
27442 | RSL1GB4ED | Offer Sustainability | Circularity Profile | End of Life Information
27443 | RSL1GB4ED | Contractual warranty | Warranty | 18 months
27444 | RSL1GB4JD | Main | range of product | Zelio Relay
27445 | RSL1GB4JD | Main | series name | Slim interface relay
27446 | RSL1GB4JD | Main | product or component type | Plug-in relay
27447 | RSL1GB4JD | Main | device short name | RSL
27448 | RSL1GB4JD | Main | contacts type and composition | 1 C/O
27449 | RSL1GB4JD | Main | contact operation | Low level
27450 | RSL1GB4JD | Main | [Uc] control circuit voltage | 12 V DC
27451 | RSL1GB4JD | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
27452 | RSL1GB4JD | Main | status LED | Without
27453 | RSL1GB4JD | Main | control type | Without push-button
27454 | RSL1GB4JD | Complementary | shape of pin | Flat (PCB type)
27455 | RSL1GB4JD | Complementary | average resistance | 848 Ohm at 23 °C +/- 10 %
27456 | RSL1GB4JD | Complementary | rated operational voltage limits | 9...16.8 V DC
27457 | RSL1GB4JD | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
27458 | RSL1GB4JD | Complementary | [Uimp] rated impulse withstand voltage | IEC 6 kV
27459 | RSL1GB4JD | Complementary | contacts material | Silver alloy - gold plated (AgSnO2)
27460 | RSL1GB4JD | Complementary | [Ie] rated operational current | 6 A (AC-1/DC-1) conforming to IEC/UL
27461 | RSL1GB4JD | Complementary | minimum switching current | 1 mA
27462 | RSL1GB4JD | Complementary | maximum switching voltage | 277 V
27463 | RSL1GB4JD | Complementary | Minimum switching voltage | 24 V
27464 | RSL1GB4JD | Complementary | maximum switching capacity | 1500 VA 50 W
27465 | RSL1GB4JD | Complementary | minimum switching capacity | 24 mW
27466 | RSL1GB4JD | Complementary | operating rate | <= 360 cycles/hour under load <= 18000 cycles/hour no-load
27467 | RSL1GB4JD | Complementary | mechanical durability | 10000000 cycles
27468 | RSL1GB4JD | Complementary | electrical durability | 60000 cycles, 6 A at 250 V, AC-1 C/O
27469 | RSL1GB4JD | Complementary | operating time | 5 ms reset 12 ms
27470 | RSL1GB4JD | Complementary | protection category | RT III
27471 | RSL1GB4JD | Complementary | test levels | Level A group mounting
27472 | RSL1GB4JD | Complementary | operating position | Any position
27473 | RSL1GB4JD | Complementary | width | 5 mm
27474 | RSL1GB4JD | Complementary | height | 28 mm
27475 | RSL1GB4JD | Complementary | depth | 18.5 mm
27476 | RSL1GB4JD | Complementary | terminals description ISO n°1 | (11-12-14)OC (A1-A2)CO
27477 | RSL1GB4JD | Complementary | net weight | 0.0054 kg
27478 | RSL1GB4JD | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
27479 | RSL1GB4JD | Complementary | average coil consumption | 0.17 W
27480 | RSL1GB4JD | Complementary | drop-out voltage threshold | >= 0.05 Uc
27481 | RSL1GB4JD | Complementary | safety reliability data | B10d = 60000
27482 | RSL1GB4JD | Complementary | mounting support | Socket or PCB
27483 | RSL1GB4JD | Complementary | device presentation | Complete product
27484 | RSL1GB4JD | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
27485 | RSL1GB4JD | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
27486 | RSL1GB4JD | Environment | product certifications | UL CSA EAC
27487 | RSL1GB4JD | Environment | ambient air temperature for storage | -40…70 °C
27488 | RSL1GB4JD | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
27489 | RSL1GB4JD | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
27490 | RSL1GB4JD | Environment | shock resistance | 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
27491 | RSL1GB4JD | Environment | ambient air temperature for operation | -40…55 °C
27492 | RSL1GB4JD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
27493 | RSL1GB4JD | Offer Sustainability | Toxic heavy metal free | Yes
27494 | RSL1GB4JD | Offer Sustainability | Mercury free | Yes
27495 | RSL1GB4JD | Offer Sustainability | RoHS exemption information | Yes
27496 | RSL1GB4JD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
27497 | RSL1GB4JD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
27498 | RSL1GB4JD | Offer Sustainability | Circularity Profile | End of Life Information
27499 | RSL1GB4JD | Contractual warranty | Warranty | 18 months
27500 | RSL1GB4ND | Main | range of product | Zelio Relay
27501 | RSL1GB4ND | Main | series name | Slim interface relay
27502 | RSL1GB4ND | Main | product or component type | Plug-in relay
27503 | RSL1GB4ND | Main | device short name | RSL
27504 | RSL1GB4ND | Main | contacts type and composition | 1 C/O
27505 | RSL1GB4ND | Main | contact operation | Low level
27506 | RSL1GB4ND | Main | [Uc] control circuit voltage | 60 V DC
27507 | RSL1GB4ND | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
27508 | RSL1GB4ND | Main | status LED | Without
27509 | RSL1GB4ND | Main | control type | Without push-button
27510 | RSL1GB4ND | Complementary | shape of pin | Flat (PCB type)
27511 | RSL1GB4ND | Complementary | average resistance | 16600 Ohm at 23 °C +/- 15 %
27512 | RSL1GB4ND | Complementary | rated operational voltage limits | 45...84 V DC
27513 | RSL1GB4ND | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
27514 | RSL1GB4ND | Complementary | [Uimp] rated impulse withstand voltage | IEC 6 kV
27515 | RSL1GB4ND | Complementary | contacts material | Silver alloy - gold plated (AgSnO2)
27516 | RSL1GB4ND | Complementary | [Ie] rated operational current | 6 A (AC-1/DC-1) conforming to IEC/UL
27517 | RSL1GB4ND | Complementary | minimum switching current | 1 mA
27518 | RSL1GB4ND | Complementary | maximum switching voltage | 277 V
27519 | RSL1GB4ND | Complementary | Minimum switching voltage | 24 V
27520 | RSL1GB4ND | Complementary | maximum switching capacity | 1500 VA 50 W
27521 | RSL1GB4ND | Complementary | minimum switching capacity | 24 mW
27522 | RSL1GB4ND | Complementary | operating rate | <= 360 cycles/hour under load <= 18000 cycles/hour no-load
27523 | RSL1GB4ND | Complementary | mechanical durability | 10000000 cycles
27524 | RSL1GB4ND | Complementary | electrical durability | 60000 cycles, 6 A at 250 V, AC-1 C/O
27525 | RSL1GB4ND | Complementary | operating time | 5 ms reset 12 ms
27526 | RSL1GB4ND | Complementary | protection category | RT III
27527 | RSL1GB4ND | Complementary | test levels | Level A group mounting
27528 | RSL1GB4ND | Complementary | operating position | Any position
27529 | RSL1GB4ND | Complementary | width | 5 mm
27530 | RSL1GB4ND | Complementary | height | 28 mm
27531 | RSL1GB4ND | Complementary | depth | 18.5 mm
27532 | RSL1GB4ND | Complementary | terminals description ISO n°1 | (A1-A2)CO (11-12-14)OC
27533 | RSL1GB4ND | Complementary | net weight | 0.0054 kg
27534 | RSL1GB4ND | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
27535 | RSL1GB4ND | Complementary | average coil consumption | 0.21 W
27536 | RSL1GB4ND | Complementary | drop-out voltage threshold | >= 0.05 Uc
27537 | RSL1GB4ND | Complementary | safety reliability data | B10d = 60000
27538 | RSL1GB4ND | Complementary | mounting support | Socket or PCB
27539 | RSL1GB4ND | Complementary | device presentation | Complete product
27540 | RSL1GB4ND | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
27541 | RSL1GB4ND | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1
27542 | RSL1GB4ND | Environment | product certifications | EAC CSA UL
27543 | RSL1GB4ND | Environment | ambient air temperature for storage | -40…70 °C
27544 | RSL1GB4ND | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
27545 | RSL1GB4ND | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
27546 | RSL1GB4ND | Environment | shock resistance | 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
27547 | RSL1GB4ND | Environment | ambient air temperature for operation | -40…55 °C
27548 | RSL1GB4ND | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
27549 | RSL1GB4ND | Offer Sustainability | Toxic heavy metal free | Yes
27550 | RSL1GB4ND | Offer Sustainability | Mercury free | Yes
27551 | RSL1GB4ND | Offer Sustainability | RoHS exemption information | Yes
27552 | RSL1GB4ND | Offer Sustainability | China RoHS Regulation | China RoHS declaration
27553 | RSL1GB4ND | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
27554 | RSL1GB4ND | Offer Sustainability | Circularity Profile | End of Life Information
27555 | RSL1GB4ND | Contractual warranty | Warranty | 18 months
27556 | RSB1A120B7 | Main | range of product | Zelio Relay
27557 | RSB1A120B7 | Main | series name | Interface relay
27558 | RSB1A120B7 | Main | product or component type | Plug-in relay
27559 | RSB1A120B7 | Main | device short name | RSB
27560 | RSB1A120B7 | Main | contacts type and composition | 1 C/O
27561 | RSB1A120B7 | Main | contact operation | Standard
27562 | RSB1A120B7 | Main | [Uc] control circuit voltage | 24 V AC
27563 | RSB1A120B7 | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
27564 | RSB1A120B7 | Main | status LED | Without
27565 | RSB1A120B7 | Main | control type | Without push-button
27566 | RSB1A120B7 | Complementary | shape of pin | Flat (PCB type)
27567 | RSB1A120B7 | Complementary | average coil resistance | 368 Ohm network: AC at 20 °C +/- 10 %
27568 | RSB1A120B7 | Complementary | [Ue] rated operational voltage | 19.2...36 V AC 50/60 Hz
27569 | RSB1A120B7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
27570 | RSB1A120B7 | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
27571 | RSB1A120B7 | Complementary | contacts material | Silver alloy (AgNi)
27572 | RSB1A120B7 | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
27573 | RSB1A120B7 | Complementary | minimum switching current | 10 mA
27574 | RSB1A120B7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
27575 | RSB1A120B7 | Complementary | minimum switching voltage | 12 V
27576 | RSB1A120B7 | Complementary | maximum switching capacity | 3000 VA/336 W
27577 | RSB1A120B7 | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
27578 | RSB1A120B7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
27579 | RSB1A120B7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
27580 | RSB1A120B7 | Complementary | mechanical durability | 10000000 cycles
27581 | RSB1A120B7 | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
27582 | RSB1A120B7 | Complementary | operating time | 20 ms operating 20 ms reset
27583 | RSB1A120B7 | Complementary | marking | CE
27584 | RSB1A120B7 | Complementary | average coil consumption | 0.75 VA AC
27585 | RSB1A120B7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
27586 | RSB1A120B7 | Complementary | safety reliability data | B10d = 100000
27587 | RSB1A120B7 | Complementary | protection category | RT I
27588 | RSB1A120B7 | Complementary | test levels | Level A group mounting
27589 | RSB1A120B7 | Complementary | operating position | Any position
27590 | RSB1A120B7 | Complementary | net weight | 0.014 kg
27591 | RSB1A120B7 | Complementary | sale per indivisible quantity | 10
27592 | RSB1A120B7 | Complementary | device presentation | Complete product
27593 | RSB1A120B7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
27594 | RSB1A120B7 | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
27595 | RSB1A120B7 | Environment | product certifications | EAC UL CSA
27596 | RSB1A120B7 | Environment | ambient air temperature for storage | -40…85 °C
27597 | RSB1A120B7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
27598 | RSB1A120B7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
27599 | RSB1A120B7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
27600 | RSB1A120B7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
27601 | RSB1A120B7 | Offer Sustainability | Sustainable offer status | Green Premium product
27602 | RSB1A120B7 | Offer Sustainability | REACh Regulation | REACh Declaration
27603 | RSB1A120B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
27604 | RSB1A120B7 | Offer Sustainability | Toxic heavy metal free | Yes
27605 | RSB1A120B7 | Offer Sustainability | Mercury free | Yes
27606 | RSB1A120B7 | Offer Sustainability | RoHS exemption information | Yes
27607 | RSB1A120B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
27608 | RSB1A120B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
27609 | RSB1A120B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
27610 | RSB1A120B7 | Contractual warranty | Warranty | 18 months
27611 | RSB1A120BD | Main | range of product | Zelio Relay
27612 | RSB1A120BD | Main | series name | Interface relay
27613 | RSB1A120BD | Main | product or component type | Plug-in relay
27614 | RSB1A120BD | Main | device short name | RSB
27615 | RSB1A120BD | Main | contacts type and composition | 1 C/O
27616 | RSB1A120BD | Main | contact operation | Standard
27617 | RSB1A120BD | Main | [Uc] control circuit voltage | 24 V DC
27618 | RSB1A120BD | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
27619 | RSB1A120BD | Main | status LED | Without
27620 | RSB1A120BD | Main | control type | Without push-button
27621 | RSB1A120BD | Complementary | shape of pin | Flat (PCB type)
27622 | RSB1A120BD | Complementary | average coil resistance | 1440 Ohm network: AC at 20 °C +/- 10 %
27623 | RSB1A120BD | Complementary | [Ue] rated operational voltage | 16.8...36 V DC
27624 | RSB1A120BD | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
27625 | RSB1A120BD | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
27626 | RSB1A120BD | Complementary | contacts material | Silver alloy (AgNi)
27627 | RSB1A120BD | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
27628 | RSB1A120BD | Complementary | minimum switching current | 10 mA
27629 | RSB1A120BD | Complementary | maximum switching voltage | 250 V DC conforming to IEC
27630 | RSB1A120BD | Complementary | minimum switching voltage | 12 V
27631 | RSB1A120BD | Complementary | maximum switching capacity | 3000 VA/336 W
27632 | RSB1A120BD | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
27633 | RSB1A120BD | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
27634 | RSB1A120BD | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
27635 | RSB1A120BD | Complementary | mechanical durability | 30000000 cycles
27636 | RSB1A120BD | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
27637 | RSB1A120BD | Complementary | operating time | 20 ms operating 20 ms reset
27638 | RSB1A120BD | Complementary | average coil consumption | 0.45 W DC
27639 | RSB1A120BD | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
27640 | RSB1A120BD | Complementary | safety reliability data | B10d = 100000
27641 | RSB1A120BD | Complementary | protection category | RT I
27642 | RSB1A120BD | Complementary | test levels | Level A group mounting
27643 | RSB1A120BD | Complementary | operating position | Any position
27644 | RSB1A120BD | Complementary | net weight | 0.014 kg
27645 | RSB1A120BD | Complementary | sale per indivisible quantity | 10
27646 | RSB1A120BD | Complementary | device presentation | Complete product
27647 | RSB1A120BD | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
27648 | RSB1A120BD | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
27649 | RSB1A120BD | Environment | product certifications | UL CSA EAC
27650 | RSB1A120BD | Environment | ambient air temperature for storage | -40…85 °C
27651 | RSB1A120BD | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
27652 | RSB1A120BD | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
27653 | RSB1A120BD | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
27654 | RSB1A120BD | Environment | ambient air temperature for operation | -40…85 °C (DC)
27655 | RSB1A120BD | Offer Sustainability | Sustainable offer status | Green Premium product
27656 | RSB1A120BD | Offer Sustainability | REACh Regulation | REACh Declaration
27657 | RSB1A120BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
27658 | RSB1A120BD | Offer Sustainability | Toxic heavy metal free | Yes
27659 | RSB1A120BD | Offer Sustainability | Mercury free | Yes
27660 | RSB1A120BD | Offer Sustainability | RoHS exemption information | Yes
27661 | RSB1A120BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
27662 | RSB1A120BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
27663 | RSB1A120BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
27664 | RSB1A120BD | Contractual warranty | Warranty | 18 months
27665 | RSB1A120E7 | Main | range of product | Zelio Relay
27666 | RSB1A120E7 | Main | series name | Interface relay
27667 | RSB1A120E7 | Main | product or component type | Plug-in relay
27668 | RSB1A120E7 | Main | device short name | RSB
27669 | RSB1A120E7 | Main | contacts type and composition | 1 C/O
27670 | RSB1A120E7 | Main | contact operation | Standard
27671 | RSB1A120E7 | Main | [Uc] control circuit voltage | 48 V AC
27672 | RSB1A120E7 | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
27673 | RSB1A120E7 | Main | status LED | Without
27674 | RSB1A120E7 | Main | control type | Without push-button
27675 | RSB1A120E7 | Complementary | shape of pin | Flat (PCB type)
27676 | RSB1A120E7 | Complementary | average coil resistance | 1540 Ohm network: AC at 20 °C +/- 10 %
27677 | RSB1A120E7 | Complementary | [Ue] rated operational voltage | 38.4...72 V AC 50/60 Hz
27678 | RSB1A120E7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
27679 | RSB1A120E7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
27680 | RSB1A120E7 | Complementary | contacts material | Silver alloy (AgNi)
27681 | RSB1A120E7 | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
27682 | RSB1A120E7 | Complementary | minimum switching current | 10 mA
27683 | RSB1A120E7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
27684 | RSB1A120E7 | Complementary | minimum switching voltage | 12 V
27685 | RSB1A120E7 | Complementary | maximum switching capacity | 3000 VA/336 W
27686 | RSB1A120E7 | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
27687 | RSB1A120E7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
27688 | RSB1A120E7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
27689 | RSB1A120E7 | Complementary | mechanical durability | 10000000 cycles
27690 | RSB1A120E7 | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
27691 | RSB1A120E7 | Complementary | operating time | 20 ms operating 20 ms reset
27692 | RSB1A120E7 | Complementary | average coil consumption | 0.75 VA AC
27693 | RSB1A120E7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
27694 | RSB1A120E7 | Complementary | safety reliability data | B10d = 100000
27695 | RSB1A120E7 | Complementary | protection category | RT I
27696 | RSB1A120E7 | Complementary | test levels | Level A group mounting
27697 | RSB1A120E7 | Complementary | operating position | Any position
27698 | RSB1A120E7 | Complementary | net weight | 0.014 kg
27699 | RSB1A120E7 | Complementary | sale per indivisible quantity | 10
27700 | RSB1A120E7 | Complementary | device presentation | Complete product
27701 | RSB1A120E7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
27702 | RSB1A120E7 | Environment | standards | EN/IEC 61810-1 UL 508 CSA C22.2 No 14
27703 | RSB1A120E7 | Environment | product certifications | UL CSA EAC
27704 | RSB1A120E7 | Environment | ambient air temperature for storage | -40…85 °C
27705 | RSB1A120E7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
27706 | RSB1A120E7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
27707 | RSB1A120E7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
27708 | RSB1A120E7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
27709 | RSB1A120E7 | Offer Sustainability | Sustainable offer status | Green Premium product
27710 | RSB1A120E7 | Offer Sustainability | REACh Regulation | REACh Declaration
27711 | RSB1A120E7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
27712 | RSB1A120E7 | Offer Sustainability | Toxic heavy metal free | Yes
27713 | RSB1A120E7 | Offer Sustainability | Mercury free | Yes
27714 | RSB1A120E7 | Offer Sustainability | RoHS exemption information | Yes
27715 | RSB1A120E7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
27716 | RSB1A120E7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
27717 | RSB1A120E7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
27718 | RSB1A120E7 | Contractual warranty | Warranty | 18 months
27719 | RSB1A120ED | Main | range of product | Zelio Relay
27720 | RSB1A120ED | Main | series name | Interface relay
27721 | RSB1A120ED | Main | product or component type | Plug-in relay
27722 | RSB1A120ED | Main | device short name | RSB
27723 | RSB1A120ED | Main | contacts type and composition | 1 C/O
27724 | RSB1A120ED | Main | contact operation | Standard
27725 | RSB1A120ED | Main | [Uc] control circuit voltage | 48 V DC
27726 | RSB1A120ED | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
27727 | RSB1A120ED | Main | status LED | Without
27728 | RSB1A120ED | Main | control type | Without push-button
27729 | RSB1A120ED | Complementary | shape of pin | Flat (PCB type)
27730 | RSB1A120ED | Complementary | average coil resistance | 5520 Ohm network: AC at 20 °C +/- 10 %
27731 | RSB1A120ED | Complementary | [Ue] rated operational voltage | 33.6...72 V DC
27732 | RSB1A120ED | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
27733 | RSB1A120ED | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
27734 | RSB1A120ED | Complementary | contacts material | Silver alloy (AgNi)
27735 | RSB1A120ED | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
27736 | RSB1A120ED | Complementary | minimum switching current | 10 mA
27737 | RSB1A120ED | Complementary | maximum switching voltage | 250 V DC conforming to IEC
27738 | RSB1A120ED | Complementary | minimum switching voltage | 12 V
27739 | RSB1A120ED | Complementary | maximum switching capacity | 3000 VA/336 W
27740 | RSB1A120ED | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
27741 | RSB1A120ED | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
27742 | RSB1A120ED | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
27743 | RSB1A120ED | Complementary | mechanical durability | 30000000 cycles
27744 | RSB1A120ED | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
27745 | RSB1A120ED | Complementary | operating time | 20 ms operating 20 ms reset
27746 | RSB1A120ED | Complementary | average coil consumption | 0.45 W DC
27747 | RSB1A120ED | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
27748 | RSB1A120ED | Complementary | safety reliability data | B10d = 100000
27749 | RSB1A120ED | Complementary | protection category | RT I
27750 | RSB1A120ED | Complementary | test levels | Level A group mounting
27751 | RSB1A120ED | Complementary | operating position | Any position
27752 | RSB1A120ED | Complementary | net weight | 0.014 kg
27753 | RSB1A120ED | Complementary | sale per indivisible quantity | 10
27754 | RSB1A120ED | Complementary | device presentation | Complete product
27755 | RSB1A120ED | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
27756 | RSB1A120ED | Environment | standards | UL 508 EN/IEC 61810-1 CSA C22.2 No 14
27757 | RSB1A120ED | Environment | product certifications | UL EAC CSA
27758 | RSB1A120ED | Environment | ambient air temperature for storage | -40…85 °C
27759 | RSB1A120ED | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
27760 | RSB1A120ED | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
27761 | RSB1A120ED | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
27762 | RSB1A120ED | Environment | ambient air temperature for operation | -40…85 °C (DC)
27763 | RSB1A120ED | Offer Sustainability | Sustainable offer status | Green Premium product
27764 | RSB1A120ED | Offer Sustainability | REACh free of SVHC | Yes
27765 | RSB1A120ED | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
27766 | RSB1A120ED | Offer Sustainability | Toxic heavy metal free | Yes
27767 | RSB1A120ED | Offer Sustainability | Mercury free | Yes
27768 | RSB1A120ED | Offer Sustainability | RoHS exemption information | Yes
27769 | RSB1A120ED | Offer Sustainability | China RoHS Regulation | China RoHS declaration
27770 | RSB1A120ED | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
27771 | RSB1A120ED | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
27772 | RSB1A120ED | Contractual warranty | Warranty | 18 months
27773 | RSB1A120F7 | Main | range of product | Zelio Relay
27774 | RSB1A120F7 | Main | series name | Interface relay
27775 | RSB1A120F7 | Main | product or component type | Plug-in relay
27776 | RSB1A120F7 | Main | device short name | RSB
27777 | RSB1A120F7 | Main | contacts type and composition | 1 C/O
27778 | RSB1A120F7 | Main | contact operation | Standard
27779 | RSB1A120F7 | Main | [Uc] control circuit voltage | 120 V AC
27780 | RSB1A120F7 | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
27781 | RSB1A120F7 | Main | status LED | Without
27782 | RSB1A120F7 | Main | control type | Without push-button
27783 | RSB1A120F7 | Complementary | shape of pin | Flat (PCB type)
27784 | RSB1A120F7 | Complementary | average coil resistance | 8360 Ohm network: AC at 20 °C +/- 10 %
27785 | RSB1A120F7 | Complementary | [Ue] rated operational voltage | 96...180 V AC 50/60 Hz
27786 | RSB1A120F7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
27787 | RSB1A120F7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
27788 | RSB1A120F7 | Complementary | contacts material | Silver alloy (AgNi)
27789 | RSB1A120F7 | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
27790 | RSB1A120F7 | Complementary | minimum switching current | 10 mA
27791 | RSB1A120F7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
27792 | RSB1A120F7 | Complementary | minimum switching voltage | 12 V
27793 | RSB1A120F7 | Complementary | maximum switching capacity | 3000 VA/336 W
27794 | RSB1A120F7 | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
27795 | RSB1A120F7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
27796 | RSB1A120F7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
27797 | RSB1A120F7 | Complementary | mechanical durability | 10000000 cycles
27798 | RSB1A120F7 | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
27799 | RSB1A120F7 | Complementary | operating time | 20 ms operating 20 ms reset
27800 | RSB1A120F7 | Complementary | average coil consumption | 0.75 VA AC
27801 | RSB1A120F7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
27802 | RSB1A120F7 | Complementary | safety reliability data | B10d = 100000
27803 | RSB1A120F7 | Complementary | protection category | RT I
27804 | RSB1A120F7 | Complementary | test levels | Level A group mounting
27805 | RSB1A120F7 | Complementary | operating position | Any position
27806 | RSB1A120F7 | Complementary | net weight | 0.014 kg
27807 | RSB1A120F7 | Complementary | sale per indivisible quantity | 10
27808 | RSB1A120F7 | Complementary | device presentation | Complete product
27809 | RSB1A120F7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
27810 | RSB1A120F7 | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508
27811 | RSB1A120F7 | Environment | product certifications | UL CSA EAC
27812 | RSB1A120F7 | Environment | ambient air temperature for storage | -40…85 °C
27813 | RSB1A120F7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
27814 | RSB1A120F7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
27815 | RSB1A120F7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
27816 | RSB1A120F7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
27817 | RSB1A120F7 | Offer Sustainability | Sustainable offer status | Green Premium product
27818 | RSB1A120F7 | Offer Sustainability | REACh Regulation | REACh Declaration
27819 | RSB1A120F7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
27820 | RSB1A120F7 | Offer Sustainability | Toxic heavy metal free | Yes
27821 | RSB1A120F7 | Offer Sustainability | Mercury free | Yes
27822 | RSB1A120F7 | Offer Sustainability | RoHS exemption information | Yes
27823 | RSB1A120F7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
27824 | RSB1A120F7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
27825 | RSB1A120F7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
27826 | RSB1A120F7 | Contractual warranty | Warranty | 18 months
27827 | RSB1A120FD | Main | range of product | Zelio Relay
27828 | RSB1A120FD | Main | series name | Interface relay
27829 | RSB1A120FD | Main | product or component type | Plug-in relay
27830 | RSB1A120FD | Main | device short name | RSB
27831 | RSB1A120FD | Main | contacts type and composition | 1 C/O
27832 | RSB1A120FD | Main | contact operation | Standard
27833 | RSB1A120FD | Main | [Uc] control circuit voltage | 110 V DC
27834 | RSB1A120FD | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
27835 | RSB1A120FD | Main | status LED | Without
27836 | RSB1A120FD | Main | control type | Without push-button
27837 | RSB1A120FD | Complementary | shape of pin | Flat (PCB type)
27838 | RSB1A120FD | Complementary | average coil resistance | 30250 Ohm network: AC at 20 °C +/- 10 %
27839 | RSB1A120FD | Complementary | [Ue] rated operational voltage | 77...165 V DC
27840 | RSB1A120FD | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
27841 | RSB1A120FD | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
27842 | RSB1A120FD | Complementary | contacts material | Silver alloy (AgNi)
27843 | RSB1A120FD | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
27844 | RSB1A120FD | Complementary | minimum switching current | 10 mA
27845 | RSB1A120FD | Complementary | maximum switching voltage | 250 V DC conforming to IEC
27846 | RSB1A120FD | Complementary | minimum switching voltage | 12 V
27847 | RSB1A120FD | Complementary | maximum switching capacity | 3000 VA/336 W
27848 | RSB1A120FD | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
27849 | RSB1A120FD | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
27850 | RSB1A120FD | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
27851 | RSB1A120FD | Complementary | mechanical durability | 30000000 cycles
27852 | RSB1A120FD | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
27853 | RSB1A120FD | Complementary | operating time | 20 ms operating 20 ms reset
27854 | RSB1A120FD | Complementary | average coil consumption | 0.45 W DC
27855 | RSB1A120FD | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
27856 | RSB1A120FD | Complementary | safety reliability data | B10d = 100000
27857 | RSB1A120FD | Complementary | protection category | RT I
27858 | RSB1A120FD | Complementary | test levels | Level A group mounting
27859 | RSB1A120FD | Complementary | operating position | Any position
27860 | RSB1A120FD | Complementary | net weight | 0.014 kg
27861 | RSB1A120FD | Complementary | sale per indivisible quantity | 10
27862 | RSB1A120FD | Complementary | device presentation | Complete product
27863 | RSB1A120FD | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
27864 | RSB1A120FD | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
27865 | RSB1A120FD | Environment | product certifications | EAC UL CSA
27866 | RSB1A120FD | Environment | ambient air temperature for storage | -40…85 °C
27867 | RSB1A120FD | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
27868 | RSB1A120FD | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
27869 | RSB1A120FD | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
27870 | RSB1A120FD | Environment | ambient air temperature for operation | -40…85 °C (DC)
27871 | RSB1A120FD | Offer Sustainability | Sustainable offer status | Green Premium product
27872 | RSB1A120FD | Offer Sustainability | REACh Regulation | REACh Declaration
27873 | RSB1A120FD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
27874 | RSB1A120FD | Offer Sustainability | Toxic heavy metal free | Yes
27875 | RSB1A120FD | Offer Sustainability | Mercury free | Yes
27876 | RSB1A120FD | Offer Sustainability | RoHS exemption information | Yes
27877 | RSB1A120FD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
27878 | RSB1A120FD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
27879 | RSB1A120FD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
27880 | RSB1A120FD | Contractual warranty | Warranty | 18 months
27881 | RSB1A120JD | Main | range of product | Zelio Relay
27882 | RSB1A120JD | Main | series name | Interface relay
27883 | RSB1A120JD | Main | product or component type | Plug-in relay
27884 | RSB1A120JD | Main | device short name | RSB
27885 | RSB1A120JD | Main | contacts type and composition | 1 C/O
27886 | RSB1A120JD | Main | contact operation | Standard
27887 | RSB1A120JD | Main | [Uc] control circuit voltage | 12 V DC
27888 | RSB1A120JD | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
27889 | RSB1A120JD | Main | status LED | Without
27890 | RSB1A120JD | Main | control type | Without push-button
27891 | RSB1A120JD | Complementary | shape of pin | Flat (PCB type)
27892 | RSB1A120JD | Complementary | average coil resistance | 360 Ohm network: DC at 20 °C +/- 10 %
27893 | RSB1A120JD | Complementary | [Ue] rated operational voltage | 8.4...18 V DC
27894 | RSB1A120JD | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
27895 | RSB1A120JD | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
27896 | RSB1A120JD | Complementary | contacts material | Silver alloy (AgNi)
27897 | RSB1A120JD | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
27898 | RSB1A120JD | Complementary | minimum switching current | 10 mA
27899 | RSB1A120JD | Complementary | maximum switching voltage | 250 V DC conforming to IEC
27900 | RSB1A120JD | Complementary | minimum switching voltage | 12 V
27901 | RSB1A120JD | Complementary | maximum switching capacity | 3000 VA/336 W
27902 | RSB1A120JD | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
27903 | RSB1A120JD | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
27904 | RSB1A120JD | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
27905 | RSB1A120JD | Complementary | mechanical durability | 30000000 cycles
27906 | RSB1A120JD | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
27907 | RSB1A120JD | Complementary | operating time | 20 ms operating 20 ms reset
27908 | RSB1A120JD | Complementary | average coil consumption | 0.45 W DC
27909 | RSB1A120JD | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
27910 | RSB1A120JD | Complementary | safety reliability data | B10d = 100000
27911 | RSB1A120JD | Complementary | protection category | RT I
27912 | RSB1A120JD | Complementary | test levels | Level A group mounting
27913 | RSB1A120JD | Complementary | operating position | Any position
27914 | RSB1A120JD | Complementary | net weight | 0.014 kg
27915 | RSB1A120JD | Complementary | sale per indivisible quantity | 10
27916 | RSB1A120JD | Complementary | device presentation | Complete product
27917 | RSB1A120JD | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
27918 | RSB1A120JD | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
27919 | RSB1A120JD | Environment | product certifications | EAC UL CSA
27920 | RSB1A120JD | Environment | ambient air temperature for storage | -40…85 °C
27921 | RSB1A120JD | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
27922 | RSB1A120JD | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
27923 | RSB1A120JD | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
27924 | RSB1A120JD | Environment | ambient air temperature for operation | -40…85 °C (DC)
27925 | RSB1A120JD | Offer Sustainability | Sustainable offer status | Green Premium product
27926 | RSB1A120JD | Offer Sustainability | REACh free of SVHC | Yes
27927 | RSB1A120JD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
27928 | RSB1A120JD | Offer Sustainability | Toxic heavy metal free | Yes
27929 | RSB1A120JD | Offer Sustainability | Mercury free | Yes
27930 | RSB1A120JD | Offer Sustainability | RoHS exemption information | Yes
27931 | RSB1A120JD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
27932 | RSB1A120JD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
27933 | RSB1A120JD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
27934 | RSB1A120JD | Contractual warranty | Warranty | 18 months
27935 | RSB1A120P7 | Main | range of product | Zelio Relay
27936 | RSB1A120P7 | Main | series name | Interface relay
27937 | RSB1A120P7 | Main | product or component type | Plug-in relay
27938 | RSB1A120P7 | Main | device short name | RSB
27939 | RSB1A120P7 | Main | contacts type and composition | 1 C/O
27940 | RSB1A120P7 | Main | contact operation | Standard
27941 | RSB1A120P7 | Main | [Uc] control circuit voltage | 230 V AC
27942 | RSB1A120P7 | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
27943 | RSB1A120P7 | Main | status LED | Without
27944 | RSB1A120P7 | Main | control type | Without push-button
27945 | RSB1A120P7 | Complementary | shape of pin | Flat (PCB type)
27946 | RSB1A120P7 | Complementary | average coil resistance | 33000 Ohm network: AC at 20 °C +/- 10 %
27947 | RSB1A120P7 | Complementary | [Ue] rated operational voltage | 184...345 V AC 50/60 Hz
27948 | RSB1A120P7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
27949 | RSB1A120P7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
27950 | RSB1A120P7 | Complementary | contacts material | Silver alloy (AgNi)
27951 | RSB1A120P7 | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
27952 | RSB1A120P7 | Complementary | minimum switching current | 10 mA
27953 | RSB1A120P7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
27954 | RSB1A120P7 | Complementary | minimum switching voltage | 12 V
27955 | RSB1A120P7 | Complementary | maximum switching capacity | 3000 VA/336 W
27956 | RSB1A120P7 | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
27957 | RSB1A120P7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
27958 | RSB1A120P7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
27959 | RSB1A120P7 | Complementary | mechanical durability | 10000000 cycles
27960 | RSB1A120P7 | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
27961 | RSB1A120P7 | Complementary | operating time | 20 ms operating 20 ms reset
27962 | RSB1A120P7 | Complementary | marking | CE
27963 | RSB1A120P7 | Complementary | average coil consumption | 0.75 VA AC
27964 | RSB1A120P7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
27965 | RSB1A120P7 | Complementary | safety reliability data | B10d = 100000
27966 | RSB1A120P7 | Complementary | protection category | RT I
27967 | RSB1A120P7 | Complementary | test levels | Level A group mounting
27968 | RSB1A120P7 | Complementary | operating position | Any position
27969 | RSB1A120P7 | Complementary | net weight | 0.014 kg
27970 | RSB1A120P7 | Complementary | sale per indivisible quantity | 10
27971 | RSB1A120P7 | Complementary | device presentation | Complete product
27972 | RSB1A120P7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
27973 | RSB1A120P7 | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
27974 | RSB1A120P7 | Environment | product certifications | EAC UL CSA
27975 | RSB1A120P7 | Environment | ambient air temperature for storage | -40…85 °C
27976 | RSB1A120P7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
27977 | RSB1A120P7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
27978 | RSB1A120P7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
27979 | RSB1A120P7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
27980 | RSB1A120P7 | Offer Sustainability | Sustainable offer status | Green Premium product
27981 | RSB1A120P7 | Offer Sustainability | REACh free of SVHC | Yes
27982 | RSB1A120P7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
27983 | RSB1A120P7 | Offer Sustainability | Toxic heavy metal free | Yes
27984 | RSB1A120P7 | Offer Sustainability | Mercury free | Yes
27985 | RSB1A120P7 | Offer Sustainability | RoHS exemption information | Yes
27986 | RSB1A120P7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
27987 | RSB1A120P7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
27988 | RSB1A120P7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
27989 | RSB1A120P7 | Contractual warranty | Warranty | 18 months
27990 | RSB1A120U7 | Main | range of product | Zelio Relay
27991 | RSB1A120U7 | Main | series name | Interface relay
27992 | RSB1A120U7 | Main | product or component type | Plug-in relay
27993 | RSB1A120U7 | Main | device short name | RSB
27994 | RSB1A120U7 | Main | contacts type and composition | 1 C/O
27995 | RSB1A120U7 | Main | contact operation | Standard
27996 | RSB1A120U7 | Main | [Uc] control circuit voltage | 240 V AC
27997 | RSB1A120U7 | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
27998 | RSB1A120U7 | Main | status LED | Without
27999 | RSB1A120U7 | Main | control type | Without push-button
28000 | RSB1A120U7 | Complementary | shape of pin | Flat (PCB type)
28001 | RSB1A120U7 | Complementary | average coil resistance | 33000 Ohm network: AC at 20 °C +/- 10 %
28002 | RSB1A120U7 | Complementary | [Ue] rated operational voltage | 192...360 V AC 50/60 Hz
28003 | RSB1A120U7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28004 | RSB1A120U7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
28005 | RSB1A120U7 | Complementary | contacts material | Silver alloy (AgNi)
28006 | RSB1A120U7 | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
28007 | RSB1A120U7 | Complementary | minimum switching current | 10 mA
28008 | RSB1A120U7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28009 | RSB1A120U7 | Complementary | minimum switching voltage | 12 V
28010 | RSB1A120U7 | Complementary | maximum switching capacity | 3000 VA/336 W
28011 | RSB1A120U7 | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
28012 | RSB1A120U7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28013 | RSB1A120U7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28014 | RSB1A120U7 | Complementary | mechanical durability | 10000000 cycles
28015 | RSB1A120U7 | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
28016 | RSB1A120U7 | Complementary | operating time | 20 ms operating 20 ms reset
28017 | RSB1A120U7 | Complementary | marking | CE
28018 | RSB1A120U7 | Complementary | average coil consumption | 0.75 VA AC
28019 | RSB1A120U7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
28020 | RSB1A120U7 | Complementary | safety reliability data | B10d = 100000
28021 | RSB1A120U7 | Complementary | protection category | RT I
28022 | RSB1A120U7 | Complementary | test levels | Level A group mounting
28023 | RSB1A120U7 | Complementary | operating position | Any position
28024 | RSB1A120U7 | Complementary | net weight | 0.014 kg
28025 | RSB1A120U7 | Complementary | sale per indivisible quantity | 10
28026 | RSB1A120U7 | Complementary | device presentation | Complete product
28027 | RSB1A120U7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28028 | RSB1A120U7 | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1
28029 | RSB1A120U7 | Environment | product certifications | CSA UL EAC
28030 | RSB1A120U7 | Environment | ambient air temperature for storage | -40…85 °C
28031 | RSB1A120U7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28032 | RSB1A120U7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28033 | RSB1A120U7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28034 | RSB1A120U7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
28035 | RSB1A120U7 | Offer Sustainability | Sustainable offer status | Green Premium product
28036 | RSB1A120U7 | Offer Sustainability | REACh free of SVHC | Yes
28037 | RSB1A120U7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28038 | RSB1A120U7 | Offer Sustainability | Toxic heavy metal free | Yes
28039 | RSB1A120U7 | Offer Sustainability | Mercury free | Yes
28040 | RSB1A120U7 | Offer Sustainability | RoHS exemption information | Yes
28041 | RSB1A120U7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28042 | RSB1A120U7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28043 | RSB1A120U7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28044 | RSB1A120U7 | Contractual warranty | Warranty | 18 months
28045 | RSB1A120M7 | Main | range of product | Zelio Relay
28046 | RSB1A120M7 | Main | series name | Interface relay
28047 | RSB1A120M7 | Main | product or component type | Plug-in relay
28048 | RSB1A120M7 | Main | device short name | RSB
28049 | RSB1A120M7 | Main | contacts type and composition | 1 C/O
28050 | RSB1A120M7 | Main | contact operation | Standard
28051 | RSB1A120M7 | Main | [Uc] control circuit voltage | 220 V AC
28052 | RSB1A120M7 | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
28053 | RSB1A120M7 | Main | status LED | Without
28054 | RSB1A120M7 | Main | control type | Without push-button
28055 | RSB1A120M7 | Complementary | shape of pin | Flat (PCB type)
28056 | RSB1A120M7 | Complementary | average coil resistance | 33000 Ohm network: AC at 20 °C +/- 10 %
28057 | RSB1A120M7 | Complementary | [Ue] rated operational voltage | 176...330 V AC 50/60 Hz
28058 | RSB1A120M7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28059 | RSB1A120M7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
28060 | RSB1A120M7 | Complementary | contacts material | Silver alloy (AgNi)
28061 | RSB1A120M7 | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
28062 | RSB1A120M7 | Complementary | minimum switching current | 10 mA
28063 | RSB1A120M7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28064 | RSB1A120M7 | Complementary | minimum switching voltage | 12 V
28065 | RSB1A120M7 | Complementary | maximum switching capacity | 3000 VA/336 W
28066 | RSB1A120M7 | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
28067 | RSB1A120M7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28068 | RSB1A120M7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28069 | RSB1A120M7 | Complementary | mechanical durability | 10000000 cycles
28070 | RSB1A120M7 | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
28071 | RSB1A120M7 | Complementary | operating time | 20 ms operating 20 ms reset
28072 | RSB1A120M7 | Complementary | average coil consumption | 0.75 VA AC
28073 | RSB1A120M7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
28074 | RSB1A120M7 | Complementary | safety reliability data | B10d = 100000
28075 | RSB1A120M7 | Complementary | protection category | RT I
28076 | RSB1A120M7 | Complementary | test levels | Level A group mounting
28077 | RSB1A120M7 | Complementary | operating position | Any position
28078 | RSB1A120M7 | Complementary | net weight | 0.014 kg
28079 | RSB1A120M7 | Complementary | sale per indivisible quantity | 10
28080 | RSB1A120M7 | Complementary | device presentation | Complete product
28081 | RSB1A120M7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28082 | RSB1A120M7 | Environment | standards | EN/IEC 61810-1 UL 508 CSA C22.2 No 14
28083 | RSB1A120M7 | Environment | product certifications | CSA EAC UL
28084 | RSB1A120M7 | Environment | ambient air temperature for storage | -40…85 °C
28085 | RSB1A120M7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28086 | RSB1A120M7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28087 | RSB1A120M7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28088 | RSB1A120M7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
28089 | RSB1A120M7 | Offer Sustainability | Sustainable offer status | Green Premium product
28090 | RSB1A120M7 | Offer Sustainability | REACh Regulation | REACh Declaration
28091 | RSB1A120M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28092 | RSB1A120M7 | Offer Sustainability | Toxic heavy metal free | Yes
28093 | RSB1A120M7 | Offer Sustainability | Mercury free | Yes
28094 | RSB1A120M7 | Offer Sustainability | RoHS exemption information | Yes
28095 | RSB1A120M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28096 | RSB1A120M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28097 | RSB1A120M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28098 | RSB1A120M7 | Contractual warranty | Warranty | 18 months
28099 | RSB1A120ND | Main | range of product | Zelio Relay
28100 | RSB1A120ND | Main | series name | Interface relay
28101 | RSB1A120ND | Main | product or component type | Plug-in relay
28102 | RSB1A120ND | Main | device short name | RSB
28103 | RSB1A120ND | Main | contacts type and composition | 1 C/O
28104 | RSB1A120ND | Main | contact operation | Standard
28105 | RSB1A120ND | Main | [Uc] control circuit voltage | 60 V DC
28106 | RSB1A120ND | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
28107 | RSB1A120ND | Main | status LED | Without
28108 | RSB1A120ND | Main | control type | Without push-button
28109 | RSB1A120ND | Complementary | shape of pin | Flat (PCB type)
28110 | RSB1A120ND | Complementary | average coil resistance | 9000 Ohm network: AC at 20 °C +/- 10 %
28111 | RSB1A120ND | Complementary | [Ue] rated operational voltage | 42...90 V DC
28112 | RSB1A120ND | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28113 | RSB1A120ND | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
28114 | RSB1A120ND | Complementary | contacts material | Silver alloy (AgNi)
28115 | RSB1A120ND | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
28116 | RSB1A120ND | Complementary | minimum switching current | 10 mA
28117 | RSB1A120ND | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28118 | RSB1A120ND | Complementary | minimum switching voltage | 12 V
28119 | RSB1A120ND | Complementary | maximum switching capacity | 3000 VA/336 W
28120 | RSB1A120ND | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
28121 | RSB1A120ND | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28122 | RSB1A120ND | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28123 | RSB1A120ND | Complementary | mechanical durability | 30000000 cycles
28124 | RSB1A120ND | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
28125 | RSB1A120ND | Complementary | operating time | 20 ms operating 20 ms reset
28126 | RSB1A120ND | Complementary | marking | CE
28127 | RSB1A120ND | Complementary | average coil consumption | 0.45 W DC
28128 | RSB1A120ND | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
28129 | RSB1A120ND | Complementary | safety reliability data | B10d = 100000
28130 | RSB1A120ND | Complementary | protection category | RT I
28131 | RSB1A120ND | Complementary | test levels | Level A group mounting
28132 | RSB1A120ND | Complementary | operating position | Any position
28133 | RSB1A120ND | Complementary | net weight | 0.014 kg
28134 | RSB1A120ND | Complementary | sale per indivisible quantity | 10
28135 | RSB1A120ND | Complementary | device presentation | Complete product
28136 | RSB1A120ND | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28137 | RSB1A120ND | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508
28138 | RSB1A120ND | Environment | product certifications | CSA UL EAC
28139 | RSB1A120ND | Environment | ambient air temperature for storage | -40…85 °C
28140 | RSB1A120ND | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28141 | RSB1A120ND | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28142 | RSB1A120ND | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28143 | RSB1A120ND | Environment | ambient air temperature for operation | -40…85 °C (DC)
28144 | RSB1A120ND | Offer Sustainability | Sustainable offer status | Green Premium product
28145 | RSB1A120ND | Offer Sustainability | REACh Regulation | REACh Declaration
28146 | RSB1A120ND | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28147 | RSB1A120ND | Offer Sustainability | Toxic heavy metal free | Yes
28148 | RSB1A120ND | Offer Sustainability | Mercury free | Yes
28149 | RSB1A120ND | Offer Sustainability | RoHS exemption information | Yes
28150 | RSB1A120ND | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28151 | RSB1A120ND | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28152 | RSB1A120ND | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28153 | RSB1A120ND | Contractual warranty | Warranty | 18 months
28154 | RSB1A120RD | Main | range of product | Harmony Relay
28155 | RSB1A120RD | Main | series name | Interface relay
28156 | RSB1A120RD | Main | product or component type | Plug-in relay
28157 | RSB1A120RD | Main | device short name | RSB
28158 | RSB1A120RD | Main | contacts type and composition | 1 C/O
28159 | RSB1A120RD | Main | contact operation | Standard
28160 | RSB1A120RD | Main | [Uc] control circuit voltage | 6 V DC
28161 | RSB1A120RD | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
28162 | RSB1A120RD | Main | status LED | Without
28163 | RSB1A120RD | Main | control type | Without push-button
28164 | RSB1A120RD | Complementary | shape of pin | Flat (PCB type)
28165 | RSB1A120RD | Complementary | average coil resistance | 90 Ohm network: AC at 20 °C +/- 10 %
28166 | RSB1A120RD | Complementary | [Ue] rated operational voltage | 4.2...9 V DC
28167 | RSB1A120RD | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28168 | RSB1A120RD | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
28169 | RSB1A120RD | Complementary | contacts material | Silver alloy (AgNi)
28170 | RSB1A120RD | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
28171 | RSB1A120RD | Complementary | minimum switching current | 10 mA
28172 | RSB1A120RD | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28173 | RSB1A120RD | Complementary | minimum switching voltage | 12 V
28174 | RSB1A120RD | Complementary | maximum switching capacity | 3000 VA/336 W
28175 | RSB1A120RD | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
28176 | RSB1A120RD | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28177 | RSB1A120RD | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28178 | RSB1A120RD | Complementary | mechanical durability | 30000000 cycles
28179 | RSB1A120RD | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
28180 | RSB1A120RD | Complementary | operating time | 20 ms operating 20 ms reset
28181 | RSB1A120RD | Complementary | marking | CE
28182 | RSB1A120RD | Complementary | average coil consumption | 0.45 W DC
28183 | RSB1A120RD | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
28184 | RSB1A120RD | Complementary | safety reliability data | B10d = 100000
28185 | RSB1A120RD | Complementary | protection category | RT I
28186 | RSB1A120RD | Complementary | test levels | Level A group mounting
28187 | RSB1A120RD | Complementary | operating position | Any position
28188 | RSB1A120RD | Complementary | net weight | 0.014 kg
28189 | RSB1A120RD | Complementary | sale per indivisible quantity | 10
28190 | RSB1A120RD | Complementary | device presentation | Complete product
28191 | RSB1A120RD | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28192 | RSB1A120RD | Environment | standards | EN/IEC 61810-1 UL 508 CSA C22.2 No 14
28193 | RSB1A120RD | Environment | product certifications | UL CSA EAC
28194 | RSB1A120RD | Environment | ambient air temperature for storage | -40…85 °C
28195 | RSB1A120RD | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28196 | RSB1A120RD | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28197 | RSB1A120RD | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28198 | RSB1A120RD | Environment | ambient air temperature for operation | -40…85 °C (DC)
28199 | RSB1A120RD | Offer Sustainability | Sustainable offer status | Green Premium product
28200 | RSB1A120RD | Offer Sustainability | REACh Regulation | REACh Declaration
28201 | RSB1A120RD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28202 | RSB1A120RD | Offer Sustainability | Toxic heavy metal free | Yes
28203 | RSB1A120RD | Offer Sustainability | Mercury free | Yes
28204 | RSB1A120RD | Offer Sustainability | RoHS exemption information | Yes
28205 | RSB1A120RD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28206 | RSB1A120RD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28207 | RSB1A120RD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28208 | RSB1A120RD | Contractual warranty | Warranty | 18 months
28209 | RSB1A160B7 | Main | range of product | Zelio Relay
28210 | RSB1A160B7 | Main | series name | Interface relay
28211 | RSB1A160B7 | Main | product or component type | Plug-in relay
28212 | RSB1A160B7 | Main | device short name | RSB
28213 | RSB1A160B7 | Main | contacts type and composition | 1 C/O
28214 | RSB1A160B7 | Main | contact operation | Standard
28215 | RSB1A160B7 | Main | [Uc] control circuit voltage | 24 V AC
28216 | RSB1A160B7 | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
28217 | RSB1A160B7 | Main | status LED | Without
28218 | RSB1A160B7 | Main | control type | Without push-button
28219 | RSB1A160B7 | Complementary | shape of pin | Flat (PCB type)
28220 | RSB1A160B7 | Complementary | average coil resistance | 368 Ohm network: AC at 20 °C +/- 10 %
28221 | RSB1A160B7 | Complementary | [Ue] rated operational voltage | 19.2...36 V AC 50/60 Hz
28222 | RSB1A160B7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28223 | RSB1A160B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
28224 | RSB1A160B7 | Complementary | contacts material | Silver alloy (AgNi)
28225 | RSB1A160B7 | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
28226 | RSB1A160B7 | Complementary | minimum switching current | 10 mA
28227 | RSB1A160B7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28228 | RSB1A160B7 | Complementary | minimum switching voltage | 12 V
28229 | RSB1A160B7 | Complementary | maximum switching capacity | 4000 VA/448 W
28230 | RSB1A160B7 | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
28231 | RSB1A160B7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28232 | RSB1A160B7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28233 | RSB1A160B7 | Complementary | mechanical durability | 10000000 cycles
28234 | RSB1A160B7 | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
28235 | RSB1A160B7 | Complementary | operating time | 20 ms operating 20 ms reset
28236 | RSB1A160B7 | Complementary | marking | CE
28237 | RSB1A160B7 | Complementary | average coil consumption | 0.75 VA AC
28238 | RSB1A160B7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
28239 | RSB1A160B7 | Complementary | safety reliability data | B10d = 100000
28240 | RSB1A160B7 | Complementary | protection category | RT I
28241 | RSB1A160B7 | Complementary | test levels | Level A group mounting
28242 | RSB1A160B7 | Complementary | operating position | Any position
28243 | RSB1A160B7 | Complementary | net weight | 0.014 kg
28244 | RSB1A160B7 | Complementary | sale per indivisible quantity | 10
28245 | RSB1A160B7 | Complementary | device presentation | Complete product
28246 | RSB1A160B7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28247 | RSB1A160B7 | Environment | standards | UL 508 EN/IEC 61810-1 CSA C22.2 No 14
28248 | RSB1A160B7 | Environment | product certifications | UL EAC CSA
28249 | RSB1A160B7 | Environment | ambient air temperature for storage | -40…85 °C
28250 | RSB1A160B7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28251 | RSB1A160B7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28252 | RSB1A160B7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28253 | RSB1A160B7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
28254 | RSB1A160B7 | Offer Sustainability | Sustainable offer status | Green Premium product
28255 | RSB1A160B7 | Offer Sustainability | REACh Regulation | REACh Declaration
28256 | RSB1A160B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28257 | RSB1A160B7 | Offer Sustainability | Toxic heavy metal free | Yes
28258 | RSB1A160B7 | Offer Sustainability | Mercury free | Yes
28259 | RSB1A160B7 | Offer Sustainability | RoHS exemption information | Yes
28260 | RSB1A160B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28261 | RSB1A160B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28262 | RSB1A160B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28263 | RSB1A160B7 | Contractual warranty | Warranty | 18 months
28264 | RSB1A160BD | Main | range of product | Zelio Relay
28265 | RSB1A160BD | Main | series name | Interface relay
28266 | RSB1A160BD | Main | product or component type | Plug-in relay
28267 | RSB1A160BD | Main | device short name | RSB
28268 | RSB1A160BD | Main | contacts type and composition | 1 C/O
28269 | RSB1A160BD | Main | contact operation | Standard
28270 | RSB1A160BD | Main | [Uc] control circuit voltage | 24 V DC
28271 | RSB1A160BD | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
28272 | RSB1A160BD | Main | status LED | Without
28273 | RSB1A160BD | Main | control type | Without push-button
28274 | RSB1A160BD | Complementary | shape of pin | Flat (PCB type)
28275 | RSB1A160BD | Complementary | average coil resistance | 1440 Ohm network: AC at 20 °C +/- 10 %
28276 | RSB1A160BD | Complementary | [Ue] rated operational voltage | 16.8...36 V DC
28277 | RSB1A160BD | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28278 | RSB1A160BD | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
28279 | RSB1A160BD | Complementary | contacts material | Silver alloy (AgNi)
28280 | RSB1A160BD | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
28281 | RSB1A160BD | Complementary | minimum switching current | 10 mA
28282 | RSB1A160BD | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28283 | RSB1A160BD | Complementary | minimum switching voltage | 12 V
28284 | RSB1A160BD | Complementary | maximum switching capacity | 4000 VA/448 W
28285 | RSB1A160BD | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
28286 | RSB1A160BD | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28287 | RSB1A160BD | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28288 | RSB1A160BD | Complementary | mechanical durability | 30000000 cycles
28289 | RSB1A160BD | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
28290 | RSB1A160BD | Complementary | operating time | 20 ms operating 20 ms reset
28291 | RSB1A160BD | Complementary | marking | CE
28292 | RSB1A160BD | Complementary | average coil consumption | 0.45 W DC
28293 | RSB1A160BD | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
28294 | RSB1A160BD | Complementary | safety reliability data | B10d = 100000
28295 | RSB1A160BD | Complementary | protection category | RT I
28296 | RSB1A160BD | Complementary | test levels | Level A group mounting
28297 | RSB1A160BD | Complementary | operating position | Any position
28298 | RSB1A160BD | Complementary | net weight | 0.014 kg
28299 | RSB1A160BD | Complementary | sale per indivisible quantity | 10
28300 | RSB1A160BD | Complementary | device presentation | Complete product
28301 | RSB1A160BD | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28302 | RSB1A160BD | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1
28303 | RSB1A160BD | Environment | product certifications | EAC CSA UL
28304 | RSB1A160BD | Environment | ambient air temperature for storage | -40…85 °C
28305 | RSB1A160BD | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28306 | RSB1A160BD | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28307 | RSB1A160BD | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28308 | RSB1A160BD | Environment | ambient air temperature for operation | -40…85 °C (DC)
28309 | RSB1A160BD | Offer Sustainability | Sustainable offer status | Green Premium product
28310 | RSB1A160BD | Offer Sustainability | REACh free of SVHC | Yes
28311 | RSB1A160BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28312 | RSB1A160BD | Offer Sustainability | Toxic heavy metal free | Yes
28313 | RSB1A160BD | Offer Sustainability | Mercury free | Yes
28314 | RSB1A160BD | Offer Sustainability | RoHS exemption information | Yes
28315 | RSB1A160BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28316 | RSB1A160BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28317 | RSB1A160BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28318 | RSB1A160BD | Contractual warranty | Warranty | 18 months
28319 | RSB1A160E7 | Main | range of product | Zelio Relay
28320 | RSB1A160E7 | Main | series name | Interface relay
28321 | RSB1A160E7 | Main | product or component type | Plug-in relay
28322 | RSB1A160E7 | Main | device short name | RSB
28323 | RSB1A160E7 | Main | contacts type and composition | 1 C/O
28324 | RSB1A160E7 | Main | contact operation | Standard
28325 | RSB1A160E7 | Main | [Uc] control circuit voltage | 48 V AC
28326 | RSB1A160E7 | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
28327 | RSB1A160E7 | Main | status LED | Without
28328 | RSB1A160E7 | Main | control type | Without push-button
28329 | RSB1A160E7 | Complementary | shape of pin | Flat (PCB type)
28330 | RSB1A160E7 | Complementary | average coil resistance | 1540 Ohm network: AC at 20 °C +/- 10 %
28331 | RSB1A160E7 | Complementary | [Ue] rated operational voltage | 38.4...72 V AC 50/60 Hz
28332 | RSB1A160E7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28333 | RSB1A160E7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
28334 | RSB1A160E7 | Complementary | contacts material | Silver alloy (AgNi)
28335 | RSB1A160E7 | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
28336 | RSB1A160E7 | Complementary | minimum switching current | 10 mA
28337 | RSB1A160E7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28338 | RSB1A160E7 | Complementary | minimum switching voltage | 12 V
28339 | RSB1A160E7 | Complementary | maximum switching capacity | 4000 VA/448 W
28340 | RSB1A160E7 | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
28341 | RSB1A160E7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28342 | RSB1A160E7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28343 | RSB1A160E7 | Complementary | mechanical durability | 10000000 cycles
28344 | RSB1A160E7 | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
28345 | RSB1A160E7 | Complementary | operating time | 20 ms operating 20 ms reset
28346 | RSB1A160E7 | Complementary | marking | CE
28347 | RSB1A160E7 | Complementary | average coil consumption | 0.75 VA AC
28348 | RSB1A160E7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
28349 | RSB1A160E7 | Complementary | safety reliability data | B10d = 100000
28350 | RSB1A160E7 | Complementary | protection category | RT I
28351 | RSB1A160E7 | Complementary | test levels | Level A group mounting
28352 | RSB1A160E7 | Complementary | operating position | Any position
28353 | RSB1A160E7 | Complementary | net weight | 0.014 kg
28354 | RSB1A160E7 | Complementary | sale per indivisible quantity | 10
28355 | RSB1A160E7 | Complementary | device presentation | Complete product
28356 | RSB1A160E7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28357 | RSB1A160E7 | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
28358 | RSB1A160E7 | Environment | product certifications | UL EAC CSA
28359 | RSB1A160E7 | Environment | ambient air temperature for storage | -40…85 °C
28360 | RSB1A160E7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28361 | RSB1A160E7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28362 | RSB1A160E7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28363 | RSB1A160E7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
28364 | RSB1A160E7 | Offer Sustainability | Sustainable offer status | Green Premium product
28365 | RSB1A160E7 | Offer Sustainability | REACh Regulation | REACh Declaration
28366 | RSB1A160E7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28367 | RSB1A160E7 | Offer Sustainability | Toxic heavy metal free | Yes
28368 | RSB1A160E7 | Offer Sustainability | Mercury free | Yes
28369 | RSB1A160E7 | Offer Sustainability | RoHS exemption information | Yes
28370 | RSB1A160E7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28371 | RSB1A160E7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28372 | RSB1A160E7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28373 | RSB1A160E7 | Contractual warranty | Warranty | 18 months
28374 | RSB1A160ED | Main | range of product | Zelio Relay
28375 | RSB1A160ED | Main | series name | Interface relay
28376 | RSB1A160ED | Main | product or component type | Plug-in relay
28377 | RSB1A160ED | Main | device short name | RSB
28378 | RSB1A160ED | Main | contacts type and composition | 1 C/O
28379 | RSB1A160ED | Main | contact operation | Standard
28380 | RSB1A160ED | Main | [Uc] control circuit voltage | 48 V DC
28381 | RSB1A160ED | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
28382 | RSB1A160ED | Main | status LED | Without
28383 | RSB1A160ED | Main | control type | Without push-button
28384 | RSB1A160ED | Complementary | shape of pin | Flat (PCB type)
28385 | RSB1A160ED | Complementary | average coil resistance | 5520 Ohm network: AC at 20 °C +/- 10 %
28386 | RSB1A160ED | Complementary | [Ue] rated operational voltage | 33.6...72 V DC
28387 | RSB1A160ED | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28388 | RSB1A160ED | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
28389 | RSB1A160ED | Complementary | contacts material | Silver alloy (AgNi)
28390 | RSB1A160ED | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
28391 | RSB1A160ED | Complementary | minimum switching current | 10 mA
28392 | RSB1A160ED | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28393 | RSB1A160ED | Complementary | minimum switching voltage | 12 V
28394 | RSB1A160ED | Complementary | maximum switching capacity | 4000 VA/448 W
28395 | RSB1A160ED | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
28396 | RSB1A160ED | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28397 | RSB1A160ED | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28398 | RSB1A160ED | Complementary | mechanical durability | 30000000 cycles
28399 | RSB1A160ED | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
28400 | RSB1A160ED | Complementary | operating time | 20 ms operating 20 ms reset
28401 | RSB1A160ED | Complementary | average coil consumption | 0.45 W DC
28402 | RSB1A160ED | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
28403 | RSB1A160ED | Complementary | safety reliability data | B10d = 100000
28404 | RSB1A160ED | Complementary | protection category | RT I
28405 | RSB1A160ED | Complementary | test levels | Level A group mounting
28406 | RSB1A160ED | Complementary | operating position | Any position
28407 | RSB1A160ED | Complementary | net weight | 0.014 kg
28408 | RSB1A160ED | Complementary | sale per indivisible quantity | 10
28409 | RSB1A160ED | Complementary | device presentation | Complete product
28410 | RSB1A160ED | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28411 | RSB1A160ED | Environment | standards | UL 508 EN/IEC 61810-1 CSA C22.2 No 14
28412 | RSB1A160ED | Environment | product certifications | EAC UL CSA
28413 | RSB1A160ED | Environment | ambient air temperature for storage | -40…85 °C
28414 | RSB1A160ED | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28415 | RSB1A160ED | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28416 | RSB1A160ED | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28417 | RSB1A160ED | Environment | ambient air temperature for operation | -40…85 °C (DC)
28418 | RSB1A160ED | Offer Sustainability | Sustainable offer status | Green Premium product
28419 | RSB1A160ED | Offer Sustainability | REACh free of SVHC | Yes
28420 | RSB1A160ED | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28421 | RSB1A160ED | Offer Sustainability | Toxic heavy metal free | Yes
28422 | RSB1A160ED | Offer Sustainability | Mercury free | Yes
28423 | RSB1A160ED | Offer Sustainability | RoHS exemption information | Yes
28424 | RSB1A160ED | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28425 | RSB1A160ED | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28426 | RSB1A160ED | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28427 | RSB1A160ED | Contractual warranty | Warranty | 18 months
28428 | RSB1A160F7 | Main | range of product | Zelio Relay
28429 | RSB1A160F7 | Main | series name | Interface relay
28430 | RSB1A160F7 | Main | product or component type | Plug-in relay
28431 | RSB1A160F7 | Main | device short name | RSB
28432 | RSB1A160F7 | Main | contacts type and composition | 1 C/O
28433 | RSB1A160F7 | Main | contact operation | Standard
28434 | RSB1A160F7 | Main | [Uc] control circuit voltage | 120 V AC
28435 | RSB1A160F7 | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
28436 | RSB1A160F7 | Main | status LED | Without
28437 | RSB1A160F7 | Main | control type | Without push-button
28438 | RSB1A160F7 | Complementary | shape of pin | Flat (PCB type)
28439 | RSB1A160F7 | Complementary | average coil resistance | 8360 Ohm network: AC at 20 °C +/- 10 %
28440 | RSB1A160F7 | Complementary | [Ue] rated operational voltage | 96...180 V AC 50/60 Hz
28441 | RSB1A160F7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28442 | RSB1A160F7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
28443 | RSB1A160F7 | Complementary | contacts material | Silver alloy (AgNi)
28444 | RSB1A160F7 | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
28445 | RSB1A160F7 | Complementary | minimum switching current | 10 mA
28446 | RSB1A160F7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28447 | RSB1A160F7 | Complementary | minimum switching voltage | 12 V
28448 | RSB1A160F7 | Complementary | maximum switching capacity | 4000 VA/448 W
28449 | RSB1A160F7 | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
28450 | RSB1A160F7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28451 | RSB1A160F7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28452 | RSB1A160F7 | Complementary | mechanical durability | 10000000 cycles
28453 | RSB1A160F7 | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
28454 | RSB1A160F7 | Complementary | operating time | 20 ms operating 20 ms reset
28455 | RSB1A160F7 | Complementary | average coil consumption | 0.75 VA AC
28456 | RSB1A160F7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
28457 | RSB1A160F7 | Complementary | safety reliability data | B10d = 100000
28458 | RSB1A160F7 | Complementary | protection category | RT I
28459 | RSB1A160F7 | Complementary | test levels | Level A group mounting
28460 | RSB1A160F7 | Complementary | operating position | Any position
28461 | RSB1A160F7 | Complementary | net weight | 0.014 kg
28462 | RSB1A160F7 | Complementary | sale per indivisible quantity | 10
28463 | RSB1A160F7 | Complementary | device presentation | Complete product
28464 | RSB1A160F7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28465 | RSB1A160F7 | Environment | standards | UL 508 EN/IEC 61810-1 CSA C22.2 No 14
28466 | RSB1A160F7 | Environment | product certifications | EAC CSA UL
28467 | RSB1A160F7 | Environment | ambient air temperature for storage | -40…85 °C
28468 | RSB1A160F7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28469 | RSB1A160F7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28470 | RSB1A160F7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28471 | RSB1A160F7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
28472 | RSB1A160F7 | Offer Sustainability | Sustainable offer status | Green Premium product
28473 | RSB1A160F7 | Offer Sustainability | REACh free of SVHC | Yes
28474 | RSB1A160F7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28475 | RSB1A160F7 | Offer Sustainability | Toxic heavy metal free | Yes
28476 | RSB1A160F7 | Offer Sustainability | Mercury free | Yes
28477 | RSB1A160F7 | Offer Sustainability | RoHS exemption information | Yes
28478 | RSB1A160F7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28479 | RSB1A160F7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28480 | RSB1A160F7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28481 | RSB1A160F7 | Contractual warranty | Warranty | 18 months
28482 | RSB1A160FD | Main | range of product | Zelio Relay
28483 | RSB1A160FD | Main | series name | Interface relay
28484 | RSB1A160FD | Main | product or component type | Plug-in relay
28485 | RSB1A160FD | Main | device short name | RSB
28486 | RSB1A160FD | Main | contacts type and composition | 1 C/O
28487 | RSB1A160FD | Main | contact operation | Standard
28488 | RSB1A160FD | Main | [Uc] control circuit voltage | 110 V DC
28489 | RSB1A160FD | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
28490 | RSB1A160FD | Main | status LED | Without
28491 | RSB1A160FD | Main | control type | Without push-button
28492 | RSB1A160FD | Complementary | shape of pin | Flat (PCB type)
28493 | RSB1A160FD | Complementary | average coil resistance | 30250 Ohm network: AC at 20 °C +/- 10 %
28494 | RSB1A160FD | Complementary | [Ue] rated operational voltage | 77...165 V DC
28495 | RSB1A160FD | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28496 | RSB1A160FD | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
28497 | RSB1A160FD | Complementary | contacts material | Silver alloy (AgNi)
28498 | RSB1A160FD | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
28499 | RSB1A160FD | Complementary | minimum switching current | 10 mA
28500 | RSB1A160FD | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28501 | RSB1A160FD | Complementary | minimum switching voltage | 12 V
28502 | RSB1A160FD | Complementary | maximum switching capacity | 4000 VA/448 W
28503 | RSB1A160FD | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
28504 | RSB1A160FD | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28505 | RSB1A160FD | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28506 | RSB1A160FD | Complementary | mechanical durability | 30000000 cycles
28507 | RSB1A160FD | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
28508 | RSB1A160FD | Complementary | operating time | 20 ms operating 20 ms reset
28509 | RSB1A160FD | Complementary | average coil consumption | 0.45 W DC
28510 | RSB1A160FD | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
28511 | RSB1A160FD | Complementary | safety reliability data | B10d = 100000
28512 | RSB1A160FD | Complementary | protection category | RT I
28513 | RSB1A160FD | Complementary | test levels | Level A group mounting
28514 | RSB1A160FD | Complementary | operating position | Any position
28515 | RSB1A160FD | Complementary | net weight | 0.014 kg
28516 | RSB1A160FD | Complementary | sale per indivisible quantity | 10
28517 | RSB1A160FD | Complementary | device presentation | Complete product
28518 | RSB1A160FD | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28519 | RSB1A160FD | Environment | standards | UL 508 EN/IEC 61810-1 CSA C22.2 No 14
28520 | RSB1A160FD | Environment | product certifications | CSA EAC UL
28521 | RSB1A160FD | Environment | ambient air temperature for storage | -40…85 °C
28522 | RSB1A160FD | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28523 | RSB1A160FD | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28524 | RSB1A160FD | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28525 | RSB1A160FD | Environment | ambient air temperature for operation | -40…85 °C (DC)
28526 | RSB1A160FD | Offer Sustainability | Sustainable offer status | Green Premium product
28527 | RSB1A160FD | Offer Sustainability | REACh Regulation | REACh Declaration
28528 | RSB1A160FD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28529 | RSB1A160FD | Offer Sustainability | Toxic heavy metal free | Yes
28530 | RSB1A160FD | Offer Sustainability | Mercury free | Yes
28531 | RSB1A160FD | Offer Sustainability | RoHS exemption information | Yes
28532 | RSB1A160FD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28533 | RSB1A160FD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28534 | RSB1A160FD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28535 | RSB1A160FD | Contractual warranty | Warranty | 18 months
28536 | RSB1A160JD | Main | range of product | Zelio Relay
28537 | RSB1A160JD | Main | series name | Interface relay
28538 | RSB1A160JD | Main | product or component type | Plug-in relay
28539 | RSB1A160JD | Main | device short name | RSB
28540 | RSB1A160JD | Main | contacts type and composition | 1 C/O
28541 | RSB1A160JD | Main | contact operation | Standard
28542 | RSB1A160JD | Main | [Uc] control circuit voltage | 12 V DC
28543 | RSB1A160JD | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
28544 | RSB1A160JD | Main | status LED | Without
28545 | RSB1A160JD | Main | control type | Without push-button
28546 | RSB1A160JD | Complementary | shape of pin | Flat (PCB type)
28547 | RSB1A160JD | Complementary | average coil resistance | 360 Ohm network: AC at 20 °C +/- 10 %
28548 | RSB1A160JD | Complementary | [Ue] rated operational voltage | 8.4...18 V DC
28549 | RSB1A160JD | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28550 | RSB1A160JD | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
28551 | RSB1A160JD | Complementary | contacts material | Silver alloy (AgNi)
28552 | RSB1A160JD | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
28553 | RSB1A160JD | Complementary | minimum switching current | 10 mA
28554 | RSB1A160JD | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28555 | RSB1A160JD | Complementary | minimum switching voltage | 12 V
28556 | RSB1A160JD | Complementary | maximum switching capacity | 4000 VA/448 W
28557 | RSB1A160JD | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
28558 | RSB1A160JD | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28559 | RSB1A160JD | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28560 | RSB1A160JD | Complementary | mechanical durability | 30000000 cycles
28561 | RSB1A160JD | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
28562 | RSB1A160JD | Complementary | operating time | 20 ms operating 20 ms reset
28563 | RSB1A160JD | Complementary | average coil consumption | 0.45 W DC
28564 | RSB1A160JD | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
28565 | RSB1A160JD | Complementary | safety reliability data | B10d = 100000
28566 | RSB1A160JD | Complementary | protection category | RT I
28567 | RSB1A160JD | Complementary | test levels | Level A group mounting
28568 | RSB1A160JD | Complementary | operating position | Any position
28569 | RSB1A160JD | Complementary | net weight | 0.014 kg
28570 | RSB1A160JD | Complementary | sale per indivisible quantity | 10
28571 | RSB1A160JD | Complementary | device presentation | Complete product
28572 | RSB1A160JD | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28573 | RSB1A160JD | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
28574 | RSB1A160JD | Environment | product certifications | EAC UL CSA
28575 | RSB1A160JD | Environment | ambient air temperature for storage | -40…85 °C
28576 | RSB1A160JD | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28577 | RSB1A160JD | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28578 | RSB1A160JD | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28579 | RSB1A160JD | Environment | ambient air temperature for operation | -40…85 °C (DC)
28580 | RSB1A160JD | Offer Sustainability | Sustainable offer status | Green Premium product
28581 | RSB1A160JD | Offer Sustainability | REACh Regulation | REACh Declaration
28582 | RSB1A160JD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28583 | RSB1A160JD | Offer Sustainability | Toxic heavy metal free | Yes
28584 | RSB1A160JD | Offer Sustainability | Mercury free | Yes
28585 | RSB1A160JD | Offer Sustainability | RoHS exemption information | Yes
28586 | RSB1A160JD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28587 | RSB1A160JD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28588 | RSB1A160JD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28589 | RSB1A160JD | Contractual warranty | Warranty | 18 months
28590 | RSB1A160P7 | Main | range of product | Zelio Relay
28591 | RSB1A160P7 | Main | series name | Interface relay
28592 | RSB1A160P7 | Main | product or component type | Plug-in relay
28593 | RSB1A160P7 | Main | device short name | RSB
28594 | RSB1A160P7 | Main | contacts type and composition | 1 C/O
28595 | RSB1A160P7 | Main | contact operation | Standard
28596 | RSB1A160P7 | Main | [Uc] control circuit voltage | 230 V AC
28597 | RSB1A160P7 | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
28598 | RSB1A160P7 | Main | status LED | Without
28599 | RSB1A160P7 | Main | control type | Without push-button
28600 | RSB1A160P7 | Complementary | shape of pin | Flat (PCB type)
28601 | RSB1A160P7 | Complementary | average coil resistance | 33000 Ohm network: AC at 20 °C +/- 10 %
28602 | RSB1A160P7 | Complementary | [Ue] rated operational voltage | 184...345 V AC 50/60 Hz
28603 | RSB1A160P7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28604 | RSB1A160P7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
28605 | RSB1A160P7 | Complementary | contacts material | Silver alloy (AgNi)
28606 | RSB1A160P7 | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
28607 | RSB1A160P7 | Complementary | minimum switching current | 10 mA
28608 | RSB1A160P7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28609 | RSB1A160P7 | Complementary | minimum switching voltage | 12 V
28610 | RSB1A160P7 | Complementary | maximum switching capacity | 4000 VA/448 W
28611 | RSB1A160P7 | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
28612 | RSB1A160P7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28613 | RSB1A160P7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28614 | RSB1A160P7 | Complementary | mechanical durability | 10000000 cycles
28615 | RSB1A160P7 | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
28616 | RSB1A160P7 | Complementary | operating time | 20 ms operating 20 ms reset
28617 | RSB1A160P7 | Complementary | average coil consumption | 0.75 VA AC
28618 | RSB1A160P7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
28619 | RSB1A160P7 | Complementary | safety reliability data | B10d = 100000
28620 | RSB1A160P7 | Complementary | protection category | RT I
28621 | RSB1A160P7 | Complementary | test levels | Level A group mounting
28622 | RSB1A160P7 | Complementary | operating position | Any position
28623 | RSB1A160P7 | Complementary | net weight | 0.014 kg
28624 | RSB1A160P7 | Complementary | sale per indivisible quantity | 10
28625 | RSB1A160P7 | Complementary | device presentation | Complete product
28626 | RSB1A160P7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28627 | RSB1A160P7 | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508
28628 | RSB1A160P7 | Environment | product certifications | UL CSA EAC
28629 | RSB1A160P7 | Environment | ambient air temperature for storage | -40…85 °C
28630 | RSB1A160P7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28631 | RSB1A160P7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28632 | RSB1A160P7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28633 | RSB1A160P7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
28634 | RSB1A160P7 | Offer Sustainability | Sustainable offer status | Green Premium product
28635 | RSB1A160P7 | Offer Sustainability | REACh Regulation | REACh Declaration
28636 | RSB1A160P7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28637 | RSB1A160P7 | Offer Sustainability | Toxic heavy metal free | Yes
28638 | RSB1A160P7 | Offer Sustainability | Mercury free | Yes
28639 | RSB1A160P7 | Offer Sustainability | RoHS exemption information | Yes
28640 | RSB1A160P7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28641 | RSB1A160P7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28642 | RSB1A160P7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28643 | RSB1A160P7 | Contractual warranty | Warranty | 18 months
28644 | RSB1A160U7 | Main | range of product | Zelio Relay
28645 | RSB1A160U7 | Main | series name | Interface relay
28646 | RSB1A160U7 | Main | product or component type | Plug-in relay
28647 | RSB1A160U7 | Main | device short name | RSB
28648 | RSB1A160U7 | Main | contacts type and composition | 1 C/O
28649 | RSB1A160U7 | Main | contact operation | Standard
28650 | RSB1A160U7 | Main | [Uc] control circuit voltage | 240 V AC
28651 | RSB1A160U7 | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
28652 | RSB1A160U7 | Main | status LED | Without
28653 | RSB1A160U7 | Main | control type | Without push-button
28654 | RSB1A160U7 | Complementary | shape of pin | Flat (PCB type)
28655 | RSB1A160U7 | Complementary | average coil resistance | 33000 Ohm network: AC at 20 °C +/- 10 %
28656 | RSB1A160U7 | Complementary | [Ue] rated operational voltage | 192...360 V AC 50/60 Hz
28657 | RSB1A160U7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28658 | RSB1A160U7 | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
28659 | RSB1A160U7 | Complementary | contacts material | Silver alloy (AgNi)
28660 | RSB1A160U7 | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
28661 | RSB1A160U7 | Complementary | minimum switching current | 10 mA
28662 | RSB1A160U7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28663 | RSB1A160U7 | Complementary | minimum switching voltage | 12 V
28664 | RSB1A160U7 | Complementary | maximum switching capacity | 4000 VA/448 W
28665 | RSB1A160U7 | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
28666 | RSB1A160U7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28667 | RSB1A160U7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28668 | RSB1A160U7 | Complementary | mechanical durability | 10000000 cycles
28669 | RSB1A160U7 | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
28670 | RSB1A160U7 | Complementary | operating time | 20 ms operating 20 ms reset
28671 | RSB1A160U7 | Complementary | average coil consumption | 0.75 VA AC
28672 | RSB1A160U7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
28673 | RSB1A160U7 | Complementary | safety reliability data | B10d = 100000
28674 | RSB1A160U7 | Complementary | protection category | RT I
28675 | RSB1A160U7 | Complementary | test levels | Level A group mounting
28676 | RSB1A160U7 | Complementary | operating position | Any position
28677 | RSB1A160U7 | Complementary | net weight | 0.014 kg
28678 | RSB1A160U7 | Complementary | sale per indivisible quantity | 10
28679 | RSB1A160U7 | Complementary | device presentation | Complete product
28680 | RSB1A160U7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28681 | RSB1A160U7 | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1
28682 | RSB1A160U7 | Environment | product certifications | UL CSA EAC
28683 | RSB1A160U7 | Environment | ambient air temperature for storage | -40…85 °C
28684 | RSB1A160U7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28685 | RSB1A160U7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28686 | RSB1A160U7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28687 | RSB1A160U7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
28688 | RSB1A160U7 | Offer Sustainability | Sustainable offer status | Green Premium product
28689 | RSB1A160U7 | Offer Sustainability | REACh Regulation | REACh Declaration
28690 | RSB1A160U7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28691 | RSB1A160U7 | Offer Sustainability | Toxic heavy metal free | Yes
28692 | RSB1A160U7 | Offer Sustainability | Mercury free | Yes
28693 | RSB1A160U7 | Offer Sustainability | RoHS exemption information | Yes
28694 | RSB1A160U7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28695 | RSB1A160U7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28696 | RSB1A160U7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28697 | RSB1A160U7 | Contractual warranty | Warranty | 18 months
28698 | RSB1A160M7 | Main | range of product | Zelio Relay
28699 | RSB1A160M7 | Main | series name | Interface relay
28700 | RSB1A160M7 | Main | product or component type | Plug-in relay
28701 | RSB1A160M7 | Main | device short name | RSB
28702 | RSB1A160M7 | Main | contacts type and composition | 1 C/O
28703 | RSB1A160M7 | Main | contact operation | Standard
28704 | RSB1A160M7 | Main | [Uc] control circuit voltage | 220 V AC
28705 | RSB1A160M7 | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
28706 | RSB1A160M7 | Main | status LED | Without
28707 | RSB1A160M7 | Main | control type | Without push-button
28708 | RSB1A160M7 | Complementary | shape of pin | Flat (PCB type)
28709 | RSB1A160M7 | Complementary | average coil resistance | 33000 Ohm network: AC at 20 °C +/- 10 %
28710 | RSB1A160M7 | Complementary | [Ue] rated operational voltage | 176...330 V AC 50/60 Hz
28711 | RSB1A160M7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28712 | RSB1A160M7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
28713 | RSB1A160M7 | Complementary | contacts material | Silver alloy (AgNi)
28714 | RSB1A160M7 | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
28715 | RSB1A160M7 | Complementary | minimum switching current | 10 mA
28716 | RSB1A160M7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28717 | RSB1A160M7 | Complementary | minimum switching voltage | 12 V
28718 | RSB1A160M7 | Complementary | maximum switching capacity | 4000 VA/448 W
28719 | RSB1A160M7 | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
28720 | RSB1A160M7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28721 | RSB1A160M7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28722 | RSB1A160M7 | Complementary | mechanical durability | 10000000 cycles
28723 | RSB1A160M7 | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
28724 | RSB1A160M7 | Complementary | operating time | 20 ms operating 20 ms reset
28725 | RSB1A160M7 | Complementary | average coil consumption | 0.75 VA AC
28726 | RSB1A160M7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
28727 | RSB1A160M7 | Complementary | safety reliability data | B10d = 100000
28728 | RSB1A160M7 | Complementary | protection category | RT I
28729 | RSB1A160M7 | Complementary | test levels | Level A group mounting
28730 | RSB1A160M7 | Complementary | operating position | Any position
28731 | RSB1A160M7 | Complementary | net weight | 0.014 kg
28732 | RSB1A160M7 | Complementary | sale per indivisible quantity | 10
28733 | RSB1A160M7 | Complementary | device presentation | Complete product
28734 | RSB1A160M7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28735 | RSB1A160M7 | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
28736 | RSB1A160M7 | Environment | product certifications | EAC UL CSA
28737 | RSB1A160M7 | Environment | ambient air temperature for storage | -40…85 °C
28738 | RSB1A160M7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28739 | RSB1A160M7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28740 | RSB1A160M7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28741 | RSB1A160M7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
28742 | RSB1A160M7 | Offer Sustainability | Sustainable offer status | Green Premium product
28743 | RSB1A160M7 | Offer Sustainability | REACh Regulation | REACh Declaration
28744 | RSB1A160M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28745 | RSB1A160M7 | Offer Sustainability | Toxic heavy metal free | Yes
28746 | RSB1A160M7 | Offer Sustainability | Mercury free | Yes
28747 | RSB1A160M7 | Offer Sustainability | RoHS exemption information | Yes
28748 | RSB1A160M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28749 | RSB1A160M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28750 | RSB1A160M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28751 | RSB1A160M7 | Contractual warranty | Warranty | 18 months
28752 | RSB1A160ND | Main | range of product | Zelio Relay
28753 | RSB1A160ND | Main | series name | Interface relay
28754 | RSB1A160ND | Main | product or component type | Plug-in relay
28755 | RSB1A160ND | Main | device short name | RSB
28756 | RSB1A160ND | Main | contacts type and composition | 1 C/O
28757 | RSB1A160ND | Main | contact operation | Standard
28758 | RSB1A160ND | Main | [Uc] control circuit voltage | 60 V DC
28759 | RSB1A160ND | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
28760 | RSB1A160ND | Main | status LED | Without
28761 | RSB1A160ND | Main | control type | Without push-button
28762 | RSB1A160ND | Complementary | shape of pin | Flat (PCB type)
28763 | RSB1A160ND | Complementary | average coil resistance | 9000 Ohm network: AC at 20 °C +/- 10 %
28764 | RSB1A160ND | Complementary | [Ue] rated operational voltage | 42...90 V DC
28765 | RSB1A160ND | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28766 | RSB1A160ND | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
28767 | RSB1A160ND | Complementary | contacts material | Silver alloy (AgNi)
28768 | RSB1A160ND | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
28769 | RSB1A160ND | Complementary | minimum switching current | 10 mA
28770 | RSB1A160ND | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28771 | RSB1A160ND | Complementary | minimum switching voltage | 12 V
28772 | RSB1A160ND | Complementary | maximum switching capacity | 4000 VA/448 W
28773 | RSB1A160ND | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
28774 | RSB1A160ND | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28775 | RSB1A160ND | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28776 | RSB1A160ND | Complementary | mechanical durability | 30000000 cycles
28777 | RSB1A160ND | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
28778 | RSB1A160ND | Complementary | operating time | 20 ms operating 20 ms reset
28779 | RSB1A160ND | Complementary | marking | CE
28780 | RSB1A160ND | Complementary | average coil consumption | 0.45 W DC
28781 | RSB1A160ND | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
28782 | RSB1A160ND | Complementary | safety reliability data | B10d = 100000
28783 | RSB1A160ND | Complementary | protection category | RT I
28784 | RSB1A160ND | Complementary | test levels | Level A group mounting
28785 | RSB1A160ND | Complementary | operating position | Any position
28786 | RSB1A160ND | Complementary | net weight | 0.014 kg
28787 | RSB1A160ND | Complementary | sale per indivisible quantity | 10
28788 | RSB1A160ND | Complementary | device presentation | Complete product
28789 | RSB1A160ND | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28790 | RSB1A160ND | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
28791 | RSB1A160ND | Environment | product certifications | UL CSA EAC
28792 | RSB1A160ND | Environment | ambient air temperature for storage | -40…85 °C
28793 | RSB1A160ND | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28794 | RSB1A160ND | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28795 | RSB1A160ND | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28796 | RSB1A160ND | Environment | ambient air temperature for operation | -40…85 °C (DC)
28797 | RSB1A160ND | Offer Sustainability | Sustainable offer status | Green Premium product
28798 | RSB1A160ND | Offer Sustainability | REACh Regulation | REACh Declaration
28799 | RSB1A160ND | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28800 | RSB1A160ND | Offer Sustainability | Toxic heavy metal free | Yes
28801 | RSB1A160ND | Offer Sustainability | Mercury free | Yes
28802 | RSB1A160ND | Offer Sustainability | RoHS exemption information | Yes
28803 | RSB1A160ND | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28804 | RSB1A160ND | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28805 | RSB1A160ND | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28806 | RSB1A160ND | Contractual warranty | Warranty | 18 months
28807 | RSB1A160RD | Main | range of product | Zelio Relay
28808 | RSB1A160RD | Main | series name | Interface relay
28809 | RSB1A160RD | Main | product or component type | Plug-in relay
28810 | RSB1A160RD | Main | device short name | RSB
28811 | RSB1A160RD | Main | contacts type and composition | 1 C/O
28812 | RSB1A160RD | Main | contact operation | Standard
28813 | RSB1A160RD | Main | [Uc] control circuit voltage | 6 V DC
28814 | RSB1A160RD | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
28815 | RSB1A160RD | Main | status LED | Without
28816 | RSB1A160RD | Main | control type | Without push-button
28817 | RSB1A160RD | Complementary | shape of pin | Flat (PCB type)
28818 | RSB1A160RD | Complementary | average coil resistance | 90 Ohm network: AC at 20 °C +/- 10 %
28819 | RSB1A160RD | Complementary | [Ue] rated operational voltage | 4.2...9 V DC
28820 | RSB1A160RD | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28821 | RSB1A160RD | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
28822 | RSB1A160RD | Complementary | contacts material | Silver alloy (AgNi)
28823 | RSB1A160RD | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
28824 | RSB1A160RD | Complementary | minimum switching current | 10 mA
28825 | RSB1A160RD | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28826 | RSB1A160RD | Complementary | minimum switching voltage | 12 V
28827 | RSB1A160RD | Complementary | maximum switching capacity | 4000 VA/448 W
28828 | RSB1A160RD | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
28829 | RSB1A160RD | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28830 | RSB1A160RD | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28831 | RSB1A160RD | Complementary | mechanical durability | 30000000 cycles
28832 | RSB1A160RD | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
28833 | RSB1A160RD | Complementary | operating time | 20 ms operating 20 ms reset
28834 | RSB1A160RD | Complementary | average coil consumption | 0.45 W DC
28835 | RSB1A160RD | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
28836 | RSB1A160RD | Complementary | safety reliability data | B10d = 100000
28837 | RSB1A160RD | Complementary | protection category | RT I
28838 | RSB1A160RD | Complementary | test levels | Level A group mounting
28839 | RSB1A160RD | Complementary | operating position | Any position
28840 | RSB1A160RD | Complementary | net weight | 0.014 kg
28841 | RSB1A160RD | Complementary | sale per indivisible quantity | 10
28842 | RSB1A160RD | Complementary | device presentation | Complete product
28843 | RSB1A160RD | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28844 | RSB1A160RD | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1
28845 | RSB1A160RD | Environment | product certifications | CSA EAC UL
28846 | RSB1A160RD | Environment | ambient air temperature for storage | -40…85 °C
28847 | RSB1A160RD | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28848 | RSB1A160RD | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28849 | RSB1A160RD | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28850 | RSB1A160RD | Environment | ambient air temperature for operation | -40…85 °C (DC)
28851 | RSB1A160RD | Offer Sustainability | Sustainable offer status | Green Premium product
28852 | RSB1A160RD | Offer Sustainability | REACh Regulation | REACh Declaration
28853 | RSB1A160RD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28854 | RSB1A160RD | Offer Sustainability | Toxic heavy metal free | Yes
28855 | RSB1A160RD | Offer Sustainability | Mercury free | Yes
28856 | RSB1A160RD | Offer Sustainability | RoHS exemption information | Yes
28857 | RSB1A160RD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28858 | RSB1A160RD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28859 | RSB1A160RD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28860 | RSB1A160RD | Contractual warranty | Warranty | 18 months
28861 | RSB2A080B7 | Main | range of product | Zelio Relay
28862 | RSB2A080B7 | Main | series name | Interface relay
28863 | RSB2A080B7 | Main | product or component type | Plug-in relay
28864 | RSB2A080B7 | Main | device short name | RSB
28865 | RSB2A080B7 | Main | contacts type and composition | 2 C/O
28866 | RSB2A080B7 | Main | contact operation | Standard
28867 | RSB2A080B7 | Main | [Uc] control circuit voltage | 24 V AC
28868 | RSB2A080B7 | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
28869 | RSB2A080B7 | Main | status LED | Without
28870 | RSB2A080B7 | Main | control type | Without push-button
28871 | RSB2A080B7 | Complementary | shape of pin | Flat (PCB type)
28872 | RSB2A080B7 | Complementary | average coil resistance | 368 Ohm network: AC at 20 °C +/- 10 %
28873 | RSB2A080B7 | Complementary | [Ue] rated operational voltage | 19.2...36 V AC 50/60 Hz
28874 | RSB2A080B7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28875 | RSB2A080B7 | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
28876 | RSB2A080B7 | Complementary | contacts material | Silver alloy (AgNi)
28877 | RSB2A080B7 | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
28878 | RSB2A080B7 | Complementary | minimum switching current | 10 mA
28879 | RSB2A080B7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28880 | RSB2A080B7 | Complementary | minimum switching voltage | 12 V
28881 | RSB2A080B7 | Complementary | maximum switching capacity | 2000 VA/224 W
28882 | RSB2A080B7 | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
28883 | RSB2A080B7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28884 | RSB2A080B7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28885 | RSB2A080B7 | Complementary | mechanical durability | 5000000 cycles
28886 | RSB2A080B7 | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
28887 | RSB2A080B7 | Complementary | operating time | 20 ms operating 20 ms reset
28888 | RSB2A080B7 | Complementary | average coil consumption | 0.75 VA AC
28889 | RSB2A080B7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
28890 | RSB2A080B7 | Complementary | safety reliability data | B10d = 100000
28891 | RSB2A080B7 | Complementary | protection category | RT I
28892 | RSB2A080B7 | Complementary | test levels | Level A group mounting
28893 | RSB2A080B7 | Complementary | operating position | Any position
28894 | RSB2A080B7 | Complementary | net weight | 0.014 kg
28895 | RSB2A080B7 | Complementary | sale per indivisible quantity | 10
28896 | RSB2A080B7 | Complementary | device presentation | Complete product
28897 | RSB2A080B7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28898 | RSB2A080B7 | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
28899 | RSB2A080B7 | Environment | product certifications | UL CSA EAC
28900 | RSB2A080B7 | Environment | ambient air temperature for storage | -40…85 °C
28901 | RSB2A080B7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28902 | RSB2A080B7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28903 | RSB2A080B7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28904 | RSB2A080B7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
28905 | RSB2A080B7 | Offer Sustainability | Sustainable offer status | Green Premium product
28906 | RSB2A080B7 | Offer Sustainability | REACh Regulation | REACh Declaration
28907 | RSB2A080B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28908 | RSB2A080B7 | Offer Sustainability | Toxic heavy metal free | Yes
28909 | RSB2A080B7 | Offer Sustainability | Mercury free | Yes
28910 | RSB2A080B7 | Offer Sustainability | RoHS exemption information | Yes
28911 | RSB2A080B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28912 | RSB2A080B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28913 | RSB2A080B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28914 | RSB2A080B7 | Contractual warranty | Warranty | 18 months
28915 | RSB2A080BD | Main | range of product | Zelio Relay
28916 | RSB2A080BD | Main | series name | Interface relay
28917 | RSB2A080BD | Main | product or component type | Plug-in relay
28918 | RSB2A080BD | Main | device short name | RSB
28919 | RSB2A080BD | Main | contacts type and composition | 2 C/O
28920 | RSB2A080BD | Main | contact operation | Standard
28921 | RSB2A080BD | Main | [Uc] control circuit voltage | 24 V DC
28922 | RSB2A080BD | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
28923 | RSB2A080BD | Main | status LED | Without
28924 | RSB2A080BD | Main | control type | Without push-button
28925 | RSB2A080BD | Complementary | shape of pin | Flat (PCB type)
28926 | RSB2A080BD | Complementary | average coil resistance | 1440 Ohm network: DC at 20 °C +/- 10 %
28927 | RSB2A080BD | Complementary | [Ue] rated operational voltage | 16.8...36 V DC
28928 | RSB2A080BD | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28929 | RSB2A080BD | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
28930 | RSB2A080BD | Complementary | contacts material | Silver alloy (AgNi)
28931 | RSB2A080BD | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
28932 | RSB2A080BD | Complementary | minimum switching current | 10 mA
28933 | RSB2A080BD | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28934 | RSB2A080BD | Complementary | minimum switching voltage | 12 V
28935 | RSB2A080BD | Complementary | maximum switching capacity | 2000 VA/224 W
28936 | RSB2A080BD | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
28937 | RSB2A080BD | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28938 | RSB2A080BD | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28939 | RSB2A080BD | Complementary | mechanical durability | 30000000 cycles
28940 | RSB2A080BD | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
28941 | RSB2A080BD | Complementary | operating time | 20 ms operating 20 ms reset
28942 | RSB2A080BD | Complementary | marking | CE
28943 | RSB2A080BD | Complementary | average coil consumption | 0.45 W DC
28944 | RSB2A080BD | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
28945 | RSB2A080BD | Complementary | safety reliability data | B10d = 100000
28946 | RSB2A080BD | Complementary | protection category | RT I
28947 | RSB2A080BD | Complementary | test levels | Level A group mounting
28948 | RSB2A080BD | Complementary | operating position | Any position
28949 | RSB2A080BD | Complementary | net weight | 0.014 kg
28950 | RSB2A080BD | Complementary | sale per indivisible quantity | 10
28951 | RSB2A080BD | Complementary | device presentation | Complete product
28952 | RSB2A080BD | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
28953 | RSB2A080BD | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1
28954 | RSB2A080BD | Environment | product certifications | UL CSA EAC
28955 | RSB2A080BD | Environment | ambient air temperature for storage | -40…85 °C
28956 | RSB2A080BD | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
28957 | RSB2A080BD | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
28958 | RSB2A080BD | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
28959 | RSB2A080BD | Environment | ambient air temperature for operation | -40…85 °C (DC)
28960 | RSB2A080BD | Offer Sustainability | Sustainable offer status | Green Premium product
28961 | RSB2A080BD | Offer Sustainability | REACh Regulation | REACh Declaration
28962 | RSB2A080BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
28963 | RSB2A080BD | Offer Sustainability | Toxic heavy metal free | Yes
28964 | RSB2A080BD | Offer Sustainability | Mercury free | Yes
28965 | RSB2A080BD | Offer Sustainability | RoHS exemption information | Yes
28966 | RSB2A080BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
28967 | RSB2A080BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
28968 | RSB2A080BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
28969 | RSB2A080BD | Contractual warranty | Warranty | 18 months
28970 | RSB2A080E7 | Main | range of product | Zelio Relay
28971 | RSB2A080E7 | Main | series name | Interface relay
28972 | RSB2A080E7 | Main | product or component type | Plug-in relay
28973 | RSB2A080E7 | Main | device short name | RSB
28974 | RSB2A080E7 | Main | contacts type and composition | 2 C/O
28975 | RSB2A080E7 | Main | contact operation | Standard
28976 | RSB2A080E7 | Main | [Uc] control circuit voltage | 48 V AC
28977 | RSB2A080E7 | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
28978 | RSB2A080E7 | Main | status LED | Without
28979 | RSB2A080E7 | Main | control type | Without push-button
28980 | RSB2A080E7 | Complementary | shape of pin | Flat (PCB type)
28981 | RSB2A080E7 | Complementary | average coil resistance | 1540 Ohm network: AC at 20 °C +/- 10 %
28982 | RSB2A080E7 | Complementary | [Ue] rated operational voltage | 38.4...72 V AC 50/60 Hz
28983 | RSB2A080E7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
28984 | RSB2A080E7 | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
28985 | RSB2A080E7 | Complementary | contacts material | Silver alloy (AgNi)
28986 | RSB2A080E7 | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
28987 | RSB2A080E7 | Complementary | minimum switching current | 10 mA
28988 | RSB2A080E7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
28989 | RSB2A080E7 | Complementary | minimum switching voltage | 12 V
28990 | RSB2A080E7 | Complementary | maximum switching capacity | 2000 VA/224 W
28991 | RSB2A080E7 | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
28992 | RSB2A080E7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
28993 | RSB2A080E7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
28994 | RSB2A080E7 | Complementary | mechanical durability | 5000000 cycles
28995 | RSB2A080E7 | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
28996 | RSB2A080E7 | Complementary | operating time | 20 ms operating 20 ms reset
28997 | RSB2A080E7 | Complementary | marking | CE
28998 | RSB2A080E7 | Complementary | average coil consumption | 0.75 VA AC
28999 | RSB2A080E7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
29000 | RSB2A080E7 | Complementary | safety reliability data | B10d = 100000
29001 | RSB2A080E7 | Complementary | protection category | RT I
29002 | RSB2A080E7 | Complementary | test levels | Level A group mounting
29003 | RSB2A080E7 | Complementary | operating position | Any position
29004 | RSB2A080E7 | Complementary | net weight | 0.014 kg
29005 | RSB2A080E7 | Complementary | sale per indivisible quantity | 10
29006 | RSB2A080E7 | Complementary | device presentation | Complete product
29007 | RSB2A080E7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
29008 | RSB2A080E7 | Environment | standards | UL 508 EN/IEC 61810-1 CSA C22.2 No 14
29009 | RSB2A080E7 | Environment | product certifications | UL CSA EAC
29010 | RSB2A080E7 | Environment | ambient air temperature for storage | -40…85 °C
29011 | RSB2A080E7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
29012 | RSB2A080E7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29013 | RSB2A080E7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
29014 | RSB2A080E7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
29015 | RSB2A080E7 | Offer Sustainability | Sustainable offer status | Green Premium product
29016 | RSB2A080E7 | Offer Sustainability | REACh Regulation | REACh Declaration
29017 | RSB2A080E7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29018 | RSB2A080E7 | Offer Sustainability | Toxic heavy metal free | Yes
29019 | RSB2A080E7 | Offer Sustainability | Mercury free | Yes
29020 | RSB2A080E7 | Offer Sustainability | RoHS exemption information | Yes
29021 | RSB2A080E7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29022 | RSB2A080E7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29023 | RSB2A080E7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29024 | RSB2A080E7 | Contractual warranty | Warranty | 18 months
29025 | RSB2A080ED | Main | range of product | Zelio Relay
29026 | RSB2A080ED | Main | series name | Interface relay
29027 | RSB2A080ED | Main | product or component type | Plug-in relay
29028 | RSB2A080ED | Main | device short name | RSB
29029 | RSB2A080ED | Main | contacts type and composition | 2 C/O
29030 | RSB2A080ED | Main | contact operation | Standard
29031 | RSB2A080ED | Main | [Uc] control circuit voltage | 48 V DC
29032 | RSB2A080ED | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
29033 | RSB2A080ED | Main | status LED | Without
29034 | RSB2A080ED | Main | control type | Without push-button
29035 | RSB2A080ED | Complementary | shape of pin | Flat (PCB type)
29036 | RSB2A080ED | Complementary | average coil resistance | 5520 Ohm network: AC at 20 °C +/- 10 %
29037 | RSB2A080ED | Complementary | [Ue] rated operational voltage | 33.6...72 V DC
29038 | RSB2A080ED | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
29039 | RSB2A080ED | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
29040 | RSB2A080ED | Complementary | contacts material | Silver alloy (AgNi)
29041 | RSB2A080ED | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
29042 | RSB2A080ED | Complementary | minimum switching current | 10 mA
29043 | RSB2A080ED | Complementary | maximum switching voltage | 250 V DC conforming to IEC
29044 | RSB2A080ED | Complementary | minimum switching voltage | 12 V
29045 | RSB2A080ED | Complementary | maximum switching capacity | 2000 VA/224 W
29046 | RSB2A080ED | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
29047 | RSB2A080ED | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
29048 | RSB2A080ED | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
29049 | RSB2A080ED | Complementary | mechanical durability | 30000000 cycles
29050 | RSB2A080ED | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
29051 | RSB2A080ED | Complementary | operating time | 20 ms operating 20 ms reset
29052 | RSB2A080ED | Complementary | marking | CE
29053 | RSB2A080ED | Complementary | average coil consumption | 0.45 W DC
29054 | RSB2A080ED | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
29055 | RSB2A080ED | Complementary | safety reliability data | B10d = 100000
29056 | RSB2A080ED | Complementary | protection category | RT I
29057 | RSB2A080ED | Complementary | test levels | Level A group mounting
29058 | RSB2A080ED | Complementary | operating position | Any position
29059 | RSB2A080ED | Complementary | net weight | 0.014 kg
29060 | RSB2A080ED | Complementary | sale per indivisible quantity | 10
29061 | RSB2A080ED | Complementary | device presentation | Complete product
29062 | RSB2A080ED | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
29063 | RSB2A080ED | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
29064 | RSB2A080ED | Environment | product certifications | EAC CSA UL
29065 | RSB2A080ED | Environment | ambient air temperature for storage | -40…85 °C
29066 | RSB2A080ED | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
29067 | RSB2A080ED | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29068 | RSB2A080ED | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
29069 | RSB2A080ED | Environment | ambient air temperature for operation | -40…85 °C (DC)
29070 | RSB2A080ED | Offer Sustainability | Sustainable offer status | Green Premium product
29071 | RSB2A080ED | Offer Sustainability | REACh Regulation | REACh Declaration
29072 | RSB2A080ED | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29073 | RSB2A080ED | Offer Sustainability | Toxic heavy metal free | Yes
29074 | RSB2A080ED | Offer Sustainability | Mercury free | Yes
29075 | RSB2A080ED | Offer Sustainability | RoHS exemption information | Yes
29076 | RSB2A080ED | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29077 | RSB2A080ED | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29078 | RSB2A080ED | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29079 | RSB2A080ED | Contractual warranty | Warranty | 18 months
29080 | RSB2A080F7 | Main | range of product | Zelio Relay
29081 | RSB2A080F7 | Main | series name | Interface relay
29082 | RSB2A080F7 | Main | product or component type | Plug-in relay
29083 | RSB2A080F7 | Main | device short name | RSB
29084 | RSB2A080F7 | Main | contacts type and composition | 2 C/O
29085 | RSB2A080F7 | Main | contact operation | Standard
29086 | RSB2A080F7 | Main | [Uc] control circuit voltage | 120 V AC
29087 | RSB2A080F7 | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
29088 | RSB2A080F7 | Main | status LED | Without
29089 | RSB2A080F7 | Main | control type | Without push-button
29090 | RSB2A080F7 | Complementary | shape of pin | Flat (PCB type)
29091 | RSB2A080F7 | Complementary | average coil resistance | 8360 Ohm network: AC at 20 °C +/- 10 %
29092 | RSB2A080F7 | Complementary | [Ue] rated operational voltage | 96...180 V AC 50/60 Hz
29093 | RSB2A080F7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
29094 | RSB2A080F7 | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
29095 | RSB2A080F7 | Complementary | contacts material | Silver alloy (AgNi)
29096 | RSB2A080F7 | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
29097 | RSB2A080F7 | Complementary | minimum switching current | 10 mA
29098 | RSB2A080F7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
29099 | RSB2A080F7 | Complementary | minimum switching voltage | 12 V
29100 | RSB2A080F7 | Complementary | maximum switching capacity | 2000 VA/224 W
29101 | RSB2A080F7 | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
29102 | RSB2A080F7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
29103 | RSB2A080F7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
29104 | RSB2A080F7 | Complementary | mechanical durability | 5000000 cycles
29105 | RSB2A080F7 | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
29106 | RSB2A080F7 | Complementary | operating time | 20 ms operating 20 ms reset
29107 | RSB2A080F7 | Complementary | marking | CE
29108 | RSB2A080F7 | Complementary | average coil consumption | 0.75 VA AC
29109 | RSB2A080F7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
29110 | RSB2A080F7 | Complementary | safety reliability data | B10d = 100000
29111 | RSB2A080F7 | Complementary | protection category | RT I
29112 | RSB2A080F7 | Complementary | test levels | Level A group mounting
29113 | RSB2A080F7 | Complementary | operating position | Any position
29114 | RSB2A080F7 | Complementary | net weight | 0.014 kg
29115 | RSB2A080F7 | Complementary | sale per indivisible quantity | 10
29116 | RSB2A080F7 | Complementary | device presentation | Complete product
29117 | RSB2A080F7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
29118 | RSB2A080F7 | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1
29119 | RSB2A080F7 | Environment | product certifications | EAC CSA UL
29120 | RSB2A080F7 | Environment | ambient air temperature for storage | -40…85 °C
29121 | RSB2A080F7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
29122 | RSB2A080F7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29123 | RSB2A080F7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
29124 | RSB2A080F7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
29125 | RSB2A080F7 | Offer Sustainability | Sustainable offer status | Green Premium product
29126 | RSB2A080F7 | Offer Sustainability | REACh Regulation | REACh Declaration
29127 | RSB2A080F7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29128 | RSB2A080F7 | Offer Sustainability | Toxic heavy metal free | Yes
29129 | RSB2A080F7 | Offer Sustainability | Mercury free | Yes
29130 | RSB2A080F7 | Offer Sustainability | RoHS exemption information | Yes
29131 | RSB2A080F7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29132 | RSB2A080F7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29133 | RSB2A080F7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29134 | RSB2A080F7 | Contractual warranty | Warranty | 18 months
29135 | RSB2A080FD | Main | range of product | Zelio Relay
29136 | RSB2A080FD | Main | series name | Interface relay
29137 | RSB2A080FD | Main | product or component type | Plug-in relay
29138 | RSB2A080FD | Main | device short name | RSB
29139 | RSB2A080FD | Main | contacts type and composition | 2 C/O
29140 | RSB2A080FD | Main | contact operation | Standard
29141 | RSB2A080FD | Main | [Uc] control circuit voltage | 110 V DC
29142 | RSB2A080FD | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
29143 | RSB2A080FD | Main | status LED | Without
29144 | RSB2A080FD | Main | control type | Without push-button
29145 | RSB2A080FD | Complementary | shape of pin | Flat (PCB type)
29146 | RSB2A080FD | Complementary | average coil resistance | 30250 Ohm network: AC at 20 °C +/- 10 %
29147 | RSB2A080FD | Complementary | [Ue] rated operational voltage | 77...165 V DC
29148 | RSB2A080FD | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
29149 | RSB2A080FD | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
29150 | RSB2A080FD | Complementary | contacts material | Silver alloy (AgNi)
29151 | RSB2A080FD | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
29152 | RSB2A080FD | Complementary | minimum switching current | 10 mA
29153 | RSB2A080FD | Complementary | maximum switching voltage | 250 V DC conforming to IEC
29154 | RSB2A080FD | Complementary | minimum switching voltage | 12 V
29155 | RSB2A080FD | Complementary | maximum switching capacity | 2000 VA/224 W
29156 | RSB2A080FD | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
29157 | RSB2A080FD | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
29158 | RSB2A080FD | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
29159 | RSB2A080FD | Complementary | mechanical durability | 30000000 cycles
29160 | RSB2A080FD | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
29161 | RSB2A080FD | Complementary | operating time | 20 ms operating 20 ms reset
29162 | RSB2A080FD | Complementary | marking | CE
29163 | RSB2A080FD | Complementary | average coil consumption | 0.45 W DC
29164 | RSB2A080FD | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
29165 | RSB2A080FD | Complementary | safety reliability data | B10d = 100000
29166 | RSB2A080FD | Complementary | protection category | RT I
29167 | RSB2A080FD | Complementary | test levels | Level A group mounting
29168 | RSB2A080FD | Complementary | operating position | Any position
29169 | RSB2A080FD | Complementary | net weight | 0.014 kg
29170 | RSB2A080FD | Complementary | sale per indivisible quantity | 10
29171 | RSB2A080FD | Complementary | device presentation | Complete product
29172 | RSB2A080FD | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
29173 | RSB2A080FD | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508
29174 | RSB2A080FD | Environment | product certifications | UL CSA EAC
29175 | RSB2A080FD | Environment | ambient air temperature for storage | -40…85 °C
29176 | RSB2A080FD | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
29177 | RSB2A080FD | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29178 | RSB2A080FD | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
29179 | RSB2A080FD | Environment | ambient air temperature for operation | -40…85 °C (DC)
29180 | RSB2A080FD | Offer Sustainability | Sustainable offer status | Green Premium product
29181 | RSB2A080FD | Offer Sustainability | REACh Regulation | REACh Declaration
29182 | RSB2A080FD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29183 | RSB2A080FD | Offer Sustainability | Toxic heavy metal free | Yes
29184 | RSB2A080FD | Offer Sustainability | Mercury free | Yes
29185 | RSB2A080FD | Offer Sustainability | RoHS exemption information | Yes
29186 | RSB2A080FD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29187 | RSB2A080FD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29188 | RSB2A080FD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29189 | RSB2A080FD | Contractual warranty | Warranty | 18 months
29190 | RSB2A080JD | Main | range of product | Zelio Relay
29191 | RSB2A080JD | Main | series name | Interface relay
29192 | RSB2A080JD | Main | product or component type | Plug-in relay
29193 | RSB2A080JD | Main | device short name | RSB
29194 | RSB2A080JD | Main | contacts type and composition | 2 C/O
29195 | RSB2A080JD | Main | contact operation | Standard
29196 | RSB2A080JD | Main | [Uc] control circuit voltage | 12 V DC
29197 | RSB2A080JD | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
29198 | RSB2A080JD | Main | status LED | Without
29199 | RSB2A080JD | Main | control type | Without push-button
29200 | RSB2A080JD | Complementary | shape of pin | Flat (PCB type)
29201 | RSB2A080JD | Complementary | average coil resistance | 360 Ohm network: AC at 20 °C +/- 10 %
29202 | RSB2A080JD | Complementary | [Ue] rated operational voltage | 8.4...18 V DC
29203 | RSB2A080JD | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
29204 | RSB2A080JD | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
29205 | RSB2A080JD | Complementary | contacts material | Silver alloy (AgNi)
29206 | RSB2A080JD | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
29207 | RSB2A080JD | Complementary | minimum switching current | 10 mA
29208 | RSB2A080JD | Complementary | maximum switching voltage | 250 V DC conforming to IEC
29209 | RSB2A080JD | Complementary | minimum switching voltage | 12 V
29210 | RSB2A080JD | Complementary | maximum switching capacity | 2000 VA/224 W
29211 | RSB2A080JD | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
29212 | RSB2A080JD | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
29213 | RSB2A080JD | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
29214 | RSB2A080JD | Complementary | mechanical durability | 30000000 cycles
29215 | RSB2A080JD | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
29216 | RSB2A080JD | Complementary | operating time | 20 ms operating 20 ms reset
29217 | RSB2A080JD | Complementary | marking | CE
29218 | RSB2A080JD | Complementary | average coil consumption | 0.45 W DC
29219 | RSB2A080JD | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
29220 | RSB2A080JD | Complementary | safety reliability data | B10d = 100000
29221 | RSB2A080JD | Complementary | protection category | RT I
29222 | RSB2A080JD | Complementary | test levels | Level A group mounting
29223 | RSB2A080JD | Complementary | operating position | Any position
29224 | RSB2A080JD | Complementary | net weight | 0.014 kg
29225 | RSB2A080JD | Complementary | sale per indivisible quantity | 10
29226 | RSB2A080JD | Complementary | device presentation | Complete product
29227 | RSB2A080JD | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
29228 | RSB2A080JD | Environment | standards | UL 508 EN/IEC 61810-1 CSA C22.2 No 14
29229 | RSB2A080JD | Environment | product certifications | CSA EAC UL
29230 | RSB2A080JD | Environment | ambient air temperature for storage | -40…85 °C
29231 | RSB2A080JD | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
29232 | RSB2A080JD | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29233 | RSB2A080JD | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
29234 | RSB2A080JD | Environment | ambient air temperature for operation | -40…85 °C (DC)
29235 | RSB2A080JD | Offer Sustainability | Sustainable offer status | Green Premium product
29236 | RSB2A080JD | Offer Sustainability | REACh Regulation | REACh Declaration
29237 | RSB2A080JD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29238 | RSB2A080JD | Offer Sustainability | Toxic heavy metal free | Yes
29239 | RSB2A080JD | Offer Sustainability | Mercury free | Yes
29240 | RSB2A080JD | Offer Sustainability | RoHS exemption information | Yes
29241 | RSB2A080JD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29242 | RSB2A080JD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29243 | RSB2A080JD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29244 | RSB2A080JD | Contractual warranty | Warranty | 18 months
29245 | RSB2A080ND | Main | range of product | Harmony Relay
29246 | RSB2A080ND | Main | series name | Interface relay
29247 | RSB2A080ND | Main | product or component type | Plug-in relay
29248 | RSB2A080ND | Main | device short name | RSB
29249 | RSB2A080ND | Main | contacts type and composition | 2 C/O
29250 | RSB2A080ND | Main | contact operation | Standard
29251 | RSB2A080ND | Main | [Uc] control circuit voltage | 60 V DC
29252 | RSB2A080ND | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
29253 | RSB2A080ND | Main | status LED | Without
29254 | RSB2A080ND | Main | control type | Without push-button
29255 | RSB2A080ND | Complementary | shape of pin | Flat (PCB type)
29256 | RSB2A080ND | Complementary | average coil resistance | 9000 Ohm network: AC at 20 °C +/- 10 %
29257 | RSB2A080ND | Complementary | [Ue] rated operational voltage | 42...90 V DC
29258 | RSB2A080ND | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
29259 | RSB2A080ND | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
29260 | RSB2A080ND | Complementary | contacts material | Silver alloy (AgNi)
29261 | RSB2A080ND | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
29262 | RSB2A080ND | Complementary | minimum switching current | 10 mA
29263 | RSB2A080ND | Complementary | maximum switching voltage | 250 V DC conforming to IEC
29264 | RSB2A080ND | Complementary | minimum switching voltage | 12 V
29265 | RSB2A080ND | Complementary | maximum switching capacity | 2000 VA/224 W
29266 | RSB2A080ND | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
29267 | RSB2A080ND | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
29268 | RSB2A080ND | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
29269 | RSB2A080ND | Complementary | mechanical durability | 30000000 cycles
29270 | RSB2A080ND | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
29271 | RSB2A080ND | Complementary | operating time | 20 ms operating 20 ms reset
29272 | RSB2A080ND | Complementary | marking | CE
29273 | RSB2A080ND | Complementary | average coil consumption | 0.45 W DC
29274 | RSB2A080ND | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
29275 | RSB2A080ND | Complementary | safety reliability data | B10d = 100000
29276 | RSB2A080ND | Complementary | protection category | RT I
29277 | RSB2A080ND | Complementary | test levels | Level A group mounting
29278 | RSB2A080ND | Complementary | operating position | Any position
29279 | RSB2A080ND | Complementary | net weight | 0.014 kg
29280 | RSB2A080ND | Complementary | sale per indivisible quantity | 10
29281 | RSB2A080ND | Complementary | device presentation | Complete product
29282 | RSB2A080ND | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
29283 | RSB2A080ND | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508
29284 | RSB2A080ND | Environment | product certifications | UL CSA EAC
29285 | RSB2A080ND | Environment | ambient air temperature for storage | -40…85 °C
29286 | RSB2A080ND | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
29287 | RSB2A080ND | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29288 | RSB2A080ND | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
29289 | RSB2A080ND | Environment | ambient air temperature for operation | -40…85 °C (DC)
29290 | RSB2A080ND | Offer Sustainability | Sustainable offer status | Green Premium product
29291 | RSB2A080ND | Offer Sustainability | REACh Regulation | REACh Declaration
29292 | RSB2A080ND | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29293 | RSB2A080ND | Offer Sustainability | Toxic heavy metal free | Yes
29294 | RSB2A080ND | Offer Sustainability | Mercury free | Yes
29295 | RSB2A080ND | Offer Sustainability | RoHS exemption information | Yes
29296 | RSB2A080ND | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29297 | RSB2A080ND | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29298 | RSB2A080ND | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29299 | RSB2A080ND | Contractual warranty | Warranty | 18 months
29300 | RSB2A080P7 | Main | range of product | Zelio Relay
29301 | RSB2A080P7 | Main | series name | Interface relay
29302 | RSB2A080P7 | Main | product or component type | Plug-in relay
29303 | RSB2A080P7 | Main | device short name | RSB
29304 | RSB2A080P7 | Main | contacts type and composition | 2 C/O
29305 | RSB2A080P7 | Main | contact operation | Standard
29306 | RSB2A080P7 | Main | [Uc] control circuit voltage | 230 V AC
29307 | RSB2A080P7 | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
29308 | RSB2A080P7 | Main | status LED | Without
29309 | RSB2A080P7 | Main | control type | Without push-button
29310 | RSB2A080P7 | Complementary | shape of pin | Flat (PCB type)
29311 | RSB2A080P7 | Complementary | average coil resistance | 33000 Ohm network: AC at 20 °C +/- 10 %
29312 | RSB2A080P7 | Complementary | [Ue] rated operational voltage | 184...345 V AC 50/60 Hz
29313 | RSB2A080P7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
29314 | RSB2A080P7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
29315 | RSB2A080P7 | Complementary | contacts material | Silver alloy (AgNi)
29316 | RSB2A080P7 | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
29317 | RSB2A080P7 | Complementary | minimum switching current | 10 mA
29318 | RSB2A080P7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
29319 | RSB2A080P7 | Complementary | minimum switching voltage | 12 V
29320 | RSB2A080P7 | Complementary | maximum switching capacity | 2000 VA/224 W
29321 | RSB2A080P7 | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
29322 | RSB2A080P7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
29323 | RSB2A080P7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
29324 | RSB2A080P7 | Complementary | mechanical durability | 5000000 cycles
29325 | RSB2A080P7 | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
29326 | RSB2A080P7 | Complementary | operating time | 20 ms operating 20 ms reset
29327 | RSB2A080P7 | Complementary | average coil consumption | 0.75 VA AC
29328 | RSB2A080P7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
29329 | RSB2A080P7 | Complementary | safety reliability data | B10d = 100000
29330 | RSB2A080P7 | Complementary | protection category | RT I
29331 | RSB2A080P7 | Complementary | test levels | Level A group mounting
29332 | RSB2A080P7 | Complementary | operating position | Any position
29333 | RSB2A080P7 | Complementary | net weight | 0.014 kg
29334 | RSB2A080P7 | Complementary | sale per indivisible quantity | 10
29335 | RSB2A080P7 | Complementary | device presentation | Complete product
29336 | RSB2A080P7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
29337 | RSB2A080P7 | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
29338 | RSB2A080P7 | Environment | product certifications | CSA EAC UL
29339 | RSB2A080P7 | Environment | ambient air temperature for storage | -40…85 °C
29340 | RSB2A080P7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
29341 | RSB2A080P7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29342 | RSB2A080P7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
29343 | RSB2A080P7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
29344 | RSB2A080P7 | Offer Sustainability | Sustainable offer status | Green Premium product
29345 | RSB2A080P7 | Offer Sustainability | REACh Regulation | REACh Declaration
29346 | RSB2A080P7 | Offer Sustainability | REACh free of SVHC | Yes
29347 | RSB2A080P7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29348 | RSB2A080P7 | Offer Sustainability | Toxic heavy metal free | Yes
29349 | RSB2A080P7 | Offer Sustainability | Mercury free | Yes
29350 | RSB2A080P7 | Offer Sustainability | RoHS exemption information | Yes
29351 | RSB2A080P7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29352 | RSB2A080P7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29353 | RSB2A080P7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29354 | RSB2A080P7 | Contractual warranty | Warranty | 18 months
29355 | RSB2A080RD | Main | range of product | Harmony Relay
29356 | RSB2A080RD | Main | series name | Interface relay
29357 | RSB2A080RD | Main | product or component type | Plug-in relay
29358 | RSB2A080RD | Main | device short name | RSB
29359 | RSB2A080RD | Main | contacts type and composition | 2 C/O
29360 | RSB2A080RD | Main | contact operation | Standard
29361 | RSB2A080RD | Main | [Uc] control circuit voltage | 6 V DC
29362 | RSB2A080RD | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
29363 | RSB2A080RD | Main | status LED | Without
29364 | RSB2A080RD | Main | control type | Without push-button
29365 | RSB2A080RD | Complementary | shape of pin | Flat (PCB type)
29366 | RSB2A080RD | Complementary | average coil resistance | 90 Ohm network: AC at 20 °C +/- 10 %
29367 | RSB2A080RD | Complementary | [Ue] rated operational voltage | 4.2...9 V DC
29368 | RSB2A080RD | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
29369 | RSB2A080RD | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
29370 | RSB2A080RD | Complementary | contacts material | Silver alloy (AgNi)
29371 | RSB2A080RD | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
29372 | RSB2A080RD | Complementary | minimum switching current | 10 mA
29373 | RSB2A080RD | Complementary | maximum switching voltage | 250 V DC conforming to IEC
29374 | RSB2A080RD | Complementary | minimum switching voltage | 12 V
29375 | RSB2A080RD | Complementary | maximum switching capacity | 2000 VA/224 W
29376 | RSB2A080RD | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
29377 | RSB2A080RD | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
29378 | RSB2A080RD | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
29379 | RSB2A080RD | Complementary | mechanical durability | 30000000 cycles
29380 | RSB2A080RD | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
29381 | RSB2A080RD | Complementary | operating time | 20 ms operating 20 ms reset
29382 | RSB2A080RD | Complementary | marking | CE
29383 | RSB2A080RD | Complementary | average coil consumption | 0.45 W DC
29384 | RSB2A080RD | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
29385 | RSB2A080RD | Complementary | safety reliability data | B10d = 100000
29386 | RSB2A080RD | Complementary | protection category | RT I
29387 | RSB2A080RD | Complementary | test levels | Level A group mounting
29388 | RSB2A080RD | Complementary | operating position | Any position
29389 | RSB2A080RD | Complementary | net weight | 0.014 kg
29390 | RSB2A080RD | Complementary | sale per indivisible quantity | 10
29391 | RSB2A080RD | Complementary | device presentation | Complete product
29392 | RSB2A080RD | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
29393 | RSB2A080RD | Environment | standards | UL 508 EN/IEC 61810-1 CSA C22.2 No 14
29394 | RSB2A080RD | Environment | product certifications | EAC CSA UL
29395 | RSB2A080RD | Environment | ambient air temperature for storage | -40…85 °C
29396 | RSB2A080RD | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
29397 | RSB2A080RD | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29398 | RSB2A080RD | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
29399 | RSB2A080RD | Environment | ambient air temperature for operation | -40…85 °C (DC)
29400 | RSB2A080RD | Offer Sustainability | Sustainable offer status | Green Premium product
29401 | RSB2A080RD | Offer Sustainability | REACh Regulation | REACh Declaration
29402 | RSB2A080RD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29403 | RSB2A080RD | Offer Sustainability | Toxic heavy metal free | Yes
29404 | RSB2A080RD | Offer Sustainability | Mercury free | Yes
29405 | RSB2A080RD | Offer Sustainability | RoHS exemption information | Yes
29406 | RSB2A080RD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29407 | RSB2A080RD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29408 | RSB2A080RD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29409 | RSB2A080RD | Contractual warranty | Warranty | 18 months
29410 | RSB2A080U7 | Main | range of product | Zelio Relay
29411 | RSB2A080U7 | Main | series name | Interface relay
29412 | RSB2A080U7 | Main | product or component type | Plug-in relay
29413 | RSB2A080U7 | Main | device short name | RSB
29414 | RSB2A080U7 | Main | contacts type and composition | 2 C/O
29415 | RSB2A080U7 | Main | contact operation | Standard
29416 | RSB2A080U7 | Main | [Uc] control circuit voltage | 240 V AC
29417 | RSB2A080U7 | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
29418 | RSB2A080U7 | Main | status LED | Without
29419 | RSB2A080U7 | Main | control type | Without push-button
29420 | RSB2A080U7 | Complementary | shape of pin | Flat (PCB type)
29421 | RSB2A080U7 | Complementary | average coil resistance | 33000 Ohm network: AC at 20 °C +/- 10 %
29422 | RSB2A080U7 | Complementary | [Ue] rated operational voltage | 192...360 V AC 50/60 Hz
29423 | RSB2A080U7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
29424 | RSB2A080U7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
29425 | RSB2A080U7 | Complementary | contacts material | Silver alloy (AgNi)
29426 | RSB2A080U7 | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
29427 | RSB2A080U7 | Complementary | minimum switching current | 10 mA
29428 | RSB2A080U7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
29429 | RSB2A080U7 | Complementary | minimum switching voltage | 12 V
29430 | RSB2A080U7 | Complementary | maximum switching capacity | 2000 VA/224 W
29431 | RSB2A080U7 | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
29432 | RSB2A080U7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
29433 | RSB2A080U7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
29434 | RSB2A080U7 | Complementary | mechanical durability | 5000000 cycles
29435 | RSB2A080U7 | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
29436 | RSB2A080U7 | Complementary | operating time | 20 ms operating 20 ms reset
29437 | RSB2A080U7 | Complementary | marking | CE
29438 | RSB2A080U7 | Complementary | average coil consumption | 0.75 VA AC
29439 | RSB2A080U7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
29440 | RSB2A080U7 | Complementary | safety reliability data | B10d = 100000
29441 | RSB2A080U7 | Complementary | protection category | RT I
29442 | RSB2A080U7 | Complementary | test levels | Level A group mounting
29443 | RSB2A080U7 | Complementary | operating position | Any position
29444 | RSB2A080U7 | Complementary | net weight | 0.014 kg
29445 | RSB2A080U7 | Complementary | sale per indivisible quantity | 10
29446 | RSB2A080U7 | Complementary | device presentation | Complete product
29447 | RSB2A080U7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
29448 | RSB2A080U7 | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
29449 | RSB2A080U7 | Environment | product certifications | EAC UL CSA
29450 | RSB2A080U7 | Environment | ambient air temperature for storage | -40…85 °C
29451 | RSB2A080U7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
29452 | RSB2A080U7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29453 | RSB2A080U7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
29454 | RSB2A080U7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
29455 | RSB2A080U7 | Offer Sustainability | Sustainable offer status | Green Premium product
29456 | RSB2A080U7 | Offer Sustainability | REACh Regulation | REACh Declaration
29457 | RSB2A080U7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29458 | RSB2A080U7 | Offer Sustainability | Toxic heavy metal free | Yes
29459 | RSB2A080U7 | Offer Sustainability | Mercury free | Yes
29460 | RSB2A080U7 | Offer Sustainability | RoHS exemption information | Yes
29461 | RSB2A080U7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29462 | RSB2A080U7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29463 | RSB2A080U7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29464 | RSB2A080U7 | Contractual warranty | Warranty | 18 months
29465 | RSB2A080M7 | Main | range of product | Zelio Relay
29466 | RSB2A080M7 | Main | series name | Interface relay
29467 | RSB2A080M7 | Main | product or component type | Plug-in relay
29468 | RSB2A080M7 | Main | device short name | RSB
29469 | RSB2A080M7 | Main | contacts type and composition | 2 C/O
29470 | RSB2A080M7 | Main | contact operation | Standard
29471 | RSB2A080M7 | Main | [Uc] control circuit voltage | 220 V AC
29472 | RSB2A080M7 | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
29473 | RSB2A080M7 | Main | status LED | Without
29474 | RSB2A080M7 | Main | control type | Without push-button
29475 | RSB2A080M7 | Complementary | shape of pin | Flat (PCB type)
29476 | RSB2A080M7 | Complementary | average coil resistance | 33000 Ohm network: AC at 20 °C +/- 10 %
29477 | RSB2A080M7 | Complementary | [Ue] rated operational voltage | 176...330 V AC 50/60 Hz
29478 | RSB2A080M7 | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
29479 | RSB2A080M7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
29480 | RSB2A080M7 | Complementary | contacts material | Silver alloy (AgNi)
29481 | RSB2A080M7 | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
29482 | RSB2A080M7 | Complementary | minimum switching current | 10 mA
29483 | RSB2A080M7 | Complementary | maximum switching voltage | 250 V DC conforming to IEC
29484 | RSB2A080M7 | Complementary | minimum switching voltage | 12 V
29485 | RSB2A080M7 | Complementary | maximum switching capacity | 2000 VA/224 W
29486 | RSB2A080M7 | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
29487 | RSB2A080M7 | Complementary | minimum switching capacity | 120 mW at 10 mA, 12 V
29488 | RSB2A080M7 | Complementary | operating rate | <= 600 cycles/hour under load <= 18000 cycles/hour no-load
29489 | RSB2A080M7 | Complementary | mechanical durability | 5000000 cycles
29490 | RSB2A080M7 | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
29491 | RSB2A080M7 | Complementary | operating time | 20 ms operating 20 ms reset
29492 | RSB2A080M7 | Complementary | marking | CE
29493 | RSB2A080M7 | Complementary | average coil consumption | 0.75 VA AC
29494 | RSB2A080M7 | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
29495 | RSB2A080M7 | Complementary | safety reliability data | B10d = 100000
29496 | RSB2A080M7 | Complementary | protection category | RT I
29497 | RSB2A080M7 | Complementary | test levels | Level A group mounting
29498 | RSB2A080M7 | Complementary | operating position | Any position
29499 | RSB2A080M7 | Complementary | net weight | 0.014 kg
29500 | RSB2A080M7 | Complementary | sale per indivisible quantity | 10
29501 | RSB2A080M7 | Complementary | device presentation | Complete product
29502 | RSB2A080M7 | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
29503 | RSB2A080M7 | Environment | standards | UL 508 EN/IEC 61810-1 CSA C22.2 No 14
29504 | RSB2A080M7 | Environment | product certifications | CSA UL EAC
29505 | RSB2A080M7 | Environment | ambient air temperature for storage | -40…85 °C
29506 | RSB2A080M7 | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
29507 | RSB2A080M7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29508 | RSB2A080M7 | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
29509 | RSB2A080M7 | Environment | ambient air temperature for operation | -40…70 °C (AC)
29510 | RSB2A080M7 | Offer Sustainability | Sustainable offer status | Green Premium product
29511 | RSB2A080M7 | Offer Sustainability | REACh Regulation | REACh Declaration
29512 | RSB2A080M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29513 | RSB2A080M7 | Offer Sustainability | Toxic heavy metal free | Yes
29514 | RSB2A080M7 | Offer Sustainability | Mercury free | Yes
29515 | RSB2A080M7 | Offer Sustainability | RoHS exemption information | Yes
29516 | RSB2A080M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29517 | RSB2A080M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29518 | RSB2A080M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29519 | RSB2A080M7 | Contractual warranty | Warranty | 18 months
29520 | RSL1PVJU | Main | range of product | Zelio Relay
29521 | RSL1PVJU | Main | series name | Interface relay
29522 | RSL1PVJU | Main | product or component type | Plug-in relay
29523 | RSL1PVJU | Main | device short name | RSL
29524 | RSL1PVJU | Main | contacts type and composition | 1 C/O
29525 | RSL1PVJU | Main | contact operation | Standard
29526 | RSL1PVJU | Main | [Uc] control circuit voltage | 12 V DC
29527 | RSL1PVJU | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
29528 | RSL1PVJU | Main | status LED | With
29529 | RSL1PVJU | Main | shape of pin | Flat (PCB type)
29530 | RSL1PVJU | Complementary | fixing mode | Plastic compression spring
29531 | RSL1PVJU | Complementary | average resistance | 848 Ohm network: DC at 23 °C +/- 10 %
29532 | RSL1PVJU | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
29533 | RSL1PVJU | Complementary | [Uimp] rated impulse withstand voltage | IEC 6 kV
29534 | RSL1PVJU | Complementary | contacts material | Silver alloy (AgSnO2)
29535 | RSL1PVJU | Complementary | [Ie] rated operational current | 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL
29536 | RSL1PVJU | Complementary | minimum switching current | 100 mA
29537 | RSL1PVJU | Complementary | maximum switching voltage | 277 V
29538 | RSL1PVJU | Complementary | switching voltage | 12 V
29539 | RSL1PVJU | Complementary | maximum switching capacity | 1500 VA 150 W
29540 | RSL1PVJU | Complementary | minimum switching capacity | 120 mW
29541 | RSL1PVJU | Complementary | operating rate | <= 72000 cycles/hour no-load <= 360 cycles/hour under load
29542 | RSL1PVJU | Complementary | mechanical durability | 10000000 cycles
29543 | RSL1PVJU | Complementary | electrical durability | 60000 cycles for resistive load, 6 A at 250 V, AC-1
29544 | RSL1PVJU | Complementary | operating time | 5 ms reset 12 ms
29545 | RSL1PVJU | Complementary | marking | CE
29546 | RSL1PVJU | Complementary | protection category | RT III
29547 | RSL1PVJU | Complementary | test levels | Level A group mounting
29548 | RSL1PVJU | Complementary | operating position | Any position
29549 | RSL1PVJU | Complementary | height | 78.6 mm
29550 | RSL1PVJU | Complementary | width | 6.2 mm
29551 | RSL1PVJU | Complementary | depth | 95 mm
29552 | RSL1PVJU | Complementary | terminals description ISO n°1 | (11-12-14)OC (A1-A2)CO
29553 | RSL1PVJU | Complementary | sale per indivisible quantity | 10
29554 | RSL1PVJU | Complementary | net weight | 0.029 kg
29555 | RSL1PVJU | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
29556 | RSL1PVJU | Complementary | average coil consumption | 0.17 W, DC
29557 | RSL1PVJU | Complementary | drop-out voltage threshold | >= 0.05 Uc
29558 | RSL1PVJU | Complementary | contact terminal arrangement | Separate
29559 | RSL1PVJU | Complementary | connections - terminals | Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) solid without cable end
29560 | RSL1PVJU | Complementary | tightening torque | < 0.5 N.m for M2.5 screw(s)
29561 | RSL1PVJU | Complementary | safety reliability data | B10d = 60000
29562 | RSL1PVJU | Complementary | control type | Without push-button
29563 | RSL1PVJU | Complementary | mounting support | 35 mm symmetrical DIN rail
29564 | RSL1PVJU | Complementary | device presentation | Complete product
29565 | RSL1PVJU | Environment | input voltage | 12 V AC/DC (input voltage limit: 11.4...14.4 V)
29566 | RSL1PVJU | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
29567 | RSL1PVJU | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
29568 | RSL1PVJU | Environment | product certifications | UL GOST CSA
29569 | RSL1PVJU | Environment | ambient air temperature for storage | -40…85 °C
29570 | RSL1PVJU | Environment | vibration resistance | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6
29571 | RSL1PVJU | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29572 | RSL1PVJU | Environment | shock resistance | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27
29573 | RSL1PVJU | Environment | ambient air temperature for operation | -40…55 °C
29574 | RSL1PVJU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29575 | RSL1PVJU | Offer Sustainability | Toxic heavy metal free | Yes
29576 | RSL1PVJU | Offer Sustainability | Mercury free | Yes
29577 | RSL1PVJU | Offer Sustainability | RoHS exemption information | Yes
29578 | RSL1PVJU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29579 | RSL1PVJU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29580 | RSL1PVJU | Offer Sustainability | Circularity Profile | End of Life Information
29581 | RSL1PVJU | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29582 | RSL1PVJU | Contractual warranty | Warranty | 18 months
29583 | RSL1PVBU | Main | range of product | Zelio Relay
29584 | RSL1PVBU | Main | series name | Interface relay
29585 | RSL1PVBU | Main | product or component type | Plug-in relay
29586 | RSL1PVBU | Main | device short name | RSL
29587 | RSL1PVBU | Main | contacts type and composition | 1 C/O
29588 | RSL1PVBU | Main | contact operation | Standard
29589 | RSL1PVBU | Main | [Uc] control circuit voltage | 24 V DC
29590 | RSL1PVBU | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
29591 | RSL1PVBU | Main | status LED | With
29592 | RSL1PVBU | Main | shape of pin | Flat (PCB type)
29593 | RSL1PVBU | Complementary | fixing mode | Plastic compression spring
29594 | RSL1PVBU | Complementary | average resistance | 3390 Ohm network: DC at 23 °C +/- 10 %
29595 | RSL1PVBU | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
29596 | RSL1PVBU | Complementary | [Uimp] rated impulse withstand voltage | 6 kV IEC
29597 | RSL1PVBU | Complementary | contacts material | Silver alloy (AgSnO2)
29598 | RSL1PVBU | Complementary | [Ie] rated operational current | 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL
29599 | RSL1PVBU | Complementary | minimum switching current | 100 mA
29600 | RSL1PVBU | Complementary | maximum switching voltage | 277 V
29601 | RSL1PVBU | Complementary | switching voltage | 12 V
29602 | RSL1PVBU | Complementary | maximum switching capacity | 1500 VA 150 W
29603 | RSL1PVBU | Complementary | minimum switching capacity | 120 mW
29604 | RSL1PVBU | Complementary | operating rate | <= 72000 cycles/hour no-load <= 360 cycles/hour under load
29605 | RSL1PVBU | Complementary | mechanical durability | 10000000 cycles
29606 | RSL1PVBU | Complementary | electrical durability | 60000 cycles for resistive load, 6 A at 250 V, AC-1
29607 | RSL1PVBU | Complementary | operating time | 5 ms reset 12 ms
29608 | RSL1PVBU | Complementary | marking | CE
29609 | RSL1PVBU | Complementary | protection category | RT III
29610 | RSL1PVBU | Complementary | test levels | Level A group mounting
29611 | RSL1PVBU | Complementary | operating position | Any position
29612 | RSL1PVBU | Complementary | height | 78.6 mm
29613 | RSL1PVBU | Complementary | width | 6.2 mm
29614 | RSL1PVBU | Complementary | depth | 95 mm
29615 | RSL1PVBU | Complementary | terminals description ISO n°1 | (A1-A2)CO (11-12-14)OC
29616 | RSL1PVBU | Complementary | sale per indivisible quantity | 10
29617 | RSL1PVBU | Complementary | net weight | 0.029 kg
29618 | RSL1PVBU | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
29619 | RSL1PVBU | Complementary | average coil consumption | 0.17 W, DC
29620 | RSL1PVBU | Complementary | drop-out voltage threshold | >= 0.05 Uc
29621 | RSL1PVBU | Complementary | contact terminal arrangement | Separate
29622 | RSL1PVBU | Complementary | connections - terminals | Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) solid without cable end
29623 | RSL1PVBU | Complementary | tightening torque | < 0.5 N.m for M2.5 screw(s)
29624 | RSL1PVBU | Complementary | safety reliability data | B10d = 60000
29625 | RSL1PVBU | Complementary | control type | Without push-button
29626 | RSL1PVBU | Complementary | mounting support | 35 mm symmetrical DIN rail
29627 | RSL1PVBU | Complementary | device presentation | Complete product
29628 | RSL1PVBU | Environment | input voltage | 24 V AC/DC (input voltage limit: 21.6...28.8 V)
29629 | RSL1PVBU | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
29630 | RSL1PVBU | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
29631 | RSL1PVBU | Environment | product certifications | UL GOST CSA
29632 | RSL1PVBU | Environment | ambient air temperature for storage | -40…85 °C
29633 | RSL1PVBU | Environment | vibration resistance | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6
29634 | RSL1PVBU | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29635 | RSL1PVBU | Environment | shock resistance | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27
29636 | RSL1PVBU | Environment | ambient air temperature for operation | -40…55 °C
29637 | RSL1PVBU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29638 | RSL1PVBU | Offer Sustainability | Toxic heavy metal free | Yes
29639 | RSL1PVBU | Offer Sustainability | Mercury free | Yes
29640 | RSL1PVBU | Offer Sustainability | RoHS exemption information | Yes
29641 | RSL1PVBU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29642 | RSL1PVBU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29643 | RSL1PVBU | Offer Sustainability | Circularity Profile | End of Life Information
29644 | RSL1PVBU | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29645 | RSL1PVBU | Contractual warranty | Warranty | 18 months
29646 | RSL1PVEU | Main | range of product | Zelio Relay
29647 | RSL1PVEU | Main | series name | Interface relay
29648 | RSL1PVEU | Main | product or component type | Plug-in relay
29649 | RSL1PVEU | Main | device short name | RSL
29650 | RSL1PVEU | Main | contacts type and composition | 1 C/O
29651 | RSL1PVEU | Main | contact operation | Standard
29652 | RSL1PVEU | Main | [Uc] control circuit voltage | 48 V DC
29653 | RSL1PVEU | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
29654 | RSL1PVEU | Main | status LED | With
29655 | RSL1PVEU | Main | shape of pin | Flat (PCB type)
29656 | RSL1PVEU | Complementary | fixing mode | Plastic compression spring
29657 | RSL1PVEU | Complementary | average resistance | 10600 Ohm network: DC at 23 °C +/- 10 %
29658 | RSL1PVEU | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
29659 | RSL1PVEU | Complementary | [Uimp] rated impulse withstand voltage | IEC 6 kV
29660 | RSL1PVEU | Complementary | contacts material | Silver alloy (AgSnO2)
29661 | RSL1PVEU | Complementary | [Ie] rated operational current | 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL
29662 | RSL1PVEU | Complementary | minimum switching current | 100 mA
29663 | RSL1PVEU | Complementary | maximum switching voltage | 277 V
29664 | RSL1PVEU | Complementary | switching voltage | 12 V
29665 | RSL1PVEU | Complementary | maximum switching capacity | 1500 VA 150 W
29666 | RSL1PVEU | Complementary | minimum switching capacity | 120 mW
29667 | RSL1PVEU | Complementary | operating rate | <= 72000 cycles/hour no-load <= 360 cycles/hour under load
29668 | RSL1PVEU | Complementary | mechanical durability | 10000000 cycles
29669 | RSL1PVEU | Complementary | electrical durability | 60000 cycles for resistive load, 6 A at 250 V, AC-1
29670 | RSL1PVEU | Complementary | operating time | 5 ms reset 12 ms
29671 | RSL1PVEU | Complementary | marking | CE
29672 | RSL1PVEU | Complementary | protection category | RT III
29673 | RSL1PVEU | Complementary | test levels | Level A group mounting
29674 | RSL1PVEU | Complementary | operating position | Any position
29675 | RSL1PVEU | Complementary | height | 78.6 mm
29676 | RSL1PVEU | Complementary | width | 6.2 mm
29677 | RSL1PVEU | Complementary | depth | 95 mm
29678 | RSL1PVEU | Complementary | terminals description ISO n°1 | (11-12-14)OC (A1-A2)CO
29679 | RSL1PVEU | Complementary | sale per indivisible quantity | 10
29680 | RSL1PVEU | Complementary | net weight | 0.029 kg
29681 | RSL1PVEU | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
29682 | RSL1PVEU | Complementary | average coil consumption | 0.17 W, DC
29683 | RSL1PVEU | Complementary | drop-out voltage threshold | >= 0.05 Uc
29684 | RSL1PVEU | Complementary | contact terminal arrangement | Separate
29685 | RSL1PVEU | Complementary | connections - terminals | Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) solid without cable end
29686 | RSL1PVEU | Complementary | tightening torque | < 0.5 N.m for M2.5 screw(s)
29687 | RSL1PVEU | Complementary | safety reliability data | B10d = 60000
29688 | RSL1PVEU | Complementary | control type | Without push-button
29689 | RSL1PVEU | Complementary | mounting support | 35 mm symmetrical DIN rail
29690 | RSL1PVEU | Complementary | device presentation | Complete product
29691 | RSL1PVEU | Environment | input voltage | 48 V AC/DC (input voltage limit: 43.2...57.6 V)
29692 | RSL1PVEU | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
29693 | RSL1PVEU | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
29694 | RSL1PVEU | Environment | product certifications | GOST CSA UL
29695 | RSL1PVEU | Environment | ambient air temperature for storage | -40…85 °C
29696 | RSL1PVEU | Environment | vibration resistance | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6
29697 | RSL1PVEU | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29698 | RSL1PVEU | Environment | shock resistance | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27
29699 | RSL1PVEU | Environment | ambient air temperature for operation | -40…55 °C
29700 | RSL1PVEU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29701 | RSL1PVEU | Offer Sustainability | Toxic heavy metal free | Yes
29702 | RSL1PVEU | Offer Sustainability | Mercury free | Yes
29703 | RSL1PVEU | Offer Sustainability | RoHS exemption information | Yes
29704 | RSL1PVEU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29705 | RSL1PVEU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29706 | RSL1PVEU | Offer Sustainability | Circularity Profile | End of Life Information
29707 | RSL1PVEU | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29708 | RSL1PVEU | Contractual warranty | Warranty | 18 months
29709 | RSL1PVFU | Main | range of product | Zelio Relay
29710 | RSL1PVFU | Main | series name | Interface relay
29711 | RSL1PVFU | Main | product or component type | Plug-in relay
29712 | RSL1PVFU | Main | device short name | RSL
29713 | RSL1PVFU | Main | contacts type and composition | 1 C/O
29714 | RSL1PVFU | Main | contact operation | Standard
29715 | RSL1PVFU | Main | [Uc] control circuit voltage | 60 V DC
29716 | RSL1PVFU | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
29717 | RSL1PVFU | Main | status LED | With
29718 | RSL1PVFU | Main | shape of pin | Flat (PCB type)
29719 | RSL1PVFU | Complementary | fixing mode | Plastic compression spring
29720 | RSL1PVFU | Complementary | average resistance | 20500 Ohm network: DC at 23 °C +/- 10 %
29721 | RSL1PVFU | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
29722 | RSL1PVFU | Complementary | [Uimp] rated impulse withstand voltage | 6 kV IEC
29723 | RSL1PVFU | Complementary | contacts material | Silver alloy (AgSnO2)
29724 | RSL1PVFU | Complementary | [Ie] rated operational current | 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL
29725 | RSL1PVFU | Complementary | minimum switching current | 100 mA
29726 | RSL1PVFU | Complementary | maximum switching voltage | 277 V
29727 | RSL1PVFU | Complementary | switching voltage | 12 V
29728 | RSL1PVFU | Complementary | maximum switching capacity | 1500 VA 150 W
29729 | RSL1PVFU | Complementary | minimum switching capacity | 120 mW
29730 | RSL1PVFU | Complementary | operating rate | <= 72000 cycles/hour no-load <= 360 cycles/hour under load
29731 | RSL1PVFU | Complementary | mechanical durability | 10000000 cycles
29732 | RSL1PVFU | Complementary | electrical durability | 60000 cycles for resistive load, 6 A at 250 V, AC-1
29733 | RSL1PVFU | Complementary | operating time | 5 ms reset 12 ms
29734 | RSL1PVFU | Complementary | reset time | 20 ms
29735 | RSL1PVFU | Complementary | marking | CE
29736 | RSL1PVFU | Complementary | protection category | RT III
29737 | RSL1PVFU | Complementary | test levels | Level A group mounting
29738 | RSL1PVFU | Complementary | operating position | Any position
29739 | RSL1PVFU | Complementary | height | 78.6 mm
29740 | RSL1PVFU | Complementary | width | 6.2 mm
29741 | RSL1PVFU | Complementary | depth | 95 mm
29742 | RSL1PVFU | Complementary | terminals description ISO n°1 | (A1-A2)CO (11-12-14)OC
29743 | RSL1PVFU | Complementary | sale per indivisible quantity | 10
29744 | RSL1PVFU | Complementary | net weight | 0.029 kg
29745 | RSL1PVFU | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
29746 | RSL1PVFU | Complementary | average coil consumption | 0.17 W, DC
29747 | RSL1PVFU | Complementary | drop-out voltage threshold | >= 0.05 Uc
29748 | RSL1PVFU | Complementary | contact terminal arrangement | Separate
29749 | RSL1PVFU | Complementary | connections - terminals | Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) solid without cable end
29750 | RSL1PVFU | Complementary | tightening torque | < 0.5 N.m for M2.5 screw(s)
29751 | RSL1PVFU | Complementary | safety reliability data | B10d = 60000
29752 | RSL1PVFU | Complementary | control type | Without push-button
29753 | RSL1PVFU | Complementary | mounting support | 35 mm symmetrical DIN rail
29754 | RSL1PVFU | Complementary | device presentation | Complete product
29755 | RSL1PVFU | Environment | input voltage | 110 V AC/DC (input voltage limit: 88...126.5 V)
29756 | RSL1PVFU | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
29757 | RSL1PVFU | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
29758 | RSL1PVFU | Environment | product certifications | CSA UL GOST
29759 | RSL1PVFU | Environment | ambient air temperature for storage | -40…85 °C
29760 | RSL1PVFU | Environment | vibration resistance | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6
29761 | RSL1PVFU | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29762 | RSL1PVFU | Environment | shock resistance | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27
29763 | RSL1PVFU | Environment | ambient air temperature for operation | -40…70 °C
29764 | RSL1PVFU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29765 | RSL1PVFU | Offer Sustainability | Toxic heavy metal free | Yes
29766 | RSL1PVFU | Offer Sustainability | Mercury free | Yes
29767 | RSL1PVFU | Offer Sustainability | RoHS exemption information | Yes
29768 | RSL1PVFU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29769 | RSL1PVFU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29770 | RSL1PVFU | Offer Sustainability | Circularity Profile | End of Life Information
29771 | RSL1PVFU | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29772 | RSL1PVFU | Contractual warranty | Warranty | 18 months
29773 | RSL1PVPU | Main | range of product | Zelio Relay
29774 | RSL1PVPU | Main | series name | Interface relay
29775 | RSL1PVPU | Main | product or component type | Plug-in relay
29776 | RSL1PVPU | Main | device short name | RSL
29777 | RSL1PVPU | Main | contacts type and composition | 1 C/O
29778 | RSL1PVPU | Main | contact operation | Standard
29779 | RSL1PVPU | Main | [Uc] control circuit voltage | 60 V DC
29780 | RSL1PVPU | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
29781 | RSL1PVPU | Main | status LED | With
29782 | RSL1PVPU | Main | shape of pin | Flat (PCB type)
29783 | RSL1PVPU | Complementary | fixing mode | Plastic compression spring
29784 | RSL1PVPU | Complementary | average resistance | 20500 Ohm network: DC at 23 °C +/- 10 %
29785 | RSL1PVPU | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
29786 | RSL1PVPU | Complementary | [Uimp] rated impulse withstand voltage | IEC 6 kV
29787 | RSL1PVPU | Complementary | contacts material | Silver alloy (AgSnO2)
29788 | RSL1PVPU | Complementary | [Ie] rated operational current | 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL
29789 | RSL1PVPU | Complementary | minimum switching current | 100 mA
29790 | RSL1PVPU | Complementary | maximum switching voltage | 277 V
29791 | RSL1PVPU | Complementary | switching voltage | 12 V
29792 | RSL1PVPU | Complementary | maximum switching capacity | 1500 VA 150 W
29793 | RSL1PVPU | Complementary | minimum switching capacity | 120 mW
29794 | RSL1PVPU | Complementary | operating rate | <= 72000 cycles/hour no-load <= 360 cycles/hour under load
29795 | RSL1PVPU | Complementary | mechanical durability | 10000000 cycles
29796 | RSL1PVPU | Complementary | electrical durability | 60000 cycles for resistive load, 6 A at 250 V, AC-1
29797 | RSL1PVPU | Complementary | operating time | 5 ms reset 12 ms
29798 | RSL1PVPU | Complementary | reset time | 20 ms
29799 | RSL1PVPU | Complementary | marking | CE
29800 | RSL1PVPU | Complementary | protection category | RT III
29801 | RSL1PVPU | Complementary | test levels | Level A group mounting
29802 | RSL1PVPU | Complementary | operating position | Any position
29803 | RSL1PVPU | Complementary | height | 78.6 mm
29804 | RSL1PVPU | Complementary | width | 6.2 mm
29805 | RSL1PVPU | Complementary | depth | 95 mm
29806 | RSL1PVPU | Complementary | terminals description ISO n°1 | (11-12-14)OC (A1-A2)CO
29807 | RSL1PVPU | Complementary | sale per indivisible quantity | 10
29808 | RSL1PVPU | Complementary | net weight | 0.029 kg
29809 | RSL1PVPU | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
29810 | RSL1PVPU | Complementary | average coil consumption | 0.17 W, DC
29811 | RSL1PVPU | Complementary | drop-out voltage threshold | >= 0.05 Uc
29812 | RSL1PVPU | Complementary | contact terminal arrangement | Separate
29813 | RSL1PVPU | Complementary | connections - terminals | Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) solid without cable end
29814 | RSL1PVPU | Complementary | tightening torque | < 0.5 N.m for M2.5 screw(s)
29815 | RSL1PVPU | Complementary | safety reliability data | B10d = 60000
29816 | RSL1PVPU | Complementary | control type | Without push-button
29817 | RSL1PVPU | Complementary | mounting support | 35 mm symmetrical DIN rail
29818 | RSL1PVPU | Complementary | device presentation | Complete product
29819 | RSL1PVPU | Environment | input voltage | 230 V AC/DC (input voltage limit: 184...264.5 V)
29820 | RSL1PVPU | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
29821 | RSL1PVPU | Environment | standards | EN/IEC 61810-1 UL 508 CSA C22.2 No 14
29822 | RSL1PVPU | Environment | product certifications | GOST CSA UL
29823 | RSL1PVPU | Environment | ambient air temperature for storage | -40…85 °C
29824 | RSL1PVPU | Environment | vibration resistance | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6
29825 | RSL1PVPU | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29826 | RSL1PVPU | Environment | shock resistance | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27
29827 | RSL1PVPU | Environment | ambient air temperature for operation | -40…70 °C
29828 | RSL1PVPU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29829 | RSL1PVPU | Offer Sustainability | Toxic heavy metal free | Yes
29830 | RSL1PVPU | Offer Sustainability | Mercury free | Yes
29831 | RSL1PVPU | Offer Sustainability | RoHS exemption information | Yes
29832 | RSL1PVPU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29833 | RSL1PVPU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29834 | RSL1PVPU | Offer Sustainability | Circularity Profile | End of Life Information
29835 | RSL1PVPU | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29836 | RSL1PVPU | Contractual warranty | Warranty | 18 months
29837 | RSL1PRJU | Main | range of product | Zelio Relay
29838 | RSL1PRJU | Main | series name | Interface relay
29839 | RSL1PRJU | Main | product or component type | Plug-in relay
29840 | RSL1PRJU | Main | device short name | RSL
29841 | RSL1PRJU | Main | contacts type and composition | 1 C/O
29842 | RSL1PRJU | Main | contact operation | Standard
29843 | RSL1PRJU | Main | [Uc] control circuit voltage | 12 V DC
29844 | RSL1PRJU | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
29845 | RSL1PRJU | Main | status LED | With
29846 | RSL1PRJU | Main | shape of pin | Flat (PCB type)
29847 | RSL1PRJU | Complementary | fixing mode | Plastic compression spring
29848 | RSL1PRJU | Complementary | average resistance | 848 Ohm network: DC at 23 °C +/- 10 %
29849 | RSL1PRJU | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
29850 | RSL1PRJU | Complementary | [Uimp] rated impulse withstand voltage | 6 kV IEC
29851 | RSL1PRJU | Complementary | contacts material | Silver alloy (AgSnO2)
29852 | RSL1PRJU | Complementary | [Ie] rated operational current | 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL
29853 | RSL1PRJU | Complementary | minimum switching current | 100 mA
29854 | RSL1PRJU | Complementary | maximum switching voltage | 277 V
29855 | RSL1PRJU | Complementary | switching voltage | 12 V
29856 | RSL1PRJU | Complementary | maximum switching capacity | 1500 VA 150 W
29857 | RSL1PRJU | Complementary | minimum switching capacity | 120 mW
29858 | RSL1PRJU | Complementary | operating rate | <= 72000 cycles/hour no-load <= 360 cycles/hour under load
29859 | RSL1PRJU | Complementary | mechanical durability | 10000000 cycles
29860 | RSL1PRJU | Complementary | electrical durability | 60000 cycles for resistive load, 6 A at 250 V, AC-1
29861 | RSL1PRJU | Complementary | operating time | 5 ms reset 12 ms
29862 | RSL1PRJU | Complementary | marking | CE
29863 | RSL1PRJU | Complementary | protection category | RT III
29864 | RSL1PRJU | Complementary | test levels | Level A group mounting
29865 | RSL1PRJU | Complementary | operating position | Any position
29866 | RSL1PRJU | Complementary | height | 78.6 mm
29867 | RSL1PRJU | Complementary | width | 6.2 mm
29868 | RSL1PRJU | Complementary | depth | 101 mm
29869 | RSL1PRJU | Complementary | terminals description ISO n°1 | (A1-A2)CO (11-12-14)OC
29870 | RSL1PRJU | Complementary | sale per indivisible quantity | 10
29871 | RSL1PRJU | Complementary | net weight | 0.029 kg
29872 | RSL1PRJU | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
29873 | RSL1PRJU | Complementary | average coil consumption | 0.17 W, DC
29874 | RSL1PRJU | Complementary | drop-out voltage threshold | >= 0.05 Uc
29875 | RSL1PRJU | Complementary | contact terminal arrangement | Separate
29876 | RSL1PRJU | Complementary | connections - terminals | Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) solid without cable end
29877 | RSL1PRJU | Complementary | tightening torque | 10...40 N.m
29878 | RSL1PRJU | Complementary | safety reliability data | B10d = 60000
29879 | RSL1PRJU | Complementary | clamping force | 10…40 N
29880 | RSL1PRJU | Complementary | control type | Without push-button
29881 | RSL1PRJU | Complementary | mounting support | 35 mm symmetrical DIN rail
29882 | RSL1PRJU | Complementary | device presentation | Complete product
29883 | RSL1PRJU | Environment | input voltage | 12 V AC/DC (input voltage limit: 11.4...14.4 V)
29884 | RSL1PRJU | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
29885 | RSL1PRJU | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
29886 | RSL1PRJU | Environment | product certifications | CSA UL GOST
29887 | RSL1PRJU | Environment | ambient air temperature for storage | -40…85 °C
29888 | RSL1PRJU | Environment | vibration resistance | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6
29889 | RSL1PRJU | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29890 | RSL1PRJU | Environment | shock resistance | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27
29891 | RSL1PRJU | Environment | ambient air temperature for operation | -40…55 °C
29892 | RSL1PRJU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29893 | RSL1PRJU | Offer Sustainability | Toxic heavy metal free | Yes
29894 | RSL1PRJU | Offer Sustainability | Mercury free | Yes
29895 | RSL1PRJU | Offer Sustainability | RoHS exemption information | Yes
29896 | RSL1PRJU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29897 | RSL1PRJU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29898 | RSL1PRJU | Offer Sustainability | Circularity Profile | End of Life Information
29899 | RSL1PRJU | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29900 | RSL1PRJU | Contractual warranty | Warranty | 18 months
29901 | RSL1PRBU | Main | range of product | Zelio Relay
29902 | RSL1PRBU | Main | series name | Interface relay
29903 | RSL1PRBU | Main | product or component type | Plug-in relay
29904 | RSL1PRBU | Main | device short name | RSL
29905 | RSL1PRBU | Main | contacts type and composition | 1 C/O
29906 | RSL1PRBU | Main | contact operation | Standard
29907 | RSL1PRBU | Main | [Uc] control circuit voltage | 24 V DC
29908 | RSL1PRBU | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
29909 | RSL1PRBU | Main | status LED | With
29910 | RSL1PRBU | Main | shape of pin | Flat (PCB type)
29911 | RSL1PRBU | Complementary | fixing mode | Plastic compression spring
29912 | RSL1PRBU | Complementary | average resistance | 3390 Ohm network: DC at 23 °C +/- 10 %
29913 | RSL1PRBU | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
29914 | RSL1PRBU | Complementary | [Uimp] rated impulse withstand voltage | 6 kV IEC
29915 | RSL1PRBU | Complementary | contacts material | Silver alloy (AgSnO2)
29916 | RSL1PRBU | Complementary | [Ie] rated operational current | 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL
29917 | RSL1PRBU | Complementary | minimum switching current | 100 mA
29918 | RSL1PRBU | Complementary | maximum switching voltage | 277 V
29919 | RSL1PRBU | Complementary | switching voltage | 12 V
29920 | RSL1PRBU | Complementary | maximum switching capacity | 1500 VA 150 W
29921 | RSL1PRBU | Complementary | minimum switching capacity | 120 mW
29922 | RSL1PRBU | Complementary | operating rate | <= 72000 cycles/hour no-load <= 360 cycles/hour under load
29923 | RSL1PRBU | Complementary | mechanical durability | 10000000 cycles
29924 | RSL1PRBU | Complementary | electrical durability | 60000 cycles for resistive load, 6 A at 250 V, AC-1
29925 | RSL1PRBU | Complementary | operating time | 5 ms reset 12 ms
29926 | RSL1PRBU | Complementary | marking | CE
29927 | RSL1PRBU | Complementary | protection category | RT III
29928 | RSL1PRBU | Complementary | test levels | Level A group mounting
29929 | RSL1PRBU | Complementary | operating position | Any position
29930 | RSL1PRBU | Complementary | height | 78.6 mm
29931 | RSL1PRBU | Complementary | width | 6.2 mm
29932 | RSL1PRBU | Complementary | depth | 101 mm
29933 | RSL1PRBU | Complementary | terminals description ISO n°1 | (A1-A2)CO (11-12-14)OC
29934 | RSL1PRBU | Complementary | sale per indivisible quantity | 10
29935 | RSL1PRBU | Complementary | net weight | 0.029 kg
29936 | RSL1PRBU | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
29937 | RSL1PRBU | Complementary | average coil consumption | 0.17 W, DC
29938 | RSL1PRBU | Complementary | drop-out voltage threshold | >= 0.05 Uc
29939 | RSL1PRBU | Complementary | contact terminal arrangement | Separate
29940 | RSL1PRBU | Complementary | connections - terminals | Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) solid without cable end
29941 | RSL1PRBU | Complementary | tightening torque | 10...40 N.m
29942 | RSL1PRBU | Complementary | safety reliability data | B10d = 60000
29943 | RSL1PRBU | Complementary | clamping force | 10…40 N
29944 | RSL1PRBU | Complementary | control type | Without push-button
29945 | RSL1PRBU | Complementary | mounting support | 35 mm symmetrical DIN rail
29946 | RSL1PRBU | Complementary | device presentation | Complete product
29947 | RSL1PRBU | Environment | input voltage | 24 V AC/DC (input voltage limit: 21.6...28.8 V)
29948 | RSL1PRBU | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
29949 | RSL1PRBU | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508
29950 | RSL1PRBU | Environment | product certifications | UL CSA GOST
29951 | RSL1PRBU | Environment | ambient air temperature for storage | -40…85 °C
29952 | RSL1PRBU | Environment | vibration resistance | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6
29953 | RSL1PRBU | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
29954 | RSL1PRBU | Environment | shock resistance | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27
29955 | RSL1PRBU | Environment | ambient air temperature for operation | -40…55 °C
29956 | RSL1PRBU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
29957 | RSL1PRBU | Offer Sustainability | Toxic heavy metal free | Yes
29958 | RSL1PRBU | Offer Sustainability | Mercury free | Yes
29959 | RSL1PRBU | Offer Sustainability | RoHS exemption information | Yes
29960 | RSL1PRBU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
29961 | RSL1PRBU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
29962 | RSL1PRBU | Offer Sustainability | Circularity Profile | End of Life Information
29963 | RSL1PRBU | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
29964 | RSL1PRBU | Contractual warranty | Warranty | 18 months
29965 | RSL1PREU | Main | range of product | Zelio Relay
29966 | RSL1PREU | Main | series name | Interface relay
29967 | RSL1PREU | Main | product or component type | Plug-in relay
29968 | RSL1PREU | Main | device short name | RSL
29969 | RSL1PREU | Main | contacts type and composition | 1 C/O
29970 | RSL1PREU | Main | contact operation | Standard
29971 | RSL1PREU | Main | [Uc] control circuit voltage | 48 V DC
29972 | RSL1PREU | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
29973 | RSL1PREU | Main | status LED | With
29974 | RSL1PREU | Main | shape of pin | Flat (PCB type)
29975 | RSL1PREU | Complementary | fixing mode | Plastic compression spring
29976 | RSL1PREU | Complementary | average resistance | 10600 Ohm network: DC at 23 °C +/- 10 %
29977 | RSL1PREU | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
29978 | RSL1PREU | Complementary | [Uimp] rated impulse withstand voltage | IEC 6 kV
29979 | RSL1PREU | Complementary | contacts material | Silver alloy (AgSnO2)
29980 | RSL1PREU | Complementary | [Ie] rated operational current | 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL
29981 | RSL1PREU | Complementary | minimum switching current | 100 mA
29982 | RSL1PREU | Complementary | maximum switching voltage | 277 V
29983 | RSL1PREU | Complementary | switching voltage | 12 V
29984 | RSL1PREU | Complementary | maximum switching capacity | 1500 VA 150 W
29985 | RSL1PREU | Complementary | minimum switching capacity | 120 mW
29986 | RSL1PREU | Complementary | operating rate | <= 72000 cycles/hour no-load <= 360 cycles/hour under load
29987 | RSL1PREU | Complementary | mechanical durability | 10000000 cycles
29988 | RSL1PREU | Complementary | electrical durability | 60000 cycles for resistive load, 6 A at 250 V, AC-1
29989 | RSL1PREU | Complementary | operating time | 5 ms reset 12 ms
29990 | RSL1PREU | Complementary | marking | CE
29991 | RSL1PREU | Complementary | protection category | RT III
29992 | RSL1PREU | Complementary | test levels | Level A group mounting
29993 | RSL1PREU | Complementary | operating position | Any position
29994 | RSL1PREU | Complementary | height | 78.6 mm
29995 | RSL1PREU | Complementary | width | 6.2 mm
29996 | RSL1PREU | Complementary | depth | 101 mm
29997 | RSL1PREU | Complementary | terminals description ISO n°1 | (11-12-14)OC (A1-A2)CO
29998 | RSL1PREU | Complementary | sale per indivisible quantity | 10
29999 | RSL1PREU | Complementary | net weight | 0.029 kg
30000 | RSL1PREU | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
30001 | RSL1PREU | Complementary | average coil consumption | 0.17 W, DC
30002 | RSL1PREU | Complementary | drop-out voltage threshold | >= 0.05 Uc
30003 | RSL1PREU | Complementary | contact terminal arrangement | Separate
30004 | RSL1PREU | Complementary | connections - terminals | Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) solid without cable end
30005 | RSL1PREU | Complementary | tightening torque | 10...40 N.m
30006 | RSL1PREU | Complementary | safety reliability data | B10d = 60000
30007 | RSL1PREU | Complementary | clamping force | 10…40 N
30008 | RSL1PREU | Complementary | control type | Without push-button
30009 | RSL1PREU | Complementary | mounting support | 35 mm symmetrical DIN rail
30010 | RSL1PREU | Complementary | device presentation | Complete product
30011 | RSL1PREU | Environment | input voltage | 48 V AC/DC (input voltage limit: 43.2...57.6 V)
30012 | RSL1PREU | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
30013 | RSL1PREU | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
30014 | RSL1PREU | Environment | product certifications | GOST CSA UL
30015 | RSL1PREU | Environment | ambient air temperature for storage | -40…85 °C
30016 | RSL1PREU | Environment | vibration resistance | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6
30017 | RSL1PREU | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30018 | RSL1PREU | Environment | shock resistance | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27
30019 | RSL1PREU | Environment | ambient air temperature for operation | -40…55 °C
30020 | RSL1PREU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
30021 | RSL1PREU | Offer Sustainability | Toxic heavy metal free | Yes
30022 | RSL1PREU | Offer Sustainability | Mercury free | Yes
30023 | RSL1PREU | Offer Sustainability | RoHS exemption information | Yes
30024 | RSL1PREU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
30025 | RSL1PREU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
30026 | RSL1PREU | Offer Sustainability | Circularity Profile | End of Life Information
30027 | RSL1PREU | Contractual warranty | Warranty | 18 months
30028 | RSL1PRFU | Main | range of product | Zelio Relay
30029 | RSL1PRFU | Main | series name | Interface relay
30030 | RSL1PRFU | Main | product or component type | Plug-in relay
30031 | RSL1PRFU | Main | device short name | RSL
30032 | RSL1PRFU | Main | contacts type and composition | 1 C/O
30033 | RSL1PRFU | Main | contact operation | Standard
30034 | RSL1PRFU | Main | [Uc] control circuit voltage | 60 V DC
30035 | RSL1PRFU | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
30036 | RSL1PRFU | Main | status LED | With
30037 | RSL1PRFU | Main | shape of pin | Flat (PCB type)
30038 | RSL1PRFU | Complementary | fixing mode | Plastic compression spring
30039 | RSL1PRFU | Complementary | average resistance | 20500 Ohm network: DC at 23 °C +/- 10 %
30040 | RSL1PRFU | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
30041 | RSL1PRFU | Complementary | [Uimp] rated impulse withstand voltage | 6 kV IEC
30042 | RSL1PRFU | Complementary | contacts material | Silver alloy (AgSnO2)
30043 | RSL1PRFU | Complementary | [Ie] rated operational current | 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL
30044 | RSL1PRFU | Complementary | minimum switching current | 100 mA
30045 | RSL1PRFU | Complementary | maximum switching voltage | 277 V
30046 | RSL1PRFU | Complementary | switching voltage | 12 V
30047 | RSL1PRFU | Complementary | maximum switching capacity | 1500 VA 150 W
30048 | RSL1PRFU | Complementary | minimum switching capacity | 120 mW
30049 | RSL1PRFU | Complementary | operating rate | <= 72000 cycles/hour no-load <= 360 cycles/hour under load
30050 | RSL1PRFU | Complementary | mechanical durability | 10000000 cycles
30051 | RSL1PRFU | Complementary | electrical durability | 60000 cycles for resistive load, 6 A at 250 V, AC-1
30052 | RSL1PRFU | Complementary | operating time | 5 ms reset 12 ms
30053 | RSL1PRFU | Complementary | reset time | 20 ms
30054 | RSL1PRFU | Complementary | marking | CE
30055 | RSL1PRFU | Complementary | protection category | RT III
30056 | RSL1PRFU | Complementary | test levels | Level A group mounting
30057 | RSL1PRFU | Complementary | operating position | Any position
30058 | RSL1PRFU | Complementary | height | 78.6 mm
30059 | RSL1PRFU | Complementary | width | 6.2 mm
30060 | RSL1PRFU | Complementary | depth | 101 mm
30061 | RSL1PRFU | Complementary | terminals description ISO n°1 | (11-12-14)OC (A1-A2)CO
30062 | RSL1PRFU | Complementary | sale per indivisible quantity | 10
30063 | RSL1PRFU | Complementary | net weight | 0.029 kg
30064 | RSL1PRFU | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
30065 | RSL1PRFU | Complementary | average coil consumption | 0.17 W, DC
30066 | RSL1PRFU | Complementary | drop-out voltage threshold | >= 0.05 Uc
30067 | RSL1PRFU | Complementary | contact terminal arrangement | Separate
30068 | RSL1PRFU | Complementary | connections - terminals | Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) solid without cable end
30069 | RSL1PRFU | Complementary | tightening torque | 10...40 N.m
30070 | RSL1PRFU | Complementary | safety reliability data | B10d = 60000
30071 | RSL1PRFU | Complementary | clamping force | 10…40 N
30072 | RSL1PRFU | Complementary | control type | Without push-button
30073 | RSL1PRFU | Complementary | mounting support | 35 mm symmetrical DIN rail
30074 | RSL1PRFU | Complementary | device presentation | Complete product
30075 | RSL1PRFU | Environment | input voltage | 110 V AC/DC (input voltage limit: 88...126.5 V)
30076 | RSL1PRFU | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
30077 | RSL1PRFU | Environment | standards | EN/IEC 61810-1 UL 508 CSA C22.2 No 14
30078 | RSL1PRFU | Environment | product certifications | CSA GOST UL
30079 | RSL1PRFU | Environment | ambient air temperature for storage | -40…85 °C
30080 | RSL1PRFU | Environment | vibration resistance | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6
30081 | RSL1PRFU | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30082 | RSL1PRFU | Environment | shock resistance | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27
30083 | RSL1PRFU | Environment | ambient air temperature for operation | -40…70 °C
30084 | RSL1PRFU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
30085 | RSL1PRFU | Offer Sustainability | Toxic heavy metal free | Yes
30086 | RSL1PRFU | Offer Sustainability | Mercury free | Yes
30087 | RSL1PRFU | Offer Sustainability | RoHS exemption information | Yes
30088 | RSL1PRFU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
30089 | RSL1PRFU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
30090 | RSL1PRFU | Offer Sustainability | Circularity Profile | End of Life Information
30091 | RSL1PRFU | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
30092 | RSL1PRFU | Contractual warranty | Warranty | 18 months
30093 | RSL1PRPU | Main | range of product | Zelio Relay
30094 | RSL1PRPU | Main | series name | Interface relay
30095 | RSL1PRPU | Main | product or component type | Plug-in relay
30096 | RSL1PRPU | Main | device short name | RSL
30097 | RSL1PRPU | Main | contacts type and composition | 1 C/O
30098 | RSL1PRPU | Main | contact operation | Standard
30099 | RSL1PRPU | Main | [Uc] control circuit voltage | 60 V DC
30100 | RSL1PRPU | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C
30101 | RSL1PRPU | Main | status LED | With
30102 | RSL1PRPU | Main | shape of pin | Flat (PCB type)
30103 | RSL1PRPU | Complementary | fixing mode | Plastic compression spring
30104 | RSL1PRPU | Complementary | average resistance | 20500 Ohm network: DC at 23 °C +/- 10 %
30105 | RSL1PRPU | Complementary | [Ui] rated insulation voltage | 250 V conforming to EN/IEC 277 V conforming to cUL
30106 | RSL1PRPU | Complementary | [Uimp] rated impulse withstand voltage | 6 kV IEC
30107 | RSL1PRPU | Complementary | contacts material | Silver alloy (AgSnO2)
30108 | RSL1PRPU | Complementary | [Ie] rated operational current | 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL
30109 | RSL1PRPU | Complementary | minimum switching current | 100 mA
30110 | RSL1PRPU | Complementary | maximum switching voltage | 277 V
30111 | RSL1PRPU | Complementary | switching voltage | 12 V
30112 | RSL1PRPU | Complementary | maximum switching capacity | 1500 VA 150 W
30113 | RSL1PRPU | Complementary | minimum switching capacity | 120 mW
30114 | RSL1PRPU | Complementary | operating rate | <= 72000 cycles/hour no-load <= 360 cycles/hour under load
30115 | RSL1PRPU | Complementary | mechanical durability | 10000000 cycles
30116 | RSL1PRPU | Complementary | electrical durability | 60000 cycles for resistive load, 6 A at 250 V, AC-1
30117 | RSL1PRPU | Complementary | operating time | 5 ms reset 12 ms
30118 | RSL1PRPU | Complementary | reset time | 20 ms
30119 | RSL1PRPU | Complementary | marking | CE
30120 | RSL1PRPU | Complementary | protection category | RT III
30121 | RSL1PRPU | Complementary | test levels | Level A group mounting
30122 | RSL1PRPU | Complementary | operating position | Any position
30123 | RSL1PRPU | Complementary | height | 78.6 mm
30124 | RSL1PRPU | Complementary | width | 6.2 mm
30125 | RSL1PRPU | Complementary | depth | 101 mm
30126 | RSL1PRPU | Complementary | terminals description ISO n°1 | (A1-A2)CO (11-12-14)OC
30127 | RSL1PRPU | Complementary | sale per indivisible quantity | 10
30128 | RSL1PRPU | Complementary | net weight | 0.029 kg
30129 | RSL1PRPU | Complementary | load current | 6 A at 250 V AC 0.5 mm mounting distance
30130 | RSL1PRPU | Complementary | average coil consumption | 0.17 W, DC
30131 | RSL1PRPU | Complementary | drop-out voltage threshold | >= 0.05 Uc
30132 | RSL1PRPU | Complementary | contact terminal arrangement | Separate
30133 | RSL1PRPU | Complementary | connections - terminals | Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) solid without cable end
30134 | RSL1PRPU | Complementary | tightening torque | 10...40 N.m
30135 | RSL1PRPU | Complementary | safety reliability data | B10d = 60000
30136 | RSL1PRPU | Complementary | clamping force | 10…40 N
30137 | RSL1PRPU | Complementary | control type | Without push-button
30138 | RSL1PRPU | Complementary | mounting support | 35 mm symmetrical DIN rail
30139 | RSL1PRPU | Complementary | device presentation | Complete product
30140 | RSL1PRPU | Environment | input voltage | 230 V AC/DC (input voltage limit: 184...264.5 V)
30141 | RSL1PRPU | Environment | dielectric strength | 1000 V AC between contacts 4000 V AC between coil and contact
30142 | RSL1PRPU | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
30143 | RSL1PRPU | Environment | product certifications | GOST CSA UL
30144 | RSL1PRPU | Environment | ambient air temperature for storage | -40…85 °C
30145 | RSL1PRPU | Environment | vibration resistance | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6
30146 | RSL1PRPU | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30147 | RSL1PRPU | Environment | shock resistance | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27
30148 | RSL1PRPU | Environment | ambient air temperature for operation | -40…70 °C
30149 | RSL1PRPU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
30150 | RSL1PRPU | Offer Sustainability | Toxic heavy metal free | Yes
30151 | RSL1PRPU | Offer Sustainability | Mercury free | Yes
30152 | RSL1PRPU | Offer Sustainability | RoHS exemption information | Yes
30153 | RSL1PRPU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
30154 | RSL1PRPU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
30155 | RSL1PRPU | Offer Sustainability | Circularity Profile | End of Life Information
30156 | RSL1PRPU | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
30157 | RSL1PRPU | Contractual warranty | Warranty | 18 months
30158 | RSB1A120B7S | Main | range of product | Zelio Relay
30159 | RSB1A120B7S | Main | series name | Interface relay
30160 | RSB1A120B7S | Main | product or component type | Plug-in relay
30161 | RSB1A120B7S | Main | device short name | RSB
30162 | RSB1A120B7S | Main | contacts type and composition | 1 C/O
30163 | RSB1A120B7S | Main | contact operation | Standard
30164 | RSB1A120B7S | Main | [Uc] control circuit voltage | 24 V AC
30165 | RSB1A120B7S | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
30166 | RSB1A120B7S | Main | status LED | Without
30167 | RSB1A120B7S | Main | control type | Without push-button
30168 | RSB1A120B7S | Complementary | shape of pin | Flat
30169 | RSB1A120B7S | Complementary | average coil resistance | 400 Ohm network: AC at 20 °C +/- 15 %
30170 | RSB1A120B7S | Complementary | [Ue] rated operational voltage | 19.2...26.4 V AC 50 Hz 20.4...26.4 V AC 60 Hz
30171 | RSB1A120B7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30172 | RSB1A120B7S | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
30173 | RSB1A120B7S | Complementary | contacts material | Silver alloy (Ag/Ni)
30174 | RSB1A120B7S | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
30175 | RSB1A120B7S | Complementary | minimum switching current | 5 mA
30176 | RSB1A120B7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
30177 | RSB1A120B7S | Complementary | minimum switching voltage | 5 V
30178 | RSB1A120B7S | Complementary | maximum switching capacity | 3000 VA AC 336 W DC
30179 | RSB1A120B7S | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
30180 | RSB1A120B7S | Complementary | minimum switching capacity | 300 mW at 5 mA
30181 | RSB1A120B7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30182 | RSB1A120B7S | Complementary | mechanical durability | 30000000 cycles
30183 | RSB1A120B7S | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
30184 | RSB1A120B7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
30185 | RSB1A120B7S | Complementary | marking | CE
30186 | RSB1A120B7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
30187 | RSB1A120B7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
30188 | RSB1A120B7S | Complementary | safety reliability data | B10d = 100000
30189 | RSB1A120B7S | Complementary | protection category | RT I
30190 | RSB1A120B7S | Complementary | operating position | Any position
30191 | RSB1A120B7S | Complementary | sale per indivisible quantity | 10
30192 | RSB1A120B7S | Complementary | device presentation | Complete product
30193 | RSB1A120B7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30194 | RSB1A120B7S | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1
30195 | RSB1A120B7S | Environment | product certifications | UL CSA GOST
30196 | RSB1A120B7S | Environment | ambient air temperature for storage | -40…85 °C
30197 | RSB1A120B7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30198 | RSB1A120B7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30199 | RSB1A120B7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30200 | RSB1A120B7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30201 | RSB1A120B7S | Offer Sustainability | Sustainable offer status | Green Premium product
30202 | RSB1A120B7S | Offer Sustainability | REACh free of SVHC | Yes
30203 | RSB1A120B7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
30204 | RSB1A120B7S | Offer Sustainability | Toxic heavy metal free | Yes
30205 | RSB1A120B7S | Offer Sustainability | Mercury free | Yes
30206 | RSB1A120B7S | Offer Sustainability | RoHS exemption information | Yes
30207 | RSB1A120B7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration
30208 | RSB1A120B7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
30209 | RSB1A120B7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
30210 | RSB1A120B7S | Contractual warranty | Warranty | 18 months
30211 | RSB1A120BDS | Main | range of product | Zelio Relay
30212 | RSB1A120BDS | Main | series name | Interface relay
30213 | RSB1A120BDS | Main | product or component type | Plug-in relay
30214 | RSB1A120BDS | Main | device short name | RSB
30215 | RSB1A120BDS | Main | contacts type and composition | 1 C/O
30216 | RSB1A120BDS | Main | contact operation | Standard
30217 | RSB1A120BDS | Main | [Uc] control circuit voltage | 24 V DC
30218 | RSB1A120BDS | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
30219 | RSB1A120BDS | Main | status LED | Without
30220 | RSB1A120BDS | Main | control type | Without push-button
30221 | RSB1A120BDS | Complementary | shape of pin | Flat
30222 | RSB1A120BDS | Complementary | average coil resistance | 1440 Ohm network: DC at 20 °C +/- 10 %
30223 | RSB1A120BDS | Complementary | [Ue] rated operational voltage | 19.2...26.4 V DC
30224 | RSB1A120BDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30225 | RSB1A120BDS | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
30226 | RSB1A120BDS | Complementary | contacts material | Silver alloy (Ag/Ni)
30227 | RSB1A120BDS | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
30228 | RSB1A120BDS | Complementary | minimum switching current | 5 mA
30229 | RSB1A120BDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
30230 | RSB1A120BDS | Complementary | minimum switching voltage | 5 V
30231 | RSB1A120BDS | Complementary | maximum switching capacity | 3000 VA AC 336 W DC
30232 | RSB1A120BDS | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
30233 | RSB1A120BDS | Complementary | minimum switching capacity | 300 mW at 5 mA
30234 | RSB1A120BDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30235 | RSB1A120BDS | Complementary | mechanical durability | 30000000 cycles
30236 | RSB1A120BDS | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
30237 | RSB1A120BDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
30238 | RSB1A120BDS | Complementary | marking | CE
30239 | RSB1A120BDS | Complementary | average coil consumption | 0.45 W DC
30240 | RSB1A120BDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
30241 | RSB1A120BDS | Complementary | safety reliability data | B10d = 100000
30242 | RSB1A120BDS | Complementary | protection category | RT I
30243 | RSB1A120BDS | Complementary | operating position | Any position
30244 | RSB1A120BDS | Complementary | sale per indivisible quantity | 10
30245 | RSB1A120BDS | Complementary | device presentation | Complete product
30246 | RSB1A120BDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30247 | RSB1A120BDS | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1
30248 | RSB1A120BDS | Environment | product certifications | UL CSA GOST
30249 | RSB1A120BDS | Environment | ambient air temperature for storage | -40…85 °C
30250 | RSB1A120BDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30251 | RSB1A120BDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30252 | RSB1A120BDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30253 | RSB1A120BDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30254 | RSB1A120BDS | Offer Sustainability | Sustainable offer status | Green Premium product
30255 | RSB1A120BDS | Offer Sustainability | REACh free of SVHC | Yes
30256 | RSB1A120BDS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
30257 | RSB1A120BDS | Offer Sustainability | Toxic heavy metal free | Yes
30258 | RSB1A120BDS | Offer Sustainability | Mercury free | Yes
30259 | RSB1A120BDS | Offer Sustainability | RoHS exemption information | Yes
30260 | RSB1A120BDS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
30261 | RSB1A120BDS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
30262 | RSB1A120BDS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
30263 | RSB1A120BDS | Contractual warranty | Warranty | 18 months
30264 | RSB1A120E7S | Main | range of product | Zelio Relay
30265 | RSB1A120E7S | Main | series name | Interface relay
30266 | RSB1A120E7S | Main | product or component type | Plug-in relay
30267 | RSB1A120E7S | Main | device short name | RSB
30268 | RSB1A120E7S | Main | contacts type and composition | 1 C/O
30269 | RSB1A120E7S | Main | contact operation | Standard
30270 | RSB1A120E7S | Main | [Uc] control circuit voltage | 48 V AC
30271 | RSB1A120E7S | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
30272 | RSB1A120E7S | Main | status LED | Without
30273 | RSB1A120E7S | Complementary | shape of pin | Flat
30274 | RSB1A120E7S | Complementary | average coil resistance | 1550 Ohm network: AC at 20 °C +/- 15 %
30275 | RSB1A120E7S | Complementary | [Ue] rated operational voltage | 38.4...57.6 V AC 50 Hz 40.8...57.6 V AC 60 Hz
30276 | RSB1A120E7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30277 | RSB1A120E7S | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
30278 | RSB1A120E7S | Complementary | contacts material | Silver alloy (Ag/Ni)
30279 | RSB1A120E7S | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
30280 | RSB1A120E7S | Complementary | minimum switching current | 5 mA
30281 | RSB1A120E7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
30282 | RSB1A120E7S | Complementary | minimum switching voltage | 5 V
30283 | RSB1A120E7S | Complementary | maximum switching capacity | 3000 VA AC 336 W DC
30284 | RSB1A120E7S | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
30285 | RSB1A120E7S | Complementary | minimum switching capacity | 300 mW at 5 mA
30286 | RSB1A120E7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30287 | RSB1A120E7S | Complementary | mechanical durability | 30000000 cycles
30288 | RSB1A120E7S | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
30289 | RSB1A120E7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
30290 | RSB1A120E7S | Complementary | marking | CE
30291 | RSB1A120E7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
30292 | RSB1A120E7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
30293 | RSB1A120E7S | Complementary | safety reliability data | B10d = 100000
30294 | RSB1A120E7S | Complementary | protection category | RT I
30295 | RSB1A120E7S | Complementary | operating position | Any position
30296 | RSB1A120E7S | Complementary | sale per indivisible quantity | 10
30297 | RSB1A120E7S | Complementary | device presentation | Complete product
30298 | RSB1A120E7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30299 | RSB1A120E7S | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508
30300 | RSB1A120E7S | Environment | product certifications | UL CSA GOST
30301 | RSB1A120E7S | Environment | ambient air temperature for storage | -40…85 °C
30302 | RSB1A120E7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30303 | RSB1A120E7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30304 | RSB1A120E7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30305 | RSB1A120E7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30306 | RSB1A120E7S | Contractual warranty | Warranty | 18 months
30307 | RSB1A120EDS | Main | range of product | Zelio Relay
30308 | RSB1A120EDS | Main | series name | Interface relay
30309 | RSB1A120EDS | Main | product or component type | Plug-in relay
30310 | RSB1A120EDS | Main | device short name | RSB
30311 | RSB1A120EDS | Main | contacts type and composition | 1 C/O
30312 | RSB1A120EDS | Main | contact operation | Standard
30313 | RSB1A120EDS | Main | [Uc] control circuit voltage | 48 V DC
30314 | RSB1A120EDS | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
30315 | RSB1A120EDS | Main | status LED | Without
30316 | RSB1A120EDS | Complementary | shape of pin | Flat
30317 | RSB1A120EDS | Complementary | average coil resistance | 5700 Ohm network: DC at 20 °C +/- 10 %
30318 | RSB1A120EDS | Complementary | [Ue] rated operational voltage | 38.4...52.8 V DC
30319 | RSB1A120EDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30320 | RSB1A120EDS | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
30321 | RSB1A120EDS | Complementary | contacts material | Silver alloy (Ag/Ni)
30322 | RSB1A120EDS | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
30323 | RSB1A120EDS | Complementary | minimum switching current | 5 mA
30324 | RSB1A120EDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
30325 | RSB1A120EDS | Complementary | minimum switching voltage | 5 V
30326 | RSB1A120EDS | Complementary | maximum switching capacity | 3000 VA AC 336 W DC
30327 | RSB1A120EDS | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
30328 | RSB1A120EDS | Complementary | minimum switching capacity | 300 mW at 5 mA
30329 | RSB1A120EDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30330 | RSB1A120EDS | Complementary | mechanical durability | 30000000 cycles
30331 | RSB1A120EDS | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
30332 | RSB1A120EDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
30333 | RSB1A120EDS | Complementary | marking | CE
30334 | RSB1A120EDS | Complementary | average coil consumption | 0.45 W DC
30335 | RSB1A120EDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
30336 | RSB1A120EDS | Complementary | safety reliability data | B10d = 100000
30337 | RSB1A120EDS | Complementary | protection category | RT I
30338 | RSB1A120EDS | Complementary | operating position | Any position
30339 | RSB1A120EDS | Complementary | sale per indivisible quantity | 10
30340 | RSB1A120EDS | Complementary | device presentation | Complete product
30341 | RSB1A120EDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30342 | RSB1A120EDS | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
30343 | RSB1A120EDS | Environment | product certifications | UL GOST CSA
30344 | RSB1A120EDS | Environment | ambient air temperature for storage | -40…85 °C
30345 | RSB1A120EDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30346 | RSB1A120EDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30347 | RSB1A120EDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30348 | RSB1A120EDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30349 | RSB1A120EDS | Contractual warranty | Warranty | 18 months
30350 | RSB1A120F7S | Main | range of product | Zelio Relay
30351 | RSB1A120F7S | Main | series name | Interface relay
30352 | RSB1A120F7S | Main | product or component type | Plug-in relay
30353 | RSB1A120F7S | Main | device short name | RSB
30354 | RSB1A120F7S | Main | contacts type and composition | 1 C/O
30355 | RSB1A120F7S | Main | contact operation | Standard
30356 | RSB1A120F7S | Main | [Uc] control circuit voltage | 120 V AC
30357 | RSB1A120F7S | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
30358 | RSB1A120F7S | Main | status LED | Without
30359 | RSB1A120F7S | Main | control type | Without push-button
30360 | RSB1A120F7S | Complementary | shape of pin | Flat
30361 | RSB1A120F7S | Complementary | average coil resistance | 10200 Ohm network: AC at 20 °C +/- 15 %
30362 | RSB1A120F7S | Complementary | [Ue] rated operational voltage | 102...144 V AC 60 Hz 96...144 V AC 50 Hz
30363 | RSB1A120F7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30364 | RSB1A120F7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
30365 | RSB1A120F7S | Complementary | contacts material | Silver alloy (Ag/Ni)
30366 | RSB1A120F7S | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
30367 | RSB1A120F7S | Complementary | minimum switching current | 5 mA
30368 | RSB1A120F7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
30369 | RSB1A120F7S | Complementary | minimum switching voltage | 5 V
30370 | RSB1A120F7S | Complementary | maximum switching capacity | 3000 VA AC 336 W DC
30371 | RSB1A120F7S | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
30372 | RSB1A120F7S | Complementary | minimum switching capacity | 300 mW at 5 mA
30373 | RSB1A120F7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30374 | RSB1A120F7S | Complementary | mechanical durability | 30000000 cycles
30375 | RSB1A120F7S | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
30376 | RSB1A120F7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
30377 | RSB1A120F7S | Complementary | marking | CE
30378 | RSB1A120F7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
30379 | RSB1A120F7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
30380 | RSB1A120F7S | Complementary | safety reliability data | B10d = 100000
30381 | RSB1A120F7S | Complementary | protection category | RT I
30382 | RSB1A120F7S | Complementary | operating position | Any position
30383 | RSB1A120F7S | Complementary | sale per indivisible quantity | 10
30384 | RSB1A120F7S | Complementary | device presentation | Complete product
30385 | RSB1A120F7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30386 | RSB1A120F7S | Environment | standards | UL 508 EN/IEC 61810-1 CSA C22.2 No 14
30387 | RSB1A120F7S | Environment | product certifications | CSA GOST UL
30388 | RSB1A120F7S | Environment | ambient air temperature for storage | -40…85 °C
30389 | RSB1A120F7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30390 | RSB1A120F7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30391 | RSB1A120F7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30392 | RSB1A120F7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30393 | RSB1A120F7S | Offer Sustainability | Sustainable offer status | Green Premium product
30394 | RSB1A120F7S | Offer Sustainability | REACh free of SVHC | Yes
30395 | RSB1A120F7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
30396 | RSB1A120F7S | Offer Sustainability | Toxic heavy metal free | Yes
30397 | RSB1A120F7S | Offer Sustainability | Mercury free | Yes
30398 | RSB1A120F7S | Offer Sustainability | RoHS exemption information | Yes
30399 | RSB1A120F7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration
30400 | RSB1A120F7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
30401 | RSB1A120F7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
30402 | RSB1A120F7S | Contractual warranty | Warranty | 18 months
30403 | RSB1A120FDS | Main | range of product | Zelio Relay
30404 | RSB1A120FDS | Main | series name | Interface relay
30405 | RSB1A120FDS | Main | product or component type | Plug-in relay
30406 | RSB1A120FDS | Main | device short name | RSB
30407 | RSB1A120FDS | Main | contacts type and composition | 1 C/O
30408 | RSB1A120FDS | Main | contact operation | Standard
30409 | RSB1A120FDS | Main | [Uc] control circuit voltage | 110 V DC
30410 | RSB1A120FDS | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
30411 | RSB1A120FDS | Main | status LED | Without
30412 | RSB1A120FDS | Complementary | shape of pin | Flat
30413 | RSB1A120FDS | Complementary | average coil resistance | 25200 Ohm network: DC at 20 °C +/- 10 %
30414 | RSB1A120FDS | Complementary | [Ue] rated operational voltage | 88...121 V DC
30415 | RSB1A120FDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30416 | RSB1A120FDS | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
30417 | RSB1A120FDS | Complementary | contacts material | Silver alloy (Ag/Ni)
30418 | RSB1A120FDS | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
30419 | RSB1A120FDS | Complementary | minimum switching current | 5 mA
30420 | RSB1A120FDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
30421 | RSB1A120FDS | Complementary | minimum switching voltage | 5 V
30422 | RSB1A120FDS | Complementary | maximum switching capacity | 3000 VA AC 336 W DC
30423 | RSB1A120FDS | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
30424 | RSB1A120FDS | Complementary | minimum switching capacity | 300 mW at 5 mA
30425 | RSB1A120FDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30426 | RSB1A120FDS | Complementary | mechanical durability | 30000000 cycles
30427 | RSB1A120FDS | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
30428 | RSB1A120FDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
30429 | RSB1A120FDS | Complementary | marking | CE
30430 | RSB1A120FDS | Complementary | average coil consumption | 0.45 W DC
30431 | RSB1A120FDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
30432 | RSB1A120FDS | Complementary | safety reliability data | B10d = 100000
30433 | RSB1A120FDS | Complementary | protection category | RT I
30434 | RSB1A120FDS | Complementary | operating position | Any position
30435 | RSB1A120FDS | Complementary | sale per indivisible quantity | 10
30436 | RSB1A120FDS | Complementary | device presentation | Complete product
30437 | RSB1A120FDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30438 | RSB1A120FDS | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1
30439 | RSB1A120FDS | Environment | product certifications | UL CSA GOST
30440 | RSB1A120FDS | Environment | ambient air temperature for storage | -40…85 °C
30441 | RSB1A120FDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30442 | RSB1A120FDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30443 | RSB1A120FDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30444 | RSB1A120FDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30445 | RSB1A120FDS | Contractual warranty | Warranty | 18 months
30446 | RSB1A120JDS | Main | range of product | Zelio Relay
30447 | RSB1A120JDS | Main | series name | Interface relay
30448 | RSB1A120JDS | Main | product or component type | Plug-in relay
30449 | RSB1A120JDS | Main | device short name | RSB
30450 | RSB1A120JDS | Main | contacts type and composition | 1 C/O
30451 | RSB1A120JDS | Main | contact operation | Standard
30452 | RSB1A120JDS | Main | [Uc] control circuit voltage | 12 V DC
30453 | RSB1A120JDS | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
30454 | RSB1A120JDS | Main | status LED | Without
30455 | RSB1A120JDS | Main | control type | Without push-button
30456 | RSB1A120JDS | Complementary | shape of pin | Flat
30457 | RSB1A120JDS | Complementary | average coil resistance | 360 Ohm network: DC at 20 °C +/- 10 %
30458 | RSB1A120JDS | Complementary | [Ue] rated operational voltage | 9.6...13.2 V DC
30459 | RSB1A120JDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30460 | RSB1A120JDS | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
30461 | RSB1A120JDS | Complementary | contacts material | Silver alloy (Ag/Ni)
30462 | RSB1A120JDS | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
30463 | RSB1A120JDS | Complementary | minimum switching current | 5 mA
30464 | RSB1A120JDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
30465 | RSB1A120JDS | Complementary | minimum switching voltage | 5 V
30466 | RSB1A120JDS | Complementary | maximum switching capacity | 3000 VA AC 336 W DC
30467 | RSB1A120JDS | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
30468 | RSB1A120JDS | Complementary | minimum switching capacity | 300 mW at 5 mA
30469 | RSB1A120JDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30470 | RSB1A120JDS | Complementary | mechanical durability | 30000000 cycles
30471 | RSB1A120JDS | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
30472 | RSB1A120JDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
30473 | RSB1A120JDS | Complementary | marking | CE
30474 | RSB1A120JDS | Complementary | average coil consumption | 0.45 W DC
30475 | RSB1A120JDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
30476 | RSB1A120JDS | Complementary | safety reliability data | B10d = 100000
30477 | RSB1A120JDS | Complementary | protection category | RT I
30478 | RSB1A120JDS | Complementary | operating position | Any position
30479 | RSB1A120JDS | Complementary | sale per indivisible quantity | 10
30480 | RSB1A120JDS | Complementary | device presentation | Complete product
30481 | RSB1A120JDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30482 | RSB1A120JDS | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
30483 | RSB1A120JDS | Environment | product certifications | UL GOST CSA
30484 | RSB1A120JDS | Environment | ambient air temperature for storage | -40…85 °C
30485 | RSB1A120JDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30486 | RSB1A120JDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30487 | RSB1A120JDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30488 | RSB1A120JDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30489 | RSB1A120JDS | Offer Sustainability | Sustainable offer status | Green Premium product
30490 | RSB1A120JDS | Offer Sustainability | REACh free of SVHC | Yes
30491 | RSB1A120JDS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
30492 | RSB1A120JDS | Offer Sustainability | Toxic heavy metal free | Yes
30493 | RSB1A120JDS | Offer Sustainability | Mercury free | Yes
30494 | RSB1A120JDS | Offer Sustainability | RoHS exemption information | Yes
30495 | RSB1A120JDS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
30496 | RSB1A120JDS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
30497 | RSB1A120JDS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
30498 | RSB1A120JDS | Contractual warranty | Warranty | 18 months
30499 | RSB1A120P7S | Main | range of product | Zelio Relay
30500 | RSB1A120P7S | Main | series name | Interface relay
30501 | RSB1A120P7S | Main | product or component type | Plug-in relay
30502 | RSB1A120P7S | Main | device short name | RSB
30503 | RSB1A120P7S | Main | contacts type and composition | 1 C/O
30504 | RSB1A120P7S | Main | contact operation | Standard
30505 | RSB1A120P7S | Main | [Uc] control circuit voltage | 230 V AC
30506 | RSB1A120P7S | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
30507 | RSB1A120P7S | Main | status LED | Without
30508 | RSB1A120P7S | Main | control type | Without push-button
30509 | RSB1A120P7S | Complementary | shape of pin | Flat
30510 | RSB1A120P7S | Complementary | average coil resistance | 38500 Ohm network: AC at 20 °C +/- 15 %
30511 | RSB1A120P7S | Complementary | [Ue] rated operational voltage | 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz
30512 | RSB1A120P7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30513 | RSB1A120P7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
30514 | RSB1A120P7S | Complementary | contacts material | Silver alloy (Ag/Ni)
30515 | RSB1A120P7S | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
30516 | RSB1A120P7S | Complementary | minimum switching current | 5 mA
30517 | RSB1A120P7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
30518 | RSB1A120P7S | Complementary | minimum switching voltage | 5 V
30519 | RSB1A120P7S | Complementary | maximum switching capacity | 3000 VA AC 336 W DC
30520 | RSB1A120P7S | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
30521 | RSB1A120P7S | Complementary | minimum switching capacity | 300 mW at 5 mA
30522 | RSB1A120P7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30523 | RSB1A120P7S | Complementary | mechanical durability | 30000000 cycles
30524 | RSB1A120P7S | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
30525 | RSB1A120P7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
30526 | RSB1A120P7S | Complementary | marking | CE
30527 | RSB1A120P7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
30528 | RSB1A120P7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
30529 | RSB1A120P7S | Complementary | safety reliability data | B10d = 100000
30530 | RSB1A120P7S | Complementary | protection category | RT I
30531 | RSB1A120P7S | Complementary | operating position | Any position
30532 | RSB1A120P7S | Complementary | sale per indivisible quantity | 10
30533 | RSB1A120P7S | Complementary | device presentation | Complete product
30534 | RSB1A120P7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30535 | RSB1A120P7S | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
30536 | RSB1A120P7S | Environment | product certifications | CSA GOST UL
30537 | RSB1A120P7S | Environment | ambient air temperature for storage | -40…85 °C
30538 | RSB1A120P7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30539 | RSB1A120P7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30540 | RSB1A120P7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30541 | RSB1A120P7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30542 | RSB1A120P7S | Offer Sustainability | Sustainable offer status | Green Premium product
30543 | RSB1A120P7S | Offer Sustainability | REACh free of SVHC | Yes
30544 | RSB1A120P7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
30545 | RSB1A120P7S | Offer Sustainability | Toxic heavy metal free | Yes
30546 | RSB1A120P7S | Offer Sustainability | Mercury free | Yes
30547 | RSB1A120P7S | Offer Sustainability | RoHS exemption information | Yes
30548 | RSB1A120P7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration
30549 | RSB1A120P7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
30550 | RSB1A120P7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
30551 | RSB1A120P7S | Contractual warranty | Warranty | 18 months
30552 | RSB1A120U7S | Main | range of product | Zelio Relay
30553 | RSB1A120U7S | Main | series name | Interface relay
30554 | RSB1A120U7S | Main | product or component type | Plug-in relay
30555 | RSB1A120U7S | Main | device short name | RSB
30556 | RSB1A120U7S | Main | contacts type and composition | 1 C/O
30557 | RSB1A120U7S | Main | contact operation | Standard
30558 | RSB1A120U7S | Main | [Uc] control circuit voltage | 240 V AC
30559 | RSB1A120U7S | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
30560 | RSB1A120U7S | Main | status LED | Without
30561 | RSB1A120U7S | Complementary | shape of pin | Flat
30562 | RSB1A120U7S | Complementary | average coil resistance | 42500 Ohm network: AC at 20 °C +/- 15 %
30563 | RSB1A120U7S | Complementary | [Ue] rated operational voltage | 192...288 V AC 50 Hz 204...288 V AC 60 Hz
30564 | RSB1A120U7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30565 | RSB1A120U7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
30566 | RSB1A120U7S | Complementary | contacts material | Silver alloy (Ag/Ni)
30567 | RSB1A120U7S | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
30568 | RSB1A120U7S | Complementary | minimum switching current | 5 mA
30569 | RSB1A120U7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
30570 | RSB1A120U7S | Complementary | minimum switching voltage | 5 V
30571 | RSB1A120U7S | Complementary | maximum switching capacity | 3000 VA AC 336 W DC
30572 | RSB1A120U7S | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
30573 | RSB1A120U7S | Complementary | minimum switching capacity | 300 mW at 5 mA
30574 | RSB1A120U7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30575 | RSB1A120U7S | Complementary | mechanical durability | 30000000 cycles
30576 | RSB1A120U7S | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
30577 | RSB1A120U7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
30578 | RSB1A120U7S | Complementary | marking | CE
30579 | RSB1A120U7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
30580 | RSB1A120U7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
30581 | RSB1A120U7S | Complementary | safety reliability data | B10d = 100000
30582 | RSB1A120U7S | Complementary | protection category | RT I
30583 | RSB1A120U7S | Complementary | operating position | Any position
30584 | RSB1A120U7S | Complementary | sale per indivisible quantity | 10
30585 | RSB1A120U7S | Complementary | device presentation | Complete product
30586 | RSB1A120U7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30587 | RSB1A120U7S | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
30588 | RSB1A120U7S | Environment | product certifications | UL GOST CSA
30589 | RSB1A120U7S | Environment | ambient air temperature for storage | -40…85 °C
30590 | RSB1A120U7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30591 | RSB1A120U7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30592 | RSB1A120U7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30593 | RSB1A120U7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30594 | RSB1A120U7S | Contractual warranty | Warranty | 18 months
30595 | RSB1A120M7S | Main | range of product | Zelio Relay
30596 | RSB1A120M7S | Main | series name | Interface relay
30597 | RSB1A120M7S | Main | product or component type | Plug-in relay
30598 | RSB1A120M7S | Main | device short name | RSB
30599 | RSB1A120M7S | Main | contacts type and composition | 1 C/O
30600 | RSB1A120M7S | Main | contact operation | Standard
30601 | RSB1A120M7S | Main | [Uc] control circuit voltage | 220 V AC
30602 | RSB1A120M7S | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
30603 | RSB1A120M7S | Main | status LED | Without
30604 | RSB1A120M7S | Complementary | shape of pin | Flat
30605 | RSB1A120M7S | Complementary | average coil resistance | 35500 Ohm network: AC at 20 °C +/- 15 %
30606 | RSB1A120M7S | Complementary | [Ue] rated operational voltage | 176...264 V AC 50 Hz 187...264 V AC 60 Hz
30607 | RSB1A120M7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30608 | RSB1A120M7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
30609 | RSB1A120M7S | Complementary | contacts material | Silver alloy (Ag/Ni)
30610 | RSB1A120M7S | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
30611 | RSB1A120M7S | Complementary | minimum switching current | 5 mA
30612 | RSB1A120M7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
30613 | RSB1A120M7S | Complementary | minimum switching voltage | 5 V
30614 | RSB1A120M7S | Complementary | maximum switching capacity | 3000 VA AC 336 W DC
30615 | RSB1A120M7S | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
30616 | RSB1A120M7S | Complementary | minimum switching capacity | 300 mW at 5 mA
30617 | RSB1A120M7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30618 | RSB1A120M7S | Complementary | mechanical durability | 30000000 cycles
30619 | RSB1A120M7S | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
30620 | RSB1A120M7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
30621 | RSB1A120M7S | Complementary | marking | CE
30622 | RSB1A120M7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
30623 | RSB1A120M7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
30624 | RSB1A120M7S | Complementary | safety reliability data | B10d = 100000
30625 | RSB1A120M7S | Complementary | protection category | RT I
30626 | RSB1A120M7S | Complementary | operating position | Any position
30627 | RSB1A120M7S | Complementary | sale per indivisible quantity | 10
30628 | RSB1A120M7S | Complementary | device presentation | Complete product
30629 | RSB1A120M7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30630 | RSB1A120M7S | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1
30631 | RSB1A120M7S | Environment | product certifications | GOST CSA UL
30632 | RSB1A120M7S | Environment | ambient air temperature for storage | -40…85 °C
30633 | RSB1A120M7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30634 | RSB1A120M7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30635 | RSB1A120M7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30636 | RSB1A120M7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30637 | RSB1A120M7S | Offer Sustainability | Sustainable offer status | Green Premium product
30638 | RSB1A120M7S | Offer Sustainability | REACh free of SVHC | Yes
30639 | RSB1A120M7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
30640 | RSB1A120M7S | Offer Sustainability | Toxic heavy metal free | Yes
30641 | RSB1A120M7S | Offer Sustainability | Mercury free | Yes
30642 | RSB1A120M7S | Offer Sustainability | RoHS exemption information | Yes
30643 | RSB1A120M7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration
30644 | RSB1A120M7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
30645 | RSB1A120M7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
30646 | RSB1A120M7S | Contractual warranty | Warranty | 18 months
30647 | RSB1A120NDS | Main | range of product | Zelio Relay
30648 | RSB1A120NDS | Main | series name | Interface relay
30649 | RSB1A120NDS | Main | product or component type | Plug-in relay
30650 | RSB1A120NDS | Main | device short name | RSB
30651 | RSB1A120NDS | Main | contacts type and composition | 1 C/O
30652 | RSB1A120NDS | Main | contact operation | Standard
30653 | RSB1A120NDS | Main | [Uc] control circuit voltage | 60 V DC
30654 | RSB1A120NDS | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
30655 | RSB1A120NDS | Main | status LED | Without
30656 | RSB1A120NDS | Complementary | shape of pin | Flat
30657 | RSB1A120NDS | Complementary | average coil resistance | 7500 Ohm network: DC at 20 °C +/- 10 %
30658 | RSB1A120NDS | Complementary | [Ue] rated operational voltage | 48...66 V DC
30659 | RSB1A120NDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30660 | RSB1A120NDS | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
30661 | RSB1A120NDS | Complementary | contacts material | Silver alloy (Ag/Ni)
30662 | RSB1A120NDS | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
30663 | RSB1A120NDS | Complementary | minimum switching current | 5 mA
30664 | RSB1A120NDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
30665 | RSB1A120NDS | Complementary | minimum switching voltage | 5 V
30666 | RSB1A120NDS | Complementary | maximum switching capacity | 3000 VA AC 336 W DC
30667 | RSB1A120NDS | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
30668 | RSB1A120NDS | Complementary | minimum switching capacity | 300 mW at 5 mA
30669 | RSB1A120NDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30670 | RSB1A120NDS | Complementary | mechanical durability | 30000000 cycles
30671 | RSB1A120NDS | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
30672 | RSB1A120NDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
30673 | RSB1A120NDS | Complementary | marking | CE
30674 | RSB1A120NDS | Complementary | average coil consumption | 0.45 W DC
30675 | RSB1A120NDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
30676 | RSB1A120NDS | Complementary | safety reliability data | B10d = 100000
30677 | RSB1A120NDS | Complementary | protection category | RT I
30678 | RSB1A120NDS | Complementary | operating position | Any position
30679 | RSB1A120NDS | Complementary | sale per indivisible quantity | 10
30680 | RSB1A120NDS | Complementary | device presentation | Complete product
30681 | RSB1A120NDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30682 | RSB1A120NDS | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
30683 | RSB1A120NDS | Environment | product certifications | CSA UL GOST
30684 | RSB1A120NDS | Environment | ambient air temperature for storage | -40…85 °C
30685 | RSB1A120NDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30686 | RSB1A120NDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30687 | RSB1A120NDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30688 | RSB1A120NDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30689 | RSB1A120NDS | Contractual warranty | Warranty | 18 months
30690 | RSB1A120RDS | Main | range of product | Zelio Relay
30691 | RSB1A120RDS | Main | series name | Interface relay
30692 | RSB1A120RDS | Main | product or component type | Plug-in relay
30693 | RSB1A120RDS | Main | device short name | RSB
30694 | RSB1A120RDS | Main | contacts type and composition | 1 C/O
30695 | RSB1A120RDS | Main | contact operation | Standard
30696 | RSB1A120RDS | Main | [Uc] control circuit voltage | 6 V DC
30697 | RSB1A120RDS | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…40 °C
30698 | RSB1A120RDS | Main | status LED | Without
30699 | RSB1A120RDS | Complementary | shape of pin | Flat
30700 | RSB1A120RDS | Complementary | average coil resistance | 90 Ohm network: DC at 20 °C +/- 10 %
30701 | RSB1A120RDS | Complementary | [Ue] rated operational voltage | 4.8...6.6 V DC
30702 | RSB1A120RDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30703 | RSB1A120RDS | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
30704 | RSB1A120RDS | Complementary | contacts material | Silver alloy (Ag/Ni)
30705 | RSB1A120RDS | Complementary | [Ie] rated operational current | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC
30706 | RSB1A120RDS | Complementary | minimum switching current | 5 mA
30707 | RSB1A120RDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
30708 | RSB1A120RDS | Complementary | minimum switching voltage | 5 V
30709 | RSB1A120RDS | Complementary | maximum switching capacity | 3000 VA AC 336 W DC
30710 | RSB1A120RDS | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC
30711 | RSB1A120RDS | Complementary | minimum switching capacity | 300 mW at 5 mA
30712 | RSB1A120RDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30713 | RSB1A120RDS | Complementary | mechanical durability | 30000000 cycles
30714 | RSB1A120RDS | Complementary | electrical durability | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC
30715 | RSB1A120RDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
30716 | RSB1A120RDS | Complementary | marking | CE
30717 | RSB1A120RDS | Complementary | average coil consumption | 0.45 W DC
30718 | RSB1A120RDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
30719 | RSB1A120RDS | Complementary | safety reliability data | B10d = 100000
30720 | RSB1A120RDS | Complementary | protection category | RT I
30721 | RSB1A120RDS | Complementary | operating position | Any position
30722 | RSB1A120RDS | Complementary | sale per indivisible quantity | 10
30723 | RSB1A120RDS | Complementary | device presentation | Complete product
30724 | RSB1A120RDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30725 | RSB1A120RDS | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508
30726 | RSB1A120RDS | Environment | product certifications | GOST UL CSA
30727 | RSB1A120RDS | Environment | ambient air temperature for storage | -40…85 °C
30728 | RSB1A120RDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30729 | RSB1A120RDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30730 | RSB1A120RDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30731 | RSB1A120RDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30732 | RSB1A120RDS | Contractual warranty | Warranty | 18 months
30733 | RSB1A160B7S | Main | range of product | Zelio Relay
30734 | RSB1A160B7S | Main | series name | Interface relay
30735 | RSB1A160B7S | Main | product or component type | Plug-in relay
30736 | RSB1A160B7S | Main | device short name | RSB
30737 | RSB1A160B7S | Main | contacts type and composition | 1 C/O
30738 | RSB1A160B7S | Main | contact operation | Standard
30739 | RSB1A160B7S | Main | [Uc] control circuit voltage | 24 V AC
30740 | RSB1A160B7S | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
30741 | RSB1A160B7S | Main | status LED | Without
30742 | RSB1A160B7S | Main | control type | Without push-button
30743 | RSB1A160B7S | Complementary | shape of pin | Flat
30744 | RSB1A160B7S | Complementary | average coil resistance | 400 Ohm network: AC at 20 °C +/- 15 %
30745 | RSB1A160B7S | Complementary | [Ue] rated operational voltage | 19.2...26.4 V AC 50 Hz 20.4...26.4 V AC 60 Hz
30746 | RSB1A160B7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30747 | RSB1A160B7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
30748 | RSB1A160B7S | Complementary | contacts material | Silver alloy (Ag/Ni)
30749 | RSB1A160B7S | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
30750 | RSB1A160B7S | Complementary | minimum switching current | 5 mA
30751 | RSB1A160B7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
30752 | RSB1A160B7S | Complementary | minimum switching voltage | 5 V
30753 | RSB1A160B7S | Complementary | maximum switching capacity | 4000 VA AC 448 W DC
30754 | RSB1A160B7S | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
30755 | RSB1A160B7S | Complementary | minimum switching capacity | 300 mW at 5 mA
30756 | RSB1A160B7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30757 | RSB1A160B7S | Complementary | mechanical durability | 30000000 cycles
30758 | RSB1A160B7S | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
30759 | RSB1A160B7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
30760 | RSB1A160B7S | Complementary | marking | CE
30761 | RSB1A160B7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
30762 | RSB1A160B7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
30763 | RSB1A160B7S | Complementary | safety reliability data | B10d = 100000
30764 | RSB1A160B7S | Complementary | protection category | RT I
30765 | RSB1A160B7S | Complementary | operating position | Any position
30766 | RSB1A160B7S | Complementary | sale per indivisible quantity | 10
30767 | RSB1A160B7S | Complementary | device presentation | Complete product
30768 | RSB1A160B7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30769 | RSB1A160B7S | Environment | standards | UL 508 EN/IEC 61810-1 CSA C22.2 No 14
30770 | RSB1A160B7S | Environment | product certifications | UL GOST CSA
30771 | RSB1A160B7S | Environment | ambient air temperature for storage | -40…85 °C
30772 | RSB1A160B7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30773 | RSB1A160B7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30774 | RSB1A160B7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30775 | RSB1A160B7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30776 | RSB1A160B7S | Offer Sustainability | Sustainable offer status | Green Premium product
30777 | RSB1A160B7S | Offer Sustainability | REACh free of SVHC | Yes
30778 | RSB1A160B7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
30779 | RSB1A160B7S | Offer Sustainability | Toxic heavy metal free | Yes
30780 | RSB1A160B7S | Offer Sustainability | Mercury free | Yes
30781 | RSB1A160B7S | Offer Sustainability | RoHS exemption information | Yes
30782 | RSB1A160B7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration
30783 | RSB1A160B7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
30784 | RSB1A160B7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
30785 | RSB1A160B7S | Contractual warranty | Warranty | 18 months
30786 | RSB1A160BDS | Main | range of product | Zelio Relay
30787 | RSB1A160BDS | Main | series name | Interface relay
30788 | RSB1A160BDS | Main | product or component type | Plug-in relay
30789 | RSB1A160BDS | Main | device short name | RSB
30790 | RSB1A160BDS | Main | contacts type and composition | 1 C/O
30791 | RSB1A160BDS | Main | contact operation | Standard
30792 | RSB1A160BDS | Main | [Uc] control circuit voltage | 24 V DC
30793 | RSB1A160BDS | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
30794 | RSB1A160BDS | Main | status LED | Without
30795 | RSB1A160BDS | Main | control type | Without push-button
30796 | RSB1A160BDS | Complementary | shape of pin | Flat
30797 | RSB1A160BDS | Complementary | average coil resistance | 1440 Ohm network: DC at 20 °C +/- 10 %
30798 | RSB1A160BDS | Complementary | [Ue] rated operational voltage | 19.2...26.4 V DC
30799 | RSB1A160BDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30800 | RSB1A160BDS | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
30801 | RSB1A160BDS | Complementary | contacts material | Silver alloy (Ag/Ni)
30802 | RSB1A160BDS | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
30803 | RSB1A160BDS | Complementary | minimum switching current | 5 mA
30804 | RSB1A160BDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
30805 | RSB1A160BDS | Complementary | minimum switching voltage | 5 V
30806 | RSB1A160BDS | Complementary | maximum switching capacity | 4000 VA AC 448 W DC
30807 | RSB1A160BDS | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
30808 | RSB1A160BDS | Complementary | minimum switching capacity | 300 mW at 5 mA
30809 | RSB1A160BDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30810 | RSB1A160BDS | Complementary | mechanical durability | 30000000 cycles
30811 | RSB1A160BDS | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
30812 | RSB1A160BDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
30813 | RSB1A160BDS | Complementary | marking | CE
30814 | RSB1A160BDS | Complementary | average coil consumption | 0.45 W DC
30815 | RSB1A160BDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
30816 | RSB1A160BDS | Complementary | safety reliability data | B10d = 100000
30817 | RSB1A160BDS | Complementary | protection category | RT I
30818 | RSB1A160BDS | Complementary | operating position | Any position
30819 | RSB1A160BDS | Complementary | sale per indivisible quantity | 10
30820 | RSB1A160BDS | Complementary | device presentation | Complete product
30821 | RSB1A160BDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30822 | RSB1A160BDS | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508
30823 | RSB1A160BDS | Environment | product certifications | CSA GOST UL
30824 | RSB1A160BDS | Environment | ambient air temperature for storage | -40…85 °C
30825 | RSB1A160BDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30826 | RSB1A160BDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30827 | RSB1A160BDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30828 | RSB1A160BDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30829 | RSB1A160BDS | Offer Sustainability | Sustainable offer status | Green Premium product
30830 | RSB1A160BDS | Offer Sustainability | REACh free of SVHC | Yes
30831 | RSB1A160BDS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
30832 | RSB1A160BDS | Offer Sustainability | Toxic heavy metal free | Yes
30833 | RSB1A160BDS | Offer Sustainability | Mercury free | Yes
30834 | RSB1A160BDS | Offer Sustainability | RoHS exemption information | Yes
30835 | RSB1A160BDS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
30836 | RSB1A160BDS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
30837 | RSB1A160BDS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
30838 | RSB1A160BDS | Contractual warranty | Warranty | 18 months
30839 | RSB1A160E7S | Main | range of product | Zelio Relay
30840 | RSB1A160E7S | Main | series name | Interface relay
30841 | RSB1A160E7S | Main | product or component type | Plug-in relay
30842 | RSB1A160E7S | Main | device short name | RSB
30843 | RSB1A160E7S | Main | contacts type and composition | 1 C/O
30844 | RSB1A160E7S | Main | contact operation | Standard
30845 | RSB1A160E7S | Main | [Uc] control circuit voltage | 48 V AC
30846 | RSB1A160E7S | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
30847 | RSB1A160E7S | Main | status LED | Without
30848 | RSB1A160E7S | Complementary | shape of pin | Flat
30849 | RSB1A160E7S | Complementary | average coil resistance | 1550 Ohm network: AC at 20 °C +/- 15 %
30850 | RSB1A160E7S | Complementary | [Ue] rated operational voltage | 38.4...57.6 V AC 50 Hz 40.8...57.6 V AC 60 Hz
30851 | RSB1A160E7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30852 | RSB1A160E7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
30853 | RSB1A160E7S | Complementary | contacts material | Silver alloy (Ag/Ni)
30854 | RSB1A160E7S | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
30855 | RSB1A160E7S | Complementary | minimum switching current | 5 mA
30856 | RSB1A160E7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
30857 | RSB1A160E7S | Complementary | minimum switching voltage | 5 V
30858 | RSB1A160E7S | Complementary | maximum switching capacity | 4000 VA AC 448 W DC
30859 | RSB1A160E7S | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
30860 | RSB1A160E7S | Complementary | minimum switching capacity | 300 mW at 5 mA
30861 | RSB1A160E7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30862 | RSB1A160E7S | Complementary | mechanical durability | 30000000 cycles
30863 | RSB1A160E7S | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
30864 | RSB1A160E7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
30865 | RSB1A160E7S | Complementary | marking | CE
30866 | RSB1A160E7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
30867 | RSB1A160E7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
30868 | RSB1A160E7S | Complementary | safety reliability data | B10d = 100000
30869 | RSB1A160E7S | Complementary | protection category | RT I
30870 | RSB1A160E7S | Complementary | operating position | Any position
30871 | RSB1A160E7S | Complementary | sale per indivisible quantity | 10
30872 | RSB1A160E7S | Complementary | device presentation | Complete product
30873 | RSB1A160E7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30874 | RSB1A160E7S | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508
30875 | RSB1A160E7S | Environment | product certifications | GOST CSA UL
30876 | RSB1A160E7S | Environment | ambient air temperature for storage | -40…85 °C
30877 | RSB1A160E7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30878 | RSB1A160E7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30879 | RSB1A160E7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30880 | RSB1A160E7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30881 | RSB1A160E7S | Offer Sustainability | Sustainable offer status | Green Premium product
30882 | RSB1A160E7S | Offer Sustainability | REACh free of SVHC | Yes
30883 | RSB1A160E7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
30884 | RSB1A160E7S | Offer Sustainability | Toxic heavy metal free | Yes
30885 | RSB1A160E7S | Offer Sustainability | Mercury free | Yes
30886 | RSB1A160E7S | Offer Sustainability | RoHS exemption information | Yes
30887 | RSB1A160E7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration
30888 | RSB1A160E7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
30889 | RSB1A160E7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
30890 | RSB1A160E7S | Contractual warranty | Warranty | 18 months
30891 | RSB1A160EDS | Main | range of product | Zelio Relay
30892 | RSB1A160EDS | Main | series name | Interface relay
30893 | RSB1A160EDS | Main | product or component type | Plug-in relay
30894 | RSB1A160EDS | Main | device short name | RSB
30895 | RSB1A160EDS | Main | contacts type and composition | 1 C/O
30896 | RSB1A160EDS | Main | contact operation | Standard
30897 | RSB1A160EDS | Main | [Uc] control circuit voltage | 48 V DC
30898 | RSB1A160EDS | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
30899 | RSB1A160EDS | Main | status LED | Without
30900 | RSB1A160EDS | Complementary | shape of pin | Flat
30901 | RSB1A160EDS | Complementary | average coil resistance | 5700 Ohm network: DC at 20 °C +/- 10 %
30902 | RSB1A160EDS | Complementary | [Ue] rated operational voltage | 38.4...52.8 V DC
30903 | RSB1A160EDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30904 | RSB1A160EDS | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
30905 | RSB1A160EDS | Complementary | contacts material | Silver alloy (Ag/Ni)
30906 | RSB1A160EDS | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
30907 | RSB1A160EDS | Complementary | minimum switching current | 5 mA
30908 | RSB1A160EDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
30909 | RSB1A160EDS | Complementary | minimum switching voltage | 5 V
30910 | RSB1A160EDS | Complementary | maximum switching capacity | 4000 VA AC 448 W DC
30911 | RSB1A160EDS | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
30912 | RSB1A160EDS | Complementary | minimum switching capacity | 300 mW at 5 mA
30913 | RSB1A160EDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30914 | RSB1A160EDS | Complementary | mechanical durability | 30000000 cycles
30915 | RSB1A160EDS | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
30916 | RSB1A160EDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
30917 | RSB1A160EDS | Complementary | marking | CE
30918 | RSB1A160EDS | Complementary | average coil consumption | 0.45 W DC
30919 | RSB1A160EDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
30920 | RSB1A160EDS | Complementary | safety reliability data | B10d = 100000
30921 | RSB1A160EDS | Complementary | protection category | RT I
30922 | RSB1A160EDS | Complementary | operating position | Any position
30923 | RSB1A160EDS | Complementary | sale per indivisible quantity | 10
30924 | RSB1A160EDS | Complementary | device presentation | Complete product
30925 | RSB1A160EDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30926 | RSB1A160EDS | Environment | standards | EN/IEC 61810-1 UL 508 CSA C22.2 No 14
30927 | RSB1A160EDS | Environment | product certifications | CSA UL GOST
30928 | RSB1A160EDS | Environment | ambient air temperature for storage | -40…85 °C
30929 | RSB1A160EDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30930 | RSB1A160EDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30931 | RSB1A160EDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30932 | RSB1A160EDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30933 | RSB1A160EDS | Contractual warranty | Warranty | 18 months
30934 | RSB1A160F7S | Main | range of product | Zelio Relay
30935 | RSB1A160F7S | Main | series name | Interface relay
30936 | RSB1A160F7S | Main | product or component type | Plug-in relay
30937 | RSB1A160F7S | Main | device short name | RSB
30938 | RSB1A160F7S | Main | contacts type and composition | 1 C/O
30939 | RSB1A160F7S | Main | contact operation | Standard
30940 | RSB1A160F7S | Main | [Uc] control circuit voltage | 120 V AC
30941 | RSB1A160F7S | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
30942 | RSB1A160F7S | Main | status LED | Without
30943 | RSB1A160F7S | Main | control type | Without push-button
30944 | RSB1A160F7S | Complementary | shape of pin | Flat
30945 | RSB1A160F7S | Complementary | average coil resistance | 10200 Ohm network: AC at 20 °C +/- 15 %
30946 | RSB1A160F7S | Complementary | [Ue] rated operational voltage | 102...144 V AC 60 Hz 96...144 V AC 50 Hz
30947 | RSB1A160F7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
30948 | RSB1A160F7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
30949 | RSB1A160F7S | Complementary | contacts material | Silver alloy (Ag/Ni)
30950 | RSB1A160F7S | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
30951 | RSB1A160F7S | Complementary | minimum switching current | 5 mA
30952 | RSB1A160F7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
30953 | RSB1A160F7S | Complementary | minimum switching voltage | 5 V
30954 | RSB1A160F7S | Complementary | maximum switching capacity | 4000 VA AC 448 W DC
30955 | RSB1A160F7S | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
30956 | RSB1A160F7S | Complementary | minimum switching capacity | 300 mW at 5 mA
30957 | RSB1A160F7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
30958 | RSB1A160F7S | Complementary | mechanical durability | 30000000 cycles
30959 | RSB1A160F7S | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
30960 | RSB1A160F7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
30961 | RSB1A160F7S | Complementary | marking | CE
30962 | RSB1A160F7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
30963 | RSB1A160F7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
30964 | RSB1A160F7S | Complementary | safety reliability data | B10d = 100000
30965 | RSB1A160F7S | Complementary | protection category | RT I
30966 | RSB1A160F7S | Complementary | operating position | Any position
30967 | RSB1A160F7S | Complementary | sale per indivisible quantity | 10
30968 | RSB1A160F7S | Complementary | device presentation | Complete product
30969 | RSB1A160F7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
30970 | RSB1A160F7S | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
30971 | RSB1A160F7S | Environment | product certifications | UL CSA GOST
30972 | RSB1A160F7S | Environment | ambient air temperature for storage | -40…85 °C
30973 | RSB1A160F7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
30974 | RSB1A160F7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
30975 | RSB1A160F7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
30976 | RSB1A160F7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
30977 | RSB1A160F7S | Offer Sustainability | Sustainable offer status | Green Premium product
30978 | RSB1A160F7S | Offer Sustainability | REACh free of SVHC | Yes
30979 | RSB1A160F7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
30980 | RSB1A160F7S | Offer Sustainability | Toxic heavy metal free | Yes
30981 | RSB1A160F7S | Offer Sustainability | Mercury free | Yes
30982 | RSB1A160F7S | Offer Sustainability | RoHS exemption information | Yes
30983 | RSB1A160F7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration
30984 | RSB1A160F7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
30985 | RSB1A160F7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
30986 | RSB1A160F7S | Contractual warranty | Warranty | 18 months
30987 | RSB1A160FDS | Main | range of product | Zelio Relay
30988 | RSB1A160FDS | Main | series name | Interface relay
30989 | RSB1A160FDS | Main | product or component type | Plug-in relay
30990 | RSB1A160FDS | Main | device short name | RSB
30991 | RSB1A160FDS | Main | contacts type and composition | 1 C/O
30992 | RSB1A160FDS | Main | contact operation | Standard
30993 | RSB1A160FDS | Main | [Uc] control circuit voltage | 110 V DC
30994 | RSB1A160FDS | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
30995 | RSB1A160FDS | Main | status LED | Without
30996 | RSB1A160FDS | Complementary | shape of pin | Flat
30997 | RSB1A160FDS | Complementary | average coil resistance | 25200 Ohm network: DC at 20 °C +/- 10 %
30998 | RSB1A160FDS | Complementary | [Ue] rated operational voltage | 88...121 V DC
30999 | RSB1A160FDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31000 | RSB1A160FDS | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
31001 | RSB1A160FDS | Complementary | contacts material | Silver alloy (Ag/Ni)
31002 | RSB1A160FDS | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
31003 | RSB1A160FDS | Complementary | minimum switching current | 5 mA
31004 | RSB1A160FDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
31005 | RSB1A160FDS | Complementary | minimum switching voltage | 5 V
31006 | RSB1A160FDS | Complementary | maximum switching capacity | 4000 VA AC 448 W DC
31007 | RSB1A160FDS | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
31008 | RSB1A160FDS | Complementary | minimum switching capacity | 300 mW at 5 mA
31009 | RSB1A160FDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31010 | RSB1A160FDS | Complementary | mechanical durability | 30000000 cycles
31011 | RSB1A160FDS | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
31012 | RSB1A160FDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
31013 | RSB1A160FDS | Complementary | marking | CE
31014 | RSB1A160FDS | Complementary | average coil consumption | 0.45 W DC
31015 | RSB1A160FDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
31016 | RSB1A160FDS | Complementary | safety reliability data | B10d = 100000
31017 | RSB1A160FDS | Complementary | protection category | RT I
31018 | RSB1A160FDS | Complementary | operating position | Any position
31019 | RSB1A160FDS | Complementary | sale per indivisible quantity | 10
31020 | RSB1A160FDS | Complementary | device presentation | Complete product
31021 | RSB1A160FDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31022 | RSB1A160FDS | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
31023 | RSB1A160FDS | Environment | product certifications | GOST UL CSA
31024 | RSB1A160FDS | Environment | ambient air temperature for storage | -40…85 °C
31025 | RSB1A160FDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31026 | RSB1A160FDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31027 | RSB1A160FDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31028 | RSB1A160FDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31029 | RSB1A160FDS | Contractual warranty | Warranty | 18 months
31030 | RSB1A160JDS | Main | range of product | Zelio Relay
31031 | RSB1A160JDS | Main | series name | Interface relay
31032 | RSB1A160JDS | Main | product or component type | Plug-in relay
31033 | RSB1A160JDS | Main | device short name | RSB
31034 | RSB1A160JDS | Main | contacts type and composition | 1 C/O
31035 | RSB1A160JDS | Main | contact operation | Standard
31036 | RSB1A160JDS | Main | [Uc] control circuit voltage | 12 V DC
31037 | RSB1A160JDS | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
31038 | RSB1A160JDS | Main | status LED | Without
31039 | RSB1A160JDS | Main | control type | Without push-button
31040 | RSB1A160JDS | Complementary | shape of pin | Flat
31041 | RSB1A160JDS | Complementary | average coil resistance | 360 Ohm network: DC at 20 °C +/- 10 %
31042 | RSB1A160JDS | Complementary | [Ue] rated operational voltage | 9.6...13.2 V DC
31043 | RSB1A160JDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31044 | RSB1A160JDS | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
31045 | RSB1A160JDS | Complementary | contacts material | Silver alloy (Ag/Ni)
31046 | RSB1A160JDS | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
31047 | RSB1A160JDS | Complementary | minimum switching current | 5 mA
31048 | RSB1A160JDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
31049 | RSB1A160JDS | Complementary | minimum switching voltage | 5 V
31050 | RSB1A160JDS | Complementary | maximum switching capacity | 4000 VA AC 448 W DC
31051 | RSB1A160JDS | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
31052 | RSB1A160JDS | Complementary | minimum switching capacity | 300 mW at 5 mA
31053 | RSB1A160JDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31054 | RSB1A160JDS | Complementary | mechanical durability | 30000000 cycles
31055 | RSB1A160JDS | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
31056 | RSB1A160JDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
31057 | RSB1A160JDS | Complementary | marking | CE
31058 | RSB1A160JDS | Complementary | average coil consumption | 0.45 W DC
31059 | RSB1A160JDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
31060 | RSB1A160JDS | Complementary | safety reliability data | B10d = 100000
31061 | RSB1A160JDS | Complementary | protection category | RT I
31062 | RSB1A160JDS | Complementary | operating position | Any position
31063 | RSB1A160JDS | Complementary | sale per indivisible quantity | 10
31064 | RSB1A160JDS | Complementary | device presentation | Complete product
31065 | RSB1A160JDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31066 | RSB1A160JDS | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
31067 | RSB1A160JDS | Environment | product certifications | GOST UL CSA
31068 | RSB1A160JDS | Environment | ambient air temperature for storage | -40…85 °C
31069 | RSB1A160JDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31070 | RSB1A160JDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31071 | RSB1A160JDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31072 | RSB1A160JDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31073 | RSB1A160JDS | Offer Sustainability | Sustainable offer status | Green Premium product
31074 | RSB1A160JDS | Offer Sustainability | REACh free of SVHC | Yes
31075 | RSB1A160JDS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
31076 | RSB1A160JDS | Offer Sustainability | Toxic heavy metal free | Yes
31077 | RSB1A160JDS | Offer Sustainability | Mercury free | Yes
31078 | RSB1A160JDS | Offer Sustainability | RoHS exemption information | Yes
31079 | RSB1A160JDS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
31080 | RSB1A160JDS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
31081 | RSB1A160JDS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
31082 | RSB1A160JDS | Contractual warranty | Warranty | 18 months
31083 | RSB1A160P7S | Main | range of product | Zelio Relay
31084 | RSB1A160P7S | Main | series name | Interface relay
31085 | RSB1A160P7S | Main | product or component type | Plug-in relay
31086 | RSB1A160P7S | Main | device short name | RSB
31087 | RSB1A160P7S | Main | contacts type and composition | 1 C/O
31088 | RSB1A160P7S | Main | contact operation | Standard
31089 | RSB1A160P7S | Main | [Uc] control circuit voltage | 230 V AC
31090 | RSB1A160P7S | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
31091 | RSB1A160P7S | Main | status LED | Without
31092 | RSB1A160P7S | Main | control type | Without push-button
31093 | RSB1A160P7S | Complementary | shape of pin | Flat
31094 | RSB1A160P7S | Complementary | average coil resistance | 38500 Ohm network: AC at 20 °C +/- 15 %
31095 | RSB1A160P7S | Complementary | [Ue] rated operational voltage | 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz
31096 | RSB1A160P7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31097 | RSB1A160P7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
31098 | RSB1A160P7S | Complementary | contacts material | Silver alloy (Ag/Ni)
31099 | RSB1A160P7S | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
31100 | RSB1A160P7S | Complementary | minimum switching current | 5 mA
31101 | RSB1A160P7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
31102 | RSB1A160P7S | Complementary | minimum switching voltage | 5 V
31103 | RSB1A160P7S | Complementary | maximum switching capacity | 4000 VA AC 448 W DC
31104 | RSB1A160P7S | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
31105 | RSB1A160P7S | Complementary | minimum switching capacity | 300 mW at 5 mA
31106 | RSB1A160P7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31107 | RSB1A160P7S | Complementary | mechanical durability | 30000000 cycles
31108 | RSB1A160P7S | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
31109 | RSB1A160P7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
31110 | RSB1A160P7S | Complementary | marking | CE
31111 | RSB1A160P7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
31112 | RSB1A160P7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
31113 | RSB1A160P7S | Complementary | safety reliability data | B10d = 100000
31114 | RSB1A160P7S | Complementary | protection category | RT I
31115 | RSB1A160P7S | Complementary | operating position | Any position
31116 | RSB1A160P7S | Complementary | sale per indivisible quantity | 10
31117 | RSB1A160P7S | Complementary | device presentation | Complete product
31118 | RSB1A160P7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31119 | RSB1A160P7S | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
31120 | RSB1A160P7S | Environment | product certifications | CSA UL GOST
31121 | RSB1A160P7S | Environment | ambient air temperature for storage | -40…85 °C
31122 | RSB1A160P7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31123 | RSB1A160P7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31124 | RSB1A160P7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31125 | RSB1A160P7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31126 | RSB1A160P7S | Offer Sustainability | Sustainable offer status | Green Premium product
31127 | RSB1A160P7S | Offer Sustainability | REACh free of SVHC | Yes
31128 | RSB1A160P7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
31129 | RSB1A160P7S | Offer Sustainability | Toxic heavy metal free | Yes
31130 | RSB1A160P7S | Offer Sustainability | Mercury free | Yes
31131 | RSB1A160P7S | Offer Sustainability | RoHS exemption information | Yes
31132 | RSB1A160P7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration
31133 | RSB1A160P7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
31134 | RSB1A160P7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
31135 | RSB1A160P7S | Contractual warranty | Warranty | 18 months
31136 | RSB1A160U7S | Main | range of product | Zelio Relay
31137 | RSB1A160U7S | Main | series name | Interface relay
31138 | RSB1A160U7S | Main | product or component type | Plug-in relay
31139 | RSB1A160U7S | Main | device short name | RSB
31140 | RSB1A160U7S | Main | contacts type and composition | 1 C/O
31141 | RSB1A160U7S | Main | contact operation | Standard
31142 | RSB1A160U7S | Main | [Uc] control circuit voltage | 240 V AC
31143 | RSB1A160U7S | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
31144 | RSB1A160U7S | Main | status LED | Without
31145 | RSB1A160U7S | Complementary | shape of pin | Flat
31146 | RSB1A160U7S | Complementary | average coil resistance | 42500 Ohm network: AC at 20 °C +/- 15 %
31147 | RSB1A160U7S | Complementary | [Ue] rated operational voltage | 192...288 V AC 50 Hz 204...288 V AC 60 Hz
31148 | RSB1A160U7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31149 | RSB1A160U7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
31150 | RSB1A160U7S | Complementary | contacts material | Silver alloy (Ag/Ni)
31151 | RSB1A160U7S | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
31152 | RSB1A160U7S | Complementary | minimum switching current | 5 mA
31153 | RSB1A160U7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
31154 | RSB1A160U7S | Complementary | minimum switching voltage | 5 V
31155 | RSB1A160U7S | Complementary | maximum switching capacity | 4000 VA AC 448 W DC
31156 | RSB1A160U7S | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
31157 | RSB1A160U7S | Complementary | minimum switching capacity | 300 mW at 5 mA
31158 | RSB1A160U7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31159 | RSB1A160U7S | Complementary | mechanical durability | 30000000 cycles
31160 | RSB1A160U7S | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
31161 | RSB1A160U7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
31162 | RSB1A160U7S | Complementary | marking | CE
31163 | RSB1A160U7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
31164 | RSB1A160U7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
31165 | RSB1A160U7S | Complementary | safety reliability data | B10d = 100000
31166 | RSB1A160U7S | Complementary | protection category | RT I
31167 | RSB1A160U7S | Complementary | operating position | Any position
31168 | RSB1A160U7S | Complementary | sale per indivisible quantity | 10
31169 | RSB1A160U7S | Complementary | device presentation | Complete product
31170 | RSB1A160U7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31171 | RSB1A160U7S | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
31172 | RSB1A160U7S | Environment | product certifications | GOST CSA UL
31173 | RSB1A160U7S | Environment | ambient air temperature for storage | -40…85 °C
31174 | RSB1A160U7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31175 | RSB1A160U7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31176 | RSB1A160U7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31177 | RSB1A160U7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31178 | RSB1A160U7S | Contractual warranty | Warranty | 18 months
31179 | RSB1A160M7S | Main | range of product | Zelio Relay
31180 | RSB1A160M7S | Main | series name | Interface relay
31181 | RSB1A160M7S | Main | product or component type | Plug-in relay
31182 | RSB1A160M7S | Main | device short name | RSB
31183 | RSB1A160M7S | Main | contacts type and composition | 1 C/O
31184 | RSB1A160M7S | Main | contact operation | Standard
31185 | RSB1A160M7S | Main | [Uc] control circuit voltage | 220 V AC
31186 | RSB1A160M7S | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
31187 | RSB1A160M7S | Main | status LED | Without
31188 | RSB1A160M7S | Complementary | shape of pin | Flat
31189 | RSB1A160M7S | Complementary | average coil resistance | 35500 Ohm network: AC at 20 °C +/- 15 %
31190 | RSB1A160M7S | Complementary | [Ue] rated operational voltage | 176...264 V AC 50 Hz 187...264 V AC 60 Hz
31191 | RSB1A160M7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31192 | RSB1A160M7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
31193 | RSB1A160M7S | Complementary | contacts material | Silver alloy (Ag/Ni)
31194 | RSB1A160M7S | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
31195 | RSB1A160M7S | Complementary | minimum switching current | 5 mA
31196 | RSB1A160M7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
31197 | RSB1A160M7S | Complementary | minimum switching voltage | 5 V
31198 | RSB1A160M7S | Complementary | maximum switching capacity | 4000 VA AC 448 W DC
31199 | RSB1A160M7S | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
31200 | RSB1A160M7S | Complementary | minimum switching capacity | 300 mW at 5 mA
31201 | RSB1A160M7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31202 | RSB1A160M7S | Complementary | mechanical durability | 30000000 cycles
31203 | RSB1A160M7S | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
31204 | RSB1A160M7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
31205 | RSB1A160M7S | Complementary | marking | CE
31206 | RSB1A160M7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
31207 | RSB1A160M7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
31208 | RSB1A160M7S | Complementary | safety reliability data | B10d = 100000
31209 | RSB1A160M7S | Complementary | protection category | RT I
31210 | RSB1A160M7S | Complementary | operating position | Any position
31211 | RSB1A160M7S | Complementary | sale per indivisible quantity | 10
31212 | RSB1A160M7S | Complementary | device presentation | Complete product
31213 | RSB1A160M7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31214 | RSB1A160M7S | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
31215 | RSB1A160M7S | Environment | product certifications | CSA UL GOST
31216 | RSB1A160M7S | Environment | ambient air temperature for storage | -40…85 °C
31217 | RSB1A160M7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31218 | RSB1A160M7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31219 | RSB1A160M7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31220 | RSB1A160M7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31221 | RSB1A160M7S | Offer Sustainability | Sustainable offer status | Green Premium product
31222 | RSB1A160M7S | Offer Sustainability | REACh free of SVHC | Yes
31223 | RSB1A160M7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
31224 | RSB1A160M7S | Offer Sustainability | Toxic heavy metal free | Yes
31225 | RSB1A160M7S | Offer Sustainability | Mercury free | Yes
31226 | RSB1A160M7S | Offer Sustainability | RoHS exemption information | Yes
31227 | RSB1A160M7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration
31228 | RSB1A160M7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
31229 | RSB1A160M7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
31230 | RSB1A160M7S | Contractual warranty | Warranty | 18 months
31231 | RSB1A160NDS | Main | range of product | Zelio Relay
31232 | RSB1A160NDS | Main | series name | Interface relay
31233 | RSB1A160NDS | Main | product or component type | Plug-in relay
31234 | RSB1A160NDS | Main | device short name | RSB
31235 | RSB1A160NDS | Main | contacts type and composition | 1 C/O
31236 | RSB1A160NDS | Main | contact operation | Standard
31237 | RSB1A160NDS | Main | [Uc] control circuit voltage | 60 V DC
31238 | RSB1A160NDS | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
31239 | RSB1A160NDS | Main | status LED | Without
31240 | RSB1A160NDS | Complementary | shape of pin | Flat
31241 | RSB1A160NDS | Complementary | average coil resistance | 7500 Ohm network: DC at 20 °C +/- 10 %
31242 | RSB1A160NDS | Complementary | [Ue] rated operational voltage | 48...66 V DC
31243 | RSB1A160NDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31244 | RSB1A160NDS | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
31245 | RSB1A160NDS | Complementary | contacts material | Silver alloy (Ag/Ni)
31246 | RSB1A160NDS | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
31247 | RSB1A160NDS | Complementary | minimum switching current | 5 mA
31248 | RSB1A160NDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
31249 | RSB1A160NDS | Complementary | minimum switching voltage | 5 V
31250 | RSB1A160NDS | Complementary | maximum switching capacity | 4000 VA AC 448 W DC
31251 | RSB1A160NDS | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
31252 | RSB1A160NDS | Complementary | minimum switching capacity | 300 mW at 5 mA
31253 | RSB1A160NDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31254 | RSB1A160NDS | Complementary | mechanical durability | 30000000 cycles
31255 | RSB1A160NDS | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
31256 | RSB1A160NDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
31257 | RSB1A160NDS | Complementary | marking | CE
31258 | RSB1A160NDS | Complementary | average coil consumption | 0.45 W DC
31259 | RSB1A160NDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
31260 | RSB1A160NDS | Complementary | safety reliability data | B10d = 100000
31261 | RSB1A160NDS | Complementary | protection category | RT I
31262 | RSB1A160NDS | Complementary | operating position | Any position
31263 | RSB1A160NDS | Complementary | sale per indivisible quantity | 10
31264 | RSB1A160NDS | Complementary | device presentation | Complete product
31265 | RSB1A160NDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31266 | RSB1A160NDS | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
31267 | RSB1A160NDS | Environment | product certifications | CSA UL GOST
31268 | RSB1A160NDS | Environment | ambient air temperature for storage | -40…85 °C
31269 | RSB1A160NDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31270 | RSB1A160NDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31271 | RSB1A160NDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31272 | RSB1A160NDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31273 | RSB1A160NDS | Contractual warranty | Warranty | 18 months
31274 | RSB1A160RDS | Main | range of product | Zelio Relay
31275 | RSB1A160RDS | Main | series name | Interface relay
31276 | RSB1A160RDS | Main | product or component type | Plug-in relay
31277 | RSB1A160RDS | Main | device short name | RSB
31278 | RSB1A160RDS | Main | contacts type and composition | 1 C/O
31279 | RSB1A160RDS | Main | contact operation | Standard
31280 | RSB1A160RDS | Main | [Uc] control circuit voltage | 6 V DC
31281 | RSB1A160RDS | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C
31282 | RSB1A160RDS | Main | status LED | Without
31283 | RSB1A160RDS | Complementary | shape of pin | Flat
31284 | RSB1A160RDS | Complementary | average coil resistance | 90 Ohm network: DC at 20 °C +/- 10 %
31285 | RSB1A160RDS | Complementary | [Ue] rated operational voltage | 4.8...6.6 V DC
31286 | RSB1A160RDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31287 | RSB1A160RDS | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
31288 | RSB1A160RDS | Complementary | contacts material | Silver alloy (Ag/Ni)
31289 | RSB1A160RDS | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC
31290 | RSB1A160RDS | Complementary | minimum switching current | 5 mA
31291 | RSB1A160RDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
31292 | RSB1A160RDS | Complementary | minimum switching voltage | 5 V
31293 | RSB1A160RDS | Complementary | maximum switching capacity | 4000 VA AC 448 W DC
31294 | RSB1A160RDS | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC
31295 | RSB1A160RDS | Complementary | minimum switching capacity | 300 mW at 5 mA
31296 | RSB1A160RDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31297 | RSB1A160RDS | Complementary | mechanical durability | 30000000 cycles
31298 | RSB1A160RDS | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC
31299 | RSB1A160RDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
31300 | RSB1A160RDS | Complementary | marking | CE
31301 | RSB1A160RDS | Complementary | average coil consumption | 0.45 W DC
31302 | RSB1A160RDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
31303 | RSB1A160RDS | Complementary | safety reliability data | B10d = 100000
31304 | RSB1A160RDS | Complementary | protection category | RT I
31305 | RSB1A160RDS | Complementary | operating position | Any position
31306 | RSB1A160RDS | Complementary | sale per indivisible quantity | 10
31307 | RSB1A160RDS | Complementary | device presentation | Complete product
31308 | RSB1A160RDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31309 | RSB1A160RDS | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508
31310 | RSB1A160RDS | Environment | product certifications | GOST UL CSA
31311 | RSB1A160RDS | Environment | ambient air temperature for storage | -40…85 °C
31312 | RSB1A160RDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31313 | RSB1A160RDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31314 | RSB1A160RDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31315 | RSB1A160RDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31316 | RSB1A160RDS | Contractual warranty | Warranty | 18 months
31317 | RSB2A080B7S | Main | range of product | Zelio Relay
31318 | RSB2A080B7S | Main | series name | Interface relay
31319 | RSB2A080B7S | Main | product or component type | Plug-in relay
31320 | RSB2A080B7S | Main | device short name | RSB
31321 | RSB2A080B7S | Main | contacts type and composition | 2 C/O
31322 | RSB2A080B7S | Main | contact operation | Standard
31323 | RSB2A080B7S | Main | [Uc] control circuit voltage | 24 V AC
31324 | RSB2A080B7S | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
31325 | RSB2A080B7S | Main | status LED | Without
31326 | RSB2A080B7S | Main | control type | Without push-button
31327 | RSB2A080B7S | Complementary | shape of pin | Flat
31328 | RSB2A080B7S | Complementary | average coil resistance | 400 Ohm network: AC at 20 °C +/- 15 %
31329 | RSB2A080B7S | Complementary | [Ue] rated operational voltage | 19.2...26.4 V AC 50 Hz 20.4...26.4 V AC 60 Hz
31330 | RSB2A080B7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31331 | RSB2A080B7S | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
31332 | RSB2A080B7S | Complementary | contacts material | Silver alloy (Ag/Ni)
31333 | RSB2A080B7S | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
31334 | RSB2A080B7S | Complementary | minimum switching current | 5 mA
31335 | RSB2A080B7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
31336 | RSB2A080B7S | Complementary | minimum switching voltage | 5 V
31337 | RSB2A080B7S | Complementary | maximum switching capacity | 2000 VA AC 224 W DC
31338 | RSB2A080B7S | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
31339 | RSB2A080B7S | Complementary | minimum switching capacity | 300 mW at 5 mA
31340 | RSB2A080B7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31341 | RSB2A080B7S | Complementary | mechanical durability | 30000000 cycles
31342 | RSB2A080B7S | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
31343 | RSB2A080B7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
31344 | RSB2A080B7S | Complementary | marking | CE
31345 | RSB2A080B7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
31346 | RSB2A080B7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
31347 | RSB2A080B7S | Complementary | safety reliability data | B10d = 100000
31348 | RSB2A080B7S | Complementary | protection category | RT I
31349 | RSB2A080B7S | Complementary | operating position | Any position
31350 | RSB2A080B7S | Complementary | sale per indivisible quantity | 10
31351 | RSB2A080B7S | Complementary | device presentation | Complete product
31352 | RSB2A080B7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31353 | RSB2A080B7S | Environment | standards | UL 508 EN/IEC 61810-1 CSA C22.2 No 14
31354 | RSB2A080B7S | Environment | product certifications | UL GOST CSA
31355 | RSB2A080B7S | Environment | ambient air temperature for storage | -40…85 °C
31356 | RSB2A080B7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31357 | RSB2A080B7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31358 | RSB2A080B7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31359 | RSB2A080B7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31360 | RSB2A080B7S | Offer Sustainability | Sustainable offer status | Green Premium product
31361 | RSB2A080B7S | Offer Sustainability | REACh free of SVHC | Yes
31362 | RSB2A080B7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
31363 | RSB2A080B7S | Offer Sustainability | Toxic heavy metal free | Yes
31364 | RSB2A080B7S | Offer Sustainability | Mercury free | Yes
31365 | RSB2A080B7S | Offer Sustainability | RoHS exemption information | Yes
31366 | RSB2A080B7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration
31367 | RSB2A080B7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
31368 | RSB2A080B7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
31369 | RSB2A080B7S | Contractual warranty | Warranty | 18 months
31370 | RSB2A080BDS | Main | range of product | Zelio Relay
31371 | RSB2A080BDS | Main | series name | Interface relay
31372 | RSB2A080BDS | Main | product or component type | Plug-in relay
31373 | RSB2A080BDS | Main | device short name | RSB
31374 | RSB2A080BDS | Main | contacts type and composition | 2 C/O
31375 | RSB2A080BDS | Main | contact operation | Standard
31376 | RSB2A080BDS | Main | [Uc] control circuit voltage | 24 V DC
31377 | RSB2A080BDS | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
31378 | RSB2A080BDS | Main | status LED | Without
31379 | RSB2A080BDS | Main | control type | Without push-button
31380 | RSB2A080BDS | Complementary | shape of pin | Flat
31381 | RSB2A080BDS | Complementary | average coil resistance | 1440 Ohm network: DC at 20 °C +/- 10 %
31382 | RSB2A080BDS | Complementary | [Ue] rated operational voltage | 19.2...26.4 V DC
31383 | RSB2A080BDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31384 | RSB2A080BDS | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
31385 | RSB2A080BDS | Complementary | contacts material | Silver alloy (Ag/Ni)
31386 | RSB2A080BDS | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
31387 | RSB2A080BDS | Complementary | minimum switching current | 5 mA
31388 | RSB2A080BDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
31389 | RSB2A080BDS | Complementary | minimum switching voltage | 5 V
31390 | RSB2A080BDS | Complementary | maximum switching capacity | 2000 VA AC 224 W DC
31391 | RSB2A080BDS | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
31392 | RSB2A080BDS | Complementary | minimum switching capacity | 300 mW at 5 mA
31393 | RSB2A080BDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31394 | RSB2A080BDS | Complementary | mechanical durability | 30000000 cycles
31395 | RSB2A080BDS | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
31396 | RSB2A080BDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
31397 | RSB2A080BDS | Complementary | marking | CE
31398 | RSB2A080BDS | Complementary | average coil consumption | 0.45 W DC
31399 | RSB2A080BDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
31400 | RSB2A080BDS | Complementary | safety reliability data | B10d = 100000
31401 | RSB2A080BDS | Complementary | protection category | RT I
31402 | RSB2A080BDS | Complementary | operating position | Any position
31403 | RSB2A080BDS | Complementary | sale per indivisible quantity | 10
31404 | RSB2A080BDS | Complementary | device presentation | Complete product
31405 | RSB2A080BDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31406 | RSB2A080BDS | Environment | standards | EN/IEC 61810-1 UL 508 CSA C22.2 No 14
31407 | RSB2A080BDS | Environment | product certifications | GOST UL CSA
31408 | RSB2A080BDS | Environment | ambient air temperature for storage | -40…85 °C
31409 | RSB2A080BDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31410 | RSB2A080BDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31411 | RSB2A080BDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31412 | RSB2A080BDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31413 | RSB2A080BDS | Offer Sustainability | Sustainable offer status | Green Premium product
31414 | RSB2A080BDS | Offer Sustainability | REACh free of SVHC | Yes
31415 | RSB2A080BDS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
31416 | RSB2A080BDS | Offer Sustainability | Toxic heavy metal free | Yes
31417 | RSB2A080BDS | Offer Sustainability | Mercury free | Yes
31418 | RSB2A080BDS | Offer Sustainability | RoHS exemption information | Yes
31419 | RSB2A080BDS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
31420 | RSB2A080BDS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
31421 | RSB2A080BDS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
31422 | RSB2A080BDS | Contractual warranty | Warranty | 18 months
31423 | RSB2A080E7S | Main | range of product | Zelio Relay
31424 | RSB2A080E7S | Main | series name | Interface relay
31425 | RSB2A080E7S | Main | product or component type | Plug-in relay
31426 | RSB2A080E7S | Main | device short name | RSB
31427 | RSB2A080E7S | Main | contacts type and composition | 2 C/O
31428 | RSB2A080E7S | Main | contact operation | Standard
31429 | RSB2A080E7S | Main | [Uc] control circuit voltage | 48 V AC
31430 | RSB2A080E7S | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
31431 | RSB2A080E7S | Main | status LED | Without
31432 | RSB2A080E7S | Complementary | shape of pin | Flat
31433 | RSB2A080E7S | Complementary | average coil resistance | 1550 Ohm network: AC at 20 °C +/- 15 %
31434 | RSB2A080E7S | Complementary | [Ue] rated operational voltage | 38.4...57.6 V AC 50 Hz 40.8...57.6 V AC 60 Hz
31435 | RSB2A080E7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31436 | RSB2A080E7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
31437 | RSB2A080E7S | Complementary | contacts material | Silver alloy (Ag/Ni)
31438 | RSB2A080E7S | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
31439 | RSB2A080E7S | Complementary | minimum switching current | 5 mA
31440 | RSB2A080E7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
31441 | RSB2A080E7S | Complementary | minimum switching voltage | 5 V
31442 | RSB2A080E7S | Complementary | maximum switching capacity | 2000 VA AC 224 W DC
31443 | RSB2A080E7S | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
31444 | RSB2A080E7S | Complementary | minimum switching capacity | 300 mW at 5 mA
31445 | RSB2A080E7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31446 | RSB2A080E7S | Complementary | mechanical durability | 30000000 cycles
31447 | RSB2A080E7S | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
31448 | RSB2A080E7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
31449 | RSB2A080E7S | Complementary | marking | CE
31450 | RSB2A080E7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
31451 | RSB2A080E7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
31452 | RSB2A080E7S | Complementary | safety reliability data | B10d = 100000
31453 | RSB2A080E7S | Complementary | protection category | RT I
31454 | RSB2A080E7S | Complementary | operating position | Any position
31455 | RSB2A080E7S | Complementary | sale per indivisible quantity | 10
31456 | RSB2A080E7S | Complementary | device presentation | Complete product
31457 | RSB2A080E7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31458 | RSB2A080E7S | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1
31459 | RSB2A080E7S | Environment | product certifications | UL GOST CSA
31460 | RSB2A080E7S | Environment | ambient air temperature for storage | -40…85 °C
31461 | RSB2A080E7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31462 | RSB2A080E7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31463 | RSB2A080E7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31464 | RSB2A080E7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31465 | RSB2A080E7S | Offer Sustainability | Sustainable offer status | Green Premium product
31466 | RSB2A080E7S | Offer Sustainability | REACh free of SVHC | Yes
31467 | RSB2A080E7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
31468 | RSB2A080E7S | Offer Sustainability | Toxic heavy metal free | Yes
31469 | RSB2A080E7S | Offer Sustainability | Mercury free | Yes
31470 | RSB2A080E7S | Offer Sustainability | RoHS exemption information | Yes
31471 | RSB2A080E7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration
31472 | RSB2A080E7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
31473 | RSB2A080E7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
31474 | RSB2A080E7S | Contractual warranty | Warranty | 18 months
31475 | RSB2A080EDS | Main | range of product | Zelio Relay
31476 | RSB2A080EDS | Main | series name | Interface relay
31477 | RSB2A080EDS | Main | product or component type | Plug-in relay
31478 | RSB2A080EDS | Main | device short name | RSB
31479 | RSB2A080EDS | Main | contacts type and composition | 2 C/O
31480 | RSB2A080EDS | Main | contact operation | Standard
31481 | RSB2A080EDS | Main | [Uc] control circuit voltage | 48 V DC
31482 | RSB2A080EDS | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
31483 | RSB2A080EDS | Main | status LED | Without
31484 | RSB2A080EDS | Complementary | shape of pin | Flat
31485 | RSB2A080EDS | Complementary | average coil resistance | 5700 Ohm network: DC at 20 °C +/- 10 %
31486 | RSB2A080EDS | Complementary | [Ue] rated operational voltage | 38.4...52.8 V DC
31487 | RSB2A080EDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31488 | RSB2A080EDS | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
31489 | RSB2A080EDS | Complementary | contacts material | Silver alloy (Ag/Ni)
31490 | RSB2A080EDS | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
31491 | RSB2A080EDS | Complementary | minimum switching current | 5 mA
31492 | RSB2A080EDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
31493 | RSB2A080EDS | Complementary | minimum switching voltage | 5 V
31494 | RSB2A080EDS | Complementary | maximum switching capacity | 2000 VA AC 224 W DC
31495 | RSB2A080EDS | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
31496 | RSB2A080EDS | Complementary | minimum switching capacity | 300 mW at 5 mA
31497 | RSB2A080EDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31498 | RSB2A080EDS | Complementary | mechanical durability | 30000000 cycles
31499 | RSB2A080EDS | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
31500 | RSB2A080EDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
31501 | RSB2A080EDS | Complementary | marking | CE
31502 | RSB2A080EDS | Complementary | average coil consumption | 0.45 W DC
31503 | RSB2A080EDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
31504 | RSB2A080EDS | Complementary | safety reliability data | B10d = 100000
31505 | RSB2A080EDS | Complementary | protection category | RT I
31506 | RSB2A080EDS | Complementary | operating position | Any position
31507 | RSB2A080EDS | Complementary | sale per indivisible quantity | 10
31508 | RSB2A080EDS | Complementary | device presentation | Complete product
31509 | RSB2A080EDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31510 | RSB2A080EDS | Environment | standards | EN/IEC 61810-1 UL 508 CSA C22.2 No 14
31511 | RSB2A080EDS | Environment | product certifications | CSA GOST UL
31512 | RSB2A080EDS | Environment | ambient air temperature for storage | -40…85 °C
31513 | RSB2A080EDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31514 | RSB2A080EDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31515 | RSB2A080EDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31516 | RSB2A080EDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31517 | RSB2A080EDS | Offer Sustainability | Sustainable offer status | Green Premium product
31518 | RSB2A080EDS | Offer Sustainability | REACh free of SVHC | Yes
31519 | RSB2A080EDS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
31520 | RSB2A080EDS | Offer Sustainability | Toxic heavy metal free | Yes
31521 | RSB2A080EDS | Offer Sustainability | Mercury free | Yes
31522 | RSB2A080EDS | Offer Sustainability | RoHS exemption information | Yes
31523 | RSB2A080EDS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
31524 | RSB2A080EDS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
31525 | RSB2A080EDS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
31526 | RSB2A080EDS | Contractual warranty | Warranty | 18 months
31527 | RSB2A080F7S | Main | range of product | Zelio Relay
31528 | RSB2A080F7S | Main | series name | Interface relay
31529 | RSB2A080F7S | Main | product or component type | Plug-in relay
31530 | RSB2A080F7S | Main | device short name | RSB
31531 | RSB2A080F7S | Main | contacts type and composition | 2 C/O
31532 | RSB2A080F7S | Main | contact operation | Standard
31533 | RSB2A080F7S | Main | [Uc] control circuit voltage | 120 V AC
31534 | RSB2A080F7S | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
31535 | RSB2A080F7S | Main | status LED | Without
31536 | RSB2A080F7S | Main | control type | Without push-button
31537 | RSB2A080F7S | Complementary | shape of pin | Flat
31538 | RSB2A080F7S | Complementary | average coil resistance | 10200 Ohm network: AC at 20 °C +/- 15 %
31539 | RSB2A080F7S | Complementary | [Ue] rated operational voltage | 102...144 V AC 60 Hz 96...144 V AC 50 Hz
31540 | RSB2A080F7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31541 | RSB2A080F7S | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
31542 | RSB2A080F7S | Complementary | contacts material | Silver alloy (Ag/Ni)
31543 | RSB2A080F7S | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
31544 | RSB2A080F7S | Complementary | minimum switching current | 5 mA
31545 | RSB2A080F7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
31546 | RSB2A080F7S | Complementary | minimum switching voltage | 5 V
31547 | RSB2A080F7S | Complementary | maximum switching capacity | 2000 VA AC 224 W DC
31548 | RSB2A080F7S | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
31549 | RSB2A080F7S | Complementary | minimum switching capacity | 300 mW at 5 mA
31550 | RSB2A080F7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31551 | RSB2A080F7S | Complementary | mechanical durability | 30000000 cycles
31552 | RSB2A080F7S | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
31553 | RSB2A080F7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
31554 | RSB2A080F7S | Complementary | marking | CE
31555 | RSB2A080F7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
31556 | RSB2A080F7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
31557 | RSB2A080F7S | Complementary | safety reliability data | B10d = 100000
31558 | RSB2A080F7S | Complementary | protection category | RT I
31559 | RSB2A080F7S | Complementary | operating position | Any position
31560 | RSB2A080F7S | Complementary | sale per indivisible quantity | 10
31561 | RSB2A080F7S | Complementary | device presentation | Complete product
31562 | RSB2A080F7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31563 | RSB2A080F7S | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508
31564 | RSB2A080F7S | Environment | product certifications | GOST UL CSA
31565 | RSB2A080F7S | Environment | ambient air temperature for storage | -40…85 °C
31566 | RSB2A080F7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31567 | RSB2A080F7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31568 | RSB2A080F7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31569 | RSB2A080F7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31570 | RSB2A080F7S | Offer Sustainability | Sustainable offer status | Green Premium product
31571 | RSB2A080F7S | Offer Sustainability | REACh free of SVHC | Yes
31572 | RSB2A080F7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
31573 | RSB2A080F7S | Offer Sustainability | Toxic heavy metal free | Yes
31574 | RSB2A080F7S | Offer Sustainability | Mercury free | Yes
31575 | RSB2A080F7S | Offer Sustainability | RoHS exemption information | Yes
31576 | RSB2A080F7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration
31577 | RSB2A080F7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
31578 | RSB2A080F7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
31579 | RSB2A080F7S | Contractual warranty | Warranty | 18 months
31580 | RSB2A080FDS | Main | range of product | Zelio Relay
31581 | RSB2A080FDS | Main | series name | Interface relay
31582 | RSB2A080FDS | Main | product or component type | Plug-in relay
31583 | RSB2A080FDS | Main | device short name | RSB
31584 | RSB2A080FDS | Main | contacts type and composition | 2 C/O
31585 | RSB2A080FDS | Main | contact operation | Standard
31586 | RSB2A080FDS | Main | [Uc] control circuit voltage | 110 V DC
31587 | RSB2A080FDS | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
31588 | RSB2A080FDS | Main | status LED | Without
31589 | RSB2A080FDS | Complementary | shape of pin | Flat
31590 | RSB2A080FDS | Complementary | average coil resistance | 25200 Ohm network: DC at 20 °C +/- 10 %
31591 | RSB2A080FDS | Complementary | [Ue] rated operational voltage | 88...121 V DC
31592 | RSB2A080FDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31593 | RSB2A080FDS | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
31594 | RSB2A080FDS | Complementary | contacts material | Silver alloy (Ag/Ni)
31595 | RSB2A080FDS | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
31596 | RSB2A080FDS | Complementary | minimum switching current | 5 mA
31597 | RSB2A080FDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
31598 | RSB2A080FDS | Complementary | minimum switching voltage | 5 V
31599 | RSB2A080FDS | Complementary | maximum switching capacity | 2000 VA AC 224 W DC
31600 | RSB2A080FDS | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
31601 | RSB2A080FDS | Complementary | minimum switching capacity | 300 mW at 5 mA
31602 | RSB2A080FDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31603 | RSB2A080FDS | Complementary | mechanical durability | 30000000 cycles
31604 | RSB2A080FDS | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
31605 | RSB2A080FDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
31606 | RSB2A080FDS | Complementary | marking | CE
31607 | RSB2A080FDS | Complementary | average coil consumption | 0.45 W DC
31608 | RSB2A080FDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
31609 | RSB2A080FDS | Complementary | safety reliability data | B10d = 100000
31610 | RSB2A080FDS | Complementary | protection category | RT I
31611 | RSB2A080FDS | Complementary | operating position | Any position
31612 | RSB2A080FDS | Complementary | sale per indivisible quantity | 10
31613 | RSB2A080FDS | Complementary | device presentation | Complete product
31614 | RSB2A080FDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31615 | RSB2A080FDS | Environment | standards | EN/IEC 61810-1 UL 508 CSA C22.2 No 14
31616 | RSB2A080FDS | Environment | product certifications | GOST CSA UL
31617 | RSB2A080FDS | Environment | ambient air temperature for storage | -40…85 °C
31618 | RSB2A080FDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31619 | RSB2A080FDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31620 | RSB2A080FDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31621 | RSB2A080FDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31622 | RSB2A080FDS | Offer Sustainability | Sustainable offer status | Green Premium product
31623 | RSB2A080FDS | Offer Sustainability | REACh free of SVHC | Yes
31624 | RSB2A080FDS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
31625 | RSB2A080FDS | Offer Sustainability | Toxic heavy metal free | Yes
31626 | RSB2A080FDS | Offer Sustainability | Mercury free | Yes
31627 | RSB2A080FDS | Offer Sustainability | RoHS exemption information | Yes
31628 | RSB2A080FDS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
31629 | RSB2A080FDS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
31630 | RSB2A080FDS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
31631 | RSB2A080FDS | Contractual warranty | Warranty | 18 months
31632 | RSB2A080JDS | Main | range of product | Zelio Relay
31633 | RSB2A080JDS | Main | series name | Interface relay
31634 | RSB2A080JDS | Main | product or component type | Plug-in relay
31635 | RSB2A080JDS | Main | device short name | RSB
31636 | RSB2A080JDS | Main | contacts type and composition | 2 C/O
31637 | RSB2A080JDS | Main | contact operation | Standard
31638 | RSB2A080JDS | Main | [Uc] control circuit voltage | 12 V DC
31639 | RSB2A080JDS | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
31640 | RSB2A080JDS | Main | status LED | Without
31641 | RSB2A080JDS | Main | control type | Without push-button
31642 | RSB2A080JDS | Complementary | shape of pin | Flat
31643 | RSB2A080JDS | Complementary | average coil resistance | 360 Ohm network: DC at 20 °C +/- 10 %
31644 | RSB2A080JDS | Complementary | [Ue] rated operational voltage | 9.6...13.2 V DC
31645 | RSB2A080JDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31646 | RSB2A080JDS | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
31647 | RSB2A080JDS | Complementary | contacts material | Silver alloy (Ag/Ni)
31648 | RSB2A080JDS | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
31649 | RSB2A080JDS | Complementary | minimum switching current | 5 mA
31650 | RSB2A080JDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
31651 | RSB2A080JDS | Complementary | minimum switching voltage | 5 V
31652 | RSB2A080JDS | Complementary | maximum switching capacity | 2000 VA AC 224 W DC
31653 | RSB2A080JDS | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
31654 | RSB2A080JDS | Complementary | minimum switching capacity | 300 mW at 5 mA
31655 | RSB2A080JDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31656 | RSB2A080JDS | Complementary | mechanical durability | 30000000 cycles
31657 | RSB2A080JDS | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
31658 | RSB2A080JDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
31659 | RSB2A080JDS | Complementary | marking | CE
31660 | RSB2A080JDS | Complementary | average coil consumption | 0.45 W DC
31661 | RSB2A080JDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
31662 | RSB2A080JDS | Complementary | safety reliability data | B10d = 100000
31663 | RSB2A080JDS | Complementary | protection category | RT I
31664 | RSB2A080JDS | Complementary | operating position | Any position
31665 | RSB2A080JDS | Complementary | sale per indivisible quantity | 10
31666 | RSB2A080JDS | Complementary | device presentation | Complete product
31667 | RSB2A080JDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31668 | RSB2A080JDS | Environment | standards | EN/IEC 61810-1 UL 508 CSA C22.2 No 14
31669 | RSB2A080JDS | Environment | product certifications | GOST UL CSA
31670 | RSB2A080JDS | Environment | ambient air temperature for storage | -40…85 °C
31671 | RSB2A080JDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31672 | RSB2A080JDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31673 | RSB2A080JDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31674 | RSB2A080JDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31675 | RSB2A080JDS | Offer Sustainability | Sustainable offer status | Green Premium product
31676 | RSB2A080JDS | Offer Sustainability | REACh free of SVHC | Yes
31677 | RSB2A080JDS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
31678 | RSB2A080JDS | Offer Sustainability | Toxic heavy metal free | Yes
31679 | RSB2A080JDS | Offer Sustainability | Mercury free | Yes
31680 | RSB2A080JDS | Offer Sustainability | RoHS exemption information | Yes
31681 | RSB2A080JDS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
31682 | RSB2A080JDS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
31683 | RSB2A080JDS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
31684 | RSB2A080JDS | Contractual warranty | Warranty | 18 months
31685 | RSB2A080NDS | Main | range of product | Zelio Relay
31686 | RSB2A080NDS | Main | series name | Interface relay
31687 | RSB2A080NDS | Main | product or component type | Plug-in relay
31688 | RSB2A080NDS | Main | device short name | RSB
31689 | RSB2A080NDS | Main | contacts type and composition | 2 C/O
31690 | RSB2A080NDS | Main | contact operation | Standard
31691 | RSB2A080NDS | Main | [Uc] control circuit voltage | 60 V DC
31692 | RSB2A080NDS | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
31693 | RSB2A080NDS | Main | status LED | Without
31694 | RSB2A080NDS | Complementary | shape of pin | Flat
31695 | RSB2A080NDS | Complementary | average coil resistance | 7500 Ohm network: DC at 20 °C +/- 10 %
31696 | RSB2A080NDS | Complementary | [Ue] rated operational voltage | 48...66 V DC
31697 | RSB2A080NDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31698 | RSB2A080NDS | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
31699 | RSB2A080NDS | Complementary | contacts material | Silver alloy (Ag/Ni)
31700 | RSB2A080NDS | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
31701 | RSB2A080NDS | Complementary | minimum switching current | 5 mA
31702 | RSB2A080NDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
31703 | RSB2A080NDS | Complementary | minimum switching voltage | 5 V
31704 | RSB2A080NDS | Complementary | maximum switching capacity | 2000 VA AC 224 W DC
31705 | RSB2A080NDS | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
31706 | RSB2A080NDS | Complementary | minimum switching capacity | 300 mW at 5 mA
31707 | RSB2A080NDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31708 | RSB2A080NDS | Complementary | mechanical durability | 30000000 cycles
31709 | RSB2A080NDS | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
31710 | RSB2A080NDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
31711 | RSB2A080NDS | Complementary | marking | CE
31712 | RSB2A080NDS | Complementary | average coil consumption | 0.45 W DC
31713 | RSB2A080NDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
31714 | RSB2A080NDS | Complementary | safety reliability data | B10d = 100000
31715 | RSB2A080NDS | Complementary | protection category | RT I
31716 | RSB2A080NDS | Complementary | operating position | Any position
31717 | RSB2A080NDS | Complementary | sale per indivisible quantity | 10
31718 | RSB2A080NDS | Complementary | device presentation | Complete product
31719 | RSB2A080NDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31720 | RSB2A080NDS | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
31721 | RSB2A080NDS | Environment | product certifications | UL GOST CSA
31722 | RSB2A080NDS | Environment | ambient air temperature for storage | -40…85 °C
31723 | RSB2A080NDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31724 | RSB2A080NDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31725 | RSB2A080NDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31726 | RSB2A080NDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31727 | RSB2A080NDS | Offer Sustainability | Sustainable offer status | Green Premium product
31728 | RSB2A080NDS | Offer Sustainability | REACh free of SVHC | Yes
31729 | RSB2A080NDS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
31730 | RSB2A080NDS | Offer Sustainability | Toxic heavy metal free | Yes
31731 | RSB2A080NDS | Offer Sustainability | Mercury free | Yes
31732 | RSB2A080NDS | Offer Sustainability | RoHS exemption information | Yes
31733 | RSB2A080NDS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
31734 | RSB2A080NDS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
31735 | RSB2A080NDS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
31736 | RSB2A080NDS | Contractual warranty | Warranty | 18 months
31737 | RSB2A080P7S | Main | range of product | Zelio Relay
31738 | RSB2A080P7S | Main | series name | Interface relay
31739 | RSB2A080P7S | Main | product or component type | Plug-in relay
31740 | RSB2A080P7S | Main | device short name | RSB
31741 | RSB2A080P7S | Main | contacts type and composition | 2 C/O
31742 | RSB2A080P7S | Main | contact operation | Standard
31743 | RSB2A080P7S | Main | [Uc] control circuit voltage | 230 V AC
31744 | RSB2A080P7S | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
31745 | RSB2A080P7S | Main | status LED | Without
31746 | RSB2A080P7S | Main | control type | Without push-button
31747 | RSB2A080P7S | Complementary | shape of pin | Flat
31748 | RSB2A080P7S | Complementary | average coil resistance | 38500 Ohm network: AC at 20 °C +/- 15 %
31749 | RSB2A080P7S | Complementary | [Ue] rated operational voltage | 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz
31750 | RSB2A080P7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31751 | RSB2A080P7S | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
31752 | RSB2A080P7S | Complementary | contacts material | Silver alloy (Ag/Ni)
31753 | RSB2A080P7S | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
31754 | RSB2A080P7S | Complementary | minimum switching current | 5 mA
31755 | RSB2A080P7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
31756 | RSB2A080P7S | Complementary | minimum switching voltage | 5 V
31757 | RSB2A080P7S | Complementary | maximum switching capacity | 2000 VA AC 224 W DC
31758 | RSB2A080P7S | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
31759 | RSB2A080P7S | Complementary | minimum switching capacity | 300 mW at 5 mA
31760 | RSB2A080P7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31761 | RSB2A080P7S | Complementary | mechanical durability | 30000000 cycles
31762 | RSB2A080P7S | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
31763 | RSB2A080P7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
31764 | RSB2A080P7S | Complementary | marking | CE
31765 | RSB2A080P7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
31766 | RSB2A080P7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
31767 | RSB2A080P7S | Complementary | safety reliability data | B10d = 100000
31768 | RSB2A080P7S | Complementary | protection category | RT I
31769 | RSB2A080P7S | Complementary | operating position | Any position
31770 | RSB2A080P7S | Complementary | sale per indivisible quantity | 10
31771 | RSB2A080P7S | Complementary | device presentation | Complete product
31772 | RSB2A080P7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31773 | RSB2A080P7S | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1
31774 | RSB2A080P7S | Environment | product certifications | GOST CSA UL
31775 | RSB2A080P7S | Environment | ambient air temperature for storage | -40…85 °C
31776 | RSB2A080P7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31777 | RSB2A080P7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31778 | RSB2A080P7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31779 | RSB2A080P7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31780 | RSB2A080P7S | Offer Sustainability | Sustainable offer status | Green Premium product
31781 | RSB2A080P7S | Offer Sustainability | REACh free of SVHC | Yes
31782 | RSB2A080P7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
31783 | RSB2A080P7S | Offer Sustainability | Toxic heavy metal free | Yes
31784 | RSB2A080P7S | Offer Sustainability | Mercury free | Yes
31785 | RSB2A080P7S | Offer Sustainability | RoHS exemption information | Yes
31786 | RSB2A080P7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration
31787 | RSB2A080P7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
31788 | RSB2A080P7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
31789 | RSB2A080P7S | Contractual warranty | Warranty | 18 months
31790 | RSB2A080RDS | Main | range of product | Zelio Relay
31791 | RSB2A080RDS | Main | series name | Interface relay
31792 | RSB2A080RDS | Main | product or component type | Plug-in relay
31793 | RSB2A080RDS | Main | device short name | RSB
31794 | RSB2A080RDS | Main | contacts type and composition | 2 C/O
31795 | RSB2A080RDS | Main | contact operation | Standard
31796 | RSB2A080RDS | Main | [Uc] control circuit voltage | 6 V DC
31797 | RSB2A080RDS | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
31798 | RSB2A080RDS | Main | status LED | Without
31799 | RSB2A080RDS | Complementary | shape of pin | Flat
31800 | RSB2A080RDS | Complementary | average coil resistance | 90 Ohm network: DC at 20 °C +/- 10 %
31801 | RSB2A080RDS | Complementary | [Ue] rated operational voltage | 4.8...6.6 V DC
31802 | RSB2A080RDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31803 | RSB2A080RDS | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
31804 | RSB2A080RDS | Complementary | contacts material | Silver alloy (Ag/Ni)
31805 | RSB2A080RDS | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
31806 | RSB2A080RDS | Complementary | minimum switching current | 5 mA
31807 | RSB2A080RDS | Complementary | maximum switching voltage | 300 V DC 400 V AC
31808 | RSB2A080RDS | Complementary | minimum switching voltage | 5 V
31809 | RSB2A080RDS | Complementary | maximum switching capacity | 2000 VA AC 224 W DC
31810 | RSB2A080RDS | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
31811 | RSB2A080RDS | Complementary | minimum switching capacity | 300 mW at 5 mA
31812 | RSB2A080RDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31813 | RSB2A080RDS | Complementary | mechanical durability | 30000000 cycles
31814 | RSB2A080RDS | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
31815 | RSB2A080RDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact
31816 | RSB2A080RDS | Complementary | marking | CE
31817 | RSB2A080RDS | Complementary | average coil consumption | 0.45 W DC
31818 | RSB2A080RDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC
31819 | RSB2A080RDS | Complementary | safety reliability data | B10d = 100000
31820 | RSB2A080RDS | Complementary | protection category | RT I
31821 | RSB2A080RDS | Complementary | operating position | Any position
31822 | RSB2A080RDS | Complementary | sale per indivisible quantity | 10
31823 | RSB2A080RDS | Complementary | device presentation | Complete product
31824 | RSB2A080RDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31825 | RSB2A080RDS | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1
31826 | RSB2A080RDS | Environment | product certifications | CSA GOST UL
31827 | RSB2A080RDS | Environment | ambient air temperature for storage | -40…85 °C
31828 | RSB2A080RDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31829 | RSB2A080RDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31830 | RSB2A080RDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31831 | RSB2A080RDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31832 | RSB2A080RDS | Contractual warranty | Warranty | 18 months
31833 | RSB2A080U7S | Main | range of product | Zelio Relay
31834 | RSB2A080U7S | Main | series name | Interface relay
31835 | RSB2A080U7S | Main | product or component type | Plug-in relay
31836 | RSB2A080U7S | Main | device short name | RSB
31837 | RSB2A080U7S | Main | contacts type and composition | 2 C/O
31838 | RSB2A080U7S | Main | contact operation | Standard
31839 | RSB2A080U7S | Main | [Uc] control circuit voltage | 240 V AC
31840 | RSB2A080U7S | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
31841 | RSB2A080U7S | Main | status LED | Without
31842 | RSB2A080U7S | Complementary | shape of pin | Flat
31843 | RSB2A080U7S | Complementary | average coil resistance | 42500 Ohm network: AC at 20 °C +/- 15 %
31844 | RSB2A080U7S | Complementary | [Ue] rated operational voltage | 192...288 V AC 50 Hz 204...288 V AC 60 Hz
31845 | RSB2A080U7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31846 | RSB2A080U7S | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
31847 | RSB2A080U7S | Complementary | contacts material | Silver alloy (Ag/Ni)
31848 | RSB2A080U7S | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
31849 | RSB2A080U7S | Complementary | minimum switching current | 5 mA
31850 | RSB2A080U7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
31851 | RSB2A080U7S | Complementary | minimum switching voltage | 5 V
31852 | RSB2A080U7S | Complementary | maximum switching capacity | 2000 VA AC 224 W DC
31853 | RSB2A080U7S | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
31854 | RSB2A080U7S | Complementary | minimum switching capacity | 300 mW at 5 mA
31855 | RSB2A080U7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31856 | RSB2A080U7S | Complementary | mechanical durability | 30000000 cycles
31857 | RSB2A080U7S | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
31858 | RSB2A080U7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
31859 | RSB2A080U7S | Complementary | marking | CE
31860 | RSB2A080U7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
31861 | RSB2A080U7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
31862 | RSB2A080U7S | Complementary | safety reliability data | B10d = 100000
31863 | RSB2A080U7S | Complementary | protection category | RT I
31864 | RSB2A080U7S | Complementary | operating position | Any position
31865 | RSB2A080U7S | Complementary | sale per indivisible quantity | 10
31866 | RSB2A080U7S | Complementary | device presentation | Complete product
31867 | RSB2A080U7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31868 | RSB2A080U7S | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508
31869 | RSB2A080U7S | Environment | product certifications | UL CSA GOST
31870 | RSB2A080U7S | Environment | ambient air temperature for storage | -40…85 °C
31871 | RSB2A080U7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31872 | RSB2A080U7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31873 | RSB2A080U7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31874 | RSB2A080U7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31875 | RSB2A080U7S | Offer Sustainability | Sustainable offer status | Green Premium product
31876 | RSB2A080U7S | Offer Sustainability | REACh free of SVHC | Yes
31877 | RSB2A080U7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
31878 | RSB2A080U7S | Offer Sustainability | Toxic heavy metal free | Yes
31879 | RSB2A080U7S | Offer Sustainability | Mercury free | Yes
31880 | RSB2A080U7S | Offer Sustainability | RoHS exemption information | Yes
31881 | RSB2A080U7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration
31882 | RSB2A080U7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
31883 | RSB2A080U7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
31884 | RSB2A080U7S | Contractual warranty | Warranty | 18 months
31885 | RSB2A080M7S | Main | range of product | Zelio Relay
31886 | RSB2A080M7S | Main | series name | Interface relay
31887 | RSB2A080M7S | Main | product or component type | Plug-in relay
31888 | RSB2A080M7S | Main | device short name | RSB
31889 | RSB2A080M7S | Main | contacts type and composition | 2 C/O
31890 | RSB2A080M7S | Main | contact operation | Standard
31891 | RSB2A080M7S | Main | [Uc] control circuit voltage | 220 V AC
31892 | RSB2A080M7S | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
31893 | RSB2A080M7S | Main | status LED | Without
31894 | RSB2A080M7S | Complementary | shape of pin | Flat
31895 | RSB2A080M7S | Complementary | average coil resistance | 35500 Ohm network: AC at 20 °C +/- 15 %
31896 | RSB2A080M7S | Complementary | [Ue] rated operational voltage | 176...264 V AC 50 Hz 187...264 V AC 60 Hz
31897 | RSB2A080M7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
31898 | RSB2A080M7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV
31899 | RSB2A080M7S | Complementary | contacts material | Silver alloy (Ag/Ni)
31900 | RSB2A080M7S | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
31901 | RSB2A080M7S | Complementary | minimum switching current | 5 mA
31902 | RSB2A080M7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
31903 | RSB2A080M7S | Complementary | minimum switching voltage | 5 V
31904 | RSB2A080M7S | Complementary | maximum switching capacity | 2000 VA AC 224 W DC
31905 | RSB2A080M7S | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
31906 | RSB2A080M7S | Complementary | minimum switching capacity | 300 mW at 5 mA
31907 | RSB2A080M7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
31908 | RSB2A080M7S | Complementary | mechanical durability | 30000000 cycles
31909 | RSB2A080M7S | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
31910 | RSB2A080M7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
31911 | RSB2A080M7S | Complementary | marking | CE
31912 | RSB2A080M7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
31913 | RSB2A080M7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
31914 | RSB2A080M7S | Complementary | safety reliability data | B10d = 100000
31915 | RSB2A080M7S | Complementary | protection category | RT I
31916 | RSB2A080M7S | Complementary | operating position | Any position
31917 | RSB2A080M7S | Complementary | sale per indivisible quantity | 10
31918 | RSB2A080M7S | Complementary | device presentation | Complete product
31919 | RSB2A080M7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
31920 | RSB2A080M7S | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508
31921 | RSB2A080M7S | Environment | product certifications | GOST UL CSA
31922 | RSB2A080M7S | Environment | ambient air temperature for storage | -40…85 °C
31923 | RSB2A080M7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
31924 | RSB2A080M7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
31925 | RSB2A080M7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
31926 | RSB2A080M7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
31927 | RSB2A080M7S | Offer Sustainability | Sustainable offer status | Green Premium product
31928 | RSB2A080M7S | Offer Sustainability | REACh free of SVHC | Yes
31929 | RSB2A080M7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
31930 | RSB2A080M7S | Offer Sustainability | Toxic heavy metal free | Yes
31931 | RSB2A080M7S | Offer Sustainability | Mercury free | Yes
31932 | RSB2A080M7S | Offer Sustainability | RoHS exemption information | Yes
31933 | RSB2A080M7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration
31934 | RSB2A080M7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
31935 | RSB2A080M7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
31936 | RSB2A080M7S | Contractual warranty | Warranty | 18 months

## pivot_datasheet
Value
| Reference | DL1BDB1 | DL1BDB3 | DL1BDB4 | DL1BDB5 | DL1BDB6 | DL1BDB8 | DL1BDG1 | DL1BDG3 | DL1BDG4 | DL1BDG5 | DL1BDG6 | DL1BDG8 | DL1BDM1 | DL1BDM3 | DL1BDM4 | DL1BDM5 | DL1BDM6 | DL1BDM8 | DL1BEB | DL1BEBS | DL1BEE | DL1BEG | DL1BEGS | DL1BEJ | DL1BEM | DL1BEMS | DL1BKB1 | DL1BKB3 | DL1BKB4 | DL1BKB5 | DL1BKB6 | DL1BKB8 | DL1BKG1 | DL1BKG3 | DL1BKG4 | DL1BKG5 | DL1BKG6 | DL1BKG8 | DL1BKM1 | DL1BKM3 | DL1BKM4 | DL1BKM5 | DL1BKM6 | DL1BKM8 | DL1EDBS | DL1EDGS | DL1EDMS | DL2EDB1SB | DL2EDB3SB | DL2EDB4SB | DL2EDB6SB | DL2EDB8SB | DL2EDG1SB | DL2EDG3SB | DL2EDG4SB | DL2EDG6SB | DL2EDG8SB | DL2EDM1SB | DL2EDM3SB | DL2EDM4SB | DL2EDM6SB | DL2EDM8SB | DL2EKB1SB | DL2EKB3SB | DL2EKB4SB | DL2EKB6SB | DL2EKB8SB | DL2EKG1SB | DL2EKG3SB | DL2EKG4SB | DL2EKG6SB | DL2EKG8SB | DL2EKM1SB | DL2EKM3SB | DL2EKM4SB | DL2EKM6SB | DL2EKM8SB | DL6BB | DL6BG | DL6BM | RE17LAMW | RE17LCBM | RE17LHBM | RE17LLBM | RE17LMBM | RE17RAMU | RE17RBMU | RE17RCMU | RE17RHMU | RE17RLJU | RE17RLMU | RE17RMEMU | RE17RMJU | RE17RMMU | RE17RMMW | RE17RMMWS | RE17RMXMU | RE22R1ACMR | RE22R1AKMR | RE22R1AMR | RE22R1CMR | RE22R1DMR | RE22R1HMR | RE22R1KMR | RE22R1MAMR | RE22R1MKMR | RE22R1MLMR | RE22R1MYMR | RE22R1QCMU | RE22R1QMQ | RE22R1QMU | RE22R2ACMR | RE22R2AMR | RE22R2AMU | RE22R2CMR | RE22R2DMR | RE22R2HMR | RE22R2KMR | RE22R2MJU | RE22R2MMU | RE22R2MMW | RE22R2MWMR | RE22R2MXMU | RE22R2MYMR | RE22R2QEMR | RE22R2QEMT | RE22R2QGMR | RE22R2QTMR | RE48ACV12MW | RE48AMH13MW | RE48AML12MW | RE48ATM12MW | RE7CV11BU | RE7ML11BU | RE7MY13MW | RE7RB11MW | RE7RB13MW | RE7TL11BU | RE7TP13BU | RE7YA12BU | RE8TA11BU | RE8TA21BU | RE8TA31BU | RENF22R2MMW | REXL2TMB7 | REXL2TMBD | REXL2TMF7 | REXL2TMJD | REXL2TMP7 | REXL4TMB7 | REXL4TMBD | REXL4TMF7 | REXL4TMJD | REXL4TMP7 | RHR411M | RHR411U | RHR4131M | RHR4138B | RHR4138BE | RHR4138F | RHR4138G | RHR4138J | RHR418B | RHR418BE | RHR418E | RHR418EN | RHR418F | RHR418G | RHR418J | RHR418P | RHR421M | RHR428B | RHR428E | RHR428F | RHT411M | RHT411U | RHT4131M | RHT4138B | RHT4138E | RHT4138F | RHT4138G | RHT4138J | RHT418B | RHT418BE | RHT418E | RHT418F | RHT418G | RHT418J | RHT421M | RHT428B | RHT428F | RHT428G | RM17JC00MW | RM17TA00 | RM17TE00 | RM17TG00 | RM17TG20 | RM17TT00 | RM17TU00 | RM17UAS14 | RM17UAS15 | RM17UAS15315M | RM17UAS16 | RM17UB310 | RM17UBE15 | RM17UBE16 | RM22JA21MR | RM22JA31MR | RM22LA32MR | RM22LA32MT | RM22LG11MR | RM22LG11MT | RM22TA31 | RM22TA33 | RM22TG20 | RM22TR31 | RM22TR33 | RM22TU21 | RM22TU23 | RM22UA21MR | RM22UA22MR | RM22UA23MR | RM22UA31MR | RM22UA32MR | RM22UA33MR | RM22UB34 | RM35ATL0MW | RM35ATR5MW | RM35ATW5MW | RM35BA10 | RM35HZ21FM | RM35JA31MW | RM35JA32MR | RM35JA32MT | RM35JA32MW | RM35LM33MW | RM35LV14MW | RM35S0MW | RM35TF30 | RM35TM250MW | RM35TM50MW | RM35UA11MW | RM35UA12MW | RM35UA13MW | RM35UB330 | RM35UB3N30 | RM4JA01B | RM4JA01F | RM4JA01M | RM4JA31F | RM4JA31M | RM4JA31MW | RM4JA31Q | RM4JA32F | RM4JA32M | RM4JA32MW | RM4JA32Q | RM4LA32B | RM4LA32F | RM4LA32M | RM4LA32MW | RM4LA32Q | RM4LG01B | RM4LG01F | RM4LG01M | RM4LG01Q | RM4TA01 | RM4TA02 | RM4TA31 | RM4TA32 | RM4TG20 | RM4TR31 | RM4TR32 | RM4TR33 | RM4TR34 | RM4TR35 | RM4TU01 | RM4TU02 | RM4UA01B | RM4UA01F | RM4UA01M | RM4UA02B | RM4UA02F | RM4UA02M | RM4UA03B | RM4UA03F | RM4UA03M | RM4UA31F | RM4UA31M | RM4UA31MW | RM4UA31Q | RM4UA32F | RM4UA32M | RM4UA32MW | RM4UA32Q | RM4UA33F | RM4UA33M | RM4UA33MW | RM4UA33Q | RM4UB34 | RM4UB35 | RMCA61BD | RMCL55BD | RMCN22BD | RMCV60BD | RMNF22TB30 | RMPT10BD | RMPT13BD | RMPT20BD | RMPT23BD | RMPT30BD | RMPT33BD | RMPT50BD | RMPT53BD | RMPT73BD | RMTJ40BD | RMTJ60BD | RMTJ80BD | RMTK80BD | RMTK90BD | RSB1A120B7 | RSB1A120B7S | RSB1A120BD | RSB1A120BDS | RSB1A120E7 | RSB1A120E7S | RSB1A120ED | RSB1A120EDS | RSB1A120F7 | RSB1A120F7S | RSB1A120FD | RSB1A120FDS | RSB1A120JD | RSB1A120JDS | RSB1A120M7 | RSB1A120M7S | RSB1A120ND | RSB1A120NDS | RSB1A120P7 | RSB1A120P7S | RSB1A120RD | RSB1A120RDS | RSB1A120U7 | RSB1A120U7S | RSB1A160B7 | RSB1A160B7S | RSB1A160BD | RSB1A160BDS | RSB1A160E7 | RSB1A160E7S | RSB1A160ED | RSB1A160EDS | RSB1A160F7 | RSB1A160F7S | RSB1A160FD | RSB1A160FDS | RSB1A160JD | RSB1A160JDS | RSB1A160M7 | RSB1A160M7S | RSB1A160ND | RSB1A160NDS | RSB1A160P7 | RSB1A160P7S | RSB1A160RD | RSB1A160RDS | RSB1A160U7 | RSB1A160U7S | RSB2A080B7 | RSB2A080B7S | RSB2A080BD | RSB2A080BDS | RSB2A080E7 | RSB2A080E7S | RSB2A080ED | RSB2A080EDS | RSB2A080F7 | RSB2A080F7S | RSB2A080FD | RSB2A080FDS | RSB2A080JD | RSB2A080JDS | RSB2A080M7 | RSB2A080M7S | RSB2A080ND | RSB2A080NDS | RSB2A080P7 | RSB2A080P7S | RSB2A080RD | RSB2A080RDS | RSB2A080U7 | RSB2A080U7S | RSL1AB4BD | RSL1AB4ED | RSL1AB4JD | RSL1AB4ND | RSL1GB4BD | RSL1GB4ED | RSL1GB4JD | RSL1GB4ND | RSL1PRBU | RSL1PREU | RSL1PRFU | RSL1PRJU | RSL1PRPU | RSL1PVBU | RSL1PVEU | RSL1PVFU | RSL1PVJU | RSL1PVPU | XVBC07 | XVBC21 | XVBC21A | XVBC21B | XVBC6B3 | XVBC6B4 | XVBC6B5 | XVBC6B6 | XVBC6B7 | XVBC6B8 | XVBC6G3 | XVBC6G4 | XVBC6G5 | XVBC6G6 | XVBC6G7 | XVBC6G8 | XVBC6M3 | XVBC6M4 | XVBC6M5 | XVBC6M6 | XVBC6M7 | XVBC6M8 | XVBC8B3 | XVBC8B4 | XVBC8B5 | XVBC8B6 | XVBC8B7 | XVBC8B8 | XVBC8E5 | XVBC8G3 | XVBC8G4 | XVBC8G5 | XVBC8G6 | XVBC8G7 | XVBC8G8 | XVBC8M3 | XVBC8M4 | XVBC8M5 | XVBC8M6 | XVBC8M7 | XVBC8M8 | XVBC9B | XVBC9M | XVBL0B3 | XVBL0B4 | XVBL0B5 | XVBL0B6 | XVBL0B7 | XVBL0B8 | XVBL0G3 | XVBL0G4 | XVBL0G5 | XVBL0G6 | XVBL0G7 | XVBL0G8 | XVBL0M3 | XVBL0M4 | XVBL0M5 | XVBL0M6 | XVBL0M7 | XVBL0M8 | XVBL1B3 | XVBL1B4 | XVBL1B5 | XVBL1B6 | XVBL1B7 | XVBL1B8 | XVBL1G3 | XVBL1G4 | XVBL1G5 | XVBL1G6 | XVBL1G7 | XVBL1G8 | XVBL1M3 | XVBL1M4 | XVBL1M5 | XVBL1M6 | XVBL1M7 | XVBL1M8 | XVBL33 | XVBL34 | XVBL35 | XVBL36 | XVBL37 | XVBL38 | XVBL4B3 | XVBL4B4 | XVBL4B5 | XVBL4B6 | XVBL4B7 | XVBL4B8 | XVBL4M3 | XVBL4M4 | XVBL4M5 | XVBL4M6 | XVBL4M7 | XVBL4M8 | XVBL6B3 | XVBL6B4 | XVBL6B5 | XVBL6B6 | XVBL6B7 | XVBL6B8 | XVBL6G3 | XVBL6G4 | XVBL6G5 | XVBL6G6 | XVBL6G7 | XVBL6G8 | XVBL6M3 | XVBL6M4 | XVBL6M5 | XVBL6M6 | XVBL6M7 | XVBL6M8 | XVBL8B3 | XVBL8B4 | XVBL8B5 | XVBL8B6 | XVBL8B7 | XVBL8B8 | XVBL8G3 | XVBL8G4 | XVBL8G5 | XVBL8G6 | XVBL8G7 | XVBL8G8 | XVBL8M3 | XVBL8M4 | XVBL8M5 | XVBL8M6 | XVBL8M7 | XVBL8M8 | XVDB1GAR | XVDB1SGAR | XVDB2AR | XVDB2CGAR | XVDB2GAR | XVDB2GAR6 | XVDB2GR | XVDB2GR6 | XVDB2SAR | XVDB2SGAR | XVDB2SGR | XVDBA6 | XVDBR6 | XVDBSA6 | XVDL33 | XVDL34 | XVDL35 | XVDL38 | XVDL4B3 | XVDL4B4 | XVDL4B5 | XVDL4B6 | XVDL4B7 | XVDL4B8 | XVDL4M3 | XVDL4M4 | XVDL4M5 | XVDL4M6 | XVDL4M7 | XVDL4M8 | XVDL6B3 | XVDL6B4 | XVDL6B5 | XVDL6B6 | XVDL6B7 | XVDL6B8 | XVDL6M3 | XVDL6M4 | XVDL6M5 | XVDL6M6 | XVDL6M7 | XVDL6M8 | XVDLS33 | XVDLS34 | XVDLS35 | XVDLS36 | XVDLS37 | XVDLS38 | XVDLS6B3 | XVDLS6B4 | XVDLS6B5 | XVDLS6B6 | XVDLS6B7 | XVDLS6B8 | XVDLS6G3 | XVDLS6G4 | XVDLS6G5 | XVDLS6G6 | XVDLS6G7 | XVDLS6G8 | XVDLS6M3 | XVDLS6M4 | XVDLS6M5 | XVDLS6M6 | XVDLS6M7 | XVDLS6M8 | XVDM1GAR | XVDM2GAR | XVDM2SGAR | XVDM2SGR | XVDMA6 | XVDMR6 | XVEL2B3 | XVEL2B4 | XVEL2B5 | XVEL2B6 | XVEL2B7 | XVEL2G3 | XVEL2G4 | XVEL2G5 | XVEL2G6 | XVEL2G7 | XVEL2M3 | XVEL2M4 | XVEL2M5 | XVEL2M6 | XVEL2M7 | XVEL33 | XVEL34 | XVEL35 | XVEL36 | XVEL37 | XVEL6B3 | XVEL6B4 | XVEL6B5 | XVEL6B6 | XVEL6B7 | XVEL6G3 | XVEL6G4 | XVEL6G5 | XVEL6G6 | XVEL6G7 | XVEL6M3 | XVEL6M4 | XVEL6M5 | XVEL6M6 | XVEL6M7 | XVMB1R6AG | XVMB1R6AGS | XVMB1RA | XVMB1RAG | XVMB1RAGB | XVMB1RAGBS | XVMB1RAGS | XVMB1RAS | XVMB1RG | XVMB1RGS | XVMC21 | XVMC29B | XVMC29G | XVMC29M | XVMG1R6AG | XVMG1R6AGS | XVMG1RA | XVMG1RAG | XVMG1RAGB | XVMG1RAGBS | XVMG1RAGS | XVMG1RAS | XVMG1RG | XVMM1R6AG | XVMM1RA | XVMM1RAG | XVMM1RAGB | XVMM1RAGBS | XVMM1RAGS | XVMM1RAS | XVMM1RG | XVMM1RGS | XVR3E03 | XVR3E04 | XVR3E05 | XVR3E06 | XVR3M04S | XVR3M05S | XVR3M06S | XVS10BMW | XVS10GMW | XVS10MMW | XVS14BMW | XVS14GMW | XVS14MMW | XVS72BMBN | XVS72BMBP | XVS72BMWN | XVS72BMWP | XVS96BMBN | XVS96BMBP | XVS96BMWN | XVS96BMWP | XVSV7BBN | XVSV7BBP | XVSV7BWN | XVSV9BBN | XVSV9BBP | XVSV9BWN | XVSV9MBN | XVSV9MWN
Section | Parameters
Complementary | 9 mm pitches | [246 empty] | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 5 | 5 | 5 | 5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 |  | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
| CAD overall depth | [154 empty] | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | 108 mm | [222 empty] | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm |  | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | [14 empty] | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | [6 empty] | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm
| CAD overall height | [154 empty] | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | 43 mm | [222 empty] | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm |  | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 157 mm | 63 mm | 63 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | 232 mm | [14 empty] | 133 mm | 133 mm | 133 mm | 133 mm | 133 mm | 133 mm | 133 mm | 133 mm | 133 mm | 133 mm | 133 mm | 133 mm | 133 mm | 133 mm | 133 mm | 133 mm | 245 mm | 245 mm | 245 mm | 245 mm | 245 mm | 245 mm | 245 mm | 245 mm | 245 mm | 245 mm | 245 mm | 245 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | 104 mm 104 mm | [6 empty] | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm | 129 mm
| CAD overall width | [154 empty] | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | 33 mm | [222 empty] | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm |  | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | [14 empty] | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | [6 empty] | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm
| Control signal pulse width | [97 empty] | 100 ms with load in parallel 30 ms | 100 ms with load in parallel 30 ms | 100 ms with load in parallel 30 ms | 100 ms with load in parallel 30 ms 100 ms with load in parallel 30 ms | 100 ms with load in parallel 30 ms | 100 ms with load in parallel 30 ms |  | 100 ms with load in parallel 30 ms |  | 100 ms with load in parallel 30 ms | 100 ms with load in parallel 30 ms |  | 30 ms 100 ms under load | 30 ms 100 ms under load | 100 ms with load in parallel 30 ms | 100 ms with load in parallel 30 ms | 30 ms 100 ms under load | 100 ms with load in parallel 30 ms | 100 ms with load in parallel 30 ms | 100 ms with load in parallel 30 ms |  | 30 ms 100 ms under load | 30 ms 100 ms under load | 30 ms 100 ms under load | 100 ms with load in parallel 30 ms | 30 ms 100 ms under load | 100 ms with load in parallel 30 ms | [19 empty] | 100 ms with load in parallel 60 ms no-load
| Maximum RF power transmitted | [143 empty] | 0.0002 mW | [161 empty] | 0.0002 mW
| Maximum communication distance | [143 empty] | 10 mm
| Minimum switching voltage | [392 empty] | 12 V | 12 V | 12 V | 12 V | 24 V | 24 V | 24 V | 24 V
| NFC operating frequency | [143 empty] | 13.56 MHz | [161 empty] | 13.56 MHz
| Power on delay | [97 empty] | 100 ms | 100 ms | 100 ms | 100 ms 100 ms | 100 ms | 100 ms | 200 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 200 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms
| Rated impulse withstand voltage | [97 empty] | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV conforming to IEC 61812-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV conforming to IEC 61812-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV conforming to IEC 61812-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV conforming to IEC 61812-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV conforming to IEC 61812-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV conforming to IEC 61812-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV conforming to IEC 61812-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | [15 empty] | 5 kV 1.2/50 µs conforming to IEC 60664-1
| Recovery time | [97 empty] | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 100 ms on de-energisation | 120 ms on de-energisation | 50 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 100 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation | [15 empty] | 120 ms on de-energisation
| Release input voltage | [97 empty] | <= 2.4 V | <= 2.4 V | <= 2.4 V | <= 2.4 V <= 2.4 V | <= 2.4 V | <= 2.4 V | <= 2.4 V | <= 2.4 V | <= 2.4 V | <= 2.4 V | <= 2.4 V | <= 2.4 V |  |  | <= 2.4 V | <= 2.4 V |  | <= 2.4 V | <= 2.4 V | <= 2.4 V | <= 2.4 V |  |  |  | <= 2.4 V |  | <= 2.4 V | <= 2.4 V | <= 38 V | <= 2.4 V | <= 2.4 V | [15 empty] | <= 2.4 V
| Run-up delay at power-up max | [305 empty] | 650 ms
| [Ie] rated operational current | [246 empty] | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C | 2 A at 24 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 2 A at 24 V DC-13 conforming to VDE 0660 70 °C 3 A at 115 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 115 V AC-15 conforming to VDE 0660 70 °C 3 A at 24 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 24 V AC-15 conforming to VDE 0660 70 °C 3 A at 250 V AC-15 conforming to IEC 60947-5-1/1991 70 °C 3 A at 250 V AC-15 conforming to VDE 0660 70 °C 0.1 A at 250 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.1 A at 250 V DC-13 conforming to VDE 0660 70 °C 0.3 A at 115 V DC-13 conforming to IEC 60947-5-1/1991 70 °C 0.3 A at 115 V DC-13 conforming to VDE 0660 70 °C | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1/1991 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1/1991 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1/1991 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1/1991 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to IEC 60947-5-1 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | 2 A at 70 °C 24 V DC-13 conforming to IEC 60947-5-1 2 A at 70 °C 24 V DC-13 conforming to VDE 0660 3 A at 70 °C 115 V AC-15 conforming to IEC 60947-5-1 3 A at 70 °C 115 V AC-15 conforming to VDE 0660 3 A at 70 °C 24 V AC-15 conforming to IEC 60947-5-1 3 A at 70 °C 24 V AC-15 conforming to VDE 0660 3 A at 70 °C 250 V AC-15 conforming to IEC 60947-5-1 3 A at 70 °C 250 V AC-15 conforming to VDE 0660 0.1 A at 70 °C 250 V DC-13 conforming to VDE 0660 0.3 A at 70 °C 115 V DC-13 conforming to IEC 60947-5-1 0.3 A at 70 °C 115 V DC-13 conforming to VDE 0660 | [19 empty] | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 12 A (AC-1/DC-1) NO conforming to IEC 6 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 6 A (AC-1/DC-1) conforming to IEC/UL | 6 A (AC-1/DC-1) conforming to IEC/UL | 6 A (AC-1/DC-1) conforming to IEC/UL | 6 A (AC-1/DC-1) conforming to IEC/UL | 6 A (AC-1/DC-1) conforming to IEC/UL | 6 A (AC-1/DC-1) conforming to IEC/UL | 6 A (AC-1/DC-1) conforming to IEC/UL | 6 A (AC-1/DC-1) conforming to IEC/UL | RSL1PRBU: 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL; RSL1PREU: 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL; RSL1PRFU: 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL; RSL1PRJU: 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL; RSL1PRPU: 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL; RSL1PVBU: 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL; RSL1PVEU: 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL; RSL1PVFU: 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL; RSL1PVJU: 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL; RSL1PVPU: 6 A 1 C/O (AC-1/DC-1) conforming to IEC/UL
| [In] rated current | [144 empty] | 5 A AC | 5 A AC | 5 A AC | 5 A AC | 5 A AC | 5 A AC | 5 A AC | 5 A AC | 5 A AC | 5 A AC
| [Ith] conventional free air thermal current | [132 empty] | 8 A | 8 A | 8 A | 5 A | 5 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | [103 empty] | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A |  |  |  |  | 8 A
| [Uc] control circuit voltage | [239 empty] | <= 3.6 V of temperature control circuit (T1-T2 terminals open) | <= 3.6 V of temperature control circuit (T1-T2 terminals open)
| [Ue] rated operational voltage | [299 empty] | >= 60 V | >= 160 V | [19 empty] | 19.2...36 V AC 50/60 Hz | 19.2...26.4 V AC 50 Hz 20.4...26.4 V AC 60 Hz | 16.8...36 V DC | 19.2...26.4 V DC | 38.4...72 V AC 50/60 Hz | 38.4...57.6 V AC 50 Hz 40.8...57.6 V AC 60 Hz | 33.6...72 V DC | 38.4...52.8 V DC | 96...180 V AC 50/60 Hz | 102...144 V AC 60 Hz 96...144 V AC 50 Hz | 77...165 V DC | 88...121 V DC | 8.4...18 V DC | 9.6...13.2 V DC | 176...330 V AC 50/60 Hz | 176...264 V AC 50 Hz 187...264 V AC 60 Hz | 42...90 V DC | 48...66 V DC | 184...345 V AC 50/60 Hz | 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz | 4.2...9 V DC | 4.8...6.6 V DC | 192...360 V AC 50/60 Hz | 192...288 V AC 50 Hz 204...288 V AC 60 Hz | 19.2...36 V AC 50/60 Hz | 19.2...26.4 V AC 50 Hz 20.4...26.4 V AC 60 Hz | 16.8...36 V DC | 19.2...26.4 V DC | 38.4...72 V AC 50/60 Hz | 38.4...57.6 V AC 50 Hz 40.8...57.6 V AC 60 Hz | 33.6...72 V DC | 38.4...52.8 V DC | 96...180 V AC 50/60 Hz | 102...144 V AC 60 Hz 96...144 V AC 50 Hz | 77...165 V DC | 88...121 V DC | 8.4...18 V DC | 9.6...13.2 V DC | 176...330 V AC 50/60 Hz | 176...264 V AC 50 Hz 187...264 V AC 60 Hz | 42...90 V DC | 48...66 V DC | 184...345 V AC 50/60 Hz | 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz | 4.2...9 V DC | 4.8...6.6 V DC | 192...360 V AC 50/60 Hz | 192...288 V AC 50 Hz 204...288 V AC 60 Hz | 19.2...36 V AC 50/60 Hz | 19.2...26.4 V AC 50 Hz 20.4...26.4 V AC 60 Hz | 16.8...36 V DC | 19.2...26.4 V DC | 38.4...72 V AC 50/60 Hz | 38.4...57.6 V AC 50 Hz 40.8...57.6 V AC 60 Hz | 33.6...72 V DC | 38.4...52.8 V DC | 96...180 V AC 50/60 Hz | 102...144 V AC 60 Hz 96...144 V AC 50 Hz | 77...165 V DC | 88...121 V DC | 8.4...18 V DC | 9.6...13.2 V DC | 176...330 V AC 50/60 Hz | 176...264 V AC 50 Hz 187...264 V AC 60 Hz | 42...90 V DC | 48...66 V DC | 184...345 V AC 50/60 Hz | 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz | 4.2...9 V DC | 4.8...6.6 V DC | 192...360 V AC 50/60 Hz | 192...288 V AC 50 Hz 204...288 V AC 60 Hz | [290 empty] | 35...60 V DC | 35...60 V DC | 35...60 V DC | 35...60 V DC | 90...253 V AC | 90...253 V AC | 90...253 V AC | [14 empty] | 10...30 V DC | 10...30 V DC | 10...30 V DC | 10...30 V DC | 10...30 V DC | 10...30 V DC | 90...264 V AC | 90...264 V AC
| [Ui] rated insulation voltage | [132 empty] | 250 V between contact circuit and control inputs IEC certified 250 V between contact circuit and power supply IEC certified 300 V between contact circuit and control inputs CSA certified 300 V between contact circuit and power supply CSA certified | 250 V between contact circuit and control inputs IEC certified 250 V between contact circuit and power supply IEC certified 300 V between contact circuit and control inputs CSA certified 300 V between contact circuit and power supply CSA certified | 250 V between contact circuit and control inputs IEC certified 250 V between contact circuit and power supply IEC certified 300 V between contact circuit and control inputs CSA certified 300 V between contact circuit and power supply CSA certified | 250 V between contact circuit and control inputs IEC certified 250 V between contact circuit and power supply IEC certified 300 V between contact circuit and control inputs CSA certified 300 V between contact circuit and power supply CSA certified | 250 V between contact circuit and control inputs IEC certified 250 V between contact circuit and power supply IEC certified 300 V between contact circuit and control inputs CSA certified 300 V between contact circuit and power supply CSA certified | 250 V between contact circuit and control inputs IEC certified 250 V between contact circuit and power supply IEC certified 300 V between contact circuit and control inputs CSA certified 300 V between contact circuit and power supply CSA certified | 250 V between contact circuit and control inputs IEC certified 250 V between contact circuit and power supply IEC certified 300 V between contact circuit and control inputs CSA certified 300 V between contact circuit and power supply CSA certified | 250 V between contact circuit and control inputs IEC certified 250 V between contact circuit and power supply IEC certified 300 V between contact circuit and control inputs CSA certified 300 V between contact circuit and power supply CSA certified | 250 V conforming to IEC 300 V conforming to CSA | 250 V conforming to IEC 300 V conforming to CSA | 250 V conforming to IEC 300 V conforming to CSA |  | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010 | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010 | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010 | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010 | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010 | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010 | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010 | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010 | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010 | 250 V conforming to IEC 255 Group C 250 V conforming to VDE 0010 | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 250 V | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 250 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1 | 250 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1 | 250 V conforming to IEC 60664-1 | 250 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 250 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1 | 250 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1 | [20 empty] | 250 V conforming to IEC 60664-1 | 250 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 250 V conforming to IEC 60664-1 |  |  | 250 V conforming to IEC 60664-1 | 250 V conforming to IEC 60664-1 | 250 V conforming to IEC 60664-1 | 250 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 250 V conforming to IEC 60664-1 600 V conforming to IEC 60664-1 | 250 V conforming to IEC 60664-1 600 V conforming to IEC 60664-1 | 250 V conforming to IEC 60664-1 600 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 500 V conforming to IEC | 2 kV | 2 kV | 2 kV | 2 kV | 400 V | 2000 V | 2000 V | 2000 V | 2000 V | 2000 V | 2000 V | 2000 V | 2000 V | 2000 V | 2 kV | 2 kV | 2 kV | 2 kV | 2 kV | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL | 250 V conforming to EN/IEC 277 V conforming to cUL |  |  | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 |  |  |  |  | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1
| [Uimp] rated impulse withstand voltage | [80 empty] | 5 kV during 1.2/50 µs | 5 kV during 1.2/50 µs | 5 kV during 1.2/50 µs | 5 kV during 1.2/50 µs | 5 kV during 1.2/50 µs | 5 kV during 1.2/50 µs | 5 kV during 1.2/50 µs | 5 kV during 1.2/50 µs | 5 kV during 1.2/50 µs | 5 kV during 1.2/50 µs | 5 kV during 1.2/50 µs | 5 kV during 1.2/50 µs | 5 kV during 1.2/50 µs | 5 kV during 1.2/50 µs | 5 kV during 1.2/50 µs | 5 kV during 1.2/50 µs | 5 kV during 1.2/50 µs | [208 empty] | 4 kV during 1.2/50 µs | [14 empty] | 3.6 kV IEC 61000-4-5 | 3.6 kV IEC 61000-4-5 | 3.6 kV IEC 61000-4-5 | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | 3.6 kV IEC 61000-4-5 | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | 3.6 kV IEC 61000-4-5 | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | 3.6 kV IEC 61000-4-5 | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | 3.6 kV IEC 61000-4-5 | 3.6 kV IEC 61000-4-5 | 3.6 kV IEC 61000-4-5 | 3.6 kV IEC 61000-4-5 | 3.6 kV IEC 61000-4-5 | 3.6 kV IEC 61000-4-5 | 3.6 kV IEC 61000-4-5 | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | 3.6 kV IEC 61000-4-5 | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | 3.6 kV IEC 61000-4-5 | IEC 61000-4-5 3.6 kV | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | 6 kV IEC | IEC 6 kV | 6 kV IEC | 6 kV IEC | IEC 6 kV | 6 kV IEC | IEC 6 kV | IEC 6 kV | 6 kV IEC | IEC 6 kV | 6 kV IEC | 6 kV IEC | 6 kV IEC | 6 kV IEC | IEC 6 kV | 6 kV IEC | IEC 6 kV | IEC 6 kV |  |  | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 4 kV IEC 60947-1 | 4 kV IEC 60947-1 4 kV IEC 60947-1 | IEC 60947-1 4 kV IEC 60947-1 4 kV | IEC 60947-1 4 kV IEC 60947-1 4 kV | 4 kV IEC 60947-1 4 kV IEC 60947-1 | 4 kV IEC 60947-1 4 kV IEC 60947-1 | 4 kV IEC 60947-1 4 kV IEC 60947-1 | 4 kV IEC 60947-1 4 kV IEC 60947-1 | IEC 60947-1 4 kV IEC 60947-1 4 kV | 4 kV IEC 60947-1 4 kV IEC 60947-1 | 4 kV IEC 60947-1 4 kV IEC 60947-1 | IEC 60947-1 4 kV IEC 60947-1 4 kV | 4 kV IEC 60947-1 4 kV IEC 60947-1 | 4 kV IEC 60947-1 4 kV IEC 60947-1 | IEC 60947-1 4 kV IEC 60947-1 4 kV | 4 kV IEC 60947-1 4 kV IEC 60947-1 | 4 kV IEC 60947-1 4 kV IEC 60947-1 | 4 kV IEC 60947-1 4 kV IEC 60947-1 | IEC 60947-1 4 kV IEC 60947-1 4 kV | 4 kV IEC 60947-1 4 kV IEC 60947-1 | 4 kV IEC 60947-1 4 kV IEC 60947-1 | IEC 60947-1 4 kV IEC 60947-1 4 kV | IEC 60947-1 4 kV IEC 60947-1 4 kV | IEC 60947-1 4 kV IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 |  |  |  |  | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | IEC 60947-1 4 kV | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | 4 kV IEC 60947-1 | 4 kV IEC 60947-1 | IEC 60947-1 4 kV | [7 empty] | 0.8 kV | 4 kV | 4 kV | 0.8 kV | 4 kV | 4 kV | 0.8 kV | 0.8 kV | 0.8 kV | 0.8 kV | 0.8 kV | 0.8 kV | 0.8 kV | 0.8 kV | 1 kV | 1 kV | 1 kV | 1 kV | 1 kV | 1 kV | 1 kV | 1 kV
| [Un] rated nominal voltage | [229 empty] | 208...480 V AC 3 phases 230 V AC single phase 208...480 V AC 3 phases 230 V AC 1 phase | [5 empty] | 24...240 V AC/DC 50/60 Hz +/- 10 % | 24...240 V AC/DC 50/60 Hz +/- 10 % | [20 empty] | 24 V AC 50/60 Hz +/- 5 % | 110...130 V AC 50/60 Hz +/- 5 % | 220...240 V AC 50/60 Hz +/- 5 % | 24...240 V DC 24...240 V AC 50/60 Hz +/- 5 % | 380...415 V AC 50/60 Hz +/- 5 % | 24 V AC 50/60 Hz +/- 5 % | 110...130 V AC 50/60 Hz +/- 5 % | 220...240 V AC 50/60 Hz +/- 5 % | 380...415 V AC 50/60 Hz +/- 5 %
| [Us] rated supply voltage | [80 empty] | 24...240 V AC/DC 50/60 Hz | 24...240 V AC 50/60 Hz | 24...240 V AC 50/60 Hz | 24...240 V AC 50/60 Hz | 24...240 V AC 50/60 Hz | 24...240 V AC 50/60 Hz 24 V DC | 24...240 V AC 50/60 Hz 24 V DC | 24...240 V AC 50/60 Hz 24 V DC | 24...240 V AC 50/60 Hz 24 V DC | 12 V AC/DC 50/60 Hz | 24...240 V AC 50/60 Hz 24 V DC | 24...240 V AC 50/60 Hz 24 V DC | 12 V AC/DC 50/60 Hz | 24...240 V AC 50/60 Hz 24 V DC | 12...240 V AC/DC 50/60 Hz | 12...240 V AC/DC 50/60 Hz | 24...240 V AC 50/60 Hz 24 V DC | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24 V DC 24...240 V AC 50/60 Hz | 380...440 V AC 230...240 V AC | 24...240 V AC 24 V DC | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC 24 V DC | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 12 V AC/DC | 24...240 V AC 24 V DC | 12...240 V AC/DC | 24...240 V AC/DC 50/60 Hz | 24...240 V AC 24 V DC | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 380...415 V AC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz |  |  |  |  | 110...240 V AC 50/60 Hz 24 V AC/DC 50/60 Hz 42...48 V AC/DC 50/60 Hz | 110...240 V AC 50/60 Hz 24 V AC/DC 50/60 Hz 42...48 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 110...240 V AC 50/60 Hz 24 V AC/DC 50/60 Hz | 110...240 V AC 50/60 Hz 24 V AC/DC 50/60 Hz 42...48 V AC/DC 50/60 Hz | 110...240 V AC 50/60 Hz 24 V AC/DC 50/60 Hz 42...48 V AC/DC 50/60 Hz | 110...240 V AC 50/60 Hz 24 V AC/DC 50/60 Hz | 110...240 V AC 50/60 Hz 24 V AC/DC 50/60 Hz | 110...240 V AC 50/60 Hz 24 V AC/DC 50/60 Hz | 24...240 V AC/DC | 24 V AC 50/60 Hz | 24 V DC | 120 V AC 50/60 Hz | 12 V DC | 230 V AC 50/60 Hz | 24 V AC 50/60 Hz | 24 V DC | 120 V AC 50/60 Hz | 12 V DC | 230 V AC 50/60 Hz | [38 empty] | 24...240 V AC/DC 50/60 Hz +/- 10 % | [6 empty] | 12 V DC +/- 10 % | 110...240 V AC/DC 50/60 Hz +/- 10 % | 220 V AC 50 Hz +/- 10 % | 24...48 V AC/DC 50/60 Hz +/- 10 % | 208...480 V AC 50/60 Hz +/- 10 % | 110...240 V AC/DC 50/60 Hz +/- 10 % | 24...48 V AC/DC 50/60 Hz +/- 10 % | 24...240 V AC/DC 50/60 Hz +/- 10 % | 24...240 V AC/DC 50/60 Hz +/- 10 % | 24...240 V AC/DC 50/60 Hz | 380...415 V AC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 380...415 V AC 50/60 Hz | 200...240 V AC | 380...480 V AC | 208...480 V AC | 200...240 V AC | 380...480 V AC | 200...240 V AC | 380...480 V AC | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 110...240 V AC 50/60 Hz | 24...240 V AC/DC 24...240 V AC/DC | 24...240 V AC/DC 24...240 V AC/DC | 24...240 V AC/DC 24...240 V AC/DC |  | 120...277 V AC 120...277 V AC | 24...240 V AC/DC 50/60 Hz +/- 10 % | 24...240 V AC/DC 50/60 Hz +/- 10 % | 380...415 V AC 50/60 Hz +/- 10 % | 24...240 V AC/DC 50/60 Hz +/- 10 % | [6 empty] | 24...240 V AC/DC 50/60 Hz +/- 10 % | 24...240 V AC/DC 50/60 Hz +/- 10 % | 24...240 V AC/DC 50/60 Hz +/- 10 % | 220...480 V AC 50/60 Hz +/- 10 % | 120...277 V AC 50/60 Hz +/- 10 % | 24 V AC 50/60 Hz +/- 5 % | 110...130 V AC 50/60 Hz +/- 5 % | 220...240 V AC 50/60 Hz +/- 5 % | 110...130 V AC 50/60 Hz +/- 5 % | 220...240 V AC 50/60 Hz +/- 5 % | 24...240 V AC 50/60 Hz +/- 5 % 24...240 V DC | 380...415 V AC 50/60 Hz +/- 5 % | 110...130 V AC 50/60 Hz +/- 5 % | 220...240 V AC 50/60 Hz +/- 5 % | 24...240 V AC 50/60 Hz +/- 5 % 24...240 V DC | 380...415 V AC 50/60 Hz +/- 5 % | [21 empty] | 24 V AC 50/60 Hz +/- 5 % | 110...130 V AC 50/60 Hz +/- 5 % | 220...240 V AC 50/60 Hz +/- 5 % | 24 V AC 50/60 Hz +/- 5 % | 110...130 V AC 50/60 Hz +/- 5 % | 220...240 V AC 50/60 Hz +/- 5 % | 24 V AC 50/60 Hz +/- 5 % | 110...130 V AC 50/60 Hz +/- 5 % | 220...240 V AC 50/60 Hz +/- 5 % | 110...130 V AC 50/60 Hz +/- 5 % | 220...240 V AC 50/60 Hz +/- 5 % | 24...240 V AC 50/60 Hz +/- 5 % 24...240 V DC | 380...415 V AC 50/60 Hz +/- 5 % | 110...130 V AC 50/60 Hz +/- 5 % | 220...240 V AC 50/60 Hz +/- 5 % | 24...240 V AC 50/60 Hz +/- 5 % 24...240 V DC | 380...415 V AC 50/60 Hz +/- 5 % | 110...130 V AC 50/60 Hz +/- 5 % | 220...240 V AC 50/60 Hz +/- 5 % | 24...240 V AC 50/60 Hz +/- 5 % 24...240 V DC | 380...415 V AC 50/60 Hz +/- 5 % | 80...220 V AC/DC | 160...300 V AC | 24 V DC +/- 20 %, isolated | 24 V DC +/- 20 %, isolated | 24 V DC +/- 20 %, non isolated | 24 V DC +/- 20 %, isolated | 208...480 V AC line to line 120...277 V AC line to neutral | 24 V DC non isolated +/- 20 % | 24 V DC non isolated +/- 20 % | 24 V DC non isolated +/- 20 % | 24 V DC non isolated +/- 20 % | 24 V DC non isolated +/- 20 % | 24 V DC non isolated +/- 20 % | 24 V DC non isolated +/- 20 % | 24 V DC non isolated +/- 20 % | 24 V DC non isolated +/- 20 % | 24 V DC +/- 20 %, non isolated | 24 V DC +/- 20 %, non isolated | 24 V DC +/- 20 %, non isolated | 24 V DC +/- 20 %, non isolated | 24 V DC +/- 20 %, non isolated | [80 empty] | XVBC21A: External: 19.2...30 V AS-Interface line: 24...31.6 V; XVBC21B: External: 19.2...30 V AS-Interface line: 24...31.6 V | [138 empty] | 48 V DC | 48 V DC | 48 V DC | 48 V DC | 100...230 V AC | 100...230 V AC | 100...230 V AC | [6 empty] | 12...24 V DC | 12...24 V DC | 12...24 V DC | 12...24 V DC | 12...24 V DC | 12...24 V DC | 12...24 V DC | 12...24 V DC | 12...24 V DC | 12...24 V DC | 12...24 V DC | 12...24 V DC | 12...24 V DC | 12...24 V DC | 100...230 V AC | 100...230 V AC
| abnormal analogue output current | [301 empty] | -30…0 mA, output selected 0...20 mA no input or input wire broken 4…30 mA, output selected 4...20 mA no input or input wire broken | 22…30 mA, output selected 0...20 mA no input or input wire broken voltage 22…30 mA, output selected 4...20 mA no input or input wire broken voltage -30…0 mA, output selected 0...20 mA no input or input wire broken current 4…30 mA, output selected 4...20 mA no input or input wire broken current | 4…30 mA no input or input wire broken | -30…0 mA, output selected 0...20 mA no input or input wire broken 4…30 mA, output selected 4...20 mA no input or input wire broken |  | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken | -30…0 mA when no input or input wire broken 22…30 mA when no input or input wire broken | -30…0 mA when no input or input wire broken | -30…0 mA when no input or input wire broken | -30…0 mA when no input or input wire broken | -30…0 mA when no input or input wire broken | -30…0 mA when no input or input wire broken
| abnormal analogue output voltage | [301 empty] | -15...0 V no input or input wire broken | 11...15 V, output selected - 10...10 V no input or input wire broken voltage 11...15 V, output selected 0...10 V no input or input wire broken voltage -15...0 V, output selected 0...20 mA no input or input wire broken current -15...0 V, output selected 4...20 mA no input or input wire broken current | -15...0 V no input or input wire broken | -15...0 V no input or input wire broken |  | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
| actuator sensor interface profile [AS-i] | [400 empty] | XVBC21A: S.7.F; XVBC21B: S.7.F
| adjustment of asymmetry threshold | [193 empty] | 5...15 % of Un selected | 5...15 % of Un selected |  |  | 5...15 % of Un selected | 5...15 % of Un selected | [13 empty] | 5...15 % of Un selected | 5...15 % of Un selected | [24 empty] | 5...15 % of Un selected | [27 empty] | 5...15 % | 5...15 % | 5...15 % | 5...15 %
| alarm threshold | [305 empty] | 166...576 V adjustable overvoltage and undervoltage detection (line to line) 96...332 V adjustable overvoltage and undervoltage detection (line to neutral) 5...150 V adjustable asymmetry 45...66 Hz adjustable overfrequency or underfrequency
| assembly style | [400 empty] | XVBC07: Customer assembly, up to 5 units; XVBC21: Customer assembly, up to 5 units; XVBC21A: Customer assembly, up to 5 units; XVBC21B: Customer assembly, up to 5 units; XVBC6B3: Customer assembly, up to 5 units; XVBC6B4: Customer assembly, up to 5 units; XVBC6B5: Customer assembly, up to 5 units; XVBC6B6: Customer assembly, up to 5 units; XVBC6B7: Customer assembly, up to 5 units; XVBC6B8: Customer assembly, up to 5 units; XVBC6G3: Customer assembly, up to 5 units; XVBC6G4: Customer assembly, up to 5 units; XVBC6G5: Customer assembly, up to 5 units; XVBC6G6: Customer assembly, up to 5 units; XVBC6G7: Customer assembly, up to 5 units; XVBC6G8: Customer assembly, up to 5 units; XVBC6M3: Customer assembly, up to 5 units; XVBC6M4: Customer assembly, up to 5 units; XVBC6M5: Customer assembly, up to 5 units; XVBC6M6: Customer assembly, up to 5 units; XVBC6M7: Customer assembly, up to 5 units; XVBC6M8: Customer assembly, up to 5 units; XVBC8B3: Customer assembly, up to 5 units; XVBC8B4: Customer assembly, up to 5 units; XVBC8B5: Customer assembly, up to 5 units; XVBC8B6: Customer assembly, up to 5 units; XVBC8B7: Customer assembly, up to 5 units; XVBC8B8: Customer assembly, up to 5 units; XVBC8E5: Customer assembly, up to 5 units; XVBC8G3: Customer assembly, up to 5 units; XVBC8G4: Customer assembly, up to 5 units; XVBC8G5: Customer assembly, up to 5 units; XVBC8G6: Customer assembly, up to 5 units; XVBC8G7: Customer assembly, up to 5 units; XVBC8G8: Customer assembly, up to 5 units; XVBC8M3: Customer assembly, up to 5 units; XVBC8M4: Customer assembly, up to 5 units; XVBC8M5: Customer assembly, up to 5 units; XVBC8M6: Customer assembly, up to 5 units; XVBC8M7: Customer assembly, up to 5 units; XVBC8M8: Customer assembly, up to 5 units; XVBC9B: Customer assembly, up to 5 units; XVBC9M: Customer assembly, up to 5 units | [13 empty] | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | Customer assembly | [97 empty] | Ready assembled | Ready assembled | Ready assembled | Ready assembled | Ready assembled | Ready assembled | Ready assembled | [14 empty] | Ready assembled | Ready assembled | Ready assembled | Ready assembled | Ready assembled | Ready assembled | Ready assembled | Ready assembled
| associated fuse rating | [703 empty] | 1 A | 1 A | 1 A | 1 A | 1 A | 1 A | 1 A | 1 A
| average coil consumption | [157 empty] | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C |  | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C |  |  |  | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C |  | 2.5 W at 20 °C | 2.5 W at 20 °C | 2.5 W at 20 °C | [128 empty] | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.45 W DC | 0.45 W DC | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.45 W DC | 0.45 W DC | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.45 W DC | 0.45 W DC | 0.45 W DC | 0.45 W DC | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.45 W DC | 0.45 W DC | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.45 W DC | 0.45 W DC | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.45 W DC | 0.45 W DC | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.45 W DC | 0.45 W DC | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.45 W DC | 0.45 W DC | 0.45 W DC | 0.45 W DC | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.45 W DC | 0.45 W DC | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.45 W DC | 0.45 W DC | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.45 W DC | 0.45 W DC | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.45 W DC | 0.45 W DC | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.45 W DC | 0.45 W DC | 0.45 W DC | 0.45 W DC | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.45 W DC | 0.45 W DC | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.45 W DC | 0.45 W DC | 0.75 VA AC | 0.75 VA AC 60 Hz | 0.17 W | 0.21 W | 0.17 W | 0.21 W | 0.17 W | 0.21 W | 0.17 W | 0.21 W | RSL1PRBU: 0.17 W, DC; RSL1PREU: 0.17 W, DC; RSL1PRFU: 0.17 W, DC; RSL1PRJU: 0.17 W, DC; RSL1PRPU: 0.17 W, DC; RSL1PVBU: 0.17 W, DC; RSL1PVEU: 0.17 W, DC; RSL1PVFU: 0.17 W, DC; RSL1PVJU: 0.17 W, DC; RSL1PVPU: 0.17 W, DC
| average coil consumption in VA | [154 empty] | 3.5 at 20 °C | 3.5 at 20 °C | 3.5 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 3.5 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 3.5 at 20 °C | 3.5 at 20 °C | 3.5 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 3.5 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C | 2.9 at 20 °C
| average coil resistance | [320 empty] | 368 Ohm network: AC at 20 °C +/- 10 % | 400 Ohm network: AC at 20 °C +/- 15 % | 1440 Ohm network: AC at 20 °C +/- 10 % | 1440 Ohm network: DC at 20 °C +/- 10 % | 1540 Ohm network: AC at 20 °C +/- 10 % | 1550 Ohm network: AC at 20 °C +/- 15 % | 5520 Ohm network: AC at 20 °C +/- 10 % | 5700 Ohm network: DC at 20 °C +/- 10 % | 8360 Ohm network: AC at 20 °C +/- 10 % | 10200 Ohm network: AC at 20 °C +/- 15 % | 30250 Ohm network: AC at 20 °C +/- 10 % | 25200 Ohm network: DC at 20 °C +/- 10 % | 360 Ohm network: DC at 20 °C +/- 10 % | 360 Ohm network: DC at 20 °C +/- 10 % | 33000 Ohm network: AC at 20 °C +/- 10 % | 35500 Ohm network: AC at 20 °C +/- 15 % | 9000 Ohm network: AC at 20 °C +/- 10 % | 7500 Ohm network: DC at 20 °C +/- 10 % | 33000 Ohm network: AC at 20 °C +/- 10 % | 38500 Ohm network: AC at 20 °C +/- 15 % | 90 Ohm network: AC at 20 °C +/- 10 % | 90 Ohm network: DC at 20 °C +/- 10 % | 33000 Ohm network: AC at 20 °C +/- 10 % | 42500 Ohm network: AC at 20 °C +/- 15 % | 368 Ohm network: AC at 20 °C +/- 10 % | 400 Ohm network: AC at 20 °C +/- 15 % | 1440 Ohm network: AC at 20 °C +/- 10 % | 1440 Ohm network: DC at 20 °C +/- 10 % | 1540 Ohm network: AC at 20 °C +/- 10 % | 1550 Ohm network: AC at 20 °C +/- 15 % | 5520 Ohm network: AC at 20 °C +/- 10 % | 5700 Ohm network: DC at 20 °C +/- 10 % | 8360 Ohm network: AC at 20 °C +/- 10 % | 10200 Ohm network: AC at 20 °C +/- 15 % | 30250 Ohm network: AC at 20 °C +/- 10 % | 25200 Ohm network: DC at 20 °C +/- 10 % | 360 Ohm network: AC at 20 °C +/- 10 % | 360 Ohm network: DC at 20 °C +/- 10 % | 33000 Ohm network: AC at 20 °C +/- 10 % | 35500 Ohm network: AC at 20 °C +/- 15 % | 9000 Ohm network: AC at 20 °C +/- 10 % | 7500 Ohm network: DC at 20 °C +/- 10 % | 33000 Ohm network: AC at 20 °C +/- 10 % | 38500 Ohm network: AC at 20 °C +/- 15 % | 90 Ohm network: AC at 20 °C +/- 10 % | 90 Ohm network: DC at 20 °C +/- 10 % | 33000 Ohm network: AC at 20 °C +/- 10 % | 42500 Ohm network: AC at 20 °C +/- 15 % | 368 Ohm network: AC at 20 °C +/- 10 % | 400 Ohm network: AC at 20 °C +/- 15 % | 1440 Ohm network: DC at 20 °C +/- 10 % | 1440 Ohm network: DC at 20 °C +/- 10 % | 1540 Ohm network: AC at 20 °C +/- 10 % | 1550 Ohm network: AC at 20 °C +/- 15 % | 5520 Ohm network: AC at 20 °C +/- 10 % | 5700 Ohm network: DC at 20 °C +/- 10 % | 8360 Ohm network: AC at 20 °C +/- 10 % | 10200 Ohm network: AC at 20 °C +/- 15 % | 30250 Ohm network: AC at 20 °C +/- 10 % | 25200 Ohm network: DC at 20 °C +/- 10 % | 360 Ohm network: AC at 20 °C +/- 10 % | 360 Ohm network: DC at 20 °C +/- 10 % | 33000 Ohm network: AC at 20 °C +/- 10 % | 35500 Ohm network: AC at 20 °C +/- 15 % | 9000 Ohm network: AC at 20 °C +/- 10 % | 7500 Ohm network: DC at 20 °C +/- 10 % | 33000 Ohm network: AC at 20 °C +/- 10 % | 38500 Ohm network: AC at 20 °C +/- 15 % | 90 Ohm network: AC at 20 °C +/- 10 % | 90 Ohm network: DC at 20 °C +/- 10 % | 33000 Ohm network: AC at 20 °C +/- 10 % | 42500 Ohm network: AC at 20 °C +/- 15 %
| average resistance | [154 empty] | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C | [200 empty] | 3390 Ohm at 23 °C +/- 15 % | 10600 Ohm at 23 °C +/- 15 % | 848 Ohm at 23 °C +/- 10 % | 16600 Ohm at 23 °C +/- 15 % | 3390 Ohm at 23 °C +/- 15 % | 10600 Ohm at 23 °C +/- 15 % | 848 Ohm at 23 °C +/- 10 % | 16600 Ohm at 23 °C +/- 15 % | RSL1PRBU: 3390 Ohm network: DC at 23 °C +/- 10 %; RSL1PREU: 10600 Ohm network: DC at 23 °C +/- 10 %; RSL1PRFU: 20500 Ohm network: DC at 23 °C +/- 10 %; RSL1PRJU: 848 Ohm network: DC at 23 °C +/- 10 %; RSL1PRPU: 20500 Ohm network: DC at 23 °C +/- 10 %; RSL1PVBU: 3390 Ohm network: DC at 23 °C +/- 10 %; RSL1PVEU: 10600 Ohm network: DC at 23 °C +/- 10 %; RSL1PVFU: 20500 Ohm network: DC at 23 °C +/- 10 %; RSL1PVJU: 848 Ohm network: DC at 23 °C +/- 10 %; RSL1PVPU: 20500 Ohm network: DC at 23 °C +/- 10 %
| breaking capacity | [80 empty] | 0.5 A AC/DC conforming to UL 0.7 A AC/DC at 20 °C | 0.5 A AC/DC conforming to UL 0.7 A AC/DC at 20 °C | 0.5 A AC/DC conforming to UL 0.7 A AC/DC at 20 °C | 0.5 A AC conforming to UL 0.7 A AC at 20 °C | 0.5 A AC conforming to UL 0.7 A AC at 20 °C | 2000 VA | 2000 VA | 2000 VA | 2000 VA | 2000 VA | 2000 VA | 2000 VA | 2000 VA | 2000 VA | 2000 VA | 2000 VA | 2000 VA | [12 empty] | 2000 VA | 2000 VA |  |  | 2000 VA |  |  |  |  | 2000 VA | 2000 VA | 2000 VA |  | 2000 VA | [5 empty] | 1250 VA | 1250 VA | 1250 VA | 1250 VA
| bulb base | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d
| cable capacitance | [208 empty] | 1 nF at HS (High Sensitivity) for probe cable 2.2 nF at St (Standard Sensitivity) for probe cable 4.7 nF at LS (Low Sensitivity) for probe cable | 1 nF at HS (High Sensitivity) for probe cable 2.2 nF at St (Standard Sensitivity) for probe cable 4.7 nF at LS (Low Sensitivity) for probe cable | 1 nF at HS (High Sensitivity) for probe cable 2.2 nF at St (Standard Sensitivity) for probe cable 4.7 nF at LS (Low Sensitivity) for probe cable | 1 nF at HS (High Sensitivity) for probe cable 2.2 nF at St (Standard Sensitivity) for probe cable 4.7 nF at LS (Low Sensitivity) for probe cable | [23 empty] | 1 nF at HS (High Sensitivity) for probe cable 2.2 nF at St (Standard Sensitivity) for probe cable 4.7 nF at LS (Low Sensitivity) | 10 nF for probe cable
| cable entry | [400 empty] | XVBC07: Bottom or side entry; XVBC21: Bottom or side entry; XVBC21A: Side entry; XVBC21B: Side entry | [41 empty] | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7
| clamping connection capacity | [301 empty] | 2 x 1.5 mm² 1 x 2.5 mm² | 2 x 1.5 mm² 1 x 2.5 mm² | 1 x 2.5 mm² 2 x 1.5 mm² | 1 x 2.5 mm² 2 x 1.5 mm² |  | 1 x 2.5 mm² 2 x 1.5 mm² | 1 x 2.5 mm² 2 x 1.5 mm² | 1 x 2.5 mm² 2 x 1.5 mm² | 2 x 1.5 mm² 1 x 2.5 mm² | 1 x 2.5 mm² 2 x 1.5 mm² | 2 x 1.5 mm² 1 x 2.5 mm² | 2 x 1.5 mm² 1 x 2.5 mm² | 1 x 2.5 mm² 2 x 1.5 mm² | 2 x 1.5 mm² 1 x 2.5 mm² | 2 x 1.5 mm² 1 x 2.5 mm² | 2 x 1.5 mm² 1 x 2.5 mm² | 2 x 1.5 mm² 1 x 2.5 mm² | 1 x 2.5 mm² 2 x 1.5 mm² | 2 x 1.5 mm² 1 x 2.5 mm² | [369 empty] | <= 1 x 1.5 mm² | <= 1 x 1.5 mm² | <= 1 x 1.5 mm² |  |  |  | <= 1 x 1.5 mm² | <= 1 x 1.5 mm² | <= 1 x 1.5 mm² | <= 1 x 1.5 mm² | <= 1 x 1.5 mm² | <= 1 x 1.5 mm² | <= 1 x 1.5 mm² | <= 1 x 1.5 mm² | <= 1 x 1.5 mm² | <= 1 x 1.5 mm² | <= 1 x 1.5 mm² | <= 1 x 1.5 mm² | <= 1 x 1.5 mm² | <= 1 x 1.5 mm² | <= 1 x 1.5 mm² | <= 1 x 1.5 mm²
| clamping force | [400 empty] | RSL1PRBU: 10…40 N; RSL1PREU: 10…40 N; RSL1PRFU: 10…40 N; RSL1PRJU: 10…40 N; RSL1PRPU: 10…40 N
| cold junction compensation | [315 empty] | Built-in, measurement: between 0 and 60 °C | Built-in, measurement: between 0 and 60 °C | Built-in, measurement: between 0 and 60 °C | Built-in, measurement: between 0 and 60 °C | Built-in, measurement: between 0 and 60 °C
| colour | [692 empty] | White | White | White | Black | Black | White | White | Black | Black | White | White | Dark grey | Dark grey | White | Dark grey | Dark grey | White | Dark grey | White
| compatibility code | [80 empty] | RE17 | RE17 | RE17 | RE17 | RE17 | RE17 | RE17 | RE17 | RE17 | RE17 | RE17 | RE17 | RE17 | RE17 | RE17 | RE17 | RE17 | [102 empty] | RM17 | RM17 | RM17 | RM17 | RM17 | RM17 | RM17 | [35 empty] | RM3 | RM3 | RM3 | RM3 | RM3 | [32 empty] | RM4 | RM4 | RM4 | RM4 | RM4 | RM4 | RM4 | RM4 | RM4 | RM4 | RM4 | RM4 | RM4 | RM4 | RM4 | RM4 | RM4 | RM4 | RM4 | RM4 | RM4
| connections - terminals | [80 empty] | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Spring terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) solid without cable end Spring terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 2 x 1.5 mm² with cable end Screw terminals, 2 x 2.5 mm² without cable end | Screw terminals, 2 x 1.5 mm² with cable end Screw terminals, 2 x 2.5 mm² without cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 2 x 1.5 mm² with cable end Screw terminals, 2 x 2.5 mm² without cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 2 x 1.5 mm² with cable end Screw terminals, 2 x 2.5 mm² without cable end | Screw terminals, 2 x 1.5 mm² with cable end Screw terminals, 2 x 2.5 mm² without cable end | Screw terminals, 2 x 1.5 mm² with cable end Screw terminals, 2 x 2.5 mm² without cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 2 x 1.5 mm² with cable end Screw terminals, 2 x 2.5 mm² without cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end |  |  |  |  | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end | Screw terminals, 2 x 1.5 mm² flexible with cable end Screw terminals, 2 x 2.5 mm² flexible without cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | [48 empty] | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | Screw terminals, 2 x 1.5 mm²flexible with cable end Screw terminals, 2 x 2.5 mm²flexible without cable end | [6 empty] | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 2 x 0.5...2 x 1.5 mm² (AWG 20...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 1 x 0.5...1 x 2.5 mm² (AWG 20...AWG 14) flexible with cable end | [94 empty] | Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) solid without cable end | Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) solid without cable end | Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) solid without cable end | Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) solid without cable end | Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Spring terminals, 1 x 0.2...1 x 1.5 mm² (AWG 24...AWG 16) solid without cable end | Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) solid without cable end | Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) solid without cable end | Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) solid without cable end | Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) solid without cable end | Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw connectors, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) solid without cable end |  |  |  |  | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Screw terminals, 1 x 0.325...1 x 1.5 mm² | Screw terminals, 1 x 0.325...1 x 1.5 mm² | Screw terminals, 1 x 0.325...1 x 1.5 mm² | Screw terminals, 1 x 0.325...1 x 1.5 mm² | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22) | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
| contact bounce time | [154 empty] | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms | <= 10 ms
| contact terminal arrangement | [400 empty] | RSL1PRBU: Separate; RSL1PREU: Separate; RSL1PRFU: Separate; RSL1PRJU: Separate; RSL1PRPU: Separate; RSL1PVBU: Separate; RSL1PVEU: Separate; RSL1PVFU: Separate; RSL1PVJU: Separate; RSL1PVPU: Separate
| contacts material | [85 empty] | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | [35 empty] | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | Silver with gold flashed contacts | Silver with gold flashed contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | Silver nickel contacts | Silver nickel contacts | Silver nickel contacts |  | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | [38 empty] | Cadmium free | [13 empty] | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free |  | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free |  |  | Cadmium free | [8 empty] | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts | 90/10 silver nickel contacts |  |  |  |  | Cadmium free | [14 empty] | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgNi) | Silver alloy (Ag/Ni) | Silver alloy (AgSnO2) | Silver alloy (AgSnO2) | Silver alloy (AgSnO2) | Silver alloy (AgSnO2) | Silver alloy - gold plated (AgSnO2) | Silver alloy - gold plated (AgSnO2) | Silver alloy - gold plated (AgSnO2) | Silver alloy - gold plated (AgSnO2) | RSL1PRBU: Silver alloy (AgSnO2); RSL1PREU: Silver alloy (AgSnO2); RSL1PRFU: Silver alloy (AgSnO2); RSL1PRJU: Silver alloy (AgSnO2); RSL1PRPU: Silver alloy (AgSnO2); RSL1PVBU: Silver alloy (AgSnO2); RSL1PVEU: Silver alloy (AgSnO2); RSL1PVFU: Silver alloy (AgSnO2); RSL1PVJU: Silver alloy (AgSnO2); RSL1PVPU: Silver alloy (AgSnO2)
| contacts type and composition | [85 empty] | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O timed contact, cadmium free | 1 C/O timed contact, cadmium free | 1 C/O timed contact, cadmium free | 1 C/O timed contact, cadmium free 1 C/O timed contact, cadmium free | 1 C/O timed contact, cadmium free | 1 C/O timed contact, cadmium free | 1 C/O timed contact, cadmium free | 1 C/O timed contact, cadmium free | 1 C/O timed contact, cadmium free | 1 C/O timed contact, cadmium free | 1 C/O timed contact, cadmium free | 1 C/O timed contact, cadmium free | 1 C/O timed contact | 1 C/O timed contact | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free | 2 C/O timed contact | 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free | 2 C/O timed contact, cadmium free | 1 C/O timed contact 1 C/O timed or instantaneous contact | 1 C/O timed contact 1 C/O timed or instantaneous contact | 1 C/O timed contact 1 C/O timed or instantaneous contact | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free | 1 C/O timed contact 1 C/O timed or instantaneous contact | 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free | 2 C/O timed contact, cadmium free | 2 C/O timed contact, cadmium free | 2 C/O timed contact, cadmium free | 2 C/O timed contact, cadmium free | [15 empty] | 2 C/O timed contact, cadmium free 1 C/O timed and instantaneous contact, cadmium free
| control circuit frequency | [192 empty] | 40...70 Hz sinusoidal | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % |  | 50...60 Hz +/- 10 % | 50 Hz +/- 10 % | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % | [24 empty] | 40...70 Hz | 40...70 Hz +/- 10 % |  |  | 40...70 Hz +/- 10 % |  |  |  | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % | 40...70 Hz +/- 10 % | 40...70 Hz +/- 10 % | 40...70 Hz +/- 10 % | 50...60 Hz +/- 15 % | 50...60 Hz +/- 15 %
| control circuit voltage limits | [154 empty] | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 |  | - 12 % + 10 % Un | - 12 % + 10 % Un | - 12 % + 10 % Un | - 12 % + 10 % Un | - 12 % + 10 % Un | - 12 % + 10 % Un | [39 empty] | - 12 % + 10 % Un | [60 empty] | 0.85...1.1 Uc | 0.85...1.1 Uc
| control signal pulse width | [80 empty] | 0.05 s typical | 0.05 s typical | 0.05 s typical | 0.05 s typical | 0.05 s typical | 100 ms with load in parallel typical 30 ms typical | 100 ms with load in parallel typical 30 ms typical | 100 ms with load in parallel typical 30 ms typical | 100 ms with load in parallel typical 30 ms typical | 100 ms with load in parallel typical 30 ms typical | 100 ms with load in parallel typical 30 ms typical | 100 ms with load in parallel typical 30 ms typical | 100 ms with load in parallel typical 30 ms typical | 100 ms with load in parallel typical 30 ms typical | 100 ms with load in parallel typical 30 ms typical | 100 ms with load in parallel typical 30 ms typical | 100 ms with load in parallel typical 30 ms typical
| control threshold overvoltage | [271 empty] | 220...300 V | 420...480 V | 242 V | 440 V | [24 empty] | 160...220 V | 220...300 V
| control threshold undervoltage | [271 empty] | 160…220 V | 300…430 V | 198 V |  |  | 160…220 V | 300…430 V | [21 empty] | 80…120 V | 160…220 V 50/60 Hz
| control type | [80 empty] | Selector switch front panel | Selector switch front panel | Selector switch front panel | Selector switch front panel | Selector switch front panel | Selector switch front panel | Selector switch front panel | Selector switch front panel | Selector switch front panel | Selector switch front panel | Selector switch front panel | Selector switch front panel | Selector switch front panel | Selector switch front panel | Selector switch front panel | Selector switch front panel | Selector switch front panel | Rotary knob Diagnostic button Potentiometer external | Rotary knob Diagnostic button Potentiometer external | Rotary knob Diagnostic button | Rotary knob Diagnostic button Potentiometer external Rotary knob Diagnostic button Potentiometer external | Rotary knob Diagnostic button | Rotary knob Diagnostic button | Rotary knob | Rotary knob Diagnostic button Potentiometer external | Rotary knob | Rotary knob Diagnostic button Potentiometer external | Rotary knob Diagnostic button Potentiometer external | Rotary knob Diagnostic button | Rotary knob front panel | Rotary knob front panel | Rotary knob Diagnostic button | Rotary knob Diagnostic button Potentiometer external | Rotary knob front panel | Rotary knob Diagnostic button | Rotary knob Diagnostic button Potentiometer external | Rotary knob Diagnostic button Potentiometer external | Rotary knob Potentiometer external | Rotary knob front panel | Rotary knob front panel | Rotary knob front panel | Rotary knob Diagnostic button Potentiometer external | Rotary knob front panel | Rotary knob Diagnostic button Potentiometer external | Rotary knob Diagnostic button | Rotary knob Diagnostic button | Rotary knob Diagnostic button | Rotary knob Diagnostic button | Selector switch front panel | Selector switch front panel | Selector switch front panel | Selector switch front panel | [268 empty] | RSL1PRBU: Without push-button; RSL1PREU: Without push-button; RSL1PRFU: Without push-button; RSL1PRJU: Without push-button; RSL1PRPU: Without push-button; RSL1PVBU: Without push-button; RSL1PVEU: Without push-button; RSL1PVFU: Without push-button; RSL1PVJU: Without push-button; RSL1PVPU: Without push-button
| creepage distance | [80 empty] | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 |  |  | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 |  | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 |  |  |  | 4 kV/3 conforming to IEC 60664-1 |  | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | [15 empty] | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1
| current consumption | 47 mA | 47 mA | 47 mA | 47 mA | 47 mA | 47 mA | 17 mA | 17 mA | 17 mA | 17 mA | 17 mA | 17 mA | 17 mA | 17 mA | 17 mA | 17 mA | 17 mA | 17 mA | [8 empty] | 47 mA | 47 mA | 47 mA | 47 mA | 47 mA | 47 mA | 17 mA | 17 mA | 17 mA | 17 mA | 17 mA | 17 mA | 17 mA | 17 mA | 17 mA | 17 mA | 17 mA | 17 mA | [257 empty] | <= 70 mA for voltage output <= 90 mA for current output | <= 70 mA for voltage output <= 90 mA for current output | <= 40 mA for voltage output <= 60 mA for current output | <= 70 mA for voltage output <= 90 mA for current output |  | <= 40 mA for voltage output <= 60 mA for current output | <= 40 mA for voltage output <= 60 mA for current output | <= 40 mA for voltage output <= 60 mA for current output | <= 40 mA for voltage output <= 60 mA for current output | <= 40 mA for voltage output <= 60 mA for current output | <= 40 mA for voltage output <= 60 mA for current output | <= 40 mA for voltage output <= 60 mA for current output | <= 40 mA for voltage output <= 60 mA for current output | <= 40 mA for voltage output <= 60 mA for current output | <= 60 mA for current output | <= 40 mA for voltage output <= 60 mA for current output | <= 40 mA for voltage output <= 60 mA for current output | <= 40 mA for voltage output <= 60 mA for current output | <= 40 mA for voltage <= 40 mA for voltage output <= 60 mA for current | [92 empty] | 250 mA under load via AS-Interface line 30 mA under load external 30 mA no load | 250 mA under load via AS-Interface line 30 mA under load external 30 mA no load | < 350 mA DC < 550 mA AC | < 350 mA DC < 550 mA AC | < 350 mA DC < 550 mA AC | < 350 mA DC < 550 mA AC | < 350 mA DC < 550 mA AC | < 350 mA DC < 550 mA AC | < 140 mA AC | < 140 mA AC | < 140 mA AC | < 140 mA AC | < 140 mA AC | < 140 mA AC | < 105 mA AC | < 105 mA AC | < 105 mA AC | < 105 mA AC | < 105 mA AC | < 105 mA AC | < 1300 mA AC < 850 mA DC | < 1300 mA AC < 850 mA DC | < 1300 mA AC < 850 mA DC | < 1300 mA AC < 850 mA DC | < 1300 mA AC < 850 mA DC | < 1300 mA AC < 850 mA DC | < 400 mA DC < 650 mA AC | < 290 mA AC | < 290 mA AC | < 290 mA AC | < 290 mA AC | < 290 mA AC | < 290 mA AC | < 280 mA AC | < 280 mA AC | < 280 mA AC | < 280 mA AC | < 280 mA AC | < 280 mA AC | < 15 mA | < 25 mA | < 47 mA AC/DC | < 47 mA AC/DC | < 47 mA AC/DC | < 47 mA AC/DC | < 47 mA AC/DC | < 47 mA AC/DC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 47 mA AC/DC | < 47 mA AC/DC | < 47 mA AC/DC | < 47 mA AC/DC | < 47 mA AC/DC | < 47 mA AC/DC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | < 17 mA AC | [18 empty] | < 350 mA DC < 550 mA AC | < 350 mA DC < 550 mA AC | < 350 mA DC < 550 mA AC | < 350 mA DC < 550 mA AC | < 350 mA DC < 550 mA AC | < 350 mA DC < 550 mA AC | < 140 mA AC | < 140 mA AC | < 140 mA AC | < 140 mA AC | < 140 mA AC | < 140 mA AC | < 105 mA AC | < 105 mA AC | < 105 mA AC | < 105 mA AC | < 105 mA AC | < 105 mA AC | < 1300 mA AC < 850 mA DC | < 1300 mA AC < 850 mA DC | < 1300 mA AC < 850 mA DC | < 1300 mA AC < 850 mA DC | < 1300 mA AC < 850 mA DC | < 1300 mA AC < 850 mA DC | < 290 mA AC | < 290 mA AC | < 290 mA AC | < 290 mA AC | < 290 mA AC | < 290 mA AC | < 280 mA AC | < 280 mA AC | < 280 mA AC | < 280 mA AC | < 280 mA AC | < 280 mA AC |  | < 20 mA on audible unit | < 47 mA on LED unit | < 47 mA on LED unit | < 47 mA on LED unit | < 350 mA on flash discharge tube unit DC < 47 mA on LED unit < 550 mA on flash discharge tube unit AC | < 47 mA on LED unit | < 350 mA on flash discharge tube unit DC < 47 mA on LED unit < 550 mA on flash discharge tube unit AC | < 20 mA on audible unit < 47 mA on LED unit | < 20 mA on audible unit < 47 mA on LED unit | < 20 mA on audible unit < 47 mA on LED unit | < 350 mA DC < 550 mA AC | < 350 mA DC < 550 mA AC | < 20 mA on audible unit < 350 mA on flash discharge tube unit DC < 550 mA on flash discharge tube unit AC | [16 empty] | < 350 mA DC < 550 mA AC | < 350 mA DC < 550 mA AC | < 350 mA DC < 550 mA AC | < 350 mA DC < 550 mA AC | < 350 mA DC < 550 mA AC | < 350 mA DC < 550 mA AC | < 105 mA AC | < 105 mA AC | < 105 mA AC | < 105 mA AC | < 105 mA AC | < 105 mA AC | [6 empty] | < 145 mA DC < 90 mA AC < 145 mA DC < 90 mA AC | < 145 mA DC < 90 mA AC < 145 mA DC < 90 mA AC | < 145 mA DC < 90 mA AC < 145 mA DC < 90 mA AC | < 145 mA DC < 90 mA AC < 145 mA DC < 90 mA AC | < 145 mA DC < 90 mA AC < 145 mA DC < 90 mA AC | < 145 mA DC < 90 mA AC < 145 mA DC < 90 mA AC | < 35 mA AC < 35 mA AC | < 35 mA AC < 35 mA AC | < 35 mA AC < 35 mA AC | < 35 mA AC < 35 mA AC | < 35 mA AC < 35 mA AC | < 35 mA AC < 35 mA AC | < 25 mA AC < 25 mA AC | < 25 mA AC < 25 mA AC | < 25 mA AC < 25 mA AC | < 25 mA AC < 25 mA AC | < 25 mA AC < 25 mA AC | < 25 mA AC < 25 mA AC |  | < 17 mA on LED unit | < 17 mA on LED unit < 50 mA on audible unit | < 17 mA on LED unit < 50 mA on audible unit | < 105 mA AC | < 105 mA AC | < 25 mA | < 25 mA | < 25 mA | < 25 mA | < 25 mA | < 25 mA | < 25 mA | < 25 mA | < 25 mA | < 25 mA | < 25 mA | < 25 mA | < 25 mA | < 25 mA | < 25 mA | [5 empty] | < 145 mA AC < 85 mA DC | < 145 mA AC < 85 mA DC | < 145 mA AC < 85 mA DC | < 145 mA AC < 85 mA DC | < 145 mA AC < 85 mA DC | < 35 mA | < 35 mA | < 35 mA | < 35 mA | < 35 mA | < 25 mA | < 25 mA | < 25 mA | < 25 mA | < 25 mA | 140 mA on flash discharge tube unit AC 98 mA on flash discharge tube unit DC | 140 mA on flash discharge tube unit AC 98 mA on flash discharge tube unit DC 15 mA on base unit |  |  |  | 15 mA on base unit | 15 mA on base unit |  |  | 15 mA on base unit |  | < 15 mA | < 18 mA | < 18 mA | 33 mA on flash discharge tube unit | 18 mA on base unit 33 mA on flash discharge tube unit |  |  |  | 18 mA on base unit | 18 mA on base unit | 18 mA on base unit |  | 20 mA on flash discharge tube unit |  |  |  | 18 mA on base unit | 18 mA on base unit | 18 mA on base unit |  | 18 mA on base unit | 1000 mA | 1000 mA | 1000 mA | 1000 mA | 500 mA | 500 mA | 500 mA | 300 mA at 24 V 500 mA | 80 mA at 120 V | 40 mA at 230 V | 350 mA at 24 V 250 mA at 12 V | 100 mA at 120 V | 50 mA at 240 V | 117 mA at 12 V 125 mA at 24 V 158 mA at 12 V 200 mA at 24 V | 117 mA at 12 V 125 mA at 24 V 158 mA at 12 V 200 mA at 24 V | 117 mA at 12 V 125 mA at 24 V 158 mA at 12 V 200 mA at 24 V | 117 mA at 12 V 125 mA at 24 V 158 mA at 12 V 200 mA at 24 V | 250 mA at 12 V 292 mA at 12 V 292 mA at 24 V 354 mA at 24 V | 250 mA at 12 V 292 mA at 12 V 292 mA at 24 V 354 mA at 24 V | 250 mA at 12 V 292 mA at 12 V 292 mA at 24 V 354 mA at 24 V | 250 mA at 12 V 292 mA at 12 V 292 mA at 24 V 354 mA at 24 V | 75 mA at 24 V DC | 75 mA at 24 V DC | 75 mA at 24 V DC | 160 mA at 24 V DC | 160 mA at 24 V DC | 160 mA at 24 V DC | 100 mA at 100 V AC | 100 mA at 100 V AC
| delay at power up | [192 empty] | 0.5 s | 650 ms | 650 ms | 650 ms | 650 ms | 650 ms | 650 ms | 1000 ms DC | 1000 ms DC 500 ms AC | 3 min minimum | 1000 ms DC 500 ms AC | 650 ms | 1000 ms DC 500 ms AC | 1000 ms DC 500 ms AC | [20 empty] | 0.2 s | 0.2 s | 0.2 s | 0.5 s | 0.5 s | 0.3 s |  |  | 0.3 s | 0.6 s | 0.5 s | 0.05 s | 650 ms | 500 ms | 500 ms | 600 ms | 600 ms | 600 ms | 650 ms | 650 ms | [20 empty] | 650 ms | 650 ms | 650 ms | 650 ms | 650 ms | 650 ms | 650 ms | 650 ms | 650 ms | 650 ms | 650 ms | 650 ms
| depth | [85 empty] | 72 mm | 72 mm | 72 mm | 72 mm | 72 mm | 72 mm | 72 mm | 72 mm | 72 mm | 72 mm | 72 mm | 72 mm | [35 empty] | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | [103 empty] | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | [9 empty] | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm |  | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm | 80 mm |  |  |  |  | 99 mm | [86 empty] | 18.5 mm | 18.5 mm | 18.5 mm | 18.5 mm | 18.5 mm | 18.5 mm | 18.5 mm | 18.5 mm | RSL1PRBU: 101 mm; RSL1PREU: 101 mm; RSL1PRFU: 101 mm; RSL1PRJU: 101 mm; RSL1PRPU: 101 mm; RSL1PVBU: 95 mm; RSL1PVEU: 95 mm; RSL1PVFU: 95 mm; RSL1PVJU: 95 mm; RSL1PVPU: 95 mm | [145 empty] | 153.2 mm | 153.2 mm | 153.2 mm | 223 mm | 223 mm | 223 mm | 69.3 mm | 69.3 mm | 69.3 mm | 69.3 mm | 58.1 mm | 58.1 mm | 58.1 mm | 58.1 mm | 24.9 mm | 24.9 mm | 24.9 mm | 50.1 mm | 50.1 mm | 50.1 mm | 50.1 mm | 50.1 mm
| device application | [703 empty] | Printing Subway Packaging | Printing Packaging Subway | Subway Packaging Printing | Subway Printing Packaging | Printing Packaging Subway | Packaging Printing Subway | Subway Packaging Printing | Packaging Subway Printing
| device presentation | [320 empty] | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | RSL1PRBU: Complete product; RSL1PREU: Complete product; RSL1PRFU: Complete product; RSL1PRJU: Complete product; RSL1PRPU: Complete product; RSL1PVBU: Complete product; RSL1PVEU: Complete product; RSL1PVFU: Complete product; RSL1PVJU: Complete product; RSL1PVPU: Complete product
| dielectric strength | [80 empty] | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1 | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1 | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1 | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1 | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1 | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1 | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1 | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1 | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1 | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1 | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1 | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1 | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1 | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1 | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1 | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1 | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
| dielectric test voltage | [305 empty] | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
| discrete output type | [132 empty] | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay
| drop-out voltage threshold | [320 empty] | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.05 Uc | >= 0.05 Uc | >= 0.05 Uc | >= 0.05 Uc | >= 0.05 Uc | >= 0.05 Uc | >= 0.05 Uc | >= 0.05 Uc | RSL1PRBU: >= 0.05 Uc; RSL1PREU: >= 0.05 Uc; RSL1PRFU: >= 0.05 Uc; RSL1PRJU: >= 0.05 Uc; RSL1PRPU: >= 0.05 Uc; RSL1PVBU: >= 0.05 Uc; RSL1PVEU: >= 0.05 Uc; RSL1PVFU: >= 0.05 Uc; RSL1PVJU: >= 0.05 Uc; RSL1PVPU: >= 0.05 Uc
| electrical connection | [400 empty] | XVBC07: 1 connector for standard input; XVBC21: 1 connector for standard input; XVBC21A: 1 connector M12 for AS-Interface line; XVBC21B: 1 remote connector M12, cable length: 1 m for AS-Interface line | [145 empty] | Cable: 6.5…8.5 mm | Cable: 6.5…8.5 mm | Cable: 6.5…8.5 mm | Cable: 6.5…8.5 mm, 0.33 mm² / AWG 22 (signalling circuit) Cable: 6.5…8.5 mm, 0.52 mm² / AWG 20 (power circuit) | Cable: 6.5…8.5 mm, 0.33 mm² / AWG 22 (signalling circuit) Cable: 6.5…8.5 mm, 0.52 mm² / AWG 20 (power circuit) | Cable: 6.5…8.5 mm, 0.33 mm² / AWG 22 (signalling circuit) Cable: 6.5…8.5 mm, 0.52 mm² / AWG 20 (power circuit)
| electrical durability | [80 empty] | 100000000 cycles | 100000000 cycles | 100000000 cycles | 100000000 cycles | 100000000 cycles | 100000 cycles (8 A at 250 V AC maximum) for resistive load | 100000 cycles (8 A at 250 V AC maximum) for resistive load | 100000 cycles (8 A at 250 V AC maximum) for resistive load | 100000 cycles (8 A at 250 V AC maximum) for resistive load | 100000 cycles (8 A at 250 V AC maximum) for resistive load | 100000 cycles (8 A at 250 V AC maximum) for resistive load | 100000 cycles (8 A at 250 V AC maximum) for resistive load | 100000 cycles (8 A at 250 V AC maximum) for resistive load | 100000 cycles (8 A at 250 V AC maximum) for resistive load | 100000 cycles (8 A at 250 V AC maximum) for resistive load | 100000 cycles (8 A at 250 V AC maximum) for resistive load | 100000 cycles (8 A at 250 V AC maximum) for resistive load | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 2 A at 24 V, DC-1 100000 cycles, 5 A at 250 V, AC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 2 A at 24 V, DC-1 100000 cycles, 5 A at 250 V, AC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles for resistive load, 8 A at 250 V, AC | 100000 cycles for resistive load, 8 A at 250 V, AC | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles for resistive load, 8 A at 250 V, AC | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 2 A at 24 V, DC-1 100000 cycles, 5 A at 250 V, AC-1 | 100000 cycles for resistive load, 8 A at 250 V, AC | 100000 cycles for resistive load, 8 A at 250 V, AC | 100000 cycles for resistive load, 8 A at 250 V, AC | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles for resistive load, 8 A at 250 V, AC | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | [11 empty] | 100000 cycles for resistive load, 8 A at 250 V, AC | 100000 cycles at 250 V AC resistive | 100000 cycles at 250 V AC resistive | 100000 cycles at 250 V AC resistive | 100000 cycles at 250 V AC resistive | 100000 cycles at 250 V AC resistive | 100000 cycles at 250 V AC resistive | 100000 cycles at 250 V AC resistive | 100000 cycles at 250 V AC resistive | 100000 cycles at 250 V AC resistive | 100000 cycles at 250 V AC resistive | [38 empty] | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 10000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 10000 cycles | 10000 cycles | 100000 cycles | 100000 cycles | 100000 cycles | 10000 cycles | 10000 cycles | [59 empty] | 100000 cycles | [14 empty] | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 12 A at 250 V, AC-1 NO 100000 cycles, 6 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 60000 cycles, 6 A at 250 V, AC-1 C/O | 60000 cycles, 6 A at 250 V, AC-1 C/O | 60000 cycles, 6 A at 250 V, AC-1 C/O | 60000 cycles, 6 A at 250 V, AC-1 C/O | 60000 cycles, 6 A at 250 V, AC-1 C/O | 60000 cycles, 6 A at 250 V, AC-1 C/O | 60000 cycles, 6 A at 250 V, AC-1 C/O | 60000 cycles, 6 A at 250 V, AC-1 C/O | RSL1PRBU: 60000 cycles for resistive load, 6 A at 250 V, AC-1; RSL1PREU: 60000 cycles for resistive load, 6 A at 250 V, AC-1; RSL1PRFU: 60000 cycles for resistive load, 6 A at 250 V, AC-1; RSL1PRJU: 60000 cycles for resistive load, 6 A at 250 V, AC-1; RSL1PRPU: 60000 cycles for resistive load, 6 A at 250 V, AC-1; RSL1PVBU: 60000 cycles for resistive load, 6 A at 250 V, AC-1; RSL1PVEU: 60000 cycles for resistive load, 6 A at 250 V, AC-1; RSL1PVFU: 60000 cycles for resistive load, 6 A at 250 V, AC-1; RSL1PVJU: 60000 cycles for resistive load, 6 A at 250 V, AC-1; RSL1PVPU: 60000 cycles for resistive load, 6 A at 250 V, AC-1
| electrical insulation class | [682 empty] | Class II | Class II | Class II | Class II | Class II | Class II | Class II
| fixing mode | [301 empty] | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail) | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail) | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail) | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail) |  | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail) | Clip-on (35 mm symmetrical DIN rail) Fixed (mounting plate) | Clip-on (35 mm symmetrical DIN rail) Fixed (mounting plate) | Clip-on (35 mm symmetrical DIN rail) Fixed (mounting plate) | Clip-on (35 mm symmetrical DIN rail) Fixed (mounting plate) | Clip-on (35 mm symmetrical DIN rail) Fixed (mounting plate) | Clip-on (35 mm symmetrical DIN rail) Fixed (mounting plate) | Clip-on (35 mm symmetrical DIN rail) Fixed (mounting plate) | Clip-on (35 mm symmetrical DIN rail) Fixed (mounting plate) | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail) | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail) | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail) | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail) | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail) | [80 empty] | RSL1PRBU: Plastic compression spring; RSL1PREU: Plastic compression spring; RSL1PRFU: Plastic compression spring; RSL1PRJU: Plastic compression spring; RSL1PRPU: Plastic compression spring; RSL1PVBU: Plastic compression spring; RSL1PVEU: Plastic compression spring; RSL1PVFU: Plastic compression spring; RSL1PVJU: Plastic compression spring; RSL1PVPU: Plastic compression spring; XVBC07: Direct or tube fixing; XVBC21: Direct or tube fixing | [148 empty] | 3 holes Ø 9 mm | 3 holes Ø 9 mm | 3 holes Ø 9 mm
| flash energy | [77 empty] | 0.8 J | 0.8 J | 0.8 J | [320 empty] | XVBL6B3: 5 J; XVBL6B4: 5 J; XVBL6B5: 5 J; XVBL6B6: 5 J; XVBL6B7: 5 J; XVBL6B8: 5 J; XVBL6G3: 5 J; XVBL6G4: 5 J; XVBL6G5: 5 J; XVBL6G6: 5 J; XVBL6G7: 5 J; XVBL6G8: 5 J; XVBL6M3: 5 J; XVBL6M4: 5 J; XVBL6M5: 5 J; XVBL6M6: 5 J; XVBL6M7: 5 J; XVBL6M8: 5 J; XVBL8B3: 10 J; XVBL8B4: 10 J; XVBL8B5: 10 J; XVBL8B6: 10 J; XVBL8B7: 10 J; XVBL8B8: 10 J; XVBL8G3: 10 J; XVBL8G4: 10 J; XVBL8G5: 10 J; XVBL8G6: 10 J; XVBL8G7: 10 J; XVBL8G8: 10 J; XVBL8M3: 10 J; XVBL8M4: 10 J; XVBL8M5: 10 J; XVBL8M6: 10 J; XVBL8M7: 10 J; XVBL8M8: 10 J |  |  |  |  | 5 J |  | 5 J |  |  |  | 5 J | 5 J | 5 J | [16 empty] | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | [6 empty] | 1 J 1 J | 1 J 1 J | 1 J 1 J | 1 J 1 J | 1 J 1 J | 1 J 1 J | 1 J 1 J | 1 J 1 J | 1 J 1 J | 1 J 1 J | 1 J 1 J | 1 J 1 J | 1 J 1 J | 1 J 1 J | 1 J 1 J | 1 J 1 J | 1 J 1 J | 1 J 1 J |  |  |  |  | 5 J | 5 J | [20 empty] | 1 J | 1 J | 1 J | 1 J | 1 J | 1 J | 1 J | 1 J | 1 J | 1 J | 1 J | 1 J | 1 J | 1 J | 1 J
| flashing frequency | [62 empty] | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 0.8 Hz | 0.8 Hz | 0.8 Hz | [334 empty] | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | [20 empty] | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | [6 empty] | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | [5 empty] | 1 Hz |  | 1 Hz |  |  |  | 1 Hz | 1 Hz | 1 Hz |  |  |  |  | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | [28 empty] | 1 Hz | 1 Hz | [20 empty] | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 1 Hz | 0.8 Hz with flash discharge tube unit | 0.8 Hz with flash discharge tube unit | [12 empty] | 0.8 Hz with flash discharge tube unit | 0.8 Hz with flash discharge tube unit | [7 empty] | 0.8 Hz with flash discharge tube unit
| functionality | [80 empty] | On-delay timing | Off-delay timing | On-delay timing | Asymmetrical flashing timer | Multifunction | On-delay timing | Pulse signal | Off-delay timing | On-delay timing | Asymmetrical flashing timer | Asymmetrical flashing timer | Multifunction | Multifunction | Multifunction | Multifunction | Multifunction | Multifunction | [106 empty] | Overvoltage and undervoltage detection | Overvoltage and undervoltage detection | Overvoltage and undervoltage detection | [38 empty] | Overvoltage and undervoltage detection | Overvoltage and undervoltage detection
| fundamental frequency | [400 empty] | XVBC9B: 2.8 kHz; XVBC9M: 2.8 kHz | 2.8 kHz | [6 empty] | 2.8 kHz | 2.8 kHz | 2.8 kHz |  |  | 2.8 kHz | [54 empty] | 2.8 kHz | 2.8 kHz | [38 empty] | 4 kHz |  |  |  | 4 kHz | 4 kHz | 4 kHz |  | 4 kHz |  | 4 kHz | 4 kHz | 4 kHz |  | 4 kHz |  |  |  | 4 kHz | 4 kHz | 4 kHz | [5 empty] | 4 kHz | 4 kHz | 4 kHz |  | 4 kHz
| height | [85 empty] | 90 mm | 90 mm | 90 mm | 90 mm | 90 mm | 90 mm | 90 mm | 90 mm | 90 mm | 90 mm | 90 mm | 90 mm | [35 empty] | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | [103 empty] | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm |  | 78 mm | [9 empty] | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm |  | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm | 78 mm |  |  |  |  | 90 mm | [86 empty] | 28 mm | 28 mm | 28 mm | 28 mm | 28 mm | 28 mm | 28 mm | 28 mm | RSL1PRBU: 78.6 mm; RSL1PREU: 78.6 mm; RSL1PRFU: 78.6 mm; RSL1PRJU: 78.6 mm; RSL1PRPU: 78.6 mm; RSL1PVBU: 78.6 mm; RSL1PVEU: 78.6 mm; RSL1PVFU: 78.6 mm; RSL1PVJU: 78.6 mm; RSL1PVPU: 78.6 mm | [138 empty] | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 139 mm | 114 mm | 114 mm | 114 mm | 114 mm | 114 mm | 114 mm | 72 mm | 72 mm | 72 mm | 72 mm | 96 mm | 96 mm | 96 mm | 96 mm | 80 mm | 80 mm | 80 mm | 105 mm | 105 mm | 105 mm | 105 mm | 105 mm
| housing colour | [660 empty] | White | White | White | White
| housing material | [80 empty] | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | Self-extinguishing | [11 empty] | Self-extinguishing | [48 empty] | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | [59 empty] | Self-extinguishing plastic
| hysteresis | [192 empty] | 15 % fixed of threshold setting | 2 % | 2 % |  |  | 2 % | 2 % | 5…20 % of threshold setting | 5…20 % of threshold setting | 5 % fixed of threshold setting | 5…20 % of threshold setting | 2 % | 3 % fixed of threshold setting | 3 % fixed of threshold setting | 5…50 % adjustable of threshold setting | 5…50 % adjustable of threshold setting for overcurrent or undercurrent detection 3 % fixed of full scale for window mode |  |  |  |  | 2 % fixed of selectable | 2 % fixed of selectable |  | 2 % fixed of selectable | 2 % fixed of selectable | 2 % fixed of selectable | 2 % fixed of selectable | 5…50 % adjustable of threshold setting | 5…50 % adjustable of threshold setting | 5…50 % adjustable of threshold setting | 3 % fixed of full scale for window mode 5…50 % adjustable of threshold setting for overvoltage or undervoltage detection | 3 % fixed of full scale for window mode 5…50 % adjustable of threshold setting for overvoltage or undervoltage detection | 3 % fixed of full scale for window mode 5…50 % adjustable of threshold setting for overvoltage or undervoltage detection | 5…50 % adjustable of threshold setting |  |  |  | 5 % of threshold | 0.3 % fixed | 5…50 % of threshold setting | 5…50 % adjustable of threshold setting for overcurrent or undercurrent detection 3 % fixed of full scale for window mode | 5…50 % adjustable of threshold setting for overcurrent or undercurrent detection 3 % fixed of full scale for window mode | 5…50 % of threshold setting |  |  | 5 % of threshold | 2 % |  |  | 5…50 % of threshold setting | 5…50 % of threshold setting | 5…50 % of threshold setting | 2 % | 2 % | 5…30 % adjustable of current threshold setting | 5…30 % adjustable of current threshold setting | 5…30 % adjustable of current threshold setting | 5…30 % adjustable of current threshold setting | 5…30 % adjustable of current threshold setting | 5…30 % adjustable of current threshold setting | 5…30 % adjustable of current threshold setting | 5…30 % adjustable of current threshold setting | 5…30 % adjustable of current threshold setting | 5…30 % adjustable of current threshold setting | 5…30 % adjustable of current threshold setting | [9 empty] | 50 % fixed of asymmetry percentage | 50 % fixed of asymmetry percentage | 50 % fixed of asymmetry percentage | 50 % fixed of asymmetry percentage |  | 5 % fixed of de-energisation threshold | 5 % fixed of de-energisation threshold | 5 % fixed of de-energisation threshold | 5 % fixed of de-energisation threshold | 5 % fixed of de-energisation threshold | 5 % fixed of de-energisation threshold | 5 % fixed of de-energisation threshold | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5…30 % adjustable of voltage threshold setting | 5 % fixed of de-energisation threshold | 5 % fixed of de-energisation threshold |  |  |  |  | 3 % of fixed for phase failure detection
| illuminating intensity | [400 empty] | XVBC6B7: 13 cd; XVBC6G7: 13 cd; XVBC6M7: 13 cd; XVBC8B7: 26 cd; XVBC8G7: 26 cd; XVBC8M7: 26 cd; XVBL6B7: 13 cd; XVBL6G7: 13 cd; XVBL6M7: 13 cd; XVBL8B7: 26 cd; XVBL8G7: 26 cd; XVBL8M7: 26 cd | [33 empty] | 13 cd | [5 empty] | 13 cd | [11 empty] | 1.4 cd 1.4 cd | [5 empty] | 1.4 cd 1.4 cd | [5 empty] | 1.4 cd 1.4 cd
| immunity to microbreaks | [97 empty] | 10 ms | 10 ms | 10 ms | 10 ms 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | [71 empty] | 20 ms at 12 V | 20 ms | 20 ms | 20 ms |  | 20 ms | 20 ms | [35 empty] | 10 ms | 10 ms | 10 ms
| impulse duration | [237 empty] | >= 5 ms high state >= 5 ms low state
| input compatibility | [132 empty] | 3/4 wires sensors PNP/NPN without internal load <50 m X1Z2 terminal(s) 3/4 wires sensors PNP/NPN without internal load <50 m X2Z2 terminal(s) | 3/4 wires sensors PNP/NPN without internal load <50 m X1Z2 terminal(s) 3/4 wires sensors PNP/NPN without internal load <50 m Y1Z2 terminal(s) | 3/4 wires sensors PNP/NPN without internal load <50 m X1Z2 terminal(s) 3/4 wires sensors PNP/NPN without internal load <50 m Y1Z2 terminal(s) | [102 empty] | 3-wire sensor (E1) PNP or NPN, 12 V, 50 mA NAMUR sensor (E2), 12 V, 1.5 kOhm Voltage input (E1), 0...30 V, 9.5 kOhm, high state >= 4.5 V low state <= 1 V Volt-free contact input (E1), 12 V, 9.5 kOhm
| input current | [192 empty] | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C
| input frequency | [237 empty] | 0.0017…20 Hz
| input type | [703 empty] | Bit: 6 channel input Binary: 63 channel input | Bit: 6 channel input Binary: 63 channel input | Bit: 6 channel input Binary: 63 channel input | Bit: 6 channel input Binary: 63 channel input | Bit: 6 channel input Binary: 63 channel input | Bit: 6 channel input Binary: 63 channel input | Bit: 6 channel input Binary: 63 channel input | Bit: 6 channel input Binary: 63 channel input
| input voltage | [132 empty] | < 60 V X1Z2 terminal(s) < 60 V X2Z2 terminal(s) | < 60 V X1Z2 terminal(s) < 60 V Y1Z2 terminal(s) | < 60 V X1Z2 terminal(s) < 60 V Y1Z2 terminal(s)
| inrush current | [682 empty] | 1 A | 1 A | 1 A | 1 A | 0.5 A | 0.5 A | 0.5 A | [14 empty] | 30 A | 30 A | 30 A | 30 A | 30 A | 30 A | 30 A | 30 A
| installation direction | [682 empty] | Upright indoor Sideways indoor Inverted indoor Upright outdoor | Upright indoor Sideways indoor Inverted indoor Upright outdoor | Upright indoor Sideways indoor Inverted indoor Upright outdoor | Upright indoor Sideways indoor Inverted indoor Upright outdoor | Upright indoor Sideways indoor Inverted indoor Upright outdoor | Upright indoor Sideways indoor Inverted indoor Upright outdoor | Upright indoor Sideways indoor Inverted indoor Upright outdoor
| installed device | [226 empty] | Pt 100 probe cable length <= 10 m | Pt 100 probe cable length <= 10 m | Pt 100 probe cable length <= 10 m
| insulation | [192 empty] | Between supply and measurement | [13 empty] | Between supply and measurement | Between supply and measurement | Between supply and measurement | Between supply and measurement | Between supply and measurement | Between supply and measurement | [7 empty] | Between supply and measurement | Between supply and measurement | Between supply and measurement | Between supply and measurement | Between supply and measurement | Between supply and measurement |  | Galvanic insulation between supply and measurement | Galvanic insulation between supply and measurement |  |  | No galvanic insulation between supply and measurement |  | Between supply and measurement | Between supply and measurement
| insulation resistance | [80 empty] | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | [15 empty] | 100 MOhm at 500 V DC conforming to IEC 60664-1 | [48 empty] | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1 | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1 | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1 | > 500 MOhm at 500 V DC between supply and relay output conforming to 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to 60664-1 | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1 | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 100 MOhm at 500 V DC conforming to IEC 60255-27 | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1 | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1 | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1 | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1 | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1 | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1 | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1 | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | [53 empty] | > 500 MOhm conforming to IEC 60664-1 at 500 V DC | > 500 MOhm conforming to IEC 60255-5 at 500 V DC |  |  |  |  | > 100 MOhm at 500 V DC conforming to IEC 60255-27
| internal input resistance | [206 empty] | 0.1 Ohm 2.5 Ohm 0.5 Ohm | 0.5 Ohm 2.5 Ohm 0.1 Ohm | [24 empty] | 0.015 Ohm 0.005 Ohm 0.05 Ohm | 0.005 Ohm 0.015 Ohm 0.05 Ohm | [12 empty] | 33 Ohm 10 Ohm 1 Ohm | 1 Ohm 33 Ohm 10 Ohm | 10 Ohm 1 Ohm 33 Ohm | 33 Ohm 10 Ohm 1 Ohm | 1 Ohm 10 Ohm 33 Ohm | 10 Ohm 33 Ohm 1 Ohm | 1 Ohm 10 Ohm 33 Ohm | 0.02 Ohm 0.06 Ohm 0.006 Ohm | 0.02 Ohm 0.06 Ohm 0.006 Ohm | 0.06 Ohm 0.006 Ohm 0.02 Ohm | 0.02 Ohm 0.006 Ohm 0.06 Ohm | [21 empty] | 43000 Ohm 6600 Ohm 71000 Ohm | 71000 Ohm 6600 Ohm 43000 Ohm | 6600 Ohm 43000 Ohm 71000 Ohm | 23000 Ohm 112000 Ohm 225000 Ohm | 23000 Ohm 112000 Ohm 225000 Ohm | 112000 Ohm 23000 Ohm 225000 Ohm | 1111000 Ohm 11110000 Ohm 668000 Ohm | 668000 Ohm 1111000 Ohm 11110000 Ohm | 11110000 Ohm 668000 Ohm 1111000 Ohm | 43000 Ohm 6600 Ohm 71000 Ohm | 71000 Ohm 43000 Ohm 6600 Ohm | 71000 Ohm 43000 Ohm 6600 Ohm | 43000 Ohm 71000 Ohm 6600 Ohm | 112000 Ohm 23000 Ohm 225000 Ohm | 112000 Ohm 225000 Ohm 23000 Ohm | 112000 Ohm 225000 Ohm 23000 Ohm | 225000 Ohm 112000 Ohm 23000 Ohm | 1111000 Ohm 668000 Ohm 11110000 Ohm | 1111000 Ohm 11110000 Ohm 668000 Ohm | 11110000 Ohm 1111000 Ohm 668000 Ohm | 668000 Ohm 1111000 Ohm 11110000 Ohm
| kit composition | [650 empty] | Cover Plastic fixing plate Aluminium support tube Base unit | Aluminium support tube Cover Plastic fixing plate Base unit | Plastic fixing plate Aluminium support tube Cover Base unit | Plastic fixing plate Base unit Aluminium support tube Cover | Plastic fixing plate Aluminium support tube Cover Base unit | Plastic fixing plate Cover Aluminium support tube Base unit | Cover Plastic fixing plate Aluminium support tube Base unit | Cover Plastic fixing plate Aluminium support tube Base unit | Base unit Aluminium support tube Cover Plastic fixing plate | Plastic fixing plate Aluminium support tube Cover Base unit |  |  |  |  | Aluminium support tube Cover Plastic fixing plate Base unit | Plastic fixing plate Aluminium support tube Cover Base unit | Cover Aluminium support tube Plastic fixing plate Base unit | Cover Base unit Plastic fixing plate Aluminium support tube | Aluminium support tube Base unit Plastic fixing plate Cover | Aluminium support tube Base unit Plastic fixing plate Cover | Aluminium support tube Base unit Cover Plastic fixing plate | Plastic fixing plate Aluminium support tube Cover Base unit | Cover Aluminium support tube Base unit Plastic fixing plate | Base unit Plastic fixing plate Cover Aluminium support tube | Aluminium support tube Plastic fixing plate Cover Base unit | Base unit Aluminium support tube Cover Plastic fixing plate | Cover Base unit Plastic fixing plate Aluminium support tube | Cover Aluminium support tube Plastic fixing plate Base unit | Base unit Cover Aluminium support tube Plastic fixing plate | Plastic fixing plate Cover Base unit Aluminium support tube | Plastic fixing plate Cover Base unit Aluminium support tube | Cover Aluminium support tube Plastic fixing plate Base unit
| length | [682 empty] | 100 mm | 100 mm | 100 mm | 100 mm | 100 mm | 100 mm | 100 mm
| load current | [392 empty] | 6 A at 250 V AC 0.5 mm mounting distance | 6 A at 250 V AC 0.5 mm mounting distance | 6 A at 250 V AC 0.5 mm mounting distance | 6 A at 250 V AC 0.5 mm mounting distance | 6 A at 250 V AC 0.5 mm mounting distance | 6 A at 250 V AC 0.5 mm mounting distance | 6 A at 250 V AC 0.5 mm mounting distance | 6 A at 250 V AC 0.5 mm mounting distance | RSL1PRBU: 6 A at 250 V AC 0.5 mm mounting distance; RSL1PREU: 6 A at 250 V AC 0.5 mm mounting distance; RSL1PRFU: 6 A at 250 V AC 0.5 mm mounting distance; RSL1PRJU: 6 A at 250 V AC 0.5 mm mounting distance; RSL1PRPU: 6 A at 250 V AC 0.5 mm mounting distance; RSL1PVBU: 6 A at 250 V AC 0.5 mm mounting distance; RSL1PVEU: 6 A at 250 V AC 0.5 mm mounting distance; RSL1PVFU: 6 A at 250 V AC 0.5 mm mounting distance; RSL1PVJU: 6 A at 250 V AC 0.5 mm mounting distance; RSL1PVPU: 6 A at 250 V AC 0.5 mm mounting distance
| local signalling | [85 empty] | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF | LED indicator for on steady: relay energised, no timing in progress LED indicator for flashing: timing in progress 80 % ON and 20 % OFF LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF | [31 empty] | 1 LED (yellow) for output relay state LED indicator (green) for flashing: relay energised timing in progress LED indicator (green) for on steady: relay energised, no timing in progress | 1 LED (yellow) for output relay state LED indicator (green) for flashing: relay energised timing in progress LED indicator (green) for on steady: relay energised, no timing in progress | 1 LED (yellow) for output relay state LED indicator (green) for flashing: relay energised timing in progress LED indicator (green) for on steady: relay energised, no timing in progress | 1 LED (yellow) for output relay state LED indicator (green) for flashing: relay energised timing in progress LED indicator (green) for on steady: relay energised, no timing in progress | [12 empty] | 1 LED (red) for output in operation 1 LED (yellow) for power ON | 1 LED (red) for output in operation 1 LED (yellow) for power ON | 1 LED (red) for output in operation 1 LED (yellow) for power ON | 1 LED (red) for output in operation 1 LED (yellow) for power ON | 1 LED (red) for output in operation 1 LED (yellow) for power ON | 1 LED (red) for output in operation 1 LED (yellow) for power ON | 1 LED (red) for output in operation 1 LED (yellow) for power ON | 1 LED (red) for output in operation 1 LED (yellow) for power ON | 1 LED (red) for output in operation 1 LED (yellow) for power ON | 1 LED (red) for output in operation 1 LED (yellow) for power ON | [38 empty] | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (yellow) for relay ON | LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green)power ON: LED (yellow)relay ON: | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | [20 empty] | 1 LED green for power ON 1 LED yellow for correct temperature (high R1) 1 LED yellow for correct temperature (low R2) | 1 LED green for power ON 1 LED yellow for correct temperature (high R1) 1 LED yellow for correct temperature (low R2) | 1 LED green for power ON 1 LED yellow for correct temperature (high R1)/(low R2) 1 LED yellow for phases of relay |  | 1 LED green for power ON 1 LED yellow for correct frequency (high R1) 1 LED yellow for correct frequency (low R2) | LED (green) for power ON LED (yellow) for relay ON |  |  | LED (green) for power ON LED (yellow) for relay ON | LED (yellow) for relay ON LED (green) for power ON LED (yellow) for timer ON | LED (yellow) for relay ON LED (green) for power ON LED (yellow) for timer ON |  | LED (green) for power ON LED (yellow) for relay ON LED (yellow) for fault | LED (green) for power ON LED (yellow) for phase of relay (R2) LED (yellow) for temperature of relay (R1) | LED (green) for power ON LED (yellow) for phase of relay (R2) LED (yellow) for temperature of relay (R1) | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | [55 empty] | LED (green)power ON: | LED (green)power ON: | LED (green)power ON: | LED (green)power ON: | LED Un: (steady), green for power ON LED R1: (steady), amber for relay energised LED R1: (blinking), amber for timing in progress LED R2: (steady), amber for relay energised LED R2: (blinking), amber for timing in progress LED PL: (steady), red for alarm phase failure triggered LED PS: (blinking), red for alarm phase sequence failure triggered LED UV: (steady), red for alarm undervoltage failure triggered LED OV: (blinking), red for alarm overvoltage failure triggered LED UF: (steady), red for alarm underfrequency failure triggered LED OF: (blinking), red for alarm overfrequency failure triggered LED ASYM: (steady), red for alarm asymmentry failure triggered | LED (green)power ON: | LED (green)power ON: | LED (green)power ON: | LED (green)power ON: | LED (green)power ON: | LED (green)power ON: | LED (green)power ON: | LED (green)power ON: | LED (green)power ON: | LED (green)power ON: | LED (green)power ON: | LED (green)power ON: | LED (green)power ON: | LED (green)power ON:
| luminance | [615 empty] | 800 cd/m² | 800 cd/m² | 800 cd/m² | 800 cd/m² | 800 cd/m² | 800 cd/m² | 800 cd/m² | 800 cd/m² | 800 cd/m² | 800 cd/m² | 800 cd/m² | 800 cd/m² | 800 cd/m² | 800 cd/m² | 800 cd/m² | 640 cd/m² | 640 cd/m² | 640 cd/m² | 640 cd/m² | 640 cd/m² | [15 empty] | 650 cd/m² for incandescent bulb unit | 650 cd/m² for incandescent bulb unit | [12 empty] | 650 cd/m² for incandescent bulb unit | 650 cd/m² for incandescent bulb unit | [7 empty] | 650 cd/m² for incandescent bulb unit
| marking | [80 empty] | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | [31 empty] | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | [49 empty] | CE : 73/23/EEC CE : EMC 89/336/EEC | CE | CE | CE | CE | CE | CE | [27 empty] | CE : EMC 89/336/EEC CE : 73/23/EEC | CE : EMC 89/336/EEC CE : 73/23/EEC | CE : EMC 89/336/EEC CE : 73/23/EEC | CE : EMC 89/336/EEC CE : 73/23/EEC | CE : 73/23/EEC CE : EMC 89/336/EEC | CE : EMC 89/336/EEC CE : 73/23/EEC |  |  | CE : EMC 89/336/EEC CE : 73/23/EEC | CE : 73/23/EEC CE : EMC 89/336/EEC | CE : EMC 89/336/EEC CE : 73/23/EEC | CE : EMC 89/336/EEC CE : 73/23/EEC | CE | CE | CE | [5 empty] | CE : LVD 73/23/EEC CE : EMC 89/336/EEC | CE : LVD 73/23/EEC CE : EMC 89/336/EEC | CE : LVD 73/23/EEC CE : EMC 89/336/EEC | CE : LVD 73/23/EEC CE : EMC 89/336/EEC | CE : LVD 73/23/EEC CE : EMC 89/336/EEC | CE : EMC 89/336/EEC CE : LVD 73/23/EEC | CE : EMC 89/336/EEC CE : LVD 73/23/EEC | CE : EMC 89/336/EEC CE : LVD 73/23/EEC | CE : LVD 73/23/EEC CE : EMC 89/336/EEC | CE : EMC 89/336/EEC CE : LVD 73/23/EEC | CE : LVD 73/23/EEC CE : EMC 89/336/EEC | CE : EMC 89/336/EEC CE : LVD 73/23/EEC | CE : LVD 73/23/EEC CE : EMC 89/336/EEC | CE : EMC 89/336/EEC CE : LVD 73/23/EEC | CE : LVD 73/23/EEC CE : EMC 89/336/EEC | CE : EMC 89/336/EEC CE : LVD 73/23/EEC | CE : LVD 73/23/EEC CE : EMC 89/336/EEC | CE : EMC 89/336/EEC CE : LVD 73/23/EEC | CE : EMC 89/336/EEC CE : LVD 73/23/EEC | CE : LVD 73/23/EEC CE : EMC 89/336/EEC | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | [21 empty] | CE : LVD 73/23/EEC CE : EMC 89/336/EEC | CE : LVD 73/23/EEC CE : EMC 89/336/EEC | CE | CE | CE | CE |  | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE |  | CE |  | CE |  | CE |  | CE |  | CE |  | CE |  | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE |  | CE |  | CE |  | CE |  | CE |  | CE | CE | CE |  | CE |  | CE |  | CE |  | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE |  | CE | CE | CE | CE | CE | [223 empty] | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | bar: RSL1PRBU to RSL1PVPU
| material | [400 empty] | XVBC21A: Glass reinforced polyamide: base unit Polycarbonate: cover unit; XVBC21B: Glass reinforced polyamide: base unit Polycarbonate: cover unit; XVDB1GAR: Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit | [52 empty] | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: cover Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | [67 empty] | PC (polycarbonate): lenses PBT (polybutylene terephthalate) + PC (polycarbonate): body EPDM (ethylene propylene diene monomer): base | PC (polycarbonate): lenses PBT (polybutylene terephthalate) + PC (polycarbonate): body EPDM (ethylene propylene diene monomer): base | PC (polycarbonate): lenses PBT (polybutylene terephthalate) + PC (polycarbonate): body EPDM (ethylene propylene diene monomer): base | PC (polycarbonate): lenses PBT (polybutylene terephthalate) + PC (polycarbonate): body EPDM (ethylene propylene diene monomer): base | PC (polycarbonate): lenses PBT (polybutylene terephthalate) + PC (polycarbonate): body EPDM (ethylene propylene diene monomer): base | PC (polycarbonate): lenses PBT (polybutylene terephthalate) + PC (polycarbonate): body EPDM (ethylene propylene diene monomer): base | PC (polycarbonate): lenses PBT (polybutylene terephthalate) + PC (polycarbonate): body EPDM (ethylene propylene diene monomer): base | PC: body | PC: body | PC: body | ASA (Acrylonitrile Styrene Acrylate): front ASA (Acrylonitrile Styrene Acrylate): back PC (polycarbonate): back cover | PC (polycarbonate): back cover PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): front PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): back | PC (polycarbonate): back cover PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): front PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): back | ABS (acrylonitrile butadiene-styrene): body PC (polycarbonate): terminal cover | ABS (acrylonitrile butadiene-styrene): body PC (polycarbonate): terminal cover | ABS (acrylonitrile butadiene-styrene): body PC (polycarbonate): terminal cover | ABS (acrylonitrile butadiene-styrene): body PC (polycarbonate): terminal cover | PC (polycarbonate): terminal cover PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): body | PC (polycarbonate): terminal cover PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): body | PC (polycarbonate): terminal cover PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): body | PC (polycarbonate): terminal cover PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): body | PC (polycarbonate): body PC (polycarbonate): back cover TPE (thermoplastic elastomer): front panel NBR (nitrile butadiene rubber) | PC (polycarbonate): body PC (polycarbonate): back cover TPE (thermoplastic elastomer): front panel NBR (nitrile butadiene rubber) | PC (polycarbonate): body PC (polycarbonate): back cover TPE (thermoplastic elastomer): front panel NBR (nitrile butadiene rubber) | PC (polycarbonate): body PC (polycarbonate): back cover TPE (thermoplastic elastomer): front panel NBR (nitrile butadiene rubber) | PC (polycarbonate): body PC (polycarbonate): back cover TPE (thermoplastic elastomer): front panel NBR (nitrile butadiene rubber) | PC (polycarbonate): body PC (polycarbonate): back cover TPE (thermoplastic elastomer): front panel NBR (nitrile butadiene rubber) | PC (polycarbonate): body PC (polycarbonate): back cover TPE (thermoplastic elastomer): front panel NBR (nitrile butadiene rubber) | PC (polycarbonate): body PC (polycarbonate): back cover TPE (thermoplastic elastomer): front panel NBR (nitrile butadiene rubber)
| maximum [Ie] rated operational current | [132 empty] | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 3 A AC-15 at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 3 A AC-15 at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 3 A AC-15 at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 3 A AC-15 at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 3 A AC-15 at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 3 A AC-15 at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 3 A AC-15 at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 3 A AC-15 at 70 °C conforming to IEC 60947-5-1/1991/VDE 0660 | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991 2 A DC-13 24 V at 70 °C conforming to VDE 0660 3 A AC-15 24 V at 70 °C conforming to IEC 60947-5-1/1991 3 A AC-15 24 V at 70 °C conforming to VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991 0.1 A DC-13 250 V at 70 °C conforming to VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991 0.2 A DC-13 115 V at 70 °C conforming to VDE 0660 | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991 2 A DC-13 24 V at 70 °C conforming to VDE 0660 3 A AC-15 24 V at 70 °C conforming to IEC 60947-5-1/1991 3 A AC-15 24 V at 70 °C conforming to VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991 0.1 A DC-13 250 V at 70 °C conforming to VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991 0.2 A DC-13 115 V at 70 °C conforming to VDE 0660 | 2 A DC-13 24 V at 70 °C conforming to IEC 60947-5-1/1991 2 A DC-13 24 V at 70 °C conforming to VDE 0660 3 A AC-15 24 V at 70 °C conforming to IEC 60947-5-1/1991 3 A AC-15 24 V at 70 °C conforming to VDE 0660 0.1 A DC-13 250 V at 70 °C conforming to IEC 60947-5-1/1991 0.1 A DC-13 250 V at 70 °C conforming to VDE 0660 0.2 A DC-13 115 V at 70 °C conforming to IEC 60947-5-1/1991 0.2 A DC-13 115 V at 70 °C conforming to VDE 0660
| maximum cable capacity | [257 empty] | 0 mF | 0 mF | 0 mF | 0 mF | 0 mF | 0 mF | 0 mF | 0 mF | 0 mF
| maximum cable distance between devices | [208 empty] | 1000 m between probe and delay | 1000 m between probe and delay | 1000 m between probe and delay | 1000 m between probe and delay | [23 empty] | 100 m | 100 m | [20 empty] | 1000 m | 1000 m | 1000 m | 1000 m | 1000 m | 100 m | 100 m | 100 m | 100 m
| maximum electrode current | [208 empty] | 1 mA | 1 mA | 1 mA | 1 mA | [45 empty] | 1 mA | 1 mA | 1 mA | 1 mA | 1 mA | 1 mA | 1 mA | 1 mA | 1 mA
| maximum electrode voltage | [208 empty] | 12 V AC | 12 V AC | 12 V AC | 12 V AC | [45 empty] | 24 V AC | 24 V AC | 24 V AC | 24 V AC | 24 V AC | 24 V AC | 24 V AC | 24 V AC | 24 V AC
| maximum input frequency | [230 empty] | 70 Hz
| maximum leakage current | [80 empty] | 5 mA | 5 mA | 5 mA | 5 mA | 5 mA
| maximum measuring cycle | [192 empty] | 30 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value |  |  | 150 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value |  | 150 ms measurement cycle as true rms value |  | 150 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value | 100 ms measurement cycle as true rms value | 100 ms measurement cycle as true rms value |  |  |  |  | 150 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value |  | 150 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value | 100 ms measurement cycle as true rms value | 100 ms measurement cycle as true rms value | 100 ms measurement cycle as true rms value | 100 ms measurement cycle as true rms value | 100 ms measurement cycle as true rms value | 100 ms measurement cycle as true rms value | 250 ms measurement cycle as true rms value |  |  |  | 140 ms as true rms value | 200 ms measurement cycle as true rms value | 30 ms measurement cycle as true rms value | 100 ms measurement cycle as true rms value | 100 ms measurement cycle as true rms value | 30 ms measurement cycle as true rms value |  |  |  | 140 ms measurement cycle as true rms value |  |  | 30 ms measurement cycle as true rms value | 30 ms measurement cycle as true rms value | 30 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value | 80 ms | 80 ms | 80 ms | 80 ms | 80 ms | 80 ms | 80 ms | 80 ms | 80 ms | 80 ms | 80 ms | [9 empty] | 80 ms | 80 ms | 80 ms | 80 ms | 80 ms | 80 ms | 80 ms | 80 ms | 80 ms | 80 ms | 80 ms | 80 ms | [21 empty] | 80 ms | 80 ms |  |  |  |  | 150 ms measurement cycle as true rms value
| maximum output current | [80 empty] | 20 A | 20 A | 20 A | 20 A | 20 A
| maximum permissible voltage | [299 empty] | <= 300 V L1 and L3 | <= 300 V L1 and L3
| maximum power consumption | [144 empty] | 1.7 VA | 1.2 W | 2.6 VA | 1.5 W | 3 VA | 1.7 VA | 1.2 W | 2.6 VA | 1.5 W | 3 VA
| maximum power consumption in W | [80 empty] | 1.5 W at 240 V DC | 1.5 W at 240 V DC | 1.5 W at 240 V DC |  | 1.5 W at 240 V DC | 0.6 W at 24 V DC | 0.6 W at 24 V DC | 0.6 W at 24 V DC | 0.6 W at 24 V DC | 0.5 W at 12 V DC | 0.6 W at 24 V DC | 0.6 W at 24 V DC | 0.5 W at 12 V DC | 0.6 W at 24 V DC | 1.5 W at 240 V DC | 1.5 W at 240 V DC | 0.6 W at 24 V DC | [35 empty] | 0.5 W at 24 V 1.2 W at 48 V | 0.5 W at 24 V 1.2 W at 48 V | 1 W at 48 V 2 W at 24 V 2 W at 240 V 3.2 W at 110 V | 1 W at 48 V 2 W at 24 V 2 W at 240 V 3.2 W at 110 V | 1 W at 48 V 2 W at 24 V 2 W at 240 V 3.2 W at 110 V | 0.5 W at 24 V | 0.8 W at 24 V 1.6 W at 48 V | 0.8 W at 24 V 1.6 W at 48 V | 0.5 W at 24 V | 0.5 W at 24 V | 0.5 W at 24 V | [49 empty] | 1 W | [6 empty] | 1 W DC | 1 W DC | 1 W | 1.6 W DC |  | 1 W DC | 1.6 W DC | 1.5 W DC | 1.5 W DC | 1.5 W DC |  | 1.5 W DC | [8 empty] | 1.5 W DC | 1.5 W DC | 1.5 W DC | 1.5 W DC | 1.5 W DC | 1.5 W DC | 2 W DC | 0.6 W DC | 0.6 W DC | 0.6 W DC |  |  | 0.6 W DC | 1.5 W DC |  | 0.6 W DC |  |  | 3 W DC |  |  |  | 0.6 W DC | 0.6 W DC | 0.6 W DC | [7 empty] | 1.2 W DC |  |  |  | 1.2 W DC | [33 empty] | 1.2 W DC |  |  |  | 1.2 W DC |  |  |  | 1.2 W DC
| maximum power dissipation in W | [44 empty] | 5 W | 5 W | 5 W | [583 empty] | 5 W | 5 W | 5 W | 5 W | 5 W
| maximum reset time | [144 empty] | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation | 250 ms after time delay, on de-energisation 50 ms during time delay, on de-energisation
| maximum resistance | [239 empty] | 1500 Ohm for temperature sensor at 20 °C | 1500 Ohm for temperature sensor at 20 °C
| maximum supply current for sensors | [208 empty] | 1 mA | 1 mA | 1 mA | 1 mA | [23 empty] | 1 mA | 40 mA | 40 mA for < 24 V AC at 25 °C 40 mA for < 24 V DC at 25 °C 50 mA for 24...240 V AC 50 mA for 24...240 V DC
| maximum switching capacity | [144 empty] | 4 x 5 A | 4 x 5 A | 4 x 5 A | 4 x 5 A | 4 x 5 A | 4 x 5 A | 4 x 5 A | 4 x 5 A | 4 x 5 A | 4 x 5 A | [166 empty] | 3000 VA/336 W | 3000 VA AC 336 W DC | 3000 VA/336 W | 3000 VA AC 336 W DC | 3000 VA/336 W | 3000 VA AC 336 W DC | 3000 VA/336 W | 3000 VA AC 336 W DC | 3000 VA/336 W | 3000 VA AC 336 W DC | 3000 VA/336 W | 3000 VA AC 336 W DC | 3000 VA/336 W | 3000 VA AC 336 W DC | 3000 VA/336 W | 3000 VA AC 336 W DC | 3000 VA/336 W | 3000 VA AC 336 W DC | 3000 VA/336 W | 3000 VA AC 336 W DC | 3000 VA/336 W | 3000 VA AC 336 W DC | 3000 VA/336 W | 3000 VA AC 336 W DC | 4000 VA/448 W | 4000 VA AC 448 W DC | 4000 VA/448 W | 4000 VA AC 448 W DC | 4000 VA/448 W | 4000 VA AC 448 W DC | 4000 VA/448 W | 4000 VA AC 448 W DC | 4000 VA/448 W | 4000 VA AC 448 W DC | 4000 VA/448 W | 4000 VA AC 448 W DC | 4000 VA/448 W | 4000 VA AC 448 W DC | 4000 VA/448 W | 4000 VA AC 448 W DC | 4000 VA/448 W | 4000 VA AC 448 W DC | 4000 VA/448 W | 4000 VA AC 448 W DC | 4000 VA/448 W | 4000 VA AC 448 W DC | 4000 VA/448 W | 4000 VA AC 448 W DC | 2000 VA/224 W | 2000 VA AC 224 W DC | 2000 VA/224 W | 2000 VA AC 224 W DC | 2000 VA/224 W | 2000 VA AC 224 W DC | 2000 VA/224 W | 2000 VA AC 224 W DC | 2000 VA/224 W | 2000 VA AC 224 W DC | 2000 VA/224 W | 2000 VA AC 224 W DC | 2000 VA/224 W | 2000 VA AC 224 W DC | 2000 VA/224 W | 2000 VA AC 224 W DC | 2000 VA/224 W | 2000 VA AC 224 W DC | 2000 VA/224 W | 2000 VA AC 224 W DC | 2000 VA/224 W | 2000 VA AC 224 W DC | 2000 VA/224 W | 2000 VA AC 224 W DC | 1500 VA 50 W | 1500 VA 50 W | 1500 VA 50 W | 1500 VA 50 W | 1500 VA 50 W | 1500 VA 50 W | 1500 VA 50 W | 1500 VA 50 W | RSL1PRBU: 1500 VA 150 W; RSL1PREU: 1500 VA 150 W; RSL1PRFU: 1500 VA 150 W; RSL1PRJU: 1500 VA 150 W; RSL1PRPU: 1500 VA 150 W; RSL1PVBU: 1500 VA 150 W; RSL1PVEU: 1500 VA 150 W; RSL1PVFU: 1500 VA 150 W; RSL1PVJU: 1500 VA 150 W; RSL1PVPU: 1500 VA 150 W
| maximum switching current | [85 empty] | 8 A AC/DC | 8 A AC/DC | 8 A AC/DC | 8 A AC/DC | 8 A AC/DC | 8 A AC/DC | 8 A AC/DC | 8 A AC/DC | 8 A AC/DC | 8 A AC/DC | 8 A AC/DC | 8 A AC/DC | 8 A | 8 A | 8 A | 8 A 8 A | 8 A | 8 A | 5 A | 8 A | 5 A | 8 A | 8 A | 8 A | 8 mA | 8 mA | 8 A | 8 A | 8 mA | 8 A | 8 A | 8 A | 5 A | 8 mA | 8 mA | 8 mA | 8 A | 8 mA | 8 A | 8 A | 8 A | 8 A | 8 A | 5 A | 5 A | 5 A | 5 A | 1 mA (X1Z2) 1 mA (X2Z2) | 1 mA (X1Z2) 1 mA (Y1Z2) | 1 mA (X1Z2) 1 mA (Y1Z2) | [8 empty] | 8 A | [49 empty] | 5 A AC 5 A DC | 5 A AC 5 A DC |  |  | 5 A AC 5 A DC | 5 A AC 5 A DC | [7 empty] | 8 A AC | 8 A AC | 8 A AC | 8 A AC | 8 A AC | 8 A AC | 8 A AC | 8 A AC | 8 A AC | 8 A AC | 8 A AC | 8 A AC | 8 A AC | 8 A AC | 8 A AC | 8 A AC | 8 A AC | 8 A AC | 8 A AC | 8 A AC | [6 empty] | 8 A AC | 8 A AC |  |  |  |  | 5 A AC 5 A DC | 5 A AC 5 A DC | 5 A AC 5 A DC | [64 empty] | 8 A AC
| maximum switching voltage | [80 empty] | 250 V AC/DC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V | 250 V | 250 V AC | 250 V AC | 250 V | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V | 250 V | 250 V | 250 V AC | 250 V | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V | 250 V | 250 V | 250 V | [48 empty] | 250 V AC/DC | 250 V AC 250 V DC | 250 V AC 250 V DC | 250 V AC 250 V DC | 250 V AC 250 V DC | 250 V AC 250 V DC | 250 V AC 250 V DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC | 250 V AC | 250 V AC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC 250 V DC | 250 V AC 250 V DC | 250 V AC 250 V DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 250 V AC/DC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC | 440 V AC |  |  |  |  | 250 V AC | [14 empty] | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 250 V DC conforming to IEC | 300 V DC 400 V AC | 277 V | 277 V | 277 V | 277 V | 277 V | 277 V | 277 V | 277 V | RSL1PRBU: 277 V; RSL1PREU: 277 V; RSL1PRFU: 277 V; RSL1PRJU: 277 V; RSL1PRPU: 277 V; RSL1PVBU: 277 V; RSL1PVEU: 277 V; RSL1PVFU: 277 V; RSL1PVJU: 277 V; RSL1PVPU: 277 V
| maximum temporary permissible current | [144 empty] | 10 A for < 10 s | 10 A for < 10 s | 10 A for < 10 s | 10 A for < 10 s | 10 A for < 10 s | 10 A for < 10 s | 10 A for < 10 s | 10 A for < 10 s | 10 A for < 10 s | 10 A for < 10 s
| maximum voltage drop | [80 empty] | <4 V 3-wire <8 V 2-wire | <4 V 3-wire <8 V 2-wire | <4 V 3-wire <8 V 2-wire | <4 V 3-wire <8 V 2-wire | <4 V 3-wire <8 V 2-wire | [69 empty] | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V
| maximum wiring resistance | [306 empty] | 0.2 Ohm connection in 2 wires | 0.2 Ohm connection in 2 wires | 0.2 Ohm connection in 2 wires | 0.2 Ohm connection in 2 wires | 0.2 Ohm connection in 2 wires | 0.2 Ohm connection in 2 wires | 0.2 Ohm connection in 2 wires | 0.2 Ohm connection in 2 wires | 0.2 Ohm connection in 2 wires
| measurement accuracy | [192 empty] | +/- 10 % of the full scale value | [6 empty] | +/- 10 % of the full scale value | +/- 10 % of the full scale value | +/- 3 % | +/- 10 % of the full scale value | +/- 10 % of the full scale value | +/- 10 % of the full scale value | +/- 10 % of the full scale value | [20 empty] | +/- 2 °C | +/- 2 °C | +/- 2 °C | +/- 10 % of the full scale value | +/- 10 % of the full scale value in input +/- 10 % of the full scale value in time delay | +/- 10 % of the full scale value |  |  | +/- 10 % of the full scale value | +/- 10 % of the full scale value +/- 20 % for the HS range | +/- 10 % of the full scale value +/- 20 % for the HS range | +/- 10 % of the full scale value |  |  |  | +/- 10 % of the full scale value | +/- 10 % of the full scale value | +/- 10 % of the full scale value | +/- 10 % of the full scale value | +/- 10 % of the full scale value
| measurement error | [192 empty] | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation |  |  | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | < 1 % over the whole range with voltage variation 0.2 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.2 %/°C with temperature variation | 0.2 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.2 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.2 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.2 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation |  | < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.2 %/°C with temperature variation |  |  |  | 1 % by volt over the whole range +/- 0.05 %/°C | +/- 0.05 %/°C with temperature variation < +/- 1 % over the whole range with voltage variation | 0.05 %/°C with temperature variation 1 by volt over the whole range with voltage variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | 0.05 %/°C with temperature variation 1 by volt over the whole range with voltage variation | 0.5 %/°C with temperature variation | 0.5 %/°C with temperature variation | +/- 0.1 %/°C with temperature variation < +/- 1 % over the whole range with voltage variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation |  |  | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | < 1 % over the whole range with voltage variation 0.05 %/°C with temperature variation | [55 empty] | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 5 % of full scale at 20 °C | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 5 % of full scale at 20 °C | < 0.05 %/Hz with frequency variation < 0.05 %/°C with temperature variation | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C +/- 1 % of full scale (2 wires) at 20 °C +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C
| measurement voltage limits | [193 empty] | 183…528 V AC | 183…528 V AC | 183…528 V AC | 183…528 V AC | 183…528 V AC | 183…528 V AC | [39 empty] | 176…528 V AC | 176…528 V AC | 176…528 V AC
| mechanical durability | [85 empty] | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 20000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 10000000 cycles | 10000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles |  |  |  |  | 10000000 cycles | [14 empty] | 10000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 10000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 10000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 10000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 10000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 10000000 cycles | 30000000 cycles | 10000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 10000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 10000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 10000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 10000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 10000000 cycles | 30000000 cycles | 5000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 5000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 5000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 5000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 5000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 5000000 cycles | 30000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles | RSL1PRBU: 10000000 cycles; RSL1PREU: 10000000 cycles; RSL1PRFU: 10000000 cycles; RSL1PRJU: 10000000 cycles; RSL1PRPU: 10000000 cycles; RSL1PVBU: 10000000 cycles; RSL1PVEU: 10000000 cycles; RSL1PVFU: 10000000 cycles; RSL1PVJU: 10000000 cycles; RSL1PVPU: 10000000 cycles
| minimum pulse duration | [128 empty] | 20 ms | 20 ms | 20 ms | 20 ms | 20 ms | 20 ms | 20 ms | 1 s | 1 s | 20 ms | 20 ms | 20 ms | 26 ms | 26 ms | 26 ms
| minimum switching capacity | [132 empty] | at 12 V 10 mA | at 12 V 10 mA | at 12 V 10 mA | at 12 V 10 mA | at 12 V 10 mA | at 12 V 10 mA | at 12 V 10 mA | at 12 V 10 mA | at 12 V 10 mA | at 12 V 10 mA | at 12 V 10 mA | [11 empty] | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 50 mVA at 1 mA, 1 V | 50 mVA at 1 mA, 1 V | 50 mVA at 1 mA, 1 V | 50 mVA at 1 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 150 mVA at 10 mA, 1 V | 50 mVA at 1 mA, 1 V | 50 mVA at 1 mA, 1 V | 50 mVA at 1 mA, 1 V | 50 mVA at 1 mA, 1 V | [128 empty] | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW at 10 mA, 12 V | 300 mW at 5 mA | 120 mW | 120 mW | 120 mW | 120 mW | 24 mW | 24 mW | 24 mW | 24 mW | RSL1PRBU: 120 mW; RSL1PREU: 120 mW; RSL1PRFU: 120 mW; RSL1PRJU: 120 mW; RSL1PRPU: 120 mW; RSL1PVBU: 120 mW; RSL1PVEU: 120 mW; RSL1PVFU: 120 mW; RSL1PVJU: 120 mW; RSL1PVPU: 120 mW
| minimum switching current | [80 empty] | 10 mA | 10 mA | 10 mA | 10 mA | 10 mA | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V | 10 mA at 5 V | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V | 10 mA at 5 V | 10 mA at 5 V | 10 mA at 5 V DC | 10 mA at 5 V | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 100 mA | 100 mA | 100 mA | 100 mA | [11 empty] | 10 mA at 5 V | 100 mA | 100 mA | 100 mA | 100 mA | 100 mA | 100 mA | 100 mA | 100 mA | 100 mA | 100 mA | [39 empty] | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | [7 empty] | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | [6 empty] | 10 mA at 5 V DC | 10 mA at 5 V DC |  |  |  |  | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | [64 empty] | 100 mA at 6 V | [14 empty] | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 5 mA | 10 mA | 10 mA | 10 mA | 10 mA | 1 mA | 1 mA | 1 mA | 1 mA | RSL1PRBU: 100 mA; RSL1PREU: 100 mA; RSL1PRFU: 100 mA; RSL1PRJU: 100 mA; RSL1PRPU: 100 mA; RSL1PVBU: 100 mA; RSL1PVEU: 100 mA; RSL1PVFU: 100 mA; RSL1PVJU: 100 mA; RSL1PVPU: 100 mA
| minimum switching voltage | [320 empty] | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V | 12 V | 5 V
| mounting diameter | [400 empty] | XVBC07: 70 mm; XVBC21: 70 mm; XVBC21A: 70 mm; XVBC21B: 70 mm; XVDB1GAR: 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | [52 empty] | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | 45 mm | [21 empty] | 80 mm | 80 mm | 80 mm | 105 mm | 105 mm | 105 mm | 105 mm | 105 mm
| mounting position | [80 empty] | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position | Any position | Any position | Any position Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position | Any position | Any position in relation to normal vertical mounting plane | Any position | Any position | Any position | Any position | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position in relation to normal vertical mounting plane | Any position | Any position in relation to normal vertical mounting plane | Any position | Any position | Any position | Any position | Any position | [15 empty] | Any position | [62 empty] | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | [6 empty] | Any position | Any position | [71 empty] | Any position
| mounting support | [80 empty] | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | Base mounted: socket Panel mounted: system supplied with the product | Base mounted: socket Panel mounted: system supplied with the product | Base mounted: socket Panel mounted: system supplied with the product | Panel mounted: system supplied with the product Base mounted: socket | [11 empty] | 35 mm DIN rail conforming to EN/IEC 60715 | [48 empty] | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | [59 empty] | 35 mm DIN rail conforming to EN/IEC 60715 | [86 empty] | Socket or PCB | Socket or PCB | Socket or PCB | Socket or PCB | Socket or PCB | Socket or PCB | Socket or PCB | Socket or PCB | RSL1PRBU: 35 mm symmetrical DIN rail; RSL1PREU: 35 mm symmetrical DIN rail; RSL1PRFU: 35 mm symmetrical DIN rail; RSL1PRJU: 35 mm symmetrical DIN rail; RSL1PRPU: 35 mm symmetrical DIN rail; RSL1PVBU: 35 mm symmetrical DIN rail; RSL1PVEU: 35 mm symmetrical DIN rail; RSL1PVFU: 35 mm symmetrical DIN rail; RSL1PVJU: 35 mm symmetrical DIN rail; RSL1PVPU: 35 mm symmetrical DIN rail | [106 empty] | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube |  |  |  |  | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | Aluminium tube | [10 empty] | Bracket | Bracket | Bracket | 72 mm DIN rail | 72 mm DIN rail | 72 mm DIN rail | 72 mm DIN rail | 96 mm DIN rail | 96 mm DIN rail | 96 mm DIN rail | 96 mm DIN rail | 72 mm DIN rail | 72 mm DIN rail | 72 mm DIN rail | 96 mm DIN rail | 96 mm DIN rail | 96 mm DIN rail | 96 mm DIN rail | 96 mm DIN rail
| net weight | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.09 kg | 0.09 kg | 0.09 kg | 0.09 kg | 0.09 kg | 0.09 kg | 0.09 kg | 0.09 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.015 kg | 0.007 kg | 0.007 kg | 0.007 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.009 kg | 0.022 kg | 0.022 kg | 0.022 kg | 0.068 kg | 0.068 kg | 0.068 kg | 0.068 kg | 0.068 kg | 0.07 kg | 0.07 kg | 0.07 kg | 0.07 kg | 0.07 kg | 0.07 kg | 0.07 kg | 0.07 kg | 0.07 kg | 0.07 kg | 0.07 kg | 0.07 kg | 0.1 kg | 0.1 kg | 0.1 kg | 0.1 kg 0.1 kg | 0.1 kg | 0.1 kg | 0.1 kg | 0.1 kg | 0.1 kg | 0.1 kg | 0.1 kg | 0.08 kg | 0.093 kg | 0.086 kg | 0.105 kg | 0.105 kg | 0.09 kg | 0.105 kg | 0.105 kg | 0.105 kg | 0.1 kg | 0.09 kg | 0.09 kg | 0.093 kg | 0.105 kg | 0.09 kg | 0.105 kg | 0.09 kg | 0.09 kg | 0.105 kg | 0.105 kg | 0.14 kg | 0.14 kg | 0.14 kg | 0.14 kg | 0.15 kg | 0.15 kg | 0.15 kg | 0.15 kg | 0.15 kg | 0.15 kg | 0.15 kg | 0.15 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.0904 kg | 0.05 kg | 0.05 kg | 0.05 kg | 0.05 kg | 0.05 kg | 0.05 kg | 0.05 kg | 0.05 kg | 0.05 kg | 0.05 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.08 kg | 0.08 kg | 0.08 kg | 0.08 kg | 0.08 kg | 0.08 kg | 0.08 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.1 kg | 0.1 kg | 0.09 kg | 0.09 kg | 0.09 kg | 0.09 kg | 0.09 kg | 0.09 kg | 0.09 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.09 kg | [5 empty] | 0.13 kg | 0.12 kg | 0.12 kg | 0.13 kg |  |  |  | 0.13 kg | 0.13 kg | 0.13 kg | 0.08 kg | 0.08 kg | 0.08 kg | 0.08 kg | 0.08 kg | 0.172 kg | 0.172 kg | 0.172 kg | 0.172 kg | 0.172 kg | 0.172 kg | 0.172 kg | 0.204 kg | 0.204 kg | 0.204 kg | 0.204 kg | 0.165 kg | 0.165 kg | 0.165 kg | 0.165 kg | 0.165 kg | 0.165 kg | 0.165 kg | 0.165 kg | 0.165 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.11 kg | 0.168 kg | 0.168 kg | 0.168 kg | 0.168 kg | 0.168 kg | 0.168 kg | 0.168 kg | 0.168 kg | 0.168 kg | 0.168 kg | 0.168 kg | 0.08 kg | 0.168 kg | 0.168 kg | 0.168 kg | 0.168 kg | 0.168 kg | 0.168 kg | 0.168 kg | 0.168 kg | 0.168 kg | 0.11 kg | 0.11 kg | 0.15 kg | 0.12 kg | 0.12 kg | 0.15 kg | 0.125 kg | 0.12 kg | 0.12 kg | 0.12 kg | 0.12 kg | 0.12 kg | 0.12 kg | 0.12 kg | 0.12 kg | 0.12 kg | 0.12 kg | 0.12 kg | 0.12 kg | 0.12 kg | 0.12 kg | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.014 kg |  | 0.0054 kg | 0.0054 kg | 0.0054 kg | 0.0054 kg | 0.0054 kg | 0.0054 kg | 0.0054 kg | 0.0054 kg | 0.029 kg | 0.029 kg | 0.029 kg | 0.029 kg | 0.029 kg | 0.029 kg | 0.029 kg | 0.029 kg | 0.029 kg | 0.029 kg | 0.16 kg | 0.19 kg | 0.19 kg | 0.3 kg | 0.295 kg | 0.295 kg | 0.295 kg | 0.295 kg | 0.295 kg | 0.295 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | [6 empty] | 0.305 kg | 0.305 kg | 0.305 kg | 0.305 kg | 0.305 kg | 0.305 kg | 0.315 kg | 0.315 kg | 0.315 kg | 0.315 kg | 0.315 kg | 0.315 kg | 0.315 kg | 0.315 kg | 0.315 kg | 0.315 kg | 0.315 kg | 0.315 kg | 0.315 kg | 0.17 kg | 0.18 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.26 kg | 0.26 kg | 0.26 kg | 0.26 kg | 0.26 kg | 0.26 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.28 kg | 0.44 kg | 0.44 kg | 0.44 kg | 0.44 kg | 0.44 kg | 0.44 kg | 0.425 kg | 0.425 kg | 0.425 kg | 0.425 kg | 0.425 kg | 0.425 kg | 0.435 kg | 0.435 kg | 0.435 kg | 0.435 kg | 0.435 kg | 0.435 kg | 0.45 kg | 0.45 kg | 0.45 kg | 0.45 kg | 0.45 kg | 0.45 kg | 0.46 kg | 0.46 kg | 0.46 kg | 0.46 kg | 0.46 kg | 0.46 kg | 0.46 kg | 0.46 kg | 0.46 kg | 0.46 kg | 0.46 kg | 0.46 kg | 0.923 kg | 1.088 kg | 0.553 kg | 0.843 kg | 0.698 kg | 0.898 kg | 0.553 kg | 0.755 kg | 0.718 kg | 0.863 kg | 0.718 kg | 0.6 kg | 0.6 kg | 0.775 kg | 0.255 kg | 0.255 kg | 0.255 kg | 0.255 kg | 0.275 kg | 0.275 kg | 0.275 kg | 0.275 kg | 0.275 kg | 0.275 kg | 0.275 kg | 0.275 kg | 0.275 kg | 0.275 kg | 0.275 kg | 0.275 kg | 0.48 kg | 0.48 kg | 0.48 kg | 0.48 kg | 0.48 kg | 0.48 kg | 0.475 kg | 0.475 kg | 0.475 kg | 0.475 kg | 0.475 kg | 0.475 kg | 0.08 kg 0.08 kg | 0.08 kg 0.08 kg | 0.08 kg 0.08 kg | 0.08 kg 0.08 kg | 0.08 kg 0.08 kg | 0.08 kg 0.08 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.085 kg 0.085 kg | 0.923 kg | 0.698 kg | 0.863 kg | 0.718 kg | 0.6 kg | 0.6 kg | 0.25 kg | 0.25 kg | 0.25 kg | 0.25 kg | 0.25 kg | 0.25 kg | 0.25 kg | 0.25 kg | 0.25 kg | 0.25 kg | 0.25 kg | 0.25 kg | 0.25 kg | 0.25 kg | 0.25 kg | 0.245 kg | 0.245 kg | 0.245 kg | 0.245 kg | 0.245 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.27 kg | 0.454 kg | 0.463 kg | 0.392 kg | 0.493 kg | 0.486 kg | 0.496 kg | 0.449 kg | 0.402 kg | 0.392 kg | 0.402 kg | 0.055 kg | 0.065 kg | 0.065 kg | 0.065 kg | 0.454 kg | 0.463 kg | 0.392 kg | 0.493 kg | 0.486 kg | 0.496 kg | 0.449 kg | 0.402 kg | 0.392 kg | 0.454 kg | 0.392 kg | 0.493 kg | 0.486 kg | 0.496 kg | 0.449 kg | 0.402 kg | 0.392 kg | 0.402 kg | 0.484 kg | 0.484 kg | 0.484 kg | 0.484 kg | 0.538 kg | 0.538 kg | 0.538 kg | 0.8 kg | 1 kg | 1 kg | 1 kg | 1.2 kg | 1.2 kg | 0.18 kg | 0.18 kg | 0.18 kg | 0.18 kg | 0.4 kg | 0.4 kg | 0.4 kg | 0.4 kg | 0.142 kg | 0.142 kg | 0.142 kg | 0.268 kg | 0.268 kg | 0.268 kg | 0.287 kg | 0.287 kg
| nominal output current | [143 empty] | 8 A | [48 empty] | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A |  |  |  |  | 8 A | 8 A |  |  |  |  | 8 A | 8 A | 8 A | 8 A | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A | 8 A | 8 A | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A | 5 A
| nominal voltage limit | [414 empty] | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | [24 empty] | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 |  |  |  |  | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1 | 0.85...1.1 Un conforming to IEC 60947-5-1
| number of cables | [246 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| on-load factor | [80 empty] | 100 % | 100 % | 100 % | 100 % | 100 % | 100 % | 100 % | 100 % | 100 % | 100 % | 100 % | 100 % | 100 % | 100 % | 100 % | 100 % | 100 % | [31 empty] | 100 % | 100 % | 100 % | 100 % | [173 empty] | 100 %
| operating frequency | [80 empty] | 10 Hz | 10 Hz | 10 Hz | 10 Hz | 10 Hz | 10 Hz | 10 Hz | 10 Hz | 10 Hz | 10 Hz | 10 Hz | 10 Hz | 10 Hz | 10 Hz | 10 Hz | 10 Hz | 10 Hz
| operating limits | [206 empty] | - 15 % + 10 % Un | - 15 % + 10 % Un | - 15 % + 10 % Un | - 15 % + 10 % Un | - 15 % + 10 % Un | - 15 % + 10 % Un | - 20 % + 20 % Un | - 20 % + 20 % Un | 183...528 V AC | - 20 % + 20 % Un | - 20 % + 20 % Un | - 20 % + 20 % Un | - 20 % + 20 % Un | [13 empty] | - 15 % + 10 % Un | - 15 % + 10 % Un
| operating position | [132 empty] | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | [11 empty] | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | [20 empty] | Any position without derating | Any position without derating | Any position without derating | Any position | Any position without derating | Any position without derating |  |  | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | Any position without derating | [19 empty] | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | RSL1PRBU: Any position; RSL1PREU: Any position; RSL1PRFU: Any position; RSL1PRJU: Any position; RSL1PRPU: Any position; RSL1PVBU: Any position; RSL1PVEU: Any position; RSL1PVFU: Any position; RSL1PVJU: Any position; RSL1PVPU: Any position
| operating rate | [192 empty] | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | [20 empty] | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load |  |  | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | [74 empty] | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 360 cycles/hour under load <= 18000 cycles/hour no-load | <= 360 cycles/hour under load <= 18000 cycles/hour no-load | <= 360 cycles/hour under load <= 18000 cycles/hour no-load | <= 360 cycles/hour under load <= 18000 cycles/hour no-load | <= 360 cycles/hour under load <= 18000 cycles/hour no-load | <= 360 cycles/hour under load <= 18000 cycles/hour no-load | <= 360 cycles/hour under load <= 18000 cycles/hour no-load | <= 360 cycles/hour under load <= 18000 cycles/hour no-load | RSL1PRBU: <= 72000 cycles/hour no-load <= 360 cycles/hour under load; RSL1PREU: <= 72000 cycles/hour no-load <= 360 cycles/hour under load; RSL1PRFU: <= 72000 cycles/hour no-load <= 360 cycles/hour under load; RSL1PRJU: <= 72000 cycles/hour no-load <= 360 cycles/hour under load; RSL1PRPU: <= 72000 cycles/hour no-load <= 360 cycles/hour under load; RSL1PVBU: <= 72000 cycles/hour no-load <= 360 cycles/hour under load; RSL1PVEU: <= 72000 cycles/hour no-load <= 360 cycles/hour under load; RSL1PVFU: <= 72000 cycles/hour no-load <= 360 cycles/hour under load; RSL1PVJU: <= 72000 cycles/hour no-load <= 360 cycles/hour under load; RSL1PVPU: <= 72000 cycles/hour no-load <= 360 cycles/hour under load
| operating time | [320 empty] | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 20 ms operating 20 ms reset | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 5 ms reset 12 ms | 5 ms reset 12 ms | 5 ms reset 12 ms | 5 ms reset 12 ms | 5 ms reset 12 ms | 5 ms reset 12 ms | 5 ms reset 12 ms | 5 ms reset 12 ms | RSL1PRBU: 5 ms reset 12 ms; RSL1PREU: 5 ms reset 12 ms; RSL1PRFU: 5 ms reset 12 ms; RSL1PRJU: 5 ms reset 12 ms; RSL1PRPU: 5 ms reset 12 ms; RSL1PVBU: 5 ms reset 12 ms; RSL1PVEU: 5 ms reset 12 ms; RSL1PVFU: 5 ms reset 12 ms; RSL1PVJU: 5 ms reset 12 ms; RSL1PVPU: 5 ms reset 12 ms
| operating voltage tolerance | [192 empty] | - 15 % + 10 % Un | [33 empty] | - 10 % + 10 % Un DC - 15 % + 10 % Un AC | - 10 % + 10 % Un DC - 15 % + 10 % Un AC | - 10 % + 10 % Un DC - 15 % + 10 % Un AC | - 15 % + 10 % Un | - 15 % + 10 % Un | - 15 % + 10 % Un |  |  | - 15 % + 10 % Un | - 15 % + 10 % Un | - 15 % + 10 % Un | - 15 % + 10 % Un |  |  |  | - 15 % + 10 % Un | - 15 % + 10 % Un | - 15 % + 10 % Un |  |  | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | [12 empty] | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc | 0.85...1.1 Uc
| output contacts | [192 empty] | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 2 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 1 C/O | 2 NO | 2 NO | 1 C/O | 1 C/O + 1 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 1 C/O | 1 C/O | 2 C/O | 2 NO | 2 NO | 2 C/O | 2 C/O | 2 C/O | 1 C/O + 1 C/O, 1 per threshold | 1 C/O + 1 C/O, 1 per threshold | 1 C/O | 1 C/O | 1 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O |  |  |  |  | 2 C/O
| output overvoltage protection | [144 empty] | 2 J | 2 J | 2 J | 2 J | 2 J | 2 J | 2 J | 2 J | 2 J | 2 J
| output relay state | [246 empty] | Tripped if V measured > V set Tripped if A measured > A set | Tripped if A measured > A set Tripped if V measured > V set | Tripped if V measured > V set Tripped if A measured > A set | Tripped if A measured > A set Tripped if V measured > V set | Tripped if V measured > V set Tripped if A measured > A set | Tripped if A measured > A set Tripped if V measured > V set | Tripped if A measured > A set Tripped if V measured > V set | Tripped if A measured > A set Tripped if V measured > V set | Tripped if A measured > A set Tripped if V measured > V set | Tripped if V measured > V set Tripped if A measured > A set | Tripped if A measured > A set Tripped if V measured > V set | According to chosen function | According to chosen function | According to chosen function | According to chosen function | According to chosen function | According to chosen function | According to chosen function | According to chosen function | According to chosen function | Tripped, fault present | Tripped, fault present | Tripped, fault present | Tripped, fault present | Tripped, fault present | Tripped, fault present | Tripped, fault present | Tripped, fault present | Tripped, fault present | Tripped, fault present | Tripped, fault present | Tripped, fault present | Tripped if A measured > A set | Tripped if A measured > A set | Tripped if A measured > A set | Tripped if A measured > A set | Tripped if A measured > A set | Tripped if A measured > A set | Tripped if A measured > A set | Tripped if A measured > A set | Tripped if A measured > A set | Tripped if A measured > A set | Tripped if A measured > A set |  | Tripped if A measured > A set | Tripped if A measured > A set | Tripped if A measured > A set | Tripped if A measured > A set | Tripped if A measured > A set | Tripped if A measured > A set | Tripped if A measured > A set | Tripped if A measured > A set | Tripped if A measured > A set | Tripped, fault present | Tripped, fault present
| output voltage | [128 empty] | 240 V at 5 A AC-12 30 V at 2 A DC-13 240 V at 1.5 A AC-15 | 240 V at 5 A AC-12 30 V at 2 A DC-13 240 V at 1.5 A AC-15 | 240 V at 5 A AC-12 30 V at 2 A DC-13 240 V at 1.5 A AC-15 | 240 V at 5 A AC-12 30 V at 2 A DC-13 240 V at 1.5 A AC-15
| overload input current | [229 empty] | 11 A permanent at 25 °C E1-L2 terminals 50 A non repetitive < 1 s at 25 °C E1-L2 terminals
| overvoltage category | [97 empty] | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 |  |  | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 |  | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 |  |  |  | III conforming to IEC 60664-1 |  | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 |  |  |  |  | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | [48 empty] | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 III conforming to UL 508 | III conforming to IEC 60664-1 III conforming to UL 508 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 III conforming to UL 508 | III conforming to IEC 60664-1 III conforming to UL 508 | III conforming to IEC 60664-1 III conforming to UL 508 | III conforming to IEC 60664-1 III conforming to UL 508 | III conforming to IEC 60664-1 III conforming to UL 508 | III conforming to IEC 60664-1 III conforming to UL 508 | III conforming to IEC 60664-1 III conforming to UL 508 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 III conforming to UL 508 | III conforming to IEC 60664-1 III conforming to UL 508 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | [394 empty] | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140
| peak current | [134 empty] | 0.001 kA for 30 s on energisation | 0.001 kA for 30 s on energisation | 0.001 kA for 30 s on energisation
| permissible continuous overload | [246 empty] | 0.15 A 0.05 A 1.5 A | 0.05 A 0.15 A 1.5 A | 1.5 A 0.15 A 0.05 A | 1.5 A 0.15 A 0.05 A | 0.05 A 1.5 A 0.15 A | 0.15 A 1.5 A 0.05 A | 0.15 A 1.5 A 0.05 A | 2 A 20 A 7 A | 7 A 20 A 2 A | 7 A 20 A 2 A | 20 A 2 A 7 A | [21 empty] | 80 V 20 V 60 V | 80 V 20 V 60 V | 20 V 80 V 60 V | 150 V 90 V 300 V | 300 V 90 V 150 V | 90 V 150 V 300 V | 550 V 400 V | 550 V 400 V | 550 V 400 V | 80 V 60 V 20 V | 20 V 60 V 80 V | 80 V 20 V 60 V | 60 V 80 V 20 V | 150 V 90 V 300 V | 90 V 150 V 300 V | 300 V 90 V 150 V | 150 V 300 V 90 V | 550 V 400 V | 400 V 550 V | 550 V 400 V | 550 V 400 V
| permissible non repetitive overload | [246 empty] | 5 A 0.2 A 0.5 A | 5 A 0.2 A 0.5 A | 5 A 0.2 A 0.5 A | 5 A 0.2 A 0.5 A | 5 A 0.2 A 0.5 A | 5 A 0.2 A 0.5 A | 5 A 0.2 A 0.5 A | 10 A for <= 3 s 100 A 15 A | 10 A for <= 3 s 100 A 15 A | 10 A for <= 3 s 100 A 15 A | 10 A for <= 3 s 100 A 15 A | [21 empty] | 100 A for <= 1 s 25 A for <= 1 s 80 A for <= 1 s | 100 A for <= 1 s 25 A for <= 1 s 80 A for <= 1 s | 100 A for <= 1 s 25 A for <= 1 s 80 A for <= 1 s | 100 A for <= 1 s 200 A for <= 1 s 400 A for <= 1 s | 100 A for <= 1 s 200 A for <= 1 s 400 A for <= 1 s | 100 A for <= 1 s 200 A for <= 1 s 400 A for <= 1 s | 500 A for <= 1 s 550 A for <= 1 s | 500 A for <= 1 s 550 A for <= 1 s | 500 A for <= 1 s 550 A for <= 1 s | 100 A for <= 1 s 25 A for <= 1 s 80 A for <= 1 s | 100 A for <= 1 s 25 A for <= 1 s 80 A for <= 1 s | 100 A for <= 1 s 25 A for <= 1 s 80 A for <= 1 s | 100 A for <= 1 s 25 A for <= 1 s 80 A for <= 1 s | 100 A for <= 1 s 200 A for <= 1 s 550 A for <= 1 s | 100 A for <= 1 s 200 A for <= 1 s 400 A for <= 1 s | 100 A for <= 1 s 200 A for <= 1 s 400 A for <= 1 s | 100 A for <= 1 s 200 A for <= 1 s 400 A for <= 1 s | 500 A for <= 1 s 550 A for <= 1 s | 500 A for <= 1 s 550 A for <= 1 s | 500 A for <= 1 s 550 A for <= 1 s | 500 A for <= 1 s 550 A for <= 1 s
| phase failure sensitivity | [193 empty] | 0.7 Un | 0.7 Un |  |  | 0.7 Un | 0.7 Un
| pick up duration | [128 empty] | 55 ms | 55 ms | 55 ms | 55 ms
| polarity | [192 empty] | Yes DC | [6 empty] | Non reversible polarity on DC supply | Non reversible polarity on DC supply |  | Non reversible polarity on DC supply |  | Non reversible polarity on DC supply | Non reversible polarity on DC supply | [25 empty] | No DC |  |  | No DC |  |  | Reversible polarity on DC supply |  |  |  | Non reversible polarity on DC supply | Non reversible polarity on DC supply | Non reversible polarity on DC supply
| potentiometer characteristic | [132 empty] | Linear 47 kOhm (+/- 20 %), 0.2 W, cable length <25 m Z1Z2 terminal(s) | Linear 47 kOhm (+/- 20 %), 0.2 W, cable length <25 m Z1Z2 terminal(s) | Linear 47 kOhm (+/- 20 %), 0.2 W, cable length <25 m Z1Z2 terminal(s) | Linear 47 kOhm (+/- 20 %), 0.2 W, cable length <25 m Z1Z2 terminal(s) | Linear 47 kOhm (+/- 20 %), 0.2 W, cable length <25 m Z1Z2 terminal(s) |  | Linear 47 kOhm (+/- 20 %), 0.2 W, cable length <25 m Z1Z2 terminal(s)
| power consumption | [235 empty] | 1.5 W DC | 1.5 W DC |  |  | 0.5 W DC | 0.5 W DC | [19 empty] | 2.4 W DC
| power consumption in VA | [80 empty] | 0…3 VA at 240 V AC | 0…3 VA at 240 V AC | 0…3 VA at 240 V AC | 0…3 VA at 240 V AC | 0…3 VA at 240 V AC | 0…32 VA at 240 V AC | 0…32 VA at 240 V AC | 0…32 VA at 240 V AC | 0…32 VA at 240 V AC | 0…0.7 VA at 12 V AC | 0…32 VA at 240 V AC | 0…32 VA at 240 V AC | 0…0.7 VA at 12 V AC | 0…32 VA at 240 V AC | 0…3 VA at 240 V AC | 0…3 VA at 240 V AC | 0…32 VA at 240 V AC | 3 VA at 240 V AC | 3 VA at 240 V AC | 3 VA at 240 V AC | 3 VA at 240 V AC 3 VA at 240 V AC | 3 VA at 240 V AC | 3 VA at 240 V AC | 3 VA at 240 V AC | 3 VA at 240 V AC | 3 VA at 240 V AC | 3 VA at 240 V AC | 3 VA at 240 V AC | 35 VA at 240 V AC | 8 VA at 230...240 V 17 VA at 380...440 V | 50 VA at 240 V AC | 3 VA at 240 V AC | 3 VA at 240 V AC | 50 VA at 240 V AC | 3 VA at 240 V AC | 3 VA at 240 V AC | 3 VA at 240 V AC | 3 VA at 240 V AC | 1.2 VA at 12 V AC | 50 VA at 240 V AC | 3 VA at 240 V AC | 3 VA at 240 V AC | 50 VA at 240 V AC | 3 VA at 240 V AC | 3 VA at 240 V AC | 15 VA at 380 V AC | 3 VA at 240 V AC | 3 VA at 240 V AC | 1.1 VA at 24 V 4.8 VA at 240 V | 1.1 VA at 24 V 4.8 VA at 240 V | 1.1 VA at 24 V 4.8 VA at 240 V | 1.1 VA at 24 V 4.8 VA at 240 V | 0.7 VA at 24 V 1.6 VA at 48 V 1.8 VA at 110 V 8.5 VA at 240 V | 0.7 VA at 24 V 1.6 VA at 48 V 1.8 VA at 110 V 8.5 VA at 240 V | 2 VA at 24 V 6 VA at 240 V 2.5 VA at 48 V 3.2 VA at 110 V | 2 VA at 24 V 6 VA at 240 V 2.5 VA at 48 V 3.2 VA at 110 V | 2 VA at 24 V 6 VA at 240 V 2.5 VA at 48 V 3.2 VA at 110 V | 0.7 VA at 24 V 1.8 VA at 110 V 8.5 VA at 240 V | 2 VA at 48 V 1.2 VA at 24 V 12.5 VA at 240 V 2.8 VA at 110 V | 2 VA at 48 V 1.2 VA at 24 V 12.5 VA at 240 V 2.8 VA at 110 V | 0.7 VA at 24 V 1.8 VA at 110 V 8.5 VA at 240 V | 0.7 VA at 24 V 1.8 VA at 110 V 8.5 VA at 240 V | 0.7 VA at 24 V 1.8 VA at 110 V 8.5 VA at 240 V | 3 VA at 240 V AC | [49 empty] | 0…22 VA at 400 V AC 50 Hz | 0…22 VA at 400 V AC 50 Hz | 0…22 VA at 400 V AC 50 Hz | 0…22 VA at 400 V AC 50 Hz | 0…22 VA at 400 V AC 50 Hz | 0…22 VA at 400 V AC 50 Hz | [7 empty] | 3.5 VA AC | 3.5 VA AC | 5 VA AC | 8 VA AC | 5 VA AC | 8 VA AC | 10 VA at 240 V AC 60 Hz | 15 VA at 480 V AC 60 Hz | 15 VA at 480 V AC 60 Hz | 10 VA at 240 V AC 60 Hz | 15 VA at 480 V AC 60 Hz | 10 VA at 240 V AC 60 Hz | 15 VA at 480 V AC 60 Hz | 3.5 VA AC | 3.5 VA AC | 3.5 VA AC | 3.5 VA AC | 3.5 VA AC | 3.5 VA AC | 5 VA AC | [6 empty] | 3.5 VA AC | 8 VA AC |  |  |  |  | 0…22 VA at 400 V AC 50 Hz | 0…4 VA at 24...240 V AC | 0…4 VA at 24...240 V AC | [64 empty] | 4 VA at 480 V AC 60 Hz
| power consumption in W | [97 empty] | 1.5 W at 240 V DC | 1.5 W at 240 V DC | 1.5 W at 240 V DC | 1.5 W at 240 V DC 1.5 W at 240 V DC | 1.5 W at 240 V DC | 1.5 W at 240 V DC | 2 W at 240 V DC | 1.5 W at 240 V DC | 2 W at 240 V DC | 1.5 W at 240 V DC | 1.5 W at 240 V DC | 0.6 W at 24 V DC |  | 0.7 W at 24 V DC | 1.5 W at 240 V DC | 1.5 W at 240 V DC | 0.7 W at 24 V DC | 1.5 W at 240 V DC | 1.5 W at 240 V DC | 1.5 W at 240 V DC | 2 W at 240 V DC | 0.5 W at 12 V DC | 0.7 W at 24 V DC | 1.5 W at 240 V DC | 1.5 W at 240 V DC | 0.7 W at 24 V DC | 1.5 W at 240 V DC | 1.5 W at 240 V DC |  | 1.5 W at 240 V DC | 1.5 W at 240 V DC | 0.5 W at 24 V 1.7 W at 240 V | 0.5 W at 24 V 1.7 W at 240 V | 0.5 W at 24 V 1.7 W at 240 V | 0.5 W at 24 V 1.7 W at 240 V | [11 empty] | 1.5 W at 240 V DC 0.6 W at 24 V DC | [538 empty] | 3 W | 3 W | 3 W | 3 W | 3.2 W | 3.2 W | 3.2 W | [14 empty] | 1.8 W | 1.8 W | 1.8 W | 3.8 W | 3.8 W | 3.8 W | 10 W | 10 W
| power on delay | [80 empty] | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | [46 empty] | 100 ms
| product compatibility | [143 empty] | NFC enabled mobile device
| product destination | [400 empty] | XVBC07: Banks without flash discharge tube unit; XVBC21: Banks without flash discharge tube unit
| product front plate size | [128 empty] | 48 x 48 mm | 48 x 48 mm | 48 x 48 mm | 48 x 48 mm
| protection category | [320 empty] | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT I | RT III | RT III | RT III | RT III | RT III | RT III | RT III | RT III | RSL1PRBU: RT III; RSL1PREU: RT III; RSL1PRFU: RT III; RSL1PRJU: RT III; RSL1PRPU: RT III; RSL1PVBU: RT III; RSL1PVEU: RT III; RSL1PVFU: RT III; RSL1PVJU: RT III; RSL1PVPU: RT III
| protection type | [301 empty] | Reverse polarity protection on output Short-circuit protection on output Overvoltage protection on output (+/- 30 V) | Reverse polarity protection on output Short-circuit protection on output Overvoltage protection on output (+/- 30 V) | Short-circuit protection on output Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output | Short-circuit protection on output Reverse polarity protection on output Overvoltage protection on output (+/- 30 V) |  | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output Reverse polarity protection on power supply | Reverse polarity protection on output Overvoltage protection on output (+/- 30 V) Reverse polarity protection on power supply Short-circuit protection on output | Reverse polarity protection on output Overvoltage protection on output (+/- 30 V) Reverse polarity protection on power supply Short-circuit protection on output | Reverse polarity protection on power supply Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output | Reverse polarity protection on power supply Short-circuit protection on output Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output | Short-circuit protection on output Reverse polarity protection on output Overvoltage protection on output (+/- 30 V) Reverse polarity protection on power supply | Reverse polarity protection on output Short-circuit protection on output Reverse polarity protection on power supply Overvoltage protection on output (+/- 30 V) | Short-circuit protection on output Reverse polarity protection on power supply Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on power supply Short-circuit protection on output Reverse polarity protection on output | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output | Reverse polarity protection on output Overvoltage protection on output (+/- 30 V) Short-circuit protection on output | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output
| quality labels | [199 empty] | CE | CE | CE | CE | CE | CE | CE | [35 empty] | CE | CE | CE | CE | CE | [32 empty] | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE | CE
| range compatibility | [400 empty] | XVBC21A: AS-Interface cabling system; XVBC21B: AS-Interface cabling system
| rated operational voltage limits | [392 empty] | 18...33.6 V DC | 36...67.2 V DC | 9...16.8 V DC | 45...84 V DC | 18...33.6 V DC | 36...67.2 V DC | 9...16.8 V DC | 45...84 V DC
| release of input voltage | [81 empty] | 7 V | 9 V | 7 V | 8 V | 10 V | 10 V | 10 V | 10 V | 5 V | 10 V | 10 V | 5 V | 10 V | 5 V | 5 V | 10 V
| repeat accuracy | [80 empty] | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.2 % of the maximum setting value conforming to IEC 61812-1 | +/- 0.2 % of the maximum setting value conforming to IEC 61812-1 | +/- 0.2 % of the maximum setting value conforming to IEC 61812-1 | +/- 0.2 % of the maximum setting value conforming to IEC 61812-1 | +/- 0.2 % | +/- 0.2 % | +/- 0.2 % | +/- 0.2 % | +/- 0.2 % | +/- 0.2 % | +/- 0.2 % | +/- 0.2 % | < 1 % | < 1 % | < 1 % | +/- 0.2 % for 10 s...999 h time delay range +/- 0.5 % for 100 ms...10 s time delay range | +/- 0.5 % | +/- 0.5 % | +/- 0.5 % | +/- 0.5 % | +/- 0.5 % | +/- 0.5 % | +/- 0.5 % | +/- 0.5 % | +/- 0.5 % | +/- 0.5 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 1 % | +/- 0.5 % for input and measurement circuit | 0.5 % for input and measurement circuit 3 % for time delay | 0.5 % for input and measurement circuit 3 % for time delay |  |  | 0.5 % for input and measurement circuit 3 % for time delay | 0.5 % for input and measurement circuit 3 % for time delay | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay | +/- 0.5 % for input and measurement circuit +/- 0.2 % for time delay | +/- 0.5 % for input and measurement circuit +/- 0.2 % for time delay | +/- 2 % for time delay | +/- 2 % for time delay | +/- 2 % for time delay | +/- 2 % for time delay | +/- 0.5 % for input and measurement circuit +/- 3 % for time delay | +/- 0.5 % for input and measurement circuit +/- 3 % for time delay |  | +/- 0.5 % for input and measurement circuit +/- 3 % for time delay | +/- 0.5 % for input and measurement circuit +/- 3 % for time delay | +/- 0.5 % for input and measurement circuit | +/- 0.5 % for input and measurement circuit | +/- 0.5 % for input and measurement circuit | +/- 0.5 % for input and measurement circuit | +/- 0.5 % for input and measurement circuit | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay |  |  |  | +/- 1 % for input and measurement circuit +/- 1 % for time delay | +/- 0.5 % for input and measurement circuit +/- 0.5 % for time delay | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay | +/- 2 % for time delay | +/- 2 % for time delay | +/- 0.5 % for input and measurement circuit +/- 0.5 % for time delay | 0.3 % for time delay 0.5 % for input and measurement circuit |  |  | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay | +/- 0.5 % for input and measurement circuit +/- 2 % for time delay | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay | +/- 0.5 % for input and measurement circuit +/- 1 % for time delay | [55 empty] | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C | +/- 0.5 % for input circuit +/- 3 % for time delay | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C | +/- 0.2 % full scale at 20 °C +/- 0.6 % full scale at 60 °C | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C
| reset threshold | [239 empty] | 1650 Ohm +/- 10 % for temperature control circuit | 1650 Ohm +/- 10 % for temperature control circuit
| reset time | [80 empty] | 350 ms on de-energisation typical | 350 ms on de-energisation typical | 350 ms on de-energisation typical | 350 ms on de-energisation typical | 350 ms on de-energisation typical | 120 ms on de-energisation typical | 120 ms on de-energisation typical | 120 ms on de-energisation typical | 120 ms on de-energisation typical | 120 ms on de-energisation typical | 120 ms on de-energisation typical | 120 ms on de-energisation typical | 120 ms on de-energisation typical | 120 ms on de-energisation typical | 120 ms on de-energisation typical | 120 ms on de-energisation typical | 120 ms on de-energisation typical | [31 empty] | 25 ms on de-energisation | 25 ms on de-energisation | 25 ms on de-energisation | 25 ms on de-energisation | 50 ms | 50 ms | 50 ms | 50 ms | 50 ms | 50 ms | 50 ms | 50 ms | 50 ms | 50 ms | 50 ms | [11 empty] | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms | 100 ms |  | 1500 ms time delay | 1500 ms time delay |  |  | 1500 ms time delay | 1500 ms time delay | 1500 ms time delay | 1500 ms time delay | 1500 ms time delay | 1500 ms time delay | 1500 ms time delay | 1500 ms time delay | 1500 ms time delay | 1500 ms at maximum voltage | 1500 ms at maximum voltage | 1750 ms | 1750 ms | 1750 ms | 1750 ms | 1500 ms at maximum voltage | 1500 ms at maximum voltage | 1500 ms at maximum voltage | 1500 ms at maximum voltage | 1500 ms at maximum voltage | 1500 ms at maximum voltage | 1500 ms at maximum voltage | 1500 ms at maximum voltage | 1500 ms at maximum voltage | 1500 ms at maximum voltage | 1500 ms at maximum voltage | 1500 ms at maximum voltage | 1500 ms at maximum voltage | 1500 ms at maximum voltage | 8 s | 8 s | 8 s | 2000 ms | 2000 ms time delay | 1500 ms time delay | 1500 ms at maximum voltage | 1500 ms at maximum voltage | 1500 ms time delay | 1750 ms | 1000 ms 4000 ms |  | 1500 ms at 480 V | 10000 ms output | 10000 ms output | 1500 ms time delay | 1500 ms time delay | 1500 ms time delay | 1500 ms time delay | 1500 ms time delay | [59 empty] | 1500 ms at maximum voltage | [94 empty] | RSL1PRFU: 20 ms; RSL1PRPU: 20 ms; RSL1PVFU: 20 ms; RSL1PVPU: 20 ms
| resistance across terminals | [206 empty] | 2.5 Ohm at E1-M terminals 0.5 Ohm at E2-M terminals 0.1 Ohm at E3-M terminals | 2.5 Ohm at E1-M terminals 0.5 Ohm at E2-M terminals 0.1 Ohm at E3-M terminals | [11 empty] | 30 kOhm at E2-M terminals 5 kOhm at E1-M terminals 50 kOhm at E3-M terminals | 110 kOhm at E2-M terminals 22 kOhm at E1-M terminals 220 kOhm at E3-M terminals | 150 kOhm at E2-M terminals 300 kOhm at E1-M terminals 500 kOhm at E3-M terminals | 30 kOhm at E2-M terminals 5 kOhm at E1-M terminals 50 kOhm at E3-M terminals | 110 kOhm at E2-M terminals 22 kOhm at E1-M terminals 220 kOhm at E3-M terminals | 150 kOhm at E2-M terminals 300 kOhm at E1-M terminals 500 kOhm at E3-M terminals |  | 1.33 kOhm at temperature | 1.33 kOhm at temperature | 600 kOhm at 3-phase 1.33 kOhm at temperature | 0.01 Ohm at E1-L2 terminals |  | 1 Ohm at E2-M terminals 5 Ohm at E1-M terminals 0.2 Ohm at E3-M terminals | 0.005 Ohm at E3-M terminals 0.015 Ohm at E2-M terminals 0.05 Ohm at E1-M terminals | 0.005 Ohm at E3-M terminals 0.015 Ohm at E2-M terminals 0.05 Ohm at E1-M terminals | 0.005 Ohm at E3-M terminals 0.015 Ohm at E2-M terminals 0.05 Ohm at E1-M terminals |  |  |  |  | 602 mOhm | 602 mOhm | 30 mOhm at E2-M terminals 5 mOhm at E1-M terminals 50 mOhm at E3-M terminals | 110 mOhm at E2-M terminals 22 mOhm at E1-M terminals 220 mOhm at E3-M terminals | 150 mOhm at E1-M terminals 300 mOhm at E2-M terminals 600 mOhm at E3-M terminals
| resistive rated load | [320 empty] | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 12 A at 250 V AC 12 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC
| response time | [143 empty] | 2 s | [48 empty] | < 200 ms (in the event of a fault) | < 200 ms (in the event of a fault) | < 200 ms (in the event of a fault) | <= 130 ms (in the event of a fault) | <= 130 ms (in the event of a fault) | < 200 ms (in the event of a fault) | < 200 ms (in the event of a fault) |  |  | <= 200 ms |  | < 200 ms (in the event of a fault) |  |  | <= 500 ms | <= 500 ms |  |  |  |  | <= 300 ms | <= 300 ms | <= 200 ms | <= 300 ms | <= 300 ms | <= 300 ms | <= 300 ms | <= 500 ms | <= 500 ms | <= 500 ms | <= 500 ms | <= 500 ms | <= 500 ms | <= 500 ms | <= 3.5 s + Tt (in case of temperature fault) <= 3.5 s (on disappearance of fault) | <= 3.5 s + Tt (in case of temperature fault) <= 3.5 s (on disappearance of fault) | <= 3.5 s + Tt (in case of temperature fault) 500 ms (in case of 3-phase fault) 500 ms (on disappearance of fault) | < 300 ms (in the event of a fault) |  |  | <= 500 ms (on crossing the threshold) | <= 500 ms (on crossing the threshold) |  |  |  | 15 ms max (on crossing the threshold) | < 200 ms (in the event of a fault) | > 50 ms (input Y1 (contact Y1-T1) and push-button) | > 50 ms (input Y1 (contact Y1-T1) and push-button) |  |  |  | < 200 ms (in the event of a fault) | < 200 ms (in the event of a fault) | [59 empty] | <= 300 ms
| rest time in memory mode | [237 empty] | 50 ms contact S2 in memory mode on time delay 1 s supply Un in memory mode on time delay
| run-up delay at power-up | [206 empty] | 0.3 s | 0.3 s | 2.5 s 0.6 s | 2.5 s 0.6 s | 0.6 s | 0.6 s | 650 ms | 650 ms | 650 ms | 650 ms | 650 ms | 650 ms | 650 ms | 600 ms | 600 ms | 600 ms | 600 ms | 600 ms | 600 ms | 600 ms | [6 empty] | 0.3 s | 0.3 s
| safety reliability data | [80 empty] | MTTFd = 353.8 years B10d = 320000 | MTTFd = 353.8 years B10d = 320000 | MTTFd = 353.8 years B10d = 320000 | B10d = 320000 MTTFd = 353.8 years | MTTFd = 353.8 years B10d = 320000 | B10d = 270000 MTTFd = 296.8 years | MTTFd = 296.8 years B10d = 270000 | B10d = 270000 MTTFd = 296.8 years | B10d = 270000 MTTFd = 296.8 years | B10d = 270000 MTTFd = 296.8 years | MTTFd = 296.8 years B10d = 270000 | MTTFd = 296.8 years B10d = 270000 | MTTFd = 296.8 years B10d = 270000 | B10d = 270000 MTTFd = 296.8 years | MTTFd = 296.8 years B10d = 270000 | MTTFd = 296.8 years B10d = 270000 | MTTFd = 296.8 years B10d = 270000 | B10d = 190000 MTTFd = 205.4 years | B10d = 180000 MTTFd = 194 years | MTTFd = 308.2 years B10d = 280000 | MTTFd = 205.4 years B10d = 190000 MTTFd = 205.4 years B10d = 190000 | B10d = 280000 MTTFd = 308.2 years | B10d = 280000 MTTFd = 308.2 years | MTTFd = 194 years B10d = 180000 | B10d = 190000 MTTFd = 205.4 years | B10d = 180000 MTTFd = 194 years | MTTFd = 194 years B10d = 180000 | MTTFd = 205.4 years B10d = 190000 | MTTFd = 285.3 years B10d = 270000 | B10d = 260000 MTTFd = 273.9 years | MTTFd = 182.6 years B10d = 170000 | MTTFd = 251.1 years B10d = 230000 | B10d = 200000 MTTFd = 216.8 years | MTTFd = 182.6 years B10d = 170000 | MTTFd = 251.1 years B10d = 230000 | B10d = 200000 MTTFd = 216.8 years | B10d = 200000 MTTFd = 216.8 years | B10d = 160000 MTTFd = 171.2 years | B10d = 190000 MTTFd = 205.4 years | MTTFd = 182.6 years B10d = 170000 | B10d = 230000 MTTFd = 251.1 years | B10d = 160000 MTTFd = 171.2 years | B10d = 170000 MTTFd = 182.6 years | B10d = 160000 MTTFd = 171.2 years | B10d = 320000 MTTFd = 353.8 years | B10d = 250000 MTTFd = 273.9 years | MTTFd = 342.4 years B10d = 320000 | MTTFd = 342.4 years B10d = 320000 | [15 empty] | MTTFd = 227.5 years 100 % duty cycle continuous operating condition at 30 °C | [49 empty] | MTTFd = 502.2 years B10d = 470000 | MTTFd = 502.2 years B10d = 470000 | MTTFd = 924.6 years B10d = 850000 | B10d = 850000 MTTFd = 924.6 years | MTTFd = 502.2 years B10d = 470000 | MTTFd = 502.2 years B10d = 470000 |  |  |  |  | B10d = 470000 MTTFd = 502.2 years | B10d = 470000 MTTFd = 502.2 years | MTTFd = 502.2 years B10d = 470000 | MTTFd = 296.8 years B10d = 270000 | MTTFd = 296.8 years B10d = 270000 | MTTFd = 182.6 years B10d = 170000 | MTTFd = 182.6 years B10d = 170000 | B10d = 120000 MTTFd = 125.5 years | MTTFd = 125.5 years B10d = 120000 | MTTFd = 388.1 years B10d = 350000 | MTTFd = 388.1 years B10d = 350000 | MTTFd = 924.6 years B10d = 850000 | MTTFd = 388.1 years B10d = 350000 | MTTFd = 388.1 years B10d = 350000 | B10d = 350000 MTTFd = 388.1 years | MTTFd = 388.1 years B10d = 350000 | B10d = 290000 MTTFd = 308.2 years | B10d = 290000 MTTFd = 308.2 years | MTTFd = 308.2 years B10d = 290000 | MTTFd = 308.2 years B10d = 290000 | B10d = 290000 MTTFd = 308.2 years | MTTFd = 308.2 years B10d = 290000 | MTTFd = 433.7 years B10d = 400000 | [5 empty] | MTTFd = 296.8 years B10d = 270000 | MTTFd = 296.8 years B10d = 270000 | MTTFd = 296.8 years B10d = 270000 | MTTFd = 296.8 years B10d = 270000 | B10d = 170000 MTTFd = 182.6 years | B10d = 170000 MTTFd = 182.6 years |  | MTTFd = 399.5 years B10d = 360000 |  |  | B10d = 290000 MTTFd = 308.2 years | B10d = 290000 MTTFd = 308.2 years | B10d = 290000 MTTFd = 308.2 years | B10d = 300000 MTTFd = 319.6 years | B10d = 470000 MTTFd = 502.2 years | [55 empty] | B10d = 22108 MTTFd = 23.9 years | B10d = 20000 MTTFd = 21.6 years | MTTFd = 73.2 years B10d = 67582 | MTTFd = 21.6 years B10d = 20000 |  | B10d = 30437 MTTFd = 32.9 years | B10d = 40564 MTTFd = 43.9 years | MTTFd = 32.9 years B10d = 30437 | B10d = 40564 MTTFd = 43.9 years | MTTFd = 32.9 years B10d = 30437 | MTTFd = 43.9 years B10d = 40564 | B10d = 30437 MTTFd = 32.9 years | MTTFd = 43.9 years B10d = 40564 | MTTFd = 43.9 years B10d = 40564 | B10d = 45447 MTTFd = 49.2 years | B10d = 45447 MTTFd = 49.2 years | MTTFd = 49.2 years B10d = 45447 | MTTFd = 49.2 years B10d = 45447 | MTTFd = 49.2 years B10d = 45447 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 60000 | B10d = 60000 | B10d = 60000 | B10d = 60000 | B10d = 60000 | B10d = 60000 | B10d = 60000 | B10d = 60000 | RSL1PRBU: B10d = 60000; RSL1PREU: B10d = 60000; RSL1PRFU: B10d = 60000; RSL1PRJU: B10d = 60000; RSL1PRPU: B10d = 60000; RSL1PVBU: B10d = 60000; RSL1PVEU: B10d = 60000; RSL1PVFU: B10d = 60000; RSL1PVJU: B10d = 60000; RSL1PVPU: B10d = 60000
| sale per indivisible quantity | [320 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | [8 empty] | RSL1PRBU: 10; RSL1PREU: 10; RSL1PRFU: 10; RSL1PRJU: 10; RSL1PRPU: 10; RSL1PVBU: 10; RSL1PVEU: 10; RSL1PVFU: 10; RSL1PVJU: 10; RSL1PVPU: 10
| sensitivity adjustment | [208 empty] | 5…100 % | 5…100 % | 5…100 % | 5…100 % | [23 empty] | 5…100 % | 5…100 %
| sensitivity scale | [208 empty] | 0.25...5 kOhm LS (Low Sensitivity) 5...100 kOhm St (Standard Sensitivity) 50...1000 kOhm HS (High Sensitivity) | 0.25...5 kOhm LS (Low Sensitivity) 5...100 kOhm St (Standard Sensitivity) 50...1000 kOhm HS (High Sensitivity) | 5...100 kOhm St (Standard Sensitivity) | 5...100 kOhm St (Standard Sensitivity) | [23 empty] | 0.25...5 kOhm LS (Low Sensitivity) 5...100 kOhm St (Standard Sensitivity) 50...1000 kOhm HS (High Sensitivity) | [5 empty] | 0.05...0.5 V E1-M terminals 0.3...3 V E2-M terminals 0.5...5 V E3-M terminals | 1...10 V E1-M terminals 10...100 V E3-M terminals 5...50 V E2-M terminals | 15...150 V E1-M terminals 30...300 V E2-M terminals 60...600 V E3-M terminals | [13 empty] | 0.25...5 kOhm LS (Low Sensitivity) 2.5...50 kOhm St (Standard Sensitivity) 25...500 kOhm HS (High Sensitivity) | 0.25...5 kOhm LS (Low Sensitivity) 2.5...50 kOhm St (Standard Sensitivity) 25...500 kOhm HS (High Sensitivity) | 0.25...5 kOhm LS (Low Sensitivity) 2.5...50 kOhm St (Standard Sensitivity) 25...500 kOhm HS (High Sensitivity) | 0.25...5 kOhm LS (Low Sensitivity) 2.5...50 kOhm St (Standard Sensitivity) 25...500 kOhm HS (High Sensitivity) | 0.25...5 kOhm LS (Low Sensitivity) 2.5...50 kOhm St (Standard Sensitivity) 25...500 kOhm HS (High Sensitivity) | 5...100 kOhm | 5...100 kOhm | 5...100 kOhm | 5...100 kOhm
| setting accuracy of the switching threshold | [206 empty] | +/- 10 % of the full scale | +/- 10 % of the full scale |  |  |  |  | +/- 10 % of the full scale | +/- 10 % of the full scale |  | +/- 10 % of the full scale | +/- 10 % of the full scale | +/- 10 % of the full scale | +/- 10 % of the full scale | [13 empty] | +/- 10 % of the full scale | +/- 10 % of the full scale for 1.5 A +/- 10 % of the full scale for 5 A +/- 20 % of the full scale for 15 A | [12 empty] | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | [9 empty] | +/-3 % | +/-3 % | +/-3 % | +/-3 % |  | +/-3 % | +/-3 % | +/-3 % | +/-3 % | +/-3 % | +/-3 % | +/-3 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-5 % | +/-3 % | +/-3 % |  |  |  |  | +/- (1.5 % + 1 V) +/- (1.5 % + 1 V)
| setting accuracy of time delay | [80 empty] | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 5 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 5 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 5 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 5 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale | +/- 10 % of full scale | +/- 10 % of full scale | +/- 10 % of full scale | +/- 10 % of full scale | +/- 10 % of full scale | +/- 10 % of full scale | +/- 10 % of full scale | +/- 20 % of full scale | +/- 20 % of full scale | +/- 20 % of full scale | +/- 1 % for 1...999 h time delay range at 25 °C +/- 2 % for 1 h time delay range at 25 °C +/- 20 ms for 100 ms...10 s time delay range at 25 °C | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1 | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1 | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1 | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1 | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1 | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1 | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1 | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1 | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1 | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1 | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 20 % of full scale | +/- 20 % of full scale | +/- 20 % of full scale | +/- 20 % of full scale | +/- 20 % of full scale | +/- 20 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | +/- 15 % of full scale | [14 empty] | 10 % | 10 P |  |  |  |  | 10 % | 10 % |  | 10 % | 10 P | 10 % | 10 % | [13 empty] | 10 P | 10 % | [12 empty] | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | [9 empty] | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P | 10 P |  |  |  |  | +/- 3 % for 10 s...60 min time delay range +/- 300 ms for 0...10 s time delay range
| shape of pin | [320 empty] | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat | Flat (PCB type) | Flat (PCB type) | Flat (PCB type) | Flat (PCB type) | Flat (PCB type) | Flat (PCB type) | Flat (PCB type) | Flat (PCB type)
| short-circuit current | [239 empty] | 0.007 A temperature sensing circuit (T1-T2 terminals short circuited) | 0.007 A temperature sensing circuit (T1-T2 terminals short circuited)
| short-circuit protection | [615 empty] | 0.63 A | 0.63 A | 0.63 A | 0.63 A | 0.63 A | 0.16 A | 0.16 A | 0.16 A | 0.16 A | 0.16 A | 0.16 A | 0.16 A | 0.16 A | 0.16 A | 0.16 A | [5 empty] | 0.63 A | 0.63 A | 0.63 A | 0.63 A | 0.63 A | 0.16 A | 0.16 A | 0.16 A | 0.16 A | 0.16 A | 0.16 A | 0.16 A | 0.16 A | 0.16 A | 0.16 A | [14 empty] | 0.2 A | 0.2 A | [7 empty] | 0.2 A
| signalling type | [400 empty] | XVBC9B: Continuous or intermittent buzzer; XVBC9M: Continuous or intermittent buzzer | [117 empty] | Continuous or intermittent buzzer | Continuous or intermittent buzzer | Continuous or intermittent buzzer | [18 empty] | Flashing Blinking Rotating | Rotating Blinking Flashing | Flashing Blinking Rotating | Rotating Flashing Blinking | Rotating Buzzer Blinking Flashing | Rotating Blinking Flashing | Blinking Rotating Flashing
| status LED | [97 empty] | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (steady) for power ON | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (steady) for power ON | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED green (flashing) for timing in progress LED green (steady) for power ON LED yellow for relay energised | LED green (flashing) for timing in progress LED green (steady) for power ON LED yellow for relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED green (flashing) for timing in progress LED green (steady) for power ON LED yellow for relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (steady) for power ON | LED green (flashing) for timing in progress LED green (steady) for power ON LED yellow for relay energised | LED green (flashing) for timing in progress LED green (steady) for power ON LED yellow for relay energised | LED green (flashing) for timing in progress LED green (steady) for power ON LED yellow for relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED green (flashing) for timing in progress LED green (steady) for power ON LED yellow for relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | [15 empty] | LED Un: (steady), green for power ON LED R1: (steady), amber for relay energised LED R2: (steady), amber for relay energised LED pairing: (steady), green for communication status LED Un: (fast blinking), green for diagnosis mode LED R1: (blinking), amber for timing in progress LED R2: (blinking), amber for timing in progress | [62 empty] | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: |  |  |  | 1 LED green for power ON 1 LED yellow for fault 1 LED yellow for relay ON |  |  | LED (yellow)relay ON: LED (green)power ON: | LED (yellow)relay ON: LED (green)power ON: |  |  |  | 1 LED green for power ON 1 LED yellow for inhibit 1 LED yellow for relay (R)
| supply circuit type | [661 empty] | AC/DC | AC | AC
| supply disconnection value | [132 empty] | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | [103 empty] | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | [12 empty] | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc | > 0.1 Uc
| supply frequency | [80 empty] | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % | [15 empty] | 50...60 Hz +/- 5 % | [49 empty] | 50/60 Hz +/- 10 % | 50/60 Hz +/- 10 % | 50/60 Hz +/- 10 % | 50/60 Hz +/- 10 % | 50/60 Hz +/- 10 % | 50/60 Hz +/- 10 % | [27 empty] | 50/60 Hz +/- 10 % | 50/60 Hz +/- 10 % | 50/60 Hz +/- 10 % | 50/60 Hz +/- 10 % | 50/60 Hz +/- 10 % | [6 empty] | 50/60 Hz +/- 10 % | 50/60 Hz +/- 10 % | 50/60 Hz +/- 10 % | 50/60 Hz +/- 10 % | [25 empty] | 50/60 Hz +/- 5 % | 50/60 Hz +/- 5 % | 50/60 Hz +/- 5 % | 50/60 Hz +/- 5 % | 50/60 Hz +/- 5 % | 50/60 Hz +/- 5 % | 50/60 Hz +/- 5 % | 50/60 Hz +/- 5 % | 50/60 Hz +/- 5 % | 50/60 Hz +/- 5 % | 50/60 Hz +/- 5 % | 50/60 Hz +/- 5 % | [21 empty] | 50/60 Hz +/- 5 % | 50/60 Hz +/- 5 %
| supply voltage for sensor | [237 empty] | 11.5...12.5 V
| supply voltage frequency | [206 empty] | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % |  |  |  |  | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 % | 40...70 Hz +/- 10 % | 40...70 Hz +/- 10 % | 40...70 Hz +/- 10 % | 40...70 Hz +/- 10 % | 40...70 Hz +/- 10 % | 40...70 Hz +/- 10 % | 50...60 Hz +/- 10 % | [79 empty] | 50...60 Hz +/- 10 %
| supply voltage limits | [192 empty] | 20.4…264 V AC/DC | 183…528 V AC | 183…528 V AC | 183…528 V AC | 183…484 V AC | 183…528 V AC | 183…528 V AC | 7…20 V DC | 50…270 V AC/DC | 165…270 V AC | 15…100 V AC/DC | 183…528 V AC | 50…270 V AC/DC | 15…100 V AC/DC | 20.4…264 V AC/DC | 20.4…264 V AC/DC | 20.4…264 V AC/DC | 323…456.5 V AC | 20.4…264 V AC/DC | 323…456.5 V AC | 160…288 V AC | 304…576 V AC | 183…528 V AC | 160…288 V AC | 304…576 V AC | 160…288 V AC | 304…576 V AC | 20.4…264 V AC/DC | 20.4…264 V AC/DC | 20.4…264 V AC/DC | 20.4…264 V AC/DC | 20.4…264 V AC/DC | 20.4…264 V AC/DC | 60…280 V AC | 20.4…264 V AC 21.6…264 V DC | 20.4…264 V AC 21.6…264 V DC | 20.4…264 V AC 21.6…264 V DC | 183…528 V AC | 102…308 V AC | 20.4…264 V AC/DC | 20.4…264 V AC/DC | 323…456.5 V AC | 20.4…264 V AC/DC | 20.4…264 V AC/DC | 20.4…264 V AC/DC | 20.4…264 V AC/DC | 194…528 V AC, 3 phases | 20.4…264 V AC 20.4…264 V DC | 20.4…264 V AC 20.4…264 V DC | 20.4…264 V AC/DC | 20.4…264 V AC/DC | 20.4…264 V AC/DC | 194…528 V AC | 114…329 V AC | [53 empty] | 60…300 V AC/DC | 160…300 V AC |  |  |  |  | 166.4…576 V AC line to line 96…332.4 V AC line to neutral
| surge withstand | [128 empty] | 1 kV differential mode conforming to IEC 61000-4-5 level 3 2 kV common mode conforming to IEC 61000-4-5 level 3 | 1 kV differential mode conforming to IEC 61000-4-5 level 3 2 kV common mode conforming to IEC 61000-4-5 level 3 | 1 kV differential mode conforming to IEC 61000-4-5 level 3 2 kV common mode conforming to IEC 61000-4-5 level 3 | 1 kV differential mode conforming to IEC 61000-4-5 level 3 2 kV common mode conforming to IEC 61000-4-5 level 3 | 2 kV conforming to IEC 61000-4-5 level 3 | 2 kV conforming to IEC 61000-4-5 level 3 | 2 kV conforming to IEC 61000-4-5 level 3 | 2 kV conforming to IEC 61000-4-5 level 3 | 2 kV conforming to IEC 61000-4-5 level 3 | 2 kV conforming to IEC 61000-4-5 level 3 | 2 kV conforming to IEC 61000-4-5 level 3 | 2 kV conforming to IEC 61000-4-5 level 3 | 2 kV conforming to IEC 61000-4-5 level 3 | 2 kV conforming to IEC 61000-4-5 level 3 | 2 kV conforming to IEC 61000-4-5 level 3 |  | 2 kV conforming to EN/IEC 61000-4-5 level 3 | 2 kV conforming to EN/IEC 61000-4-5 level 3 | 2 kV conforming to EN/IEC 61000-4-5 level 3 | 2 kV conforming to EN/IEC 61000-4-5 level 3 | 2 kV conforming to EN/IEC 61000-4-5 level 3 | 2 kV conforming to EN/IEC 61000-4-5 level 3 | 2 kV conforming to EN/IEC 61000-4-5 level 3 | 2 kV conforming to EN/IEC 61000-4-5 level 3 | 2 kV conforming to EN/IEC 61000-4-5 level 3 | 2 kV conforming to EN/IEC 61000-4-5 level 3 | [147 empty] | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 |  | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
| switching capacity in VA | [97 empty] | 2000 VA | 2000 VA | 2000 VA | 2000 VA 2000 VA | 2000 VA | 2000 VA | 1250 VA | 2000 VA | 1250 VA | 2000 VA | 2000 VA | 2000 VA |  |  | 2000 VA | 2000 VA |  | 2000 VA | 2000 VA | 2000 VA | 1250 VA |  |  |  | 2000 VA |  | 2000 VA | 2000 VA | 2000 VA | 2000 VA | 2000 VA | [15 empty] | 2000 VA
| switching capacity in mA | [246 empty] | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V | 10 mA at 12 V
| switching threshold drift | [206 empty] | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range |  |  |  |  | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range |  | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range | [13 empty] | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range | [12 empty] | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | [9 empty] | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range |  | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range | <= 0.06 % per degree centigrade depending permissible ambient air temperature <= 0.5 % within the measuring range
| switching time | [154 empty] | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
| switching voltage | [246 empty] | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | 250 V AC | [99 empty] | RSL1PRBU: 12 V; RSL1PREU: 12 V; RSL1PRFU: 12 V; RSL1PRJU: 12 V; RSL1PRPU: 12 V; RSL1PVBU: 12 V; RSL1PVEU: 12 V; RSL1PVFU: 12 V; RSL1PVJU: 12 V; RSL1PVPU: 12 V
| temperature coefficient | [301 empty] | 1000 ppm/°C, range: 0...5 A 2000 ppm/°C, range: 0...15 A 500 ppm/°C, range: 0...1.5 A | 200 ppm/°C | 200 ppm/°C | 200 ppm/°C |  | 150 ppm/°C | 150 ppm/°C | 150 ppm/°C | 150 ppm/°C | 150 ppm/°C | 150 ppm/°C | 150 ppm/°C | 150 ppm/°C | 150 ppm/°C | 200 ppm/°C | 200 ppm/°C | 200 ppm/°C | 200 ppm/°C | 200 ppm/°C
| temperature drift | [80 empty] | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.02 %/°C of the maximum setting value conforming to IEC 61812-1 | +/- 0.02 %/°C of the maximum setting value conforming to IEC 61812-1 | +/- 0.02 %/°C of the maximum setting value conforming to IEC 61812-1 | +/- 0.02 %/°C of the maximum setting value conforming to IEC 61812-1 | < 0.07 %/°C | < 0.07 %/°C | < 0.07 %/°C | < 0.07 %/°C | < 0.07 %/°C | < 0.07 %/°C | < 0.07 %/°C | < 0.07 %/°C | < 0.2 %/°C | < 0.2 %/°C | < 0.2 %/°C | +/- 0.05 %/°C | 0.05 %/°C | 0.05 %/°C | 0.05 %/°C | 0.05 %/°C | 0.05 %/°C | 0.05 %/°C | 0.05 %/°C | 0.05 %/°C | 0.05 %/°C | 0.05 %/°C
| temperature probe type | [226 empty] | Pt 100 - 3-wire | Pt 100 - 3-wire | Pt 100 - 3-wire
| terminal description | [132 empty] | (B1-A2)CO ALT (15-16-18)OC_OFF | (Y1)UNUSED (15-16-18)OC (Z1)UNUSED (Z2)UNUSED (B1-A2)CO ALT (X1)UNUSED | (25-26-28)OC_OFF (15-16-18)OC_OFF (Z1)UNUSED (X1)UNUSED (Y1)UNUSED (Z2)UNUSED (A1-A2)CO | (A1-A2)CO (15-16-18)OC_OFF | (15-16-18)OC_OFF (25-26-28)OC_OFF (Z1)UNUSED (Z2)UNUSED (A1-A2)CO | (15-16-18)OC_OFF (B1-A2)CO ALT | (B1-A2)CO (Z2)UNUSED (15-16-18)OC_OFF (Z1)UNUSED ALT (25-26-28)OC_ON | (B1-A2)CO (25-26-28)OC_ON ALT (15-16-18)OC_ON (Z2)UNUSED | ALT (A1-B1)CO (15-16-18)OC_OFF | ALT (A1-B1)CO (15-16-18)OC_OFF | ALT (A1-B1)CO (15-16-18)OC_OFF
| terminals description ISO n°1 | [154 empty] | (31-32-34)OC (41-42-44)OC (21-22-24)OC (11-12-14)OC (B1-A2-B2)CO | (41-42-44)OC (21-22-24)OC (B1-A2-B2)CO (11-12-14)OC (31-32-34)OC | (41-42-44)OC (B1-A2-B2)CO (21-22-24)OC (31-32-34)OC (11-12-14)OC | (B1-A2-B2)CO (41-42-44)OC (31-32-34)OC (11-12-14)OC (21-22-24)OC | (B1-A2-B2)CO (11-12-14)OC (21-22-24)OC (41-42-44)OC (31-32-34)OC | (11-12-14)OC (31-32-34)OC (21-22-24)OC (41-42-44)OC (B1-A2-B2)CO | (41-42-44)OC (11-12-14)OC (B1-A2-B2)CO (21-22-24)OC (31-32-34)OC | (31-32-34)OC (21-22-24)OC (41-42-44)OC (B1-A2-B2)CO (11-12-14)OC | (41-42-44)OC (11-12-14)OC (31-32-34)OC (21-22-24)OC (B1-A2-B2)CO | (31-32-34)OC (21-22-24)OC (11-12-14)OC (41-42-44)OC (B1-A2-B2)CO | (11-12-14)OC (41-42-44)OC (21-22-24)OC (B1-A2-B2)CO (31-32-34)OC | (B1-A2-B2)CO (31-32-34)OC (41-42-44)OC (21-22-24)OC (11-12-14)OC | (B1-A2-B2)CO (11-12-14)OC (31-32-34)OC (21-22-24)OC (41-42-44)OC | (41-42-44)OC (31-32-34)OC (B1-A2-B2)CO (11-12-14)OC (21-22-24)OC | (31-32-34)OC (11-12-14)OC (B1-A2-B2)CO (21-22-24)OC (41-42-44)OC | (31-32-34)OC (B1-A2-B2)CO (21-22-24)OC (41-42-44)OC (11-12-14)OC | (31-32-34)OC (21-22-24)OC (41-42-44)OC (11-12-14)OC (B1-A2-B2)CO | (B1-A2-B2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC | (B1-A2-B2)CO (21-22-24)OC (41-42-44)OC (31-32-34)OC (11-12-14)OC | (11-12-14)OC (41-42-44)OC (21-22-24)OC (31-32-34)OC (B1-A2-B2)CO | (31-32-34)OC (A1-A2)CO (11-12-14)OC (21-22-24)OC (41-42-44)OC | (21-22-24)OC (31-32-34)OC (41-42-44)OC (A1-A2)CO (11-12-14)OC | (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC | (21-22-24)OC (41-42-44)OC (31-32-34)OC (11-12-14)OC (A1-A2)CO | (31-32-34)OC (A1-A2)CO (11-12-14)OC (41-42-44)OC (21-22-24)OC | (A1-A2)CO (31-32-34)OC (11-12-14)OC (21-22-24)OC (41-42-44)OC | (31-32-34)OC (41-42-44)OC (A1-A2)CO (21-22-24)OC (11-12-14)OC | (A1-A2)CO (11-12-14)OC (41-42-44)OC (31-32-34)OC (21-22-24)OC | (31-32-34)OC (21-22-24)OC (11-12-14)OC (A1-A2)CO (41-42-44)OC | (31-32-34)OC (41-42-44)OC (11-12-14)OC (21-22-24)OC (A1-A2)CO | (21-22-24)OC (11-12-14)OC (41-42-44)OC (A1-A2)CO (31-32-34)OC | (41-42-44)OC (A1-A2)CO (11-12-14)OC (21-22-24)OC (31-32-34)OC | (31-32-34)OC (21-22-24)OC (41-42-44)OC (A1-A2)CO (11-12-14)OC | (41-42-44)OC (A1-A2)CO (21-22-24)OC (11-12-14)OC (31-32-34)OC | (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC | (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC | (A1-A2)CO (41-42-44)OC (11-12-14)OC (31-32-34)OC (21-22-24)OC | (A1-A2)CO (41-42-44)OC (11-12-14)OC (21-22-24)OC (31-32-34)OC | [54 empty] | (C-B1-B2-B3)CO (15-16-18)OC (A1-A2)CO | (A1-A2)CO (15-16-18)OC (C-B1-B2-B3)CO | (15-16-18)OC (C-B1-B2-B3)CO (A1-A2)CO | (25-26-28)OC (C-B1-B2-B3)CO (A1-A2)CO (15-16-18)OC | (C-B1-B2-B3)CO (25-26-28)OC (A1-A2)CO (15-16-18)OC | (25-26-28)OC (C-B1-B2-B3)CO (15-16-18)OC (A1-A2)CO | (A1-A2)CO (15-16-18)OC (C-B1-B2-B3)CO (25-26-28)OC | (15-16-18)OC (C-B1-B2-B3)CO (A1-A2)CO (25-26-28)OC | (15-16-18)OC (C-B1-B2-B3)CO (25-26-28)OC (A1-A2)CO | (C-B1-B2-B3)CO (25-26-28)OC (A1-A2)CO (15-16-18)OC | (15-16-18)OC (25-26-28)OC (C-B1-B2-B3)CO (A1-A2)CO | (B1-B2-B3)CO (A1-A2)CO (15-16-18)OC (25-26-28)OC | (A1-A2)CO (15-16-18)OC (25-26-28)OC (B1-B2-B3)CO | (A1-A2)CO (25-26-28)OC (B1-B2-B3)CO (15-16-18)OC | (15-16-18)OC (25-26-28)OC (B1-B2-B3)CO (A1-A2)CO | (15-16-18)OC (B1-B2-B3)CO (A1-A2)CO (25-26-28)OC | (15-16-18)OC (A1-A2)CO (B1-B2-B3)CO | (B1-B2-B3)CO (15-16-18)OC (A1-A2)CO | (B1-B2-B3)CO (15-16-18)OC (A1-A2)CO | (B1-B2-B3)CO (A1-A2)CO (15-16-18)OC | (15-16-18)OC (L1-L2-L3)CO | (15-16-18)OC (L1-L2-L3)CO | (25-26-28)OC (15-16-18)OC (L1-L2-L3)CO | (25-26-28)OC (L1-L2-L3)CO (15-16-18)OC | (L1-L2-L3)CO (15-16-18)OC (25-26-28)OC ALT | (25-26-28)OC (L1-L2-L3)CO (15-16-18)OC | (15-16-18)OC (L1-L2-L3)CO (25-26-28)OC | (25-26-28)OC (15-16-18)OC (L1-L2-L3)CO | (15-16-18)OC (25-26-28)OC (L1-L2-L3)CO | (L1-L2-L3)CO (25-26-28)OC (15-16-18)OC | ALT (L1-L2-L3)CO (25-26-28)OC (15-16-18)OC | ALT (25-26-28)OC (L1-L2-L3)CO (15-16-18)OC | (A1-A2)CO (C-B1-B2-B3)CO (15-16-18)OC | (C-B1-B2-B3)CO (15-16-18)OC (A1-A2)CO | (15-16-18)OC (A1-A2)CO (C-B1-B2-B3)CO | (15-16-18)OC (A1-A2)CO (C-B1-B2-B3)CO | (C-B1-B2-B3)CO (15-16-18)OC (A1-A2)CO | (C-B1-B2-B3)CO (15-16-18)OC (A1-A2)CO | (A1-A2)CO (C-B2-B3)CO (15-16-18)OC | (A1-A2)CO (C-B2-B3)CO (15-16-18)OC | (A1-A2)CO (15-16-18)OC (C-B2-B3)CO | (15-16-18)OC (A1-A2)CO (C-B1-B2-B3)CO (25-26-28)OC | (25-26-28)OC (C-B1-B2-B3)CO (A1-A2)CO (15-16-18)OC |  | (A1-A2)CO (25-26-28)OC (C-B1-B2-B3)CO (15-16-18)OC | (15-16-18)OC (25-26-28)OC (A1-A2)CO (C-B1-B2-B3)CO | (C-B1-B2-B3)CO (25-26-28)OC (A1-A2)CO (15-16-18)OC | (15-16-18)OC (25-26-28)OC (C-B1-B2-B3)CO (A1-A2)CO | (C-B1-B2-B3)CO (15-16-18)OC (A1-A2)CO (25-26-28)OC | (C-B2-B3)CO (15-16-18)OC (A1-A2)CO (25-26-28)OC | (C-B2-B3)CO (15-16-18)OC (25-26-28)OC (A1-A2)CO | (25-26-28)OC (C-B2-B3)CO (15-16-18)OC (A1-A2)CO | (C-B2-B3)CO (A1-A2)CO (25-26-28)OC (15-16-18)OC | (15-16-18)OC (L1-L3)CO (25-26-28)OC | (15-16-18)OC | [91 empty] | (11-12-14)OC (A1-A2)CO | (A1-A2)CO (11-12-14)OC | (A1-A2)CO (11-12-14)OC | (11-12-14)OC (A1-A2)CO | (A1-A2)CO (11-12-14)OC | (A1-A2)CO (11-12-14)OC | (11-12-14)OC (A1-A2)CO | (A1-A2)CO (11-12-14)OC | (A1-A2)CO (11-12-14)OC | (11-12-14)OC (A1-A2)CO | (11-12-14)OC (A1-A2)CO | (A1-A2)CO (11-12-14)OC | (A1-A2)CO (11-12-14)OC | (A1-A2)CO (11-12-14)OC | (11-12-14)OC (A1-A2)CO | (A1-A2)CO (11-12-14)OC | (11-12-14)OC (A1-A2)CO | (11-12-14)OC (A1-A2)CO | (COM-2)PW (COM-3)PW (COM-1)PW (GND)GROUND (COM-4)PW (COM-5)PW | (GND)GROUND (COM-1)PW (COM-4)PW (COM-3)PW (COM-5)PW (COM-2)PW | (COM-5)PW (COM-1)PW (COM-4)PW (COM-3)PW (GND)GROUND (COM-2)PW | (COM-4)PW (COM-2)PW (COM-3)PW (COM-1)PW (GND)GROUND (COM-5)PW | [39 empty] | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | [14 empty] | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW (GND)GROUND (COM-1)PW | [6 empty] | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND | (GND)GROUND (COM-1)PW
| terminals description ISO n°2 | [270 empty] | (11-12-14)OC ALT (L1-L2-L3)CO (21-22-24)OC | [5 empty] | (21-22-24)OC (11-12-14)OC (L1-L2-L3)CO ALT | (L1-L2-L3)CO (11-12-14)OC (21-22-24)OC ALT
| test levels | [320 empty] | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting |  | Level A group mounting | Level A group mounting | Level A group mounting | Level A group mounting | Level A group mounting | Level A group mounting | Level A group mounting | Level A group mounting | RSL1PRBU: Level A group mounting; RSL1PREU: Level A group mounting; RSL1PRFU: Level A group mounting; RSL1PRJU: Level A group mounting; RSL1PRPU: Level A group mounting; RSL1PVBU: Level A group mounting; RSL1PVEU: Level A group mounting; RSL1PVFU: Level A group mounting; RSL1PVJU: Level A group mounting; RSL1PVPU: Level A group mounting
| threshold adjustment voltage | [193 empty] | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC | -2...-17 % in the range 220 V AC +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC 2...20 % of Un selected |  |  | -2...-17 % in the range 220 V AC 2...20 % of Un selected +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC | -2...-12 % in the range 208 V AC -2...-17 % in the range 220 V AC 2...20 % of Un selected +2...+17 % in the range 480 V AC | [13 empty] | 2...20 % of Un selected | 2...20 % of Un selected |  | 2...20 % of Un selected | 2...20 % of Un selected | 2...20 % of Un selected | 2...20 % of Un selected | [19 empty] | -20...-2 % in the range 380...480 V AC 2...20 % of Un selected -12...-2 % in the range 220 V AC +2...+20 % in the range 220...440 V AC +2...+10 % in the range 480 V AC
| threshold setting | [192 empty] | 10...100 % | [13 empty] | 10...100 % | 10...100 % | [22 empty] | -2...10 Hz -10...2 Hz | 10...100 % | 10...100 % | 10...100 % | 10...100 % |  |  | 10...100 % |  |  |  | 10...100 % | 10...100 % | 10...100 %
| tightening torque | [80 empty] | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 |  | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 |  |  |  |  | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1 N.m conforming to IEC 60947-1 0.60…0.99 N.m conforming to IEC 60947-1 | [48 empty] | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.60…0.99 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1 N.m conforming to IEC 60947-1 0.60…0.99 N.m conforming to IEC 60947-1 | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | 0.6…1.1 N.m | [80 empty] | RSL1PRBU: 10...40 N.m; RSL1PREU: 10...40 N.m; RSL1PRFU: 10...40 N.m; RSL1PRJU: 10...40 N.m; RSL1PRPU: 10...40 N.m; RSL1PVBU: < 0.5 N.m for M2.5 screw(s); RSL1PVEU: < 0.5 N.m for M2.5 screw(s); RSL1PVFU: < 0.5 N.m for M2.5 screw(s); RSL1PVJU: < 0.5 N.m for M2.5 screw(s); RSL1PVPU: < 0.5 N.m for M2.5 screw(s)
| time delay drift | [206 empty] | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range |  |  |  |  | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range |  | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range | [13 empty] | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range | <= 0.05 % per degree centigrade depending permissible ambient air temperature <= 1 % within the supply voltage range | [15 empty] | <= 0.07 % per degree centigrade depending on temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | [9 empty] | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range |  | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range | [9 empty] | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the supply voltage range (0.85...1.1 Un) | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range | <= 0.07 % per degree centigrade depending on the rated operational temperature <= 0.5 % within the measuring range
| time delay on de-energisation | [266 empty] | 0.5 s | 0.5 s | 0.1…10 s | 0.1…10 s
| time delay range | [97 empty] | 3...30 min 1...10 s 30...300 s 10...100 s 3...30 s 30...300 min 30...300 h 0.3...3 s 0.05...1 s 3...30 h | 30...300 h 3...30 min 30...300 s 0.05...1 s 30...300 min 10...100 s 0.3...3 s 3...30 h 1...10 s | 3...30 s 30...300 s 10...100 s 0.05...1 s 1...10 s 30...300 h 30...300 min 0.3...3 s 3...30 h 3...30 min | 10...100 s 3...30 s 0.05...1 s 30...300 s 30...300 h 30...300 min 3...30 min 3...30 h 0.3...3 s 1...10 s 10...100 s 3...30 s 0.05...1 s 30...300 s 30...300 h 30...300 min 3...30 min 3...30 h 0.3...3 s 1...10 s | 0.05...1 s 30...300 h 30...300 min 30...300 s 3...30 min 1...10 s 3...30 s 0.3...3 s 10...100 s 3...30 h | 3...30 s 0.3...3 s 30...300 s 30...300 h 0.05...1 s 1...10 s 3...30 min 30...300 min 3...30 h 10...100 s | 10...100 s 1...10 min 1...10 s 0.3...3 s 3...30 s 0.05...1 s 30...300 s | 3...30 h 0.05...1 s 30...300 s 3...30 min 3...30 s 30...300 h 30...300 min 0.3...3 s 10...100 s 1...10 s | 0.3...3 s 0.05...0.5 s 3...30 s 0.1...1 s 30...300 s 10...100 s 1...10 s | 0.05...1 s 30...300 min 30...300 h 30...300 s 3...30 h 0.3...3 s 3...30 min 3...30 s 10...100 s 1...10 s | 30...300 s 10...100 s 3...30 s 30...300 min 3...30 min 0.3...3 s 0.05...1 s 30...300 h 1...10 s 3...30 h | 10...100 s 3...30 s 0.1...1 s 0.3...3 s 0.05...0.5 s 1...10 s 30...300 s | 1...10 h 10...100 h 6...60 s 1...10 min 0.1...1 s 1...10 s 6...60 min | 1...10 min 6...60 s 0.1...1 s 1...10 h 1...10 s 6...60 min 10...100 h | 3...30 h 30...300 h 0.05...1 s 30...300 s 0.3...3 s 10...100 s 1...10 s 3...30 min 30...300 min 3...30 s | 0.05...1 s 0.3...3 s 3...30 h 30...300 min 10...100 s 30...300 s 3...30 s 30...300 h 1...10 s 3...30 min | 1...10 min 10...100 h 1...10 s 0.1...1 s 6...60 s 6...60 min 1...10 h | 10...100 s 3...30 h 1...10 s 3...30 s 30...300 h 0.3...3 s 0.05...1 s 30...300 min 30...300 s 3...30 min | 1...10 s 30...300 min 3...30 s 10...100 s 30...300 h 30...300 s 3...30 min 0.3...3 s 0.05...1 s 3...30 h | 1...10 s 3...30 h 10...100 s 30...300 s 0.05...1 s 3...30 min 0.3...3 s 3...30 s 30...300 min 30...300 h | 10...100 s 0.05...1 s 30...300 s 3...30 s 1...10 min 1...10 s 0.3...3 s | 1...10 min 6...60 min 0.1...1 s 6...60 s 1...10 s 1...10 h 10...100 h | 10...100 h 6...60 s 0.1...1 s 1...10 h 1...10 s 1...10 min 6...60 min | 0.1...1 s 6...60 s 1...10 h 1...10 min 1...10 s 10...100 h 6...60 min | 0.05...1 s 30...300 min 30...300 s 3...30 h 0.3...3 s 1...10 s 3...30 s 30...300 h 3...30 min 10...100 s | 0.1...1 s 1...10 h 1...10 s 6...60 min 10...100 h 6...60 s 1...10 min | 3...30 min 30...300 min 0.3...3 s 3...30 h 10...100 s 1...10 s 0.05...1 s 30...300 s 30...300 h 3...30 s | 0.3...30 s | 0.3...30 s | 3...30 s 0.05...1 s 30...300 s 30...300 min 0.3...3 s 1...10 s 3...30 h 10...100 s 30...300 h 3...30 min | 1...10 s 3...30 s 10...100 s 30...300 min 0.05...1 s 3...30 min 0.3...3 s 30...300 s 3...30 h 30...300 h | [15 empty] | 0.1 s...999 h
| time delay type | [80 empty] | A | C | H | L, Li | A, Ac, At, B, Bw, C, D, Di, H, Ht | A, At | B | C | H, Ht | L, Li | L, Li | A, At, B, C, D, Di, H, Ht | A, Ac, At, B, Bw, C, D, Di, H, Ht | A, Ac, At, B, Bw, C, D, Di, H, Ht | A, Ac, At, B, Bw, C, D, Di, H, Ht | A, Ac, At, B, Bw, C, D, Di, H, Ht | Ad, Ah, N, O, P, Pt, TI, Tt, W | Ac Act | Ak Akt | A Aw | C Ct C Ct | Dw D | Hw H | K | A At Aw | K He | Li Lit L Lt | Dw Ac C Dit Ht D A Di Hw W Ct Act At Wt H Dt Diw Aw | Qc | Q | Q | Ac | Aw A | At A | C | D Dw | H Hw | K | B C Di Ht Bw Ac H At A D | Ht At Bw C Di B Ac H A D | C Di D B At H Bw Ac A | W Wt | Pt O P A Tl Ah N Tt W | Ht Dit Qgt D Dt W Ct Dw A Qt Qtt Diw C Wt Di Hw Qg At Aw H | Qe | Qe | Qg | Qt | [15 empty] | Tt Ak Ah Di Pt H At Dt Ad A Qt N Li L Qtt O Ht Lit C Lt W Tl P Ac Dit B D Bw
| tripping threshold | [239 empty] | 3100 Ohm +/- 10 % for temperature control circuit | 3100 Ohm +/- 10 % for temperature control circuit
| utilisation category | [193 empty] | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | [7 empty] | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | [6 empty] | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1 |  |  |  |  | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | [64 empty] | AC-15 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-1 conforming to IEC 60947-4-1 DC-1 conforming to IEC 60947-4-1
| voltage detection threshold | [195 empty] | < 100 V AC | < 100 V AC | [6 empty] | 183 V | [8 empty] | < 100 V AC | < 100 V AC | < 100 V AC | < 100 V AC | < 100 V AC | < 100 V AC | < 100 V AC | [19 empty] | < 194 V | [5 empty] | 194 V | 114 V
| voltage drift | [80 empty] | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V of the maximum setting value at 48...240 V +/- 1 %/V of the maximum setting value at 24...48 V | +/- 0.2 %/V of the maximum setting value at 48...240 V +/- 1 %/V of the maximum setting value at 24...48 V | +/- 0.2 %/V of the maximum setting value at 48...240 V +/- 1 %/V of the maximum setting value at 24...48 V | +/- 0.2 %/V of the maximum setting value at 48...240 V +/- 1 %/V of the maximum setting value at 24...48 V | < 0.2 %/V | < 0.2 %/V | < 0.2 %/V | < 0.2 %/V | < 0.2 %/V | < 0.2 %/V | < 0.2 %/V | < 0.2 %/V | < 2.5 %/V | < 2.5 %/V | < 2.5 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V
| voltage range | [80 empty] | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.9...1.2 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.9...1.2 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.9...1.2 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.16 Us | 0.85...1.1 Us | 0.85...1.1 Us |  |  |  |  | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.85...1.1 Us | 0.9...1.1 Us | 0.9...1.1 Us | 0.9...1.1 Us | 0.85...1.1 Un | 0.85...1.15 Us | 0.9...1.1 Us | 0.85...1.15 Us | 0.9...1.1 Us | 0.85...1.15 Us | 0.85...1.15 Us | 0.9...1.1 Us | 0.85...1.15 Us | 0.9...1.1 Us | 0.85...1.15 Us | [39 empty] | 208...480 V phase to phase | 208...480 V phase to phase | 183...528 V | 183...484 V | 208...480 V phase to phase | 208...480 V phase to phase | [13 empty] | 200...240 V phase to phase | 380...480 V phase to phase |  | 200...240 V phase to phase | 380...480 V phase to phase | 200...240 V phase to phase | 380...480 V phase to phase | [19 empty] | 220...480 V phase to phase | 176...528 V | 176...528 V
| width | [97 empty] | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm |  |  |  |  | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | [48 empty] | 17.5 mm | 17.5 mm | 17.5 mm | 17.5 mm | 17.5 mm | 17.5 mm | 17.5 mm | 17.5 mm | 17.5 mm | 17.5 mm | 17.5 mm | 17.5 mm | 17.5 mm | 17.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 35 mm | 35 mm | 35 mm | 35 mm | 35 mm | 35 mm | 35 mm | 35 mm | 35 mm | 35 mm | 35 mm | 35 mm | 35 mm | 35 mm | 35 mm | 35 mm | 35 mm | 35 mm | 35 mm | 35 mm | 23 mm | 23 mm | 23 mm | 23 mm | 23 mm | 23 mm | 23 mm | 45 mm | 45 mm | 45 mm | 45 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm |  |  |  |  | 22.5 mm | [86 empty] | 5 mm | 5 mm | 5 mm | 5 mm | 5 mm | 5 mm | 5 mm | 5 mm | 6.2 mm | 6.2 mm | 6.2 mm | 6.2 mm | 6.2 mm | 6.2 mm | 6.2 mm | 6.2 mm | 6.2 mm | 6.2 mm | [272 empty] | 100 mm | 100 mm | 100 mm | 100 mm | 100 mm | 100 mm | 100 mm | 114 mm | 114 mm | 114 mm | 140 mm | 140 mm | 140 mm | 72 mm | 72 mm | 72 mm | 72 mm | 96 mm | 96 mm | 96 mm | 96 mm | 80 mm | 80 mm | 80 mm | 105 mm | 105 mm | 105 mm | 105 mm | 105 mm
| width pitch dimension | [132 empty] | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm | 22.5 mm
Contractual warranty | Warranty | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | [48 empty] | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months |  | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months |  | 18 months | 18 months | 18 months | 18 months | [20 empty] | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months |  |  | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months |  | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | [7 empty] | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months
Environment | IP degree of protection | [80 empty] | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminal block) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminal block: conforming to IEC 60529 IP40 front face: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminal block: conforming to IEC 60529 IP40 front face: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminal block: conforming to IEC 60529 IP40 front face: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminal block: conforming to IEC 60529 IP40 front face: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminal block: conforming to IEC 60529 IP40 front face: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminal block: conforming to IEC 60529 IP40 front face: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP50 front face: conforming to IEC 60529 IP20 terminal block: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | IP40 (housing) conforming to IEC 60529 IP50 (front face) conforming to IEC 60529 | IP40 (housing) conforming to IEC 60529 IP50 (front face) conforming to IEC 60529 | IP40 (housing) conforming to IEC 60529 IP50 (front face) conforming to IEC 60529 | IP40 (housing) conforming to IEC 60529 IP50 (front face) conforming to IEC 60529 | IP20 (terminals) IP50 (housing) | IP20 (terminals) IP50 (housing) | IP20 (terminals) IP50 (housing) | IP20 (terminals) IP50 (housing) | IP20 (terminals) IP50 (housing) | IP20 (terminals) IP50 (housing) | IP20 (terminals) IP50 (housing) | IP20 (terminals) IP50 (housing) | IP20 (terminals) IP50 (casing) | IP20 (terminals) IP50 (casing) | IP20 (terminals) IP50 (casing) | IP40 housing: conforming to IEC 60529 IP40 front face: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 | IP50 conforming to IEC 60529 | IP50 conforming to IEC 60529 | IP50 conforming to IEC 60529 | IP50 conforming to IEC 60529 | IP50 conforming to IEC 60529 | IP50 conforming to IEC 60529 | IP50 conforming to IEC 60529 | IP50 conforming to IEC 60529 | IP50 conforming to IEC 60529 | IP50 conforming to IEC 60529 | [38 empty] | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 IP30 (housing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (front panel) conforming to IEC 60529 IP30 (housing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP50 (casing) conforming to IEC 60529 | IP20 (terminal block) IP50 (housing) | IP20 (terminal block) IP50 (housing) | IP20 (terminal block) IP50 (housing) | IP20 (terminal block) IP50 (housing) | IP20 (terminals) conforming to IEC 60529 IP40 (housing) conforming to IEC 60529 IP40 (front panel) conforming to IEC 60529 | IP20 (terminal block) IP50 (housing) | IP20 (terminal block) IP50 (housing) | IP20 (terminal block) IP50 (housing) | IP20 (terminal block) IP50 (housing) | IP20 (terminal block) IP50 (housing) | IP20 (terminal block) IP50 (housing) | IP20 (terminal block) IP50 (housing) | IP20 (terminal block) IP50 (housing) | IP20 (terminal block) IP50 (housing) | IP20 (terminal block) IP50 (housing) | IP20 (terminal block) IP50 (housing) | IP20 (terminal block) IP50 (housing) | IP20 (terminal block) IP50 (housing) | IP20 (terminal block) IP50 (housing) | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 |  |  | IP65 conforming to IEC 60529 IP65 conforming to NF C 20-010 | IP65 conforming to IEC 60529 IP65 conforming to NF C 20-010 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP65 on fixing base XVBZ0. conforming to IEC 60529 IP66 on base unit conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP40 any position except vertical position conforming to IEC 60529 IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP54 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP42 vertical position conforming to IEC 60529 | IP65 (upright) IP23 (sideways) IP23 (inverted) | IP65 (upright) IP23 (sideways) IP23 (inverted) | IP65 (upright) IP23 (sideways) IP23 (inverted) | IP65 (upright) IP23 (sideways) IP23 (inverted) | IP23 (sideways) IP23 (inverted) IP23 (upright) | IP23 (sideways) IP23 (inverted) IP23 (upright) | IP23 (sideways) IP23 (inverted) IP23 (upright) | IP53 | IP53 | IP53 | IP53 conforming to EN/IEC 60529 | IP53 conforming to EN/IEC 60529 | IP53 conforming to EN/IEC 60529 | Panel mounted: IP54 conforming to EN/IEC 60529 | Panel mounted: IP54 conforming to EN/IEC 60529 | Panel mounted: IP54 conforming to EN/IEC 60529 | Panel mounted: IP54 conforming to EN/IEC 60529 | Panel mounted: IP54 conforming to EN/IEC 60529 | Panel mounted: IP54 conforming to EN/IEC 60529 | Panel mounted: IP54 conforming to EN/IEC 60529 | Panel mounted: IP54 conforming to EN/IEC 60529 | Panel mounted: IP65 conforming to EN/IEC 60529 Wall mounted: IP20 | Panel mounted: IP65 conforming to EN/IEC 60529 Wall mounted: IP20 | Panel mounted: IP65 conforming to EN/IEC 60529 Wall mounted: IP20 | Panel mounted: IP65 conforming to EN/IEC 60529 Wall mounted: IP20 | Panel mounted: IP65 conforming to EN/IEC 60529 Wall mounted: IP20 | Panel mounted: IP65 conforming to EN/IEC 60529 Wall mounted: IP20 | Panel mounted: IP65 conforming to EN/IEC 60529 Wall mounted: IP20 | Panel mounted: IP65 conforming to EN/IEC 60529 Wall mounted: IP20
| NEMA degree of protection | [410 empty] | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor) | NEMA 4X conforming to UL 508 (indoor)
| [Us] rated supply voltage | [692 empty] | 12 V DC 24 V DC | 120 V AC | 240 V AC
| ambient air temperature for operation | [80 empty] | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C at 60 Hz -20…60 °C at 50 Hz AC/DC | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | -20…65 °C | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | -20…60 °C | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) | -40…70 °C (AC) -40…85 °C (DC) | -40…55 °C | -40…55 °C | -40…55 °C | -40…55 °C | -40…55 °C | -40…55 °C | -40…55 °C | -40…55 °C | -40…55 °C | -40…55 °C | -40…70 °C | -40…55 °C | -40…70 °C | -40…55 °C | -40…55 °C | -40…70 °C | -40…55 °C | -40…70 °C |  |  | -10…50 °C | -10…50 °C | [37 empty] | -25…50 °C | -25…50 °C | [36 empty] | -25…50 °C: LED -25…70 °C: incandescent | -25…50 °C: LED -25…70 °C: incandescent | -25…50 °C: LED -25…70 °C: incandescent | -25…50 °C: LED -25…70 °C: incandescent | -25…50 °C: LED -25…70 °C: incandescent | -25…50 °C: LED -25…70 °C: incandescent | [48 empty] | -25…70 °C | -25…70 °C | -25…50 °C | -25…50 °C | -25…50 °C | -25…50 °C | -25…50 °C | -25…50 °C | -25…50 °C | -25…50 °C | -25…50 °C | -25…50 °C | -25…50 °C | -25…50 °C | -25…50 °C: LED -25…70 °C: incandescent | -25…50 °C: LED -25…70 °C: incandescent | -25…50 °C: LED -25…70 °C: incandescent | -25…50 °C: LED -25…70 °C: incandescent | -25…40 °C: incandescent -25…50 °C: LED | -25…40 °C: incandescent -25…50 °C: LED | -25…40 °C: incandescent -25…50 °C: LED | -25…40 °C: incandescent -25…50 °C: LED | -25…40 °C: incandescent -25…50 °C: LED | -25…40 °C: incandescent -25…50 °C: LED | -25…40 °C: incandescent -25…50 °C: LED | -25…40 °C: incandescent -25…50 °C: LED | -25…40 °C: incandescent -25…50 °C: LED | -25…40 °C: incandescent -25…50 °C: LED | -25…40 °C: incandescent -25…50 °C: LED | -25…40 °C: incandescent -25…50 °C: LED | [8 empty] | -25…50 °C | -25…50 °C | -25…50 °C | -25…50 °C | -25…70 °C -25…70 °C | -25…70 °C -25…70 °C | -25…70 °C -25…70 °C | -25…70 °C -25…70 °C | -25…70 °C -25…70 °C | -25…70 °C -25…70 °C | -10…50 °C -10…50 °C | -10…50 °C -10…50 °C | -10…50 °C -10…50 °C | -10…50 °C -10…50 °C | -10…50 °C -10…50 °C | -10…50 °C -10…50 °C | -10…50 °C -10…50 °C | [11 empty] | -25…50 °C | -25…50 °C | -25…50 °C | -25…50 °C | -25…50 °C | -25…50 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -25…55 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -30…50 °C | -30…50 °C | -30…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -10…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | -10…55 °C | -10…55 °C | -10…55 °C | -10…55 °C | -10…55 °C | -10…55 °C | 0…50 °C | 0…50 °C
| ambient air temperature for storage | [80 empty] | -30…60 °C | -30…60 °C | -30…60 °C | -30…60 °C | -30…60 °C | -30…60 °C | -30…60 °C | -30…60 °C | -30…60 °C | -30…60 °C | -30…60 °C | -30…60 °C | -30…60 °C | -30…60 °C | -30…60 °C | -30…60 °C | -30…60 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -30…60 °C | -30…60 °C | -40…70 °C | -40…70 °C | -30…60 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -30…60 °C | -30…60 °C | -30…60 °C | -40…70 °C | -30…60 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…70 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…70 °C | -40…70 °C | -20…70 °C | -20…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -25…70 °C | -35…70 °C | -35…70 °C | -35…70 °C | -35…70 °C | -20…70 °C | -20…70 °C | -20…70 °C | -35…70 °C | -35…70 °C | -35…70 °C | -35…70 °C | -35…70 °C | -35…70 °C | -35…70 °C | -35…70 °C | -35…70 °C | -35…70 °C | -35…70 °C | -35…70 °C | -35…70 °C | -35…70 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C | -20…60 °C
| derating factor | [80 empty] | 5 mA/°C | 5 mA/°C | 5 mA/°C | 5 mA/°C | 5 mA/°C
| dielectric strength | [97 empty] | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 1 kV 1 mA/1 minute conforming to IEC 61812-1 | 1 kV 1 mA/1 minute conforming to IEC 61812-1 | 1 kV 1 mA/1 minute conforming to IEC 61812-1 | 1 kV 1 mA/1 minute conforming to IEC 61812-1 | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV |  |  |  | 2.5 kV for 1 mA/1 minute at 50 Hz with between relay output and power supply with basic insulation with basic insulation | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1 | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1 | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1 | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1 | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1 | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1 | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1 | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1 | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1 | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1 | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | 2500 V | [37 empty] | 2 kV AC 50 Hz (shock wave 4 kV) | [90 empty] | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact | 1000 V AC between contacts 4000 V AC between coil and contact
| dielectric test voltage | [140 empty] | 2.5 kV | 2.5 kV | 2.5 kV | [49 empty] | 2 kV AC 50 Hz | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz | 2 kV, 1 min AC 50 Hz | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2 kV, 1 min AC 50 Hz | 2 kV, 1 min AC 50 Hz | 2 kV, 1 min AC 50 Hz |  | 2 kV AC 50 Hz | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV AC 50 Hz | 2 kV, 1 min AC 50 Hz | 2 kV, 1 min AC 50 Hz | 2 kV, 1 min AC 50 Hz | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz | 2 kV, 1 min AC 50 Hz | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV | 2.5 kV
| directives | [97 empty] | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | [15 empty] | 2014/35/EU - low voltage directive 2014/53/EU - radio equipment directive 2014/30/EU - electromagnetic compatibility | [49 empty] | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | [32 empty] | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | [20 empty] | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility | [6 empty] | 2014/30/EU - electromagnetic compatibility 2014/35/EU - low voltage directive 2014/53/EU - radio equipment directive 2015/863/EU - RoHS directive
| discrete output type | [695 empty] | NPN | PNP | NPN | PNP | NPN | PNP | NPN | PNP | NPN | PNP | NPN | NPN | PNP | NPN | NPN | NPN
| disturbance radiated/conducted | [128 empty] | Class B 0.15...30 MHz conforming to EN 55022 (EN 55011 group 1) | Class B 0.15...30 MHz conforming to EN 55022 (EN 55011 group 1) | Class B 0.15...30 MHz conforming to EN 55022 (EN 55011 group 1) | Class B 0.15...30 MHz conforming to EN 55022 (EN 55011 group 1) | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A |  | Class B conforming to EN 55022 (EN 55011 group 1) | Class B conforming to EN 55022 (EN 55011 group 1) | Class B conforming to EN 55022 (EN 55011 group 1) | Class B conforming to EN 55022 (EN 55011 group 1) | Class B conforming to EN 55022 (EN 55011 group 1) | Class B conforming to EN 55022 (EN 55011 group 1) | Class B conforming to EN 55022 (EN 55011 group 1) | Class B conforming to EN 55022 (EN 55011 group 1) | Class B conforming to EN 55022 (EN 55011 group 1) | Class B conforming to EN 55022 (EN 55011 group 1) | [92 empty] | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 11 group 1 - class A CISPR 22 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 22 - class A CISPR 11 group 1 - class A | CISPR 11 CISPR 22 group 1 - class B | CISPR 22 group 1 - class B CISPR 11 | CISPR 22 group 1 - class B CISPR 11 | CISPR 11 CISPR 22 group 1 - class B |  | CISPR 11 CISPR 22 group 1 - class B | CISPR 11 CISPR 22 group 1 - class B | CISPR 11 CISPR 22 group 1 - class B | CISPR 22 group 1 - class B CISPR 11 | CISPR 22 group 1 - class B CISPR 11 | CISPR 22 group 1 - class B CISPR 11 | CISPR 11 CISPR 22 group 1 - class B | CISPR 22 group 1 - class B CISPR 11 | CISPR 11 CISPR 22 group 1 - class B | CISPR 11 CISPR 22 group 1 - class B | CISPR 22 group 1 - class B CISPR 11 | CISPR 22 group 1 - class B CISPR 11 | CISPR 11 CISPR 22 group 1 - class B | CISPR 11 CISPR 22 group 1 - class B
| electrical shock protection class | [414 empty] | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube conforming to IEC 61140 Class II on base unit conforming to IEC 61140 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on base unit conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I on support tube, with metal fixing plate conforming to IEC 60536 Class II on support tube, with plastic fixing plate conforming to IEC 60536 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 61140 Class I plastic tube mounting conforming to IEC 61140 | [10 empty] | Class I aluminium tube mounting conforming to IEC 60947-1 Class I aluminium tube mounting conforming to IEC 60947-5-1 Class I aluminium tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 60947-1 Class I aluminium tube mounting conforming to IEC 60947-5-1 Class I aluminium tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 60947-1 Class I aluminium tube mounting conforming to IEC 60947-5-1 Class I aluminium tube mounting conforming to IEC 61140 | Class I aluminium tube mounting conforming to IEC 60947-1 Class I aluminium tube mounting conforming to IEC 60947-5-1 Class I aluminium tube mounting conforming to IEC 61140 | [25 empty] | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140
| electromagnetic compatibility | [80 empty] | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 Conducted and radiated emissions: , class B, conforming to EN 55022 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Conducted and radiated emissions class B conforming to EN 55022 | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Conducted and radiated emissions class B conforming to EN 55022 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Conducted and radiated emissions class B conforming to EN 55022 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Conducted and radiated emissions class B conforming to EN 55022 | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Conducted and radiated emissions class B conforming to EN 55022 | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Conducted and radiated emissions class B conforming to EN 55022 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Surge immunity test - test level: 2 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 4 kV level 3 (common mode) conforming to IEC 61000-4-5 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | [15 empty] | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Radiated emission class B conforming to EN 55022 Conducted emission class A conforming to EN 55022 Electromagnetic field immunity test - test level: 3 V/m level 2 (1.4 GHz...2 GHz) conforming to IEC 61000-4-3 Electromagnetic field immunity test - test level: 1 V/m level 1 (2...2.7 GHz) conforming to IEC 61000-4-3 | [48 empty] | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 Emission standard for residential, commercial and light-industrial environments (except radiated emission) conforming to EN/IEC 61000-6-3 | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 Emission standard for residential, commercial and light-industrial environments (except radiated emission) conforming to EN/IEC 61000-6-3 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Resistance to electrostatic discharge - test level: 6 kV (contact) conforming to IEC 61000-4-2 level 3 Resistance to electrostatic discharge - test level: 8 kV (air) conforming to IEC 61000-4-2 level 3 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | [6 empty] | Voltage dips and interruptions immunity test - test level: 70 % (25/30 cycles) conforming to IEC 61000-4-11 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Conducted and radiated emissions class B group 1 conforming to CISPR 11 Conducted and radiated emissions class B conforming to CISPR 22 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 1 MHz damped oscillating wave - test level: 2.5 kV CM, 1 kV DM criteria B conforming to IEC 61000-4-18 Voltage dips and interruptions immunity test - test level: 0 % (0.5...25 cycles) conforming to IEC 61000-4-11 Magnetic field at power frequency - test level: 30 A/m (continuous)-300 A/m (1-3 s) level 4 conforming to IEC 61000-4-8 Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 Voltage dips and interruptions immunity test - test level: 40 % (10/12 cycles) conforming to IEC 61000-4-11 Voltage interruptions - test level: 0 % criteria C (250/300 cycles) conforming to IEC 61000-4-29 Electrical fast transient/burst immunity test - test level: 4 kV criteria B (direct) conforming to IEC 61000-4-4 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Conducted RF disturbances level 3 conforming to IEC 61000-4-6 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
| environmental characteristic | [232 empty] | 3K3 C | 3K3 C | [12 empty] | 3K3 | 3K3 | 3K3 | 3K3 | 3K3 | 3K3 | 3K3 | 3K3 | 3K3 | 3K3 | 3K3
| fire resistance | [301 empty] | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL |  | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
| humidity drift | [128 empty] | +/- 0.05 %/%RH of the maximum setting value conforming to IEC 61812-1 | +/- 0.05 %/%RH of the maximum setting value conforming to IEC 61812-1 | +/- 0.05 %/%RH of the maximum setting value conforming to IEC 61812-1 | +/- 0.05 %/%RH of the maximum setting value conforming to IEC 61812-1
| immunity to microbreaks | [80 empty] | 20 ms | 20 ms | 20 ms | 20 ms | 20 ms | 20 ms | 20 ms | 20 ms | 20 ms | 20 ms | 20 ms | 20 ms | 20 ms | 20 ms | 20 ms | 20 ms | 20 ms | [31 empty] | 10 ms | 10 ms | 10 ms | 10 ms | 3 ms | 3 ms | 3 ms | 3 ms | 3 ms | 3 ms | 3 ms | 3 ms | 3 ms | 3 ms | 3 ms | 10 ms | 5 ms | 5 ms | 5 ms | 5 ms | 5 ms | 5 ms | 5 ms | 5 ms | 5 ms | 5 ms | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms | [13 empty] | 50 ms | 50 ms | 100 ms DC 90 ms AC | 100 ms DC 90 ms AC | 100 ms DC 90 ms AC | 100 ms DC 90 ms AC | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 10 ms | 20 ms | 10 ms | 10 ms | 10 ms | 500 ms | 10 ms | 50 ms | 50 ms | 50 ms | 50 ms | 100 ms DC 90 ms AC | 100 ms DC 90 ms AC | 50 ms |  | 20 ms at 20.4 V | 20 ms at 20.4 V | [64 empty] | 10 ms
| immunity to radioelectric fields | [128 empty] | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3 | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3 | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3 | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3 | [12 empty] | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3 | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3 | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3 | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3 | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3 | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3 | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3 | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3 | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3 | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
| immunity to voltage dips | [128 empty] | 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 95 % / 5 s conforming to EN/IEC 61000-4-11 | 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 95 % / 5 s conforming to EN/IEC 61000-4-11 | 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 95 % / 5 s conforming to EN/IEC 61000-4-11 | 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 95 % / 5 s conforming to EN/IEC 61000-4-11 | [12 empty] | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11 | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 30 % / 10 ms conforming to EN/IEC 61000-4-11 60 % / 100 ms conforming to EN/IEC 61000-4-11
| input voltage | [400 empty] | 24 V AC/DC (input voltage limit: 21.6...28.8 V) | 48 V AC/DC (input voltage limit: 43.2...57.6 V) | 110 V AC/DC (input voltage limit: 88...126.5 V) | 12 V AC/DC (input voltage limit: 11.4...14.4 V) | 230 V AC/DC (input voltage limit: 184...264.5 V) | 24 V AC/DC (input voltage limit: 21.6...28.8 V) | 48 V AC/DC (input voltage limit: 43.2...57.6 V) | 110 V AC/DC (input voltage limit: 88...126.5 V) | 12 V AC/DC (input voltage limit: 11.4...14.4 V) | 230 V AC/DC (input voltage limit: 184...264.5 V)
| noise level | [544 empty] | 70…90 dB at 1 m | [6 empty] | 70…90 dB at 1 m | 70…90 dB at 1 m | 70…90 dB at 1 m |  |  | 70…90 dB at 1 m | [54 empty] | 70…90 dB at 1 m | 70…90 dB at 1 m | [38 empty] | 0…80 dB at 1 m |  |  |  | 0…80 dB at 1 m | 0…80 dB at 1 m | 0…80 dB at 1 m |  | 0…80 dB at 1 m |  | 0…80 dB at 1 m | 0…80 dB at 1 m | 0…80 dB at 1 m |  | 0…80 dB at 1 m |  |  |  | 0…80 dB at 1 m | 0…80 dB at 1 m | 0…80 dB at 1 m | [5 empty] | 0…80 dB at 1 m | 0…80 dB at 1 m | 0…80 dB at 1 m |  | 0…80 dB at 1 m | [10 empty] | 0…105 dB (continuous or intermittent tone) at 1 m | 0…105 dB (continuous or intermittent tone) at 1 m | 0…105 dB (continuous or intermittent tone) at 1 m | 0…90 dB (continuous or intermittent tone) at 1 m | 0…90 dB (continuous or intermittent tone) at 1 m | 0…90 dB (continuous or intermittent tone) at 1 m | 0…90 dB (continuous or intermittent tone) at 1 m | 0…96 dB (continuous or intermittent tone) at 1 m | 0…96 dB (continuous or intermittent tone) at 1 m | 0…96 dB (continuous or intermittent tone) at 1 m | 0…96 dB (continuous or intermittent tone) at 1 m | 0…89 dB (stop or suppress) at 1 m | 0…89 dB (stop or suppress) at 1 m | 0…89 dB (stop or suppress) at 1 m | 0…97 dB (stop or suppress) at 1 m | 0…97 dB (stop or suppress) at 1 m | 0…97 dB (stop or suppress) at 1 m | 0…97 dB (stop or suppress) at 1 m | 0…97 dB (stop or suppress) at 1 m
| non-dissipating shock wave | [132 empty] | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | [49 empty] | 4 kV | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV | 4 kV | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | [20 empty] | 4 kV | 4 kV | 4 kV |  | 4 kV | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 |  |  | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 |  |  | 4 kV | 4 kV | 4 kV | 4 kV | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV | 4 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | [9 empty] | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV | 4.8 kV
| overvoltage category | [305 empty] | III conforming to IEC 60664-1 III conforming to UL 508 | [106 empty] | Class I conforming to IEC 60536 | Class I conforming to IEC 60536 | [236 empty] | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 |  |  |  |  | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | Class I conforming to IEC 60947-1 Class I conforming to IEC 60947-5-1 Class I conforming to IEC 61140 | [10 empty] | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140 | Class II conforming to EN/IEC 61140
| pollution degree | [97 empty] | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 |  |  | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 |  | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 |  |  |  | 3 conforming to IEC 60664-1 |  | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 |  |  |  |  | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | [48 empty] | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 3 conforming to UL 508 | 3 conforming to IEC 60664-1 3 conforming to UL 508 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 3 conforming to UL 508 | 3 conforming to IEC 60664-1 3 conforming to UL 508 | 3 conforming to IEC 60664-1 3 conforming to UL 508 | 3 conforming to IEC 60664-1 3 conforming to UL 508 | 3 conforming to IEC 60664-1 3 conforming to UL 508 | 3 conforming to IEC 60664-1 3 conforming to UL 508 | 3 conforming to IEC 60664-1 3 conforming to UL 508 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 3 conforming to UL 508 | 3 conforming to IEC 60664-1 3 conforming to UL 508 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 3 conforming to UL 508 | 2 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | [133 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [50 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| product certifications | [80 empty] | GL CSA CULus | CSA GL CULus | CULus CSA GL | CULus GL CSA | GL CULus CSA | CSA CULus GL | GL CULus CSA | CULus GL CSA | CULus CSA GL | CSA CULus GL | GL CULus CSA | CSA CULus | CSA GL CULus | CSA GL CULus | CSA GL CULus | GL CULus CSA | CULus GL CSA | CE CCC GL UL China RoHS CSA EAC RCM | China RoHS EAC CSA UL RCM CCC GL CE | CE UL GL CCC China RoHS EAC RCM CSA | UL CE CCC CSA China RoHS GL RCM EAC UL CE CCC CSA China RoHS GL RCM EAC | China RoHS GL EAC UL CCC CSA CE RCM | CE EAC CSA RCM China RoHS CCC GL UL | CCC CSA GL China RoHS RCM CE EAC UL | EAC CSA RCM UL China RoHS GL CE CCC | GL UL CSA RCM CCC China RoHS CE EAC | EAC UL GL China RoHS CSA RCM CCC CE | RCM GL EAC CE CSA CCC China RoHS UL | GL China RoHS CE CCC EAC UL CSA RCM | CULus RCM CSA China RoHS EAC GL CCC CE | CSA China RoHS EAC RCM CE CCC GL CULus | China RoHS RCM CCC CSA UL EAC CE GL | CE CCC GL China RoHS UL RCM EAC CSA | CULus CE EAC CSA RCM CCC China RoHS GL | CSA CCC RCM China RoHS CE GL UL EAC | CCC China RoHS CSA RCM GL CE UL EAC | RCM CSA CE EAC UL CCC GL China RoHS | China RoHS EAC UL RCM GL CCC CSA CE | CSA CULus China RoHS CE EAC GL CCC RCM | CULus CSA CE China RoHS CCC RCM GL EAC | CSA CE CULus GL RCM CCC China RoHS EAC | UL GL CE China RoHS CSA RCM EAC CCC | China RoHS CSA CCC GL CULus EAC CE RCM | RCM CE China RoHS EAC CSA CCC UL GL | CE CSA GL China RoHS EAC UL RCM CCC | EAC GL CSA China RoHS UL CCC RCM CE | CCC CSA RCM GL EAC CE UL China RoHS | CCC GL UL EAC RCM CSA China RoHS CE | GL UL C-Tick CULus CSA | GL CULus UL CSA C-Tick | GL UL CULus CSA C-Tick | GL UL CULus C-Tick CSA | UL CSA GL | CSA GL UL | GL UL CSA | GL CSA UL | GL CSA UL | CSA GL UL | GL CSA UL | GL UL CSA | CSA UL GL | CSA GL UL | CSA UL GL | CE CSA KC UL CCC EAC DNV-GL | UL CUL | CUL UL | CUL UL | UL CUL | UL CUL | UL CUL | UL CUL | CUL UL | UL CUL | CUL UL | USSR EDF BV ASE CSA | USSR BV ASE EDF CSA | ASE EDF USSR BV CSA | ASE EDF BV CSA USSR | ASE CSA USSR EDF BV | EDF USSR ASE CSA BV | USSR EDF ASE CSA BV | USSR CSA BV ASE EDF | ASE CSA EDF USSR BV | EDF BV CSA ASE USSR | EDF CSA ASE BV USSR | BV USSR EDF CSA ASE | ASE CSA BV USSR EDF | USSR EDF CSA BV ASE | ASE USSR BV EDF CSA | EDF CSA ASE USSR BV | USSR ASE BV EDF CSA | CSA USSR ASE EDF BV | ASE USSR BV EDF CSA | ASE USSR BV CSA EDF | USSR CSA ASE EDF BV | USSR CSA EDF ASE BV | EDF ASE BV CSA USSR | ASE EDF USSR BV CSA | ASE EDF USSR BV CSA | EDF BV CSA USSR ASE | BV ASE CSA USSR EDF | ASE USSR EDF BV CSA | EDF USSR CSA ASE BV | ASE EDF USSR BV CSA | CSA EDF ASE BV USSR | EDF CSA BV USSR ASE | BV ASE EDF CSA USSR | ASE BV USSR CSA EDF | USSR ASE EDF CSA BV | USSR EDF ASE BV CSA | USSR EDF CSA ASE BV | EDF USSR ASE CSA BV | GL C-Tick GOST UL CSA | GOST CSA GL C-Tick UL | GOST C-Tick CSA UL GL | C-Tick GL CSA UL GOST | GOST C-Tick UL CSA GL | UL GL C-Tick GOST CSA | GL GOST UL C-Tick CSA | CSA C-Tick GL UL GOST | GL UL GOST CSA C-Tick | UL | CSA GL UL GOST C-Tick | GOST UL GL C-Tick CSA | UL GL GOST C-Tick CSA | C-Tick GOST GL CSA UL | EAC CSA China RoHS CE RCM CCC UL GL | CSA CE EAC CCC GL RCM China RoHS UL | China RoHS UL RCM CSA GL CCC CE EAC | GL UL CCC EAC RCM CE CSA China RoHS | GL RCM CCC CSA UL China RoHS EAC CE | CSA GL RCM UL China RoHS EAC CE CCC | GL EAC China RoHS UL CSA RCM CCC CE | GL EAC CCC CE CSA China RoHS UL RCM | CE EAC China RoHS RCM GL CSA UL CCC | CSA CCC EAC China RoHS RCM CE GL UL | GL China RoHS CSA RCM CE EAC CCC UL | RCM CE China RoHS CSA GL CCC UL EAC | CSA RCM UL GL China RoHS CE CCC EAC | UL China RoHS EAC CSA GL CCC RCM CE | CE China RoHS CCC EAC CSA RCM UL GL | CE China RoHS CCC GL RCM UL EAC CSA | CE CSA RCM GL China RoHS CCC EAC UL | GL UL CCC EAC CE China RoHS RCM CSA | RCM UL China RoHS EAC CSA CE GL CCC | CCC China RoHS CE CSA EAC UL GL RCM | GOST GL C-Tick UL CSA | GL GOST C-Tick CSA UL | GL UL C-Tick CSA GOST | C-Tick CSA GOST UL GL | GL UL CSA C-Tick GOST | GL CSA GOST UL C-Tick | CE GL CCC EAC RCM China RoHS UL CSA | CCC EAC CSA China RoHS RCM UL GL CE | GL UL GOST C-Tick CSA | CSA GL UL C-Tick GOST | GOST CSA UL GL C-Tick | C-Tick GOST UL GL CSA | GL UL CSA GOST C-Tick | CSA C-Tick GOST UL GL | GL UL GOST C-Tick CSA | GOST CSA GL UL C-Tick | GOST C-Tick UL GL CSA | GOST UL GL C-Tick CSA | C-Tick GOST CSA GL UL | UL C-Tick GL CSA GOST | GL CSA UL | CSA UL GL | CSA UL GL | CSA GL UL | UL CSA GL | CSA GL UL | UL GL CSA | GL CSA UL | UL GL CSA | GL UL CSA | CSA GL UL | CSA UL GL | UL GL CSA | CSA UL GL | UL GL CSA | CSA UL GL | UL GL CSA | UL CSA GL | GL CSA UL | GL CSA UL | CSA UL GL | UL CSA GL | GL CSA UL | UL CSA GL | GL UL CSA | UL GL CSA | CSA GL UL | CSA UL GL | UL GL CSA | UL CSA GL | GL UL CSA | CSA GL UL | GL UL CSA | GL CSA UL | CSA UL GL | GL UL CSA | CSA GL UL | CSA GL UL | UL GL CSA | CSA UL GL | UL GL CSA | CSA UL GL | GL UL CSA | GL UL CSA | CSA GL UL | UL CSA GL | GL CSA UL | GL CSA UL | CSA UL GL | UL CSA GL | UL GL CSA | GL CSA UL | GL CSA UL | GL CSA UL | UL GL CSA | CSA UL GL | UL GL CSA | GL CSA UL | UL GL CSA | CE UL CSA CCC EAC RCM | UL GL CSA | CSA UL GL | GL CSA UL | CSA UL GL | GL UL CSA | UL GL CSA | CSA UL GL | UL CSA GL | GL UL CSA | CSA GL UL | CSA GL UL | UL GL CSA | CSA UL GL | GL UL CSA | EAC UL CSA | UL CSA GOST | UL CSA EAC | UL CSA GOST | UL CSA EAC | UL CSA GOST | UL EAC CSA | UL GOST CSA | UL CSA EAC | CSA GOST UL | EAC UL CSA | UL CSA GOST | EAC UL CSA | UL GOST CSA | CSA EAC UL | GOST CSA UL | CSA UL EAC | CSA UL GOST | EAC UL CSA | CSA GOST UL | UL CSA EAC | GOST UL CSA | CSA UL EAC | UL GOST CSA | UL EAC CSA | UL GOST CSA | EAC CSA UL | CSA GOST UL | UL EAC CSA | GOST CSA UL | EAC UL CSA | CSA UL GOST | EAC CSA UL | UL CSA GOST | CSA EAC UL | GOST UL CSA | EAC UL CSA | GOST UL CSA | EAC UL CSA | CSA UL GOST | UL CSA EAC | CSA UL GOST | UL CSA EAC | CSA UL GOST | CSA EAC UL | GOST UL CSA | UL CSA EAC | GOST CSA UL | UL CSA EAC | UL GOST CSA | UL CSA EAC | GOST UL CSA | UL CSA EAC | UL GOST CSA | EAC CSA UL | CSA GOST UL | EAC CSA UL | GOST UL CSA | UL CSA EAC | GOST CSA UL | CSA EAC UL | GOST UL CSA | CSA UL EAC | GOST UL CSA | UL CSA EAC | UL GOST CSA | CSA EAC UL | GOST CSA UL | EAC CSA UL | CSA GOST UL | EAC UL CSA | UL CSA GOST | CSA UL EAC | UL EAC CSA | EAC CSA UL | CSA UL EAC | EAC CSA UL | CSA UL EAC | UL CSA EAC | EAC CSA UL | UL CSA GOST | GOST CSA UL | CSA GOST UL | CSA UL GOST | GOST CSA UL | UL GOST CSA | GOST CSA UL | CSA UL GOST | UL GOST CSA | GOST CSA UL | CCC UL 508 CSA C22-2 No 14 GOST | CCC UL 508 GOST CSA C22-2 No 14 | AS-Interface No 25701 CSA | CSA AS-Interface No 25701 | UL 508 CSA C22-2 No 14 CCC GOST | UL 508 CCC GOST CSA C22-2 No 14 | CSA C22-2 No 14 CCC GOST UL 508 | CCC UL 508 CSA C22-2 No 14 GOST | CSA C22-2 No 14 UL 508 GOST CCC | CCC GOST CSA C22-2 No 14 UL 508 | CCC UL 508 CSA C22-2 No 14 GOST | CCC GOST CSA C22-2 No 14 UL 508 | CSA C22-2 No 14 CCC UL 508 GOST | CSA C22-2 No 14 CCC UL 508 GOST | CCC GOST CSA C22-2 No 14 UL 508 | CSA C22-2 No 14 UL 508 GOST CCC | GOST CSA C22-2 No 14 UL 508 CCC | UL 508 CCC CSA C22-2 No 14 GOST | CCC CSA C22-2 No 14 UL 508 GOST | UL 508 GOST CCC CSA C22-2 No 14 | CSA C22-2 No 14 GOST UL 508 CCC | UL 508 CSA C22-2 No 14 GOST CCC | UL 508 CCC CSA C22-2 No 14 GOST | CSA C22-2 No 14 CCC GOST UL 508 | UL 508 GOST CCC CSA C22-2 No 14 | UL 508 GOST CCC CSA C22-2 No 14 | CCC CSA C22-2 No 14 UL 508 GOST | CSA C22-2 No 14 GOST UL 508 CCC | CCC CSA C22-2 No 14 UL 508 GOST | CCC CSA C22-2 No 14 GOST UL 508 | CCC GOST CSA C22-2 No 14 UL 508 | GOST CSA C22-2 No 14 CCC UL 508 | UL 508 CCC GOST CSA C22-2 No 14 | GOST CSA C22-2 No 14 CCC UL 508 | GOST CSA C22-2 No 14 UL 508 CCC | CSA C22-2 No 14 CCC UL 508 GOST | UL 508 CCC CSA C22-2 No 14 GOST | CSA C22-2 No 14 UL 508 CCC GOST | CCC CSA C22-2 No 14 GOST UL 508 | CCC GOST CSA C22-2 No 14 UL 508 | UL 508 CCC CSA C22-2 No 14 GOST | CSA C22-2 No 14 GOST UL 508 CCC | UL 508 GOST CCC CSA C22-2 No 14 | GOST UL 508 CCC CSA C22-2 No 14 | CSA C22-2 No 14 UL 508 GOST CCC | GOST UL 508 CSA C22-2 No 14 CCC | CSA C22-2 No 14 CCC GOST UL 508 | CSA C22-2 No 14 GOST CCC UL 508 | GOST UL 508 CSA C22-2 No 14 CCC | UL 508 CCC CSA C22-2 No 14 GOST | CSA C22-2 No 14 UL 508 GOST CCC | UL 508 CCC CSA C22-2 No 14 GOST | GOST CSA C22-2 No 14 UL 508 CCC | CSA C22-2 No 14 GOST UL 508 CCC | CCC UL 508 GOST CSA C22-2 No 14 | CCC GOST CSA C22-2 No 14 UL 508 | UL 508 CCC GOST CSA C22-2 No 14 | CCC UL 508 GOST CSA C22-2 No 14 | GOST CCC UL 508 CSA C22-2 No 14 | CSA C22-2 No 14 CCC GOST UL 508 | CCC GOST UL 508 CSA C22-2 No 14 | CCC UL 508 CSA C22-2 No 14 GOST | UL 508 GOST CCC CSA C22-2 No 14 | GOST CSA C22-2 No 14 CCC UL 508 | CCC GOST CSA C22-2 No 14 UL 508 | CCC UL 508 GOST CSA C22-2 No 14 | CCC UL 508 GOST CSA C22-2 No 14 | CCC CSA C22-2 No 14 UL 508 GOST | CCC CSA C22-2 No 14 UL 508 GOST | CCC GOST UL 508 CSA C22-2 No 14 | CCC UL 508 GOST CSA C22-2 No 14 | CSA C22-2 No 14 GOST CCC UL 508 | CSA C22-2 No 14 CCC GOST UL 508 | CCC UL 508 GOST CSA C22-2 No 14 | CSA C22-2 No 14 GOST UL 508 CCC | GOST CSA C22-2 No 14 UL 508 CCC | CCC GOST CSA C22-2 No 14 UL 508 | CCC GOST UL 508 CSA C22-2 No 14 | UL 508 GOST CSA C22-2 No 14 CCC | GOST CCC UL 508 CSA C22-2 No 14 | CCC CSA C22-2 No 14 UL 508 GOST | CCC GOST UL 508 CSA C22-2 No 14 | CSA C22-2 No 14 GOST CCC UL 508 | CCC CSA C22-2 No 14 UL 508 GOST | UL 508 CCC GOST CSA C22-2 No 14 | UL 508 CCC GOST CSA C22-2 No 14 | UL 508 CSA C22-2 No 14 GOST CCC | CSA C22-2 No 14 GOST CCC UL 508 | CCC GOST CSA C22-2 No 14 UL 508 | CCC GOST CSA C22-2 No 14 UL 508 | CCC UL 508 GOST CSA C22-2 No 14 | CCC UL 508 CSA C22-2 No 14 GOST | UL 508 GOST CCC CSA C22-2 No 14 | CSA C22-2 No 14 UL 508 CCC GOST | CSA C22-2 No 14 CCC GOST UL 508 | CCC GOST CSA C22-2 No 14 UL 508 | UL 508 GOST CSA C22-2 No 14 CCC | UL 508 CSA C22-2 No 14 GOST CCC | CCC UL 508 GOST CSA C22-2 No 14 | UL 508 CSA C22-2 No 14 CCC GOST | UL 508 GOST CSA C22-2 No 14 CCC | GOST CSA C22-2 No 14 CCC UL 508 | UL 508 GOST CSA C22-2 No 14 CCC | UL 508 GOST CCC CSA C22-2 No 14 | GOST UL 508 CCC CSA C22-2 No 14 | CCC CSA C22-2 No 14 GOST UL 508 | CSA C22-2 No 14 UL 508 CCC GOST | UL 508 CCC GOST CSA C22-2 No 14 | CSA C22-2 No 14 UL 508 CCC GOST | CCC CSA C22-2 No 14 GOST UL 508 | CSA C22-2 No 14 GOST UL 508 CCC | UL 508 CCC CSA C22-2 No 14 GOST | UL 508 GOST CCC CSA C22-2 No 14 | GOST UL 508 CSA C22-2 No 14 CCC | UL 508 GOST CSA C22-2 No 14 CCC | UL 508 CSA C22-2 No 14 GOST CCC | UL 508 CCC CSA C22-2 No 14 GOST | UL 508 CCC CSA C22-2 No 14 GOST | CSA C22-2 No 14 UL 508 CCC GOST | GOST CCC UL 508 CSA C22-2 No 14 | GOST CSA C22-2 No 14 UL 508 CCC | GOST CSA C22-2 No 14 CCC UL 508 | CCC UL 508 GOST CSA C22-2 No 14 | CSA C22-2 No 14 GOST UL 508 CCC | CSA C22-2 No 14 CCC UL 508 GOST | CCC UL 508 GOST CSA C22-2 No 14 | GOST CSA C22-2 No 14 CCC UL 508 | GOST UL 508 CCC CSA C22-2 No 14 | GOST UL 508 CCC CSA C22-2 No 14 | CSA C22-2 No 14 UL 508 GOST CCC | GOST UL 508 CSA C22-2 No 14 CCC | CSA C22-2 No 14 CCC GOST UL 508 | CCC GOST CSA C22-2 No 14 UL 508 | UL CSA GOST | UL CSA GOST | GOST UL CSA | UL GOST CSA | GOST CSA UL | CSA GOST UL | GOST CSA UL | UL GOST CSA | GOST UL CSA | GOST CSA UL | UL CSA GOST | UL CSA GOST | CSA GOST UL | UL GOST CSA | CSA GOST UL | UL CSA GOST | UL CSA GOST | GOST UL CSA | GOST UL CSA | GOST CSA UL | UL GOST CSA | CSA GOST UL | CSA UL GOST | GOST CSA UL | UL GOST CSA | UL GOST CSA | CSA UL GOST | CSA UL GOST | UL CSA GOST | UL GOST CSA | GOST CSA UL | GOST CSA UL | UL CSA GOST | CSA UL GOST | UL CSA GOST | GOST UL CSA | GOST UL CSA | UL CSA GOST | UL GOST CSA | CSA UL GOST | CSA GOST UL | GOST CSA UL | CSA UL CSA UL | UL CSA UL CSA | CSA UL CSA UL | UL CSA UL CSA | CSA UL CSA UL | CSA UL CSA UL | CSA UL CSA UL | UL CSA UL CSA | CSA UL CSA UL | CSA UL CSA UL | UL CSA UL CSA | CSA UL CSA UL | CSA UL CSA UL | CSA UL CSA UL | CSA UL CSA UL | CSA UL CSA UL | CSA UL CSA UL | UL CSA UL CSA | CSA UL CSA UL | UL CSA UL CSA | CSA UL CSA UL | CSA UL CSA UL | UL CSA UL CSA | CSA UL CSA UL | CSA UL GOST | GOST UL CSA | UL CSA GOST | GOST UL CSA | CSA GOST UL | CSA UL GOST | CSA CCC UL | UL CCC CSA | CCC CSA UL | CCC CSA UL | CCC UL CSA | UL CCC CSA | CCC CSA UL | CCC UL CSA | CCC UL CSA | UL CSA CCC | UL CCC CSA | UL CCC CSA | UL CSA CCC | UL CSA CCC | CCC UL CSA | CSA UL CCC | UL CSA CCC | CCC CSA UL | CCC CSA UL | UL CCC CSA | CSA CCC UL | UL CCC CSA | UL CSA CCC | CCC CSA UL | CSA UL CCC | CSA CCC UL | CCC CSA UL | CSA CCC UL | CCC CSA UL | CCC CSA UL | CSA UL CCC | CCC UL CSA | CCC UL CSA | UL CCC CSA | CSA UL CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC | CCC |  |  |  | UL | UL | UL | UR | UR | UR | UR
| protection against electric shocks | [128 empty] | 4 kV class III conforming to IEC 60664-1 4 kV class III conforming to IEC 61812-1 | 4 kV class III conforming to IEC 60664-1 4 kV class III conforming to IEC 61812-1 | 4 kV class III conforming to IEC 60664-1 4 kV class III conforming to IEC 61812-1 | 4 kV class III conforming to IEC 60664-1 4 kV class III conforming to IEC 61812-1 | [114 empty] | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | [12 empty] | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV: level 3 conforming to IEC 61000-4-5 | 2 kV conforming to IEC 61000-4-5 level 3 | 2 kV conforming to IEC 61000-4-5 level 3
| protective treatment | [154 empty] | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | [218 empty] | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | [7 empty] | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC | TC
| relative humidity | [80 empty] | 93 % without condensation conforming to IEC 60068-2-30 | 93 % without condensation conforming to IEC 60068-2-30 | 93 % without condensation conforming to IEC 60068-2-30 | 93 % without condensation conforming to IEC 60068-2-30 | 93 % without condensation conforming to IEC 60068-2-30 | 93 % without condensation conforming to IEC 60068-2-30 | 93 % without condensation conforming to IEC 60068-2-30 | 93 % without condensation conforming to IEC 60068-2-30 | 93 % without condensation conforming to IEC 60068-2-30 | 93 % without condensation conforming to IEC 60068-2-30 | 93 % without condensation conforming to IEC 60068-2-30 | 93 % without condensation conforming to IEC 60068-2-30 | 93 % without condensation conforming to IEC 60068-2-30 | 93 % without condensation conforming to IEC 60068-2-30 | 93 % without condensation conforming to IEC 60068-2-30 | 93 % without condensation conforming to IEC 60068-2-30 | 93 % without condensation conforming to IEC 60068-2-30 | 95 % at 25…55 °C | 95 % at 25…55 °C | 95 % at 25…55 °C | 95 % at 25…55 °C 95 % at 25…55 °C | 95 % at 25…55 °C | 95 % at 25…55 °C | 95 % at 25…55 °C | 95 % at 25…55 °C | 95 % at 25…55 °C | 95 % at 25…55 °C | 95 % at 25…55 °C | 95 % at 25…55 °C | 93 %, without condensation conforming to IEC 60068-2-30 | 93 %, without condensation conforming to IEC 60068-2-30 | 95 % at 25…55 °C | 95 % at 25…55 °C | 93 %, without condensation conforming to IEC 60068-2-30 | 95 % at 25…55 °C | 95 % at 25…55 °C | 95 % at 25…55 °C | 95 % at 25…55 °C | 93 %, without condensation conforming to IEC 60068-2-30 | 93 %, without condensation conforming to IEC 60068-2-30 | 93 %, without condensation conforming to IEC 60068-2-30 | 95 % at 25…55 °C | 93 %, without condensation conforming to IEC 60068-2-30 | 95 % at 25…55 °C | 95 % at 25…55 °C | 95 % at 25…55 °C | 95 % at 25…55 °C | 95 % at 25…55 °C | 93 % without condensation conforming to IEC 60068-2-3 | 93 % without condensation conforming to IEC 60068-2-3 | 93 % without condensation conforming to IEC 60068-2-3 | 93 % without condensation conforming to IEC 60068-2-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 95 % at 25…55 °C | 95 % without condensation conforming to IEC 60068-2-6 | 95 % without condensation conforming to IEC 60068-2-6 | 95 % without condensation conforming to IEC 60068-2-6 | 95 % without condensation conforming to IEC 60068-2-6 | 95 % without condensation conforming to IEC 60068-2-6 | 95 % without condensation conforming to IEC 60068-2-6 | 95 % without condensation conforming to IEC 60068-2-6 | 95 % without condensation conforming to IEC 60068-2-6 | 95 % without condensation conforming to IEC 60068-2-6 | 95 % without condensation conforming to IEC 60068-2-6 | [38 empty] | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 |  |  |  | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 15…85 % conforming to IEC 60721-3-3 | 15…85 % conforming to IEC 60721-3-3 | 15…85 % conforming to IEC 60721-3-3 | 15…85 % conforming to IEC 60721-3-3 | 15…85 % conforming to IEC 60721-3-3 | 15…85 % conforming to IEC 60721-3-3 | 15…85 % conforming to IEC 60721-3-3 | 15…85 % conforming to IEC 60721-3-3 | 15…85 % conforming to IEC 60721-3-3 | 15…85 % conforming to IEC 60721-3-3 | 15…85 % conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 | 15…85 % 3K3 conforming to IEC 60721-3-3 |  |  |  |  | 93…97 % at 25…55 °C conforming to IEC 60068-2-30 | [376 empty] | 35…85 % without condensation | 35…85 % without condensation | 35…85 % without condensation | 35…85 % without condensation | 35…85 % without condensation | 35…85 % without condensation | 35…85 % without condensation | [14 empty] | 35…85 % without condensation | 35…85 % without condensation | 35…85 % without condensation | 35…85 % without condensation | 35…85 % without condensation | 35…85 % without condensation | 35…85 % without condensation | 35…85 % without condensation
| resistance to electromagnetic fields | [128 empty] | 10 V/m 26 MHz to 1 GHz conforming to EN/IEC 61000-4-3 level 3 | 10 V/m 26 MHz to 1 GHz conforming to IEC 61000-4-3 level 3 | 10 V/m 26 MHz to 1 GHz conforming to IEC 61000-4-3 level 3 | 10 V/m 26 MHz to 1 GHz conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 |  | 10 V/m conforming to EN/IEC 61000-4-3 level 3 | 10 V/m conforming to EN/IEC 61000-4-3 level 3 | 10 V/m conforming to EN/IEC 61000-4-3 level 3 | 10 V/m conforming to EN/IEC 61000-4-3 level 3 | 10 V/m conforming to EN/IEC 61000-4-3 level 3 | 10 V/m conforming to EN/IEC 61000-4-3 level 3 | 10 V/m conforming to EN/IEC 61000-4-3 level 3 | 10 V/m conforming to EN/IEC 61000-4-3 level 3 | 10 V/m conforming to EN/IEC 61000-4-3 level 3 | 10 V/m conforming to EN/IEC 61000-4-3 level 3 | [92 empty] | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3 | 10 V/m conforming to IEC 61000-4-3 level 3
| resistance to electrostatic discharge | [128 empty] | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3 | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3 | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3 | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3 | 6 kV in contact conforming to IEC 61000-4-2 level 3 8 kV in air conforming to IEC 61000-4-2 level 3 | 6 kV in contact conforming to IEC 61000-4-2 level 3 8 kV in air conforming to IEC 61000-4-2 level 3 | 6 kV in contact conforming to IEC 61000-4-2 level 3 8 kV in air conforming to IEC 61000-4-2 level 3 | 6 kV in contact conforming to IEC 61000-4-2 level 3 8 kV in air conforming to IEC 61000-4-2 level 3 | 6 kV in contact conforming to IEC 61000-4-2 level 3 8 kV in air conforming to IEC 61000-4-2 level 3 | 6 kV in contact conforming to IEC 61000-4-2 level 3 8 kV in air conforming to IEC 61000-4-2 level 3 | 6 kV in contact conforming to IEC 61000-4-2 level 3 8 kV in air conforming to IEC 61000-4-2 level 3 | 6 kV in contact conforming to IEC 61000-4-2 level 3 8 kV in air conforming to IEC 61000-4-2 level 3 |  |  |  |  | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3 | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3 | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3 | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3 | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3 | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3 | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3 | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3 | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3 | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 8 kV in air conforming to EN/IEC 61000-4-2 level 3 | [92 empty] | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV contact conforming to IEC 61000-4-2 level 3 8 kV air conforming to IEC 61000-4-2 level 3 | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3 | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3 | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3 | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3 | [10 empty] | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3 | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3 | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3 | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3 | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
| resistance to fast transients | [128 empty] | 2 kV (capacitive connecting clip) conforming to EN/IEC 61000-4-4 level 4 4 kV (direct) conforming to EN/IEC 61000-4-4 level 4 | 2 kV (capacitive connecting clip) conforming to EN/IEC 61000-4-4 level 4 4 kV (direct) conforming to EN/IEC 61000-4-4 level 4 | 2 kV (capacitive connecting clip) conforming to EN/IEC 61000-4-4 level 4 4 kV (direct) conforming to EN/IEC 61000-4-4 level 4 | 2 kV (capacitive connecting clip) conforming to EN/IEC 61000-4-4 level 4 4 kV (direct) conforming to EN/IEC 61000-4-4 level 4 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 |  | 2 kV conforming to EN/IEC 61000-4-4 level 3 | 2 kV conforming to EN/IEC 61000-4-4 level 3 | 2 kV conforming to EN/IEC 61000-4-4 level 3 | 2 kV conforming to EN/IEC 61000-4-4 level 3 | 2 kV conforming to EN/IEC 61000-4-4 level 3 | 2 kV conforming to EN/IEC 61000-4-4 level 3 | 2 kV conforming to EN/IEC 61000-4-4 level 3 | 2 kV conforming to EN/IEC 61000-4-4 level 3 | 2 kV conforming to EN/IEC 61000-4-4 level 3 | 2 kV conforming to EN/IEC 61000-4-4 level 3 | [92 empty] | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 2 kV conforming to IEC 61000-4-4 level 3 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 |  | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
| shock resistance | [80 empty] | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 |  |  |  |  | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 |  |  |  | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | [10 empty] | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 5 gn conforming to IEC 60068-2-27 | 5 gn conforming to IEC 60068-2-27 | 5 gn conforming to IEC 60068-2-27 | 5 gn conforming to IEC 60068-2-27 | 5 gn conforming to IEC 60068-2-27 | 5 gn conforming to IEC 60068-2-27 | 5 gn conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 5 gn conforming to IEC 60068-2-27 | 5 gn conforming to IEC 60068-2-27 | 5 gn conforming to IEC 60068-2-27 | 5 gn conforming to IEC 60068-2-27 | 5 gn conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn conforming to IEC 60068-2-27 for 11 ms | 15 gn conforming to IEC 60068-2-27 for 11 ms | 50 gn for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 |  |  | 25 gn conforming to IEC 60068-2-27 | 25 gn conforming to IEC 60068-2-27
| signalling type | [692 empty] | 43 tones siren | 43 tones siren | 43 tones siren | 16 tones alarm | 16 tones alarm | 16 tones alarm | 16 tones alarm | 16 tones alarm | 16 tones alarm | 16 tones alarm | 16 tones alarm | Adjustable vocal sound | Adjustable vocal sound | Adjustable vocal sound | Adjustable vocal sound | Adjustable vocal sound | Adjustable vocal sound | Adjustable vocal sound | Adjustable vocal sound
| standards | [80 empty] | 2004/108/EC EN 61000-6-1 2006/95/EC EN 61000-6-3 EN 61000-6-2 IEC 61812-1 EN 61000-6-4 | 2004/108/EC EN 61000-6-3 2006/95/EC EN 61000-6-2 IEC 61812-1 EN 61000-6-4 EN 61000-6-1 | 2006/95/EC EN 61000-6-1 EN 61000-6-3 EN 61000-6-2 IEC 61812-1 EN 61000-6-4 2004/108/EC | EN 61000-6-2 EN 61000-6-4 IEC 61812-1 EN 61000-6-1 EN 61000-6-3 2006/95/EC 2004/108/EC | 2004/108/EC EN 61000-6-2 IEC 61812-1 EN 61000-6-4 EN 61000-6-1 2006/95/EC EN 61000-6-3 | 2006/95/EC 2004/108/EC IEC 61812-1 EN 61000-6-3 EN 61000-6-1 EN 61000-6-4 EN 61000-6-2 | 2006/95/EC EN 61000-6-2 EN 61000-6-3 EN 61000-6-4 IEC 61812-1 EN 61000-6-1 2004/108/EC | EN 61000-6-4 EN 61000-6-2 EN 61000-6-3 2004/108/EC 2006/95/EC IEC 61812-1 EN 61000-6-1 | EN 61000-6-4 EN 61000-6-1 2006/95/EC EN 61000-6-3 IEC 61812-1 2004/108/EC EN 61000-6-2 | 2006/95/EC 2004/108/EC EN 61000-6-4 IEC 61812-1 EN 61000-6-3 EN 61000-6-2 EN 61000-6-1 | 2006/95/EC EN 61000-6-2 EN 61000-6-4 2004/108/EC IEC 61812-1 EN 61000-6-3 EN 61000-6-1 | 2004/108/EC EN 61000-6-2 EN 61000-6-3 EN 61000-6-1 2006/95/EC IEC 61812-1 EN 61000-6-4 | 2006/95/EC 2004/108/EC EN 61000-6-4 EN 61000-6-1 EN 61000-6-3 IEC 61812-1 EN 61000-6-2 | 2006/95/EC 2004/108/EC IEC 61812-1 EN 61000-6-2 EN 61000-6-3 EN 61000-6-4 EN 61000-6-1 | 2006/95/EC EN 61000-6-3 IEC 61812-1 EN 61000-6-2 EN 61000-6-1 2004/108/EC EN 61000-6-4 | 2006/95/EC EN 61000-6-4 2004/108/EC EN 61000-6-3 IEC 61812-1 EN 61000-6-2 EN 61000-6-1 | 2006/95/EC 2004/108/EC EN 61000-6-1 EN 61000-6-4 EN 61000-6-2 EN 61000-6-3 IEC 61812-1 | IEC 61812-1 UL 508 | UL 508 IEC 61812-1 | UL 508 IEC 61812-1 | UL 508 IEC 61812-1 UL 508 IEC 61812-1 | UL 508 IEC 61812-1 | UL 508 IEC 61812-1 | IEC 61812-1 UL 508 | UL 508 IEC 61812-1 | IEC 61812-1 UL 508 | IEC 61812-1 UL 508 | IEC 61812-1 UL 508 | UL 508 IEC 61812-1 | EN 61000-6-4 IEC 61812-1 EN 61000-6-1 EN 61000-6-3 EN 61000-6-2 | EN 61000-6-4 EN 61000-6-2 EN 61000-6-3 EN 61000-6-1 IEC 61812-1 | UL 508 IEC 61812-1 | UL 508 IEC 61812-1 | EN 61000-6-3 EN 61000-6-4 EN 61000-6-2 IEC 61812-1 EN 61000-6-1 | UL 508 IEC 61812-1 | IEC 61812-1 UL 508 | IEC 61812-1 UL 508 | IEC 61812-1 UL 508 | EN 61000-6-1 IEC 61812-1 EN 61000-6-4 EN 61000-6-3 EN 61000-6-2 | IEC 61812-1 EN 61000-6-1 EN 61000-6-2 EN 61000-6-3 EN 61000-6-4 | IEC 61812-1 EN 61000-6-2 EN 61000-6-1 EN 61000-6-4 EN 61000-6-3 | UL 508 IEC 61812-1 | IEC 61812-1 EN 61000-6-1 EN 61000-6-3 EN 61000-6-4 EN 61000-6-2 | UL 508 IEC 61812-1 | IEC 61812-1 UL 508 | IEC 61812-1 UL 508 | UL 508 IEC 61812-1 | IEC 61812-1 UL 508 | EN 50081-1/2 EN 50082-1/2 IEC 61812-1 93/68/EEC 89/336/EEC IEC 60669-2-3 73/23/EEC | EN 50082-1/2 EN 50081-1/2 93/68/EEC 73/23/EEC 89/336/EEC IEC 60669-2-3 IEC 61812-1 | IEC 61812-1 EN 50081-1/2 93/68/EEC 89/336/EEC EN 50082-1/2 IEC 60669-2-3 73/23/EEC | 73/23/EEC 93/68/EEC EN 50082-1/2 89/336/EEC EN 50081-1/2 IEC 61812-1 IEC 60669-2-3 | EN/IEC 61812-1 | EN/IEC 61812-1 | EN/IEC 61812-1 | EN/IEC 61812-1 | EN/IEC 61812-1 | EN/IEC 61812-1 | EN/IEC 61812-1 | EN/IEC 61812-1 | EN/IEC 61812-1 | EN/IEC 61812-1 | EN/IEC 61812-1 | EN 61000-6-1 EN 61000-6-2 EN 61000-6-4 EN 61812-1 EN 61000-6-3 | EN 50081-2 EN 61000-6-2 EN/IEC 60601-2 EN/IEC 61812-1 93/68/EEC 73/23/EEC 89/336/EEC EN/IEC 60601-1 | 73/23/EEC EN 50081-2 93/68/EEC EN/IEC 61812-1 EN 61000-6-2 EN/IEC 60601-1 EN/IEC 60601-2 89/336/EEC | EN 61000-6-2 93/68/EEC EN 50081-2 EN/IEC 61812-1 73/23/EEC EN/IEC 60601-2 89/336/EEC EN/IEC 60601-1 | 93/68/EEC EN/IEC 61812-1 EN/IEC 60601-1 89/336/EEC EN/IEC 60601-2 73/23/EEC EN 61000-6-2 EN 50081-2 | EN/IEC 60601-1 89/336/EEC EN 61000-6-2 EN 50081-2 EN/IEC 61812-1 73/23/EEC EN/IEC 60601-2 93/68/EEC | EN/IEC 60601-1 89/336/EEC EN/IEC 61812-1 EN/IEC 60601-2 73/23/EEC 93/68/EEC EN 61000-6-2 EN 50081-2 | EN/IEC 60601-2 EN 61000-6-2 73/23/EEC EN/IEC 61812-1 93/68/EEC EN/IEC 60601-1 89/336/EEC EN 50081-2 | EN 61000-6-2 EN/IEC 60601-1 89/336/EEC 93/68/EEC EN/IEC 61812-1 EN/IEC 60601-2 73/23/EEC EN 50081-2 | 93/68/EEC EN 50081-2 73/23/EEC EN 61000-6-2 EN/IEC 60601-2 EN/IEC 60601-1 89/336/EEC EN/IEC 61812-1 | EN 61000-6-2 EN 50081-2 EN/IEC 60601-1 EN/IEC 60601-2 73/23/EEC 93/68/EEC 89/336/EEC EN/IEC 61812-1 | NF C 45-250 IEC 60255 VDE 0435 | IEC 60255 NF C 45-250 VDE 0435 | NF C 45-250 IEC 60255 VDE 0435 | NF C 45-250 VDE 0435 IEC 60255 | NF C 45-250 IEC 60255 VDE 0435 | IEC 60255 VDE 0435 NF C 45-250 | NF C 45-250 VDE 0435 IEC 60255 | IEC 60255 VDE 0435 NF C 45-250 | VDE 0435 IEC 60255 NF C 45-250 | NF C 45-250 VDE 0435 IEC 60255 | VDE 0435 IEC 60255 NF C 45-250 | VDE 0435 NF C 45-250 IEC 60255 | IEC 60255 VDE 0435 NF C 45-250 | VDE 0435 IEC 60255 NF C 45-250 | IEC 60255 NF C 45-250 VDE 0435 | IEC 60255 VDE 0435 NF C 45-250 | VDE 0435 NF C 45-250 IEC 60255 | IEC 60255 VDE 0435 NF C 45-250 | NF C 45-250 IEC 60255 VDE 0435 | NF C 45-250 VDE 0435 IEC 60255 | NF C 45-250 VDE 0435 IEC 60255 | VDE 0435 NF C 45-250 IEC 60255 | VDE 0435 IEC 60255 NF C 45-250 | VDE 0435 NF C 45-250 IEC 60255 | VDE 0435 IEC 60255 NF C 45-250 | IEC 60255 NF C 45-250 VDE 0435 | NF C 45-250 VDE 0435 IEC 60255 | IEC 60255 NF C 45-250 VDE 0435 | NF C 45-250 VDE 0435 IEC 60255 | IEC 60255 NF C 45-250 VDE 0435 | VDE 0435 IEC 60255 NF C 45-250 | NF C 45-250 VDE 0435 IEC 60255 | IEC 60255 VDE 0435 NF C 45-250 | IEC 60255 VDE 0435 NF C 45-250 | VDE 0435 IEC 60255 NF C 45-250 | IEC 60255 NF C 45-250 VDE 0435 | NF C 45-250 IEC 60255 VDE 0435 | IEC 60255 VDE 0435 NF C 45-250 | EN/IEC 60255-6 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-1 | EN/IEC 60255-6 | EN/IEC 60255-1 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-1 | IEC 60255-6 NF EN 60255-6 | IEC 60255-6 NF EN 60255-6 | NF EN 60255-6 IEC 60255-6 | EN/IEC 60255-6 | IEC 60255-6 NF EN 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | NF EN 60255-6 IEC 60255-6 | EN/IEC 60255-1 | EN/IEC 60255-6 IEC 60034-11-2 | EN/IEC 60255-6 IEC 60034-11-2 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-1 | EN/IEC 60255-1 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | EN/IEC 60255-6 | IEC 60947-1 IEC 60584-1 | IEC 60947-1 IEC 60584-1 | IEC 60584-1 IEC 60947-1 | IEC 60584-1 IEC 60947-1 | EN/IEC 60255-1 | DIN 43760 EN/IEC 60584-1 EN/IEC 60947-1 EN/IEC 60751 | EN/IEC 60751 EN/IEC 60584-1 DIN 43760 EN/IEC 60947-1 | DIN 43760 EN/IEC 60751 EN/IEC 60584-1 EN/IEC 60947-1 | EN/IEC 60947-1 EN/IEC 60584-1 DIN 43760 EN/IEC 60751 | DIN 43760 EN/IEC 60751 EN/IEC 60947-1 EN/IEC 60584-1 | DIN 43760 EN/IEC 60584-1 EN/IEC 60751 EN/IEC 60947-1 | EN/IEC 60947-1 EN/IEC 60584-1 DIN 43760 EN/IEC 60751 | DIN 43760 EN/IEC 60751 EN/IEC 60947-1 EN/IEC 60584-1 | DIN 43760 EN/IEC 60584-1 EN/IEC 60947-1 EN/IEC 60751 | IEC 60947-1 IEC 60584-1 | IEC 60584-1 IEC 60947-1 | IEC 60584-1 IEC 60947-1 | IEC 60584-1 IEC 60947-1 | IEC 60584-1 IEC 60947-1 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | EN/IEC 61810-1 UL 508 CSA C22.2 No 14 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | UL 508 EN/IEC 61810-1 CSA C22.2 No 14 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | UL 508 EN/IEC 61810-1 CSA C22.2 No 14 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | EN/IEC 61810-1 UL 508 CSA C22.2 No 14 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | EN/IEC 61810-1 UL 508 CSA C22.2 No 14 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | UL 508 EN/IEC 61810-1 CSA C22.2 No 14 | UL 508 EN/IEC 61810-1 CSA C22.2 No 14 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | UL 508 EN/IEC 61810-1 CSA C22.2 No 14 | EN/IEC 61810-1 UL 508 CSA C22.2 No 14 | UL 508 EN/IEC 61810-1 CSA C22.2 No 14 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | UL 508 EN/IEC 61810-1 CSA C22.2 No 14 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | UL 508 EN/IEC 61810-1 CSA C22.2 No 14 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | EN/IEC 61810-1 UL 508 CSA C22.2 No 14 | UL 508 EN/IEC 61810-1 CSA C22.2 No 14 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | EN/IEC 61810-1 UL 508 CSA C22.2 No 14 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | EN/IEC 61810-1 UL 508 CSA C22.2 No 14 | UL 508 EN/IEC 61810-1 CSA C22.2 No 14 | EN/IEC 61810-1 UL 508 CSA C22.2 No 14 | UL 508 EN/IEC 61810-1 CSA C22.2 No 14 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | UL 508 EN/IEC 61810-1 CSA C22.2 No 14 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | UL 508 EN/IEC 61810-1 CSA C22.2 No 14 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | EN/IEC 61810-1 UL 508 CSA C22.2 No 14 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | EN/IEC 61810-1 UL 508 CSA C22.2 No 14 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | [7 empty] | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN 61000-6-2 EN 55014-2 EN 55022 EN 61000-6-3 | EN 61000-6-2 EN 61000-6-3 EN 60947 EN 60947-5 | EN 61000-6-3 EN 60947-5-1 EN 60947-01 EN 61000-6-2 | UL 464 EN/IEC 61000-6-3 EN/IEC 61000-6-2 | UL 464 EN/IEC 61000-6-3 EN/IEC 61000-6-2 | EN/IEC 61000-6-2 UL 464 EN/IEC 61000-6-3 | EN/IEC 61000-6-3 EN/IEC 61000-6-2 UL 464 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-5-1 EN/IEC 60947-1 | EN/IEC 60947-1 EN/IEC 60947-5-1 | EN/IEC 60947-5-1 EN/IEC 60947-1
| vibration resistance | [80 empty] | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | [11 empty] | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 ms (f= 10…55 Hz) conforming to IEC 60068-2-6 | 0.35 mm conforming to IEC 60068-2-6 (f = 10…55 Hz) | 0.35 mm conforming to IEC 60068-2-6 (f = 10…55 Hz) | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 1 gn (f= 58.1…150 Hz) not in operation conforming to IEC 60068-2-6 0.035 mm (f= 10…58.1 Hz) in operation conforming to IEC 60068-2-6 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6 | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6 | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6 | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6 | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6 | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6 | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6 | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6 | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6 | 10 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles not operating conforming to EN/IEC 60068-2-6 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)10 cycles in operation conforming to EN/IEC 60068-2-6 |  |  | 5 gn conforming to IEC 60068-2-6 | 5 gn conforming to IEC 60068-2-6 | [268 empty] | 4.6 gn (sideways) 4.6 gn (inverted) 7.1 gn (upright) | 4.6 gn (sideways) 4.6 gn (inverted) 7.1 gn (upright) | 4.6 gn (sideways) 4.6 gn (inverted) 7.1 gn (upright) | 4.6 gn (sideways) 4.6 gn (inverted) 7.1 gn (upright) | 4.6 gn (sideways) 4.6 gn (inverted) 4.6 gn (upright) | 4.6 gn (sideways) 4.6 gn (inverted) 4.6 gn (upright) | 4.6 gn (sideways) 4.6 gn (inverted) 4.6 gn (upright) | [14 empty] | 7 gn | 7 gn | 7 gn | 7 gn | 7 gn | 7 gn | 7 gn | 7 gn
Main | App for product | [143 empty] | Zelio NFC (downloadable from Google Play store) | [161 empty] | Zelio NFC (downloadable from Google Play store)
| Supported OS | [143 empty] | Android | [161 empty] | Android
| [In] rated current | [128 empty] | 5 A | 5 A | 5 A | 5 A
| [Ithe] conventional enclosed thermal current | [154 empty] | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 1 A 40 °C | 1 A 40 °C | 1 A 40 °C | 1 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 5 A 40 °C | 1 A 40 °C | 1 A 40 °C | 1 A 40 °C | 1 A 40 °C | [128 empty] | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 12 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 16 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 6 A at -40…55 °C | 6 A at -40…55 °C | 6 A at -40…55 °C | 6 A at -40…55 °C | 6 A at -40…55 °C | 6 A at -40…55 °C | 6 A at -40…55 °C | 6 A at -40…55 °C | 6 A at -40…55 °C | 6 A at -40…55 °C | 6 A at -40…55 °C | 6 A at -40…55 °C | 6 A at -40…55 °C | 6 A at -40…55 °C | 6 A at -40…55 °C | 6 A at -40…55 °C | 6 A at -40…55 °C | 6 A at -40…55 °C
| [Uc] control circuit voltage | [154 empty] | 220 V AC 50/60 Hz | 240 V AC 50/60 Hz | 220 V AC 50/60 Hz | 24 V AC/DC 50/60 Hz | 27 V AC/DC 50/60 Hz | 110 V AC/DC 50/60 Hz | 127 V AC/DC 50/60 Hz | 12 V AC/DC 50/60 Hz | 24 V AC/DC 50/60 Hz | 27 V AC/DC 50/60 Hz | 48 V AC/DC 50/60 Hz | 72 V AC/DC 50/60 Hz | 110 V AC/DC 50/60 Hz | 127 V AC/DC 50/60 Hz | 12 V AC/DC 50/60 Hz | 60 V AC/DC 50/60 Hz | 220 V AC 50/60 Hz | 24 V AC/DC 50/60 Hz | 48 V AC/DC 50/60 Hz | 127 V AC/DC 50/60 Hz | 220 V AC 50/60 Hz | 240 V AC 50/60 Hz | 220 V AC 50/60 Hz | 24 V AC/DC 50/60 Hz | 48 V AC/DC 50/60 Hz | 110 V AC/DC 50/60 Hz | 125 V AC/DC 50/60 Hz | 12 V AC/DC 50/60 Hz | 24 V AC/DC 50/60 Hz | 27 V AC/DC 50/60 Hz | 48 V AC/DC 50/60 Hz | 110 V AC/DC 50/60 Hz | 125 V AC/DC 50/60 Hz | 12 V AC/DC 50/60 Hz | 220 V AC 50/60 Hz | 24 V AC/DC 50/60 Hz | 110 V AC/DC 50/60 Hz | 127 V AC/DC 50/60 Hz | [128 empty] | 24 V AC | 24 V AC | 24 V DC | 24 V DC | 48 V AC | 48 V AC | 48 V DC | 48 V DC | 120 V AC | 120 V AC | 110 V DC | 110 V DC | 12 V DC | 12 V DC | 220 V AC | 220 V AC | 60 V DC | 60 V DC | 230 V AC | 230 V AC | 6 V DC | 6 V DC | 240 V AC | 240 V AC | 24 V AC | 24 V AC | 24 V DC | 24 V DC | 48 V AC | 48 V AC | 48 V DC | 48 V DC | 120 V AC | 120 V AC | 110 V DC | 110 V DC | 12 V DC | 12 V DC | 220 V AC | 220 V AC | 60 V DC | 60 V DC | 230 V AC | 230 V AC | 6 V DC | 6 V DC | 240 V AC | 240 V AC | 24 V AC | 24 V AC | 24 V DC | 24 V DC | 48 V AC | 48 V AC | 48 V DC | 48 V DC | 120 V AC | 120 V AC | 110 V DC | 110 V DC | 12 V DC | 12 V DC | 220 V AC | 220 V AC | 60 V DC | 60 V DC | 230 V AC | 230 V AC | 6 V DC | 6 V DC | 240 V AC | 240 V AC | 24 V DC | 48 V DC | 12 V DC | 60 V DC | 24 V DC | 48 V DC | 12 V DC | 60 V DC | 24 V DC | 48 V DC | 60 V DC | 12 V DC | 60 V DC | 24 V DC | 48 V DC | 60 V DC | 12 V DC | 60 V DC
| [Us] rated supply voltage | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 24 V | 24 V | 48 V | 120 V | 120 V | 12 V | 230 V | 230 V | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 24 V AC/DC | 120 V AC/DC | 230 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 24 V AC/DC | 120 V AC | 230 V AC | [48 empty] | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | [105 empty] | 24...240 V AC/DC | [176 empty] | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 48 V AC/DC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 12...48 V AC/DC | 120...230 V AC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | <= 250 V | <= 250 V | <= 250 V | <= 250 V | <= 250 V | <= 250 V | 24 V AC 24...48 V DC | 24 V AC 24...48 V DC | 24 V AC 24...48 V DC | 24 V AC 24...48 V DC | 24 V AC 24...48 V DC | 24 V AC 24...48 V DC | 48...230 V AC | 48...230 V AC | 48...230 V AC | 48...230 V AC | 48...230 V AC | 48...230 V AC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | <= 250 V | <= 250 V | <= 250 V | <= 250 V | 24 V AC 24...48 V DC | 24 V AC 24...48 V DC | 24 V AC 24...48 V DC | 24 V AC 24...48 V DC | 24 V AC 24...48 V DC | 24 V AC 24...48 V DC | 48...230 V AC | 48...230 V AC | 48...230 V AC | 48...230 V AC | 48...230 V AC | 48...230 V AC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | <= 230 V <= 230 V | <= 230 V <= 230 V | <= 230 V <= 230 V | <= 230 V <= 230 V | <= 230 V <= 230 V | <= 230 V <= 230 V | 24 V AC/DC 24 V AC/DC | 24 V AC/DC 24 V AC/DC | 24 V AC/DC 24 V AC/DC | 24 V AC/DC 24 V AC/DC | 24 V AC/DC 24 V AC/DC | 24 V AC/DC 24 V AC/DC | 120 V AC 120 V AC | 120 V AC 120 V AC | 120 V AC 120 V AC | 120 V AC 120 V AC | 120 V AC 120 V AC | 120 V AC 120 V AC | 230 V AC 230 V AC | 230 V AC 230 V AC | 230 V AC 230 V AC | 230 V AC 230 V AC | 230 V AC 230 V AC | 230 V AC 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 230 V AC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 230...240 V AC | 230...240 V AC | 230...240 V AC | 230...240 V AC | 230...240 V AC | <= 240 V AC/DC | <= 240 V AC/DC | <= 240 V AC/DC | <= 240 V AC/DC | <= 240 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 120 V AC | 230...240 V AC | 230...240 V AC | 230...240 V AC | 230...240 V AC | 230...240 V AC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC | 24 V AC/DC |  | 24 V | 120 V | 230 V | 120 V AC/DC | 120 V AC | 120 V AC/DC | 120 V AC/DC | 120 V AC/DC | 120 V AC | 120 V AC | 120 V AC | 120 V AC/DC | 230 V AC/DC | 230 V AC/DC | 230 V AC/DC | 230 V AC/DC | 230 V AC | 230 V AC | 230 V AC | 230 V AC/DC | 230 V AC | [7 empty] | 12 V AC/DC 24 V AC/DC | 120 V AC | 230 V AC
| accessory / separate part category | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessories | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory | Lighting accessory
| accessory / separate part designation | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Incandescent bulb | Incandescent bulb | Incandescent bulb | Incandescent bulb | Incandescent bulb | Incandescent bulb | Incandescent bulb | Incandescent bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Protected LED bulb | Incandescent bulb | Incandescent bulb | Incandescent bulb | [30 empty] | Flash discharge tube | Flash discharge tube | Flash discharge tube
| accessory / separate part destination | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank | Beacon and indicator bank
| accessory / separate part type | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | Incandescent bulb | Incandescent bulb | Incandescent bulb | Incandescent bulb | Incandescent bulb | Incandescent bulb | Incandescent bulb | Incandescent bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | LED bulb | Incandescent bulb | Incandescent bulb | Incandescent bulb | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Super bright LED | Flash discharge tube | Flash discharge tube | Flash discharge tube
| analogue input type | [301 empty] | Current 0...1.5 A AC/DC 50/60 Hz Current 0...15 A AC/DC 50/60 Hz Current 0...5 A AC/DC 50/60 Hz | Current 0...20 mA Current 4...20 mA Voltage +/- 10 V DC Voltage 0...10 V DC | Current 4...20 mA Voltage 0...10 V DC | Voltage 0...300 V AC/DC 50/60 Hz Voltage 0...50 V AC/DC 50/60 Hz Voltage 0...500 V AC/DC 50/60 Hz |  | Temperature probe - 40...40 °C/- 40...104 °F Pt 100 2, 3 or 4 wires | Temperature probe - 40...40 °C/- 40...104 °F Pt 100 2, 3 or 4 wires | Temperature probe - 100...100 °C/- 148...212 °F Pt 100 2, 3 or 4 wires | Temperature probe - 100...100 °C/- 148...212 °F Pt 100 2, 3 or 4 wires | Temperature probe 0...100 °C/32..212 °F Pt 100 2, 3 or 4 wires | Temperature probe 0...100 °C/32..212 °F Pt 100 2, 3 or 4 wires | Temperature probe 0...250 °C/32...482 °F Pt 100 2, 3 or 4 wires | Temperature probe 0...250 °C/32...482 °F Pt 100 2, 3 or 4 wires | Temperature probe 0...500 °C/32...932 °F Pt 100 2, 3 or 4 wires | Thermocouple 0...150 °C/32...302 °F thermocouple J conforming to IEC 60584 | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584 | Thermocouple 0...600 °C/32...1112 °F thermocouple J conforming to IEC 60584 | Thermocouple 0...600 °C/32...1112 °F thermocouple K conforming to IEC 60584 | Thermocouple 0...1200 °C/32...2192 °F thermocouple K conforming to IEC 60584
| analogue output type | [301 empty] | Current 0...20 mA <= 500 Ohm by cabling Current 4...20 mA <= 500 Ohm by cabling Voltage 0...10 V >= 100 kOhm by cabling | Current 0...20 mA <= 500 Ohm switchable Current 4...20 mA <= 500 Ohm switchable Voltage +/- 10 V >= 100 kOhm switchable Voltage 0...10 V >= 100 kOhm switchable | Current 4...20 mA <= 500 Ohm by cabling Voltage 0...10 V >= 100 kOhm by cabling | Current 0...20 mA <= 500 Ohm switchable Current 4...20 mA <= 500 Ohm switchable Voltage 0...10 V >= 100 kOhm switchable |  | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | Voltage 0...10 V >= 100 kOhm | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
| beacon or indicator bank unit type | [414 empty] | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Illuminated unit | Audible unit | Audible unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | Base unit direct or tube fixing Illuminated unit | 3 illuminated units | 3 illuminated units + 1 audible buzzer unit | 2 illuminated units | 4 illuminated units | 3 illuminated units | 3 illuminated units | 2 illuminated units | 2 illuminated units | 2 illuminated units + 1 audible buzzer unit | 3 illuminated units + 1 audible buzzer unit | 2 illuminated units + 1 audible buzzer unit | 1 illuminated unit | 1 illuminated unit | 1 illuminated unit + 1 audible buzzer unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | 3 illuminated units | 3 illuminated units | 3 illuminated units + 1 audible buzzer unit | 2 illuminated units + 1 audible buzzer unit | 1 illuminated unit | 1 illuminated unit | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 1 base unit 1 illuminated unit 1 screw fixing cover 1 short fixing base | 3 illuminated units | 3 illuminated units | 2 illuminated units | 3 illuminated units | 4 illuminated units | 4 illuminated units | 3 illuminated units | 2 illuminated units | 2 illuminated units | 2 illuminated units |  |  |  |  | 3 illuminated units | 3 illuminated units | 2 illuminated units | 3 illuminated units | 4 illuminated units | 4 illuminated units | 3 illuminated units | 2 illuminated units | 2 illuminated units | 3 illuminated units | 2 illuminated units | 3 illuminated units | 4 illuminated units | 4 illuminated units | 3 illuminated units | 2 illuminated units | 2 illuminated units | 2 illuminated units | LED unit | LED unit | LED unit | LED unit | LED unit | LED unit | LED unit | [14 empty] | Sound unit | Sound unit | Sound unit | Sound unit | Sound unit | Sound unit | Sound unit | Sound unit
| bulb base | [44 empty] | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d | BA 15d
| bulb type | [414 empty] | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube |  |  | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent Incandescent with BA 15d base Protected LED | Incandescent Incandescent with BA 15d base Protected LED | Incandescent Incandescent with BA 15d base Protected LED | Incandescent Incandescent with BA 15d base Protected LED | Incandescent Incandescent with BA 15d base Protected LED | Incandescent Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | [14 empty] | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent Incandescent with BA 15d base Protected LED | Incandescent Incandescent with BA 15d base Protected LED | Incandescent Incandescent with BA 15d base Protected LED | Incandescent Incandescent with BA 15d base Protected LED | Incandescent Incandescent with BA 15d base Protected LED | Incandescent Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Incandescent with BA 15d base Protected LED | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Incandescent with BA 15d base Incandescent with BA 15d base | Incandescent with BA 15d base Incandescent with BA 15d base | Incandescent with BA 15d base Incandescent with BA 15d base | Incandescent with BA 15d base Incandescent with BA 15d base | Incandescent with BA 15d base Incandescent with BA 15d base | Incandescent with BA 15d base Incandescent with BA 15d base | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | Flash discharge tube Flash discharge tube | [6 empty] | LED | LED | LED | LED | LED | LED | LED | LED | LED | LED | LED | LED | LED | LED | LED | Incandescent with BA 15d base | Incandescent with BA 15d base | Incandescent with BA 15d base | Incandescent with BA 15d base | Incandescent with BA 15d base | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube | Flash discharge tube
| coil interference suppression | [154 empty] | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With | With
| colour | [689 empty] | White | White | White
| component name | [80 empty] | RE17L | RE17L | RE17L | RE17L | RE17L | [43 empty] | RE48A | RE48 | RE48A | RE48 | RE7 | RE7 | RE7 | RE7 | RE7 | RE7 | RE7 | RE7 | RE8 | RE8 | RE8 |  | REXL | REXL | REXL | REXL | REXL | REXL | REXL | REXL | REXL | REXL | [256 empty] | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBC | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVBL | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVD | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVDLS XVDLS | XVD | XVD | XVD | XVD | XVD | XVD | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVE | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM | XVM
| contact operation | [154 empty] | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Low level | Low level | Low level | Low level | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Low level | Low level | Low level | Low level | [128 empty] | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Low level | Low level | Low level | Low level | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard | Standard
| contacts type and composition | [128 empty] | 2 C/O timed contacts, AgNi (cadmium free) | 1 C/O + 1 C/O timed or instantaneous contact, AgNi (cadmium free) | 2 C/O timed contacts, AgNi (cadmium free) | 2 C/O timed contacts, AgNi (cadmium free) |  |  | 2 C/O |  | 2 C/O |  | 2 C/O | 2 C/O |  |  |  |  | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | 4 C/O | [54 empty] | 1 C/O | 1 C/O | 1 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 2 C/O | 2 C/O |  | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | [19 empty] | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O | 1 C/O
| control type | [154 empty] | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | Selector switch | [128 empty] | Without push-button | Without push-button | Without push-button | Without push-button | Without push-button |  | Without push-button |  | Without push-button | Without push-button | Without push-button |  | Without push-button | Without push-button | Without push-button |  | Without push-button |  | Without push-button | Without push-button | Without push-button |  | Without push-button |  | Without push-button | Without push-button | Without push-button | Without push-button | Without push-button |  | Without push-button |  | Without push-button | Without push-button | Without push-button |  | Without push-button | Without push-button | Without push-button |  | Without push-button |  | Without push-button | Without push-button | Without push-button |  | Without push-button |  | Without push-button | Without push-button | Without push-button | Without push-button | Without push-button |  | Without push-button |  | Without push-button | Without push-button | Without push-button |  | Without push-button | Without push-button | Without push-button |  | Without push-button |  | Without push-button | Without push-button | Without push-button |  | Without push-button |  | Without push-button | Without push-button | Without push-button | Without push-button | Without push-button | Without push-button | Without push-button | Without push-button
| device application | [682 empty] | Forklift Automated guided vehicle (AGV) Bulldozer | Forklift Automated guided vehicle (AGV) Bulldozer | Forklift Automated guided vehicle (AGV) Bulldozer | Forklift Automated guided vehicle (AGV) Bulldozer | Bulldozer Automated guided vehicle (AGV) Forklift | Forklift Bulldozer Automated guided vehicle (AGV) | Automated guided vehicle (AGV) Forklift Bulldozer
| device short name | [85 empty] | RE17R | RE17R | RE17R | RE17R | RE17R | RE17R | RE17R | RE17R | RE17R | RE17R | RE17R | RE17R | RE22 | RE22 | RE22 | RE22 RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | RE22 | [15 empty] | RENF22 | [10 empty] | RHR | RHR | RHR | RHR | RHR | RHR | RHR | RHR | RHR | RHR | RHR | RHR | RHR | RHR | RHR | RHR | RHR | RHR | RHR | RHR | RHT | RHT | RHT | RHT | RHT | RHT | RHT | RHT | RHT | RHT | RHT | RHT | RHT | RHT | RHT | RHT | RHT | RHT | [128 empty] | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSB | RSL | RSL | RSL | RSL | RSL | RSL | RSL | RSL | RSL | RSL | RSL | RSL | RSL | RSL | RSL | RSL | RSL | RSL | [272 empty] | XVR3 | XVR3 | XVR3 | XVR3 | XVR3 | XVR3 | XVR3 | XVS | XVS | XVS | XVS | XVS | XVS | XVS | XVS | XVS | XVS | XVS | XVS | XVS | XVS | XVSV | XVSV | XVSV | XVSV | XVSV | XVSV | XVSV | XVSV
| discrete output type | [80 empty] | Solid state | Solid state | Solid state | Solid state | Solid state | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | [12 empty] | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay | Relay
| electrical connection | [128 empty] | Plug-in sub-base 11 pin(s) | Plug-in sub-base 8 pin(s) | Plug-in sub-base 11 pin(s) | Plug-in sub-base 8 pin(s) | [167 empty] | 2 conductors cable 1.5 mm² flexible cable with cable end conforming to IEC 60947-1 2 conductors cable 2.5 mm² flexible cable without cable end conforming to IEC 60947-1 | 2 conductors cable 1.5 mm² flexible cable with cable end conforming to IEC 60947-1 2 conductors cable 2.5 mm² flexible cable without cable end conforming to IEC 60947-1
| fixing mode | [144 empty] | Plug-in (socket) | Plug-in (socket) | Plug-in (socket) | Plug-in (socket) | Plug-in (socket) | Plug-in (socket) | Plug-in (socket) | Plug-in (socket) | Plug-in (socket) | Plug-in (socket)
| flash energy | [414 empty] | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 5 J | 10 J | 10 J | 10 J | 10 J | 10 J | 10 J | 10 J | 10 J | 10 J | 10 J | 10 J | 10 J | 10 J | 10 J | 10 J | 10 J | 10 J | 10 J | 10 J
| indicator bank base type | [650 empty] | Base without buzzer | Base with integrated buzzer | Base without buzzer | Base without buzzer | Base without buzzer | Base with integrated buzzer | Base with integrated buzzer | Base with integrated buzzer | Base without buzzer | Base with integrated buzzer | Base without buzzer | Base with integrated buzzer | Base with integrated buzzer | Base with integrated buzzer | Base without buzzer | Base with integrated buzzer | Base without buzzer | Base without buzzer | Base without buzzer | Base with integrated buzzer | Base with integrated buzzer | Base with integrated buzzer | Base without buzzer | Base without buzzer | Base without buzzer | Base without buzzer | Base without buzzer | Base with integrated buzzer | Base with integrated buzzer | Base with integrated buzzer | Base without buzzer | Base with integrated buzzer
| kit composition | [660 empty] | Cover Base unit | Base unit Cover | Base unit Cover | Cover Base unit
| light block color | [543 empty] | Green/orange/red | Green/orange/red | Orange/red | Clear/green/orange/red | Green/orange/red | Green/orange/red (flashing) | Green/red | Green/red (flashing) | Orange/red | Green/orange/red | Green/red |  |  | Orange (flashing) | [52 empty] | Green/orange/red | Green/orange/red | Green/orange/red | Green/red | [37 empty] | Orange/green/red (flashing) | Orange/green/red (flashing) | Red/orange | Red/orange/green | Red/orange/green/blue | Red/orange/green/blue | Red/orange/green | Red/orange | Red/green | Red/green |  |  |  |  | Orange/green/red (flashing) | Orange/green/red (flashing) | Red/orange | Red/orange/green | Red/orange/green/blue | Red/orange/green/blue | Red/orange/green | Red/orange | Red/green | Orange/green/red (flashing) | Red/orange | Red/orange/green | Red/orange/green/blue | Red/orange/green/blue | Red/orange/green | Red/orange | Red/green | Red/green
| light source | [414 empty] | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Integral flash discharge tube, yellow | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Integral flash discharge tube, yellow | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Integral flash discharge tube, yellow | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Integral flash discharge tube, yellow | Integral flash discharge tube, orange | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Integral flash discharge tube, yellow | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Integral flash discharge tube, yellow |  |  | Integral LED, green | Integral LED, red | Integral LED, orange | Integral LED, blue | Integral LED, clear | Integral LED, yellow | Integral LED, green | Integral LED, red | Integral LED, orange | Integral LED, blue | Integral LED, clear | Integral LED, yellow | Integral LED, green | Integral LED, red | Integral LED, orange | Integral LED, blue | Integral LED, clear | Integral LED, yellow | Integral LED, green | Integral LED, red | Integral LED, orange | Integral LED, blue | Integral LED, clear | Integral LED, yellow | Integral LED, green | Integral LED, red | Integral LED, orange | Integral LED, blue | Integral LED, clear | Integral LED, yellow | Integral LED, green | Integral LED, red | Integral LED, orange | Integral LED, blue | Integral LED, clear | Integral LED, yellow | Bulb not included, green | Bulb not included, red | Bulb not included, orange | Bulb not included, blue | Bulb not included, clear | Bulb not included, yellow | Bulb not included, green | Bulb not included, red | Bulb not included, orange | Bulb not included, blue | Bulb not included, clear | Bulb not included, yellow | Bulb not included, green | Bulb not included, red | Bulb not included, orange | Bulb not included, blue | Bulb not included, clear | Bulb not included, yellow | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Integral flash discharge tube, yellow | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Integral flash discharge tube, yellow | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Integral flash discharge tube, yellow | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Integral flash discharge tube, yellow | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Integral flash discharge tube, yellow | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Integral flash discharge tube, yellow | Green incandescent bulb with BA 15d base steady signalling <10 W Orange incandescent bulb with BA 15d base steady signalling <10 W Red incandescent bulb with BA 15d base steady signalling <10 W | Green incandescent bulb with BA 15d base steady signalling <10 W Orange incandescent bulb with BA 15d base steady signalling <10 W Red incandescent bulb with BA 15d base steady signalling <10 W | Orange LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling | Clear LED with BA 15d base steady signalling Green LED with BA 15d base steady signalling Orange LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling | Green LED with BA 15d base steady signalling Orange LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling | Red flash discharge tubeflashing signalling Green LED with BA 15d base steady signalling Orange LED with BA 15d base steady signalling | Green LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling | Red flash discharge tubeflashing signalling Green LED with BA 15d base steady signalling | Orange LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling | Green LED with BA 15d base steady signalling Orange LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling | Green LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling | Flash discharge tube, orange | Flash discharge tube, red | Orange flash discharge tubeflashing signalling | Bulb not included, green | Bulb not included, red | Bulb not included, orange | Bulb not included, yellow | Bulb not included, green | Bulb not included, red | Bulb not included, orange | Bulb not included, blue | Bulb not included, clear | Bulb not included, yellow | Bulb not included, green | Bulb not included, red | Bulb not included, orange | Bulb not included, blue | Bulb not included, clear | Bulb not included, yellow | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Integral flash discharge tube, yellow | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Integral flash discharge tube, yellow | Bulb not included, green Bulb not included, green | Bulb not included, red Bulb not included, red | Bulb not included, orange Bulb not included, orange | Bulb not included, blue Bulb not included, blue | Bulb not included, clear Bulb not included, clear | Bulb not included, yellow Bulb not included, yellow | Integral flash discharge tube, green Integral flash discharge tube, green | Integral flash discharge tube, red Integral flash discharge tube, red | Integral flash discharge tube, orange Integral flash discharge tube, orange | Integral flash discharge tube, blue Integral flash discharge tube, blue | Integral flash discharge tube, clear Integral flash discharge tube, clear | Integral flash discharge tube, yellow Integral flash discharge tube, yellow | Integral flash discharge tube, green Integral flash discharge tube, green | Integral flash discharge tube, red Integral flash discharge tube, red | Integral flash discharge tube, orange Integral flash discharge tube, orange | Integral flash discharge tube, blue Integral flash discharge tube, blue | Integral flash discharge tube, clear Integral flash discharge tube, clear | Integral flash discharge tube, yellow Integral flash discharge tube, yellow | Integral flash discharge tube, green Integral flash discharge tube, green | Integral flash discharge tube, red Integral flash discharge tube, red | Integral flash discharge tube, orange Integral flash discharge tube, orange | Integral flash discharge tube, blue Integral flash discharge tube, blue | Integral flash discharge tube, clear Integral flash discharge tube, clear | Integral flash discharge tube, yellow Integral flash discharge tube, yellow | Green incandescent bulb with BA 15d base steady signalling <10 W Orange incandescent bulb with BA 15d base steady signalling <10 W Red incandescent bulb with BA 15d base steady signalling <10 W | Green LED with BA 15d base steady signalling Orange LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling | Green LED with BA 15d base steady signalling Orange LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling | Green LED with BA 15d base steady signalling Red LED with BA 15d base steady signalling | Flash discharge tube, orange | Flash discharge tube, red | Integral LED, green | Integral LED, red | Integral LED, orange | Integral LED, blue | Integral LED, clear | Integral LED, green | Integral LED, red | Integral LED, orange | Integral LED, blue | Integral LED, clear | Integral LED, green | Integral LED, red | Integral LED, orange | Integral LED, blue | Integral LED, clear | Bulb not included, green | Bulb not included, red | Bulb not included, orange | Bulb not included, blue | Bulb not included, clear | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Integral flash discharge tube, green | Integral flash discharge tube, red | Integral flash discharge tube, orange | Integral flash discharge tube, blue | Integral flash discharge tube, clear | Orange incandescent bulb with BA 15d base steady signalling <5 W Red flash discharge tubeflashing signalling Green incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Red flash discharge tubeflashing signalling Green incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W Blue incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W Blue incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W | Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W | Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W |  |  |  |  | Orange incandescent bulb with BA 15d base steady signalling <5 W Red flash discharge tubeflashing signalling Green incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Red flash discharge tubeflashing signalling Green incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W Blue incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W Blue incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W | Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Red flash discharge tubeflashing signalling Green incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W Blue incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W Blue incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W | Orange incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W | Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W | Green incandescent bulb with BA 15d base steady signalling <5 W Red incandescent bulb with BA 15d base steady signalling <5 W | LED, green | LED, red | LED, orange | LED, blue | LED, red | LED, orange | LED, blue
| luminance | [44 empty] | 650 cd/m² | 650 cd/m² | 650 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m² | 900 cd/m²
| material | [410 empty] | Glass reinforced polyamide: base unit | Glass reinforced polyamide: base unit Polycarbonate: cover unit |  |  | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate | Polycarbonate |  |  | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | [14 empty] | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
| maximum power consumption in VA | [192 empty] | 3 VA | [33 empty] | 3.5 VA AC | 3.5 VA AC | 3.5 VA AC | 5 VA AC | 6 VA AC | 3.5 VA AC |  |  | 3.5 VA AC |  |  | 5 VA AC | [8 empty] | 2 VA AC | 3.3 VA AC | 3.5 VA AC | 3.3 VA AC | 3.4 VA AC | 3.3 VA AC | 3 VA AC | 3.3 VA AC | 3.4 VA AC | 3.3 VA AC | 3 VA AC
| maximum power dissipation in W | [489 empty] | 7 W | 7 W | 7 W | 7 W | 7 W | 7 W | 7 W | 7 W | 7 W | 7 W | 7 W | 7 W | 7 W | 7 W | 7 W | 7 W | 7 W | 7 W | [50 empty] | 10 W | 10 W | 10 W | 10 W | 10 W | 10 W | 10 W | 10 W | 10 W | 10 W | 10 W | 10 W | 10 W | 10 W | 10 W | 10 W | [12 empty] | 5 W 5 W | 5 W 5 W | 5 W 5 W | 5 W 5 W | 5 W 5 W | 5 W 5 W
| maximum switching current | [199 empty] | 5 A AC/DC | 5 A AC/DC | 5 A AC/DC | 5 A AC/DC | 5 A AC/DC | 5 A AC/DC | 5 A AC/DC | [23 empty] | 5 A AC/DC |  | 5 A AC |  |  | 5 A AC/DC | 5 A AC/DC | 5 A AC/DC |  |  |  |  | 5 A AC/DC | 5 A AC/DC | 5 A AC/DC | 5 A AC/DC | 5 A AC/DC | [53 empty] | 8 A AC at 250 V | 8 A AC at 250 V
| measurement range | [192 empty] | 2...20 A current | 208...480 V voltage AC | 208...480 V voltage AC | 208...480 V voltage AC | 208...480 V voltage AC | 208...480 V voltage AC | 208...480 V voltage AC | 9...15 V voltage DC | 65...260 V voltage AC 50/60 Hz 65...260 V voltage DC | 165 V voltage AC | 20...80 V voltage AC 50/60 Hz 20...80 V voltage DC | 183...528 V voltage AC | 65...260 V voltage AC/DC | 20...80 V voltage AC 50/60 Hz 20...80 V voltage DC | 4...40 mA E1-M terminals 20...200 mA E2-M terminals 100...1000 mA E3-M terminals 4 mA...1 A current AC/DC 50/60 Hz | 4...40 mA E1-M terminals 20...200 mA E2-M terminals 100...1000 mA E3-M terminals 4 mA...1 A current AC/DC 50/60 Hz | 250 Ohm...1 MOhm | 250 Ohm...1 MOhm | 5...100 kOhm | 5...100 kOhm | 200...240 V voltage AC | 380...480 V voltage AC | 183...528 V voltage AC | 200...240 V voltage AC | 380...480 V voltage AC | 200...240 V voltage AC | 380...480 V voltage AC | 50 mV...5 V voltage AC/DC 50/60 Hz | 1...100 V voltage AC/DC 50/60 Hz | 15...500 V voltage AC/DC 50/60 Hz | 50 mV...5 V voltage AC/DC 50/60 Hz | 1...100 V voltage AC/DC 50/60 Hz | 15...500 V voltage AC/DC 50/60 Hz | 80...300 V voltage AC/DC 50/60 Hz |  |  |  | 1...10 A AC | 40...70 Hz frequency | 10...100 mA E2-M terminals 2...20 mA E1-M terminals 2...500 mA current 50...500 mA E3-M terminals | 0.15...1.5 A E1-M terminals 0.5...5 A E2-M terminals 1.5...15 A E3-M terminals 150 mA...15 A current AC/DC 50/60 Hz | 0.15...1.5 A E1-M terminals 0.5...5 A E2-M terminals 1.5...15 A E3-M terminals 150 mA...15 A current AC/DC 50/60 Hz | 0.15...1.5 A E1-M terminals 0.5...5 A E2-M terminals 1.5...15 A E3-M terminals 150 mA...15 A current | 250 Ohm...1 MOhm |  | 0.05...0.5 s 0.5...5 min 1...10 min 1...10 s 0.5...5 s 0.1...1 s 0.1...1 min | 208...480 V voltage AC | 208...480 V voltage AC 0...20 Ohm short-circuit detection | 208...480 V voltage AC 0...20 Ohm short-circuit detection | 0.05...5 V voltage | 1...100 V voltage | 15...600 V voltage | 194...528 V voltage AC 50/60 Hz | 114...329 V voltage AC 50/60 Hz | 0.3...30 mA current AC 50/60 Hz 0.3...30 mA current DC 10...100 mA current AC 50/60 Hz 10...100 mA current DC 100...1000 mA current AC 50/60 Hz 100...1000 mA current DC | 0.3...30 mA current AC 50/60 Hz 0.3...30 mA current DC 10...100 mA current AC 50/60 Hz 10...100 mA current DC 100...1000 mA current AC 50/60 Hz 100...1000 mA current DC | 0.3...30 mA current AC 50/60 Hz 0.3...30 mA current DC 10...100 mA current AC 50/60 Hz 10...100 mA current DC 100...1000 mA current AC 50/60 Hz 100...1000 mA current DC | 0.3...30 mA current AC 50/60 Hz 0.3...30 mA current DC 10...100 mA current AC 50/60 Hz 10...100 mA current DC 100...1000 mA current AC 50/60 Hz 100...1000 mA current DC | 0.3...30 mA current DC 10...100 mA current DC 100...1000 mA current DC 0.3...30 mA current AC 10...100 mA current AC 100...1000 mA current AC | 0.3...30 mA current DC 10...100 mA current DC 100...1000 mA current DC 0.3...30 mA current AC 10...100 mA current AC 100...1000 mA current AC | 0.3...30 mA current DC 10...100 mA current DC 100...1000 mA current DC 0.3...30 mA current AC 10...100 mA current AC 100...1000 mA current AC | 1...5 A current AC 1...5 A current DC 3...15 A current AC 3...15 A current DC 300...1500 mA current AC 300...1500 mA current DC | 1...5 A current AC 1...5 A current DC 3...15 A current AC 3...15 A current DC 300...1500 mA current AC 300...1500 mA current DC | 1...5 A current AC 1...5 A current DC 3...15 A current AC 3...15 A current DC 300...1500 mA current AC 300...1500 mA current DC | 1...5 A current AC 1...5 A current DC 3...15 A current AC 3...15 A current DC 300...1500 mA current AC 300...1500 mA current DC | [9 empty] | 160...300 V | 290...484 V | 160...300 V | 290...484 V | 198...484 V | 160...300 V | 290...484 V | 160...300 V | 290...484 V |  | 160...300 V | 290...484 V | 0.05...0.5 V voltage AC 50/60 Hz 0.3...3 V voltage AC 50/60 Hz 0.5...5 V voltage AC 50/60 Hz <= 80 ms cycle 0.05...0.5 V voltage DC 0.3...3 V voltage DC 0.5...5 V voltage DC | 0.05...0.5 V voltage AC 50/60 Hz 0.3...3 V voltage AC 50/60 Hz 0.5...5 V voltage AC 50/60 Hz <= 80 ms cycle 0.05...0.5 V voltage DC 0.3...3 V voltage DC 0.5...5 V voltage DC | 0.05...0.5 V voltage AC 50/60 Hz 0.3...3 V voltage AC 50/60 Hz 0.5...5 V voltage AC 50/60 Hz <= 80 ms cycle 0.05...0.5 V voltage DC 0.3...3 V voltage DC 0.5...5 V voltage DC | 1...10 V voltage AC 50/60 Hz 10...100 V voltage AC 50/60 Hz 5...50 V voltage AC 50/60 Hz <= 80 ms cycle 1...10 V voltage DC 10...100 V voltage DC 5...50 V voltage DC | 1...10 V voltage AC 50/60 Hz 10...100 V voltage AC 50/60 Hz 5...50 V voltage AC 50/60 Hz <= 80 ms cycle 1...10 V voltage DC 10...100 V voltage DC 5...50 V voltage DC | 1...10 V voltage AC 50/60 Hz 10...100 V voltage AC 50/60 Hz 5...50 V voltage AC 50/60 Hz <= 80 ms cycle 1...10 V voltage DC 10...100 V voltage DC 5...50 V voltage DC | 30...300 V voltage AC 50/60 Hz 50...500 V voltage AC 50/60 Hz <= 80 ms cycle 30...300 V voltage DC 50...500 V voltage DC | 30...300 V voltage AC 50/60 Hz 50...500 V voltage AC 50/60 Hz <= 80 ms cycle 30...300 V voltage DC 50...500 V voltage DC | 30...300 V voltage AC 50/60 Hz 50...500 V voltage AC 50/60 Hz <= 80 ms cycle 30...300 V voltage DC 50...500 V voltage DC | 0.05...0.5 V voltage AC 50/60 Hz 0.3...3 V voltage AC 50/60 Hz 0.5...5 V voltage AC 50/60 Hz 0.05...0.5 V voltage DC 0.3...3 V voltage DC 0.5...5 V voltage DC | 0.05...0.5 V voltage AC 50/60 Hz 0.3...3 V voltage AC 50/60 Hz 0.5...5 V voltage AC 50/60 Hz 0.05...0.5 V voltage DC 0.3...3 V voltage DC 0.5...5 V voltage DC | 0.05...0.5 V voltage AC 50/60 Hz 0.3...3 V voltage AC 50/60 Hz 0.5...5 V voltage AC 50/60 Hz 0.05...0.5 V voltage DC 0.3...3 V voltage DC 0.5...5 V voltage DC | 0.05...0.5 V voltage AC 50/60 Hz 0.3...3 V voltage AC 50/60 Hz 0.5...5 V voltage AC 50/60 Hz 0.05...0.5 V voltage DC 0.3...3 V voltage DC 0.5...5 V voltage DC | 1...10 V voltage AC 50/60 Hz 10...100 V voltage AC 50/60 Hz 5...50 V voltage AC 50/60 Hz 1...10 V voltage DC 10...100 V voltage DC 5...50 V voltage DC | 1...10 V voltage AC 50/60 Hz 10...100 V voltage AC 50/60 Hz 5...50 V voltage AC 50/60 Hz 1...10 V voltage DC 10...100 V voltage DC 5...50 V voltage DC | 1...10 V voltage AC 50/60 Hz 10...100 V voltage AC 50/60 Hz 5...50 V voltage AC 50/60 Hz 1...10 V voltage DC 10...100 V voltage DC 5...50 V voltage DC | 1...10 V voltage AC 50/60 Hz 10...100 V voltage AC 50/60 Hz 5...50 V voltage AC 50/60 Hz 1...10 V voltage DC 10...100 V voltage DC 5...50 V voltage DC | 30...300 V voltage AC 50/60 Hz 50...500 V voltage AC 50/60 Hz 30...300 V voltage DC 50...500 V voltage DC | 30...300 V voltage AC 50/60 Hz 50...500 V voltage AC 50/60 Hz 30...300 V voltage DC 50...500 V voltage DC | 30...300 V voltage AC 50/60 Hz 50...500 V voltage AC 50/60 Hz 30...300 V voltage DC 50...500 V voltage DC | 30...300 V voltage AC 50/60 Hz 50...500 V voltage AC 50/60 Hz 30...300 V voltage DC 50...500 V voltage DC
| minimum switching current | [192 empty] | 10 mA at 5 V DC | [6 empty] | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | [20 empty] | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC |  |  | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC |  |  |  | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC | [53 empty] | 10 mA at 12 V | 10 mA at 12 V
| mounting diameter | [414 empty] | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | [14 empty] | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 70 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | 45 mm 45 mm | [73 empty] | 100 mm | 100 mm | 100 mm | 100 mm | 100 mm | 100 mm | 100 mm
| mounting mode | [650 empty] | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical |  |  |  |  | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical | Vertical
| network number of phases | [212 empty] | 3 phases | 3 phases | 3 phases | 3 phases | 3 phases | 3 phases | 3 phases | 1 phase | 1 phase | 1 phase | 1 phase | 1 phase | 1 phase | 1 phase | [79 empty] | 3 phases
| noise level | [451 empty] | 70…90 dB at 1 m | 70…90 dB at 1 m | [236 empty] | 106 dB (continuous or intermittent tone) at 1 m | 106 dB (continuous or intermittent tone) at 1 m | 106 dB (continuous or intermittent tone) at 1 m
| nominal output current | [80 empty] | 0.7 A | 0.7 A | 0.7 A | 0.7 A | 0.7 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A 8 A | 8 A | 8 A | 5 A | 8 A | 5 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 5 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A | 8 A
| poles description | [266 empty] | 3P | 3P | 3P | 3P | 3P | 3P | 3P | 3P | 3P | 3P | 3P | 3P | [21 empty] | 1P | 1P
| power consumption | [235 empty] | 5 VA AC | 5 VA AC | [20 empty] | 3.1 VA AC | 2.7 VA AC | 2.6 VA AC | 2.7 VA AC | 3.4 VA AC | 1.9 VA AC | 2.6 VA AC | 2.4 VA AC | 2.9 VA AC
| power consumption in VA | [200 empty] | 0…3 VA AC | 0…3 VA AC | 0…3.9 VA AC | 0…22 VA at 400 V AC 50 Hz | 0…3 VA AC | 0…3.9 VA AC | [35 empty] | 0…3.5 VA AC | 0…3.5 VA AC | 0…3.5 VA AC | 0…22 VA at 400 V AC 50 Hz | 0…3.9 VA AC | [32 empty] | 2 VA AC | 1.9…3.3 VA AC | 2.7…3.5 VA AC | 2 VA AC | 1.9…3.3 VA AC | 2.7…3.5 VA AC | 2 VA AC | 1.9…3.3 VA AC | 2.7…3.5 VA AC | 1.9…3.3 VA AC | 2.7…3.4 VA AC | 1.5…3.3 VA AC | 2.7…3.4 VA AC | 1.9…3.3 VA AC | 2.7…3.4 VA AC | 1.5…3.3 VA AC | 2.7…3 VA AC | 1.9…3.3 VA AC | 2.7…3.4 VA AC | 1.5…3.3 VA AC | 2.7…3 VA AC
| power dissipation in W | [18 empty] | 6.5 W | 4 W | 6 W | 7 W | 5 W | 7 W | 7 W | 5 W
| product compatibility | [305 empty] | NFC enabled mobile device