## status
0 | RM17JC00MW | https://www.se.com/ww/en/product/RM17JC00MW/ | Found
1 | RM17TA00 | https://www.se.com/ww/en/product/RM17TA00/ | Found
2 | RM17TE00 | https://www.se.com/ww/en/product/RM17TE00/ | Found
3 | RM10TE00 | https://www.se.com/ww/en/product/RM10TE00/ | Not Found
4 | RE22R2AMR | https://www.se.com/ww/en/product/RE22R2AMR/ | Not Found
5 | RE22R2CMR | https://www.se.com/ww/en/product/RE22R2CMR/ | Found
6 | RMTJ60BD | https://www.se.com/ww/en/product/RMTJ60BD/ | Found
7 | XVDLS37 | https://www.se.com/ww/en/product/XVDLS37/ | Found
8 | XVDLS38 | https://www.se.com/ww/en/product/XVDLS38/ | Found
9 | RHT428B | https://www.se.com/ww/en/product/RHT428B/ | Found
10 | RHT418BE | https://www.se.com/ww/en/product/RHT418BE/ | Found
11 | RSB1A160M7S | https://www.se.com/ww/en/product/RSB1A160M7S/ | Found
12 | RSB1A160NDS | https://www.se.com/ww/en/product/RSB1A160NDS/ | Found
13 | RSB2A080P7S | https://www.se.com/ww/en/product/RSB2A080P7S/ | Found
14 | RSB2A080RDS | https://www.se.com/ww/en/product/RSB2A080RDS/ | Found
15 | RSB2A080U7S | https://www.se.com/ww/en/product/RSB2A080U7S/ | Found
16 | RSB2A080M7S | https://www.se.com/ww/en/product/RSB2A080M7S/ | Found

## raw_datasheet
| Reference | Section | Parameters | Value | Param_ID
0 | RM17JC00MW | Main | range of product | Zelio Control | RM17JC00MWrange of product
1 | RM17JC00MW | Main | product or component type | Modular measurement and control relays | RM17JC00MWproduct or component type
2 | RM17JC00MW | Main | relay type | Current control relay | RM17JC00MWrelay type
3 | RM17JC00MW | Main | relay name | RM17JC | RM17JC00MWrelay name
4 | RM17JC00MW | Main | relay monitored parameters | Overcurrent detection | RM17JC00MWrelay monitored parameters
5 | RM17JC00MW | Main | time delay | Without | RM17JC00MWtime delay
6 | RM17JC00MW | Main | switching capacity in VA | 1250 VA | RM17JC00MWswitching capacity in VA
7 | RM17JC00MW | Main | minimum switching current | 10 mA at 5 V DC | RM17JC00MWminimum switching current
8 | RM17JC00MW | Main | maximum power consumption in VA | 3 VA | RM17JC00MWmaximum power consumption in VA
9 | RM17JC00MW | Main | measurement range | 2...20 A current | RM17JC00MWmeasurement range
10 | RM17JC00MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1 | RM17JC00MWutilisation category
11 | RM17JC00MW | Complementary | maximum switching voltage | 250 V AC/DC | RM17JC00MWmaximum switching voltage
12 | RM17JC00MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 % | RM17JC00MW[Us] rated supply voltage
13 | RM17JC00MW | Complementary | supply voltage limits | 20.4…264 V AC/DC | RM17JC00MWsupply voltage limits
14 | RM17JC00MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un | RM17JC00MWoperating voltage tolerance
15 | RM17JC00MW | Complementary | maximum power consumption in W | 1 W | RM17JC00MWmaximum power consumption in W
16 | RM17JC00MW | Complementary | control circuit frequency | 40...70 Hz sinusoidal | RM17JC00MWcontrol circuit frequency
17 | RM17JC00MW | Complementary | output contacts | 1 C/O | RM17JC00MWoutput contacts
18 | RM17JC00MW | Complementary | nominal output current | 5 A | RM17JC00MWnominal output current
19 | RM17JC00MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value | RM17JC00MWmaximum measuring cycle
20 | RM17JC00MW | Complementary | hysteresis | 15 % fixed of threshold setting | RM17JC00MWhysteresis
21 | RM17JC00MW | Complementary | delay at power up | 0.5 s | RM17JC00MWdelay at power up
22 | RM17JC00MW | Complementary | measurement accuracy | +/- 10 % of the full scale value | RM17JC00MWmeasurement accuracy
23 | RM17JC00MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit | RM17JC00MWrepeat accuracy
24 | RM17JC00MW | Complementary | measurement error | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | RM17JC00MWmeasurement error
25 | RM17JC00MW | Complementary | response time | < 200 ms (in the event of a fault) | RM17JC00MWresponse time
26 | RM17JC00MW | Complementary | polarity | Yes DC | RM17JC00MWpolarity
27 | RM17JC00MW | Complementary | threshold setting | 10...100 % | RM17JC00MWthreshold setting
28 | RM17JC00MW | Complementary | input current | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C | RM17JC00MWinput current
29 | RM17JC00MW | Complementary | marking | CE : 73/23/EEC CE : EMC 89/336/EEC | RM17JC00MWmarking
30 | RM17JC00MW | Complementary | overvoltage category | III conforming to IEC 60664-1 | RM17JC00MWovervoltage category
31 | RM17JC00MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | RM17JC00MWinsulation resistance
32 | RM17JC00MW | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1 | RM17JC00MW[Ui] rated insulation voltage
33 | RM17JC00MW | Complementary | insulation | Between supply and measurement | RM17JC00MWinsulation
34 | RM17JC00MW | Complementary | operating position | Any position without derating | RM17JC00MWoperating position
35 | RM17JC00MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | RM17JC00MWconnections - terminals
36 | RM17JC00MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | RM17JC00MWtightening torque
37 | RM17JC00MW | Complementary | housing material | Self-extinguishing plastic | RM17JC00MWhousing material
38 | RM17JC00MW | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON | RM17JC00MWlocal signalling
39 | RM17JC00MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | RM17JC00MWmounting support
40 | RM17JC00MW | Complementary | electrical durability | 100000 cycles | RM17JC00MWelectrical durability
41 | RM17JC00MW | Complementary | mechanical durability | 30000000 cycles | RM17JC00MWmechanical durability
42 | RM17JC00MW | Complementary | operating rate | <= 360 operations/hour full load | RM17JC00MWoperating rate
43 | RM17JC00MW | Complementary | contacts material | Cadmium free | RM17JC00MWcontacts material
44 | RM17JC00MW | Complementary | width | 17.5 mm | RM17JC00MWwidth
45 | RM17JC00MW | Complementary | net weight | 0.13 kg | RM17JC00MWnet weight
46 | RM17JC00MW | Environment | immunity to microbreaks | 10 ms | RM17JC00MWimmunity to microbreaks
47 | RM17JC00MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | RM17JC00MWelectromagnetic compatibility
48 | RM17JC00MW | Environment | standards | EN/IEC 60255-6 | RM17JC00MWstandards
49 | RM17JC00MW | Environment | product certifications | GL C-Tick GOST UL CSA | RM17JC00MWproduct certifications
50 | RM17JC00MW | Environment | ambient air temperature for storage | -40…70 °C | RM17JC00MWambient air temperature for storage
51 | RM17JC00MW | Environment | ambient air temperature for operation | -20…50 °C | RM17JC00MWambient air temperature for operation
52 | RM17JC00MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30 | RM17JC00MWrelative humidity
53 | RM17JC00MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | RM17JC00MWvibration resistance
54 | RM17JC00MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1 | RM17JC00MWshock resistance
55 | RM17JC00MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | RM17JC00MWIP degree of protection
56 | RM17JC00MW | Environment | pollution degree | 3 conforming to IEC 60664-1 | RM17JC00MWpollution degree
57 | RM17JC00MW | Environment | dielectric test voltage | 2 kV AC 50 Hz | RM17JC00MWdielectric test voltage
58 | RM17JC00MW | Environment | non-dissipating shock wave | 4 kV | RM17JC00MWnon-dissipating shock wave
59 | RM17JC00MW | Offer Sustainability | Sustainable offer status | Green Premium product | RM17JC00MWSustainable offer status
60 | RM17JC00MW | Offer Sustainability | REACh Regulation | REACh Declaration | RM17JC00MWREACh Regulation
61 | RM17JC00MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RM17JC00MWEU RoHS Directive
62 | RM17JC00MW | Offer Sustainability | Mercury free | Yes | RM17JC00MWMercury free
63 | RM17JC00MW | Offer Sustainability | RoHS exemption information | Yes | RM17JC00MWRoHS exemption information
64 | RM17JC00MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RM17JC00MWChina RoHS Regulation
65 | RM17JC00MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RM17JC00MWEnvironmental Disclosure
66 | RM17JC00MW | Offer Sustainability | Circularity Profile | End of Life Information | RM17JC00MWCircularity Profile
67 | RM17JC00MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RM17JC00MWWEEE
68 | RM17JC00MW | Contractual warranty | Warranty | 18 months | RM17JC00MWWarranty
69 | RM17TA00 | Main | range of product | Zelio Control | RM17TA00range of product
70 | RM17TA00 | Main | product or component type | Modular measurement and control relays | RM17TA00product or component type
71 | RM17TA00 | Main | relay type | Multifunction control relay | RM17TA00relay type
72 | RM17TA00 | Main | product specific application | For 3-phase supply | RM17TA00product specific application
73 | RM17TA00 | Main | relay name | RM17TA | RM17TA00relay name
74 | RM17TA00 | Main | relay monitored parameters | Asymmetry Phase sequence Phase failure detection | RM17TA00relay monitored parameters
75 | RM17TA00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value | RM17TA00time delay
76 | RM17TA00 | Main | switching capacity in VA | 1250 VA | RM17TA00switching capacity in VA
77 | RM17TA00 | Main | measurement range | 208...480 V voltage AC | RM17TA00measurement range
78 | RM17TA00 | Complementary | reset time | 1500 ms time delay | RM17TA00reset time
79 | RM17TA00 | Complementary | maximum switching voltage | 250 V AC 250 V DC | RM17TA00maximum switching voltage
80 | RM17TA00 | Complementary | minimum switching current | 10 mA at 5 V DC | RM17TA00minimum switching current
81 | RM17TA00 | Complementary | maximum switching current | 5 A AC 5 A DC | RM17TA00maximum switching current
82 | RM17TA00 | Complementary | supply voltage limits | 183…528 V AC | RM17TA00supply voltage limits
83 | RM17TA00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un | RM17TA00control circuit voltage limits
84 | RM17TA00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz | RM17TA00power consumption in VA
85 | RM17TA00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 % | RM17TA00control circuit frequency
86 | RM17TA00 | Complementary | output contacts | 1 C/O | RM17TA00output contacts
87 | RM17TA00 | Complementary | nominal output current | 5 A | RM17TA00nominal output current
88 | RM17TA00 | Complementary | measurement voltage limits | 183…528 V AC | RM17TA00measurement voltage limits
89 | RM17TA00 | Complementary | hysteresis | 2 % | RM17TA00hysteresis
90 | RM17TA00 | Complementary | delay at power up | 650 ms | RM17TA00delay at power up
91 | RM17TA00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value | RM17TA00maximum measuring cycle
92 | RM17TA00 | Complementary | threshold adjustment voltage | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC | RM17TA00threshold adjustment voltage
93 | RM17TA00 | Complementary | voltage range | 208...480 V phase to phase | RM17TA00voltage range
94 | RM17TA00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected | RM17TA00adjustment of asymmetry threshold
95 | RM17TA00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit 3 % for time delay | RM17TA00repeat accuracy
96 | RM17TA00 | Complementary | measurement error | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | RM17TA00measurement error
97 | RM17TA00 | Complementary | phase failure sensitivity | 0.7 Un | RM17TA00phase failure sensitivity
98 | RM17TA00 | Complementary | response time | < 200 ms (in the event of a fault) | RM17TA00response time
99 | RM17TA00 | Complementary | marking | CE | RM17TA00marking
100 | RM17TA00 | Complementary | overvoltage category | III conforming to IEC 60664-1 | RM17TA00overvoltage category
101 | RM17TA00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | RM17TA00insulation resistance
102 | RM17TA00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1 | RM17TA00[Ui] rated insulation voltage
103 | RM17TA00 | Complementary | supply frequency | 50/60 Hz +/- 10 % | RM17TA00supply frequency
104 | RM17TA00 | Complementary | operating position | Any position without derating | RM17TA00operating position
105 | RM17TA00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | RM17TA00connections - terminals
106 | RM17TA00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | RM17TA00tightening torque
107 | RM17TA00 | Complementary | housing material | Self-extinguishing plastic | RM17TA00housing material
108 | RM17TA00 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON | RM17TA00local signalling
109 | RM17TA00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | RM17TA00mounting support
110 | RM17TA00 | Complementary | electrical durability | 100000 cycles | RM17TA00electrical durability
111 | RM17TA00 | Complementary | mechanical durability | 30000000 cycles | RM17TA00mechanical durability
112 | RM17TA00 | Complementary | operating rate | <= 360 operations/hour full load | RM17TA00operating rate
113 | RM17TA00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | RM17TA00utilisation category
114 | RM17TA00 | Complementary | safety reliability data | MTTFd = 502.2 years B10d = 470000 | RM17TA00safety reliability data
115 | RM17TA00 | Complementary | width | 17.5 mm | RM17TA00width
116 | RM17TA00 | Complementary | net weight | 0.13 kg | RM17TA00net weight
117 | RM17TA00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | RM17TA00electromagnetic compatibility
118 | RM17TA00 | Environment | standards | EN/IEC 60255-1 | RM17TA00standards
119 | RM17TA00 | Environment | product certifications | GOST CSA GL C-Tick UL | RM17TA00product certifications
120 | RM17TA00 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | RM17TA00directives
121 | RM17TA00 | Environment | ambient air temperature for storage | -40…70 °C | RM17TA00ambient air temperature for storage
122 | RM17TA00 | Environment | ambient air temperature for operation | -20…50 °C | RM17TA00ambient air temperature for operation
123 | RM17TA00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30 | RM17TA00relative humidity
124 | RM17TA00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | RM17TA00vibration resistance
125 | RM17TA00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1 | RM17TA00shock resistance
126 | RM17TA00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | RM17TA00IP degree of protection
127 | RM17TA00 | Environment | pollution degree | 3 conforming to IEC 60664-1 | RM17TA00pollution degree
128 | RM17TA00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | RM17TA00dielectric test voltage
129 | RM17TA00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | RM17TA00non-dissipating shock wave
130 | RM17TA00 | Offer Sustainability | Sustainable offer status | Green Premium product | RM17TA00Sustainable offer status
131 | RM17TA00 | Offer Sustainability | REACh Regulation | REACh Declaration | RM17TA00REACh Regulation
132 | RM17TA00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RM17TA00EU RoHS Directive
133 | RM17TA00 | Offer Sustainability | Mercury free | Yes | RM17TA00Mercury free
134 | RM17TA00 | Offer Sustainability | RoHS exemption information | Yes | RM17TA00RoHS exemption information
135 | RM17TA00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RM17TA00China RoHS Regulation
136 | RM17TA00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RM17TA00Environmental Disclosure
137 | RM17TA00 | Offer Sustainability | Circularity Profile | End of Life Information | RM17TA00Circularity Profile
138 | RM17TA00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RM17TA00WEEE
139 | RM17TA00 | Contractual warranty | Warranty | 18 months | RM17TA00Warranty
140 | RM17TE00 | Main | range of product | Zelio Control | RM17TE00range of product
141 | RM17TE00 | Main | product or component type | Modular measurement and control relays | RM17TE00product or component type
142 | RM17TE00 | Main | relay type | Multifunction control relay | RM17TE00relay type
143 | RM17TE00 | Main | product specific application | For 3-phase supply | RM17TE00product specific application
144 | RM17TE00 | Main | relay name | RM17TE | RM17TE00relay name
145 | RM17TE00 | Main | relay monitored parameters | Undervoltage and overvoltage in window mode Asymmetry Phase sequence Phase failure detection | RM17TE00relay monitored parameters
146 | RM17TE00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value | RM17TE00time delay
147 | RM17TE00 | Main | switching capacity in VA | 1250 VA | RM17TE00switching capacity in VA
148 | RM17TE00 | Main | measurement range | 208...480 V voltage AC | RM17TE00measurement range
149 | RM17TE00 | Complementary | reset time | 1500 ms time delay | RM17TE00reset time
150 | RM17TE00 | Complementary | maximum switching voltage | 250 V AC 250 V DC | RM17TE00maximum switching voltage
151 | RM17TE00 | Complementary | minimum switching current | 10 mA at 5 V DC | RM17TE00minimum switching current
152 | RM17TE00 | Complementary | maximum switching current | 5 A AC 5 A DC | RM17TE00maximum switching current
153 | RM17TE00 | Complementary | supply voltage limits | 183…528 V AC | RM17TE00supply voltage limits
154 | RM17TE00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un | RM17TE00control circuit voltage limits
155 | RM17TE00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz | RM17TE00power consumption in VA
156 | RM17TE00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 % | RM17TE00control circuit frequency
157 | RM17TE00 | Complementary | output contacts | 1 C/O | RM17TE00output contacts
158 | RM17TE00 | Complementary | nominal output current | 5 A | RM17TE00nominal output current
159 | RM17TE00 | Complementary | measurement voltage limits | 183…528 V AC | RM17TE00measurement voltage limits
160 | RM17TE00 | Complementary | hysteresis | 2 % | RM17TE00hysteresis
161 | RM17TE00 | Complementary | delay at power up | 650 ms | RM17TE00delay at power up
162 | RM17TE00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value | RM17TE00maximum measuring cycle
163 | RM17TE00 | Complementary | threshold adjustment voltage | -2...-17 % in the range 220 V AC +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC 2...20 % of Un selected | RM17TE00threshold adjustment voltage
164 | RM17TE00 | Complementary | voltage range | 208...480 V phase to phase | RM17TE00voltage range
165 | RM17TE00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected | RM17TE00adjustment of asymmetry threshold
166 | RM17TE00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit 3 % for time delay | RM17TE00repeat accuracy
167 | RM17TE00 | Complementary | measurement error | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | RM17TE00measurement error
168 | RM17TE00 | Complementary | phase failure sensitivity | 0.7 Un | RM17TE00phase failure sensitivity
169 | RM17TE00 | Complementary | response time | < 200 ms (in the event of a fault) | RM17TE00response time
170 | RM17TE00 | Complementary | marking | CE | RM17TE00marking
171 | RM17TE00 | Complementary | overvoltage category | III conforming to IEC 60664-1 | RM17TE00overvoltage category
172 | RM17TE00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | RM17TE00insulation resistance
173 | RM17TE00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1 | RM17TE00[Ui] rated insulation voltage
174 | RM17TE00 | Complementary | supply frequency | 50/60 Hz +/- 10 % | RM17TE00supply frequency
175 | RM17TE00 | Complementary | operating position | Any position without derating | RM17TE00operating position
176 | RM17TE00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | RM17TE00connections - terminals
177 | RM17TE00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | RM17TE00tightening torque
178 | RM17TE00 | Complementary | housing material | Self-extinguishing plastic | RM17TE00housing material
179 | RM17TE00 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON | RM17TE00local signalling
180 | RM17TE00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | RM17TE00mounting support
181 | RM17TE00 | Complementary | electrical durability | 100000 cycles | RM17TE00electrical durability
182 | RM17TE00 | Complementary | mechanical durability | 30000000 cycles | RM17TE00mechanical durability
183 | RM17TE00 | Complementary | operating rate | <= 360 operations/hour full load | RM17TE00operating rate
184 | RM17TE00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | RM17TE00utilisation category
185 | RM17TE00 | Complementary | safety reliability data | MTTFd = 502.2 years B10d = 470000 | RM17TE00safety reliability data
186 | RM17TE00 | Complementary | width | 17.5 mm | RM17TE00width
187 | RM17TE00 | Complementary | net weight | 0.13 kg | RM17TE00net weight
188 | RM17TE00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | RM17TE00electromagnetic compatibility
189 | RM17TE00 | Environment | standards | EN/IEC 60255-1 | RM17TE00standards
190 | RM17TE00 | Environment | product certifications | GOST C-Tick CSA UL GL | RM17TE00product certifications
191 | RM17TE00 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | RM17TE00directives
192 | RM17TE00 | Environment | ambient air temperature for storage | -40…70 °C | RM17TE00ambient air temperature for storage
193 | RM17TE00 | Environment | ambient air temperature for operation | -20…50 °C | RM17TE00ambient air temperature for operation
194 | RM17TE00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30 | RM17TE00relative humidity
195 | RM17TE00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | RM17TE00vibration resistance
196 | RM17TE00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1 | RM17TE00shock resistance
197 | RM17TE00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | RM17TE00IP degree of protection
198 | RM17TE00 | Environment | pollution degree | 3 conforming to IEC 60664-1 | RM17TE00pollution degree
199 | RM17TE00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | RM17TE00dielectric test voltage
200 | RM17TE00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | RM17TE00non-dissipating shock wave
201 | RM17TE00 | Offer Sustainability | Sustainable offer status | Green Premium product | RM17TE00Sustainable offer status
202 | RM17TE00 | Offer Sustainability | REACh Regulation | REACh Declaration | RM17TE00REACh Regulation
203 | RM17TE00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RM17TE00EU RoHS Directive
204 | RM17TE00 | Offer Sustainability | Mercury free | Yes | RM17TE00Mercury free
205 | RM17TE00 | Offer Sustainability | RoHS exemption information | Yes | RM17TE00RoHS exemption information
206 | RM17TE00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RM17TE00China RoHS Regulation
207 | RM17TE00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RM17TE00Environmental Disclosure
208 | RM17TE00 | Offer Sustainability | Circularity Profile | End of Life Information | RM17TE00Circularity Profile
209 | RM17TE00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RM17TE00WEEE
210 | RM17TE00 | Contractual warranty | Warranty | 18 months | RM17TE00Warranty
211 | RE22R2CMR | Main | range of product | Zelio Time | RE22R2CMRrange of product
212 | RE22R2CMR | Main | product or component type | Modular timing relay | RE22R2CMRproduct or component type
213 | RE22R2CMR | Main | discrete output type | Relay | RE22R2CMRdiscrete output type
214 | RE22R2CMR | Main | device short name | RE22 | RE22R2CMRdevice short name
215 | RE22R2CMR | Main | nominal output current | 8 A | RE22R2CMRnominal output current
216 | RE22R2CMR | Complementary | contacts type and composition | 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free | RE22R2CMRcontacts type and composition
217 | RE22R2CMR | Complementary | time delay type | C | RE22R2CMRtime delay type
218 | RE22R2CMR | Complementary | time delay range | 10...100 s 3...30 h 1...10 s 3...30 s 30...300 h 0.3...3 s 0.05...1 s 30...300 min 30...300 s 3...30 min | RE22R2CMRtime delay range
219 | RE22R2CMR | Complementary | control type | Rotary knob Diagnostic button | RE22R2CMRcontrol type
220 | RE22R2CMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz | RE22R2CMR[Us] rated supply voltage
221 | RE22R2CMR | Complementary | Release input voltage | <= 2.4 V | RE22R2CMRRelease input voltage
222 | RE22R2CMR | Complementary | voltage range | 0.85...1.1 Us | RE22R2CMRvoltage range
223 | RE22R2CMR | Complementary | supply frequency | 50...60 Hz +/- 5 % | RE22R2CMRsupply frequency
224 | RE22R2CMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | RE22R2CMRconnections - terminals
225 | RE22R2CMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | RE22R2CMRtightening torque
226 | RE22R2CMR | Complementary | housing material | Self-extinguishing | RE22R2CMRhousing material
227 | RE22R2CMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1 | RE22R2CMRrepeat accuracy
228 | RE22R2CMR | Complementary | temperature drift | +/- 0.05 %/°C | RE22R2CMRtemperature drift
229 | RE22R2CMR | Complementary | voltage drift | +/- 0.2 %/V | RE22R2CMRvoltage drift
230 | RE22R2CMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | RE22R2CMRsetting accuracy of time delay
231 | RE22R2CMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms | RE22R2CMRControl signal pulse width
232 | RE22R2CMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1 | RE22R2CMRinsulation resistance
233 | RE22R2CMR | Complementary | Recovery time | 120 ms on de-energisation | RE22R2CMRRecovery time
234 | RE22R2CMR | Complementary | immunity to microbreaks | 10 ms | RE22R2CMRimmunity to microbreaks
235 | RE22R2CMR | Complementary | power consumption in VA | 3 VA at 240 V AC | RE22R2CMRpower consumption in VA
236 | RE22R2CMR | Complementary | power consumption in W | 1.5 W at 240 V DC | RE22R2CMRpower consumption in W
237 | RE22R2CMR | Complementary | switching capacity in VA | 2000 VA | RE22R2CMRswitching capacity in VA
238 | RE22R2CMR | Complementary | minimum switching current | 10 mA at 5 V DC | RE22R2CMRminimum switching current
239 | RE22R2CMR | Complementary | maximum switching current | 8 A | RE22R2CMRmaximum switching current
240 | RE22R2CMR | Complementary | maximum switching voltage | 250 V AC | RE22R2CMRmaximum switching voltage
241 | RE22R2CMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | RE22R2CMRelectrical durability
242 | RE22R2CMR | Complementary | mechanical durability | 10000000 cycles | RE22R2CMRmechanical durability
243 | RE22R2CMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | RE22R2CMRRated impulse withstand voltage
244 | RE22R2CMR | Complementary | Power on delay | 100 ms | RE22R2CMRPower on delay
245 | RE22R2CMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1 | RE22R2CMRcreepage distance
246 | RE22R2CMR | Complementary | overvoltage category | III conforming to IEC 60664-1 | RE22R2CMRovervoltage category
247 | RE22R2CMR | Complementary | safety reliability data | MTTFd = 251.1 years B10d = 230000 | RE22R2CMRsafety reliability data
248 | RE22R2CMR | Complementary | mounting position | Any position | RE22R2CMRmounting position
249 | RE22R2CMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715 | RE22R2CMRmounting support
250 | RE22R2CMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | RE22R2CMRstatus LED
251 | RE22R2CMR | Complementary | width | 22.5 mm | RE22R2CMRwidth
252 | RE22R2CMR | Complementary | net weight | 0.105 kg | RE22R2CMRnet weight
253 | RE22R2CMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | RE22R2CMRdielectric strength
254 | RE22R2CMR | Environment | standards | UL 508 IEC 61812-1 | RE22R2CMRstandards
255 | RE22R2CMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | RE22R2CMRdirectives
256 | RE22R2CMR | Environment | product certifications | CSA CCC RCM China RoHS CE GL UL EAC | RE22R2CMRproduct certifications
257 | RE22R2CMR | Environment | ambient air temperature for operation | -20…60 °C | RE22R2CMRambient air temperature for operation
258 | RE22R2CMR | Environment | ambient air temperature for storage | -40…70 °C | RE22R2CMRambient air temperature for storage
259 | RE22R2CMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | RE22R2CMRIP degree of protection
260 | RE22R2CMR | Environment | pollution degree | 3 conforming to IEC 60664-1 | RE22R2CMRpollution degree
261 | RE22R2CMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | RE22R2CMRvibration resistance
262 | RE22R2CMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | RE22R2CMRshock resistance
263 | RE22R2CMR | Environment | relative humidity | 95 % at 25…55 °C | RE22R2CMRrelative humidity
264 | RE22R2CMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | RE22R2CMRelectromagnetic compatibility
265 | RE22R2CMR | Offer Sustainability | Sustainable offer status | Green Premium product | RE22R2CMRSustainable offer status
266 | RE22R2CMR | Offer Sustainability | REACh Regulation | REACh Declaration | RE22R2CMRREACh Regulation
267 | RE22R2CMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RE22R2CMREU RoHS Directive
268 | RE22R2CMR | Offer Sustainability | Mercury free | Yes | RE22R2CMRMercury free
269 | RE22R2CMR | Offer Sustainability | RoHS exemption information | Yes | RE22R2CMRRoHS exemption information
270 | RE22R2CMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RE22R2CMRChina RoHS Regulation
271 | RE22R2CMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RE22R2CMREnvironmental Disclosure
272 | RE22R2CMR | Offer Sustainability | Circularity Profile | End of Life Information | RE22R2CMRCircularity Profile
273 | RMTJ60BD | Main | range of product | Zelio Analog | RMTJ60BDrange of product
274 | RMTJ60BD | Main | product or component type | Converter for thermocouples | RMTJ60BDproduct or component type
275 | RMTJ60BD | Main | analogue input type | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584 | RMTJ60BDanalogue input type
276 | RMTJ60BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | RMTJ60BDanalogue output type
277 | RMTJ60BD | Complementary | protection type | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output | RMTJ60BDprotection type
278 | RMTJ60BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | RMTJ60BDabnormal analogue output voltage
279 | RMTJ60BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken | RMTJ60BDabnormal analogue output current
280 | RMTJ60BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, non isolated | RMTJ60BD[Us] rated supply voltage
281 | RMTJ60BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output | RMTJ60BDcurrent consumption
282 | RMTJ60BD | Complementary | local signalling | LED (green)power ON: | RMTJ60BDlocal signalling
283 | RMTJ60BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C | RMTJ60BDmeasurement error
284 | RMTJ60BD | Complementary | repeat accuracy | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C | RMTJ60BDrepeat accuracy
285 | RMTJ60BD | Complementary | temperature coefficient | 200 ppm/°C | RMTJ60BDtemperature coefficient
286 | RMTJ60BD | Complementary | cold junction compensation | Built-in, measurement: between 0 and 60 °C | RMTJ60BDcold junction compensation
287 | RMTJ60BD | Complementary | clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm² | RMTJ60BDclamping connection capacity
288 | RMTJ60BD | Complementary | tightening torque | 0.6…1.1 N.m | RMTJ60BDtightening torque
289 | RMTJ60BD | Complementary | marking | CE | RMTJ60BDmarking
290 | RMTJ60BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | RMTJ60BDsurge withstand
291 | RMTJ60BD | Complementary | [Ui] rated insulation voltage | 2 kV | RMTJ60BD[Ui] rated insulation voltage
292 | RMTJ60BD | Complementary | fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail) | RMTJ60BDfixing mode
293 | RMTJ60BD | Complementary | safety reliability data | B10d = 45447 MTTFd = 49.2 years | RMTJ60BDsafety reliability data
294 | RMTJ60BD | Complementary | net weight | 0.12 kg | RMTJ60BDnet weight
295 | RMTJ60BD | Environment | standards | IEC 60584-1 IEC 60947-1 | RMTJ60BDstandards
296 | RMTJ60BD | Environment | product certifications | CSA GL UL | RMTJ60BDproduct certifications
297 | RMTJ60BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing) | RMTJ60BDIP degree of protection
298 | RMTJ60BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | RMTJ60BDfire resistance
299 | RMTJ60BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27 | RMTJ60BDshock resistance
300 | RMTJ60BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | RMTJ60BDvibration resistance
301 | RMTJ60BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3 | RMTJ60BDresistance to electrostatic discharge
302 | RMTJ60BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | RMTJ60BDresistance to fast transients
303 | RMTJ60BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B CISPR 11 | RMTJ60BDdisturbance radiated/conducted
304 | RMTJ60BD | Environment | ambient air temperature for storage | -40…85 °C | RMTJ60BDambient air temperature for storage
305 | RMTJ60BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | RMTJ60BDambient air temperature for operation
306 | RMTJ60BD | Environment | pollution degree | 2 conforming to IEC 60664-1 | RMTJ60BDpollution degree
307 | RMTJ60BD | Packing Units | Package 1 Weight | 0.101 kg | RMTJ60BDPackage 1 Weight
308 | RMTJ60BD | Packing Units | Package 1 Height | 0.270 dm | RMTJ60BDPackage 1 Height
309 | RMTJ60BD | Packing Units | Package 1 width | 0.820 dm | RMTJ60BDPackage 1 width
310 | RMTJ60BD | Packing Units | Package 1 Length | 0.850 dm | RMTJ60BDPackage 1 Length
311 | RMTJ60BD | Offer Sustainability | Sustainable offer status | Green Premium product | RMTJ60BDSustainable offer status
312 | RMTJ60BD | Offer Sustainability | REACh Regulation | REACh Declaration | RMTJ60BDREACh Regulation
313 | RMTJ60BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RMTJ60BDEU RoHS Directive
314 | RMTJ60BD | Offer Sustainability | Mercury free | Yes | RMTJ60BDMercury free
315 | RMTJ60BD | Offer Sustainability | RoHS exemption information | Yes | RMTJ60BDRoHS exemption information
316 | RMTJ60BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RMTJ60BDChina RoHS Regulation
317 | RMTJ60BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RMTJ60BDEnvironmental Disclosure
318 | RMTJ60BD | Offer Sustainability | Circularity Profile | End of Life Information | RMTJ60BDCircularity Profile
319 | RMTJ60BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RMTJ60BDWEEE
320 | RMTJ60BD | Contractual warranty | Warranty | 18 months | RMTJ60BDWarranty
321 | XVDLS37 | Main | range of product | Harmony XVD Optimum | XVDLS37range of product
322 | XVDLS37 | Main | product or component type | Complete miniature beacon | XVDLS37product or component type
323 | XVDLS37 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit | XVDLS37beacon or indicator bank unit type
324 | XVDLS37 | Main | signalling type | Steady | XVDLS37signalling type
325 | XVDLS37 | Main | mounting diameter | 45 mm | XVDLS37mounting diameter
326 | XVDLS37 | Main | component name | XVDLS | XVDLS37component name
327 | XVDLS37 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | XVDLS37material
328 | XVDLS37 | Main | light source | Bulb not included, clear | XVDLS37light source
329 | XVDLS37 | Main | bulb type | Incandescent with BA 15d base | XVDLS37bulb type
330 | XVDLS37 | Main | [Us] rated supply voltage | <= 230 V | XVDLS37[Us] rated supply voltage
331 | XVDLS37 | Main | maximum power dissipation in W | 5 W | XVDLS37maximum power dissipation in W
332 | XVDLS37 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | XVDLS37connections - terminals
333 | XVDLS37 | Complementary | cable entry | 1 entry tapped for Pg 7 | XVDLS37cable entry
334 | XVDLS37 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1 | XVDLS37[Ui] rated insulation voltage
335 | XVDLS37 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1 | XVDLS37[Uimp] rated impulse withstand voltage
336 | XVDLS37 | Complementary | CAD overall width | 45 mm | XVDLS37CAD overall width
337 | XVDLS37 | Complementary | CAD overall height | 104 mm | XVDLS37CAD overall height
338 | XVDLS37 | Complementary | CAD overall depth | 45 mm | XVDLS37CAD overall depth
339 | XVDLS37 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW | XVDLS37terminals description ISO n°1
340 | XVDLS37 | Complementary | net weight | 0.08 kg | XVDLS37net weight
341 | XVDLS37 | Environment | product certifications | CSA UL | XVDLS37product certifications
342 | XVDLS37 | Environment | standards | EN/IEC 60947-5-1 | XVDLS37standards
343 | XVDLS37 | Environment | protective treatment | TC | XVDLS37protective treatment
344 | XVDLS37 | Environment | ambient air temperature for operation | -25…70 °C | XVDLS37ambient air temperature for operation
345 | XVDLS37 | Environment | ambient air temperature for storage | -40…70 °C | XVDLS37ambient air temperature for storage
346 | XVDLS37 | Environment | electrical shock protection class | Class II conforming to IEC 60536 | XVDLS37electrical shock protection class
347 | XVDLS37 | Environment | IP degree of protection | IP40 conforming to IEC 60529 | XVDLS37IP degree of protection
348 | XVDLS37 | Packing Units | Package 1 Weight | 0.101 kg | XVDLS37Package 1 Weight
349 | XVDLS37 | Offer Sustainability | Sustainable offer status | Green Premium product | XVDLS37Sustainable offer status
350 | XVDLS37 | Offer Sustainability | REACh Regulation | REACh Declaration | XVDLS37REACh Regulation
351 | XVDLS37 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | XVDLS37EU RoHS Directive
352 | XVDLS37 | Offer Sustainability | Mercury free | Yes | XVDLS37Mercury free
353 | XVDLS37 | Offer Sustainability | RoHS exemption information | Yes | XVDLS37RoHS exemption information
354 | XVDLS37 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | XVDLS37China RoHS Regulation
355 | XVDLS37 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | XVDLS37Environmental Disclosure
356 | XVDLS37 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | XVDLS37WEEE
357 | XVDLS37 | Contractual warranty | Warranty | 18 months | XVDLS37Warranty
358 | XVDLS38 | Main | range of product | Harmony XVD Optimum | XVDLS38range of product
359 | XVDLS38 | Main | product or component type | Complete miniature beacon | XVDLS38product or component type
360 | XVDLS38 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit | XVDLS38beacon or indicator bank unit type
361 | XVDLS38 | Main | signalling type | Steady | XVDLS38signalling type
362 | XVDLS38 | Main | mounting diameter | 45 mm | XVDLS38mounting diameter
363 | XVDLS38 | Main | component name | XVDLS | XVDLS38component name
364 | XVDLS38 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | XVDLS38material
365 | XVDLS38 | Main | light source | Bulb not included, yellow | XVDLS38light source
366 | XVDLS38 | Main | bulb type | Incandescent with BA 15d base | XVDLS38bulb type
367 | XVDLS38 | Main | [Us] rated supply voltage | <= 230 V | XVDLS38[Us] rated supply voltage
368 | XVDLS38 | Main | maximum power dissipation in W | 5 W | XVDLS38maximum power dissipation in W
369 | XVDLS38 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | XVDLS38connections - terminals
370 | XVDLS38 | Complementary | cable entry | 1 entry tapped for Pg 7 | XVDLS38cable entry
371 | XVDLS38 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1 | XVDLS38[Ui] rated insulation voltage
372 | XVDLS38 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1 | XVDLS38[Uimp] rated impulse withstand voltage
373 | XVDLS38 | Complementary | CAD overall width | 45 mm | XVDLS38CAD overall width
374 | XVDLS38 | Complementary | CAD overall height | 104 mm | XVDLS38CAD overall height
375 | XVDLS38 | Complementary | CAD overall depth | 45 mm | XVDLS38CAD overall depth
376 | XVDLS38 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND | XVDLS38terminals description ISO n°1
377 | XVDLS38 | Complementary | net weight | 0.08 kg | XVDLS38net weight
378 | XVDLS38 | Environment | product certifications | CSA UL | XVDLS38product certifications
379 | XVDLS38 | Environment | standards | EN/IEC 60947-5-1 | XVDLS38standards
380 | XVDLS38 | Environment | protective treatment | TC | XVDLS38protective treatment
381 | XVDLS38 | Environment | ambient air temperature for operation | -25…70 °C | XVDLS38ambient air temperature for operation
382 | XVDLS38 | Environment | ambient air temperature for storage | -40…70 °C | XVDLS38ambient air temperature for storage
383 | XVDLS38 | Environment | electrical shock protection class | Class II conforming to IEC 60536 | XVDLS38electrical shock protection class
384 | XVDLS38 | Environment | IP degree of protection | IP40 conforming to IEC 60529 | XVDLS38IP degree of protection
385 | XVDLS38 | Packing Units | Package 1 Weight | 0.100 kg | XVDLS38Package 1 Weight
386 | XVDLS38 | Offer Sustainability | Sustainable offer status | Green Premium product | XVDLS38Sustainable offer status
387 | XVDLS38 | Offer Sustainability | REACh Regulation | REACh Declaration | XVDLS38REACh Regulation
388 | XVDLS38 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | XVDLS38EU RoHS Directive
389 | XVDLS38 | Offer Sustainability | Mercury free | Yes | XVDLS38Mercury free
390 | XVDLS38 | Offer Sustainability | RoHS exemption information | Yes | XVDLS38RoHS exemption information
391 | XVDLS38 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | XVDLS38China RoHS Regulation
392 | XVDLS38 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | XVDLS38Environmental Disclosure
393 | XVDLS38 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | XVDLS38WEEE
394 | XVDLS38 | Contractual warranty | Warranty | 18 months | XVDLS38Warranty
395 | RHT428B | Main | range of product | Zelio Relay | RHT428Brange of product
396 | RHT428B | Main | product or component type | Plug-in relay Timing relay | RHT428Bproduct or component type
397 | RHT428B | Main | device short name | RHT | RHT428Bdevice short name
398 | RHT428B | Main | contacts type and composition | 4 C/O | RHT428Bcontacts type and composition
399 | RHT428B | Main | contact operation | Low level | RHT428Bcontact operation
400 | RHT428B | Main | [Uc] control circuit voltage | 24 V AC/DC 50/60 Hz | RHT428B[Uc] control circuit voltage
401 | RHT428B | Main | time delay type | On-delay | RHT428Btime delay type
402 | RHT428B | Main | time delay range | 15...300 s 0.2...3 s 1.5...30 s | RHT428Btime delay range
403 | RHT428B | Main | [Ithe] conventional enclosed thermal current | 1 A 40 °C | RHT428B[Ithe] conventional enclosed thermal current
404 | RHT428B | Main | status LED | With | RHT428Bstatus LED
405 | RHT428B | Main | control type | Selector switch | RHT428Bcontrol type
406 | RHT428B | Main | coil interference suppression | With | RHT428Bcoil interference suppression
407 | RHT428B | Complementary | [Ui] rated insulation voltage | 250 V | RHT428B[Ui] rated insulation voltage
408 | RHT428B | Complementary | operating position | Any position | RHT428Boperating position
409 | RHT428B | Complementary | minimum switching capacity | 50 mVA at 1 mA, 1 V | RHT428Bminimum switching capacity
410 | RHT428B | Complementary | contact bounce time | <= 10 ms | RHT428Bcontact bounce time
411 | RHT428B | Complementary | maximum voltage drop | <100 V for 3 A at 24 V | RHT428Bmaximum voltage drop
412 | RHT428B | Complementary | average resistance | 30 mOhm at 20 °C | RHT428Baverage resistance
413 | RHT428B | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | RHT428Bswitching time
414 | RHT428B | Complementary | average coil consumption | 2.5 W at 20 °C | RHT428Baverage coil consumption
415 | RHT428B | Complementary | average coil consumption in VA | 2.9 at 20 °C | RHT428Baverage coil consumption in VA
416 | RHT428B | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255 | RHT428Bcontrol circuit voltage limits
417 | RHT428B | Complementary | mechanical durability | 20000000 cycles | RHT428Bmechanical durability
418 | RHT428B | Complementary | repeat accuracy | +/- 1 % | RHT428Brepeat accuracy
419 | RHT428B | Complementary | setting accuracy of time delay | +/- 15 % of full scale | RHT428Bsetting accuracy of time delay
420 | RHT428B | Complementary | reset time | 100 ms | RHT428Breset time
421 | RHT428B | Complementary | CAD overall width | 33 mm | RHT428BCAD overall width
422 | RHT428B | Complementary | CAD overall height | 43 mm | RHT428BCAD overall height
423 | RHT428B | Complementary | CAD overall depth | 108 mm | RHT428BCAD overall depth
424 | RHT428B | Complementary | terminals description ISO n°1 | (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC | RHT428Bterminals description ISO n°1
425 | RHT428B | Complementary | net weight | 0.13 kg | RHT428Bnet weight
426 | RHT428B | Environment | standards | IEC 60255 NF C 45-250 VDE 0435 | RHT428Bstandards
427 | RHT428B | Environment | product certifications | USSR EDF ASE BV CSA | RHT428Bproduct certifications
428 | RHT428B | Environment | protective treatment | TC | RHT428Bprotective treatment
429 | RHT428B | Environment | dielectric strength | 2500 V | RHT428Bdielectric strength
430 | RHT428B | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255 | RHT428Bambient air temperature for operation
431 | RHT428B | Environment | ambient air temperature for storage | -40…70 °C | RHT428Bambient air temperature for storage
432 | RHT428B | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | RHT428Bvibration resistance
433 | RHT428B | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608 | RHT428Bshock resistance
434 | RHT428B | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay | RHT428Bimmunity to microbreaks
435 | RHT428B | Contractual warranty | Warranty | 18 months | RHT428BWarranty
436 | RHT418BE | Main | range of product | Zelio Relay | RHT418BErange of product
437 | RHT418BE | Main | product or component type | Timing relay Plug-in relay | RHT418BEproduct or component type
438 | RHT418BE | Main | device short name | RHT | RHT418BEdevice short name
439 | RHT418BE | Main | contacts type and composition | 4 C/O | RHT418BEcontacts type and composition
440 | RHT418BE | Main | contact operation | Standard | RHT418BEcontact operation
441 | RHT418BE | Main | [Uc] control circuit voltage | 27 V AC/DC 50/60 Hz | RHT418BE[Uc] control circuit voltage
442 | RHT418BE | Main | time delay type | On-delay | RHT418BEtime delay type
443 | RHT418BE | Main | time delay range | 0.2...3 s 15...300 s 1.5...30 s | RHT418BEtime delay range
444 | RHT418BE | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C | RHT418BE[Ithe] conventional enclosed thermal current
445 | RHT418BE | Main | status LED | With | RHT418BEstatus LED
446 | RHT418BE | Main | control type | Selector switch | RHT418BEcontrol type
447 | RHT418BE | Main | coil interference suppression | With | RHT418BEcoil interference suppression
448 | RHT418BE | Complementary | [Ui] rated insulation voltage | 250 V | RHT418BE[Ui] rated insulation voltage
449 | RHT418BE | Complementary | operating position | Any position | RHT418BEoperating position
450 | RHT418BE | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V | RHT418BEminimum switching capacity
451 | RHT418BE | Complementary | contact bounce time | <= 10 ms | RHT418BEcontact bounce time
452 | RHT418BE | Complementary | maximum voltage drop | <100 V for 3 A at 24 V | RHT418BEmaximum voltage drop
453 | RHT418BE | Complementary | average resistance | 30 mOhm at 20 °C | RHT418BEaverage resistance
454 | RHT418BE | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | RHT418BEswitching time
455 | RHT418BE | Complementary | average coil consumption | 2.5 W at 20 °C | RHT418BEaverage coil consumption
456 | RHT418BE | Complementary | average coil consumption in VA | 2.9 at 20 °C | RHT418BEaverage coil consumption in VA
457 | RHT418BE | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255 | RHT418BEcontrol circuit voltage limits
458 | RHT418BE | Complementary | mechanical durability | 20000000 cycles | RHT418BEmechanical durability
459 | RHT418BE | Complementary | repeat accuracy | +/- 1 % | RHT418BErepeat accuracy
460 | RHT418BE | Complementary | setting accuracy of time delay | +/- 15 % of full scale | RHT418BEsetting accuracy of time delay
461 | RHT418BE | Complementary | reset time | 100 ms | RHT418BEreset time
462 | RHT418BE | Complementary | CAD overall width | 33 mm | RHT418BECAD overall width
463 | RHT418BE | Complementary | CAD overall height | 43 mm | RHT418BECAD overall height
464 | RHT418BE | Complementary | CAD overall depth | 108 mm | RHT418BECAD overall depth
465 | RHT418BE | Complementary | terminals description ISO n°1 | (31-32-34)OC (41-42-44)OC (11-12-14)OC (21-22-24)OC (A1-A2)CO | RHT418BEterminals description ISO n°1
466 | RHT418BE | Complementary | net weight | 0.13 kg | RHT418BEnet weight
467 | RHT418BE | Environment | standards | IEC 60255 NF C 45-250 VDE 0435 | RHT418BEstandards
468 | RHT418BE | Environment | product certifications | ASE EDF USSR BV CSA | RHT418BEproduct certifications
469 | RHT418BE | Environment | protective treatment | TC | RHT418BEprotective treatment
470 | RHT418BE | Environment | dielectric strength | 2500 V | RHT418BEdielectric strength
471 | RHT418BE | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255 | RHT418BEambient air temperature for operation
472 | RHT418BE | Environment | ambient air temperature for storage | -40…70 °C | RHT418BEambient air temperature for storage
473 | RHT418BE | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | RHT418BEvibration resistance
474 | RHT418BE | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608 | RHT418BEshock resistance
475 | RHT418BE | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay | RHT418BEimmunity to microbreaks
476 | RHT418BE | Contractual warranty | Warranty | 18 months | RHT418BEWarranty
477 | RSB1A160M7S | Main | range of product | Zelio Relay | RSB1A160M7Srange of product
478 | RSB1A160M7S | Main | series name | Interface relay | RSB1A160M7Sseries name
479 | RSB1A160M7S | Main | product or component type | Plug-in relay | RSB1A160M7Sproduct or component type
480 | RSB1A160M7S | Main | device short name | RSB | RSB1A160M7Sdevice short name
481 | RSB1A160M7S | Main | contacts type and composition | 1 C/O | RSB1A160M7Scontacts type and composition
482 | RSB1A160M7S | Main | contact operation | Standard | RSB1A160M7Scontact operation
483 | RSB1A160M7S | Main | [Uc] control circuit voltage | 220 V AC | RSB1A160M7S[Uc] control circuit voltage
484 | RSB1A160M7S | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C | RSB1A160M7S[Ithe] conventional enclosed thermal current
485 | RSB1A160M7S | Main | status LED | Without | RSB1A160M7Sstatus LED
486 | RSB1A160M7S | Complementary | shape of pin | Flat | RSB1A160M7Sshape of pin
487 | RSB1A160M7S | Complementary | average coil resistance | 35500 Ohm network: AC at 20 °C +/- 15 % | RSB1A160M7Saverage coil resistance
488 | RSB1A160M7S | Complementary | [Ue] rated operational voltage | 176...264 V AC 50 Hz 187...264 V AC 60 Hz | RSB1A160M7S[Ue] rated operational voltage
489 | RSB1A160M7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | RSB1A160M7S[Ui] rated insulation voltage
490 | RSB1A160M7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV | RSB1A160M7S[Uimp] rated impulse withstand voltage
491 | RSB1A160M7S | Complementary | contacts material | Silver alloy (Ag/Ni) | RSB1A160M7Scontacts material
492 | RSB1A160M7S | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | RSB1A160M7S[Ie] rated operational current
493 | RSB1A160M7S | Complementary | minimum switching current | 5 mA | RSB1A160M7Sminimum switching current
494 | RSB1A160M7S | Complementary | maximum switching voltage | 300 V DC 400 V AC | RSB1A160M7Smaximum switching voltage
495 | RSB1A160M7S | Complementary | minimum switching voltage | 5 V | RSB1A160M7Sminimum switching voltage
496 | RSB1A160M7S | Complementary | maximum switching capacity | 4000 VA AC 448 W DC | RSB1A160M7Smaximum switching capacity
497 | RSB1A160M7S | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC | RSB1A160M7Sresistive rated load
498 | RSB1A160M7S | Complementary | minimum switching capacity | 300 mW at 5 mA | RSB1A160M7Sminimum switching capacity
499 | RSB1A160M7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | RSB1A160M7Soperating rate
500 | RSB1A160M7S | Complementary | mechanical durability | 30000000 cycles | RSB1A160M7Smechanical durability
501 | RSB1A160M7S | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | RSB1A160M7Selectrical durability
502 | RSB1A160M7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | RSB1A160M7Soperating time
503 | RSB1A160M7S | Complementary | marking | CE | RSB1A160M7Smarking
504 | RSB1A160M7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz | RSB1A160M7Saverage coil consumption
505 | RSB1A160M7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC | RSB1A160M7Sdrop-out voltage threshold
506 | RSB1A160M7S | Complementary | safety reliability data | B10d = 100000 | RSB1A160M7Ssafety reliability data
507 | RSB1A160M7S | Complementary | protection category | RT I | RSB1A160M7Sprotection category
508 | RSB1A160M7S | Complementary | operating position | Any position | RSB1A160M7Soperating position
509 | RSB1A160M7S | Complementary | sale per indivisible quantity | 10 | RSB1A160M7Ssale per indivisible quantity
510 | RSB1A160M7S | Complementary | device presentation | Complete product | RSB1A160M7Sdevice presentation
511 | RSB1A160M7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | RSB1A160M7Sdielectric strength
512 | RSB1A160M7S | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | RSB1A160M7Sstandards
513 | RSB1A160M7S | Environment | product certifications | CSA UL GOST | RSB1A160M7Sproduct certifications
514 | RSB1A160M7S | Environment | ambient air temperature for storage | -40…85 °C | RSB1A160M7Sambient air temperature for storage
515 | RSB1A160M7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | RSB1A160M7Svibration resistance
516 | RSB1A160M7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | RSB1A160M7SIP degree of protection
517 | RSB1A160M7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | RSB1A160M7Sshock resistance
518 | RSB1A160M7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | RSB1A160M7Sambient air temperature for operation
519 | RSB1A160M7S | Offer Sustainability | Sustainable offer status | Green Premium product | RSB1A160M7SSustainable offer status
520 | RSB1A160M7S | Offer Sustainability | REACh free of SVHC | Yes | RSB1A160M7SREACh free of SVHC
521 | RSB1A160M7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RSB1A160M7SEU RoHS Directive
522 | RSB1A160M7S | Offer Sustainability | Toxic heavy metal free | Yes | RSB1A160M7SToxic heavy metal free
523 | RSB1A160M7S | Offer Sustainability | Mercury free | Yes | RSB1A160M7SMercury free
524 | RSB1A160M7S | Offer Sustainability | RoHS exemption information | Yes | RSB1A160M7SRoHS exemption information
525 | RSB1A160M7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RSB1A160M7SChina RoHS Regulation
526 | RSB1A160M7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RSB1A160M7SEnvironmental Disclosure
527 | RSB1A160M7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RSB1A160M7SWEEE
528 | RSB1A160M7S | Contractual warranty | Warranty | 18 months | RSB1A160M7SWarranty
529 | RSB1A160NDS | Main | range of product | Zelio Relay | RSB1A160NDSrange of product
530 | RSB1A160NDS | Main | series name | Interface relay | RSB1A160NDSseries name
531 | RSB1A160NDS | Main | product or component type | Plug-in relay | RSB1A160NDSproduct or component type
532 | RSB1A160NDS | Main | device short name | RSB | RSB1A160NDSdevice short name
533 | RSB1A160NDS | Main | contacts type and composition | 1 C/O | RSB1A160NDScontacts type and composition
534 | RSB1A160NDS | Main | contact operation | Standard | RSB1A160NDScontact operation
535 | RSB1A160NDS | Main | [Uc] control circuit voltage | 60 V DC | RSB1A160NDS[Uc] control circuit voltage
536 | RSB1A160NDS | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C | RSB1A160NDS[Ithe] conventional enclosed thermal current
537 | RSB1A160NDS | Main | status LED | Without | RSB1A160NDSstatus LED
538 | RSB1A160NDS | Complementary | shape of pin | Flat | RSB1A160NDSshape of pin
539 | RSB1A160NDS | Complementary | average coil resistance | 7500 Ohm network: DC at 20 °C +/- 10 % | RSB1A160NDSaverage coil resistance
540 | RSB1A160NDS | Complementary | [Ue] rated operational voltage | 48...66 V DC | RSB1A160NDS[Ue] rated operational voltage
541 | RSB1A160NDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | RSB1A160NDS[Ui] rated insulation voltage
542 | RSB1A160NDS | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5 | RSB1A160NDS[Uimp] rated impulse withstand voltage
543 | RSB1A160NDS | Complementary | contacts material | Silver alloy (Ag/Ni) | RSB1A160NDScontacts material
544 | RSB1A160NDS | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | RSB1A160NDS[Ie] rated operational current
545 | RSB1A160NDS | Complementary | minimum switching current | 5 mA | RSB1A160NDSminimum switching current
546 | RSB1A160NDS | Complementary | maximum switching voltage | 300 V DC 400 V AC | RSB1A160NDSmaximum switching voltage
547 | RSB1A160NDS | Complementary | minimum switching voltage | 5 V | RSB1A160NDSminimum switching voltage
548 | RSB1A160NDS | Complementary | maximum switching capacity | 4000 VA AC 448 W DC | RSB1A160NDSmaximum switching capacity
549 | RSB1A160NDS | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC | RSB1A160NDSresistive rated load
550 | RSB1A160NDS | Complementary | minimum switching capacity | 300 mW at 5 mA | RSB1A160NDSminimum switching capacity
551 | RSB1A160NDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | RSB1A160NDSoperating rate
552 | RSB1A160NDS | Complementary | mechanical durability | 30000000 cycles | RSB1A160NDSmechanical durability
553 | RSB1A160NDS | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | RSB1A160NDSelectrical durability
554 | RSB1A160NDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | RSB1A160NDSoperating time
555 | RSB1A160NDS | Complementary | marking | CE | RSB1A160NDSmarking
556 | RSB1A160NDS | Complementary | average coil consumption | 0.45 W DC | RSB1A160NDSaverage coil consumption
557 | RSB1A160NDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC | RSB1A160NDSdrop-out voltage threshold
558 | RSB1A160NDS | Complementary | safety reliability data | B10d = 100000 | RSB1A160NDSsafety reliability data
559 | RSB1A160NDS | Complementary | protection category | RT I | RSB1A160NDSprotection category
560 | RSB1A160NDS | Complementary | operating position | Any position | RSB1A160NDSoperating position
561 | RSB1A160NDS | Complementary | sale per indivisible quantity | 10 | RSB1A160NDSsale per indivisible quantity
562 | RSB1A160NDS | Complementary | device presentation | Complete product | RSB1A160NDSdevice presentation
563 | RSB1A160NDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | RSB1A160NDSdielectric strength
564 | RSB1A160NDS | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | RSB1A160NDSstandards
565 | RSB1A160NDS | Environment | product certifications | CSA UL GOST | RSB1A160NDSproduct certifications
566 | RSB1A160NDS | Environment | ambient air temperature for storage | -40…85 °C | RSB1A160NDSambient air temperature for storage
567 | RSB1A160NDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | RSB1A160NDSvibration resistance
568 | RSB1A160NDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | RSB1A160NDSIP degree of protection
569 | RSB1A160NDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | RSB1A160NDSshock resistance
570 | RSB1A160NDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | RSB1A160NDSambient air temperature for operation
571 | RSB1A160NDS | Contractual warranty | Warranty | 18 months | RSB1A160NDSWarranty
572 | RSB2A080P7S | Main | range of product | Zelio Relay | RSB2A080P7Srange of product
573 | RSB2A080P7S | Main | series name | Interface relay | RSB2A080P7Sseries name
574 | RSB2A080P7S | Main | product or component type | Plug-in relay | RSB2A080P7Sproduct or component type
575 | RSB2A080P7S | Main | device short name | RSB | RSB2A080P7Sdevice short name
576 | RSB2A080P7S | Main | contacts type and composition | 2 C/O | RSB2A080P7Scontacts type and composition
577 | RSB2A080P7S | Main | contact operation | Standard | RSB2A080P7Scontact operation
578 | RSB2A080P7S | Main | [Uc] control circuit voltage | 230 V AC | RSB2A080P7S[Uc] control circuit voltage
579 | RSB2A080P7S | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C | RSB2A080P7S[Ithe] conventional enclosed thermal current
580 | RSB2A080P7S | Main | status LED | Without | RSB2A080P7Sstatus LED
581 | RSB2A080P7S | Main | control type | Without push-button | RSB2A080P7Scontrol type
582 | RSB2A080P7S | Complementary | shape of pin | Flat | RSB2A080P7Sshape of pin
583 | RSB2A080P7S | Complementary | average coil resistance | 38500 Ohm network: AC at 20 °C +/- 15 % | RSB2A080P7Saverage coil resistance
584 | RSB2A080P7S | Complementary | [Ue] rated operational voltage | 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz | RSB2A080P7S[Ue] rated operational voltage
585 | RSB2A080P7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | RSB2A080P7S[Ui] rated insulation voltage
586 | RSB2A080P7S | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5 | RSB2A080P7S[Uimp] rated impulse withstand voltage
587 | RSB2A080P7S | Complementary | contacts material | Silver alloy (Ag/Ni) | RSB2A080P7Scontacts material
588 | RSB2A080P7S | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | RSB2A080P7S[Ie] rated operational current
589 | RSB2A080P7S | Complementary | minimum switching current | 5 mA | RSB2A080P7Sminimum switching current
590 | RSB2A080P7S | Complementary | maximum switching voltage | 300 V DC 400 V AC | RSB2A080P7Smaximum switching voltage
591 | RSB2A080P7S | Complementary | minimum switching voltage | 5 V | RSB2A080P7Sminimum switching voltage
592 | RSB2A080P7S | Complementary | maximum switching capacity | 2000 VA AC 224 W DC | RSB2A080P7Smaximum switching capacity
593 | RSB2A080P7S | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC | RSB2A080P7Sresistive rated load
594 | RSB2A080P7S | Complementary | minimum switching capacity | 300 mW at 5 mA | RSB2A080P7Sminimum switching capacity
595 | RSB2A080P7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | RSB2A080P7Soperating rate
596 | RSB2A080P7S | Complementary | mechanical durability | 30000000 cycles | RSB2A080P7Smechanical durability
597 | RSB2A080P7S | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | RSB2A080P7Selectrical durability
598 | RSB2A080P7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | RSB2A080P7Soperating time
599 | RSB2A080P7S | Complementary | marking | CE | RSB2A080P7Smarking
600 | RSB2A080P7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz | RSB2A080P7Saverage coil consumption
601 | RSB2A080P7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC | RSB2A080P7Sdrop-out voltage threshold
602 | RSB2A080P7S | Complementary | safety reliability data | B10d = 100000 | RSB2A080P7Ssafety reliability data
603 | RSB2A080P7S | Complementary | protection category | RT I | RSB2A080P7Sprotection category
604 | RSB2A080P7S | Complementary | operating position | Any position | RSB2A080P7Soperating position
605 | RSB2A080P7S | Complementary | sale per indivisible quantity | 10 | RSB2A080P7Ssale per indivisible quantity
606 | RSB2A080P7S | Complementary | device presentation | Complete product | RSB2A080P7Sdevice presentation
607 | RSB2A080P7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | RSB2A080P7Sdielectric strength
608 | RSB2A080P7S | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | RSB2A080P7Sstandards
609 | RSB2A080P7S | Environment | product certifications | GOST CSA UL | RSB2A080P7Sproduct certifications
610 | RSB2A080P7S | Environment | ambient air temperature for storage | -40…85 °C | RSB2A080P7Sambient air temperature for storage
611 | RSB2A080P7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | RSB2A080P7Svibration resistance
612 | RSB2A080P7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | RSB2A080P7SIP degree of protection
613 | RSB2A080P7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | RSB2A080P7Sshock resistance
614 | RSB2A080P7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | RSB2A080P7Sambient air temperature for operation
615 | RSB2A080P7S | Offer Sustainability | Sustainable offer status | Green Premium product | RSB2A080P7SSustainable offer status
616 | RSB2A080P7S | Offer Sustainability | REACh free of SVHC | Yes | RSB2A080P7SREACh free of SVHC
617 | RSB2A080P7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RSB2A080P7SEU RoHS Directive
618 | RSB2A080P7S | Offer Sustainability | Toxic heavy metal free | Yes | RSB2A080P7SToxic heavy metal free
619 | RSB2A080P7S | Offer Sustainability | Mercury free | Yes | RSB2A080P7SMercury free
620 | RSB2A080P7S | Offer Sustainability | RoHS exemption information | Yes | RSB2A080P7SRoHS exemption information
621 | RSB2A080P7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RSB2A080P7SChina RoHS Regulation
622 | RSB2A080P7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RSB2A080P7SEnvironmental Disclosure
623 | RSB2A080P7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RSB2A080P7SWEEE
624 | RSB2A080P7S | Contractual warranty | Warranty | 18 months | RSB2A080P7SWarranty
625 | RSB2A080RDS | Main | range of product | Zelio Relay | RSB2A080RDSrange of product
626 | RSB2A080RDS | Main | series name | Interface relay | RSB2A080RDSseries name
627 | RSB2A080RDS | Main | product or component type | Plug-in relay | RSB2A080RDSproduct or component type
628 | RSB2A080RDS | Main | device short name | RSB | RSB2A080RDSdevice short name
629 | RSB2A080RDS | Main | contacts type and composition | 2 C/O | RSB2A080RDScontacts type and composition
630 | RSB2A080RDS | Main | contact operation | Standard | RSB2A080RDScontact operation
631 | RSB2A080RDS | Main | [Uc] control circuit voltage | 6 V DC | RSB2A080RDS[Uc] control circuit voltage
632 | RSB2A080RDS | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C | RSB2A080RDS[Ithe] conventional enclosed thermal current
633 | RSB2A080RDS | Main | status LED | Without | RSB2A080RDSstatus LED
634 | RSB2A080RDS | Complementary | shape of pin | Flat | RSB2A080RDSshape of pin
635 | RSB2A080RDS | Complementary | average coil resistance | 90 Ohm network: DC at 20 °C +/- 10 % | RSB2A080RDSaverage coil resistance
636 | RSB2A080RDS | Complementary | [Ue] rated operational voltage | 4.8...6.6 V DC | RSB2A080RDS[Ue] rated operational voltage
637 | RSB2A080RDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | RSB2A080RDS[Ui] rated insulation voltage
638 | RSB2A080RDS | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV | RSB2A080RDS[Uimp] rated impulse withstand voltage
639 | RSB2A080RDS | Complementary | contacts material | Silver alloy (Ag/Ni) | RSB2A080RDScontacts material
640 | RSB2A080RDS | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | RSB2A080RDS[Ie] rated operational current
641 | RSB2A080RDS | Complementary | minimum switching current | 5 mA | RSB2A080RDSminimum switching current
642 | RSB2A080RDS | Complementary | maximum switching voltage | 300 V DC 400 V AC | RSB2A080RDSmaximum switching voltage
643 | RSB2A080RDS | Complementary | minimum switching voltage | 5 V | RSB2A080RDSminimum switching voltage
644 | RSB2A080RDS | Complementary | maximum switching capacity | 2000 VA AC 224 W DC | RSB2A080RDSmaximum switching capacity
645 | RSB2A080RDS | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC | RSB2A080RDSresistive rated load
646 | RSB2A080RDS | Complementary | minimum switching capacity | 300 mW at 5 mA | RSB2A080RDSminimum switching capacity
647 | RSB2A080RDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | RSB2A080RDSoperating rate
648 | RSB2A080RDS | Complementary | mechanical durability | 30000000 cycles | RSB2A080RDSmechanical durability
649 | RSB2A080RDS | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | RSB2A080RDSelectrical durability
650 | RSB2A080RDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | RSB2A080RDSoperating time
651 | RSB2A080RDS | Complementary | marking | CE | RSB2A080RDSmarking
652 | RSB2A080RDS | Complementary | average coil consumption | 0.45 W DC | RSB2A080RDSaverage coil consumption
653 | RSB2A080RDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC | RSB2A080RDSdrop-out voltage threshold
654 | RSB2A080RDS | Complementary | safety reliability data | B10d = 100000 | RSB2A080RDSsafety reliability data
655 | RSB2A080RDS | Complementary | protection category | RT I | RSB2A080RDSprotection category
656 | RSB2A080RDS | Complementary | operating position | Any position | RSB2A080RDSoperating position
657 | RSB2A080RDS | Complementary | sale per indivisible quantity | 10 | RSB2A080RDSsale per indivisible quantity
658 | RSB2A080RDS | Complementary | device presentation | Complete product | RSB2A080RDSdevice presentation
659 | RSB2A080RDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | RSB2A080RDSdielectric strength
660 | RSB2A080RDS | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | RSB2A080RDSstandards
661 | RSB2A080RDS | Environment | product certifications | CSA GOST UL | RSB2A080RDSproduct certifications
662 | RSB2A080RDS | Environment | ambient air temperature for storage | -40…85 °C | RSB2A080RDSambient air temperature for storage
663 | RSB2A080RDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | RSB2A080RDSvibration resistance
664 | RSB2A080RDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | RSB2A080RDSIP degree of protection
665 | RSB2A080RDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | RSB2A080RDSshock resistance
666 | RSB2A080RDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | RSB2A080RDSambient air temperature for operation
667 | RSB2A080RDS | Contractual warranty | Warranty | 18 months | RSB2A080RDSWarranty
668 | RSB2A080U7S | Main | range of product | Zelio Relay | RSB2A080U7Srange of product
669 | RSB2A080U7S | Main | series name | Interface relay | RSB2A080U7Sseries name
670 | RSB2A080U7S | Main | product or component type | Plug-in relay | RSB2A080U7Sproduct or component type
671 | RSB2A080U7S | Main | device short name | RSB | RSB2A080U7Sdevice short name
672 | RSB2A080U7S | Main | contacts type and composition | 2 C/O | RSB2A080U7Scontacts type and composition
673 | RSB2A080U7S | Main | contact operation | Standard | RSB2A080U7Scontact operation
674 | RSB2A080U7S | Main | [Uc] control circuit voltage | 240 V AC | RSB2A080U7S[Uc] control circuit voltage
675 | RSB2A080U7S | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C | RSB2A080U7S[Ithe] conventional enclosed thermal current
676 | RSB2A080U7S | Main | status LED | Without | RSB2A080U7Sstatus LED
677 | RSB2A080U7S | Complementary | shape of pin | Flat | RSB2A080U7Sshape of pin
678 | RSB2A080U7S | Complementary | average coil resistance | 42500 Ohm network: AC at 20 °C +/- 15 % | RSB2A080U7Saverage coil resistance
679 | RSB2A080U7S | Complementary | [Ue] rated operational voltage | 192...288 V AC 50 Hz 204...288 V AC 60 Hz | RSB2A080U7S[Ue] rated operational voltage
680 | RSB2A080U7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | RSB2A080U7S[Ui] rated insulation voltage
681 | RSB2A080U7S | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5 | RSB2A080U7S[Uimp] rated impulse withstand voltage
682 | RSB2A080U7S | Complementary | contacts material | Silver alloy (Ag/Ni) | RSB2A080U7Scontacts material
683 | RSB2A080U7S | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | RSB2A080U7S[Ie] rated operational current
684 | RSB2A080U7S | Complementary | minimum switching current | 5 mA | RSB2A080U7Sminimum switching current
685 | RSB2A080U7S | Complementary | maximum switching voltage | 300 V DC 400 V AC | RSB2A080U7Smaximum switching voltage
686 | RSB2A080U7S | Complementary | minimum switching voltage | 5 V | RSB2A080U7Sminimum switching voltage
687 | RSB2A080U7S | Complementary | maximum switching capacity | 2000 VA AC 224 W DC | RSB2A080U7Smaximum switching capacity
688 | RSB2A080U7S | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC | RSB2A080U7Sresistive rated load
689 | RSB2A080U7S | Complementary | minimum switching capacity | 300 mW at 5 mA | RSB2A080U7Sminimum switching capacity
690 | RSB2A080U7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | RSB2A080U7Soperating rate
691 | RSB2A080U7S | Complementary | mechanical durability | 30000000 cycles | RSB2A080U7Smechanical durability
692 | RSB2A080U7S | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | RSB2A080U7Selectrical durability
693 | RSB2A080U7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | RSB2A080U7Soperating time
694 | RSB2A080U7S | Complementary | marking | CE | RSB2A080U7Smarking
695 | RSB2A080U7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz | RSB2A080U7Saverage coil consumption
696 | RSB2A080U7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC | RSB2A080U7Sdrop-out voltage threshold
697 | RSB2A080U7S | Complementary | safety reliability data | B10d = 100000 | RSB2A080U7Ssafety reliability data
698 | RSB2A080U7S | Complementary | protection category | RT I | RSB2A080U7Sprotection category
699 | RSB2A080U7S | Complementary | operating position | Any position | RSB2A080U7Soperating position
700 | RSB2A080U7S | Complementary | sale per indivisible quantity | 10 | RSB2A080U7Ssale per indivisible quantity
701 | RSB2A080U7S | Complementary | device presentation | Complete product | RSB2A080U7Sdevice presentation
702 | RSB2A080U7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | RSB2A080U7Sdielectric strength
703 | RSB2A080U7S | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | RSB2A080U7Sstandards
704 | RSB2A080U7S | Environment | product certifications | UL CSA GOST | RSB2A080U7Sproduct certifications
705 | RSB2A080U7S | Environment | ambient air temperature for storage | -40…85 °C | RSB2A080U7Sambient air temperature for storage
706 | RSB2A080U7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | RSB2A080U7Svibration resistance
707 | RSB2A080U7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | RSB2A080U7SIP degree of protection
708 | RSB2A080U7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | RSB2A080U7Sshock resistance
709 | RSB2A080U7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | RSB2A080U7Sambient air temperature for operation
710 | RSB2A080U7S | Offer Sustainability | Sustainable offer status | Green Premium product | RSB2A080U7SSustainable offer status
711 | RSB2A080U7S | Offer Sustainability | REACh free of SVHC | Yes | RSB2A080U7SREACh free of SVHC
712 | RSB2A080U7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RSB2A080U7SEU RoHS Directive
713 | RSB2A080U7S | Offer Sustainability | Toxic heavy metal free | Yes | RSB2A080U7SToxic heavy metal free
714 | RSB2A080U7S | Offer Sustainability | Mercury free | Yes | RSB2A080U7SMercury free
715 | RSB2A080U7S | Offer Sustainability | RoHS exemption information | Yes | RSB2A080U7SRoHS exemption information
716 | RSB2A080U7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RSB2A080U7SChina RoHS Regulation
717 | RSB2A080U7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RSB2A080U7SEnvironmental Disclosure
718 | RSB2A080U7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RSB2A080U7SWEEE
719 | RSB2A080U7S | Contractual warranty | Warranty | 18 months | RSB2A080U7SWarranty
720 | RSB2A080M7S | Main | range of product | Zelio Relay | RSB2A080M7Srange of product
721 | RSB2A080M7S | Main | series name | Interface relay | RSB2A080M7Sseries name
722 | RSB2A080M7S | Main | product or component type | Plug-in relay | RSB2A080M7Sproduct or component type
723 | RSB2A080M7S | Main | device short name | RSB | RSB2A080M7Sdevice short name
724 | RSB2A080M7S | Main | contacts type and composition | 2 C/O | RSB2A080M7Scontacts type and composition
725 | RSB2A080M7S | Main | contact operation | Standard | RSB2A080M7Scontact operation
726 | RSB2A080M7S | Main | [Uc] control circuit voltage | 220 V AC | RSB2A080M7S[Uc] control circuit voltage
727 | RSB2A080M7S | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C | RSB2A080M7S[Ithe] conventional enclosed thermal current
728 | RSB2A080M7S | Main | status LED | Without | RSB2A080M7Sstatus LED
729 | RSB2A080M7S | Complementary | shape of pin | Flat | RSB2A080M7Sshape of pin
730 | RSB2A080M7S | Complementary | average coil resistance | 35500 Ohm network: AC at 20 °C +/- 15 % | RSB2A080M7Saverage coil resistance
731 | RSB2A080M7S | Complementary | [Ue] rated operational voltage | 176...264 V AC 50 Hz 187...264 V AC 60 Hz | RSB2A080M7S[Ue] rated operational voltage
732 | RSB2A080M7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | RSB2A080M7S[Ui] rated insulation voltage
733 | RSB2A080M7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV | RSB2A080M7S[Uimp] rated impulse withstand voltage
734 | RSB2A080M7S | Complementary | contacts material | Silver alloy (Ag/Ni) | RSB2A080M7Scontacts material
735 | RSB2A080M7S | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | RSB2A080M7S[Ie] rated operational current
736 | RSB2A080M7S | Complementary | minimum switching current | 5 mA | RSB2A080M7Sminimum switching current
737 | RSB2A080M7S | Complementary | maximum switching voltage | 300 V DC 400 V AC | RSB2A080M7Smaximum switching voltage
738 | RSB2A080M7S | Complementary | minimum switching voltage | 5 V | RSB2A080M7Sminimum switching voltage
739 | RSB2A080M7S | Complementary | maximum switching capacity | 2000 VA AC 224 W DC | RSB2A080M7Smaximum switching capacity
740 | RSB2A080M7S | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC | RSB2A080M7Sresistive rated load
741 | RSB2A080M7S | Complementary | minimum switching capacity | 300 mW at 5 mA | RSB2A080M7Sminimum switching capacity
742 | RSB2A080M7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | RSB2A080M7Soperating rate
743 | RSB2A080M7S | Complementary | mechanical durability | 30000000 cycles | RSB2A080M7Smechanical durability
744 | RSB2A080M7S | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | RSB2A080M7Selectrical durability
745 | RSB2A080M7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | RSB2A080M7Soperating time
746 | RSB2A080M7S | Complementary | marking | CE | RSB2A080M7Smarking
747 | RSB2A080M7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz | RSB2A080M7Saverage coil consumption
748 | RSB2A080M7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC | RSB2A080M7Sdrop-out voltage threshold
749 | RSB2A080M7S | Complementary | safety reliability data | B10d = 100000 | RSB2A080M7Ssafety reliability data
750 | RSB2A080M7S | Complementary | protection category | RT I | RSB2A080M7Sprotection category
751 | RSB2A080M7S | Complementary | operating position | Any position | RSB2A080M7Soperating position
752 | RSB2A080M7S | Complementary | sale per indivisible quantity | 10 | RSB2A080M7Ssale per indivisible quantity
753 | RSB2A080M7S | Complementary | device presentation | Complete product | RSB2A080M7Sdevice presentation
754 | RSB2A080M7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | RSB2A080M7Sdielectric strength
755 | RSB2A080M7S | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | RSB2A080M7Sstandards
756 | RSB2A080M7S | Environment | product certifications | GOST UL CSA | RSB2A080M7Sproduct certifications
757 | RSB2A080M7S | Environment | ambient air temperature for storage | -40…85 °C | RSB2A080M7Sambient air temperature for storage
758 | RSB2A080M7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | RSB2A080M7Svibration resistance
759 | RSB2A080M7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | RSB2A080M7SIP degree of protection
760 | RSB2A080M7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | RSB2A080M7Sshock resistance
761 | RSB2A080M7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | RSB2A080M7Sambient air temperature for operation
762 | RSB2A080M7S | Offer Sustainability | Sustainable offer status | Green Premium product | RSB2A080M7SSustainable offer status
763 | RSB2A080M7S | Offer Sustainability | REACh free of SVHC | Yes | RSB2A080M7SREACh free of SVHC
764 | RSB2A080M7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | RSB2A080M7SEU RoHS Directive
765 | RSB2A080M7S | Offer Sustainability | Toxic heavy metal free | Yes | RSB2A080M7SToxic heavy metal free
766 | RSB2A080M7S | Offer Sustainability | Mercury free | Yes | RSB2A080M7SMercury free
767 | RSB2A080M7S | Offer Sustainability | RoHS exemption information | Yes | RSB2A080M7SRoHS exemption information
768 | RSB2A080M7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration | RSB2A080M7SChina RoHS Regulation
769 | RSB2A080M7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | RSB2A080M7SEnvironmental Disclosure
770 | RSB2A080M7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | RSB2A080M7SWEEE
771 | RSB2A080M7S | Contractual warranty | Warranty | 18 months | RSB2A080M7SWarranty

## pivot_datasheet
| Reference | RE22R2CMR | RHT418BE | RHT428B | RM17JC00MW | RM17TA00 | RM17TE00 | RMTJ60BD | RSB1A160M7S | RSB1A160NDS | RSB2A080M7S | RSB2A080P7S | RSB2A080RDS | RSB2A080U7S | XVDLS37 | XVDLS38
|  | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value
Section | Parameters
Complementary | CAD overall depth |  | 108 mm | 108 mm | [10 empty] | 45 mm | 45 mm
| CAD overall height |  | 43 mm | 43 mm | [10 empty] | 104 mm | 104 mm
| CAD overall width |  | 33 mm | 33 mm | [10 empty] | 45 mm | 45 mm
| Control signal pulse width | 100 ms with load in parallel 30 ms
| Power on delay | 100 ms
| Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
| Recovery time | 120 ms on de-energisation
| Release input voltage | <= 2.4 V
| [Ie] rated operational current | [7 empty] | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
| [Ue] rated operational voltage | [7 empty] | 176...264 V AC 50 Hz 187...264 V AC 60 Hz | 48...66 V DC | 176...264 V AC 50 Hz 187...264 V AC 60 Hz | 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz | 4.8...6.6 V DC | 192...288 V AC 50 Hz 204...288 V AC 60 Hz
| [Ui] rated insulation voltage |  | 250 V | 250 V | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 2 kV | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1
| [Uimp] rated impulse withstand voltage | [7 empty] | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1
| [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz |  |  | 24...240 V AC/DC 50/60 Hz +/- 10 % |  |  | 24 V DC +/- 20 %, non isolated
| abnormal analogue output current | [6 empty] | -30…0 mA when no input or input wire broken
| abnormal analogue output voltage | [6 empty] | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
| adjustment of asymmetry threshold |  |  |  |  | 5...15 % of Un selected | 5...15 % of Un selected
| average coil consumption |  | 2.5 W at 20 °C | 2.5 W at 20 °C |  |  |  |  | 0.75 VA AC 60 Hz | 0.45 W DC | 0.75 VA AC 60 Hz | 0.75 VA AC 60 Hz | 0.45 W DC | 0.75 VA AC 60 Hz
| average coil consumption in VA |  | 2.9 at 20 °C | 2.9 at 20 °C
| average coil resistance | [7 empty] | 35500 Ohm network: AC at 20 °C +/- 15 % | 7500 Ohm network: DC at 20 °C +/- 10 % | 35500 Ohm network: AC at 20 °C +/- 15 % | 38500 Ohm network: AC at 20 °C +/- 15 % | 90 Ohm network: DC at 20 °C +/- 10 % | 42500 Ohm network: AC at 20 °C +/- 15 %
| average resistance |  | 30 mOhm at 20 °C | 30 mOhm at 20 °C
| cable entry | [13 empty] | 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7
| clamping connection capacity | [6 empty] | 2 x 1.5 mm² 1 x 2.5 mm²
| cold junction compensation | [6 empty] | Built-in, measurement: between 0 and 60 °C
| connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end |  |  | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | [7 empty] | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
| contact bounce time |  | <= 10 ms | <= 10 ms
| contacts material |  |  |  | Cadmium free |  |  |  | Silver alloy (Ag/Ni) | Silver alloy (Ag/Ni) | Silver alloy (Ag/Ni) | Silver alloy (Ag/Ni) | Silver alloy (Ag/Ni) | Silver alloy (Ag/Ni)
| contacts type and composition | 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free
| control circuit frequency |  |  |  | 40...70 Hz sinusoidal | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 %
| control circuit voltage limits |  | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 |  | - 12 % + 10 % Un | - 12 % + 10 % Un
| control type | Rotary knob Diagnostic button
| creepage distance | 4 kV/3 conforming to IEC 60664-1
| current consumption | [6 empty] | <= 40 mA for voltage output <= 60 mA for current output
| delay at power up |  |  |  | 0.5 s | 650 ms | 650 ms
| device presentation | [7 empty] | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product
| drop-out voltage threshold | [7 empty] | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.15 Uc AC
| electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 |  |  | 100000 cycles | 100000 cycles | 100000 cycles |  | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
| fixing mode | [6 empty] | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
| housing material | Self-extinguishing |  |  | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic
| hysteresis |  |  |  | 15 % fixed of threshold setting | 2 % | 2 %
| immunity to microbreaks | 10 ms
| input current |  |  |  | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C
| insulation |  |  |  | Between supply and measurement
| insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1 |  |  | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
| local signalling |  |  |  | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green)power ON:
| marking |  |  |  | CE : 73/23/EEC CE : EMC 89/336/EEC | CE | CE | CE | CE | CE | CE | CE | CE | CE
| maximum measuring cycle |  |  |  | 30 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value
| maximum power consumption in W |  |  |  | 1 W
| maximum switching capacity | [7 empty] | 4000 VA AC 448 W DC | 4000 VA AC 448 W DC | 2000 VA AC 224 W DC | 2000 VA AC 224 W DC | 2000 VA AC 224 W DC | 2000 VA AC 224 W DC
| maximum switching current | 8 A |  |  |  | 5 A AC 5 A DC | 5 A AC 5 A DC
| maximum switching voltage | 250 V AC |  |  | 250 V AC/DC | 250 V AC 250 V DC | 250 V AC 250 V DC |  | 300 V DC 400 V AC | 300 V DC 400 V AC | 300 V DC 400 V AC | 300 V DC 400 V AC | 300 V DC 400 V AC | 300 V DC 400 V AC
| maximum voltage drop |  | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V
| measurement accuracy |  |  |  | +/- 10 % of the full scale value
| measurement error |  |  |  | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C
| measurement voltage limits |  |  |  |  | 183…528 V AC | 183…528 V AC
| mechanical durability | 10000000 cycles | 20000000 cycles | 20000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles |  | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles
| minimum switching capacity |  | 150 mVA at 10 mA, 1 V | 50 mVA at 1 mA, 1 V |  |  |  |  | 300 mW at 5 mA | 300 mW at 5 mA | 300 mW at 5 mA | 300 mW at 5 mA | 300 mW at 5 mA | 300 mW at 5 mA
| minimum switching current | 10 mA at 5 V DC |  |  |  | 10 mA at 5 V DC | 10 mA at 5 V DC |  | 5 mA | 5 mA | 5 mA | 5 mA | 5 mA | 5 mA
| minimum switching voltage | [7 empty] | 5 V | 5 V | 5 V | 5 V | 5 V | 5 V
| mounting position | Any position
| mounting support | 35 mm DIN rail conforming to EN/IEC 60715 |  |  | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
| net weight | 0.105 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.12 kg | [6 empty] | 0.08 kg | 0.08 kg
| nominal output current |  |  |  | 5 A | 5 A | 5 A
| operating position |  | Any position | Any position | Any position without derating | Any position without derating | Any position without derating |  | Any position | Any position | Any position | Any position | Any position | Any position
| operating rate |  |  |  | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load |  | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
| operating time | [7 empty] | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
| operating voltage tolerance |  |  |  | - 15 % + 10 % Un
| output contacts |  |  |  | 1 C/O | 1 C/O | 1 C/O
| overvoltage category | III conforming to IEC 60664-1 |  |  | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1
| phase failure sensitivity |  |  |  |  | 0.7 Un | 0.7 Un
| polarity |  |  |  | Yes DC
| power consumption in VA | 3 VA at 240 V AC |  |  |  | 0…22 VA at 400 V AC 50 Hz | 0…22 VA at 400 V AC 50 Hz
| power consumption in W | 1.5 W at 240 V DC
| protection category | [7 empty] | RT I | RT I | RT I | RT I | RT I | RT I
| protection type | [6 empty] | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output
| repeat accuracy | +/- 0.5 % conforming to IEC 61812-1 | +/- 1 % | +/- 1 % | +/- 0.5 % for input and measurement circuit | 0.5 % for input and measurement circuit 3 % for time delay | 0.5 % for input and measurement circuit 3 % for time delay | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C
| reset time |  | 100 ms | 100 ms |  | 1500 ms time delay | 1500 ms time delay
| resistive rated load | [7 empty] | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC
| response time |  |  |  | < 200 ms (in the event of a fault) | < 200 ms (in the event of a fault) | < 200 ms (in the event of a fault)
| safety reliability data | MTTFd = 251.1 years B10d = 230000 |  |  |  | MTTFd = 502.2 years B10d = 470000 | MTTFd = 502.2 years B10d = 470000 | B10d = 45447 MTTFd = 49.2 years | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000
| sale per indivisible quantity | [7 empty] | 10 | 10 | 10 | 10 | 10 | 10
| setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 15 % of full scale | +/- 15 % of full scale
| shape of pin | [7 empty] | Flat | Flat | Flat | Flat | Flat | Flat
| status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
| supply frequency | 50...60 Hz +/- 5 % |  |  |  | 50/60 Hz +/- 10 % | 50/60 Hz +/- 10 %
| supply voltage limits |  |  |  | 20.4…264 V AC/DC | 183…528 V AC | 183…528 V AC
| surge withstand | [6 empty] | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
| switching capacity in VA | 2000 VA
| switching time |  | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
| temperature coefficient | [6 empty] | 200 ppm/°C
| temperature drift | +/- 0.05 %/°C
| terminals description ISO n°1 |  | (31-32-34)OC (41-42-44)OC (11-12-14)OC (21-22-24)OC (A1-A2)CO | (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC | [10 empty] | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND
| threshold adjustment voltage |  |  |  |  | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC | -2...-17 % in the range 220 V AC +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC 2...20 % of Un selected
| threshold setting |  |  |  | 10...100 %
| tightening torque | 0.6…1 N.m conforming to IEC 60947-1 |  |  | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1.1 N.m
| time delay range | 10...100 s 3...30 h 1...10 s 3...30 s 30...300 h 0.3...3 s 0.05...1 s 30...300 min 30...300 s 3...30 min
| time delay type | C
| utilisation category |  |  |  |  | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
| voltage drift | +/- 0.2 %/V
| voltage range | 0.85...1.1 Us |  |  |  | 208...480 V phase to phase | 208...480 V phase to phase
| width | 22.5 mm |  |  | 17.5 mm | 17.5 mm | 17.5 mm
Contractual warranty | Warranty |  | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months
Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 |  |  | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminal block) IP50 (housing) | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529
| ambient air temperature for operation | -20…60 °C | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -20…50 °C | -20…50 °C | -20…50 °C | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -25…70 °C | -25…70 °C
| ambient air temperature for storage | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…70 °C | -40…70 °C
| dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2500 V | 2500 V |  |  |  |  | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
| dielectric test voltage |  |  |  | 2 kV AC 50 Hz | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
| directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility |  |  |  | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
| disturbance radiated/conducted | [6 empty] | CISPR 22 group 1 - class B CISPR 11
| electrical shock protection class | [13 empty] | Class II conforming to IEC 60536 | Class II conforming to IEC 60536
| electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 |  |  | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2
| fire resistance | [6 empty] | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
| immunity to microbreaks |  | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay | 10 ms
| non-dissipating shock wave |  |  |  | 4 kV | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
| pollution degree | 3 conforming to IEC 60664-1 |  |  | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1
| product certifications | CSA CCC RCM China RoHS CE GL UL EAC | ASE EDF USSR BV CSA | USSR EDF ASE BV CSA | GL C-Tick GOST UL CSA | GOST CSA GL C-Tick UL | GOST C-Tick CSA UL GL | CSA GL UL | CSA UL GOST | CSA UL GOST | GOST UL CSA | GOST CSA UL | CSA GOST UL | UL CSA GOST | CSA UL | CSA UL
| protective treatment |  | TC | TC | [10 empty] | TC | TC
| relative humidity | 95 % at 25…55 °C |  |  | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30
| resistance to electrostatic discharge | [6 empty] | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
| resistance to fast transients | [6 empty] | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
| shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
| standards | UL 508 IEC 61812-1 | IEC 60255 NF C 45-250 VDE 0435 | IEC 60255 NF C 45-250 VDE 0435 | EN/IEC 60255-6 | EN/IEC 60255-1 | EN/IEC 60255-1 | IEC 60584-1 IEC 60947-1 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1
| vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
Main | [Ithe] conventional enclosed thermal current |  | 5 A 40 °C | 1 A 40 °C |  |  |  |  | 16 A at -40…40 °C | 16 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C
| [Uc] control circuit voltage |  | 27 V AC/DC 50/60 Hz | 24 V AC/DC 50/60 Hz |  |  |  |  | 220 V AC | 60 V DC | 220 V AC | 230 V AC | 6 V DC | 240 V AC
| [Us] rated supply voltage | [13 empty] | <= 230 V | <= 230 V
| analogue input type | [6 empty] | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584
| analogue output type | [6 empty] | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
| beacon or indicator bank unit type | [13 empty] | Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit
| bulb type | [13 empty] | Incandescent with BA 15d base | Incandescent with BA 15d base
| coil interference suppression |  | With | With
| component name | [13 empty] | XVDLS | XVDLS
| contact operation |  | Standard | Low level |  |  |  |  | Standard | Standard | Standard | Standard | Standard | Standard
| contacts type and composition |  | 4 C/O | 4 C/O |  |  |  |  | 1 C/O | 1 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O
| control type |  | Selector switch | Selector switch | [7 empty] | Without push-button
| device short name | RE22 | RHT | RHT |  |  |  |  | RSB | RSB | RSB | RSB | RSB | RSB
| discrete output type | Relay
| light source | [13 empty] | Bulb not included, clear | Bulb not included, yellow
| material | [13 empty] | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
| maximum power consumption in VA |  |  |  | 3 VA
| maximum power dissipation in W | [13 empty] | 5 W | 5 W
| measurement range |  |  |  | 2...20 A current | 208...480 V voltage AC | 208...480 V voltage AC
| minimum switching current |  |  |  | 10 mA at 5 V DC
| mounting diameter | [13 empty] | 45 mm | 45 mm
| nominal output current | 8 A
| product or component type | Modular timing relay | Timing relay Plug-in relay | Plug-in relay Timing relay | Modular measurement and control relays | Modular measurement and control relays | Modular measurement and control relays | Converter for thermocouples | Plug-in relay | Plug-in relay | Plug-in relay | Plug-in relay | Plug-in relay | Plug-in relay | Complete miniature beacon | Complete miniature beacon
| product specific application |  |  |  |  | For 3-phase supply | For 3-phase supply
| range of product | Zelio Time | Zelio Relay | Zelio Relay | Zelio Control | Zelio Control | Zelio Control | Zelio Analog | Zelio Relay | Zelio Relay | Zelio Relay | Zelio Relay | Zelio Relay | Zelio Relay | Harmony XVD Optimum | Harmony XVD Optimum
| relay monitored parameters |  |  |  | Overcurrent detection | Asymmetry Phase sequence Phase failure detection | Undervoltage and overvoltage in window mode Asymmetry Phase sequence Phase failure detection
| relay name |  |  |  | RM17JC | RM17TA | RM17TE
| relay type |  |  |  | Current control relay | Multifunction control relay | Multifunction control relay
| series name | [7 empty] | Interface relay | Interface relay | Interface relay | Interface relay | Interface relay | Interface relay
| signalling type | [13 empty] | Steady | Steady
| status LED |  | With | With |  |  |  |  | Without | Without | Without | Without | Without | Without
| switching capacity in VA |  |  |  | 1250 VA | 1250 VA | 1250 VA
| time delay |  |  |  | Without | Adjustable 0.1...10 s, +/- 10 % of the full scale value | Adjustable 0.1...10 s, +/- 10 % of the full scale value
| time delay range |  | 0.2...3 s 15...300 s 1.5...30 s | 15...300 s 0.2...3 s 1.5...30 s
| time delay type |  | On-delay | On-delay
| utilisation category |  |  |  | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
Offer Sustainability | China RoHS Regulation | China RoHS declaration |  |  | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration |  | China RoHS declaration | China RoHS declaration |  | China RoHS declaration | China RoHS declaration | China RoHS declaration
| Circularity Profile | End of Life Information |  |  | End of Life Information | End of Life Information | End of Life Information | End of Life Information
| EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration |  |  | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration |  | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration |  | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
| Environmental Disclosure | Product Environmental Profile |  |  | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile |  | Product Environmental Profile | Product Environmental Profile |  | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile
| Mercury free | Yes |  |  | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  | Yes | Yes | Yes
| REACh Regulation | REACh Declaration |  |  | REACh Declaration | REACh Declaration | REACh Declaration | REACh Declaration | [6 empty] | REACh Declaration | REACh Declaration
| REACh free of SVHC | [7 empty] | Yes |  | Yes | Yes |  | Yes
| RoHS exemption information | Yes |  |  | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  | Yes | Yes | Yes
| Sustainable offer status | Green Premium product |  |  | Green Premium product | Green Premium product | Green Premium product | Green Premium product | Green Premium product |  | Green Premium product | Green Premium product |  | Green Premium product | Green Premium product | Green Premium product
| Toxic heavy metal free | [7 empty] | Yes |  | Yes | Yes |  | Yes
| WEEE |  |  |  | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins |  | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins |  | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
Packing Units | Package 1 Height | [6 empty] | 0.270 dm
| Package 1 Length | [6 empty] | 0.850 dm
| Package 1 Weight | [6 empty] | 0.101 kg | [6 empty] | 0.101 kg | 0.100 kg
| Package 1 width | [6 empty] | 0.820 dm

## pivot1_datasheet
Section | Parameters | Value
Complementary | CAD overall depth | 45 mm 45 mm 108 mm 108 mm
| CAD overall height | 104 mm 104 mm 43 mm 43 mm
| CAD overall width | 45 mm 45 mm 33 mm 33 mm
| Control signal pulse width | 100 ms with load in parallel 30 ms
| Power on delay | 100 ms
| Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
| Recovery time | 120 ms on de-energisation
| Release input voltage | <= 2.4 V
| [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
| [Ue] rated operational voltage | 176...264 V AC 50 Hz 187...264 V AC 60 Hz 48...66 V DC 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz 4.8...6.6 V DC 192...288 V AC 50 Hz 204...288 V AC 60 Hz 176...264 V AC 50 Hz 187...264 V AC 60 Hz
| [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1 2 kV 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 250 V 250 V 400 V conforming to EN/IEC 60947 400 V conforming to EN/IEC 60947 400 V conforming to EN/IEC 60947 400 V conforming to EN/IEC 60947 400 V conforming to EN/IEC 60947 400 V conforming to EN/IEC 60947
| [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1 4 kV IEC 60947-1 IEC 61000-4-5 3.6 kV 3.6 kV IEC 61000-4-5 3.6 kV IEC 61000-4-5 IEC 61000-4-5 3.6 kV 3.6 kV IEC 61000-4-5 IEC 61000-4-5 3.6 kV
| [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 % 24...240 V AC/DC 50/60 Hz 24 V DC +/- 20 %, non isolated
| abnormal analogue output current | -30…0 mA when no input or input wire broken
| abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
| adjustment of asymmetry threshold | 5...15 % of Un selected 5...15 % of Un selected
| average coil consumption | 2.5 W at 20 °C 2.5 W at 20 °C 0.75 VA AC 60 Hz 0.45 W DC 0.75 VA AC 60 Hz 0.45 W DC 0.75 VA AC 60 Hz 0.75 VA AC 60 Hz
| average coil consumption in VA | 2.9 at 20 °C 2.9 at 20 °C
| average coil resistance | 35500 Ohm network: AC at 20 °C +/- 15 % 7500 Ohm network: DC at 20 °C +/- 10 % 38500 Ohm network: AC at 20 °C +/- 15 % 90 Ohm network: DC at 20 °C +/- 10 % 42500 Ohm network: AC at 20 °C +/- 15 % 35500 Ohm network: AC at 20 °C +/- 15 %
| average resistance | 30 mOhm at 20 °C 30 mOhm at 20 °C
| cable entry | 1 entry tapped for Pg 7 1 entry tapped for Pg 7
| clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm²
| cold junction compensation | Built-in, measurement: between 0 and 60 °C
| connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end
| contact bounce time | <= 10 ms <= 10 ms
| contacts material | Cadmium free Silver alloy (Ag/Ni) Silver alloy (Ag/Ni) Silver alloy (Ag/Ni) Silver alloy (Ag/Ni) Silver alloy (Ag/Ni) Silver alloy (Ag/Ni)
| contacts type and composition | 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free
| control circuit frequency | 40...70 Hz sinusoidal 50...60 Hz +/- 10 % 50...60 Hz +/- 10 %
| control circuit voltage limits | - 12 % + 10 % Un - 12 % + 10 % Un 0.8...1.1 Uc conforming to IEC 60255 0.8...1.1 Uc conforming to IEC 60255
| control type | Rotary knob Diagnostic button
| creepage distance | 4 kV/3 conforming to IEC 60664-1
| current consumption | <= 40 mA for voltage output <= 60 mA for current output
| delay at power up | 0.5 s 650 ms 650 ms
| device presentation | Complete product Complete product Complete product Complete product Complete product Complete product
| drop-out voltage threshold | >= 0.15 Uc AC >= 0.1 Uc DC >= 0.15 Uc AC >= 0.1 Uc DC >= 0.15 Uc AC >= 0.15 Uc AC
| electrical durability | 100000 cycles 100000 cycles 100000 cycles 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
| fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
| housing material | Self-extinguishing plastic Self-extinguishing plastic Self-extinguishing plastic Self-extinguishing
| hysteresis | 15 % fixed of threshold setting 2 % 2 %
| immunity to microbreaks | 10 ms
| input current | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C
| insulation | Between supply and measurement
| insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 100 MOhm at 500 V DC conforming to IEC 60664-1
| local signalling | LED (green) for power ON LED (yellow) for relay ON LED (green) for power ON LED (yellow) for relay ON LED (green) for power ON LED (yellow) for relay ON LED (green)power ON:
| marking | CE : 73/23/EEC CE : EMC 89/336/EEC CE CE CE CE CE CE CE CE CE
| maximum measuring cycle | 30 ms measurement cycle as true rms value 150 ms measurement cycle as true rms value 150 ms measurement cycle as true rms value
| maximum power consumption in W | 1 W
| maximum switching capacity | 4000 VA AC 448 W DC 4000 VA AC 448 W DC 2000 VA AC 224 W DC 2000 VA AC 224 W DC 2000 VA AC 224 W DC 2000 VA AC 224 W DC
| maximum switching current | 5 A AC 5 A DC 5 A AC 5 A DC 8 A
| maximum switching voltage | 250 V AC/DC 250 V AC 250 V DC 250 V AC 250 V DC 250 V AC 300 V DC 400 V AC 300 V DC 400 V AC 300 V DC 400 V AC 300 V DC 400 V AC 300 V DC 400 V AC 300 V DC 400 V AC
| maximum voltage drop | <100 V for 3 A at 24 V <100 V for 3 A at 24 V
| measurement accuracy | +/- 10 % of the full scale value
| measurement error | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C
| measurement voltage limits | 183…528 V AC 183…528 V AC
| mechanical durability | 30000000 cycles 30000000 cycles 30000000 cycles 10000000 cycles 20000000 cycles 20000000 cycles 30000000 cycles 30000000 cycles 30000000 cycles 30000000 cycles 30000000 cycles 30000000 cycles
| minimum switching capacity | 50 mVA at 1 mA, 1 V 150 mVA at 10 mA, 1 V 300 mW at 5 mA 300 mW at 5 mA 300 mW at 5 mA 300 mW at 5 mA 300 mW at 5 mA 300 mW at 5 mA
| minimum switching current | 10 mA at 5 V DC 10 mA at 5 V DC 10 mA at 5 V DC 5 mA 5 mA 5 mA 5 mA 5 mA 5 mA
| minimum switching voltage | 5 V 5 V 5 V 5 V 5 V 5 V
| mounting position | Any position
| mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 35 mm symmetrical DIN rail conforming to EN/IEC 60715 35 mm symmetrical DIN rail conforming to EN/IEC 60715 35 mm DIN rail conforming to EN/IEC 60715
| net weight | 0.13 kg 0.13 kg 0.13 kg 0.105 kg 0.12 kg 0.08 kg 0.08 kg 0.13 kg 0.13 kg
| nominal output current | 5 A 5 A 5 A
| operating position | Any position without derating Any position without derating Any position without derating Any position Any position Any position Any position Any position Any position Any position Any position
| operating rate | <= 360 operations/hour full load <= 360 operations/hour full load <= 360 operations/hour full load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 600 cycles/hour under load <= 72000 cycles/hour no-load
| operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
| operating voltage tolerance | - 15 % + 10 % Un
| output contacts | 1 C/O 1 C/O 1 C/O
| overvoltage category | III conforming to IEC 60664-1 III conforming to IEC 60664-1 III conforming to IEC 60664-1 III conforming to IEC 60664-1
| phase failure sensitivity | 0.7 Un 0.7 Un
| polarity | Yes DC
| power consumption in VA | 0…22 VA at 400 V AC 50 Hz 0…22 VA at 400 V AC 50 Hz 3 VA at 240 V AC
| power consumption in W | 1.5 W at 240 V DC
| protection category | RT I RT I RT I RT I RT I RT I
| protection type | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output
| repeat accuracy | +/- 0.5 % for input and measurement circuit 0.5 % for input and measurement circuit 3 % for time delay 0.5 % for input and measurement circuit 3 % for time delay +/- 0.5 % conforming to IEC 61812-1 +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C +/- 1 % +/- 1 %
| reset time | 1500 ms time delay 1500 ms time delay 100 ms 100 ms
| resistive rated load | 16 A at 250 V AC 16 A at 28 V DC 16 A at 250 V AC 16 A at 28 V DC 8 A at 250 V AC 8 A at 28 V DC 8 A at 250 V AC 8 A at 28 V DC 8 A at 250 V AC 8 A at 28 V DC 8 A at 250 V AC 8 A at 28 V DC
| response time | < 200 ms (in the event of a fault) < 200 ms (in the event of a fault) < 200 ms (in the event of a fault)
| safety reliability data | MTTFd = 502.2 years B10d = 470000 MTTFd = 502.2 years B10d = 470000 MTTFd = 251.1 years B10d = 230000 B10d = 45447 MTTFd = 49.2 years B10d = 100000 B10d = 100000 B10d = 100000 B10d = 100000 B10d = 100000 B10d = 100000
| sale per indivisible quantity | 10 10 10 10 10 10
| setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 +/- 15 % of full scale +/- 15 % of full scale
| shape of pin | Flat Flat Flat Flat Flat Flat
| status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
| supply frequency | 50/60 Hz +/- 10 % 50/60 Hz +/- 10 % 50...60 Hz +/- 5 %
| supply voltage limits | 20.4…264 V AC/DC 183…528 V AC 183…528 V AC
| surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
| switching capacity in VA | 2000 VA
| switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
| temperature coefficient | 200 ppm/°C
| temperature drift | +/- 0.05 %/°C
| terminals description ISO n°1 | (GND)GROUND (COM-1)PW (COM-1)PW (GND)GROUND (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC (31-32-34)OC (41-42-44)OC (11-12-14)OC (21-22-24)OC (A1-A2)CO
| threshold adjustment voltage | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC -2...-17 % in the range 220 V AC +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC 2...20 % of Un selected
| threshold setting | 10...100 %
| tightening torque | 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1.1 N.m
| time delay range | 10...100 s 3...30 h 1...10 s 3...30 s 30...300 h 0.3...3 s 0.05...1 s 30...300 min 30...300 s 3...30 min
| time delay type | C
| utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
| voltage drift | +/- 0.2 %/V
| voltage range | 208...480 V phase to phase 208...480 V phase to phase 0.85...1.1 Us
| width | 17.5 mm 17.5 mm 17.5 mm 22.5 mm
Contractual warranty | Warranty | 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months
Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 IP20 (terminal block) IP50 (housing) IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529
| ambient air temperature for operation | -20…50 °C -20…50 °C -20…50 °C -20…60 °C 0…50 °C mounting side by side 0…60 °C 2 cm spacing -25…70 °C -25…70 °C -5…40 °C conforming to IEC 60255 -5…40 °C conforming to IEC 60255 -40…70 °C (AC) -40…85 °C (DC) -40…70 °C (AC) -40…85 °C (DC) -40…70 °C (AC) -40…85 °C (DC) -40…70 °C (AC) -40…85 °C (DC) -40…70 °C (AC) -40…85 °C (DC) -40…70 °C (AC) -40…85 °C (DC)
| ambient air temperature for storage | -40…70 °C -40…70 °C -40…70 °C -40…70 °C -40…85 °C -40…70 °C -40…70 °C -40…70 °C -40…70 °C -40…85 °C -40…85 °C -40…85 °C -40…85 °C -40…85 °C -40…85 °C
| dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 2500 V 2500 V 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
| dielectric test voltage | 2 kV AC 50 Hz 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
| directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
| disturbance radiated/conducted | CISPR 22 group 1 - class B CISPR 11
| electrical shock protection class | Class II conforming to IEC 60536 Class II conforming to IEC 60536
| electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
| fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
| immunity to microbreaks | 10 ms 10 ms during time delay 2 ms after time delay 10 ms during time delay 2 ms after time delay
| non-dissipating shock wave | 4 kV 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
| pollution degree | 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 2 conforming to IEC 60664-1
| product certifications | GL C-Tick GOST UL CSA GOST CSA GL C-Tick UL GOST C-Tick CSA UL GL CSA CCC RCM China RoHS CE GL UL EAC CSA GL UL CSA UL CSA UL USSR EDF ASE BV CSA ASE EDF USSR BV CSA CSA UL GOST CSA UL GOST GOST CSA UL CSA GOST UL UL CSA GOST GOST UL CSA
| protective treatment | TC TC TC TC
| relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30 95 % at 55 °C conforming to IEC 60068-2-30 95 % at 55 °C conforming to IEC 60068-2-30 95 % at 25…55 °C
| resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
| resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
| shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1 15 gn for 11 ms conforming to IEC 60255-21-1 15 gn for 11 ms conforming to IEC 60255-21-1 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 50 gn for 11 ms conforming to IEC 60068-2-27 50 gn for 11 ms conforming to NF C 20-608 50 gn for 11 ms conforming to NF C 20-608 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
| standards | EN/IEC 60255-6 EN/IEC 60255-1 EN/IEC 60255-1 UL 508 IEC 61812-1 IEC 60584-1 IEC 60947-1 EN/IEC 60947-5-1 EN/IEC 60947-5-1 IEC 60255 NF C 45-250 VDE 0435 IEC 60255 NF C 45-250 VDE 0435 CSA C22.2 No 14 UL 508 EN/IEC 61810-1 CSA C22.2 No 14 EN/IEC 61810-1 UL 508 UL 508 CSA C22.2 No 14 EN/IEC 61810-1 CSA C22.2 No 14 UL 508 EN/IEC 61810-1 CSA C22.2 No 14 EN/IEC 61810-1 UL 508 EN/IEC 61810-1 CSA C22.2 No 14 UL 508
| vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
Main | [Ithe] conventional enclosed thermal current | 1 A 40 °C 5 A 40 °C 16 A at -40…40 °C 16 A at -40…40 °C 8 A at -40…40 °C 8 A at -40…40 °C 8 A at -40…40 °C 8 A at -40…40 °C
| [Uc] control circuit voltage | 24 V AC/DC 50/60 Hz 27 V AC/DC 50/60 Hz 220 V AC 60 V DC 230 V AC 6 V DC 240 V AC 220 V AC
| [Us] rated supply voltage | <= 230 V <= 230 V
| analogue input type | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584
| analogue output type | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
| beacon or indicator bank unit type | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit
| bulb type | Incandescent with BA 15d base Incandescent with BA 15d base
| coil interference suppression | With With
| component name | XVDLS XVDLS
| contact operation | Low level Standard Standard Standard Standard Standard Standard Standard
| contacts type and composition | 4 C/O 4 C/O 1 C/O 1 C/O 2 C/O 2 C/O 2 C/O 2 C/O
| control type | Selector switch Selector switch Without push-button
| device short name | RE22 RHT RHT RSB RSB RSB RSB RSB RSB
| discrete output type | Relay
| light source | Bulb not included, clear Bulb not included, yellow
| material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
| maximum power consumption in VA | 3 VA
| maximum power dissipation in W | 5 W 5 W
| measurement range | 2...20 A current 208...480 V voltage AC 208...480 V voltage AC
| minimum switching current | 10 mA at 5 V DC
| mounting diameter | 45 mm 45 mm
| nominal output current | 8 A
| product or component type | Modular measurement and control relays Modular measurement and control relays Modular measurement and control relays Modular timing relay Converter for thermocouples Complete miniature beacon Complete miniature beacon Plug-in relay Timing relay Timing relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay
| product specific application | For 3-phase supply For 3-phase supply
| range of product | Zelio Control Zelio Control Zelio Control Zelio Time Zelio Analog Harmony XVD Optimum Harmony XVD Optimum Zelio Relay Zelio Relay Zelio Relay Zelio Relay Zelio Relay Zelio Relay Zelio Relay Zelio Relay
| relay monitored parameters | Overcurrent detection Asymmetry Phase sequence Phase failure detection Undervoltage and overvoltage in window mode Asymmetry Phase sequence Phase failure detection
| relay name | RM17JC RM17TA RM17TE
| relay type | Current control relay Multifunction control relay Multifunction control relay
| series name | Interface relay Interface relay Interface relay Interface relay Interface relay Interface relay
| signalling type | Steady Steady
| status LED | With With Without Without Without Without Without Without
| switching capacity in VA | 1250 VA 1250 VA 1250 VA
| time delay | Without Adjustable 0.1...10 s, +/- 10 % of the full scale value Adjustable 0.1...10 s, +/- 10 % of the full scale value
| time delay range | 15...300 s 0.2...3 s 1.5...30 s 0.2...3 s 15...300 s 1.5...30 s
| time delay type | On-delay On-delay
| utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
Offer Sustainability | China RoHS Regulation | China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration
| Circularity Profile | End of Life Information End of Life Information End of Life Information End of Life Information End of Life Information
| EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
| Environmental Disclosure | Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile
| Mercury free | Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes
| REACh Regulation | REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration
| REACh free of SVHC | Yes Yes Yes Yes
| RoHS exemption information | Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes
| Sustainable offer status | Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product
| Toxic heavy metal free | Yes Yes Yes Yes
| WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
Packing Units | Package 1 Height | 0.270 dm
| Package 1 Length | 0.850 dm
| Package 1 Weight | 0.101 kg 0.101 kg 0.100 kg
| Package 1 width | 0.820 dm