## Revision History
HISTORY OF CHANGES:
Date | Author | Revision | Description of change
2013-11-11 | Liew Yew Loung | 01 | 1) Initial Draft (Add in Symphony Number) 2) All competitor information and existing product information are only for references 3) Detail Product Technical Specification listed in worksheet: - 3P Voltage Control Spec - 1P Voltage Control Spec - 1P Current Control Spec - Level Control Spec 4) Others Technical Specification: - List of References - Function Diagram - Terminal Assignment - Wiring Diagram - Product Dimension - Product Architecture
2013-11-12 | Liew Yew Loung | 02 | 1) Change "Slow Blink (50% ON; 50% OFF)" to "Slow Blink (80% ON; 20% OFF)"
2013-11-28 | Liew Yew Loung | 03 | 1) Add in "Spec Category" next to "T-Rex" column, to indication if the specificaton belong to, -Standard Requirement -Internal Requirement / Manufacturer Documentation only -Design Specification / Parameters -Marketing Requirement 2) Linkage of each specification to reference standard ( to ease references) -Main standard -Sub standard
2013-12-02 | Liew Yew Loung | 04 | 1) Precise shock vibration specification --->15gn - 11ms ; 3 X 6 axis to 15gn - 11ms ; 3 X 6 axis (Output non-energized) 5gn - 11ms ; 3 X 6 axis (Output energized) 2) Precise BUMP specification --->10gn - 16ms ; 1000 X 6 axis to 10gn - 16ms ; 1000 X 6 axis (Output non-energized)
2014-06-25 | Wong Yoon Nam | 05 | Update of product specifications according to latest team input
2014-12-30 | Wong Yoon Nam | 06 | CHANGES CAPTURED IN CHANGE REQUEST CR_0001 1) Update of product references according to latest nonmenclature RM22TA10 => RM22TA31 RM22TA30 => RM22TA33 RM22TU01 => RM22TU21 RM22TU02 => RM22TU23 RM22TR32 => RM22TR33 RM22UA11MR => RM22UA21MR RM22UA12MR => RM22UA22MR RM22UA13MR => RM22UA23MR RM22JA11MR => RM22JA21MR 2) Ambient air temperature around the device (All references) Change from -20oC..+60oC @50Hz, -20oC..+50oC @60Hz (F0), -20oC..+70oC (F1) TO -20oC..+60oC @50Hz, -20oC..+50oC @60Hz (F0), -20oC..+70oC (F1) 3) Degree of protection - Housing (RM35JA32MR & RM35JA32MT) Change from IP40 to IP40 4) Update weight information (All references) 5) Add Rated insulation voltage - Catalog specification (All references) 6) Update Rated insulation voltage - Power supply (All references) 7) Update Rated impulse withstand voltage (Dielectric II) - Catalog specification (All references) 8) Update Rated impulse withstand voltage (Dielectric II) - Power supply (All references) 9) Update Min Creepage distance and clearance - Power supply (All references)
10) Add Insulation Resistance - Catalog specification (All references) 11) Update Insulation Resistance specification according to Offer Requirement (All references) Change from 500MOhm @ -- 500V TO 100MOhm @ -- 500V 12) Add Dielectric voltage withstand (AC RMS) (Dielectric I) - Catalog specification (All references) 13) Update specification for RM22UA23MR, RM22UA33MR, RM22UA33MT Overvoltage cateory: Change from IEC60664-1 : III, UL508 : III TO IEC60664-1 : II, UL508 : II Full Measurement range: Change from ~/-- 15…600 TO ~/-- 15…500 E3-M / B3-C: Change from 600 TO 500 14) Update specification for RM22UA33MT Emission - Radiated RF & electromagnetic field (IT equiment): Change from Class B TO Class A Emission - Radiated RF & electromagnetic field (Medical equiment): Change from Class B, Group 1 TO Class A, Group 1 15) Update description for Special Feature - Test (Diagnostic) Button (All references) 16) Update Ambient air temperature around the device - Storage as per Offer Requirement (All references) Change from '-40oC..+80oC to -40oC..+70oC 17) Update PRJ-STR-xxx numbers according to Offer Requirements (All references) 18) Update Maximum switching capacity (All references) Change from 2000VA TO 1250VA
2015-02-10 | Wong Yoon Nam | 07 | CHANGES CAPTURED IN CHANGE REQUEST CR_0002 1) Update power consumption as per latest measurement results - RM22TG20 from 34VA to 15VA - RM22TU23 from 20VA to 15VA - RM22TA33 from 20VA to 15VA - RM22TR33 from 20VA to 15VA - RM22UB34 from 3.5VA to 5VA - RM22UB34 from 1.5W to 2W - RM22UA33MT from 10VA to 8VA - RM35JA32MT from 10VA to 8VA - RM22LG11MR from 3.5VA to 5VA - RM22LG11MT from 10VA to 8VA - RM22LA32MR from 3.5VA to 5VA - RM22LA32MT from 10VA to 8VA 2) Update Rated supply voltage, Us - RM22UB34 from ~110…240 to ~/--110…240 3) Update Dielectric voltage withstand (AC RMS) (Dielectric I) - All references from 2.5kV/1min/1mA/50Hz to 2.5kV/1min/3mA/50Hz
2015-03-05 | Wong Yoon Nam | 08 | CHANGES CAPTURED IN CHANGE REQUEST CR_0003 1) Update Maximum switching capacity (All references) - From 1250VA to 2000VA 2) Update Input Resistance (RM22JA21MR & RM22JA31MR) - E1-M / B1-C from 5ohm to 2.5ohm - E2-M / B2-C from 1ohm to 0.5ohm - E3-M / B3-C from 0.2ohm to 0.1ohm 3) Update Timing Range (RM22UA21MR, RM22UA22MR & RM22UA23MR) - From 0.3…30 to NIL 4) Update Timing range (RM22UA23MR, RM22UA31MR, RM22UA32MR, RM22UA33MR, RM22UA33MT, RM22UB34, RM22JA31MR, RM35JA32MR, RM35JA32MT) - From Adjustable 0.3…30 to Adjustable 0.1…30 5) Update Climatic category (All references) - Remove 3k3 6) Update Vibration resistance (All references) - Change from ±0.35mm from 5Hz…57.6Hz to ±0.035mm from 5Hz…57.6Hz - Change from 1g from 57.6Hz..150Hz to 0.5g from 57.6Hz..150Hz 7) Update Degree of protection - Housing (RM35JA32MR & RM35JA32MT) - Change from IP40 to IP30
2015-08-25 | Wong Yoon Nam | 09 | 1) Change Ambient air temperature around the device - Operation from "-20oC..+60oC @50Hz" to "-20oC..+60oC @50Hz or DC" for below references: RM22UA21MR, RM22UA22MR, RM22UA23MR, RM22UA31MR, RM22UA32MR, RM22UA33MR, RM22UA33MT, RM22UB34, RM22JA21MR, RM22JA31MR, RM35JA32MR, RM35JA32MT, RM22LG11MR, RM22LG11MT, RM22LA32MR, RM22LA32MT 2) All references: Change Vibration resistance from "±0.035mm from 5Hz…57.6Hz; 0.5g from 57.6Hz..150Hz" to "0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating); 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating)" 3) All references: Change Shock resistance from "15gn - 11ms ; 3 X 6 axis (Output non-energized); 5gn - 11ms ; 3 X 6 axis (Output energized)" to "15gn - 11ms ; 3 X 6 axis (Non-Operating); 5gn - 11ms ; 3 X 6 axis (Operating)" 4) Change Setting accuracy for RM35JA32MT - From +/- 10% of full scale value to +/- 10% of full scale value (For 1.5A and 5A); +/- 20% of full scale value (For 15A) 5) Add detail cross references information into "List of References" worksheet
6) RM22TR31 & RM22TR33 - Change Monitoring functions from Undervoltage and Overvoltagre to Over / undervoltage (windows mode) 7) Change Hysteresis from "Adjustable 5%...50% of threshold setting" to "Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting; Window mode: Fix 3% of full scale value" for below references: RM22UA31MR, RM22UA32MR, RM22UA33MR, RM22UA33MT 8) Change Hysteresis from "Adjustable 5%...50% of threshold setting" to "Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting; Window mode: Fix 3% of full scale value" for below references: RM22JA31MR, RM35JA32MR, RM35JA32MT 9) All references: Change Bump from "10gn - 16ms ; 1000 X 6 axis (Output non-energized)" to "10gn - 16ms ; 1000 X 6 axis (Non-Operating)" 10) RM22TA33: Change Phase asymmetry from "19…72" to "19…96"
2020-09-04 | Liew Yew Loung / Wong Yoon Nam | 10 | 1) Combine and add Catch-Up (EAV4933102-V09) & Juret (EAV9808800-V06)Product Specification 2) Include all Crouzet references even though similar to SE references 3) Standardize & precise all "Output Circuit Characteristics" serves as common paramaters for all references 4) Standardize & precise "Electrical Isolation" 5) Add in internal built-in characteristics: Voltage Regeneration, Extreme undervoltage, Extreme overvoltage, Extreme asymmetry 6) Include Kizuna project updated parameters on: Mechanical durability, Time delay of pick-up, Response time on crossing the threshold, Maximum power consumption 7) Include: RM*TG (3 references) update information on "2 or more phase cut" 8) Fill in the blank specification with known specification for all RMC2 ranges (non Catchup-References) 9) Update Weight (without packaging) information 10) Update Wiring connection (Clamping Capacity) - Solid cable without cable end (screw terminal) & Flexible cable with cable end (screw terminal) to consistent with product marking 11) Update Maximum measuring cycles for RM22TR33 frpm 150ms to 170ms 12) Update and commonize Immunity to micro-breakage parameter 13) Update power consumption value for RM22

## EMC Test Level (hidden)
Guides For Defining / Selecting Different Test Level for EMC Immunity Test
ESD Immunity | IEC61000-4-2 | Air | Contact
Level I | Used in environment: =<35% RH, with antistatic material | 2kV | 2kV
Level II | Used in environment: =<10% RH, with antistatic material | 4kV | 4kV
Level III | Used in environment: =<50% RH, No antistatic material, with synthetic material | 6kV | 8kV
Level IV | Used in environment: =<10% RH, No antistatic material, with synthetic material | 8kV | 15kV
Level X | Special environment
RF Immunity | IEC61000-4-3 | Test Field Strength
Level I | Low-level electromagnetic radiation environment. Levels typical of local radio/television stations located at more than 1 km, and transmitters/receivers of low power. | 1 V/m
Level II | Moderate electromagnetic radiation environment. Low power portable transceivers (typically less than 1 W rating) are in use, but with restrictions on use in close proximity to the equipment. A typical commercial environment | 3 V/m
Level III | Severe electromagnetic radiation environment. Portable transceivers (2 W rating or more) are in use relatively close to the equipment but not less than 1 m. High power broadcast transmitters are in close proximity to the equipment and ISM equipment may be located close by. A typical industrial environment | 10 V/m
Level IV | Portable transceivers are in use within less than 1 m of the equipment. Other sources of significant interference may be within 1 m of the equipment | 30 V/m
Level X | Special environment
Fast Transient | IEC61000-4-4 | Power Port | I/O Port
Level I | Well-protected environment: – suppression of all EFT/B in the switched power supply and control circuits; – separation between power supply lines (a.c. and d.c.) and control and measurement circuits coming from other environments belonging to higher severity levels: – shielded power supply cables with the screens earthed at both ends on the reference ground of the installation, and power supply protection by filtering – computer room | 0.5kV (5kHz or 100kHz) | 0.25V (5kHz or 100kHz)
Level II | Protected environment: – partial suppression of EFT/B in the power supply and control circuits which are switched only by relays (no contactors); – poor separation of the industrial circuits belonging to the industrial environment from other circuits associated with environments of higher severity levels; – physical separation of unshielded power supply and control cables from signal and communication cables – control room or terminal room of industrial and electrical plants | 1kV (5kHz or 100kHz) | 0.5V (5kHz or 100kHz)
Level III | Typical industrial environment: – no suppression of EFT/B in the power supply and control circuits which are switched only by relays (no contactors); – poor separation of the industrial circuits from other circuits associated with environments of higher severity levels; – dedicated cables for power supply, control, signal and communication lines; – poor separation between power supply, control, signal and communication cables; – availability of earthing system represented by conductive pipes, earth conductors in the cable trays (connected to the protective earth system) and by a ground mesh – area of industrial process equipment | 2kV (5kHz or 100kHz) | 1V (5kHz or 100kHz)
Level IV | Severe industrial environment: – no suppression of EFT/B in the power supply and control and power circuits which are switched by relays and contactors; – no separation of the industrial circuits belonging to the severe industrial environment from other circuits associated with environments of higher severity levels; – no separation between power supply, control, signal and communication cables; – use of multicore cables in common for control and signal lines – outdoor area of industrial process equipment where no specific installation practice has been adopted, power plants, the relay rooms of open-air H.V. substations and gas insulated substations of up to 500 kV operating voltage (with typical installation practice) | 4kV (5kHz or 100kHz) | 2V (5kHz or 100kHz)
Level X | Special situations to be analysed
Surge Immunity | IEC61000-4-5 | DM | CM
Level I |  | - | 0.5kV
Level II |  | 0.5kV | 1kV
Level III |  | 1kV | 2kV
Level IV |  | 2kV | 4kV
Level X | Special environment
Conducted Immunity | IEC61000-4-6 | dB (uV) | Vrms
Level I | Low-level electromagnetic radiation environment. Typical level where radio/television stations are located at a distance of more than 1 km and typical level for lowpower transceivers | 120 | 1
Level II | Moderate electromagnetic radiation environment. Low-power portable transceivers (typically less than 1 W rating) are in use, but with restrictions on use in close proximity to the equipment. A typical commercial environment | 130 | 3
Level III | Severe electromagnetic radiation environment. Portable transceivers (2 W and more) are in use relatively close to the equipment but at a distance not less than 1 m. Highpowered broadcast transmitters are in close proximity to the equipment and ISM equipment may be located close by. A typical industrial environment | 140 | 10
Level X | X is an open level which may be negotiated and specified in the dedicated equipment specifications or equipment standards
Power Freq. Mag Field | IEC61000-4-8 | Magnetic Field Strength
Level I | Environmental level where sensitive device using electron beam can be used | 1 A/m
Level II | Well protected environment: Household, office, hospital, areas of industrial installations | 3 A/m
Level III | Protected environment: Commercial areas, control building, field of not heavy industrial plants, computer room of H.V. sub-stations | 10 A/m
Level IV | Typical industrial environment: Fields of heavy industrial and power plants and the control room of H.V. sub-stations | 30 A/m
Level V | Severe industrial environment: Switchyard areas of heavy industrial plants, M.V., H.V. and power stations | 100 A/m
Level X | Special environment
Pulse Mag Field | IEC61000-4-9 | Magnetic Field Strength
Level I | Environmental level where sensitive device using electron beam can be used | N.A
Level II | Well protected environment: Household, office, hospital, areas of industrial installations | N.A
Level III | Protected environment: Commercial areas, control building, field of not heavy industrial plants, computer room of H.V. sub-stations | 100 A/m (peak)
Level IV | Typical industrial environment: Fields of heavy industrial and power plants and the control room of H.V. sub-stations | 300 A/m (peak)
Level V | Severe industrial environment: Switchyard areas of heavy industrial plants, M.V., H.V. and power stations | 1000 A/m (peak)
Level X | Special environment
Damped Oscillatory Magnetic Field | IEC61000-4-10 | Magnetic Field Strength
Level I | Environmental level where sensitive device using electron beam can be used | N.A
Level II | Well protected environment: Household, office, hospital, areas of industrial installations | N.A
Level III | Protected environment: Commercial areas, control building, field of not heavy industrial plants, computer room of H.V. sub-stations | 10 A/m (peak)
Level IV | Typical industrial environment: Fields of heavy industrial and power plants and the control room of H.V. sub-stations | 30 A/m (peak)
Level V | Severe industrial environment: Switchyard areas of heavy industrial plants, M.V., H.V. and power stations | 100 A/m (peak)
Level X | Special environment
Voltage Dips / Interr. | IEC61000-4-11 | Voltage Dip (%U) | Short Interruption(%U)
Class I | Environments normally contain equipment which requires protection by such apparatus as uninterruptible power supplies (UPS), filters, or surge suppressers. | Manufacturer to define | Manufacturer to define
Class II | Components designed for application in public networks may be used in this class of industrial environment | 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) | 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz)
Class III | Welding machines are present, large motors are frequently started, loads vary rapidly, a major part of the load is fed through converters; | 0%, 1/2 cycle 0%, 1 cycle 40%, 10 cycles (50Hz) 40%, 12 cycles (60Hz) 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 80%, 250 cycles (50Hz) 80%, 300 cycles (60Hz) | 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz)
Level X | Special environment
Ring Wave Immunity | IEC61000-4-12 | DM | CM
Level I | The port connected to protected local power source (e.g.uninterruptible power system, power converter) / control room | 0.25kV | 0.5kV
Level II | The port directly connected to mains distribution systems of residential area / isolation transformers / protection devices / shielded cables. | 0.5kV | 1kV
Level III | The port connected to dedicated power distribution systems in electrical and industrial plants / to outdoor cables provided with shielding provisions | 1kV | 2kV
Level IV | The port connected to power source characterized by heavy inductive loads in industrial or electrical plants / to outdoor cables without shielding provisions | 2kV | 4kV
Level X | Special environment
Low Freq. Harmonic | IEC61000-4-13 | 5th…37th Harmonic
Class I | Environments normally contain equipment which requires protection by such apparatus as uninterruptible power supplies (UPS), filters, or surge suppressers.
Class II | Components designed for application in public networks may be used in this class of industrial environment
Class III | Welding machines are present, large motors are frequently started, loads vary rapidly, a major part of the load is fed through converters;
Level X | Special environment
|  | Slow Damped Oscillatory Wave (100 kHz or 1 MHz) |  | Fast Damped Oscillatory Wave (3 MHz, 10 MHz or 30 MHz)
1 MHz oscillation wave Immunity | IEC61000-4-18 | DM | CM | DM | CM
Level I | Ports connected to cables running in a limited area of the control building | 0.25kV | 0.5kV | - | 0.5kV
Level II | Ports connected to cables of equipment in the control building and relay house (kiosks). The equipment concerned is installed in the control building and relay house. | 0.5kV | 1kV | - | 1kV
Level III | Ports connected to cables of equipment installed in the relay house. The equipment concerned are those installed in the relay house. For these equipment, level 3 assumes the value of 2,5 kV | 1kV | 2.5kV | - | 2kV
Level IV | Slow damped oscillatory waves are not applicable to equipment for use in electrical plants, particularly HV substations, while fast damped oscillatory waves are applicable. Whenever this level seems to be necessary, proper mitigation methods should be adopted | - | - | - | 4kV
Level X | Special environment
DC voltage interruption | IEC61000-4-29 | Voltage Dip (%U) | Short Interruption (%U) | Voltage Variation (%U)
- | Not specified level. Only 1 defined condition | 40% or 70% (10ms, 30ms, 100ms, 300ms, 1s or X) | 0% (1ms, 3ms, 10ms, 30ms, 100ms, 300ms, 1s or X) | 85% or 120% (100ms, 300ms, 1s, 3s, 10s or X)
Guides For Defining / Selecting Different Test Level for EMC Emission Test
Generic Standard | Generic Standard Description | Equivalent Standard
IEC 61000-6-4 | Emission Standard for Industrial Environments | EN 50081-2 | CISPR 11, Group 1 Class A | CISPR 22, Class A
IEC 61000-6-3 | Emission standard for residential, commercial and light-industrial environments | EN 50081-1 | CISPR 11, Group 1 Class B | CISPR 22, Class B
IEC 61000-6-2 | Immunity for Industrial Environments
IEC 61000-6-1 | Immunity for residential, commercial and light-industrial environments
Standard List:
CISPR 11 | Emission for industrial, scientific, and medical apparatus
CISPR 22 | Emission for information technology [IT] equipment
IEC 61000-6-4 | Emission Standard for Industrial Environments = EN 50081-2
IEC 61000-6-3 | Emission standard for residential, commercial and light-industrial environments = EN 50081-1
IEC 61000-6-2 | Immunity for Industrial Environments
IEC 61000-6-1 | Immunity for residential, commercial and light-industrial environments
EN 61326 | Electrical equipment for measurement, control and laboratory use – EMC requirements – Part 1: General requirements
Emission Class:
Class A: Used in low voltage non-public/industrial networks/location/installations including highly disturbing sources (test @ 10m or 30m)
Class B: Used in low voltage public networks like domestics, commercial & light industrial locations/installation. High disturbing sources are not covered (test @ 3m or 10m)
EMC 1: Bridge and open deck zone
EMC 2: General power distribution zone
Emission Group:
Group 1: contains all equipment in the scope of this standard which is not classified as group 2 equipment.
Group 2: contains all ISM RF equipment in which radio-frequency energy in the frequency range 9 kHz to 400 GHz is intentionally generated and used or only used,
in the form of electromagnetic radiation, inductive and/or capacitive coupling, for the treatment of material or inspection/analysis purposes.
Only For Control Relay

## 3P Voltage Control Spec
|  | Brand --> |  |  | brown text - widely used every where |  |  |  | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | CROUZET | EBERLE | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | CROUZET | EBERLE | CROUZET | EBERLE | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | CROUZET | SCHNEIDER ELECTRIC | CROUZET | CROUZET | SCHNEIDER ELECTRIC | CROUZET | EBERLE | MANITOWOC | SCHNEIDER ELECTRIC | CROUZET | SCHNEIDER ELECTRIC | CROUZET | CROUZET | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | CROUZET | CROUZET | SCHNEIDER ELECTRIC | CROUZET | CROUZET | SCHNEIDER ELECTRIC | CROUZET | CROUZET | OLD SE | CROUZET | CROUZET | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | CROUZET | CROUZET | ABB | OMRON | CARLO GAVAZZI
|  | Base Design Reference --> | 4 |  | black text - product nature specific |  |  |  | HW adapted from 84873034 | HW & FW adapted from RM17UB310 | HW & FW adapted from RM17UB310 | HW & FW adapted from RM17TU00 | HW & FW adapted from RM17TU00 | HW & FW adapted from RM17TA00 | HW & FW adapted from RM17TA00 | HW adapated from RM17TG00 |  |  | Main Architecture (1) | HW & FW = 100% same as RM17TG00 |  |  |  |  | Main Architecture (2) | HW & FW = 100% same as RM17TE00 |  | HW & FW adapted from RM17TE00 |  | HW & FW adapted from RM17TE00 | HW & FW adapted from RM17TE00 |  |  | HW & FW adapted from RM17TE00 | HW & FW adapted from RM17TE00 |  | Main Architecture (3) |  |  | HW = 100% same as RM35TF30 | HW & FW adapted from RM35TF30 |  |  | Main Architecture (4) |  |  | HW = 100% same as RM17TE00 |  |  | (RM4 + Crouzet)
|  | Firmware Type --> | 19 | [5 empty] | 1 | 3 | 6 | 14 | 13 | 9 | 10 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 2 | 2 | 2 | 17 | 17 | 18 | 11 | 11 | 11 | 19 | 12 | 12 | 4 | 4 | 4 | 15 | 16 | 16 | 16 | 5 | 5 | 5 | 8 | 8 | 8
Main Parameters | Category | Sub Parameters | Conforming to | Remark | Standardized Datasheet Param | Selected for Publication | Old Datasheet | Unit | RM22TG20 | RM22TR33 | RM22TR31 | RM22TU23 | RM22TU21 | RM22TA33 | RM22TA31 | RM17TG20 | 84873021 | 84873891 | RM17TG00 | RM10TG00 | 84873029 | 84873890 | 84873034 | 84873195 | RM17TE00 | RM10TE00 | 84873025 | RM17TU00 | 84873023 | 84873805 | RM17TA00 | 84873024 | 84873892 | 84873804 | RM17TT00 | 84873022 | RM35TF30 | 84873026 | 84873893 | RM35TF30SP01 | RM35UB330 | 84873220 | 84873894 | RM35UB3N30 | 84873221 | 84873895 | RM17UB310 | 84873222 | 84873896 | Competitor Spec Reference | 84873034 (Catch-Up Juret - Actual) | 84873034 (Catch-Up Juret - For Crouzet) | RM4TR | RM4TG20 | RM4TU | RM4TA | RM4UB | 84873004 | 848792299 | 1SVR 630 794 R3300 | K8DS-PH1 (1 C/O) K8AK-PH1 (2 C/O) | DPA51CM44
Standard
Product standard |  |  |  | Common C_Rly Spec | standards | Published | Published |  | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM17TE00 | Same as RM17TE00 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM17TU00 | Same as RM17TU00 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM17TT00 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM35UB330 | Same as RM35UB330 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM35UB3N30 | Same as RM35UB3N30 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | Same as RM17UB310 | Same as RM17UB310 |  | EN60255-1, IEC60255-1 | EN60255-1, IEC60255-1 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | Not specified | Not specified | EN60255-6, IEC60255-6, EN50178 | EN60947-5-1 | Not specified
Product certifications |  |  |  | Common C_Rly Spec | product certifications | Published | Published |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | CCC, CE, China ROHS | UL, CSA, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CE, China ROHS | Same as 84873034 | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | Same as RM35TF30 | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS |  | UL, CSA, CE, EAC | UL, CSA, CE, EAC | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | cULus, CE | cULus, CE | cULus, CSA, GL, C-Tick, GOST, CCC, CB |  | UL, CSA
Marking |  |  |  | Common C_Rly Spec | marking | Published |  |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | CCC, CE, China ROHS | UL, CSA, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CE, China ROHS | Same as 84873034 | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | Same as RM35TF30 | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, CCC, CE, China ROHS | UL, CSA, CE, China ROHS |  | UL, CSA, CE, EAC | UL, CSA, CE, EAC | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | cULus, CE | cULus, CE | cULus, CSA, GL, C-Tick, GOST, CCC, CB, CE |  | UL, CSA, CE
Low voltage directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 2014/35/EU | Same as RM17TE00 | Same as RM17TE00 | 2014/35/EU | Same as RM17TU00 | Same as RM17TU00 | 2014/35/EU | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 2014/35/EU | Same as RM17TT00 | 2014/35/EU | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 2014/35/EU | Same as RM35UB330 | Same as RM35UB330 | 2014/35/EU | Same as RM35UB3N30 | Same as RM35UB3N30 | 2014/35/EU | Same as RM17UB310 | Same as RM17UB310 |  | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | 2006/95/EC | 2006/95/EC | 2006/95/EC | 2006/95/EC | 2006/95/EC | Not specified | Not specified | 2006/95/EG |  | Not specified
EMC directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 2014/30/EU | Same as RM17TE00 | Same as RM17TE00 | 2014/30/EU | Same as RM17TU00 | Same as RM17TU00 | 2014/30/EU | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 2014/30/EU | Same as RM17TT00 | 2014/30/EU | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 2014/30/EU | Same as RM35UB330 | Same as RM35UB330 | 2014/30/EU | Same as RM35UB3N30 | Same as RM35UB3N30 | 2014/30/EU | Same as RM17UB310 | Same as RM17UB310 |  | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | 2004/108/EC | 2004/108/EC | 2004/108/EC | 2004/108/EC | 2004/108/EC | Not specified | Not specified | 2004/108/EG |  | Not specified
ROHS directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 2011/65/EU | Same as RM17TE00 | Same as RM17TE00 | 2011/65/EU | Same as RM17TU00 | Same as RM17TU00 | 2011/65/EU | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 2011/65/EU | Same as RM17TT00 | 2011/65/EU | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 2011/65/EU | Same as RM35UB330 | Same as RM35UB330 | 2011/65/EU | Same as RM35UB3N30 | Same as RM35UB3N30 | 2011/65/EU | Same as RM17UB310 | Same as RM17UB310 |  | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC | Not specified | Not specified | 2002/95/EC |  | Not specified
Environment Characteristics
Environmental Condition |  | Climatic category | IEC60721-3-3 | Common C_Rly Spec |  |  |  |  | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM17TE00 | Same as RM17TE00 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM17TU00 | Same as RM17TU00 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM17TT00 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM35UB330 | Same as RM35UB330 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM35UB3N30 | Same as RM35UB3N30 | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | Same as RM17UB310 | Same as RM17UB310 |  | Not specified | Not specified | 3K3 | 3K3 | 3K3 | 3K3 | 3K3 | Not specified | Not specified | 3K3 |  | Not specified
|  | Environmental category | Germanisher Lloyd | Common C_Rly Spec |  |  |  |  | Class C | Class C | Class C | Class C | Class C | Class C | Class C | Class C | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Class C | Same as RM17TE00 | Same as RM17TE00 | Class C | Same as RM17TU00 | Same as RM17TU00 | Class C | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Class C | Same as RM17TT00 | Class C | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Class C | Same as RM35UB330 | Same as RM35UB330 | Class C | Same as RM35UB3N30 | Same as RM35UB3N30 | Class C | Same as RM17UB310 | Same as RM17UB310
Ambient air temperature around the device |  | Storage |  | Common C_Rly Spec | ambient air temperature for storage | Published | Published | oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | -30oC..+70oC | Same as 84873034 | -40oC..+70oC | Same as RM17TE00 | Same as RM17TE00 | -40oC..+70oC | Same as RM17TU00 | Same as RM17TU00 | -40oC..+70oC | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | -40oC..+70oC | Same as RM17TT00 | -40oC..+70oC | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | -40oC..+70oC | Same as RM35UB330 | Same as RM35UB330 | -40oC..+70oC | Same as RM35UB3N30 | Same as RM35UB3N30 | -40oC..+70oC | Same as RM17UB310 | Same as RM17UB310 |  | -30…+70 | -30…+70 | -40…+85 | -40…+85 | -40…+85 | -40…+85 | -40…+85 | -30…+70 | -30…+70 | -40…+85 | -25…+65 | -30…+80, R.H. < 95%
|  | Operation |  |  | ambient air temperature for operation | Published | Published | oC | -20oC..+60oC @50Hz -20oC..+50oC @60Hz | -20oC..+60oC @50Hz -20oC..+50oC @60Hz | -20oC..+60oC @50Hz -20oC..+50oC @60Hz | -20oC..+60oC @50Hz -20oC..+50oC @60Hz | -20oC..+60oC @50Hz -20oC..+50oC @60Hz | -20oC..+60oC @50Hz -20oC..+50oC @60Hz | -20oC..+60oC @50Hz -20oC..+50oC @60Hz | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM17TE00 | Same as RM17TE00 | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM17TU00 | Same as RM17TU00 | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM17TT00 | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM35UB330 | Same as RM35UB330 | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM35UB3N30 | Same as RM35UB3N30 | -20oC..+50oC @50Hz -20oC..+50oC @60Hz | Same as RM17UB310 | Same as RM17UB310 |  | -20…+50 | -20…+50 | -20…+65 | -20…+65 | -20…+65 | -20…+65 | -20…+65 | Not specified | Not specified | -25…+60 | -20…+60 | -20…+50, R.H. < 95%
Relative humidity |  | Damp heat | IEC60068-2-30 | Common C_Rly Spec | relative humidity | Published | Published |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TE00 | Same as RM17TE00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TU00 | Same as RM17TU00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TT00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM35UB330 | Same as RM35UB330 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM35UB3N30 | Same as RM35UB3N30 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17UB310 | Same as RM17UB310 |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 2 cycles 24h ;+25°C +55°C 95%HR | 15%...85% | 15%...85% | 15%...85% | 15%...85% | 15%...85% | Not specified | Not specified | +55°C, 6 cycles |  | Not specified
|  | Cyclic Damp Heat Test | IEC60947-5-1 | Common C_Rly Spec |  |  |  |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | - | Same as 84873034 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TE00 | Same as RM17TE00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TU00 | Same as RM17TU00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17TT00 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM35UB330 | Same as RM35UB330 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM35UB3N30 | Same as RM35UB3N30 | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | Same as RM17UB310 | Same as RM17UB310 |  | Not specified | Not specified
Vibration resistance |  |  | IEC60068-2-6 | Common C_Rly Spec | vibration resistance | Published | Published |  | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM17TE00 | Same as RM17TE00 | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM17TU00 | Same as RM17TU00 | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM17TT00 | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM35UB330 | Same as RM35UB330 | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM35UB3N30 | Same as RM35UB3N30 | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | Same as RM17UB310 | Same as RM17UB310 |  | ±0.35mm from 5Hz…57.6Hz 1g from 57.6Hz..150Hz | 0.035mm from 10Hz…150Hz | a=0.35ms from 10Hz…55Hz | a=0.35ms from 10Hz…55Hz | a=0.35ms from 10Hz…55Hz | a=0.35ms from 10Hz…55Hz | a=0.35ms from 10Hz…55Hz | Not specified | Not specified | Class 2 |  | Not specified
Shock resistance |  |  | IEC60068-2-27 | Common C_Rly Spec | shock resistance | Published | Published |  | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM17TE00 | Same as RM17TE00 | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM17TU00 | Same as RM17TU00 | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM17TT00 | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM35UB330 | Same as RM35UB330 | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM35UB3N30 | Same as RM35UB3N30 | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | Same as RM17UB310 | Same as RM17UB310 |  | 15gn - 11ms | 5 gn | 15 gn | 15 gn | 15 gn | 15 gn | 15 gn | Not specified | Not specified | Class 2 |  | Not specified
Bump resistance |  |  | IEC60068-2-29 | Common C_Rly Spec | bump resistance |  |  |  | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM17TE00 | Same as RM17TE00 | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM17TU00 | Same as RM17TU00 | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM17TT00 | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM35UB330 | Same as RM35UB330 | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM35UB3N30 | Same as RM35UB3N30 | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | Same as RM17UB310 | Same as RM17UB310
Seismic resistance |  |  | IEC60068-3-3 | Common C_Rly Spec | seismic resistance |  |  |  | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM17TE00 | Same as RM17TE00 | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM17TU00 | Same as RM17TU00 | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM17TT00 | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM35UB330 | Same as RM35UB330 | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM35UB3N30 | Same as RM35UB3N30 | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Same as RM17UB310 | Same as RM17UB310
IP degree of protection |  | Terminal Block | IEC60529 |  | IP degree of protection | Published | Published |  | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | IP20 | Same as RM17TE00 | Same as RM17TE00 | IP20 | Same as RM17TU00 | Same as RM17TU00 | IP20 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | IP20 | Same as RM17TT00 | IP20 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | IP20 | Same as RM35UB330 | Same as RM35UB330 | IP20 | Same as RM35UB3N30 | Same as RM35UB3N30 | IP20 | Same as RM17UB310 | Same as RM17UB310 |  | IP20 | IP40 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 |  | IP20
|  | Housing | IEC60529 |  | IP degree of protection | Published | Published |  | IP40 | IP40 | IP40 | IP40 | IP40 | IP40 | IP40 | IP30 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | IP30 | Same as RM17TE00 | Same as RM17TE00 | IP30 | Same as RM17TU00 | Same as RM17TU00 | IP30 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | IP30 | Same as RM17TT00 | IP30 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | IP30 | Same as RM35UB330 | Same as RM35UB330 | IP30 | Same as RM35UB3N30 | Same as RM35UB3N30 | IP30 | Same as RM17UB310 | Same as RM17UB310 |  | IP40 | IP20 | IP50 | IP50 | IP50 | IP50 | IP50 | IP40 | IP40 | IP50 |  | Not specified
|  | Front Panel | IEC60529 |  | IP degree of protection |  |  |  | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | - | Same as RM17TG20 | - | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | IP40 | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified |  | Not specified
Installation Data
Dimension (nominal) |  | Width |  |  | width | Published |  | mm | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 | 17.5 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | 22.5 | Same as 84873034 | 17.5 | Same as RM17TE00 | Same as RM17TE00 | 17.5 | Same as RM17TU00 | Same as RM17TU00 | 17.5 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 17.5 | Same as RM17TT00 | 35 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 35 | Same as RM35UB330 | Same as RM35UB330 | 35 | Same as RM35UB3N30 | Same as RM35UB3N30 | 17.5 | Same as RM17UB310 | Same as RM17UB310 |  | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 78 x 80 | 22.5 x 78 x 80 | 22.5 x 78 x 80 | 22.5 x 78 x 80 | 22.5 x 78 x 80 | 22.5 x 78.5 x 100 | 22.5 x 78.5 x 100 | 22.5 x 78 x 100 |  | 17.5 x 81 x 67.2
|  | Height |  |  | height | Published |  | mm | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | 90 | Same as 84873034 | 90 | Same as RM17TE00 | Same as RM17TE00 | 90 | Same as RM17TU00 | Same as RM17TU00 | 90 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 90 | Same as RM17TT00 | 90 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 90 | Same as RM35UB330 | Same as RM35UB330 | 90 | Same as RM35UB3N30 | Same as RM35UB3N30 | 90 | Same as RM17UB310 | Same as RM17UB310
|  | Depth |  |  | depth | Published |  | mm | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 72 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | 73 | Same as 84873034 | 72 | Same as RM17TE00 | Same as RM17TE00 | 72 | Same as RM17TU00 | Same as RM17TU00 | 72 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 72 | Same as RM17TT00 | 72 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 72 | Same as RM35UB330 | Same as RM35UB330 | 72 | Same as RM35UB3N30 | Same as RM35UB3N30 | 72 | Same as RM17UB310 | Same as RM17UB310
Weight (without packaging) |  |  |  |  | net weight | Published |  | g | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 85 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 80 | Same as RM17TE00 | Same as RM17TE00 | 80 | Same as RM17TU00 | Same as RM17TU00 | 80 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 80 | Same as RM17TT00 | 120 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 130 | Same as RM35UB330 | Same as RM35UB330 | 130 | Same as RM35UB3N30 | Same as RM35UB3N30 | 80 | Same as RM17UB310 | Same as RM17UB310 |  | ? | To be updated | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 130 |  | 75
Mounting |  | Without socket | IEC/EN 60715 |  | mounting support | Published | Published |  | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | On 35 mm DIN rail | Same as RM17TE00 | Same as RM17TE00 | On 35 mm DIN rail | Same as RM17TU00 | Same as RM17TU00 | On 35 mm DIN rail | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | On 35 mm DIN rail | Same as RM17TT00 | On 35 mm DIN rail | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | On 35 mm DIN rail | Same as RM35UB330 | Same as RM35UB330 | On 35 mm DIN rail | Same as RM35UB3N30 | Same as RM35UB3N30 | On 35 mm DIN rail | Same as RM17UB310 | Same as RM17UB310 |  | On 35 mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail |  |  | DIN rail snap-on mounting without any tool |  | Mounting in DIN rail according EN50022
|  | With socket | IEC/EN 60715 |  | mounting support |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | - | - | - | - | - | - | - | - |  | -
Mounting position |  | In relation to normal vertical mounting plane |  | Common C_Rly Spec | mounting position | Published | Published |  | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Any position | Same as RM17TE00 | Same as RM17TE00 | Any position | Same as RM17TU00 | Same as RM17TU00 | Any position | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Any position | Same as RM17TT00 | Any position | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Any position | Same as RM35UB330 | Same as RM35UB330 | Any position | Same as RM35UB3N30 | Same as RM35UB3N30 | Any position | Same as RM17UB310 | Same as RM17UB310 |  | Any position | Any position | Any position | Any position | Any position | Any position | Any position |  |  | Any position |  | Not specified
Minimum distance to adjacent devices |  | Horizontal |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | 1x product height | 1x product height | 1x product height | 1x product height | 1x product height | 1x product height | 1x product height | 1x product height | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1x product height | Same as RM17TE00 | Same as RM17TE00 | 1x product height | Same as RM17TU00 | Same as RM17TU00 | 1x product height | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1x product height | Same as RM17TT00 | 1x product height | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1x product height | Same as RM35UB330 | Same as RM35UB330 | 1x product height | Same as RM35UB3N30 | Same as RM35UB3N30 | 1x product height | Same as RM17UB310 | Same as RM17UB310 |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | None |  | Not specified
|  | Vertical |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | 1x product width | 1x product width | 1x product width | 1x product width | 1x product width | 1x product width | 1x product width | 1x product width | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1x product width | Same as RM17TE00 | Same as RM17TE00 | 1x product width | Same as RM17TU00 | Same as RM17TU00 | 1x product width | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1x product width | Same as RM17TT00 | 1x product width | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1x product width | Same as RM35UB330 | Same as RM35UB330 | 1x product width | Same as RM35UB3N30 | Same as RM35UB3N30 | 1x product width | Same as RM17UB310 | Same as RM17UB310 |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | None |  | Not specified
Wiring connection (Clamping Capacity) |  | Solid cable without cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM17TE00 | Same as RM17TE00 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM17TU00 | Same as RM17TU00 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1 conductor: 0.5…4 (AWG 20…AWG 11) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM17TT00 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM35UB330 | Same as RM35UB330 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM35UB3N30 | Same as RM35UB3N30 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | Same as RM17UB310 | Same as RM17UB310 |  | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | 1 conductor:0.5…4 2 conductor:0.5…2.5 | 2 conductor: 2.5 | 2 conductor: 2.5 | 2 conductor: 2.5 | 2 conductor: 2.5 | 2 conductor: 2.5 | 1 conductor: 4 (AWG11) 2 conductor:2.5 (AWG14) | 1 conductor: 4 (AWG11) 2 conductor:2.5 (AWG14) | 2 conductor:0.75…2.5 (AWG18…AWG14) |  | Not specified
|  | Flexible cable with cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | Same as RM17TE00 | Same as RM17TE00 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | Same as RM17TU00 | Same as RM17TU00 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | Same as RM17TT00 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | Same as RM35UB330 | Same as RM35UB330 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | Same as RM35UB3N30 | Same as RM35UB3N30 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | Same as RM17UB310 | Same as RM17UB310 |  | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | 1 conductor:0.2…2.5 2 conductor:0.2…1.5 | 2 conductor: 1.5 | 2 conductor: 1.5 | 2 conductor: 1.5 | 2 conductor: 1.5 | 2 conductor: 1.5 | 2 conductor: 1.5 (AWG16) | 2 conductor: 1.5 (AWG16) | 2 conductor:0.5…4 (AWG20…AWG12) |  | Not specified
|  | Solid cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Flexible cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Tightening torque | IEC60947-1 | Common C_Rly Spec | tightening torque | Published | Published | Nm | 0.6…1 Nm | 0.6…1 Nm | 0.6…1 Nm | 0.6…1 Nm | 0.6…1 Nm | 0.6…1 Nm | 0.6…1 Nm | 0.6…1 Nm | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 0.6…1 Nm | Same as RM17TE00 | Same as RM17TE00 | 0.6…1 Nm | Same as RM17TU00 | Same as RM17TU00 | 0.6…1 Nm | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 0.6…1 Nm | Same as RM17TT00 | 0.6…1 Nm | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 0.6…1 Nm | Same as RM35UB330 | Same as RM35UB330 | 0.6…1 Nm | Same as RM35UB3N30 | Same as RM35UB3N30 | 0.6…1 Nm | Same as RM17UB310 | Same as RM17UB310 |  | 0.6…1.0 | 0.6…1 | 0.6…1.1 | 0.6…1.1 | 0.6…1.1 | 0.6…1.1 | 0.6…1.1 | Max 1 | Max 1 | 0.6…0.8 | 0.54Nm (Rec) 0.59Nm (Max) | 0.5Nm (Max)
|  | Cable stripping length |  | Common C_Rly Spec | cable stripping length |  |  | mm | 6mm (Screw Terminal) | 6mm (Screw Terminal) | 6mm (Screw Terminal) | 6mm (Screw Terminal) | 6mm (Screw Terminal) | 6mm (Screw Terminal) | 6mm (Screw Terminal) | 6mm (Screw Terminal) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 6mm (Screw Terminal) | Same as RM17TE00 | Same as RM17TE00 | 6mm (Screw Terminal) | Same as RM17TU00 | Same as RM17TU00 | 6mm (Screw Terminal) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 6mm (Screw Terminal) | Same as RM17TT00 | 6mm (Screw Terminal) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 6mm (Screw Terminal) | Same as RM35UB330 | Same as RM35UB330 | 6mm (Screw Terminal) | Same as RM35UB3N30 | Same as RM35UB3N30 | 6mm (Screw Terminal) | Same as RM17UB310 | Same as RM17UB310 |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified |  |  | 7 |  | Not specified
Duty time |  |  |  | Common C_Rly Spec | duty time |  |  | % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 100% | Same as RM17TE00 | Same as RM17TE00 | 100% | Same as RM17TU00 | Same as RM17TU00 | 100% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 100% | Same as RM17TT00 | 100% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 100% | Same as RM35UB330 | Same as RM35UB330 | 100% | Same as RM35UB3N30 | Same as RM35UB3N30 | 100% | Same as RM17UB310 | Same as RM17UB310 |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified |  |  | 100 |  | Not specified
Electromagnetic Compatibility
Immunity |  | Generic immunity standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | IEC61000-6-1, IEC 61000-6-2 | Same as RM17TE00 | Same as RM17TE00 | IEC61000-6-1, IEC 61000-6-2 | Same as RM17TU00 | Same as RM17TU00 | IEC61000-6-1, IEC 61000-6-2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | IEC61000-6-1, IEC 61000-6-2 | Same as RM17TT00 | IEC61000-6-1, IEC 61000-6-2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | IEC61000-6-1, IEC 61000-6-2 | Same as RM35UB330 | Same as RM35UB330 | IEC61000-6-1, IEC 61000-6-2 | Same as RM35UB3N30 | Same as RM35UB3N30 | IEC61000-6-1, IEC 61000-6-2 | Same as RM17UB310 | Same as RM17UB310 |  | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-2 | IEC50082-2 | IEC50082-2 | IEC50082-2 | IEC50082-2 | IEC50082-2 | Not specified | Not specified | IEC61000-6-1, IEC61000-6-2 |  | IEC61000-6-2
|  | Electrostatic discharge | IEC61000-4-2 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Level III (Contact : 6kV / Air : 8kV) | Same as RM17TE00 | Same as RM17TE00 | Level III (Contact : 6kV / Air : 8kV) | Same as RM17TU00 | Same as RM17TU00 | Level III (Contact : 6kV / Air : 8kV) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Level III (Contact : 6kV / Air : 8kV) | Same as RM17TT00 | Level III (Contact : 6kV / Air : 8kV) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Level III (Contact : 6kV / Air : 8kV) | Same as RM35UB330 | Same as RM35UB330 | Level III (Contact : 6kV / Air : 8kV) | Same as RM35UB3N30 | Same as RM35UB3N30 | Level III (Contact : 6kV / Air : 8kV) | Same as RM17UB310 | Same as RM17UB310 |  | Level III (Contact : 6kV / Air : 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Not specified | Not specified | Level 3 (6kV / 8kV) |  | Not specified
|  | Radiated RF & electromagnetic field | IEC61000-4-3 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM17TE00 | Same as RM17TE00 | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM17TU00 | Same as RM17TU00 | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM17TT00 | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM35UB330 | Same as RM35UB330 | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM35UB3N30 | Same as RM35UB3N30 | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Same as RM17UB310 | Same as RM17UB310 |  | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Not specified | Not specified | Level 3 (10V/m) |  | Not specified
|  | Fast transient / burst | IEC61000-4-4 |  | electromagnetic compatibility | Published |  |  | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level IV (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM17TE00 | Same as RM17TE00 | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM17TU00 | Same as RM17TU00 | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM17TT00 | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM35UB330 | Same as RM35UB330 | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM35UB3N30 | Same as RM35UB3N30 | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Same as RM17UB310 | Same as RM17UB310 |  | Level III (Supply: 2kV, 5kHx / 100kHz) (I/O: 2kV, 5kHx / 100kHz) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Not specified | Not specified | Level 3 (2kV / 2kHz) |  | Not specified
|  | Surge | IEC61000-4-5 |  | electromagnetic compatibility | Published |  |  | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level IV (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM17TE00 | Same as RM17TE00 | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM17TU00 | Same as RM17TU00 | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM17TT00 | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM35UB330 | Same as RM35UB330 | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM35UB3N30 | Same as RM35UB3N30 | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Same as RM17UB310 | Same as RM17UB310 |  | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Not specified | Not specified | Level 3 (2kV phase-phase) |  | Not specified
|  | Conducted RF disturbance | IEC61000-4-6 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (10Vrms : 0.15MHz to 80MHz) | Level III (10Vrms : 0.15MHz to 80MHz) | Level III (10Vrms : 0.15MHz to 80MHz) | Level III (10Vrms : 0.15MHz to 80MHz) | Level III (10Vrms : 0.15MHz to 80MHz) | Level III (10Vrms : 0.15MHz to 80MHz) | Level III (10Vrms : 0.15MHz to 80MHz) | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM17TE00 | Same as RM17TE00 | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM17TU00 | Same as RM17TU00 | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM17TT00 | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM35UB330 | Same as RM35UB330 | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM35UB3N30 | Same as RM35UB3N30 | Level III (10Vrms : 0.15MHz to 80MHz) | Same as RM17UB310 | Same as RM17UB310 |  | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Not specified | Not specified | Level 3 (10V) |  | Not specified
|  | Power frequency magnetic field | IEC61000-4-8 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM17TE00 | Same as RM17TE00 | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM17TU00 | Same as RM17TU00 | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM17TT00 | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM35UB330 | Same as RM35UB330 | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM35UB3N30 | Same as RM35UB3N30 | Level IV (30A/m : continous) (300A/m : 3s) | Same as RM17UB310 | Same as RM17UB310 |  | - | -
|  | Voltage dips, short interruption & variations on power line | IEC61000-4-11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM17TE00 | Same as RM17TE00 | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM17TU00 | Same as RM17TU00 | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM17TT00 | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM35UB330 | Same as RM35UB330 | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM35UB3N30 | Same as RM35UB3N30 | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Same as RM17UB310 | Same as RM17UB310 |  | - | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Not specified | Not specified | Not specified |  | Not specified
|  | 1 MHz oscillation wave | IEC61000-4-18 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM17TE00 | Same as RM17TE00 | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM17TU00 | Same as RM17TU00 | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM17TT00 | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM35UB330 | Same as RM35UB330 | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM35UB3N30 | Same as RM35UB3N30 | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Same as RM17UB310 | Same as RM17UB310 |  | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | -
|  | DC voltage interruption | IEC61000-4-29 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | -
|  | Low frequency harmonics | IEC61000-4-13 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | Not tested | Not tested | Not tested | Not tested | Not tested | Not specified | Not specified | Class 3 |  | Not specified
|  | Conducted low frequency interference (harmonics) | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM17TE00 | Same as RM17TE00 | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM17TU00 | Same as RM17TU00 | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM17TT00 | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM35UB330 | Same as RM35UB330 | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM35UB3N30 | Same as RM35UB3N30 | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | Same as RM17UB310 | Same as RM17UB310 |  | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | · | ? | ? | ? | ? | ? | Not specified | Not specified
Emission |  | Generic emission standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | IEC61000-6-3, IEC 61000-6-4 | Same as RM17TE00 | Same as RM17TE00 | IEC61000-6-3, IEC 61000-6-4 | Same as RM17TU00 | Same as RM17TU00 | IEC61000-6-3, IEC 61000-6-4 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | IEC61000-6-3, IEC 61000-6-4 | Same as RM17TT00 | IEC61000-6-3, IEC 61000-6-4 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | IEC61000-6-3, IEC 61000-6-4 | Same as RM35UB330 | Same as RM35UB330 | IEC61000-6-3, IEC 61000-6-4 | Same as RM35UB3N30 | Same as RM35UB3N30 | IEC61000-6-3, IEC 61000-6-4 | Same as RM17UB310 | Same as RM17UB310 |  | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC50081-1, IEC50081-2 | IEC50081-1, IEC50081-2 | IEC50081-1, IEC50081-2 | IEC50081-1, IEC50081-2 | IEC50081-1, IEC50081-2 | Not specified | Not specified | IEC61000-6-3, IEC61000-6-4 |  | IEC50081-1
|  | Radiated RF & electromagnetic field (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B | Class B | Class B | Class B | Class B | Class B | Class B | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Class B | Same as RM17TE00 | Same as RM17TE00 | Class B | Same as RM17TU00 | Same as RM17TU00 | Class B | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Class B | Same as RM17TT00 | Class B | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Class B | Same as RM35UB330 | Same as RM35UB330 | Class B | Same as RM35UB3N30 | Same as RM35UB3N30 | Class B | Same as RM17UB310 | Same as RM17UB310 |  | - | Class B | Class B Group 1 | Class B Group 1 | Class B Group 1 | Class B Group 1 | Class B Group 1 | Not specified | Not specified | Class B |  | Not specified
|  | Radiated RF & electromagnetic field (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Class B, Group 1 | Same as RM17TE00 | Same as RM17TE00 | Class B, Group 1 | Same as RM17TU00 | Same as RM17TU00 | Class B, Group 1 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Class B, Group 1 | Same as RM17TT00 | Class B, Group 1 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Class B, Group 1 | Same as RM35UB330 | Same as RM35UB330 | Class B, Group 1 | Same as RM35UB3N30 | Same as RM35UB3N30 | Class B, Group 1 | Same as RM17UB310 | Same as RM17UB310 |  | Class B, Group 2 | Class B | Class B Group 1 | Class B Group 1 | Class B Group 1 | Class B Group 1 | Class B Group 1 | Not specified | Not specified | - |  | Not specified
|  | Radiated emission from enclosure port | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | EMC 2 | Same as RM17TE00 | Same as RM17TE00 | EMC 2 | Same as RM17TU00 | Same as RM17TU00 | EMC 2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | EMC 2 | Same as RM17TT00 | EMC 2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | EMC 2 | Same as RM35UB330 | Same as RM35UB330 | EMC 2 | Same as RM35UB3N30 | Same as RM35UB3N30 | EMC 2 | Same as RM17UB310 | Same as RM17UB310 |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | Not specified | Not specified | Not specified |  | -
|  | Conducted RF emission on power line (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B | Class B | Class B | Class B | Class B | Class B | Class B | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Class B | Same as RM17TE00 | Same as RM17TE00 | Class B | Same as RM17TU00 | Same as RM17TU00 | Class B | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Class B | Same as RM17TT00 | Class B | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Class B | Same as RM35UB330 | Same as RM35UB330 | Class B | Same as RM35UB3N30 | Same as RM35UB3N30 | Class B | Same as RM17UB310 | Same as RM17UB310 |  | - | Class B | Class B Group 1 | Class B Group 1 | Class B Group 1 | Class B Group 1 | Class B Group 1 | Not specified | Not specified | Class B |  | Not specified
|  | Conducted RF emission on power line (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Class B, Group 1 | Same as RM17TE00 | Same as RM17TE00 | Class B, Group 1 | Same as RM17TU00 | Same as RM17TU00 | Class B, Group 1 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Class B, Group 1 | Same as RM17TT00 | Class B, Group 1 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Class B, Group 1 | Same as RM35UB330 | Same as RM35UB330 | Class B, Group 1 | Same as RM35UB3N30 | Same as RM35UB3N30 | Class B, Group 1 | Same as RM17UB310 | Same as RM17UB310 |  | Class B, Group 2 | Class B | Class B Group 1 | Class B Group 1 | Class B Group 1 | Class B Group 1 | Class B Group 1 | Not specified | Not specified | - |  | Not specified
|  | Conducted emission | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | EMC 2 | Same as RM17TE00 | Same as RM17TE00 | EMC 2 | Same as RM17TU00 | Same as RM17TU00 | EMC 2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | EMC 2 | Same as RM17TT00 | EMC 2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | EMC 2 | Same as RM35UB330 | Same as RM35UB330 | EMC 2 | Same as RM35UB3N30 | Same as RM35UB3N30 | EMC 2 | Same as RM17UB310 | Same as RM17UB310 |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | Not specified | Not specified | Not specified |  | -
Electrical Isolation
Degree of pollution |  |  | IEC60664-1 | Common C_Rly Spec | pollution degree | Published | Published |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 3 | Same as RM17TE00 | Same as RM17TE00 | 3 | Same as RM17TU00 | Same as RM17TU00 | 3 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 3 | Same as RM17TT00 | 3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 3 | Same as RM35UB330 | Same as RM35UB330 | 3 | Same as RM35UB3N30 | Same as RM35UB3N30 | 3 | Same as RM17UB310 | Same as RM17UB310
Overvoltage category |  |  | IEC60664-1 | Common C_Rly Spec | overvoltage category | Published | Published |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 3 | Same as RM17TE00 | Same as RM17TE00 | 3 | Same as RM17TU00 | Same as RM17TU00 | 3 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 3 | Same as RM17TT00 | 3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 3 | Same as RM35UB330 | Same as RM35UB330 | 3 | Same as RM35UB3N30 | Same as RM35UB3N30 | 3 | Same as RM17UB310 | Same as RM17UB310
Circuit Group | Terminal | Supply |  |  | circuit group | Published |  |  | L1, L2, L3 | L1, L2, L3 | L1, L2, L3 | L1, L2, L3 | L1, L2, L3 | L1, L2, L3 | L1, L2, L3 | L1, L2, L3 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | L1, L2, L3 | Same as RM17TE00 | Same as RM17TE00 | L1, L2, L3 | Same as RM17TU00 | Same as RM17TU00 | L1, L2, L3 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | L1, L2, L3 | Same as RM17TT00 | L1, L2, L3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | L1, L2, L3 | Same as RM35UB330 | Same as RM35UB330 | L1, L2, L3, N | Same as RM35UB3N30 | Same as RM35UB3N30 | L1, L2, L3 | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 |  |  | circuit group | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 |  |  | circuit group | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 |  |  | circuit group | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 1 |  |  | circuit group | Published |  |  | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 11,12,14 | Same as RM17TE00 | Same as RM17TE00 | 11,12,14 | Same as RM17TU00 | Same as RM17TU00 | 11,12,14 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 11,12,14 | Same as RM17TT00 | 11,12,14 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 11,12,14 | Same as RM35UB330 | Same as RM35UB330 | 11,12,14 | Same as RM35UB3N30 | Same as RM35UB3N30 | 11,12,14 | Same as RM17UB310 | Same as RM17UB310
|  | Output 2 |  |  | circuit group | Published |  |  | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 21,22,24 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 21,22,24 | Same as RM35UB330 | Same as RM35UB330 | 21,22,24 | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
| Rated | Supply | [6 empty] | 208..480 AC | 380..480 AC | 208..240 AC | 380..480 AC | 208..240 AC | 380..480 AC | 208..240 AC | 208..440 AC | Same as RM17TG20 | Same as RM17TG20 | 208..480 AC | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 208..480 AC | Same as RM17TE00 | Same as RM17TE00 | 208..480 AC | Same as RM17TU00 | Same as RM17TU00 | 208..480 AC | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 208..480 AC | Same as RM17TT00 | 208..480 AC | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 220..480 AC | Same as RM35UB330 | Same as RM35UB330 | 120..277 AC | Same as RM35UB3N30 | Same as RM35UB3N30 | 208..480 AC | Same as RM17UB310 | Same as RM17UB310
| Voltage | Input 1 | [6 empty] | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
| Spec | Input 2 | [6 empty] | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 | [6 empty] | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 1 | [6 empty] | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | Same as RM17TG20 | Same as RM17TG20 | 250V | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 250V | Same as RM17TE00 | Same as RM17TE00 | 250V | Same as RM17TU00 | Same as RM17TU00 | 250V | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 250V | Same as RM17TT00 | 250V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 250V | Same as RM35UB330 | Same as RM35UB330 | 250V | Same as RM35UB3N30 | Same as RM35UB3N30 | 250V | Same as RM17UB310 | Same as RM17UB310
|  | Output 2 | [6 empty] | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 250V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 250V | Same as RM35UB330 | Same as RM35UB330 | 250V | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Rated Insulation Voltage |  | Supply | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | 500V | 500V | 500V | 500V | 500V | 500V | 500V | Same as RM17TG20 | Same as RM17TG20 | 500V | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 500V | Same as RM17TE00 | Same as RM17TE00 | 500V | Same as RM17TU00 | Same as RM17TU00 | 500V | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 500V | Same as RM17TT00 | 500V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 500V | Same as RM35UB330 | Same as RM35UB330 | 500V | Same as RM35UB3N30 | Same as RM35UB3N30 | 500V | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | Same as RM17TG20 | Same as RM17TG20 | 250V | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 250V | Same as RM17TE00 | Same as RM17TE00 | 250V | Same as RM17TU00 | Same as RM17TU00 | 250V | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 250V | Same as RM17TT00 | 250V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 250V | Same as RM35UB330 | Same as RM35UB330 | 250V | Same as RM35UB3N30 | Same as RM35UB3N30 | 250V | Same as RM17UB310 | Same as RM17UB310
|  | Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 250V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 250V | Same as RM35UB330 | Same as RM35UB330 | 250V | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 500V | 500V | 500V | 500V | 500V | 500V | 500V | 500V | Same as RM17TG20 | Same as RM17TG20 | 500V | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 500V | Same as RM17TE00 | Same as RM17TE00 | 500V | Same as RM17TU00 | Same as RM17TU00 | 500V | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 500V | Same as RM17TT00 | 500V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 500V | Same as RM35UB330 | Same as RM35UB330 | 500V | Same as RM35UB3N30 | Same as RM35UB3N30 | 500V | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 500V | 500V | 500V | 500V | 500V | 500V | 500V | 500V | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 500V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 500V | Same as RM35UB330 | Same as RM35UB330 | 500V | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 250V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 250V | Same as RM35UB330 | Same as RM35UB330 | 250V | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Rated Impulse Voltage |  | Supply | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | Same as RM17TG20 | Same as RM17TG20 | 4kV, OVC3 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 4kV, OVC3 | Same as RM17TE00 | Same as RM17TE00 | 4kV, OVC3 | Same as RM17TU00 | Same as RM17TU00 | 4kV, OVC3 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 4kV, OVC3 | Same as RM17TT00 | 4kV, OVC3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 4kV, OVC3 | Same as RM35UB330 | Same as RM35UB330 | 4kV, OVC3 | Same as RM35UB3N30 | Same as RM35UB3N30 | 4kV, OVC3 | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | Same as RM17TG20 | Same as RM17TG20 | 4kV, OVC3 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 4kV, OVC3 | Same as RM17TE00 | Same as RM17TE00 | 4kV, OVC3 | Same as RM17TU00 | Same as RM17TU00 | 4kV, OVC3 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 4kV, OVC3 | Same as RM17TT00 | 4kV, OVC3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 4kV, OVC3 | Same as RM35UB330 | Same as RM35UB330 | 4kV, OVC3 | Same as RM35UB3N30 | Same as RM35UB3N30 | 4kV, OVC3 | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 4kV, OVC3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 4kV, OVC3 | Same as RM35UB330 | Same as RM35UB330 | 4kV, OVC3 | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 4kV, OVC3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 4kV, OVC3 | Same as RM35UB330 | Same as RM35UB330 | 4kV, OVC3 | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Dielectric test voltage |  | Supply / Input 1 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Output 1 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | Same as RM17TG20 | Same as RM17TG20 | 2.0kV, 50/60Hz for 1 min | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 2.0kV, 50/60Hz for 1 min | Same as RM17TE00 | Same as RM17TE00 | 2.0kV, 50/60Hz for 1 min | Same as RM17TU00 | Same as RM17TU00 | 2.0kV, 50/60Hz for 1 min | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 2.0kV, 50/60Hz for 1 min | Same as RM17TT00 | 2.0kV, 50/60Hz for 1 min | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 2.0kV, 50/60Hz for 1 min | Same as RM35UB330 | Same as RM35UB330 | 2.0kV, 50/60Hz for 1 min | Same as RM35UB3N30 | Same as RM35UB3N30 | 2.0kV, 50/60Hz for 1 min | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 2.0kV, 50/60Hz for 1 min | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 2.0kV, 50/60Hz for 1 min | Same as RM35UB330 | Same as RM35UB330 | 2.0kV, 50/60Hz for 1 min | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 1 / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | 2.0kV, 50/60Hz for 1 min | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 2.0kV, 50/60Hz for 1 min | Same as RM35UB330 | Same as RM35UB330 | 2.0kV, 50/60Hz for 1 min | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Insulation resistance |  | Supply / Input 1 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Output 1 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | Same as RM17TG20 | Same as RM17TG20 | >100 MOhm at 500 V DC | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | >100 MOhm at 500 V DC | Same as RM17TE00 | Same as RM17TE00 | >100 MOhm at 500 V DC | Same as RM17TU00 | Same as RM17TU00 | >100 MOhm at 500 V DC | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | >100 MOhm at 500 V DC | Same as RM17TT00 | >100 MOhm at 500 V DC | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | >100 MOhm at 500 V DC | Same as RM35UB330 | Same as RM35UB330 | >100 MOhm at 500 V DC | Same as RM35UB3N30 | Same as RM35UB3N30 | >100 MOhm at 500 V DC | Same as RM17UB310 | Same as RM17UB310
|  | Supply / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | >100 MOhm at 500 V DC | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | >100 MOhm at 500 V DC | Same as RM35UB330 | Same as RM35UB330 | >100 MOhm at 500 V DC | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Output 1 / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | >100 MOhm at 500 V DC | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | >100 MOhm at 500 V DC | Same as RM35UB330 | Same as RM35UB330 | >100 MOhm at 500 V DC | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 3 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 2 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Input 1 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Power Supply Characteristics
Rated supply voltage, Us |  |  |  |  | [Us] rated supply voltage | Published | Published | V | ~ 3 x 208…3 x 480 | ~ 3 x 380… 3 x 480 | ~ 3 x 200…3 x 240 | ~ 3 x 380… 3 x 480 | ~ 3 x 200…3 x 240 | ~ 3 x 380… 3 x 480 | ~ 3 x 200…3 x 240 | ~ 3 x 208…3 x 440 | Same as RM17TG20 | Same as RM17TG20 | ~ 3 x 208…3 x 480 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | ~ 3 x 230…3 x 440 | Same as 84873034 | ~ 3 x 208…3 x 480 | Same as RM17TE00 | Same as RM17TE00 | ~ 3 x 208…3 x 480 | Same as RM17TU00 | Same as RM17TU00 | ~ 3 x 208…3 x 480 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | ~ 3 x 208…3 x 480 | Same as RM17TT00 | ~ 3 x 220…3 x 480 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | ~ 3 x 220…3 x 480 | Same as RM35UB330 | Same as RM35UB330 | ~ 3 x 120…3 x 277 | Same as RM35UB3N30 | Same as RM35UB3N30 | ~ 3 x 208…3 x 480 | Same as RM17UB310 | Same as RM17UB310 |  | ~ 3 x 208…3 x 480 | ~ 3 x 230…3 x 440 | RM4TR31: ~ 3 x 200…3 x 240 RM4TR32: ~ 3 x 300…3 x 500 RM4TR33: ~ 3 x 220 RM4TR33: ~ 3 x 400 | ~ 3 x 200…3 x 500 | RM4TU01: ~ 3 x 200…3 x 240 RM4TU02: ~ 3 x 380…3 x 500 | RM4TA01/31: ~ 3 x 200…3 x 240 RM4TA02/32: ~ 3 x 380…3 x 500 | RM4UB34: ~80…220 RM4UB35: ~160…300 | ~ 3 x 230…3 x 440 | ~ 3 x 230…3 x 440 | ~ 3 x 300…3 x 500 |  | ~ 3 x 208…3 x 480
Supply voltage operating range |  |  |  |  | supply voltage limits | Published | Published | V | ~ 3 x 183…3 x 528 | ~ 3 x 304…3 x 576 | ~ 3 x 160…3 x 288 | ~ 3 x 304…3 x 576 | ~ 3 x 160…3 x 288 | ~ 3 x 304…3 x 576 | ~ 3 x 160…3 x 288 | ~ 3 x 183…3 x 484 | Same as RM17TG20 | Same as RM17TG20 | ~ 3 x 183…3 x 528 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | ~ 3 x 200…3 x 460 | Same as 84873034 | ~ 3 x 183…3 x 528 | Same as RM17TE00 | Same as RM17TE00 | ~ 3 x 183…3 x 528 | Same as RM17TU00 | Same as RM17TU00 | ~ 3 x 183…3 x 528 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | ~ 3 x 183…3 x 528 | Same as RM17TT00 | ~ 3 x 194…3 x 528 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | ~ 3 x 194…3 x 528 | Same as RM35UB330 | Same as RM35UB330 | ~ 3 x 114…3 x 329 | Same as RM35UB3N30 | Same as RM35UB3N30 | ~ 3 x 183…3 x 528 | Same as RM17UB310 | Same as RM17UB310 |  | ~ 3 x 183…3 x 528 | ~ 3 x 207…3 x 484 | RM4TR31/33: ~ 3 x 160…3 x 300 RM4TR32/34: ~ 3 x 290…3 x 580 | ~ 3 x 140…3 x 580 | RM4TU01: ~ 3 x 160…3 x 300 RM4TU01: ~ 3 x 290…3 x 580 | RM4TA01/31: ~ 3 x 160…3 x 300 RM4TA02/32: ~ 3 x 290…3 x 580 | RM4UB34: ~60…300 RM4UB35: ~160…300 | Not specified | Not specified | ~ 3 x 255…3 x 550 |  | ~ 3 x 177…3 x 550
Polarity on d.c. supply |  |  |  |  | polarity |  | Published |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | - | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Rated frequency |  |  |  |  | supply frequency | Published | Published | Hz | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 50 / 60 | Same as RM17TE00 | Same as RM17TE00 | 50 / 60 | Same as RM17TU00 | Same as RM17TU00 | 50 / 60 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 50 / 60 | Same as RM17TT00 | 50 / 60 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 50 / 60 | Same as RM35UB330 | Same as RM35UB330 | 50 / 60 | Same as RM35UB3N30 | Same as RM35UB3N30 | 50 / 60 | Same as RM17UB310 | Same as RM17UB310 |  | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 |  | 50 / 60
Frequency operating range |  |  |  |  | supply frequency | Published | Published | Hz | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 45…66 | Same as RM17TE00 | Same as RM17TE00 | 45…66 | Same as RM17TU00 | Same as RM17TU00 | 45…66 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 45…66 | Same as RM17TT00 | 45…66 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 45…66 | Same as RM35UB330 | Same as RM35UB330 | 45…66 | Same as RM35UB3N30 | Same as RM35UB3N30 | 45…66 | Same as RM17UB310 | Same as RM17UB310 |  | 45…66 | 49…61 | 47.5…63 | 47.5…63 | 47.5…63 | 47.5…63 | 47.5…63 | 49…61 | 49…61 | 45…66 |  | 45…66
Maximum power consumption |  |  |  |  | power consumption | Published | Published |  | 18VA @ 480VAC, 60Hz 12VA @ 400VAC, 50Hz | 18VA @ 480VAC, 60Hz 12VA @ 400VAC, 50Hz | 10VA @ 240VAC, 60Hz | 15VA | 10VA | 15VA | 10VA | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | 28VA @ 480VAC, 60Hz 18VA @ 415VAC, 50Hz | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz | Same as RM17TE00 | Same as RM17TE00 | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz | Same as RM17TU00 | Same as RM17TU00 | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz | Same as RM17TT00 | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz | Same as RM35UB330 | Same as RM35UB330 | 3.9VA @ 480VAC, 60Hz | Same as RM35UB3N30 | Same as RM35UB3N30 | 28VA @ 480VAC, 60Hz 18VA @ 400VAC, 50Hz | Same as RM17UB310 | Same as RM17UB310 |  | 25 | 25 | Not specified | Not specified | Not specified | Not specified | Not specified | 25 | 25 | 25mA / 18VA (400VAC) |  | 13VA (400VAC, 50Hz) by L2, L3
Immunity to micro-breakage |  |  |  |  | immunity to microbreaks | Published | Published | ms | =<20 @ Output Energized Internal Design Spec: =<40 @ Output Energized | =<20 @ Output Energized Internal Design Spec: =<40 @ Output Energized | =<20 @ Output Energized Internal Design Spec: =<40 @ Output Energized | =<20 @ Output Energized Internal Design Spec: =<40 @ Output Energized | =<20 @ Output Energized Internal Design Spec: =<40 @ Output Energized | =<20 @ Output Energized Internal Design Spec: =<40 @ Output Energized | =<20 @ Output Energized Internal Design Spec: =<40 @ Output Energized | =<20 @ Output Energized Internal Design Spec: =<40 @ Output Energized | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | =<20 @ Output Energized Internal Design Spec: =<40 @ Output Energized | Same as RM17TE00 | Same as RM17TE00 | =<20 @ Output Energized Internal Design Spec: =<40 @ Output Energized | Same as RM17TU00 | Same as RM17TU00 | =<20 @ Output Energized Internal Design Spec: =<40 @ Output Energized | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | =<20 @ Output Energized Internal Design Spec: =<40 @ Output Energized | Same as RM17TT00 | =<20 @ Output Energized Internal Design Spec: =<40 @ Output Energized | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | =<20 @ Output Energized Internal Design Spec: =<40 @ Output Energized | Same as RM35UB330 | Same as RM35UB330 | 5 | Same as RM35UB3N30 | Same as RM35UB3N30 | =<20 @ Output Energized Internal Design Spec: =<40 @ Output Energized | Same as RM17UB310 | Same as RM17UB310 |  | 10 |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | - |  | -
Supply terminal |  |  |  |  | supply terminal |  |  |  | L1-L3 | L1-L3 | L1-L3 | L1-L3 | L1-L3 | L1-L3 | L1-L3 | L1-L3 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | L1-L3 | Same as RM17TE00 | Same as RM17TE00 | L1-L3 | Same as RM17TU00 | Same as RM17TU00 | L1-L3 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | L1-L3 | Same as RM17TT00 | L1-L3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | L1-N | Same as RM35UB330 | Same as RM35UB330 | L1-L3 | Same as RM35UB3N30 | Same as RM35UB3N30 | L1-L3 | Same as RM17UB310 | Same as RM17UB310 |  | L1-L3 | L1-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L3 | Not specified | Not specified | L1-L2-L3 |  | L1-L2-L3
On Load Factor |  |  |  | Common C_Rly Spec | on-load factor |  |  | % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 100% | Same as RM17TE00 | Same as RM17TE00 | 100% | Same as RM17TU00 | Same as RM17TU00 | 100% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 100% | Same as RM17TT00 | 100% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 100% | Same as RM35UB330 | Same as RM35UB330 | 100% | Same as RM35UB3N30 | Same as RM35UB3N30 | 100% | Same as RM17UB310 | Same as RM17UB310 |  |  | Not specified
Release of input voltage |  |  |  |  | release of input voltage |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  | Not specified
Input Circuit Characteristics
Monitoring functions |  | Phase lost |  |  | monitoring functions | Published |  |  | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TE00 | Same as RM17TE00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TU00 | Same as RM17TU00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TT00 | governed by response time only, status reflects to both R1 & R2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB330 | Same as RM35UB330 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB3N30 | Same as RM35UB3N30 | governed by response time only, status reflects to both R1 & R2 | Same as RM17UB310 | Same as RM17UB310 |  | · | · | · | · | · | · | - | · | · | · |  | ·
|  | Phase sequence |  |  | monitoring functions | Published |  |  | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TE00 | Same as RM17TE00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TU00 | Same as RM17TU00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TT00 | governed by response time only, status reflects to both R1 & R2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB330 | Same as RM35UB330 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB3N30 | Same as RM35UB3N30 | governed by response time only, status reflects to both R1 & R2 | Same as RM17UB310 | Same as RM17UB310 |  | · | · | · | · | · | · | - | · | · | can be switched off |  | ·
|  | Over / undervoltage (symmetry windows mode) |  |  | monitoring functions | Published |  |  | - | governed by time delay, status reflects to both R1 & R2 | governed by time delay, status reflects to both R1 & R2 | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | governed by time delay, status reflects to both R1 & R2 | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Over voltage |  |  | monitoring functions | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | governed by time delay, status reflects to both R1 & R2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | governed by time delay Tt1, status reflects to R1 | Same as RM35UB330 | Same as RM35UB330 | governed by time delay Tt1, status reflects to R1 | Same as RM35UB3N30 | Same as RM35UB3N30 | governed by time delay, status reflects to both R1 & R2 | Same as RM17UB310 | Same as RM17UB310 |  | - | - | · | - | - | - | - | - | - | · |  | -
|  | Undervoltage |  |  | monitoring functions | Published |  |  | - | - | - | governed by time delay, status reflects to both R1 & R2 | governed by time delay, status reflects to both R1 & R2 | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | governed by time delay, status reflects to both R1 & R2 | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | governed by time delay, status reflects to both R1 & R2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | governed by time delay Tt2, status reflects to R2 | Same as RM35UB330 | Same as RM35UB330 | governed by time delay Tt2, status reflects to R2 | Same as RM35UB3N30 | Same as RM35UB3N30 | governed by time delay, status reflects to both R1 & R2 | Same as RM17UB310 | Same as RM17UB310 |  | - | - | · | - | · | - | - | - | - | · |  | -
|  | Phase asymmetry |  |  | monitoring functions | Published |  |  | - | - | - | - | - | governed by time delay, status reflects to both R1 & R2 | governed by time delay, status reflects to both R1 & R2 | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | governed by time delay, status reflects to both R1 & R2 | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | governed by time delay, status reflects to both R1 & R2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | governed by time delay, status reflects to both R1 & R2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | - | - | - | · | - | - | - | - |  | -
|  | Disconnection of neutral |  |  | monitoring functions | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Voltage Regeneration |  |  | monitoring functions | Published |  |  | - | - | - | - | - | governed by time delay, status reflects to both R1 & R2 | governed by time delay, status reflects to both R1 & R2 | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Extreme undervoltage |  |  | monitoring functions | Published |  |  | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TE00 | Same as RM17TE00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TU00 | Same as RM17TU00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TT00 | governed by response time only, status reflects to both R1 & R2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB330 | Same as RM35UB330 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB3N30 | Same as RM35UB3N30 | governed by response time only, status reflects to both R1 & R2 | Same as RM17UB310 | Same as RM17UB310
|  | Extreme overvoltage |  |  | monitoring functions |  |  |  | - | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TE00 | Same as RM17TE00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TU00 | Same as RM17TU00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TT00 | governed by response time only, status reflects to both R1 & R2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB330 | Same as RM35UB330 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB3N30 | Same as RM35UB3N30 | governed by response time only, status reflects to both R1 & R2 | Same as RM17UB310 | Same as RM17UB310
|  | Extreme asymmetry |  |  | monitoring functions |  |  |  | - | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | governed by response time only, status reflects to both R1 & R2 | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | governed by response time only, status reflects to both R1 & R2 | Same as RM17TT00 | governed by response time only, status reflects to both R1 & R2 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB330 | Same as RM35UB330 | governed by response time only, status reflects to both R1 & R2 | Same as RM35UB3N30 | Same as RM35UB3N30 | governed by response time only, status reflects to both R1 & R2 | Same as RM17UB310 | Same as RM17UB310
Monitoring function characteristics |  | Measurement mode | [6 empty] | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Resistive Voltage Step Down | Same as RM17TE00 | Same as RM17TE00 | Resistive Voltage Step Down | Same as RM17TU00 | Same as RM17TU00 | Resistive Voltage Step Down | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Resistive Voltage Step Down | Same as RM17TT00 | Resistive Voltage Step Down | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Resistive Voltage Step Down | Same as RM35UB330 | Same as RM35UB330 | Resistive Voltage Step Down | Same as RM35UB3N30 | Same as RM35UB3N30 | Resistive Voltage Step Down | Same as RM17UB310 | Same as RM17UB310 |  | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down |  |  | Resistive Voltage Step Down |  | Resistive Voltage Step Down
|  | Internal input resistance |  |  | internal input resistance |  |  | W | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | Not specified | - | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified |  | Not specified
|  | Input terminal |  |  | input terminal |  |  |  | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | L1-L2-L3 | Same as RM17TE00 | Same as RM17TE00 | L1-L2-L3 | Same as RM17TU00 | Same as RM17TU00 | L1-L2-L3 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | L1-L2-L3 | Same as RM17TT00 | L1-L2-L3 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | L1-L2-L3 | Same as RM35UB330 | Same as RM35UB330 | L1-L2-L3-N | Same as RM35UB3N30 | Same as RM35UB3N30 | L1-L2-L3 | Same as RM17UB310 | Same as RM17UB310 |  | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 | L1-L3 | L1-L2-L3 | L1-L2-L3 | L1-L2-L3 |  | L1-L2-L3
|  | Input nominal voltage selection |  |  | Input nominal voltage selection |  |  | V | - | 380, 400, 415, 440, 480 | 200, 208, 220, 240 | 380, 400, 415, 440, 480 | 200, 208, 220, 240 | 380, 400, 415, 440, 480 | 200, 208, 220, 240 | - | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG21 | Same as 84873034 | 208, 220, 380, 400, 415, 440, 480 | Same as RM17TE00 | Same as RM17TE00 | 208, 220, 380, 400, 415, 440, 480 | Same as RM17TU00 | - | 208, 220, 380, 400, 415, 440, 480 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 208, 220, 380, 400, 415, 440, 480 | Same as RM17TT00 | 220, 380, 400, 415, 440, 480 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 220, 380, 400, 415, 440, 480 | Same as RM35UB330 | Same as RM35UB330 | 120, 127, 220, 230, 240, 260, 277 | Same as RM35UB3N30 | Same as RM35UB3N30 | 208, 220, 380, 400, 415, 440, 480 | Same as RM17UB310 | Same as RM17UB310 |  | Fixed @ ~ 3 x 183…3 x 528 | Fixed @ ~ 3 x 230…3 x 440 | RM4TR31/33: ~ 3 x 160…3 x 300 RM4TR32/34: ~ 3 x 290…3 x 580 | Fixed @ ~ 3 x 140…3 x 580 | RM4TU01: ~ 3 x 160…3 x 300 RM4TU01: ~ 3 x 290…3 x 580 | RM4TU0131: ~ 3 x 160…3 x 300 RM4TU02/32: ~ 3 x 290…3 x 580 | RM4UB34: ~ 160…300 RM4UB35: ~ 160…300 | Fixed @ ~ 3 x 230…3 x 440 | Fixed @ ~ 3 x 230…3 x 440 | Fixed @ ~ 3 x 255…3 x 550 |  | Fixed @ ~ 3 x 177…3 x 550
|  | permissible input overload |  |  | permissible input overload |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | - | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG22 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified |  | Not specified
|  | Rated frequency |  |  | input frequency | Published | Published | Hz | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 50 / 60 | Same as RM17TE00 | Same as RM17TE00 | 50 / 60 | Same as RM17TU00 | Same as RM17TU00 | 50 / 60 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 50 / 60 | Same as RM17TT00 | 50 / 60 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 50 / 60 | Same as RM35UB330 | Same as RM35UB330 | 50 / 60 | Same as RM35UB3N30 | Same as RM35UB3N30 | 50 / 60 | Same as RM17UB310 | Same as RM17UB310 |  | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 |  | 50 / 60
|  | Frequency operating range |  |  | input frequency | Published | Published | Hz | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 45…66 | Same as RM17TE00 | Same as RM17TE00 | 45…66 | Same as RM17TU00 | Same as RM17TU00 | 45…66 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 45…66 | Same as RM17TT00 | 45…66 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 45…66 | Same as RM35UB330 | Same as RM35UB330 | 45…66 | Same as RM35UB3N30 | Same as RM35UB3N30 | 45…66 | Same as RM17UB310 | Same as RM17UB310 |  | 45…66 | 49…61 | 47.5…63 | 47.5…63 | 47.5…63 | 47.5…63 | 47.5…63 | 49…61 | 49…61 | 45…66 |  | 45…66
|  | Setting accuracy |  |  | setting accuracy of the switching threshold | Published | Published |  | - | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | Same as RM17TE00 | Same as RM17TE00 | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | Same as RM17TU00 | Same as RM17TU00 | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | Same as RM35UB330 | Same as RM35UB330 | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | Same as RM35UB3N30 | Same as RM35UB3N30 | +/- 10% of selected Un Internal Design spec: 9% of selected Un (5% Base accuracy, 2% Marking, 2% Equipment uncertainty) | Same as RM17UB310 | Same as RM17UB310 |  | - | - | +/- 3% of set value | +/- 3% of set value | +/- 3% of set value | +/- 3% of set value | +/- 3% of set value | - | - | Not specified |  | -
|  | Repeat accuracy (constant parameters) |  |  | repeat accuracy of the switching threshold | Published | Published | % | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | +/- 0.5% | Same as RM17TE00 | Same as RM17TE00 | +/- 0.5% | Same as RM17TU00 | Same as RM17TU00 | +/- 0.5% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | +/- 0.5% | Same as RM17TT00 | +/- 0.5% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | +/- 0.5% | Same as RM35UB330 | Same as RM35UB330 | +/- 0.5% | Same as RM35UB3N30 | Same as RM35UB3N30 | +/- 0.5% | Same as RM17UB310 | Same as RM17UB310 |  | +/- 0.5% | +/- 0.5% | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | < +/- 0.2% |  | +/- 0.5% on full scale
|  | Measurement method |  |  | measurement method | Published | Published |  | Non True RMS | True RMS | True RMS | True RMS | True RMS | True RMS | True RMS | Non True RMS | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | True RMS | Same as RM17TE00 | Same as RM17TE00 | True RMS | Same as RM17TU00 | Same as RM17TU00 | True RMS | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | True RMS | Same as RM17TT00 | True RMS | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | True RMS | Same as RM35UB330 | Same as RM35UB330 | True RMS | Same as RM35UB3N30 | Same as RM35UB3N30 | True RMS | Same as RM17UB310 | Same as RM17UB310 |  | Not specified | Not specified | Voltage Peak Detection | Voltage Peak Detection | Voltage Peak Detection | Voltage Peak Detection | Voltage Peak Detection | Not specified | Not specified | True RMS |  | Not specified
|  | Measurement error with supply voltage variation |  |  | switching threshold drift | Published | Published | %/V | - | < 1% of selected Un | < 1% of selected Un | < 1% of selected Un | < 1% of selected Un | < 1% of selected Un | < 1% of selected Un | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | < 1% of selected Un | Same as RM17TE00 | Same as RM17TE00 | < 1% of selected Un | Same as RM17TU00 | Same as RM17TU00 | < 1% of selected Un | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | < 1% of selected Un | Same as RM17TT00 | < 1% of selected Un | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | < 1% of selected Un | Same as RM35UB330 | Same as RM35UB330 | < 1% of selected Un | Same as RM35UB3N30 | Same as RM35UB3N30 | < 1% of selected Un | Same as RM17UB310 | Same as RM17UB310 |  | < 1% over whole range | < 1% over whole range | < 0.5% | < 0.5% | < 0.5% | < 0.5% | < 0.5% | Not specified | Not specified | < 0.5% |  | -
|  | Measurement error with temperature variation |  |  | switching threshold drift | Published | Published | %/oC | - | < 0.05% / oC | < 0.05% / oC | < 0.05% / oC | < 0.05% / oC | < 0.05% / oC | < 0.05% / oC | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | < 0.05% / oC | Same as RM17TE00 | Same as RM17TE00 | < 0.05% / oC | Same as RM17TU00 | Same as RM17TU00 | < 0.05% / oC | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | < 0.05% / oC | Same as RM17TT00 | < 0.05% / oC | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | < 0.05% / oC | Same as RM35UB330 | Same as RM35UB330 | < 0.05% / oC | Same as RM35UB3N30 | Same as RM35UB3N30 | < 0.05% / oC | Same as RM17UB310 | Same as RM17UB310 |  | 0.05% / oC | 0.05% / oC | =< 0.06% / oC | =< 0.06% / oC | =< 0.06% / oC | =< 0.06% / oC | =< 0.06% / oC | Not specified | Not specified | =< 0.06% / oC |  | 0.1% / oC
|  | Maximum measuring cycles |  |  | maximum measuring cycle | Published | Published | ms | - | 170ms / measurement as true rms value | 150ms / measurement as true rms value | 150ms / measurement as true rms value | 150ms / measurement as true rms value | 150ms / measurement as true rms value | 150ms / measurement as true rms value | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 150ms / measurement as true rms value | Same as RM17TE00 | Same as RM17TE00 | 150ms / measurement as true rms value | Same as RM17TU00 | Same as RM17TU00 | 150ms / measurement as true rms value | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 150ms / measurement as true rms value | Same as RM17TT00 | 140ms / measurement as true rms value | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 150ms / measurement as true rms value | Same as RM35UB330 | Same as RM35UB330 | 150ms / measurement as true rms value | Same as RM35UB3N30 | Same as RM35UB3N30 | 150ms / measurement as true rms value | Same as RM17UB310 | Same as RM17UB310 |  | Not specified | Not specified | 80 | 80 | 80 | 80 | 80 | Not specified | Not specified | 100 |  | -
Measurement range |  | Phase lost |  |  | measurement range | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | Fixed value | - | Fixed value | Fixed value | Fixed value | Fixed value | Fixed value | Not specified | Not specified | Not specified |  | Not specified
|  | Phase sequence |  |  | measurement range | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | Fixed value | - | Fixed value | Fixed value | Fixed value | Fixed value | Fixed value | Not specified | Not specified | Not specified |  | Not specified
|  | Over / undervoltage (symmetry windows mode) |  |  | measurement range | Published | Published |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | -2…-20 % in the ranges 3 x ~ 380…480 -2…-12 % in the range 3 x ~ 208 -2…-17 % in the range 3 x ~ 220 +2…+20 % in the ranges 3 x ~ 208…440 +2…+10 % in the range 3 x ~ 480 | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Over voltage |  |  | measurement range | Published | Published |  | - | +2…+20 % in the ranges 3 x 380…480 | +2…+20 % in the ranges 3 x ~200…240 | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | +2…+20 % in the ranges 3 x ~ 220…440 +2…+10 % in the range 3 x ~ 480 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | +2…+20 % in the ranges 3 x ~ 220…440 +2…+10 % in the range 3 x ~ 480 | Same as RM35UB330 | Same as RM35UB330 | +2…+20 % in the ranges 3 x ~ 120…277 | Same as RM35UB3N30 | Same as RM35UB3N30 | +2…+20 % in the ranges 3 x ~ 208…440 +2…+10 % in the range 3 x ~ 480 | Same as RM17UB310 | Same as RM17UB310 |  | - | - | RM4TR31: ~ 3 x 160…3 x 300 RM4TR32: ~ 3 x 420…3 x 480 RM4TR33: ~ 3 x 198 RM4TR34: ~ 3 x 360 | - | - | - | RM4UB34: ~ 160…220 RM4UB34: ~ 220…300 | - | - | ~ 3 x 420…3 x 500 |  | -
|  | Undervoltage |  |  | measurement range | Published | Published |  | - | -2…-20 % in the ranges 3 x 380…480 | -2…-20 % in the ranges 3 x ~ 200…240 | -2…-20 % in the ranges 3 x 380…480 | -2…-20 % in the ranges 3 x ~ 200…240 | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | -2…-20 % in the ranges 3 x ~ 380…480 -2…-12 % in the range 3 x ~ 208 -2…-17 % in the range 3 x ~ 220 | Same as RM17TU00 | Fixed 400 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | -12…-2 % in the range 3 x ~ 220 -20…-2 % in the ranges 3 x ~ 380…480 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | -12…-2 % in the range 3 x ~ 220 -20…-2 % in the ranges 3 x ~ 380…480 | Same as RM35UB330 | Same as RM35UB330 | -2…-20 % in the ranges 3 x ~ 120…277 | Same as RM35UB3N30 | Same as RM35UB3N30 | -2…-20 % in the ranges 3 x ~ 380…480 -2…-12 % in the range 3 x ~ 208 -2…-17 % in the range 3 x ~ 220 | Same as RM17UB310 | Same as RM17UB310 |  | - | - | RM4TR31: ~ 3 x 220…3 x 300 RM4TR32: ~ 3 x 300…3 x 430 RM4TR33: ~ 3 x 242 RM4TR34: ~ 3 x 440 | - | RM4TU01: ~ 3 x 160…3 x 220 RM4TU02: ~ 3 x 300…3 x 430 | - | RM4UB34: ~ 80…120 RM4UB34: ~ 160…220 | - | - | ~ 3 x 300…3 x 380 |  | -
|  | Phase asymmetry |  |  | measurement range | Published | Published |  | - | - | - | - | - | +5…+15 % in the ranges 3 x ~ 380…480 | +5…+15 % in the ranges 3 x ~ 200…240 | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | +5…+15 % in the ranges 3 x ~ 208…480 | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | +5…+15 % in the ranges 3 x ~ 208…480 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | +5…+15 % in the ranges 3 x ~ 220…480 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | - | - | - | Not specified | - | - | - | - |  | -
|  | Disconnection of neutral |  |  | measurement range | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Voltage Regeneration |  |  | measurement range | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Extreme undervoltage |  |  | measurement range | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Overvoltage |  |  | measurement range |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Asymmetry |  |  | measurement range |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Tripping threshold |  | Phase cut |  |  | tripping threshold | Published | Published |  | 1 or more phase cut | 1 or more phase cut | 1 or more phase cut | 1 or more phase cut | 1 or more phase cut | 1 or more phase cut | 1 or more phase cut | 1 or more phase cut | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1 or more phase cut | Same as RM17TE00 | Same as RM17TE00 | 1 or more phase cut | Same as RM17TU00 | Same as RM17TU00 | 1 or more phase cut | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1 or more phase cut | Same as RM17TT00 | 1 or more phase cut | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1 or more phase cut | Same as RM35UB330 | Same as RM35UB330 | 1 or more phase cut | Same as RM35UB3N30 | Same as RM35UB3N30 | 1 or more phase cut | Same as RM17UB310 | Same as RM17UB310 |  | (L2-L1) or (L3-L1) or (L2-L3) < 100 | (L2-L1) or (L3-L1) or (L2-L3) < 100 | RM4TR32: (L2-L1) or (L3-L1) or (L2-L3) < 290 or Differences of (L2-L1) / (L3-L1) /(L2-L3) > 105V Other: Unknown | Unknown | Unknown | Unknown | - | Not specified | Not specified | - |  | 1 phase below 85% of other phase
|  | Phase sequence |  |  | tripping threshold | Published | Published |  | Total swap of phase Internal design spec: L31 lag L21 =< 10o or L31 lag L21 >= 150o | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Total swap of phase Internal design spec: L31 lag L21 =< 10o or L31 lag L21 >= 150o | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Same as RM17TE00 | Same as RM17TE00 | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Same as RM17TU00 | Same as RM17TU00 | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Same as RM17TT00 | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Same as RM35UB330 | Same as RM35UB330 | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Same as RM35UB3N30 | Same as RM35UB3N30 | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Same as RM17UB310 | Same as RM17UB310 |  | (L2-L1) leads (L3-L1) < 10o or (L2-L1) leads (L3-L1) > 150o | (L2-L1) leads (L3-L1) < 10o or (L2-L1) leads (L3-L1) > 150o | Total swap of phase | Total swap of phase | Total swap of phase | Total swap of phase | - | Not specified | Not specified | - |  | -
|  | Over / undervoltage (symmetry windows mode) |  |  | tripping threshold | Published | Published |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Adjustable 2%...20% of selected Un | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Over voltage |  |  | tripping threshold | Published | Published |  | - | Adjustable 2%...20% of selected Un | Adjustable 2%...20% of selected Un | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Adjustable 2%...20% of selected Un | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Adjustable 2%...20% of selected Un | Same as RM35UB330 | Same as RM35UB330 | Adjustable 2%...20% of selected Un | Same as RM35UB3N30 | Same as RM35UB3N30 | Adjustable 2%...20% of selected Un | Same as RM17UB310 | Same as RM17UB310 |  | - | - | Adjustable within measurement range | - | - | - | Adjustable within measurement range | - | - | Adjustable within measurement range |  | -
|  | Undervoltage |  |  | tripping threshold | Published | Published |  | - | Adjustable 2%...20% of selected Un | Adjustable 2%...20% of selected Un | Adjustable 2%...20% of selected Un | Adjustable 2%...20% of selected Un | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | Adjustable 2%...20% of selected Un | Same as RM17TU00 | Fixed -10% of Un | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Adjustable 2%...20% of selected Un | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Adjustable 2%...20% of selected Un | Same as RM35UB330 | Same as RM35UB330 | Adjustable 2%...20% of selected Un | Same as RM35UB3N30 | Same as RM35UB3N30 | Adjustable 2%...20% of selected Un | Same as RM17UB310 | Same as RM17UB310 |  | - | - | Adjustable within measurement range | - | Adjustable within measurement range | - | Adjustable within measurement range | - | - | Adjustable within measurement range |  | -
|  | Phase asymmetry |  |  | tripping threshold | Published | Published |  | - | - | - | - | - | Adjustable 5%...15% of selected Un | Adjustable 5%...15% of selected Un | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Adjustable 5%...15% of selected Un | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | Adjustable 5%...15% of selected Un | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Adjustable 5%...15% of selected Un | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | - | - | - | Adjustable 5%...15% of selected Un | - | - | - | - |  | -
|  | Disconnection of neutral |  |  | tripping threshold | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | Total cut of N | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Voltage Regeneration |  |  | tripping threshold | Published |  |  | - | - | - | - | - | 1 or more phase < 70% of selected Un Internal design spec: 30% +/- 5% | 1 or more phase < 70% of selected Un Internal design spec: 30% +/- 5% | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1 or more phase < 70% of selected Un Internal design spec: 30% +/- 5% | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Extreme undervoltage (Phase loss) |  |  | tripping threshold | Published |  | V | 2 or more phase < 100V Internal design spec: 2 or more phase <150V +/- 10% | 1 or more phase < 250V Internal design spec: 1 or more phase <290V +/- 5% | 1 or more phase < 150V Internal design spec: 1 or more phase <160V +/- 5% | 1 or more phase < 250V Internal design spec: 1 or more phase <290V +/- 5% | 1 or more phase < 150V Internal design spec: 1 or more phase <160V +/- 5% | 1 or more phase < 250V Internal design spec: 1 or more phase <290V +/- 5% | 1 or more phase < 150V Internal design spec: 1 or more phase <160V +/- 5% | 2 or more phase < 100V Internal design spec: 2 or more phase <150V +/- 10% | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% | Same as RM17TE00 | Same as RM17TE00 | 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% | Same as RM17TU00 | Same as RM17TU00 | 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% | Same as RM17TT00 | 1 or more phase < 150V Internal design spec: 1 or more phase <188V +/- 5% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1 or more phase < 150V Internal design spec: 1 or more phase <188V +/- 5% | Same as RM35UB330 | Same as RM35UB330 | 1 or more phase < 80V Internal design spec: 1 or more phase <86V +/- 5% | Same as RM35UB3N30 | Same as RM35UB3N30 | 1 or more phase < 150V Internal design spec: 1 or more phase <175V +/- 5% | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Overvoltage |  |  | tripping threshold |  |  | V | - | Internal design spec: 593V +/- 5% | Internal design spec: 297V +/- 5% | Internal design spec: 593V +/- 5% | Internal design spec: 297V +/- 5% | Internal design spec: 593V +/- 5% | Internal design spec: 297V +/- 5% | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Internal design spec: 543V +/- 5% | Same as RM17TE00 | Same as RM17TE00 | Internal design spec: 543V +/- 5% | Same as RM17TU00 | Same as RM17TU00 | Internal design spec: 543V +/- 5% | Same as RM17TA00 | Same as RM17TA00 | When > 543V +/- 5% last longer than 2s +/- 10% , output de-energized When > 543V +/- 5% last shorter than 2s +/- 10% , output energized | Internal design spec: 543V +/- 5% | Same as RM17TT00 | Internal design spec: 543V +/- 5% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Internal design spec: 543V +/- 5% | Same as RM35UB330 | Same as RM35UB330 | Internal design spec: 368V +/- 5% | Same as RM35UB3N30 | Same as RM35UB3N30 | Internal design spec: 543V +/- 5% | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Asymmetry |  |  | tripping threshold |  |  | % | - | Internal design spec: 48% +/- 6% | Internal design spec: 48% +/- 6% | Internal design spec: 48% +/- 6% | Internal design spec: 48% +/- 6% | Internal design spec: 48% +/- 6% | Internal design spec: 48% +/- 6% | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Internal design spec: 48% +/- 6% | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | Internal design spec: 48% +/- 6% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Internal design spec: 48% +/- 6% | Same as RM17TT00 | Internal design spec: 48% +/- 6% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Internal design spec: 48% +/- 6% | Same as RM35UB330 | Same as RM35UB330 | Internal design spec: 48% +/- 6% | Same as RM35UB3N30 | Same as RM35UB3N30 | Internal design spec: 48% +/- 6% | Same as RM17UB310 | Same as RM17UB310
Hysteresis |  | Phase cut |  |  | hysteresis | Published | Published |  | All phase cut recover | All phase cut recover | All phase cut recover | All phase cut recover | All phase cut recover | All phase cut recover | All phase cut recover | All phase cut recover | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | All phase cut recover | Same as RM17TE00 | Same as RM17TE00 | All phase cut recover | Same as RM17TU00 | Same as RM17TU00 | All phase cut recover | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | All phase cut recover | Same as RM17TT00 | All phase cut recover | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | All phase cut recover | Same as RM35UB330 | Same as RM35UB330 | All phase cut recover | Same as RM35UB3N30 | Same as RM35UB3N30 | All phase cut recover | Same as RM17UB310 | Same as RM17UB310 |  | - | Not specified | - | - | - | - | - | Not specified | Not specified | - |  | -
|  | Phase sequence |  |  | hysteresis | Published | Published |  | Total phase swap recover Internal design spec: L31 lag L21 >= 15o or L31 lag L21 <= 135o | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Total phase swap recover Internal design spec: L31 lag L21 >= 15o or L31 lag L21 <= 135o | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Same as RM17TE00 | Same as RM17TE00 | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Same as RM17TU00 | Same as RM17TU00 | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Same as RM17TT00 | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Same as RM35UB330 | Same as RM35UB330 | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Same as RM35UB3N30 | Same as RM35UB3N30 | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Same as RM17UB310 | Same as RM17UB310 |  | (L2-L1) leads (L3-L1) >=15o or (L2-L1) leads (L3-L1) =< 135o | (L2-L1) leads (L3-L1) >=15o or (L2-L1) leads (L3-L1) =< 135o | - | - | - | - | - | Not specified | Not specified | - |  | -
|  | Over / undervoltage (symmetry windows mode) |  |  | hysteresis | Published | Published |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Over voltage |  |  | hysteresis | Published | Published |  | - | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM35TF30 | Same as RM35TF30 | Fixed 5.35% of selected Un Internal design spec: 5.35% +/- 1.5% | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM35UB330 | Same as RM35UB330 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM35UB3N30 | Same as RM35UB3N30 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM17UB310 | Same as RM17UB310 |  | - | - | Fixed 5% of de-energization threshold | Fixed 5% of de-energization threshold | Fixed 5% of de-energization threshold | Fixed 5% of de-energization threshold | Fixed 5% of de-energization threshold | - | - | Fixed 5% |  | -
|  | Undervoltage |  |  | hysteresis | Published | Published |  | - | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM17TU00 | Fixed 5% of selected Un Internal design spec: 5% +/- 1.5% | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM35TF30 | Same as RM35TF30 | Fixed 5.35% of selected Un Internal design spec: 5.35% +/- 1.5% | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM35UB330 | Same as RM35UB330 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM35UB3N30 | Same as RM35UB3N30 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM17UB310 | Same as RM17UB310 |  | - | - | Fixed 5% of de-energization threshold | Fixed 5% of de-energization threshold | Fixed 5% of de-energization threshold | Fixed 5% of de-energization threshold | Fixed 5% of de-energization threshold | - | - | Fixed 5% |  | -
|  | Phase asymmetry |  |  | hysteresis | Published | Published |  | - | - | - | - | - | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Disconnection of neutral |  |  | hysteresis | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Voltage Regeneration |  |  | hysteresis | Published |  |  | - | - | - | - | - | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | Fixed 2% of selected Un Internal design spec: 2% +/- 1.5% | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 30% | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Extreme undervoltage (Phase loss) |  |  | hysteresis | Published |  |  | All phases > 183V Internal design spec: All phases >153V +/- 10% | All phases > 315V Internal design spec: All phases >296V +/- 5% | All phases > 175V Internal design spec: All phases >163V +/- 5% | All phases > 315V Internal design spec: All phases >296V +/- 5% | All phases > 175V Internal design spec: All phases >163V +/- 5% | All phases > 315V Internal design spec: All phases >296V +/- 5% | All phases > 175V Internal design spec: All phases >163V +/- 5% | All phases > 183V Internal design spec: All phases >153V +/- 10% | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | All phases > 195V Internal design spec: All phases >180V +/- 5% | Same as RM17TE00 | Same as RM17TE00 | All phases > 195V Internal design spec: All phases >180V +/- 5% | Same as RM17TU00 | Same as RM17TU00 | All phases >195V Internal design spec: All phases >180V +/- 5% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | All phases > 195V Internal design spec: All phases >180V +/- 5% | Same as RM17TT00 | All phases > 205V Internal design spec: All phases >190V +/- 5% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | All phases > 205V Internal design spec: All phases >190V +/- 5% | Same as RM35UB330 | Same as RM35UB330 | All phases > 100V Internal design spec: All phases >88V +/- 5% | Same as RM35UB3N30 | Same as RM35UB3N30 | All phases > 195V Internal design spec: All phases >180V +/- 5% | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Overvoltage |  |  | hysteresis |  |  |  | - | Internal design spec: All phases <583V +/- 5% | Internal design spec: All phases <287V +/- 5% | Internal design spec: All phases <583V +/- 5% | Internal design spec: All phases <287V +/- 5% | Internal design spec: All phases <583V +/- 5% | Internal design spec: All phases <287V +/- 5% | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Internal design spec: All phases <533V +/- 5% | Same as RM17TE00 | Same as RM17TE00 | Internal design spec: All phases <533V +/- 5% | Same as RM17TU00 | Same as RM17TU00 | Internal design spec: All phases <533V +/- 5% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Internal design spec: All phases <533V +/- 5% | Same as RM17TT00 | Internal design spec: All phases <533V +/- 5% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Internal design spec: All phases > <533V +/- 5% | Same as RM35UB330 | Same as RM35UB330 | Internal design spec: All phases <358V +/- 5% | Same as RM35UB3N30 | Same as RM35UB3N30 | Internal design spec: All phases <533V +/- 5% | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Asymmetry |  |  | hysteresis |  |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Output Circuit Characteristics | [44 empty] | Same as RM35UB3N30 | Same as RM35UB3N30
Type of output |  |  |  |  | output type | Published | Published |  | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | Same as RM17TG20 | Same as RM17TG20 | 1 x C/O relay contacts | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1 x C/O relay contacts | Same as RM17TE00 | Same as RM17TE00 | 1 x C/O relay contacts | Same as RM17TU00 | Same as RM17TU00 | 1 x C/O relay contacts | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1 x C/O relay contacts | Same as RM17TT00 | 2 x C/O relay contacts | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1 x C/O + 1 x C/O relay contacts | Same as RM35UB330 | Same as RM35UB330 | 1 x C/O + 1 x C/O relay contacts | Same as RM35UB3N30 | Same as RM35UB3N30 | 1 x C/O relay contacts | Same as RM17UB310 | Same as RM17UB310 |  | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 1 x C/O relay contacts | 2 x C/O relay contacts |  | 1 x C/O relay contact
Output terminal |  |  |  |  | output terminal |  |  |  | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 11-12-14, 21-22-24 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 11-12-14 | Same as RM17TE00 | Same as RM17TE00 | 11-12-14 | Same as RM17TU00 | Same as RM17TU00 | 11-12-14 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 11-12-14 | Same as RM17TT00 | 11-12-14, 21-22-24 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 11-12-14, 21-22-24 | Same as RM35UB330 | Same as RM35UB330 | 11-12-14, 21-22-24 | Same as RM35UB3N30 | Same as RM35UB3N30 | 11-12-14 | Same as RM17UB310 | Same as RM17UB310 |  | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 15-16-18, 25-26-28 | 11-12-14, 21-22-24 | 2014-11-12
Operation principle |  | R1 (11-12-14) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Energized on fault-free | Same as RM17TE00 | Same as RM17TE00 | Energized on fault-free | Same as RM17TU00 | Same as RM17TU00 | Energized on fault-free | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Energized on fault-free | Same as RM17TT00 | Energized on fault-free | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Energized on fault-free | Same as RM35UB330 | Same as RM35UB330 | Energized on fault-free | Same as RM35UB3N30 | Same as RM35UB3N30 | Energized on fault-free | Same as RM17UB310 | Same as RM17UB310 |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free |  | -
|  | R2 (21-22-24) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Energized on fault-free | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Energized on fault-free | Same as RM35UB330 | Same as RM35UB330 | Energized on fault-free | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  | -
Contact material |  |  |  | Common C_Rly Spec | contacts material | Published | Published |  | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Cadmium free | Same as RM17TE00 | Same as RM17TE00 | Cadmium free | Same as RM17TU00 | Same as RM17TU00 | Cadmium free | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Cadmium free | Same as RM17TT00 | Cadmium free | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Cadmium free | Same as RM35UB330 | Same as RM35UB330 | Cadmium free | Same as RM35UB3N30 | Same as RM35UB3N30 | Cadmium free | Same as RM17UB310 | Same as RM17UB310 |  | Cadmium-free | Cadmium-free | 90/10 Nickel Silver | 90/10 Nickel Silver | 90/10 Nickel Silver | 90/10 Nickel Silver | 90/10 Nickel Silver | Cadmium-free | Cadmium-free | AgNi alloy, cadmium-free |  | AgSnO2
Mechanical durability |  |  | IEC61810-1 | Common C_Rly Spec | mechanical durability | Published | Published | Cyc | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 30 x 106 cycles | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 30 x 106 cycles | Same as RM17TE00 | Same as RM17TE00 | 30 x 106 cycles | Same as RM17TU00 | Same as RM17TU00 | 30 x 106 cycles | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 30 x 106 cycles | Same as RM17TT00 | 30 x 106 cycles | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 30 x 106 cycles | Same as RM35UB330 | Same as RM35UB330 | 30 x 106 cycles | Same as RM35UB3N30 | Same as RM35UB3N30 | 30 x 106 cycles | Same as RM17UB310 | Same as RM17UB310 |  | 30 x 106 switching cycles | 20 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 20 x 106 switching cycles | 20 x 106 switching cycles | 30 x 106 switching cycles |  | >= 30 x 106 switching cycles
Electrical durability |  | AC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/5A, 100k cycles | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | NO: 250VAC/5A, 100k cycles | Same as RM17TE00 | Same as RM17TE00 | NO: 250VAC/5A, 100k cycles | Same as RM17TU00 | Same as RM17TU00 | NO: 250VAC/5A, 100k cycles | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | NO: 250VAC/5A, 100k cycles | Same as RM17TT00 | NO: 250VAC/5A, 100k cycles | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | NO: 250VAC/5A, 100k cycles | Same as RM35UB330 | Same as RM35UB330 | NO: 250VAC/5A, 100k cycles | Same as RM35UB3N30 | Same as RM35UB3N30 | NO: 250VAC/5A, 100k cycles | Same as RM17UB310 | Same as RM17UB310 |  | 1 x 104 switching cycles | 1 x 104 switching cycles | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | 1 x 105 switching cycles | - | >= 1 x 105 switching cycles @ 5A, 250VAC
|  | DC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | NO: 24VDC/5A, 100k cycles | Same as RM17TE00 | Same as RM17TE00 | NO: 24VDC/5A, 100k cycles | Same as RM17TU00 | Same as RM17TU00 | NO: 24VDC/5A, 100k cycles | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | NO: 24VDC/5A, 100k cycles | Same as RM17TT00 | NO: 24VDC/5A, 100k cycles | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | NO: 24VDC/5A, 100k cycles | Same as RM35UB330 | Same as RM35UB330 | NO: 24VDC/5A, 100k cycles | Same as RM35UB3N30 | Same as RM35UB3N30 | NO: 24VDC/5A, 100k cycles | Same as RM17UB310 | Same as RM17UB310 | [11 empty] | -
|  | AC-15 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | NO: 250VAC/0.15A, 100k cycles | Same as RM17TE00 | Same as RM17TE00 | NO: 250VAC/0.15A, 100k cycles | Same as RM17TU00 | Same as RM17TU00 | NO: 250VAC/0.15A, 100k cycles | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | NO: 250VAC/0.15A, 100k cycles | Same as RM17TT00 | NO: 250VAC/0.15A, 100k cycles | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | NO: 250VAC/0.15A, 100k cycles | Same as RM35UB330 | Same as RM35UB330 | NO: 250VAC/0.15A, 100k cycles | Same as RM35UB3N30 | Same as RM35UB3N30 | NO: 250VAC/0.15A, 100k cycles | Same as RM17UB310 | Same as RM17UB310 | [11 empty] | -
|  | DC-13 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | NO: 24VDC/1A, 100k cycles | Same as RM17TE00 | Same as RM17TE00 | NO: 24VDC/1A, 100k cycles | Same as RM17TU00 | Same as RM17TU00 | NO: 24VDC/1A, 100k cycles | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | NO: 24VDC/1A, 100k cycles | Same as RM17TT00 | NO: 24VDC/1A, 100k cycles | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | NO: 24VDC/1A, 100k cycles | Same as RM35UB330 | Same as RM35UB330 | NO: 24VDC/1A, 100k cycles | Same as RM35UB3N30 | Same as RM35UB3N30 | NO: 24VDC/1A, 100k cycles | Same as RM17UB310 | Same as RM17UB310 | [11 empty] | -
Rated capacity |  | Rated switching voltage | IEC61810-1 | Common C_Rly Spec | [Ue] rated operational voltage | Published |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 250V | Same as RM17TE00 | Same as RM17TE00 | 250V | Same as RM17TU00 | Same as RM17TU00 | 250V | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 250V | Same as RM17TT00 | 250V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 250V | Same as RM35UB330 | Same as RM35UB330 | 250V | Same as RM35UB3N30 | Same as RM35UB3N30 | 250V | Same as RM17UB310 | Same as RM17UB310
|  | Rated switching current | IEC61810-1 | Common C_Rly Spec | [Ie] rated operational current | Published | Published | A | 8A | 8A | 8A | 8A | 8A | 8A | 8A | 5A | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | 8A | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 5A | Same as RM17TE00 | Same as RM17TE00 | 5A | Same as RM17TU00 | Same as RM17TU00 | 5A | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 5A | Same as RM17TT00 | 5A | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 5A | Same as RM35UB330 | Same as RM35UB330 | 5A | Same as RM35UB3N30 | Same as RM35UB3N30 | 5A | Same as RM17UB310 | Same as RM17UB310
Maximum switching capacity |  | Maximum switching voltage |  | Common C_Rly Spec | maximum switching capacity | Published | Published | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 250V | Same as RM17TE00 | Same as RM17TE00 | 250V | Same as RM17TU00 | Same as RM17TU00 | 250V | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 250V | Same as RM17TT00 | 250V | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 250V | Same as RM35UB330 | Same as RM35UB330 | 250V | Same as RM35UB3N30 | Same as RM35UB3N30 | 250V | Same as RM17UB310 | Same as RM17UB310 |  | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~/-- 250 |  | -
|  | Maximum switching current |  | Common C_Rly Spec | maximum switching capacity | Published | Published | A | 8A | 8A | 8A | 8A | 8A | 8A | 8A | 5A | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | 8A | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 5A | Same as RM17TE00 | Same as RM17TE00 | 5A | Same as RM17TU00 | Same as RM17TU00 | 5A | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 5A | Same as RM17TT00 | 5A | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 5A | Same as RM35UB330 | Same as RM35UB330 | 5A | Same as RM35UB3N30 | Same as RM35UB3N30 | 5A | Same as RM17UB310 | Same as RM17UB310 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | - |  | -
|  | Maximum switching capacity |  | Common C_Rly Spec | maximum switching capacity | Published | Published | VA | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
Minimum switching capacity |  | Minimum switching voltage | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | 5 | 5 | 12 | 12 | 12 | 12 | 12 | 5 | 5 | 24
|  | Minimum switching current | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | mA | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | Minimum switching capacity | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published | Published | mW | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM17TE00 | Same as RM17TE00 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM17TU00 | Same as RM17TU00 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM17TT00 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM35UB330 | Same as RM35UB330 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM35UB3N30 | Same as RM35UB3N30 | NO: 12V/10mA, MCTF > 80,000,000 | Same as RM17UB310 | Same as RM17UB310 |  | 50 | 50 | 120 | 120 | 120 | 120 | 120 | 50 | 50 | 240
Maximum voltage drop at terminals |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum voltage drop |  |  | V | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  | -
Leakage current |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum leakage current |  |  | mA | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  | -
Thermal Current |  |  | IEC60947-5-1 | Common C_Rly Spec | thermal current |  |  | A | 8A | 8A | 8A | 8A | 8A | 8A | 8A | 5A | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | 8A | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 5A | Same as RM17TE00 | Same as RM17TE00 | 5A | Same as RM17TU00 | Same as RM17TU00 | 5A | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 5A | Same as RM17TT00 | 5A | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 5A | Same as RM35UB330 | Same as RM35UB330 | 5A | Same as RM35UB3N30 | Same as RM35UB3N30 | 5A | Same as RM17UB310 | Same as RM17UB310 |  |  | -
Short circuit protection |  | Relay Output by external fuse | IEC60947-5-1 | Common C_Rly Spec | short circuit protection |  |  | gG | 8A | 8A | 8A | 8A | 8A | 8A | 8A | 5A | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | 8A | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 5A | Same as RM17TE00 | Same as RM17TE00 | 5A | Same as RM17TU00 | Same as RM17TU00 | 5A | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 5A | Same as RM17TT00 | 5A | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 5A | Same as RM35UB330 | Same as RM35UB330 | 5A | Same as RM35UB3N30 | Same as RM35UB3N30 | 5A | Same as RM17UB310 | Same as RM17UB310 |  |  | -
|  | Solid State Output by external fuse | IEC62314 | Common C_Rly Spec | short circuit protection |  |  | gG | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  |  | -
Time Delay Characteristics
Time delay functions |  | "OFF" delay |  |  | time delay type | Published |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Yes | Same as RM17TE00 | Same as RM17TE00 | Yes | Same as RM17TU00 | Same as RM17TU00 | Yes | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Yes | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Yes | Same as RM35UB330 | Same as RM35UB330 | Yes | Same as RM35UB3N30 | Same as RM35UB3N30 | Yes | Same as RM17UB310 | Same as RM17UB310 |  | - | - | · | · | · | · | · | - | - | · |  | -
|  | "ON" delay |  |  | time delay type | Published |  |  | - | Yes | Yes | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | · | · | · | · | · | - | - | · |  | -
|  | Inhibition |  |  | time delay type | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | - | - | - | - | - | - | - | - |  | -
Timing range |  | "OFF" delay |  |  | time delay range | Published | Published | s | - | Adjustable 0.1…30 | Adjustable 0.1…30 | - | - | Adjustable 0.1…30 | Adjustable 0.1…30 | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Adjustable 0.1…10 | Same as RM17TE00 | Same as RM17TE00 | Adjustable 0.1…10 | Same as RM17TU00 | Fixed 3.5s +/- 5% | Adjustable 0.1…10 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Adjustable 0.1…10 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Adjustable Tt1 0.1…30 for overvoltage @ R1 (11-12-14) Adjustable Tt2 0.1…30 for undervoltage @ R2 (21-22-24) | Same as RM35UB330 | Same as RM35UB330 | Adjustable Tt1 0.1…30 for overvoltage @ R1 (11-12-14) Adjustable Tt2 0.1…30 for undervoltage @ R2 (21-22-24) | Same as RM35UB3N30 | Same as RM35UB3N30 | Adjustable 0.1…30 | Same as RM17UB310 | Same as RM17UB310 |  | - | - | Adjustable 0.1…10 | Adjustable 0.1…10 | Adjustable 0.1…10 | Adjustable 0.1…10 | Adjustable 0.1…10 | - | - | Adjustable 0.1…30 |  | -
|  | "ON" delay |  |  | time delay range | Published |  | s | - | Adjustable 0.1…30 | Adjustable 0.1…30 | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | - | - | - | - | - | - | - | - |  | -
|  | Inhibition |  |  | time delay range | Published | Published | s | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | - | - | - | - | - | - | - | - |  | -
Response time |  | on crossing the threshold |  |  | response time | Published | Published | ms | =< 200 | =< 300 | =< 300 | =< 300 | =< 300 | =< 300 | =< 300 | =< 130 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | =< 200 | Same as RM17TE00 | Same as RM17TE00 | =< 200 | Same as RM17TU00 | Same as RM17TU00 | =< 200 | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | =< 200 | Same as RM17TT00 | =< 200 | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | =< 200 | Same as RM35UB330 | Same as RM35UB330 | =< 200 | Same as RM35UB3N30 | Same as RM35UB3N30 | =< 200 | Same as RM17UB310 | Same as RM17UB310 |  | =< 300 | =< 300 | Not specified | Not specified | Not specified | Not specified | Not specified | =< 300 | =< 300 | - |  | < 100 for ON delay ; < 300 for OFF delay
|  |  |  | Reserved for other products | response time | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  |  |  | Reserved for other products | response time | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  |  |  | Reserved for other products | response time | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  |  |  | Reserved for other products | response time | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Time delay of pick-up |  |  |  |  | power on delay | Published | Published | ms | =< 650 Internal Design spec: >300ms and =< 650ms when product is fully discharged at min rated voltage | =< 650 Internal Design spec: >300ms and =< 650ms when product is fully discharged at min rated voltage | =< 650 Internal Design spec: >300ms and =< 650ms when product is fully discharged at min rated voltage | =< 650 Internal Design spec: >300ms and =< 650ms when product is fully discharged at min rated voltage | =< 650 Internal Design spec: >300ms and =< 650ms when product is fully discharged at min rated voltage | =< 650 Internal Design spec: >300ms and =< 650ms when product is fully discharged at min rated voltage | =< 650 Internal Design spec: >300ms and =< 650ms when product is fully discharged at min rated voltage | =< 650 Internal Design spec: >300ms and =< 650ms when product is fully discharged at min rated voltage | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | =< 650 Internal Design spec: >300ms and =< 650ms when product is fully discharged at min rated voltage | Same as RM17TE00 | Same as RM17TE00 | =< 650 Internal Design spec: >300ms and =< 650ms when product is fully discharged at min rated voltage | Same as RM17TU00 | Same as RM17TU00 | =< 650 Internal Design spec: >300ms and =< 650ms when product is fully discharged at min rated voltage | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | =< 650 Internal Design spec: >300ms and =< 650ms when product is fully discharged at min rated voltage | Same as RM17TT00 | =< 650 Internal Design spec: >300ms and =< 650ms when product is fully discharged at min rated voltage | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | =< 650 Internal Design spec: >300ms and =< 650ms when product is fully discharged at min rated voltage | Same as RM35UB330 | Same as RM35UB330 | =< 650 Internal Design spec: >300ms and =< 650ms when product is fully discharged at min rated voltage | Same as RM35UB3N30 | Same as RM35UB3N30 | =< 650 Internal Design spec: >300ms and =< 650ms when product is fully discharged at min rated voltage | Same as RM17UB310 | Same as RM17UB310 |  | =< 650 | =< 650 | Not specified | Not specified | Not specified | Not specified | Not specified | =< 200 | =< 200 | Fixed 200 |  | -
Reset time |  | through Un power reset |  |  | reset time | Published | Published | ms | =< 1500 at maximum rated supply voltage | =< 1500 at maximum rated supply voltage | =< 1500 at maximum rated supply voltage | =< 1500 at maximum rated supply voltage | =< 1500 at maximum rated supply voltage | =< 1500 at maximum rated supply voltage | =< 1500 at maximum rated supply voltage | =< 1500 at maximum rated supply voltage | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | =< 1500 at maximum rated supply voltage | Same as RM17TE00 | Same as RM17TE00 | =< 1500 at maximum rated supply voltage | Same as RM17TU00 | Same as RM17TU00 | =< 1500 at maximum rated supply voltage | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | =< 1500 at maximum rated supply voltage | Same as RM17TT00 | =< 1500 at maximum rated supply voltage | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | =< 1500 at maximum rated supply voltage | Same as RM35UB330 | Same as RM35UB330 | =< 1500 at maximum rated supply voltage | Same as RM35UB3N30 | Same as RM35UB3N30 | =< 1500 at maximum rated supply voltage | Same as RM17UB310 | Same as RM17UB310 |  | - | - | Not specified | Not specified | Not specified | Not specified | Not specified | - | - | - |  | -
|  | through front panel reset |  | Reserved for other products | reset time | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | through input control reset |  | Reserved for other products | reset time | Published |  |  | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Setting accuracy |  |  |  | Common C_Rly Spec | setting accuracy of time delay | Published | Published | % | - | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | - | - | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | Same as RM17TE00 | Same as RM17TE00 | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | Same as RM17TU00 | Same as RM17TU00 | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | Same as RM35UB330 | Same as RM35UB330 | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | Same as RM35UB3N30 | Same as RM35UB3N30 | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite) | Same as RM17UB310 | Same as RM17UB310 |  | - | - | +/- 10% of full scales value | +/- 10% of full scales value | +/- 10% of full scales value | +/- 10% of full scales value | +/- 10% of full scales value | - | - | - |  | -
Repeat accuracy (constant parameters) |  |  |  | Common C_Rly Spec | repeat accuracy of time delay | Published |  | % | - | +/- 3% | +/- 3% | - | - | +/- 3% | +/- 3% | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | +/- 3% | Same as RM17TE00 | Same as RM17TE00 | +/- 3% | Same as RM17TU00 | Same as RM17TU00 | +/- 3% | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | +/- 3% | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | +/- 3% | Same as RM35UB330 | Same as RM35UB330 | +/- 3% | Same as RM35UB3N30 | Same as RM35UB3N30 | +/- 3% | Same as RM17UB310 | Same as RM17UB310 |  | - | - | Not specified | Not specified | Not specified | Not specified | Not specified | - | - | < +/- 0.2% |  | -
Timing error with supply voltage variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/V | - | < 1 | < 1 | - | - | < 1 | < 1 | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | < 0.5% | < 0.5% | < 0.5% | < 0.5% | < 0.5% | - | - | < 0.5% |  | -
Timing error with temperature variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/oC | - | < 0.05 | < 0.05 | - | - | < 0.05 | < 0.05 | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310 |  | - | - | =< 0.07% / oC | =< 0.07% / oC | =< 0.07% / oC | =< 0.07% / oC | =< 0.07% / oC | - | - | =< 0.06% / oC |  | -
LED Indication
status LED |  |  |  |  | status LED |  |  |  | Un (Green) R (Amber) | Dial pointer (Green) R (Amber) Def (Red) | Dial pointer (Green) R (Amber) Def (Red) | Dial pointer (Green) R (Amber) Def (Red) | Dial pointer (Green) R (Amber) Def (Red) | Dial pointer (Green) R (Amber) Def (Red) | Dial pointer (Green) R (Amber) Def (Red) | R (Amber) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | R (Amber) | Rel (Amber) | Un (Green) R (Amber) | Same as RM17TE00 | Same as RM17TE00 | Un (Green) R (Amber) | Same as RM17TU00 | R (Amber) | Un (Green) R (Amber) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Un (Green) R (Amber) | Same as RM17TT00 | Un (Green) R (Amber) Def (Amber) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Un (Green) R1 (Amber) R2 (Amber) | Same as RM35UB330 | Same as RM35UB330 | Un (Green) R1 (Amber) R2 (Amber) | Same as RM35UB3N30 | Same as RM35UB3N30 | Un (Green) R (Amber) | Same as RM17UB310 | Same as RM17UB310
local signalling |  | Power supply availability |  |  | local signalling |  |  |  | Un - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | - | - | Un - ON | Same as RM17TE00 | Same as RM17TE00 | Un - ON | Same as RM17TU00 | - | Un - ON | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Un - ON | Same as RM17TT00 | Un - ON | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Un - ON | Same as RM35UB330 | Same as RM35UB330 | Un - ON | Same as RM35UB3N30 | Same as RM35UB3N30 | Un - ON | Same as RM17UB310 | Same as RM17UB310
|  | Power supply not availability |  |  | local signalling |  |  |  | Un - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | - | - | Un - OFF | Same as RM17TE00 | Same as RM17TE00 | Un - OFF | Same as RM17TU00 | - | Un - OFF | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Un - OFF | Same as RM17TT00 | Un - OFF | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Un - OFF | Same as RM35UB330 | Same as RM35UB330 | Un - OFF | Same as RM35UB3N30 | Same as RM35UB3N30 | Un - OFF | Same as RM17UB310 | Same as RM17UB310
|  | Timing in-progress |  |  | local signalling |  |  |  | - | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | - | - | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM17TE00 | Same as RM17TE00 | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM17TU00 | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM17TT00 | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM35UB330 | Same as RM35UB330 | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM35UB3N30 | Same as RM35UB3N30 | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM17UB310 | Same as RM17UB310
|  | Output is energized |  |  | local signalling |  |  |  | R - ON | R - ON | R - ON | R - ON | R - ON | R - ON | R - ON | R - ON | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | R - ON | R - ON | R - ON | Same as RM17TE00 | Same as RM17TE00 | R - ON | Same as RM17TU00 | R - ON | R - ON | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | R - ON | Same as RM17TT00 | R - ON | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R1 / R2 - ON | Same as RM35UB330 | Same as RM35UB330 | R1 / R2 - ON | Same as RM35UB3N30 | Same as RM35UB3N30 | R - ON | Same as RM17UB310 | Same as RM17UB310
|  | Output is de-energized |  |  | local signalling |  |  |  | R - OFF | R - OFF | R - OFF | R - OFF | R - OFF | R - OFF | R - OFF | R - OFF | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | R - OFF | R - OFF | R - OFF | Same as RM17TE00 | Same as RM17TE00 | R - OFF | Same as RM17TU00 | R - OFF | R - OFF | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | R - OFF | Same as RM17TT00 | R - OFF | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R 1 / R2 - OFF | Same as RM35UB330 | Same as RM35UB330 | R 1 / R2 - OFF | Same as RM35UB3N30 | Same as RM35UB3N30 | R - OFF | Same as RM17UB310 | Same as RM17UB310
|  | Range Setting Changes |  |  | local signalling |  |  |  | - | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | - | - | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | Same as RM17TE00 | Same as RM17TE00 | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | Same as RM17TU00 | - | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | Same as RM17TT00 | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | Same as RM35UB330 | Same as RM35UB330 | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | Same as RM35UB3N30 | Same as RM35UB3N30 | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | Same as RM17UB310 | Same as RM17UB310
|  | Phase Cut |  |  | local signalling |  |  |  | - | Def - Permanent OFF | Def - Permanent OFF | Def - Permanent OFF | Def - Permanent OFF | Def - Permanent OFF | Def - Permanent OFF | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Def - Permanent OFF | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R 1 / R2 - OFF | Same as RM35UB330 | Same as RM35UB330 | R 1 / R2 - OFF | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Phase Sequence Swap |  |  | local signalling |  |  |  | - | Def - Permanent ON | Def - Permanent ON | Def - Permanent ON | Def - Permanent ON | Def - Permanent ON | Def - Permanent ON | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Def - Permanent OFF | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R 1 / R2 - OFF | Same as RM35UB330 | Same as RM35UB330 | R 1 / R2 - OFF | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Undervoltage <U |  |  | local signalling |  |  |  | - | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R2 - OFF | Same as RM35UB330 | Same as RM35UB330 | R2 - OFF | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Overvoltage >U |  |  | local signalling |  |  |  | - | Def - Fast Blink (5% ON; 95% OFF) @ 1Hz | Def - Fast Blink (5% ON; 95% OFF) @ 1Hz | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R 1 - OFF | Same as RM35UB330 | Same as RM35UB330 | R 1 - OFF | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Phase Asymmetry |  |  | local signalling |  |  |  | - | - | - | - | - | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Def - Permanent ON | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Voltage Regeneration |  |  | local signalling | Published |  |  | - | - | - | - | - | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | Def - Slow Blink (50% ON; 50% OFF) @ 1Hz | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Undervoltage <U (Phase loss) |  |  | local signalling |  |  |  | - | Def - Permanent OFF | Def - Permanent OFF | Def - Permanent OFF | Def - Permanent OFF | Def - Permanent OFF | Def - Permanent OFF | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Def - Permanent OFF | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R 1 / R2 - OFF | Same as RM35UB330 | Same as RM35UB330 | R 1 / R2 - OFF | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Overvoltage >U |  |  | local signalling |  |  |  | - | Def - Permanent ON | Def - Permanent ON | Def - Permanent ON | Def - Permanent ON | Def - Permanent ON | Def - Permanent ON | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Def - Permanent OFF | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | R 1 / R2 - OFF | Same as RM35UB330 | Same as RM35UB330 | R 1 / R2 - OFF | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
|  | Extreme Phase Asymmetry |  |  | local signalling |  |  |  | - | - | - | - | - | Def - Permanent OFF | Def - Permanent OFF | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | Def - Permanent OFF | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Special Features
True RMS | [8 empty] | No | Yes | Yes | Yes | Yes | Yes | Yes | No | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Yes | Same as RM17TE00 | Same as RM17TE00 | Yes | Same as RM17TU00 | Same as RM17TU00 | Yes | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Yes | Same as RM17TT00 | Yes | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Yes | Same as RM35UB330 | Same as RM35UB330 | Yes | Same as RM35UB3N30 | Same as RM35UB3N30 | Yes | Same as RM17UB310 | Same as RM17UB310
Backlight Indicator | [8 empty] | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Diagnostic Button |  |  |  |  | diagnostic button | Published |  |  | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Pre-Alarm Output | [8 empty] | - | - | - | - | - | - | - | - | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | - | Same as RM17TE00 | Same as RM17TE00 | - | Same as RM17TU00 | Same as RM17TU00 | - | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | - | Same as RM17TT00 | - | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | - | Same as RM35UB330 | Same as RM35UB330 | - | Same as RM35UB3N30 | Same as RM35UB3N30 | - | Same as RM17UB310 | Same as RM17UB310
Output | [8 empty] | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM17TE00 | Same as RM17TE00 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM17TU00 | Same as RM17TU00 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM17TT00 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM35UB330 | Same as RM35UB330 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM35UB3N30 | Same as RM35UB3N30 | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | Same as RM17UB310 | Same as RM17UB310
Reliability Data
Reliability Data |  | MTTF |  |  | safety reliability data | Published |  | hrs | 8,100,000 hours | 3,400,000 hours | 3,400,000 hours | 3,400,000 hours | 3,400,000 hours | 3,400,000 hours | 3,400,000 hours | 8,100,000 hours | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 4,400,000 hours | Same as RM17TE00 | Same as RM17TE00 | 4,400,000 hours | Same as RM17TU00 | Same as RM17TU00 | 4,400,000 hours | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 4,400,000 hours | Same as RM17TT00 | 3,500,000 hours | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 2,800,000 hours | Same as RM35UB330 | Same as RM35UB330 | 4,400,000 hours | Same as RM35UB3N30 | Same as RM35UB3N30 | 4,400,000 hours | Same as RM17UB310 | Same as RM17UB310
|  | B10 |  |  | safety reliability data | Published |  | hrs | 850,000 hours | 350,000 hours | 350,000 hours | 350,000 hours | 350,000 hours | 350,000 hours | 350,000 hours | 850,000 hours | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | 470,000 hours | Same as RM17TE00 | Same as RM17TE00 | 470,000 hours | Same as RM17TU00 | Same as RM17TU00 | 470,000 hours | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | 470,000 hours | Same as RM17TT00 | 360,000 hours | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | 300,000 hours | Same as RM35UB330 | Same as RM35UB330 | 470,000 hours | Same as RM35UB3N30 | Same as RM35UB3N30 | 470,000 hours | Same as RM17UB310 | Same as RM17UB310
|  | MTTFd | [5 empty] | hrs | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM17TE00 | Same as RM17TE00 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM17TU00 | Same as RM17TU00 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM17TT00 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM35UB330 | Same as RM35UB330 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM35UB3N30 | Same as RM35UB3N30 | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Same as RM17UB310 | Same as RM17UB310
|  | B10d | [5 empty] | hrs | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG20 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG00 | Same as RM17TG20 | Same as 84873034 | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM17TE00 | Same as RM17TE00 | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM17TU00 | Same as RM17TU00 | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM17TA00 | Same as RM17TA00 | Same as RM17TA00 | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM17TT00 | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM35TF30 | Same as RM35TF30 | Same as RM35TF30 | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM35UB330 | Same as RM35UB330 | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM35UB3N30 | Same as RM35UB3N30 | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Same as RM17UB310 | Same as RM17UB310
Drawing / Diagram
[9 empty] | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram | Drawing / Diagram
Note on K3: Main firmware type
Note on T3: Main firmware type
Note on Z3: Main firmware type
Note on AL3: Main firmware type
Note on D18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.1
Note on J36: Align with marking
Note on K36: Align with marking
Note on L36: Align with marking
Note on M36: Align with marking
Note on N36: Align with marking
Note on O36: Align with marking
Note on P36: Align with marking
Note on Q36: Align with marking
Note on Z36: Align with marking
Note on AC36: Align with marking
Note on AF36: Align with marking
Note on AL36: Align with marking
Note on AP36: Align with marking
Note on AS36: Align with marking
Note on AV36: Align with marking
Note on J37: Align with marking
Note on K37: Align with marking
Note on L37: Align with marking
Note on M37: Align with marking
Note on N37: Align with marking
Note on O37: Align with marking
Note on P37: Align with marking
Note on Q37: Align with marking
Note on Z37: Align with marking
Note on AC37: Align with marking
Note on AF37: Align with marking
Note on AL37: Align with marking
Note on AP37: Align with marking
Note on AS37: Align with marking
Note on AV37: Align with marking
Note on A42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Typical Product Operation Rate: 100% - product mostly will be powered and in operation in the actual application 50% - product is powered and in operation in the actual application @ ~50% of the time
Note on A44: Protection : Normal performance within the specification limits Command and control : Normal performance within the specification limits Measurement : Temporary degradation during test, with self-recovery at the end of the test. No loss of stored data Integral human-machine interface and visual alarms: Temporary degradation or loss of function during test, with self-recovery at the end of the test. No loss of stored data Data communication : Possible bit error rate increase but no loss of transmitted data
Note on A156: Measured with Yokogawa power meter and 3P4W connection
Note on A160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The minimum level of supply voltage that causes the product out-of power to operate. This must be a value other than 0V or total cut-off
Note on A162: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe list of available functions performed by the product as checklist
Note on A173: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe the characteristics and behaviors of the product when performing monitoring operation
Note on A186: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe the valid monitoring range able to be performed by the product for each type of functions
Note on A197: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe how the product is recognizing the Threshold to decide on triggering its output
Note on A208: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe how the product is recognizing the Hysteresis to decide on recovering its output
Note on D226: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-4-1 GB14048.4
Note on D227: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-4-1 GB14048.4
Note on D228: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-5-1 GB14048.5
Note on D229: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-5-1 GB14048.5
Note on D240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.5
Note on D241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.5
Note on C277: Same as Phase cut
Note on A287: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Product Developed Before 2019: follow UTE C80-810 Product Developed After 2019 and require recalculation of MTBF: follow SN29500

## Level Control Spec
|  | Brand --> |  |  | brown text - widely used every where |  |  |  | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | OLD SE | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | CROUZET | SCHNEIDER ELECTRIC | CROUZET
|  | Base Design Reference --> |  |  | black text - product nature specific |  |  |  | HW adapted from 8487020x | HW adapted from 8487020x | HW & FW adapted from RM35LM33MW | HW & FW adapted from RM35LM33MW |  |  | (RM4 + Crouzet)
Firmware Type -->
Main Parameters | Category | Sub Parameters | Conforming to | Remark | Standardized Datasheet Param | Selected for Publication | Old Datasheet | Unit | RM22LG11MR | RM22LG11MT | RM22LA32MR | RM22LA32MT | RM35LM33MW | RM35LV14MW | Competitor Spec Reference | RM35LM33MW | RM35LV14MW | RM4LA32 | RM4LG01 | RM22 (Catch Up) | 8487020x | RM22 (Catch Up) | 8487021x
Standard
Product standard |  |  |  | Common C_Rly Spec | standards | Published | Published |  | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | NF EN 60255-6 and IEC 60255-6 | NF EN 60255-6 and IEC 60255-6 |  | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | Not specified | EN60255-6, IEC60255-6 | Not specified
Product certifications |  |  |  | Common C_Rly Spec | product certifications | Published | Published |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST |  | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | cULus, CE, CSA | UL, CSA, GL, C-Tick, GOST | cULus, CE, CSA
Marking |  |  |  | Common C_Rly Spec | marking | Published |  |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | 1: 73/23/EEC and EMC 89/336/EEC | 1: 73/23/EEC and EMC 89/336/EEC |  | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE | cULus, CE, CSA | UL, CSA, GL, C-Tick, GOST, CE | cULus, CE, CSA
Low voltage directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU |  |  |  | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | Not specified | No 73/23/EEC + 93/68/EEC | Not specified
EMC directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU |  |  |  | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | Not specified | No 89/336/EEC + 92/31/EEC + 93/68/EEC | Not specified
ROHS directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU |  |  |  | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC | Not specified | 2002/95/EC | Not specified
Environment Characteristics
Environmental Condition |  | Climatic category | IEC60721-3-3 | Common C_Rly Spec |  |  |  |  | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | Environmental category | Germanisher Lloyd | Common C_Rly Spec |  |  |  |  | Class C | Class C | Class C | Class C
Ambient air temperature around the device |  | Storage |  | Common C_Rly Spec | ambient air temperature for storage | Published | Published | oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | - 40…+ 70 | - 40…+ 70 |  | -40…+70 | -40…+70 | Not specified | Not specified | -40…+70 | -40…+70 | -40…+70 | -40…+70
|  | Operation |  |  | ambient air temperature for operation | Published | Published | oC | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | - 20…+ 50 | - 20…+ 50 |  | -20…+50 | -20…+50 | Not specified | Not specified | -20…+50 | -20…+50 | -20…+50 | -20…+50
Relative humidity |  | Damp heat | IEC60068-2-30 | Common C_Rly Spec | relative humidity | Published | Published |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 2 x 24 hours…+ 95 % RH at + 55 °C (without condensation) | 2 x 24 hours…+ 95 % RH at + 55 °C (without condensation) |  | 2 cycles 24h ;+25°C +55°C 95%HR | 2 cycles 24h ;+25°C +55°C 95%HR | Not specified | Not specified | 2 cycles 24h ;+25°C +55°C 95%HR | Not specified | 2 cycles 24h ;+25°C +55°C 95%HR | Not specified
|  | Cyclic Damp Heat Test | IEC60947-5-1 | Common C_Rly Spec |  |  |  |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97%
Vibration resistance |  |  | IEC60068-2-6 | Common C_Rly Spec | vibration resistance | Published | Published |  | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.035 mm from 10…150 Hz | 0.035 mm from 10…150 Hz |  | 0.035mm from 10Hz…150Hz | 0.035mm from 10Hz…150Hz | Not specified | Not specified | 0.035mm from 10Hz…150Hz | Not specified | 0.035mm from 10Hz…150Hz | Not specified
Shock resistance |  |  | IEC60068-2-27 | Common C_Rly Spec | shock resistance | Published | Published |  | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 5 gn | 5 gn |  | 5 gn | 5 gn | Not specified | Not specified | 5 gn | Not specified | 5 gn | Not specified
Bump resistance |  |  | IEC60068-2-29 | Common C_Rly Spec | bump resistance |  |  |  | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating)
Seismic resistance |  |  | IEC60068-3-3 | Common C_Rly Spec | seismic resistance |  |  |  | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz
IP degree of protection |  | Terminal Block | IEC60529 |  | IP degree of protection | Published | Published |  | IP20 | IP20 | IP20 | IP20 | IP 20 | IP 20 |  | IP20 | IP20 | Not specified | Not specified | IP20 | Not specified | IP20 | Not specified
|  | Housing | IEC60529 |  | IP degree of protection | Published | Published |  | IP40 | IP40 | IP40 | IP40 | IP 30 | IP 30 |  | IP30 | IP30 | Not specified | Not specified | IP30 | Not specified | IP30 | Not specified
|  | Front Panel | IEC60529 |  | IP degree of protection |  |  |  | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover)
Installation Data
Dimension (nominal) |  | Width |  |  | width | Published |  | mm | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 |  |  |  | 35 x 90 x 72 | 35 x 90 x 72 | 22.5 x 78 x 80 | 22.5 x 78 x 80 | 22.5 x ? x ? | 22.5 x 78.5 x 100 | 22.5 x ? x ? | 22.5 x 78.5 x 100
|  | Height |  |  | height | Published |  | mm
|  | Depth |  |  | depth | Published |  | mm
Weight (without packaging) |  |  |  |  | net weight | Published |  | g | 100 | 100 | 110 | 110 |  |  |  | 130 | 130 | 168 | 168 | ? | 150 | ? | 150
Mounting |  | Without socket | IEC/EN 60715 |  | mounting support | Published | Published |  | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 4 rail | On 4 rail |  | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail
|  | With socket | IEC/EN 60715 |  | mounting support |  |  |  | - | - | - | - |  |  |  | - | - | - | - | - | - | - | -
Mounting position |  | In relation to normal vertical mounting plane |  | Common C_Rly Spec | mounting position | Published | Published |  | Any position | Any position | Any position | Any position | Any position | Any position |  | Any position | Any position | Not specified | Not specified | Any position | Not specified | Any position | Not specified
Minimum distance to adjacent devices |  | Horizontal |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | Not specified | Not specified | Not specified | Not specified |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | Vertical |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | Not specified | Not specified | Not specified | Not specified |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Wiring connection (Clamping Capacity) |  | Solid cable without cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…4 (AWG 20…AWG 11) | 1 conductor: 0.5…4 (AWG 20…AWG 11) |  | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | Not specified | Not specified | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | Not specified | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | Not specified
|  | Flexible cable with cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 2 conductors: 0.5…2.5 (AWG 20…AWG 14) |  | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | Not specified | Not specified | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | Not specified | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | Not specified
|  | Solid cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | - | - | - | 1 conductor: 0.2…2.5 (AWG 24…AWG 12) | 1 conductor: 0.2…2.5 (AWG 24…AWG 12) |  | - | - | - | - | - | - | - | -
|  | Flexible cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | - | - | - | 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 2 conductors: 0.2…1.5 (AWG 24…AWG 16) |  | - | - | - | - | - | - | - | -
|  | Tightening torque | IEC60947-1 | Common C_Rly Spec | tightening torque | Published | Published | Nm | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | 0.6…1N.m / 5.3…8.8 Lbf.In | 0.6…1N.m / 5.3…8.8 Lbf.In |  | 0.6…1 | 0.6…1 | Not specified | Not specified | 0.6…1 | Not specified | 0.6…1 | Not specified
|  | Cable stripping length |  | Common C_Rly Spec | cable stripping length |  |  | mm | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Duty time |  |  |  | Common C_Rly Spec | duty time |  |  | % | 100% | 100% | 100% | 100% |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Electromagnetic Compatibility
Immunity |  | Generic immunity standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | Immunity NF EN 61000-6-2 2002 / IEC 61000-6-2 | Immunity NF EN 61000-6-2 2002 / IEC 61000-6-2 |  | IEC61000-6-2 | IEC61000-6-2 | IEC50082-2 | IEC50082-2 | IEC61000-6-2 | Not specified | IEC61000-6-2 | Not specified
|  | Electrostatic discharge | IEC61000-4-2 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) |  |  |  | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Not specified | Level 3 (6kV / 8kV) | Not specified
|  | Radiated RF & electromagnetic field | IEC61000-4-3 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) |  |  |  | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Not specified | Level 3 (10V/m) | Not specified
|  | Fast transient / burst | IEC61000-4-4 |  | electromagnetic compatibility | Published |  |  | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) |  |  |  | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Not specified | Level 3 (2kV coupling / 4kV direct) | Not specified
|  | Surge | IEC61000-4-5 |  | electromagnetic compatibility | Published |  |  | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) |  |  |  | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Not specified | Level 3 (1kV phase-phase) | Not specified
|  | Conducted RF disturbance | IEC61000-4-6 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) |  |  |  | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Not specified | Level 3 (10V) | Not specified
|  | Power frequency magnetic field | IEC61000-4-8 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s)
|  | Voltage dips, short interruption & variations on power line | IEC61000-4-11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | - | - | - |  |  |  | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Not specified | Class 3 (0%, 40%, 70%, 80% of Us) | Not specified
|  | 1 MHz oscillation wave | IEC61000-4-18 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV)
|  | DC voltage interruption | IEC61000-4-29 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms
|  | Low frequency harmonics | IEC61000-4-13 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | - | - | - |  |  |  | Not tested | Not tested | Not tested | Not tested | Not tested | Not specified | Not tested | Not specified
|  | Conducted low frequency interference (harmonics) | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | Emission NF EN 61000-6-4, NF EN 61000-6-3, IEC 61000-6-4, IEC 61000-6-3 | Emission NF EN 61000-6-4, NF EN 61000-6-3, IEC 61000-6-4, IEC 61000-6-3 |  | · | · | ? | ? | · | Not specified | · | Not specified
Emission |  | Generic emission standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 |  |  |  | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | Not specified | IEC61000-6-3, IEC61000-6-4 | Not specified
|  | Radiated RF & electromagnetic field (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B | Class B | Class B |  |  |  | Class B | Class B | Class B Group1 | Class B Group1 | Class B | Not specified | Class B | Not specified
|  | Radiated RF & electromagnetic field (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 |  |  |  | Class B | Class B | Class B Group1 | Class B Group1 | Class B | Not specified | Class B | Not specified
|  | Radiated emission from enclosure port | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | Not specified | EMC 2 | Not specified
|  | Conducted RF emission on power line (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B | Class B | Class B |  |  |  | Class B | Class B | Class B Group1 | Class B Group1 | Class B | Not specified | Class B | Not specified
|  | Conducted RF emission on power line (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 |  |  |  | Class B | Class B | Class B Group1 | Class B Group1 | Class B | Not specified | Class B | Not specified
|  | Conducted emission | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | Not specified | EMC 2 | Not specified
Electrical Isolation
Degree of pollution |  |  | IEC60664-1 | Common C_Rly Spec | pollution degree | Published | Published |  | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | Not specified | Not specified | 3 | Not specified | 3 | Not specified
Overvoltage category |  |  | IEC60664-1 | Common C_Rly Spec | overvoltage category | Published | Published |  | 3 | 3 | 3 | 3 | III | III |  | III | III | Not specified | Not specified | III | Not specified | III | Not specified
Circuit Group | Terminal | Supply |  |  | circuit group | Published |  |  | A1, A2 | A1, A2 | A1, A2 | A1, A2
|  | Input 1 |  |  | circuit group | Published |  |  | Min, Max, C | Min, Max, C | Min, Max, C | Min, Max, C
|  | Input 2 |  |  | circuit group | Published |  |  | - | - | - | -
|  | Input 3 |  |  | circuit group | Published |  |  | - | - | - | -
|  | Output 1 |  |  | circuit group | Published |  |  | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14
|  | Output 2 |  |  | circuit group | Published |  |  | - | - | 21,22,24 | 21,22,24 |  |  |  | 600 | 600 | Not specified | Not specified | 600 | Not specified | 600 | Not specified
| Rated | Supply | [6 empty] | 24…240 AC/DC | 380…415 AC | 24…240 AC/DC | 380…415 AC |  |  |  | 600 | 600 | Not specified | Not specified | 600 | Not specified | 600 | Not specified
| Voltage | Input 1 | [6 empty] | Level probe | Level probe | Level probe | Level probe |  |  |  | 600 | 600 | Not specified | Not specified | 600 | Not specified | 600 | Not specified
| Spec | Input 2 | [6 empty] | - | - | - | -
|  | Input 3 | [6 empty] | - | - | - | -
|  | Output 1 | [6 empty] | 250V | 250V | 250V | 250V
|  | Output 2 | [6 empty] | - | - | 250V | 250V
Rated Insulation Voltage |  | Supply | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 400V | 250V | 400V | 250 | 250
|  | Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 10V | 10V | 10V | 10V
|  | Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V |  |  |  | 4 | 4 | Not specified | Not specified | 4 | Not specified | 4 | Not specified
|  | Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | 250V | 250V
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 400V | 250V | 400V
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Supply / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 400V | 250V | 400V
|  | Supply / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | - | - | 250V | 400V
|  | Output 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | - | - | 250V | 250V
|  | Input 1 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V
|  | Input 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | 250V | 250V
|  | Input 2 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Input 2 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - |  |  |  | 2 @ 50Hz for 1 minutes | 2 @ 50Hz for 1 minutes | Not specified | Not specified | 2 @ 50Hz for 1 minutes | Not specified | 2 @ 50Hz for 1 minutes | Not specified
|  | Input 3 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Input 3 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Input 1 / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
Rated Impulse Voltage |  | Supply | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4 (1.2/50 µs) | 4 (1.2/50 µs)
|  | Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Supply / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Supply / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | - | - | 4kV, OVC3 | 4kV, OVC3
|  | Output 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | - | - | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | 4kV, OVC3 | 4kV, OVC3
|  | Input 2 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 2 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - |  |  |  | > 500MOhm @ -- 500V | > 500MOhm @ -- 500V | Not specified | Not specified | > 500MOhm @ -- 500V | Not specified | > 500MOhm @ -- 500V | Not specified
|  | Input 3 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 3 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 1 / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
Dielectric test voltage |  | Supply / Input 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2, 1 50 Hz, 1 min. | 2, 1 50 Hz, 1 min. |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
|  | Supply / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
|  | Supply / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - |  |  |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
|  | Supply / Output 1 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Supply / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | - | - | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Output 1 / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | - | - | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 2 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
|  | Input 2 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
|  | Input 3 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
|  | Input 3 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
|  | Input 1 / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
|  | Input 2 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
|  | Input 1 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
Insulation resistance |  | Supply / Input 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | > 500 MΩ, 2 500 V | > 500 MΩ, 2 500 V
|  | Supply / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Supply / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Supply / Output 1 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | - | - | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Output 1 / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | - | - | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 2 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Input 2 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Input 3 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Input 3 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Input 1 / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Input 2 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Input 1 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
Power Supply Characteristics
Rated supply voltage, Us |  |  |  |  | [Us] rated supply voltage | Published | Published | V | ~/-- 24…240 | ~380…415 | ~/-- 24…240 | ~380…415 | ~/-- 24…240 | 1/2 24…240 |  | ~/-- 24…240 | ~/-- 24…240 | RM4LA32B: ~ 24 RM4LA32F: ~110…130 RM4LA32M: ~220…240 RM4LA32MW: ~/-- 24…240 RM4LA32Q: ~380…415 | RM4LA32B: ~ 24 RM4LA32F: ~110…130 RM4LA32M: ~220…240 RM4LA32Q: ~380…415 | ~/-- 24…240 | 84870201: ~ 24 84870203: ~120 84870204: ~230 | ~/-- 24…240 | 84870211: ~ 24 84870213: ~120 84870214: ~230
Supply voltage operating range |  |  |  |  | supply voltage limits | Published | Published | V | ~/-- 20.4…264 | ~323…456.5 | ~/-- 20.4…264 | ~323…456.5 | ~/-- 20.4…264 | 1/2 20.4…264 |  | ~/-- 20.4…264 | ~/-- 20.4…264 | Not specified | Not specified | ~/-- 20.4…264 | Not specified | ~/-- 20.4…264 | Not specified
Polarity on d.c. supply |  |  |  |  | polarity |  | Published
Rated frequency |  |  |  |  | supply frequency | Published | Published | Hz | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50/60 Hz ± 10 % | 50/60 Hz ± 10 % |  | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60
Frequency operating range |  |  |  |  | supply frequency | Published | Published | Hz | 45…66 | 45…66 | 45…66 | 45…66 |  |  |  | 45…66 | 45…66 | Not specified | Not specified | 45…66 | Not specified | 45…66 | Not specified
Maximum power consumption |  |  |  |  | power consumption | Published | Published |  | ~ 3.5VA, ~5VA, 1.5W | ~ 10VA ~ 8VA | ~ 3.5VA, ~5VA, 1.5W | ~ 10VA ~ 8VA | 5VA / 1.5W | 5VA / 1.5W |  | ~ 5VA, -- 1.5W | ~ 5VA, -- 1.5W | RM4LA32B: 3.1VA RM4LA32F: 2.7VA RM4LA32M: 2.6VA RM4LA32MW: 2.7VA, 2.4W RM4LA32Q: 3.4VA | RM4LG01B: 1.9VA RM4LG01F: 2.6VA RM4LG01M: 2.4VA RM4LG01Q: 2.9VA | ~ 5VA, -- 1.5W | 3VA | ~ 5VA, -- 1.5W | 3VA
Immunity to micro-breakage |  |  |  |  | immunity to microbreaks | Published | Published | ms | ~ 90, -- 100 | ~ 90, -- 100 | ~ 90, -- 100 | ~ 90, -- 100 | ~ 90, -- 100 | ~ 90, -- 100 |  | 90 (AC), 100 (DC) | 90 (AC), 100 (DC) | Not specified | Not specified | 90 (AC), 100 (DC) | Not specified | 90 (AC), 100 (DC) | Not specified
Supply terminal |  |  |  |  | supply terminal |  |  |  | A1-A2 | A1-A2 | A1-A2 | A1-A2 |  |  |  | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2
On Load Factor |  |  |  | Common C_Rly Spec | on-load factor |  |  | % | 100% | 100% | 100% | 100%
Release of input voltage |  |  |  |  | release of input voltage |  |  | V | - | - | - | -
Input Circuit Characteristics
Monitoring functions |  | 1 level - Fill operation |  |  | monitoring functions |  |  |  | - governed by response time - status reflects to both R1 & R2 | - governed by response time - status reflects to both R1 & R2 | - governed by time delay - status reflects to both R1 & R2 | - governed by time delay - status reflects to both R1 & R2
|  | 1 level - Empty operation |  |  | monitoring functions |  |  |  | - governed by response time - status reflects to both R1 & R2 | - governed by response time - status reflects to both R1 & R2 | - governed by time delay - status reflects to both R1 & R2 | - governed by time delay - status reflects to both R1 & R2
|  | 2 level - Fill operation |  |  | monitoring functions |  |  |  | - governed by response time - status reflects to both R1 & R2 | - governed by response time - status reflects to both R1 & R2 | - governed by time delay - status reflects to both R1 & R2 | - governed by time delay - status reflects to both R1 & R2
|  | 2 level - Empty operation |  |  | monitoring functions |  |  |  | - governed by response time - status reflects to both R1 & R2 | - governed by response time - status reflects to both R1 & R2 | - governed by time delay - status reflects to both R1 & R2 | - governed by time delay - status reflects to both R1 & R2
Monitoring function characteristics |  | Measurement mode
|  | Internal input resistance |  |  | internal input resistance |  |  |  | - | - | - | -
|  | Input terminal |  |  | input terminal |  |  |  | Min-Max-C | Min-Max-C | Min-Max-C | Min-Max-C
|  | Maximum probe supplied voltage |  |  | Maximum probe supplied voltage |  |  | V | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 24 | 24 | 12 | 24 | 12 | 24
|  | Maximum probe supplied current |  |  | Maximum probe supplied current |  |  | mA | 1 | 1 | 1 | 1 | < 1 | 40 |  | 1 | 40 | 1 | 1 | 1 | 1 | 1 | 1
|  | Maximum length of probes cable |  |  | Maximum length of probes cable |  |  | m | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 1000 | 1000 | 100 | Not specified | 100 | Not specified
|  | Maximum cable capacitance |  |  | input frequency |  |  | nF | 1 for LS 2.2 for St 4.7 for HS | 1 for LS 2.2 for St 4.7 for HS | 1 for LS 2.2 for St 4.7 for HS | 1 for LS 2.2 for St 4.7 for HS | 1 for LS 2.2 for St 4.7 pour HS | 10 | [6 empty] | 10 |  | 10
|  | Setting accuracy |  |  | setting accuracy of the switching threshold |  |  | % | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value for LS '+/- 10% of full scale value for St '+/- 35% of full scale value for HS | +/- 10% of full scale value for LS '+/- 10% of full scale value for St '+/- 35% of full scale value for HS | ± 10 % of the full scale ± 20 % for the HS range | ± 10 % of the full scale ± 20 % for the HS range |  | +/- 10% of full scale value, +/- 20% for HS range | +/- 10% of full scale value | Not specified | Not specified | +/- 10% of full scale value, +/- 20% for HS range | +/- 30% at max sensitivity | +/- 10% of full scale value, +/- 20% for HS range | +/- 30% at max sensitivity
|  | Repeat accuracy (constant parameters) |  |  | repeat accuracy of the switching threshold |  |  | % | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | Measurement method |  |  | measurement method |  |  |  | Liquid level resistive probe | Liquid level resistive probe | Liquid level resistive probe | Liquid level resistive probe |  |  |  | Liquid level probe | 12V NPN/PNP ultrasonics sensor | Liquid level probe | Liquid level probe | Liquid level probe | Liquid level probe | Liquid level probe | Liquid level probe
|  | Measurement error with supply voltage variation |  |  | switching threshold drift |  |  | %/V | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | Measurement error with temperature variation |  |  | switching threshold drift |  |  | %/oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.5 % / °C | 0.5 % / °C |  | 0.5% / oC | 0.5% / oC | Not specified | Not specified | 0.5% / oC | Not specified | 0.5% / oC | Not specified
|  | Maximum measuring cycles |  |  | maximum measuring cycle
Measurement range |  | 1 level - Fill operation |  |  | measurement range |  |  | kW | 5kW…100kW | 5kW…100kW | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS | 250 Ω…5 kΩ | –
|  | 1 level - Empty operation |  |  | measurement range |  |  | kW | 5kW…100kW | 5kW…100kW | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS | 5 kΩ…100 kΩ | –
|  | 2 level - Fill operation |  |  | measurement range |  |  | kW | 5kW…100kW | 5kW…100kW | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS | 50 kΩ…1 MΩ | –
|  | 2 level - Empty operation |  |  | measurement range |  |  | kW | 5kW…100kW | 5kW…100kW | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS | 250W…5kW @ selected LS 5kW…100kW @ selected St 50kW…1MW @ selected HS
Tripping threshold |  | 1 level - Fill operation |  |  | tripping threshold |  |  | % | Adjustable 5%...100% of 100kW | Adjustable 5%...100% of 100kW | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS | 5…100 % of the range | –
|  | 1 level - Empty operation |  |  | tripping threshold |  |  | % | Adjustable 5%...100% of 100kW | Adjustable 5%...100% of 100kW | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS
|  | 2 level - Fill operation |  |  | tripping threshold |  |  | % | Adjustable 5%...100% of 100kW | Adjustable 5%...100% of 100kW | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS
|  | 2 level - Empty operation |  |  | tripping threshold |  |  | % | Adjustable 5%...100% of 100kW | Adjustable 5%...100% of 100kW | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS | Adjustable 5%...100% of 5kW @ LS Adjustable 5%...100% of 100kW @ St Adjustable 5%...100% of 1MW @ HS
Hysteresis |  | 1 level - Fill operation |  |  | hysteresis |  |  |  | - | - | - | -
|  | 1 level - Empty operation |  |  | hysteresis |  |  |  | - | - | - | -
|  | 2 level - Fill operation |  |  | hysteresis |  |  |  | - | - | - | -
|  | 2 level - Empty operation |  |  | hysteresis |  |  |  | - | - | - | -
Output Circuit Characteristics
Type of output |  |  |  |  | output type | Published | Published |  | 1 x C/O relay contacts | 1 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 C/O contacts | 1 C/O contact |  | 2 x C/O relay contacts | 1 x C/O relay contacts | 2 x C/O relay contacts | 1 x C/O relay contacts | 1 x C/O relay contacts | 1 x C/O relay contacts | 2 x C/O relay contacts | 1 x C/O relay contacts
Output terminal |  |  |  |  | output terminal |  |  |  | 11/12/14, | 11/12/14, | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 |  |  |  | 11-12-14, 21-22-24 | 11-12-14 | 15-16-18, 25-26-28 | 15-16-18 | 11-12-14 | 11-12-14 | 11-12-14, 21-22-24 | 11-12-14
Operation principle |  | R1 (11-12-14) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | R2 (21-22-24) |  |  | output logic |  |  |  | - | - | Energized on fault-free | Energized on fault-free
Contact material |  |  |  | Common C_Rly Spec | contacts material | Published | Published |  | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium-free | Cadmium-free |  | Cadmium-free | Cadmium-free | Not specified | Not specified | Cadmium-free | Cadmium-free | Cadmium-free | Cadmium-free
Mechanical durability |  |  | IEC61810-1 | Common C_Rly Spec | mechanical durability | Published | Published | Cyc | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 30 x 106 operating cycles | 30 x 106 operating cycles |  | 30 x 106 switching cycles | 30 x 106 switching cycles | Not specified | Not specified | 30 x 106 switching cycles | Not specified | 30 x 106 switching cycles | Not specified
Electrical durability |  | AC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | 1 x 105 operating cycles | 1 x 105 operating cycles |  | 1 x 105 switching cycles | 1 x 105 switching cycles | Not specified | Not specified | 1 x 105 switching cycles | Not specified | 1 x 105 switching cycles | Not specified
|  | DC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | AC-12, AC-13, AC-14, AC-15, DC-12, DC-13 | AC-12, AC-13, AC-14, AC-15, DC-12, DC-13
|  | AC-15 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles
|  | DC-13 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles
Rated capacity |  | Rated switching voltage | IEC61810-1 | Common C_Rly Spec | [Ue] rated operational voltage | Published |  | V | 250V | 250V | 250V | 250V | 1250 | 1250
|  | Rated switching current | IEC61810-1 | Common C_Rly Spec | [Ie] rated operational current | Published | Published | A | 8A | 8A | 8A | 8A | 5 | 5
Maximum switching capacity |  | Maximum switching voltage |  | Common C_Rly Spec | maximum switching capacity | Published | Published | V | 250V | 250V | 250V | 250V | 1/2 250 | 1/2 250 |  | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | Not specified | ~ 250 | Not specified
|  | Maximum switching current |  | Common C_Rly Spec | maximum switching capacity | Published | Published | A | 8A | 8A | 8A | 8A | 1/2 5 | 1/2 5 |  | ~ 5 | ~ 5 | 8 | 8 | ~ 8 | Not specified | ~ 5 | Not specified
|  | Maximum switching capacity |  | Common C_Rly Spec | maximum switching capacity | Published | Published | VA | - | - | - | - |  |  |  | 1250 | 1250 | 2000VA | 2000VA | 2000 | Not specified | 1250 | Not specified
Minimum switching capacity |  | Minimum switching voltage | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | V | - | - | - | - |  |  |  | 5 | 5 | Not specified | Not specified | 5 | Not specified | 5 | Not specified
|  | Minimum switching current | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | mA | - | - | - | - |  |  |  | 10 | 10 | Not specified | Not specified | 10 | Not specified | 10 | Not specified
|  | Minimum switching capacity | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published | Published | mW | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | 10/ 2 5 V | 10/ 2 5 V |  | 50 | 50 | Not specified | Not specified | 50 | Not specified | 50 | Not specified
Maximum voltage drop at terminals |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum voltage drop |  |  | V | - | - | - | - |  |  |  | - | - | - | - | - | - | - | -
Leakage current |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum leakage current |  |  | mA | - | - | - | - |  |  |  | - | - | - | - | - | - | - | -
Thermal Current |  |  | IEC60947-5-1 | Common C_Rly Spec | thermal current |  |  | A | 8A | 8A | 8A | 8A |  |  |  | 5 | 5 | 8 | 8 | 8
Short circuit protection |  | Relay Output by external fuse | IEC60947-5-1 | Common C_Rly Spec | short circuit protection |  |  | gG | 8A | 8A | 8A | 8A |  |  |  | 8 |  |  |  | 8
|  | Solid State Output by external fuse | IEC62314 | Common C_Rly Spec | short circuit protection |  |  | gG | - | - | - | -
Time Delay Characteristics
Time delay functions |  | "OFF" delay |  |  | time delay type | Published |  |  | - | - | Yes | Yes |  |  |  | · | · | · | - | - | - | · | ·
|  | "ON" delay |  |  | time delay type | Published |  |  | Yes | Yes | Yes | Yes |  |  |  | · | · | · | - | - | - | · | ·
|  | Inhibition |  |  | time delay type | Published |  |  | - | - | - | - |  |  |  | - | - | - | - | - | - | - | -
Timing range |  | "OFF" delay |  |  | time delay range | Published | Published | s | - | - | Adjustable 0.1…30 | Adjustable 0.1…30 | 0.1…5, 0 + 10 % | 0.1…5, 0 + 10 % |  | Adjustable 0.1…5 | Adjustable 0.1…5 | Adjustable 0.1…10 | - | - | - | Adjustable 0.1…5 | Adjustable 0.1…5
|  | "ON" delay |  |  | time delay range | Published |  | s | - | - | Adjustable 0.1…30 | Adjustable 0.1…30 |  |  |  | Adjustable 0.1…5 | Adjustable 0.1…5 | Adjustable 0.1…10 | - | - | - | Adjustable 0.1…5 | Adjustable 0.1…5
|  | Inhibition |  |  | time delay range | Published | Published | s | - | - | - | - |  |  |  | - | - | - | - | - | - | - | -
Response time |  | on crossing the threshold |  |  | response time | Published | Published | ms | =< 850 | =< 850 | =< 850 (Ls/St) =< 2500 (Hs) | =< 850 (Ls/St) =< 2500 (Hs) |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | 300 high level; 500 low level | Not specified | 300 high level; 500 low level
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
Time delay of pick-up |  |  |  |  | power on delay | Published | Published | ms | =< 600 | =< 600 | =< 600 =< 600 (Ls/St) =< 2500 (Hs) | =< 600 =< 600 (Ls/St) =< 2500 (Hs) | 600 | 500 |  | =< 600 | =< 600 | Not specified | Not specified | =< 600 | Not specified | =< 600 | Not specified
Reset time |  | through Un power reset |  |  | reset time | Published | Published | ms | =< 1750 | =< 1750 | =< 1750 | =< 1750 | 1.75 | 4 if 1 line broken / 1 if 2 lines broken |  | =< 1750 at maximum supply voltage | =< 1000 at maximum supply voltage =< 4000 at maximum supply voltage | Not specified | Not specified | =< 1750 at maximum supply voltage | Not specified | =< 1750 at maximum supply voltage | Not specified
|  | through front panel reset |  | Reserved for other products | reset time | Published
|  | through input control reset |  | Reserved for other products | reset time | Published
Setting accuracy |  |  |  | Common C_Rly Spec | setting accuracy of time delay | Published | Published | % | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales |  |  |  | +/- 10% of full scales | +/- 10% of full scales | Not specified | Not specified | +/- 10% of full scales | Not specified | +/- 10% of full scales | Not specified
Repeat accuracy (constant parameters) |  |  |  | Common C_Rly Spec | repeat accuracy of time delay | Published |  | % | +/- 2% | +/- 2% | +/- 2% | +/- 2% | ± 2 % | ± 2 % |  | +/- 2% | +/- 2% | Not specified | Not specified | +/- 2% | Not specified | +/- 2% | Not specified
Timing error with supply voltage variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/V | < 1 | < 1 | < 1 | < 1 |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Timing error with temperature variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/oC | < 0.05 | < 0.05 | < 0.05 | < 0.05 |  |  |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
LED Indication
status LED |  |  |  |  | status LED |  |  |  | R (Amber) | R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber)
local signalling |  | Power supply availability |  |  | local signalling |  |  |  | - | - | Dial pointer - ON | Dial pointer - ON | Green LED | Green LED
|  | Power supply not availability |  |  | local signalling |  |  |  | - | - | Dial pointer - OFF | Dial pointer - OFF
|  | Timing in-progress |  |  | local signalling |  |  |  | - | - | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz
|  | Output is energized |  |  | local signalling |  |  |  | R - ON | R - ON | R - ON | R - ON | Yellow LED | Yellow LED
|  | Output is de-energized |  |  | local signalling |  |  |  | R - OFF | R - OFF | R - OFF | R - OFF | Yellow LED | Yellow LED
|  | Range Setting Changes |  |  | local signalling |  |  |  | - | - | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
Special Features
True RMS | [8 empty] | - | - | - | -
Backlight Indicator | [8 empty] | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product
Diagnostic Button |  |  |  |  | diagnostic button | Published |  |  | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated
Pre-Alarm Output | [8 empty] | - | - | - | -
Output | [8 empty] | 1) Output is energized/ de-energized according to function diagram 2) When input monitored @ fault condition, output is always de-energized | 1) Output is energized/ de-energized according to function diagram 2) When input monitored @ fault condition, output is always de-energized | 1) Output is energized/ de-energized according to function diagram 2) When input monitored @ fault condition, output is always de-energized | 1) Output is energized/ de-energized according to function diagram 2) When input monitored @ fault condition, output is always de-energized
Reliability Data
Reliability Data |  | MTTF |  |  | safety reliability data | Published |  |  | 1,100,000 hours | 1,100,000 hours | 1,600,000 hours | 1,600,000 hours
|  | B10 |  |  | safety reliability data | Published |  |  | 120,000 hours | 120,000 hours | 170,000 hours | 170,000 hours
|  | MTTFd | [6 empty] | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product)
|  | B10d | [6 empty] | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product)
Drawing / Diagram
Note on D18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.1
Note on A42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Typical Product Operation Rate: 100% - product mostly will be powered and in operation in the actual application 50% - product is powered and in operation in the actual application @ ~50% of the time
Note on A44: Protection : Normal performance within the specification limits Command and control : Normal performance within the specification limits Measurement : Temporary degradation during test, with self-recovery at the end of the test. No loss of stored data Integral human-machine interface and visual alarms: Temporary degradation or loss of function during test, with self-recovery at the end of the test. No loss of stored data Data communication : Possible bit error rate increase but no loss of transmitted data
Note on A156: Measured with Yokogawa power meter and 3P4W connection
Note on A160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The minimum level of supply voltage that causes the product out-of power to operate. This must be a value other than 0V or total cut-off
Note on A162: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe list of available functions performed by the product as checklist
Note on A173: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe the characteristics and behaviors of the product when performing monitoring operation
Note on A186: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe the valid monitoring range able to be performed by the product for each type of functions
Note on A197: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe how the product is recognizing the Threshold to decide on triggering its output
Note on A208: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe how the product is recognizing the Hysteresis to decide on recovering its output
Note on D226: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-4-1 GB14048.4
Note on D227: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-4-1 GB14048.4
Note on D228: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-5-1 GB14048.5
Note on D229: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-5-1 GB14048.5
Note on D240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.5
Note on D241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.5
Note on A287: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Product Developed Before 2019: follow UTE C80-810 Product Developed After 2019 and require recalculation of MTBF: follow SN29500

## RM35HZ Spec
|  | Brand --> |  |  | brown text - widely used every where |  |  |  | SCHNEIDER ELECTRIC
|  | Base Design Reference --> |  |  | black text - product nature specific
Firmware Type -->
Main Parameters | Category | Sub Parameters | Conforming to | Remark | Standardized Datasheet Param | Selected for Publication | Old Datasheet | Unit | RM35HZ21FM
Standard
Product standard |  |  |  | Common C_Rly Spec | standards | Published | Published |  | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
Product certifications |  |  |  | Common C_Rly Spec | product certifications | Published | Published |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
Marking |  |  |  | Common C_Rly Spec | marking | Published |  |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
Low voltage directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/35/EU
EMC directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/30/EU
ROHS directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2011/65/EU
Environment Characteristics
Environmental Condition |  | Climatic category | IEC60721-3-3 | Common C_Rly Spec |  |  |  |  | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation)
|  | Environmental category | Germanisher Lloyd | Common C_Rly Spec |  |  |  |  | Class C
Ambient air temperature around the device |  | Storage |  | Common C_Rly Spec | ambient air temperature for storage | Published | Published | oC | -40oC..+70oC
|  | Operation |  |  | ambient air temperature for operation | Published | Published | oC | -20oC..+60oC @50Hz -20oC..+50oC @60Hz
Relative humidity |  | Damp heat | IEC60068-2-30 | Common C_Rly Spec | relative humidity | Published | Published |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97%
|  | Cyclic Damp Heat Test | IEC60947-5-1 | Common C_Rly Spec |  |  |  |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97%
Vibration resistance |  |  | IEC60068-2-6 | Common C_Rly Spec | vibration resistance | Published | Published |  | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating)
Shock resistance |  |  | IEC60068-2-27 | Common C_Rly Spec | shock resistance | Published | Published |  | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating)
Bump resistance |  |  | IEC60068-2-29 | Common C_Rly Spec | bump resistance |  |  |  | 10gn - 16ms ; 1000 X 6 axis (Non-Operating)
Seismic resistance |  |  | IEC60068-3-3 | Common C_Rly Spec | seismic resistance |  |  |  | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz
IP degree of protection |  | Terminal Block | IEC60529 |  | IP degree of protection | Published | Published |  | IP20
|  | Housing | IEC60529 |  | IP degree of protection | Published | Published |  | IP30
|  | Front Panel | IEC60529 |  | IP degree of protection |  |  |  | IP50 (With Transparent Cover)
Installation Data
Dimension (nominal) |  | Width |  |  | width | Published |  | mm | 35
|  | Height |  |  | height | Published |  | mm | 90
|  | Depth |  |  | depth | Published |  | mm | 72
Weight (without packaging) |  |  |  |  | net weight | Published |  | g | 95
Mounting |  | Without socket | IEC/EN 60715 |  | mounting support | Published | Published |  | On 35 mm DIN rail
|  | With socket | IEC/EN 60715 |  | mounting support |  |  |  | -
Mounting position |  | In relation to normal vertical mounting plane |  | Common C_Rly Spec | mounting position | Published | Published |  | Any position
Minimum distance to adjacent devices |  | Horizontal |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | 1x product height
|  | Vertical |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | 1x product width
Wiring connection (Clamping Capacity) |  | Solid cable without cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14)
|  | Flexible cable with cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16)
|  | Solid cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | -
|  | Flexible cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | -
|  | Tightening torque | IEC60947-1 | Common C_Rly Spec | tightening torque | Published | Published | Nm | 0.6…1 Nm
|  | Cable stripping length |  | Common C_Rly Spec | cable stripping length |  |  | mm | 6mm (Screw Terminal)
Duty time |  |  |  | Common C_Rly Spec | duty time |  |  | % | 100%
Electromagnetic Compatibility
Immunity |  | Generic immunity standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-1, IEC 61000-6-2
|  | Electrostatic discharge | IEC61000-4-2 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Contact : 6kV / Air : 8kV)
|  | Radiated RF & electromagnetic field | IEC61000-4-3 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz)
|  | Fast transient / burst | IEC61000-4-4 |  | electromagnetic compatibility | Published |  |  | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz)
|  | Surge | IEC61000-4-5 |  | electromagnetic compatibility | Published |  |  | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV)
|  | Conducted RF disturbance | IEC61000-4-6 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (10Vrms : 0.15MHz to 80MHz)
|  | Power frequency magnetic field | IEC61000-4-8 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level IV (30A/m : continous) (300A/m : 3s)
|  | Voltage dips, short interruption & variations on power line | IEC61000-4-11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz)
|  | 1 MHz oscillation wave | IEC61000-4-18 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV)
|  | DC voltage interruption | IEC61000-4-29 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | -
|  | Low frequency harmonics | IEC61000-4-13 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | -
|  | Conducted low frequency interference (harmonics) | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W
Emission |  | Generic emission standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-3, IEC 61000-6-4
|  | Radiated RF & electromagnetic field (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B
|  | Radiated RF & electromagnetic field (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1
|  | Radiated emission from enclosure port | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2
|  | Conducted RF emission on power line (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B
|  | Conducted RF emission on power line (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1
|  | Conducted emission | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2
Electrical Isolation
Degree of pollution |  |  | IEC60664-1 | Common C_Rly Spec | pollution degree | Published | Published |  | 3
Overvoltage category |  |  | IEC60664-1 | Common C_Rly Spec | overvoltage category | Published | Published |  | 3
Circuit Group | Terminal | Supply |  |  | circuit group | Published |  |  | A1, A2
|  | Input 1 |  |  | circuit group | Published |  |  | -
|  | Input 2 |  |  | circuit group | Published |  |  | -
|  | Input 3 |  |  | circuit group | Published |  |  | -
|  | Output 1 |  |  | circuit group | Published |  |  | 11,12,14
|  | Output 2 |  |  | circuit group | Published |  |  | 21,22,24
| Rated | Supply | [6 empty] | 120…277 AC/DC
| Voltage | Input 1 | [6 empty] | -
| Spec | Input 2 | [6 empty] | -
|  | Input 3 | [6 empty] | -
|  | Output 1 | [6 empty] | 250V
|  | Output 2 | [6 empty] | 250V
Rated Insulation Voltage |  | Supply | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V
|  | Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V
|  | Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Supply / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V
|  | Supply / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V
|  | Output 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V
|  | Input 1 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 2 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 2 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 3 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 3 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 1 / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | -
Rated Impulse Voltage |  | Supply | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3
|  | Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Supply / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3
|  | Supply / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3
|  | Output 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3
|  | Input 1 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 2 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 2 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 3 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 3 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 1 / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | -
Dielectric test voltage |  | Supply / Input 1 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Supply / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Supply / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Supply / Output 1 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min
|  | Supply / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min
|  | Output 1 / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Input 1 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Input 2 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Input 2 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Input 3 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Input 3 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Input 1 / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Input 2 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | -
|  | Input 1 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | -
Insulation resistance |  | Supply / Input 1 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Supply / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Supply / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Supply / Output 1 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC
|  | Supply / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC
|  | Output 1 / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC
|  | Input 1 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Input 1 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Input 2 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Input 2 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Input 3 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Input 3 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Input 1 / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Input 2 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | -
|  | Input 1 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | -
Power Supply Characteristics
Rated supply voltage, Us |  |  |  |  | [Us] rated supply voltage | Published | Published | V | ~ 120…277
Supply voltage operating range |  |  |  |  | supply voltage limits | Published | Published | V | ~ 102…308
Polarity on d.c. supply |  |  |  |  | polarity |  | Published |  | -
Rated frequency |  |  |  |  | supply frequency | Published | Published | Hz | 50 / 60
Frequency operating range |  |  |  |  | supply frequency | Published | Published | Hz | 45…66
Maximum power consumption |  |  |  |  | power consumption | Published | Published |  | 6
Immunity to micro-breakage |  |  |  |  | immunity to microbreaks | Published | Published | ms | 10
Supply terminal |  |  |  |  | supply terminal |  |  |  | A1-A2
On Load Factor |  |  |  | Common C_Rly Spec | on-load factor |  |  | % | 100%
Release of input voltage |  |  |  |  | release of input voltage |  |  | V | -
Input Circuit Characteristics
Monitoring functions |  | Over frequency @ 50Hz, With Memory |  |  | monitoring functions |  |  |  | - governed by time delay - status reflects to R1 - fault status will be memorized and only resetable through power cycle
|  | Over frequency @ 50Hz, Without Memory |  |  | monitoring functions |  |  |  | - governed by time delay - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis
|  | Over frequency @ 60Hz, With Memory |  |  | monitoring functions |  |  |  | - governed by time delay - status reflects to R1 - fault status will be memorized and only resetable through power cycle
|  | Over frequency @ 60Hz, Without Memory |  |  | monitoring functions |  |  |  | - governed by time delay - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis
|  | Under frequency @ 50Hz, With Memory |  |  | monitoring functions |  |  |  | - governed by time delay - status reflects to R2 - fault status will be memorized and only resetable through power cycle
|  | Under frequency @ 50Hz, Without Memory |  |  | monitoring functions |  |  |  | - governed by time delay - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis
|  | Under frequency @ 60Hz, With Memory |  |  | monitoring functions |  |  |  | - governed by time delay - status reflects to R2 - fault status will be memorized and only resetable through power cycle
|  | Under frequency @ 60Hz, Without Memory |  |  | monitoring functions |  |  |  | - governed by time delay - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis
Monitoring function characteristics |  | Measurement mode | [6 empty] | Resistive Voltage Step Down
|  | Internal input resistance |  |  | internal input resistance |  |  | W | -
|  | Input terminal |  |  | input terminal |  |  |  | A1-A2
|  | Input nominal frequency selection |  |  | Input nominal frequency selection |  |  | Hz | 50, 60
|  | permissible input overload |  |  | permissible input overload |  |  | Hz | 70
|  | Rated frequency |  |  | input frequency |  |  | Hz | 50 / 60
|  | Frequency operating range |  |  | input frequency |  |  | Hz | 40…70
|  | Setting accuracy |  |  | setting accuracy of the switching threshold |  |  | % | ± 10 % of the full scale value
|  | Repeat accuracy (constant parameters) |  |  | repeat accuracy of the switching threshold |  |  | % | +/- 0.5%
|  | Measurement method |  |  | measurement method |  |  |  | -
|  | Measurement error with supply voltage variation |  |  | switching threshold drift |  |  | %/V | < 1% of selected Un
|  | Measurement error with temperature variation |  |  | switching threshold drift |  |  | %/oC | < 0.05% / oC
|  | Maximum measuring cycles |  |  | maximum measuring cycle |  |  |  | 200ms / measurement as true rms value
Measurement range |  | Over frequency @ 50Hz, With Memory |  |  | measurement range |  |  | Hz | 40...70
|  | Over frequency @ 50Hz, Without Memory |  |  | measurement range |  |  | Hz | same as above
|  | Over frequency @ 60Hz, With Memory |  |  | measurement range |  |  | Hz | same as above
|  | Over frequency @ 60Hz, Without Memory |  |  | measurement range |  |  | Hz | same as above
|  | Under frequency @ 50Hz, With Memory |  |  | measurement range |  |  | Hz | same as above
|  | Under frequency @ 50Hz, Without Memory |  |  | measurement range |  |  | Hz | same as above
|  | Under frequency @ 60Hz, With Memory |  |  | measurement range |  |  | Hz | same as above
|  | Under frequency @ 60Hz, Without Memory |  |  | measurement range |  |  | Hz | same as above
Tripping threshold |  | Over frequency @ 50Hz, With Memory |  |  | tripping threshold |  |  | Hz | Adjustable -1 Hz…5 Hz for x1 scale Adjustable -2 Hz…10 Hz for x2 scale
|  | Over frequency @ 50Hz, Without Memory |  |  | tripping threshold |  |  | Hz | same as above
|  | Over frequency @ 60Hz, With Memory |  |  | tripping threshold |  |  | Hz | same as above
|  | Over frequency @ 60Hz, Without Memory |  |  | tripping threshold |  |  | Hz | same as above
|  | Under frequency @ 50Hz, With Memory |  |  | tripping threshold |  |  | Hz | Adjustable -5 Hz…1 Hz for x1 scale Adjustable -10 Hz…2 Hz for x2 scale
|  | Under frequency @ 50Hz, Without Memory |  |  | tripping threshold |  |  | Hz | same as above
|  | Under frequency @ 60Hz, With Memory |  |  | tripping threshold |  |  | Hz | same as above
|  | Under frequency @ 60Hz, Without Memory |  |  | tripping threshold |  |  | Hz | same as above
Hysteresis |  | Over frequency @ 50Hz, With Memory |  |  | hysteresis |  |  | Hz | Fixed +/- 0.3Hz Internal design spec: Fixed +/- 0.2Hz
|  | Over frequency @ 50Hz, Without Memory |  |  | hysteresis |  |  | Hz | same as above
|  | Over frequency @ 60Hz, With Memory |  |  | hysteresis |  |  | Hz | same as above
|  | Over frequency @ 60Hz, Without Memory |  |  | hysteresis |  |  | Hz | same as above
|  | Under frequency @ 50Hz, With Memory |  |  | hysteresis |  |  | Hz | same as above
|  | Under frequency @ 50Hz, Without Memory |  |  | hysteresis |  |  | Hz | same as above
|  | Under frequency @ 60Hz, With Memory |  |  | hysteresis |  |  | Hz | same as above
|  | Under frequency @ 60Hz, Without Memory |  |  | hysteresis |  |  | Hz | same as above
Output Circuit Characteristics
Type of output |  |  |  |  | output type | Published | Published |  | 2 x C/O relay contacts
Output terminal |  |  |  |  | output terminal |  |  |  | 15-16-18, 25-26-28
Operation principle |  | R1 (11-12-14) |  |  | output logic |  |  |  | Energized on fault-free
|  | R2 (21-22-24) |  |  | output logic |  |  |  | Energized on fault-free
Contact material |  |  |  | Common C_Rly Spec | contacts material | Published | Published |  | Cadmium free
Mechanical durability |  |  | IEC61810-1 | Common C_Rly Spec | mechanical durability | Published | Published | Cyc | 10 x 106 cycles
Electrical durability |  | AC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles
|  | DC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/5A, 100k cycles
|  | AC-15 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/0.15A, 100k cycles
|  | DC-13 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/1A, 100k cycles
Rated capacity |  | Rated switching voltage | IEC61810-1 | Common C_Rly Spec | [Ue] rated operational voltage | Published |  | V | 250V
|  | Rated switching current | IEC61810-1 | Common C_Rly Spec | [Ie] rated operational current | Published | Published | A | 8A
Maximum switching capacity |  | Maximum switching voltage |  | Common C_Rly Spec | maximum switching capacity | Published | Published | V | 250V
|  | Maximum switching current |  | Common C_Rly Spec | maximum switching capacity | Published | Published | A | 8A
|  | Maximum switching capacity |  | Common C_Rly Spec | maximum switching capacity | Published | Published | VA | -
Minimum switching capacity |  | Minimum switching voltage | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | V | -
|  | Minimum switching current | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | mA | -
|  | Minimum switching capacity | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published | Published | mW | NO: 12V/10mA, MCTF > 80,000,000
Maximum voltage drop at terminals |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum voltage drop |  |  | V | -
Leakage current |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum leakage current |  |  | mA | -
Thermal Current |  |  | IEC60947-5-1 | Common C_Rly Spec | thermal current |  |  | A | 8A
Short circuit protection |  | Relay Output by external fuse | IEC60947-5-1 | Common C_Rly Spec | short circuit protection |  |  | gG | 8A
|  | Solid State Output by external fuse | IEC62314 | Common C_Rly Spec | short circuit protection |  |  | gG | -
Time Delay Characteristics
Time delay functions |  | "OFF" delay |  |  | time delay type | Published |  |  | Yes
|  | "ON" delay |  |  | time delay type | Published |  |  | -
|  | Inhibition |  |  | time delay type | Published |  |  | -
Timing delay range |  | "OFF" delay |  |  | time delay range | Published | Published | s | Adjustable 0.1…10
|  | "ON" delay |  |  | time delay range | Published |  | s | -
|  | Inhibition |  |  | time delay range | Published | Published | s | -
Response time |  | on crossing the threshold (all monitoring functions) |  |  | response time | Published | Published | ms | TBD
|  | on crossing the hysteresis (all monitoring functions) |  | Reserved for other products | response time | Published |  |  | -
|  | on crossing the threshold (specific monitoring functions 1) |  | Reserved for other products | response time | Published |  |  | -
|  | on crossing the threshold (specific monitoring functions 2) |  | Reserved for other products | response time | Published |  |  | -
|  | on crossing the threshold (specific monitoring functions 3) |  | Reserved for other products | response time | Published |  |  | -
Time delay of pick-up |  |  |  |  | power on delay | Published | Published | ms | =< 500 Internal Design spec: TBD
Reset time |  | through Un power reset |  |  | reset time | Published | Published | ms | =< 2000 at maximum rated supply voltage
|  | through front panel reset |  | Reserved for other products | reset time | Published |  |  | -
|  | through input control reset |  | Reserved for other products | reset time | Published |  |  | -
Setting accuracy |  |  |  | Common C_Rly Spec | setting accuracy of time delay | Published | Published | % | +/- 10% of full scales value Internal Design Spec: +/- 10% of full scales value (potentiometer turns left to right and oppossite)
Repeat accuracy (constant parameters) |  |  |  | Common C_Rly Spec | repeat accuracy of time delay | Published |  | % | +/- 0.5%
Timing error with supply voltage variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/V | -
Timing error with temperature variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/oC | -
LED Indication
status LED |  |  |  |  | status LED |  |  |  | Un (Green) R1 (Amber) R2 (Amber)
local signalling |  | Power supply availability |  |  | local signalling |  |  |  | Un - ON
|  | Power supply not availability |  |  | local signalling |  |  |  | Un - OFF
|  | Timing in-progress |  |  | local signalling |  |  |  | Rx - Slow Blink (50% ON; 50% OFF) @ 1Hz
|  | Output is energized |  |  | local signalling |  |  |  | Rx - ON
|  | Output is de-energized |  |  | local signalling |  |  |  | Rx - OFF
|  | Range Setting Changes |  |  | local signalling |  |  |  | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
Special Features
True RMS | [8 empty] | -
Backlight Indicator | [8 empty] | -
Diagnostic Button |  |  |  |  | diagnostic button | Published |  |  | -
Pre-Alarm Output | [8 empty] | -
Output | [8 empty] | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
Reliability Data
Reliability Data |  | MTTF |  |  | safety reliability data | Published |  |  | TBD
|  | B10 |  |  | safety reliability data | Published |  |  | TBD
|  | MTTFd | [6 empty] | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product)
|  | B10d | [6 empty] | Cannot declare B10 = B10d (Note: customer confuses as safety product)
Drawing / Diagram
Note on D18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.1
Note on J36: Align with marking
Note on J37: Align with marking
Note on A42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Typical Product Operation Rate: 100% - product mostly will be powered and in operation in the actual application 50% - product is powered and in operation in the actual application @ ~50% of the time
Note on A44: Protection : Normal performance within the specification limits Command and control : Normal performance within the specification limits Measurement : Temporary degradation during test, with self-recovery at the end of the test. No loss of stored data Integral human-machine interface and visual alarms: Temporary degradation or loss of function during test, with self-recovery at the end of the test. No loss of stored data Data communication : Possible bit error rate increase but no loss of transmitted data
Note on A160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The minimum level of supply voltage that causes the product out-of power to operate. This must be a value other than 0V or total cut-off
Note on A162: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe list of available functions performed by the product as checklist
Note on A173: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe the characteristics and behaviors of the product when performing monitoring operation
Note on A186: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe the valid monitoring range able to be performed by the product for each type of functions
Note on A197: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe how the product is recognizing the Threshold to decide on triggering its output
Note on A208: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe how the product is recognizing the Hysteresis to decide on recovering its output
Note on D226: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-4-1 GB14048.4
Note on D227: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-4-1 GB14048.4
Note on D228: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-5-1 GB14048.5
Note on D229: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-5-1 GB14048.5
Note on D240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.5
Note on D241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.5
Note on A287: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Product Developed Before 2019: follow UTE C80-810 Product Developed After 2019 and require recalculation of MTBF: follow SN29500

## RM35TM Spec
|  | Brand --> |  |  | brown text - widely used every where |  |  |  | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC
|  | Base Design Reference --> |  |  | black text - product nature specific
Firmware Type -->
Main Parameters | Category | Sub Parameters | Conforming to | Remark | Standardized Datasheet Param | Selected for Publication | Old Datasheet | Unit | RM35TM250MW | RM35TM50MW
Standard
Product standard |  |  |  | Common C_Rly Spec | standards | Published | Published |  | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5
Product certifications |  |  |  | Common C_Rly Spec | product certifications | Published | Published |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
Marking |  |  |  | Common C_Rly Spec | marking | Published |  |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS
Low voltage directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/35/EU | 2014/35/EU
EMC directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/30/EU | 2014/30/EU
ROHS directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2011/65/EU | 2011/65/EU
Environment Characteristics
Environmental Condition |  | Climatic category | IEC60721-3-3 | Common C_Rly Spec |  |  |  |  | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation) | 3K9 (refer absolute Humidity 36g/m3 as worst case product Mission Profile RH evaluation)
|  | Environmental category | Germanisher Lloyd | Common C_Rly Spec |  |  |  |  | Class C | Class C
Ambient air temperature around the device |  | Storage |  | Common C_Rly Spec | ambient air temperature for storage | Published | Published | oC | -40oC..+70oC | -40oC..+70oC
|  | Operation |  |  | ambient air temperature for operation | Published | Published | oC | -20oC..+60oC @50Hz -20oC..+50oC @60Hz | -20oC..+60oC @50Hz -20oC..+50oC @60Hz
Relative humidity |  | Damp heat | IEC60068-2-30 | Common C_Rly Spec | relative humidity | Published | Published |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97%
|  | Cyclic Damp Heat Test | IEC60947-5-1 | Common C_Rly Spec |  |  |  |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97%
Vibration resistance |  |  | IEC60068-2-6 | Common C_Rly Spec | vibration resistance | Published | Published |  | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating)
Shock resistance |  |  | IEC60068-2-27 | Common C_Rly Spec | shock resistance | Published | Published |  | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating)
Bump resistance |  |  | IEC60068-2-29 | Common C_Rly Spec | bump resistance |  |  |  | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating)
Seismic resistance |  |  | IEC60068-3-3 | Common C_Rly Spec | seismic resistance |  |  |  | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz
IP degree of protection |  | Terminal Block | IEC60529 |  | IP degree of protection | Published | Published |  | IP20 | IP20
|  | Housing | IEC60529 |  | IP degree of protection | Published | Published |  | IP30 | IP30
|  | Front Panel | IEC60529 |  | IP degree of protection |  |  |  | IP50 (With Transparent Cover) | IP50 (With Transparent Cover)
Installation Data
Dimension (nominal) |  | Width |  |  | width | Published |  | mm | 35 | 35
|  | Height |  |  | height | Published |  | mm | 90 | 90
|  | Depth |  |  | depth | Published |  | mm | 72 | 72
Weight (without packaging) |  |  |  |  | net weight | Published |  | g | 95 | 95
Mounting |  | Without socket | IEC/EN 60715 |  | mounting support | Published | Published |  | On 35 mm DIN rail | On 35 mm DIN rail
|  | With socket | IEC/EN 60715 |  | mounting support |  |  |  | - | -
Mounting position |  | In relation to normal vertical mounting plane |  | Common C_Rly Spec | mounting position | Published | Published |  | Any position | Any position
Minimum distance to adjacent devices |  | Horizontal |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | 1x product height | 1x product height
|  | Vertical |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | 1x product width | 1x product width
Wiring connection (Clamping Capacity) |  | Solid cable without cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14)
|  | Flexible cable with cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16) | 1 conductor: 0.5…2.5 (AWG 20…AWG 14) 2 conductors: 0.5…1.5 (AWG 20…AWG 16)
|  | Solid cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | -
|  | Flexible cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | -
|  | Tightening torque | IEC60947-1 | Common C_Rly Spec | tightening torque | Published | Published | Nm | 0.6…1 Nm | 0.6…1 Nm
|  | Cable stripping length |  | Common C_Rly Spec | cable stripping length |  |  | mm | 6mm (Screw Terminal) | 6mm (Screw Terminal)
Duty time |  |  |  | Common C_Rly Spec | duty time |  |  | % | 100% | 100%
Electromagnetic Compatibility
Immunity |  | Generic immunity standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2
|  | Electrostatic discharge | IEC61000-4-2 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV)
|  | Radiated RF & electromagnetic field | IEC61000-4-3 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz)
|  | Fast transient / burst | IEC61000-4-4 |  | electromagnetic compatibility | Published |  |  | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) | Level III (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz)
|  | Surge | IEC61000-4-5 |  | electromagnetic compatibility | Published |  |  | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) | Level III (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV)
|  | Conducted RF disturbance | IEC61000-4-6 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (10Vrms : 0.15MHz to 80MHz) | Level III (10Vrms : 0.15MHz to 80MHz)
|  | Power frequency magnetic field | IEC61000-4-8 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s)
|  | Voltage dips, short interruption & variations on power line | IEC61000-4-11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz) | Class II 0%, 1/2 cycle 0%, 1 cycle 70% 25 cycles (50Hz) 70%, 30 cycles (60Hz) 0%, 250 cycles (50Hz) 0%, 300 cycles (60Hz)
|  | 1 MHz oscillation wave | IEC61000-4-18 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV)
|  | DC voltage interruption | IEC61000-4-29 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | -
|  | Low frequency harmonics | IEC61000-4-13 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | -
|  | Conducted low frequency interference (harmonics) | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) - Not applicable AC Supply : 1st…200th harmonics, Max 2W
Emission |  | Generic emission standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4
|  | Radiated RF & electromagnetic field (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B
|  | Radiated RF & electromagnetic field (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1
|  | Radiated emission from enclosure port | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2
|  | Conducted RF emission on power line (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B
|  | Conducted RF emission on power line (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1
|  | Conducted emission | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2
Electrical Isolation
Degree of pollution |  |  | IEC60664-1 | Common C_Rly Spec | pollution degree | Published | Published |  | 3 | 3
Overvoltage category |  |  | IEC60664-1 | Common C_Rly Spec | overvoltage category | Published | Published |  | 3 | 3
Circuit Group | Terminal | Supply |  |  | circuit group | Published |  |  | A1, A2 | A1, A2
|  | Input 1 |  |  | circuit group | Published |  |  | T1, T2 | T1, T2
|  | Input 2 |  |  | circuit group | Published |  |  | Y1 | -
|  | Input 3 |  |  | circuit group | Published |  |  | L1, L2, L3 | L1, L2, L3
|  | Output 1 |  |  | circuit group | Published |  |  | 11,12,14 | 11,12,14
|  | Output 2 |  |  | circuit group | Published |  |  | 21,22,24 | 21,22,24
| Rated | Supply | [6 empty] | 24…240 AC/DC | 24…240 AC/DC
| Voltage | Input 1 | [6 empty] | PTC probe | PTC probe
| Spec | Input 2 | [6 empty] | Push Button Switch | Push Button Switch
|  | Input 3 | [6 empty] | 208..480 AC/DC | 208..480 AC/DC
|  | Output 1 | [6 empty] | 250V | 250V
|  | Output 2 | [6 empty] | 250V | 250V
Rated Insulation Voltage |  | Supply | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V
|  | Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 10V | 10V
|  | Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 10V | -
|  | Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | 500V
|  | Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V
|  | Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | 500V
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | -
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | 500V
|  | Supply / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V
|  | Supply / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V
|  | Output 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V
|  | Input 1 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | 500V
|  | Input 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | 500V
|  | Input 2 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | -
|  | Input 2 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | -
|  | Input 3 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | 500V
|  | Input 3 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 500V | 500V
|  | Input 1 / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | -
Rated Impulse Voltage |  | Supply | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | -
|  | Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | -
|  | Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | -
|  | Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | -
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | -
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Supply / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Supply / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Output 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Input 2 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | -
|  | Input 2 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | -
|  | Input 3 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Input 3 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | -
Dielectric test voltage |  | Supply / Input 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Supply / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | -
|  | Supply / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Supply / Output 1 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Supply / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Output 1 / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 2 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | -
|  | Input 2 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | -
|  | Input 3 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 3 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | -
|  | Input 2 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | -
|  | Input 1 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | -
Insulation resistance |  | Supply / Input 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | -
|  | Supply / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Output 1 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Output 1 / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 2 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | -
|  | Input 2 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | -
|  | Input 3 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 3 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | -
|  | Input 2 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | -
|  | Input 1 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | -
Power Supply Characteristics
Rated supply voltage, Us |  |  |  |  | [Us] rated supply voltage | Published | Published | V | ~/-- 24…240 | ~/-- 24…240
Supply voltage operating range |  |  |  |  | supply voltage limits | Published | Published | V | ~/-- 20.4…264 | ~/-- 20.4…264
Polarity on d.c. supply |  |  |  |  | polarity |  | Published |  | No | No
Rated frequency |  |  |  |  | supply frequency | Published | Published | Hz | 50 / 60 | 50 / 60
Frequency operating range |  |  |  |  | supply frequency | Published | Published | Hz | 45…66 | 45…66
Maximum power consumption |  |  |  |  | power consumption | Published | Published |  | 1 4 VA / 2 0.5 W | 1 4 VA / 2 0.5 W
Immunity to micro-breakage |  |  |  |  | immunity to microbreaks | Published | Published | ms | 20 ms at 20.4 V | 20 ms at 20.4 V
Supply terminal |  |  |  |  | supply terminal |  |  |  | A1-A2 | A1-A2
On Load Factor |  |  |  | Common C_Rly Spec | on-load factor |  |  | % | 100% | 100%
Release of input voltage |  |  |  |  | release of input voltage |  |  | V | - | -
Input Circuit Characteristics
Monitoring functions |  | Motor temperature through PTC sensor, With Memory |  |  | monitoring functions |  |  |  | - governed by response time only - status reflects to R1 - fault status will be memorized and only resetable through power cycle, Test/Reset button or Y1-T1 volt-free input | -
|  | Motor temperature through PTC sensor, Without Memory |  |  | monitoring functions |  |  |  | - governed by response time only - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis | - governed by response time only - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis
|  | Short circuit of PTC sensor |  |  | monitoring functions |  |  |  | - governed by response time only - status reflects to R1 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis | - governed by response time only - status reflects to R1 - fault status will not be memorized and be recovered through hysteresis
|  | Phase lost |  |  | monitoring functions |  |  |  | - governed by response time only, - status reflects to R2 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis | - governed by response time only, - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis
|  | Phase sequence |  |  | monitoring functions |  |  |  | - governed by response time only, - status reflects to R2 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis | - governed by response time only, - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis
|  | Voltage Regeneration |  |  | monitoring functions |  |  |  | - governed by response time only, - status reflects to R2 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis | - governed by response time only, - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis
|  | Extreme undervoltage (Phase loss) |  |  | monitoring functions |  |  |  | - governed by response time only, - status reflects to R2 - only governed by "No Memory"function, fault status will not be memorized and be recovered through hysteresis | - governed by response time only, - status reflects to R2 - fault status will not be memorized and be recovered through hysteresis
Monitoring function characteristics | Motor temperature | Input terminal |  |  | input terminal |  |  |  | T1-T2 | T1-T2
|  | Maximum voltage of temperature control circuit |  |  | Maximum voltage of temperature control circuit |  |  | V | 3.6V when T1-T2 is open | 3.6V when T1-T2 is open
|  | Temperature sensing circuit short-circuit current |  |  | Temperature sensing circuit short-circuit current |  |  | mA | 7mA when T1-T2 is short-circuited | 7mA when T1-T2 is short-circuited
|  | Maximum resistance of temperature sensor at 20°C |  |  | Maximum resistance of temperature sensor at 20°C |  |  | W | 1500Ω | 1500Ω
| 3 Phase | Measurement mode |  |  | input frequency |  |  |  | Resistive Voltage Step Down | Resistive Voltage Step Down
|  | Internal input resistance |  |  | setting accuracy of the switching threshold |  |  | kW | 602/line | 602/line
|  | Input terminal |  |  | repeat accuracy of the switching threshold |  |  |  | L1-L2-L3 | L1-L2-L3
|  | Input nominal voltage selection |  |  | measurement method |  |  |  | - | -
|  | permissible input overload |  |  | switching threshold drift |  |  | V | ~ 3 x 176…3 x 528 | ~ 3 x 176…3 x 528
|  | Rated frequency |  |  | switching threshold drift |  |  | Hz | 50 / 60 | 50 / 60
|  | Frequency operating range |  |  | maximum measuring cycle |  |  | Hz | 45…66 | 45…66
Measurement range |  | Motor temperature through PTC sensor | IEC60034-11 |  | measurement range |  |  |  | Mark A probe characteristics | Mark A probe characteristics
|  | Short circuit of PTC sensor |  |  | measurement range |  |  | V | ~ 3 x 208…3 x 480 | ~ 3 x 208…3 x 480
|  | Phase lost |  |  | measurement range |  |  |  | same as above | same as above
|  | Phase sequence |  |  | measurement range |  |  |  | same as above | same as above
|  | Voltage Regeneration |  |  | measurement range |  |  |  | same as above | same as above
Tripping threshold |  | Motor temperature through PTC sensor |  |  | tripping threshold |  |  | W | 3100 ± 10 % Internal design spec: TBD | 3100 ± 10 % Internal design spec: TBD
|  | Short circuit of PTC sensor |  |  | tripping threshold |  |  | W | 0…15 ± 5 Internal design spec: TBD | 0…15 ± 5 Internal design spec: TBD
|  | Phase lost |  |  | tripping threshold |  |  |  | 1 or more phase cut | 1 or more phase cut
|  | Phase sequence |  |  | tripping threshold |  |  |  | Total swap of phase Internal design spec: L23 lags L13 >= 180o | Total swap of phase Internal design spec: L23 lags L13 >= 180o
|  | Voltage Regeneration |  |  | tripping threshold |  |  | % | 1 or more phase =< 30% * [(L21 + L31 + L32) / 3] Internal design spec: TBD | 1 or more phase =< 30% * [(L21 + L31 + L32) / 3] Internal design spec: TBD
|  | Extreme undervoltage (Phase loss) |  |  | tripping threshold |  |  |  | Internal design spec: TBD | Internal design spec: TBD
Hysteresis |  | Motor temperature through PTC sensor |  |  | hysteresis |  |  | W | 1650 ± 10 % Internal design spec: TBD | 1650 ± 10 % Internal design spec: TBD
|  | Short circuit of PTC sensor |  |  | hysteresis |  |  | W | Internal design spec: TBD | Internal design spec: TBD
|  | Phase lost |  |  | hysteresis |  |  |  | All phase cut recover | All phase cut recover
|  | Phase sequence |  |  | hysteresis |  |  |  | Total phase swap recover Internal design spec: L23 lags L13 < 180o | Total phase swap recover Internal design spec: L23 lags L13 < 180o
|  | Voltage Regeneration |  |  | hysteresis |  |  | % | Internal design spec: TBD | Internal design spec: TBD
|  | Extreme undervoltage (Phase loss) |  |  | hysteresis |  |  |  | Internal design spec: TBD | Internal design spec: TBD
Output Circuit Characteristics
Type of output |  |  |  |  | output type | Published | Published |  | 2 x C/O relay contacts | 2 x C/O relay contacts
Output terminal |  |  |  |  | output terminal |  |  |  | 15-16-18, 25-26-28 | 15-16-18, 25-26-28
Operation principle |  | R1 (11-12-14) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free
|  | R2 (21-22-24) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free
Contact material |  |  |  | Common C_Rly Spec | contacts material | Published | Published |  | Cadmium free | Cadmium free
Mechanical durability |  |  | IEC61810-1 | Common C_Rly Spec | mechanical durability | Published | Published | Cyc | 10 x 106 cycles | 10 x 106 cycles
Electrical durability |  | AC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles
|  | DC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles
|  | AC-15 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles
|  | DC-13 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles
Rated capacity |  | Rated switching voltage | IEC61810-1 | Common C_Rly Spec | [Ue] rated operational voltage | Published |  | V | 250V | 250V
|  | Rated switching current | IEC61810-1 | Common C_Rly Spec | [Ie] rated operational current | Published | Published | A | 8A | 8A
Maximum switching capacity |  | Maximum switching voltage |  | Common C_Rly Spec | maximum switching capacity | Published | Published | V | 250V | 250V
|  | Maximum switching current |  | Common C_Rly Spec | maximum switching capacity | Published | Published | A | 8A | 8A
|  | Maximum switching capacity |  | Common C_Rly Spec | maximum switching capacity | Published | Published | VA | - | -
Minimum switching capacity |  | Minimum switching voltage | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | V | - | -
|  | Minimum switching current | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | mA | - | -
|  | Minimum switching capacity | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published | Published | mW | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000
Maximum voltage drop at terminals |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum voltage drop |  |  | V | - | -
Leakage current |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum leakage current |  |  | mA | - | -
Thermal Current |  |  | IEC60947-5-1 | Common C_Rly Spec | thermal current |  |  | A | 8A | 8A
Short circuit protection |  | Relay Output by external fuse | IEC60947-5-1 | Common C_Rly Spec | short circuit protection |  |  | gG | 8A | 8A
|  | Solid State Output by external fuse | IEC62314 | Common C_Rly Spec | short circuit protection |  |  | gG | - | -
Time Delay Characteristics
Time delay functions |  | "OFF" delay |  |  | time delay type | Published |  |  | - | -
|  | "ON" delay |  |  | time delay type | Published |  |  | - | -
|  | Inhibition |  |  | time delay type | Published |  |  | - | -
Timing delay range |  | "OFF" delay |  |  | time delay range | Published | Published | s | - | -
|  | "ON" delay |  |  | time delay range | Published |  | s | - | -
|  | Inhibition |  |  | time delay range | Published | Published | s | - | -
Response time |  | on crossing the threshold (Motor Temperature) |  |  | response time | Published | Published | ms | 300 | 300
|  | on crossing the hysteresis (all 3 Phase functions) |  | Reserved for other products | response time | Published |  | ms | 300 | 300
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
Time delay of pick-up |  |  |  |  | power on delay | Published | Published | ms | 500 | 500
Reset time |  | through Un power reset |  |  | reset time | Published | Published | ms | 10 000 | 10 000
|  | through front panel reset |  | Reserved for other products | reset time | Published |  | ms | >= 50 (press to release) | -
|  | through input control reset |  | Reserved for other products | reset time | Published |  | ms | >= 50 (Y1 short to T1) | -
Setting accuracy |  |  |  | Common C_Rly Spec | setting accuracy of time delay | Published | Published | % | - | -
Repeat accuracy (constant parameters) |  |  |  | Common C_Rly Spec | repeat accuracy of time delay | Published |  | % | - | -
Timing error with supply voltage variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/V | - | -
Timing error with temperature variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/oC | - | -
LED Indication
status LED |  |  |  |  | status LED |  |  |  | Un (Green) R1 (Amber) R2 (Amber) | Un (Green) R1 (Amber) R2 (Amber)
local signalling |  | Power supply availability |  |  | local signalling |  |  |  | Un - ON | Un - ON
|  | Power supply not availability |  |  | local signalling |  |  |  | Un - OFF | Un - OFF
|  | Timing in-progress |  |  | local signalling |  |  |  | - | -
|  | Output is energized |  |  | local signalling |  |  |  | Rx - ON | Rx - ON
|  | Output is de-energized |  |  | local signalling |  |  |  | Rx - OFF | Rx - OFF
|  | Range Setting Changes |  |  | local signalling |  |  |  | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | -
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
Special Features
Test / Reset button | [8 empty] | 1) When Set to "No Memory" 1a) When motor temperature is normal, - pressing the "Test/Reset" button simulates overheating, R1 is de-energized - R1 will remain energized as long as "Test/Reset" button remains pressed 1b) When motor temperature is abnormal, - pressing the "Test/Reset" button will not change any product status 2) When Set to "Memory" 2a) When motor temperature is normal, - pressing the "Test/Reset" button simulates overheating, R1 is de-energized - R1 will remain energized as long as "Test/Reset" button remains pressed 2b) When motor temperature is abnormal, - pressing the "Test/Reset" button will not change any product status 2c) When motor temperature is abnormal at first and recover to normal - pressing the "Test/Reset" button will reset the fault, R1 is energized | -
Y1-T1 voltage free contact | [8 empty] | 1) Same function as per Test / Reset button 2) Short Y1 to T1 is the same meaning as pressing "Test/Reset" button 3) Open Y1 to T1 is the same meaning as releasing "Test/Reset" button | -
Diagnostic Button |  |  |  |  | diagnostic button | Published |  |  | - | -
Pre-Alarm Output | [8 empty] | - | -
Output | [8 empty] | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
Reliability Data
Reliability Data |  | MTTF |  |  | safety reliability data | Published |  |  | TBD | TBD
|  | B10 |  |  | safety reliability data | Published |  |  | TBD | TBD
|  | MTTFd | [6 empty] | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product)
|  | B10d | [6 empty] | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product)
Drawing / Diagram
Note on D18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.1
Note on J36: Align with marking
Note on K36: Align with marking
Note on J37: Align with marking
Note on K37: Align with marking
Note on A42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Typical Product Operation Rate: 100% - product mostly will be powered and in operation in the actual application 50% - product is powered and in operation in the actual application @ ~50% of the time
Note on A44: Protection : Normal performance within the specification limits Command and control : Normal performance within the specification limits Measurement : Temporary degradation during test, with self-recovery at the end of the test. No loss of stored data Integral human-machine interface and visual alarms: Temporary degradation or loss of function during test, with self-recovery at the end of the test. No loss of stored data Data communication : Possible bit error rate increase but no loss of transmitted data
Note on A160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The minimum level of supply voltage that causes the product out-of power to operate. This must be a value other than 0V or total cut-off
Note on A162: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe list of available functions performed by the product as checklist
Note on A173: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe the characteristics and behaviors of the product when performing monitoring operation
Note on A186: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe the valid monitoring range able to be performed by the product for each type of functions
Note on A197: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe how the product is recognizing the Threshold to decide on triggering its output
Note on A208: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Describe how the product is recognizing the Hysteresis to decide on recovering its output
Note on D226: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-4-1 GB14048.4
Note on D227: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-4-1 GB14048.4
Note on D228: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-5-1 GB14048.5
Note on D229: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-5-1 GB14048.5
Note on D240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.5
Note on D241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.5
Note on A287: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Product Developed Before 2019: follow UTE C80-810 Product Developed After 2019 and require recalculation of MTBF: follow SN29500

## 1P Voltage Control Spec
|  | Brand --> |  |  | brown text - widely used every where |  |  |  | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | OLD SE | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC
|  | Base Design Reference --> |  |  | black text - product nature specific |  |  |  | HW & FW adapted from RM35UA11MW | HW & FW adapted from RM35UA12MW | HW & FW adapted from RM35UA13MW | HW & FW adapted from RM35UA11MW | HW & FW adapted from RM35UA12MW | HW & FW adapted from RM35UA13MW | HW & FW adapted from RM35UA13MW | HW & FW adapted from RM17UBE15 | (RM4 + Crouzet)
Firmware Type -->
Main Parameters | Category | Sub Parameters | Conforming to | Remark | Standardized Datasheet Param | Selected for Publication | Old Datasheet | Unit | RM22UA21MR | RM22UA22MR | RM22UA23MR | RM22UA31MR | RM22UA32MR | RM22UA33MR | RM22UA33MT | RM22UB34 | Competitor Spec Reference | RM35UA11MW | RM35UA12MW | RM35UA13MW | RM22UA3 (Catch Up) | RM4UA3 | RM4UA0
Standard
Product standard |  |  |  | Common C_Rly Spec | standards | Published | Published |  | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 |  | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6
Product certifications |  |  |  | Common C_Rly Spec | product certifications | Published | Published |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS |  | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST
Marking |  |  |  | Common C_Rly Spec | marking | Published |  |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS |  | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE
Low voltage directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU |  | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC
EMC directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU |  | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC
ROHS directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU |  | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC | 2002/95/EC
Environment Characteristics
Environmental Condition |  | Climatic category | IEC60721-3-3 | Common C_Rly Spec |  |  |  |  | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | Environmental category | Germanisher Lloyd | Common C_Rly Spec |  |  |  |  | Class C | Class C | Class C | Class C | Class C | Class C | Class C | Class C
Ambient air temperature around the device |  | Storage |  | Common C_Rly Spec | ambient air temperature for storage | Published | Published | oC | -40oC..+80oC | -40oC..+80oC | -40oC..+80oC | -40oC..+80oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC |  | -40…+70 | -40…+70 | -40…+70 | -40…+70 | Not specified | Not specified
|  | Operation |  |  | ambient air temperature for operation | Published | Published | oC | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) |  | -20…+50 | -20…+50 | -20…+50 | -20…+50 | Not specified | Not specified
Relative humidity |  | Damp heat | IEC60068-2-30 | Common C_Rly Spec | relative humidity | Published | Published |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% |  | 2 cycles 24h ;+25°C +55°C 95%HR | 2 cycles 24h ;+25°C +55°C 95%HR | 2 cycles 24h ;+25°C +55°C 95%HR | 2 cycles 24h ;+25°C +55°C 95%HR | Not specified | Not specified
|  | Cyclic Damp Heat Test | IEC60947-5-1 | Common C_Rly Spec |  |  |  |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97%
Vibration resistance |  |  | IEC60068-2-6 | Common C_Rly Spec | vibration resistance | Published | Published |  | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) |  | 0.035mm from 10Hz…150Hz | 0.035mm from 10Hz…150Hz | 0.035mm from 10Hz…150Hz | 0.035mm from 10Hz…150Hz | Not specified | Not specified
Shock resistance |  |  | IEC60068-2-27 | Common C_Rly Spec | shock resistance | Published | Published |  | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) |  | 5 gn | 5 gn | 5 gn | 5 gn | Not specified | Not specified
Bump resistance |  |  | IEC60068-2-29 | Common C_Rly Spec | bump resistance |  |  |  | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating)
Seismic resistance |  |  | IEC60068-3-3 | Common C_Rly Spec | seismic resistance |  |  |  | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz
IP degree of protection |  | Terminal Block | IEC60529 |  | IP degree of protection | Published | Published |  | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 | IP20 |  | IP20 | IP20 | IP20 | IP20 | Not specified | Not specified
|  | Housing | IEC60529 |  | IP degree of protection | Published | Published |  | IP40 | IP40 | IP40 | IP40 | IP40 | IP40 | IP40 | IP40 |  | IP30 | IP30 | IP30 | IP30 | Not specified | Not specified
|  | Front Panel | IEC60529 |  | IP degree of protection |  |  |  | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover)
Installation Data
Dimension (nominal) |  | Width |  |  | width | Published |  | mm | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 |  | 35 x 90 x 72 | 35 x 90 x 72 | 35 x 90 x 72 | 22.5 x ? x ? | 22.5 x 78 x 80 | 22.5 x 78 x 80
|  | Height |  |  | height | Published |  | mm
|  | Depth |  |  | depth | Published |  | mm
Weight (without packaging) |  |  |  |  | net weight | Published |  | g | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 90 |  | 130 | 130 | 130 | ? | 168 | 168
Mounting |  | Without socket | IEC/EN 60715 |  | mounting support | Published | Published |  | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail |  | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail
|  | With socket | IEC/EN 60715 |  | mounting support |  |  |  | - | - | - | - | - | - | - | - |  | - | - | - | - | - | -
Mounting position |  | In relation to normal vertical mounting plane |  | Common C_Rly Spec | mounting position | Published | Published |  | Any position | Any position | Any position | Any position | Any position | Any position | Any position | Any position |  | Any position | Any position | Any position | Any position | Not specified | Not specified
Minimum distance to adjacent devices |  | Horizontal |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | Vertical |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Wiring connection (Clamping Capacity) |  | Solid cable without cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) |  | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | Not specified | Not specified
|  | Flexible cable with cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) |  | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | Not specified | Not specified
|  | Solid cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | - | - | - | - | - | - | - |  | - | - | - | - | - | -
|  | Flexible cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | - | - | - | - | - | - | - |  | - | - | - | - | - | -
|  | Tightening torque | IEC60947-1 | Common C_Rly Spec | tightening torque | Published | Published | Nm | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 |  | 0.6…1 | 0.6…1 | 0.6…1 | 0.6…1 | Not specified | Not specified
|  | Cable stripping length |  | Common C_Rly Spec | cable stripping length |  |  | mm | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Duty time |  |  |  | Common C_Rly Spec | duty time |  |  | % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Electromagnetic Compatibility
Immunity |  | Generic immunity standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 |  | IEC61000-6-2 | IEC61000-6-2 | IEC61000-6-2 | IEC61000-6-2 | IEC50082-2 | IEC50082-2
|  | Electrostatic discharge | IEC61000-4-2 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) |  | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV)
|  | Radiated RF & electromagnetic field | IEC61000-4-3 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) |  | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m)
|  | Fast transient / burst | IEC61000-4-4 |  | electromagnetic compatibility | Published |  |  | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) |  | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct)
|  | Surge | IEC61000-4-5 |  | electromagnetic compatibility | Published |  |  | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) |  | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase)
|  | Conducted RF disturbance | IEC61000-4-6 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) |  | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V)
|  | Power frequency magnetic field | IEC61000-4-8 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s)
|  | Voltage dips, short interruption & variations on power line | IEC61000-4-11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | - | - | - | - | - | - | - |  | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us)
|  | 1 MHz oscillation wave | IEC61000-4-18 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV)
|  | DC voltage interruption | IEC61000-4-29 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms
|  | Low frequency harmonics | IEC61000-4-13 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | - | - | - | - | - | - | - |  | Not tested | Not tested | Not tested | Not tested | Not tested | Not tested
|  | Conducted low frequency interference (harmonics) | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W |  | · | · | · | · | ? | ?
Emission |  | Generic emission standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 (Except Radiared RF IEC 61000-6-4 only) | IEC61000-6-3, IEC 61000-6-4 |  | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4
|  | Radiated RF & electromagnetic field (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B | Class B | Class B | Class B | Class B | Class A | Class B |  | Class B | Class B | Class B | Class B | Class B Group1 | Class B Group1
|  | Radiated RF & electromagnetic field (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class A, Group 1 | Class B, Group 1 |  | Class B | Class B | Class B | Class B | Class B Group1 | Class B Group1
|  | Radiated emission from enclosure port | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2
|  | Conducted RF emission on power line (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B | Class B | Class B | Class B | Class B | Class B | Class B |  | Class B | Class B | Class B | Class B | Class B Group1 | Class B Group1
|  | Conducted RF emission on power line (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 |  | Class B | Class B | Class B | Class B | Class B Group1 | Class B Group1
|  | Conducted emission | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2
Electrical Isolation
Degree of pollution |  |  | IEC60664-1 | Common C_Rly Spec | pollution degree | Published | Published |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | Not specified | Not specified
Overvoltage category |  |  | IEC60664-1 | Common C_Rly Spec | overvoltage category | Published | Published |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | III | III | III | III | Not specified | Not specified
Circuit Group | Terminal | Supply |  |  | circuit group | Published |  |  | A1, A2 | A1, A2 | A1, A2 | A1, A2 | A1, A2 | A1, A2 | A1, A2 | A1, A2
|  | Input 1 |  |  | circuit group | Published |  |  | E1, M | E1, M | E1, M | E1, M | E1, M | E1, M | E1, M | -
|  | Input 2 |  |  | circuit group | Published |  |  | E2, M | E2, M | E2, M | E2, M | E2, M | E2, M | E2, M | -
|  | Input 3 |  |  | circuit group | Published |  |  | E3, M | E3, M | E3, M | E3, M | E3, M | E3, M | E3, M | -
|  | Output 1 |  |  | circuit group | Published |  |  | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14
|  | Output 2 |  |  | circuit group | Published |  |  | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 |  | 600 | 600 | 600 | 600 | Not specified | Not specified
| Rated | Supply | [6 empty] | 24…240 AC/DC | 24…240 AC/DC | 24…240 AC/DC | 24…240 AC/DC | 24…240 AC/DC | 24…240 AC/DC | 380…415 AC | 110…240 AC/DC |  | 600 | 600 | 600 | 600 | Not specified | Not specified
| Voltage | Input 1 | [6 empty] | 0.05..0.5 AC/DC [full: 0.05..0.5 AC/DC] | 1..10 AC/DC [full: 1..10 AC/DC] | 18..125 AC/DC [full: 15..150 AC/DC] | 0.05..0.5 AC/DC [full: 0.05..0.5 AC/DC] | 1..10 AC/DC [full: 1..10 AC/DC] | 18..125 AC/DC [full: 15..150 AC/DC] | 18..125 AC/DC [full: 15..150 AC/DC] | - |  | 600 | 600 | 600 | 600 | Not specified | Not specified
| Spec | Input 2 | [6 empty] | 0.3..3 AC/DC [full: 0.3..3 AC/DC] | 5..50 AC/DC [full: 5..50 AC/DC] | 37..250 AC/DC [full: 30..300 AC/DC] | 0.3..3 AC/DC [full: 0.3..3 AC/DC] | 5..50 AC/DC [full: 5..50 AC/DC] | 37..250 AC/DC [full: 30..300 AC/DC] | 37..250 AC/DC [full: 30..300 AC/DC] | -
|  | Input 3 | [6 empty] | 0.5..5 AC/DC [full: 0.5..5 AC/DC] | 10..100 AC/DC [full: 10..100 AC/DC] | 75..440 AC/DC [full: 50..500 AC/DC] | 0.5..5 AC/DC [full: 0.5..5 AC/DC] | 10..100 AC/DC [full: 10..100 AC/DC] | 75..440 AC/DC [full: 50..500 AC/DC] | 75..440 AC/DC [full: 50..500 AC/DC] | -
|  | Output 1 | [6 empty] | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V
|  | Output 2 | [6 empty] | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V
Rated Insulation Voltage |  | Supply | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 400V | 250V
|  | Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 12.5 | 12.5 | 125V | 12.5 | 12.5 | 125V | 125V | -
|  | Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 12.5 | 50 | 250V | 12.5 | 50 | 250V | 250V | -
|  | Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 12.5 | 100 | 500V | 12.5 | 100 | 500V | 500V | -
|  | Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V |  | 4 | 4 | 4 | 4 | Not specified | Not specified
|  | Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 400V | -
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 400V | -
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 500V | 250V | 250V | 500V | 500V | -
|  | Supply / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 400V | 250V
|  | Supply / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 400V | 250V
|  | Output 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V
|  | Input 1 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | -
|  | Input 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | -
|  | Input 2 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | -
|  | Input 2 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | - |  | 2 @ 50Hz for 1 minutes | 2 @ 50Hz for 1 minutes | 2 @ 50Hz for 1 minutes | 2 @ 50Hz for 1 minutes | Not specified | Not specified
|  | Input 3 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 500V | 250V | 250V | 500V | 500V | -
|  | Input 3 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 500V | 250V | 250V | 500V | 500V | -
|  | Input 1 / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | - | - | - | - | -
Rated Impulse Voltage |  | Supply | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 0.8kV, OVC3 | 0.8kV, OVC3 | 2.5kV, OVC3 | 0.8kV, OVC3 | 0.8kV, OVC3 | 2.5kV, OVC3 | 2.5kV, OVC3 | -
|  | Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 0.8kV, OVC3 | 0.8kV, OVC3 | 4kV, OVC3 | 0.8kV, OVC3 | 0.8kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
|  | Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 0.8kV, OVC3 | 1.5kV, OVC3 | 4kV, OVC3 | 0.8kV, OVC3 | 1.5kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
|  | Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | -
|  | Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | -
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
|  | Supply / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Supply / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Output 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
|  | Input 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
|  | Input 2 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
|  | Input 2 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | - |  | > 500MOhm @ -- 500V | > 500MOhm @ -- 500V | > 500MOhm @ -- 500V | > 500MOhm @ -- 500V | Not specified | Not specified
|  | Input 3 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
|  | Input 3 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | -
|  | Input 1 / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | - | - | - | - | -
Dielectric test voltage |  | Supply / Input 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | - |  | Yes | Yes | Yes | Yes | Yes | Yes
|  | Supply / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | - |  | Yes | Yes | Yes | Yes | Yes | Yes
|  | Supply / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | - |  | Yes | Yes | Yes | Yes | Yes | Yes
|  | Supply / Output 1 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Supply / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Output 1 / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | -
|  | Input 1 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | -
|  | Input 2 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | -
|  | Input 2 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | -
|  | Input 3 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | -
|  | Input 3 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | -
|  | Input 1 / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | -
|  | Input 2 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | -
|  | Input 1 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | - | - | - | - | -
Insulation resistance |  | Supply / Input 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Supply / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Supply / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Supply / Output 1 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Output 1 / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Input 1 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Input 2 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Input 2 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Input 3 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Input 3 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | -
|  | Input 1 / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | -
|  | Input 2 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | -
|  | Input 1 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | - | - | - | - | -
Power Supply Characteristics
Rated supply voltage, Us |  |  |  |  | [Us] rated supply voltage | Published | Published | V | ~/-- 24…240 | ~/-- 24…240 | ~/-- 24…240 | ~/-- 24…240 | ~/-- 24…240 | ~/-- 24…240 | ~380…415 | ~/--110…240 |  | ~/-- 24…240 | ~/-- 24…240 | ~/-- 24…240 | ~/-- 24…240 | RM4UA3xMW: ~/-- 24…240 RM4UA3xF: ~110…130 RM4UA3xM: ~220…240 RM4UA3xQ: ~380…415 | RM4UA0xB: ~24 RM4UA0xF: ~110…130 RM4UA0xM: ~220…240
Supply voltage operating range |  |  |  |  | supply voltage limits | Published | Published | V | ~/-- 20.4…264 | ~/-- 20.4…264 | ~/-- 20.4…264 | ~/-- 20.4…264 | ~/-- 20.4…264 | ~/-- 20.4…264 | ~323…456.5 | ~60…280 (F0) ~80…300 (F1) |  | ~/-- 20.4…264 | ~/-- 20.4…264 | 0.85…1.1 Un (~/-- 20.4…264) | ~/-- 20.4…264 | 0.85…1.1 Un | 0.85…1.1 Un
Polarity on d.c. supply |  |  |  |  | polarity |  | Published
Rated frequency |  |  |  |  | supply frequency | Published | Published | Hz | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 |  | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60
Frequency operating range |  |  |  |  | supply frequency | Published | Published | Hz | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 | 45…66 |  | 45…66 | 45…66 | 45…66 | 45…66 | Not specified | Not specified
Maximum power consumption |  |  |  |  | power consumption | Published | Published |  | ~ 3.5VA, -- 0.6W 1.5W | ~ 3.5VA, -- 0.6W 1.5W | ~ 3.5VA, -- 0.6W 1.5W | ~ 3.5VA, -- 0.6W 1.5W | ~ 3.5VA, -- 0.6W 1.5W | ~ 3.5VA, -- 0.6W 1.5W | ~ 10VA ~ 8VA | ~ 3.5VA, -- 1.5W ~ 5VA, -- 2W |  | ~ 3.5VA, -- 0.6W | ~ 3.5VA, -- 0.6W | ~ 3.5VA, -- 0.6W | ~ 3.5VA, -- 0.6W | RM4UA3xMW: ~ 3.3VA, -- 1.2W RM4UA3xF: ~ 3.3VA RM4UA3xM: ~ 3.4VA RM4UA3xQ: ~ 3VA | RM4UA0xB: ~ 2VA RM4UA0xF: ~ 3.3VA RM4UA0xM: ~ 3.5VA
Immunity to micro-breakage |  |  |  |  | immunity to microbreaks | Published | Published | ms | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 |  | 10 | 10 | 10 | 10 | Not specified | Not specified
Supply terminal |  |  |  |  | supply terminal |  |  |  | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1+ - A2- |  | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2
On Load Factor |  |  |  | Common C_Rly Spec | on-load factor |  |  | % | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Release of input voltage |  |  |  |  | release of input voltage |  |  | V | - | - | - | - | - | - | - | -
Input Circuit Characteristics
Monitoring functions |  | Over / undervoltage (windows mode) | [6 empty] | - | - | - | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Selectable threshold |  | - | - | - | - | - | -
|  | Over voltage | [6 empty] | Without memory | Without memory | Without memory | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | - |  | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Without memory | Without memory
|  | Undervoltage | [6 empty] | - | - | - | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | - |  | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Without memory | -
Full Measurement range | [7 empty] | V | ~/-- 0.05…5 | ~/-- 1…100 | ~/-- 15…500 | ~/-- 0.05…5 | ~/-- 1…100 | ~/-- 15…500 | ~/-- 15…500 | ~60…280 (F0) ~60…300 (F1) ~/--80…300 (F1) |  | ~/-- 0.05…5 | ~/-- 1…100 | ~/-- 15…600 | ~/-- 0.05…5 | RM4UA31xx: ~/-- 0.05…5 RM4UA32xx: ~/-- 1…100 RM4UA33xx: ~/-- 30…500 | RM4UA01xx: ~/-- 0.05…5 RM4UA02xx: ~/-- 1…100 RM4UA03xx: ~/-- 30…500
Input Resistance |  | E1-M / B1-C | [5 empty] | kW | 5 | 22 | 150 | 5 | 22 | 150 | 150 | - |  | 5 | 22 | 150 | RM22UA31MW: 5 RM22UA32MW: 22 RM22UA33MW: 150 | RM4UA31xx: 6.6 RM4UA32xx: ~/-- 23 | RM4UA31xx: 6.6 RM4UA32xx: ~/-- 23
|  | E2-M / B2-C | [5 empty] | kW | 30 | 110 | 300 | 30 | 110 | 300 | 300 | - |  | 30 | 110 | 300 | RM22UA31MW: 30 RM22UA32MW: 110 RM22UA33MW: 300 | RM4UA31xx: 43 RM4UA32xx: ~/-- 112 RM4UA33xx: ~/-- 668 | RM4UA01xx: 43 RM4UA02xx: ~/-- 112 RM4UA03xx: ~/-- 668
|  | E3-M / B3-C | [5 empty] | kW | 50 | 220 | 500 | 50 | 220 | 500 | 500 | - |  | 50 | 220 | 600 | RM22UA31MW: 50 RM22UA32MW: 220 RM22UA33MW: 600 | RM4UA31xx: 71 RM4UA32xx: ~/-- 225 RM4UA33xx: ~/-- 1111 | RM4UA01xx: 71 RM4UA02xx: ~/-- 225 RM4UA03xx: ~/-- 1111
|  | A1+ / A2- | [5 empty] | kW | - | - | - | - | - | - | - | Not specified
|  | Built in current transformer | [5 empty] | kW | - | - | - | - | - | - | - | - |  | - | - | - | - | - | -
Sub measurement range |  | E1-M / B1-C | [5 empty] | V | ~/-- 0.05…0.5 | ~/-- 1…10 | ~/-- 15…150 | ~/-- 0.05…0.5 | ~/-- 1…10 | ~/-- 15…150 | ~/-- 15…150 | - |  | ~/-- 0.05…0.5 | ~/-- 1…10 | ~/-- 15…150 | RM22UA31MW: ~/-- 0.05…0.5 RM22UA32MW: ~/-- 1…10 RM22UA33MW: ~/-- 15…150 | RM4UA31xx: ~/-- 0.05…0.5 RM4UA32xx: ~/-- 1…10 | RM4UA01xx: ~/-- 0.05…0.5 RM4UA02xx: ~/-- 1…10
|  | E2-M / B2-C | [5 empty] | V | ~/-- 0.3…3 | ~/-- 5…50 | ~/-- 30…300 | ~/-- 0.3…3 | ~/-- 5…50 | ~/-- 30…300 | ~/-- 30…300 | - |  | ~/-- 0.3…3 | ~/-- 5…50 | ~/-- 30…300 | RM22UA31MW: ~/-- 0.5…3 RM22UA32MW: ~/-- 5…50 RM22UA33MW: ~/-- 30…300 | RM4UA31xx: ~/-- 0.3…3 RM4UA32xx: ~/-- 5…50 RM4UA33xx: ~/-- 30…300 | RM4UA01xx: ~/-- 0.3…3 RM4UA02xx: ~/-- 5…50 RM4UA03xx: ~/-- 30…300
|  | E3-M / B3-C | [5 empty] | V | ~/-- 0.5…5 | ~/-- 10…100 | ~/-- 50…500 | ~/-- 0.5…5 | ~/-- 10…100 | ~/-- 50…500 | ~/-- 50…500 | - |  | ~/-- 0.5…5 | ~/-- 10…100 | ~/-- 60…600 | RM22UA31MW: ~/-- 0.5…5 RM22UA32MW: ~/-- 10…100 RM22UA33MW: ~/-- 60…600 | RM4UA31xx: ~/-- 0.5…5 RM4UA32xx: ~/-- 10…100 RM4UA33xx: ~/-- 50…500 | RM4UA01xx: ~/-- 0.5…5 RM4UA02xx: ~/-- 10…100 RM4UA03xx: ~/-- 50…500
|  | A1+ / A2- | [5 empty] | V | - | - | - | - | - | - | - | -
|  | Built in current transformer | [6 empty] | - | - | - | - | - | - | - | - |  | - | - | - | - | - | -
Threshold |  | E1-M / B1-C | [5 empty] | V | Adjustable 10%...100% of 0.5V | Adjustable 10%...100% of 10V | Adjustable 10%...100% of 150V | Adjustable 10%...100% of 0.5V | Adjustable 10%...100% of 10V | Adjustable 10%...100% of 150V | Adjustable 10%...100% of 150V | - |  | Adjustable 10%...100% of 0.5V | Adjustable 10%...100% of 0.5V | Adjustable 10%...100% | Adjustable 10%...100% of full range | - | -
|  | E2-M / B2-C | [5 empty] | V | Adjustable 10%...100% of 3V | Adjustable 10%...100% of 50V | Adjustable 10%...100% of 300V | Adjustable 10%...100% of 3V | Adjustable 10%...100% of 50V | Adjustable 10%...100% of 300V | Adjustable 10%...100% of 300V | - |  | Adjustable 10%...100% of 3V | Adjustable 10%...100% of 3V | Adjustable 10%...100% | Adjustable 10%...100% of full range | Adjustable 10%...100% | Adjustable 10%...100%
|  | E3-M / B3-C | [5 empty] | V | Adjustable 10%...100% of 5V | Adjustable 10%...100% of 100V | Adjustable 10%...100% of 500V | Adjustable 10%...100% of 5V | Adjustable 10%...100% of 100V | Adjustable 10%...100% of 500V | Adjustable 10%...100% of 500V | - |  | Adjustable 10%...100% of 5V | Adjustable 10%...100% of 5V | Adjustable 10%...100% | Adjustable 10%...100% of full range | Adjustable 10%...100% | Adjustable 10%...100%
|  | A1+ / A2- | [5 empty] | V | - | - | - | - | - | - | - | Adjustable <U : 80…300 Adjustable >U : 80…300
|  | Built in current transformer | [6 empty] | - | - | - | - | - | - | - | - |  | - | - | - | - | - | -
Hysteresis |  | E1-M / B1-C | [5 empty] | V | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | - |  | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...30% of threshold setting | Adjustable 5%...30% of threshold setting
|  | E2-M / B2-C | [5 empty] | V | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | - |  | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...30% of threshold setting | Adjustable 5%...30% of threshold setting
|  | E3-M / B3-C | [5 empty] | V | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overvoltage or Undervoltage: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | - |  | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...30% of threshold setting | Adjustable 5%...30% of threshold setting
|  | A1+ / A2- | [5 empty] | V | - | - | - | - | - | - | - | Fixed 3% of threshold setting
|  | Built in current transformer | [6 empty] | - | - | - | - | - | - | - | - |  | - | - | - | - | - | -
Measurement mode | [8 empty] | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down |  | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down | Resistive Voltage Step Down
Connection terminals | [8 empty] | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | A1+ / A2- |  | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | B1-C, B2-C, B3-C | B1-C, B2-C, B3-C
Rated frequency | [7 empty] | Hz | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 |  | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60
Frequency operating range | [7 empty] | Hz | 36…77 | 36…77 | 36…77 | 36…77 | 36…77 | 36…77 | 36…77 | 45…66 |  | 36…77 | 36…77 | 36…77 | 36…77 | Not specified | Not specified
Setting accuracy | [8 empty] | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value |  | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 5% of full scale value | +/- 5% of full scale value
Repeat accuracy (constant parameters) | [8 empty] | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% |  | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% | Not specified | Not specified
Measurement error with supply voltage variation | [7 empty] | %/V | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range |  | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 0.5% over whole range | < 0.5% over whole range
Measurement error with temperature variation | [7 empty] | %/oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.2% / oC |  | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.06% / oC | 0.06% / oC
Maximum measuring cycles | [7 empty] | ms | 30 100 | 30 100 | 30 100 | 30 100 | 30 100 | 30 100 | 30 100 | 250 |  | 30 | 30 | 30 | 30 | 80 | 80
Measurement method | [8 empty] | True RMS | True RMS | True RMS | True RMS | True RMS | True RMS | True RMS | True RMS |  | True RMS | True RMS | True RMS | True RMS | Voltage Peak Detection | Voltage Peak Detection
Output Circuit Characteristics
Type of output |  |  |  |  | output type | Published | Published |  | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts |  | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 1 x C/O relay contacts
Output terminal |  |  |  |  | output terminal |  |  |  | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 |  | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 15-16-18, 25-26-28 | 15-16-18
Operation principle |  | R1 (11-12-14) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault | Energized on fault
|  | R2 (21-22-24) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free
Contact material |  |  |  | Common C_Rly Spec | contacts material | Published | Published |  | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free | Cadmium free |  | Cadmium-free | Cadmium-free | Cadmium-free | Cadmium-free | Not specified | Not specified
Mechanical durability |  |  | IEC61810-1 | Common C_Rly Spec | mechanical durability | Published | Published | Cyc | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles |  | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | Not specified | Not specified
Electrical durability |  | AC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles |  | 1 x 105 switching cycles | 1 x 105 switching cycles | 1 x 105 switching cycles | 1 x 105 switching cycles | Not specified | Not specified
|  | DC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles
|  | AC-15 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles
|  | DC-13 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles
Rated capacity |  | Rated switching voltage | IEC61810-1 | Common C_Rly Spec | [Ue] rated operational voltage | Published |  | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V
|  | Rated switching current | IEC61810-1 | Common C_Rly Spec | [Ie] rated operational current | Published | Published | A | 8A | 8A | 8A | 8A | 8A | 8A | 8A | 8A
Maximum switching capacity |  | Maximum switching voltage |  | Common C_Rly Spec | maximum switching capacity | Published | Published | V | 250V | 250V | 250V | 250V | 250V | 250V | 250V | 250V |  | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250
|  | Maximum switching current |  | Common C_Rly Spec | maximum switching capacity | Published | Published | A | 8A | 8A | 8A | 8A | 8A | 8A | 8A | 8A |  | 5 | 5 | 5 | ~ 8 | 8 | 8
|  | Maximum switching capacity |  | Common C_Rly Spec | maximum switching capacity | Published | Published | VA | - | - | - | - | - | - | - | - |  | 1250 | 1250 | 1250 | 2000 | 2000VA | 2000VA
Minimum switching capacity |  | Minimum switching voltage | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | V | - | - | - | - | - | - | - | - |  | 5 | 5 | 5 | 5 | Not specified | Not specified
|  | Minimum switching current | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | mA | - | - | - | - | - | - | - | - |  | 10 | 10 | 10 | 10 | Not specified | Not specified
|  | Minimum switching capacity | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published | Published | mW | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 |  | 50 | 50 | 50 | 50 | Not specified | Not specified
Maximum voltage drop at terminals |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum voltage drop |  |  | V | - | - | - | - | - | - | - | - |  | - | - | - | - | - | -
Leakage current |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum leakage current |  |  | mA | - | - | - | - | - | - | - | - |  | - | - | - | - | - | -
Thermal Current |  |  | IEC60947-5-1 | Common C_Rly Spec | thermal current |  |  | A | 8A | 8A | 8A | 8A | 8A | 8A | 8A | 8A
Short circuit protection |  | Relay Output by external fuse | IEC60947-5-1 | Common C_Rly Spec | short circuit protection |  |  | gG | 8A | 8A | 8A | 8A | 8A | 8A | 8A | 8A
|  | Solid State Output by external fuse | IEC62314 | Common C_Rly Spec | short circuit protection |  |  | gG | - | - | - | - | - | - | - | -
Time Delay Characteristics
Time delay functions |  | "OFF" delay |  |  | time delay type | Published |  |  | - | - | - | Yes | Yes | Yes | Yes | Yes |  | · | · | · | · | · | -
|  | "ON" delay |  |  | time delay type | Published |  |  | - | - | - | - | - | - | - | Yes |  | - | - | - | - | - | -
|  | Inhibition |  |  | time delay type | Published |  |  | - | - | - | - | - | - | - | - |  | - | - | - | - | - | -
Timing range |  | "OFF" delay |  |  | time delay range | Published | Published | s | - | - | - | Adjustable 0.1…30 | Adjustable 0.1…30 | Adjustable 0.1…30 | Adjustable 0.1…30 | Adjustable 0.1…30 |  | Adjustable 0.3…30 | Adjustable 0.3…30 | Adjustable 0.3…30 | Adjustable 0.3…30 | Adjustable (0.5…1),(0.15…3),(0.5…10),(1.5…30) | -
|  | "ON" delay |  |  | time delay range | Published |  | s | - | - | - | - | - | - | - | Adjustable 0.1…30 |  | - | - | - | - | - | -
|  | Inhibition |  |  | time delay range | Published | Published | s | - | - | - | - | - | - | - | - |  | - | - | - | - | - | -
Response time |  | on crossing the threshold |  |  | response time | Published | Published | ms | Not specified =< 300ms | Not specified =< 300ms | Not specified =< 300ms | Not specified =< 300ms | Not specified =< 300ms | Not specified =< 300ms | Not specified =< 300ms | Not specified =< 300ms |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
Time delay of pick-up |  |  |  |  | power on delay | Published | Published | ms | =< 600 | =< 600 | =< 600 | =< 600 | =< 600 | =< 600 | =< 600 | =< 600 |  | =< 600 | =< 600 | =< 600 | =< 600 | Not specified | Not specified
Reset time |  | through Un power reset |  |  | reset time | Published | Published | ms | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage |  | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage | Not specified | Not specified
|  | through front panel reset |  | Reserved for other products | reset time | Published
|  | through input control reset |  | Reserved for other products | reset time | Published
Setting accuracy |  |  |  | Common C_Rly Spec | setting accuracy of time delay | Published | Published | % | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales |  | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | -
Repeat accuracy (constant parameters) |  |  |  | Common C_Rly Spec | repeat accuracy of time delay | Published |  | % | +/- 2% | +/- 2% | +/- 2% | +/- 2% | +/- 2% | +/- 2% | +/- 2% | +/- 2% |  | +/- 2% | +/- 2% | +/- 2% | +/- 2% | Not specified | Not specified
Timing error with supply voltage variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/V | < 1 | < 1 | < 1 | < 1 | < 1 | < 1 | < 1 | < 1 |  | Not specified | Not specified | Not specified | Not specified | < 0.5% over whole range | -
Timing error with temperature variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/oC | < 0.05 | < 0.05 | < 0.05 | < 0.05 | < 0.05 | < 0.05 | < 0.05 | < 0.05 |  | Not specified | Not specified | Not specified | Not specified | 0.07% / oC | -
LED Indication
status LED |  |  |  |  | status LED |  |  |  | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber)
local signalling |  | Power supply availability |  |  | local signalling |  |  |  | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON
|  | Power supply not availability |  |  | local signalling |  |  |  | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF
|  | Timing in-progress |  |  | local signalling |  |  |  | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz
|  | Output is energized |  |  | local signalling |  |  |  | R - ON | R - ON | R - ON | R - ON | R - ON | R - ON | R - ON | R - ON
|  | Output is de-energized |  |  | local signalling |  |  |  | R - OFF | R - OFF | R - OFF | R - OFF | R - OFF | R - OFF | R - OFF | R - OFF
|  | Range Setting Changes |  |  | local signalling |  |  |  | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
Special Features
True RMS | [8 empty] | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Backlight Indicator | [8 empty] | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product
Diagnostic Button |  |  |  |  | diagnostic button | Published |  |  | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated
Pre-Alarm Output | [8 empty] | - | - | - | - | - | - | - | -
Output | [8 empty] | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
Reliability Data
Reliability Data |  | MTTF |  |  | safety reliability data | Published |  |  | 2,700,000 hours | 2,700,000 hours | 2,700,000 hours | 2,700,000 hours | 2,700,000 hours | 2,700,000 hours | 2,700,000 hours | 3,800,000 hours
|  | B10 |  |  | safety reliability data | Published |  |  | 290,000 hours | 290,000 hours | 290,000 hours | 290,000 hours | 290,000 hours | 290,000 hours | 290,000 hours | 400,000 hours
|  | MTTFd | [6 empty] | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product)
|  | B10d | [6 empty] | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product)
Drawing / Diagram
Note on D18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.1
Note on A42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Typical Product Operation Rate: 100% - product mostly will be powered and in operation in the actual application 50% - product is powered and in operation in the actual application @ ~50% of the time
Note on A44: Protection : Normal performance within the specification limits Command and control : Normal performance within the specification limits Measurement : Temporary degradation during test, with self-recovery at the end of the test. No loss of stored data Integral human-machine interface and visual alarms: Temporary degradation or loss of function during test, with self-recovery at the end of the test. No loss of stored data Data communication : Possible bit error rate increase but no loss of transmitted data
Note on A156: Measured with Yokogawa power meter and 3P4W connection
Note on A160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The minimum level of supply voltage that causes the product out-of power to operate. This must be a value other than 0V or total cut-off
Note on D226: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-4-1 GB14048.4
Note on D227: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-4-1 GB14048.4
Note on D228: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-5-1 GB14048.5
Note on D229: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-5-1 GB14048.5
Note on D240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.5
Note on D241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.5
Note on A287: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Product Developed Before 2019: follow UTE C80-810 Product Developed After 2019 and require recalculation of MTBF: follow SN29500

## 1P Current Control Spec
|  | Brand --> |  |  | brown text - widely used every where |  |  |  | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | OLD SE | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | SCHNEIDER ELECTRIC | CROUZET
|  | Base Design Reference --> |  |  | black text - product nature specific |  |  |  | HW & FW adapted from RM35JA31MW | HW & FW adapted from RM35JA31MW | HW & FW adapted from RM35JA32MW | HW & FW adapted from RM35JA32MW | (RM4 + Crouzet)
Firmware Type -->
Main Parameters | Category | Sub Parameters | Conforming to | Remark | Standardized Datasheet Param | Selected for Publication | Old Datasheet | Unit | RM22JA21MR | RM22JA31MR | RM35JA32MR | RM35JA32MT | Competitor Spec Reference | RM35JA31MW | RM35JA32MW | RM4JA3 | RM4JA01 | RM17JC00MW | RM22JA31MW (Catch Up) | 84893852 (Catch Up) | 84893852 (Autelec Distribution)
Standard
Product standard |  |  |  | Common C_Rly Spec | standards | Published | Published |  | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 | EN/IEC 60255-1/60255-26/60255-27; EN/IEC 61000-6-1 to 61000-6-4; UL 508; CSA C22.2 No. 14, GB/T14048.5 |  | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | EN60255-6, IEC60255-6 | Not specified
Product certifications |  |  |  | Common C_Rly Spec | product certifications | Published | Published |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS |  | UL, CSA, GL, C-Tick, GOST | UL, CSA, GL, C-Tick, GOST, CCC | UL, CSA, GL, C-Tick, GOST, CCC | UL, CSA, GL, C-Tick, GOST, CCC | UL, CSA, GL, C-Tick, GOST, CCC | UL, CSA, GL, C-Tick, GOST, CCC | UL, CSA, GL, C-Tick, GOST, CCC | Not specified
Marking |  |  |  | Common C_Rly Spec | marking | Published |  |  | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS | UL, CSA, DNVGL, RCM, EAC, CCC, CE, China ROHS |  | UL, CSA, GL, C-Tick, GOST, CE | UL, CSA, GL, C-Tick, GOST, CE, CCC | UL, CSA, GL, C-Tick, GOST, CE, CCC | UL, CSA, GL, C-Tick, GOST, CE, CCC | UL, CSA, GL, C-Tick, GOST, CE, CCC | UL, CSA, GL, C-Tick, GOST, CE, CCC | UL, CSA, GL, C-Tick, GOST, CE, CCC | CE
Low voltage directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/35/EU | 2014/35/EU | 2014/35/EU | 2014/35/EU |  | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC |  |  | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | No 73/23/EEC + 93/68/EEC | Not specified
EMC directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2014/30/EU | 2014/30/EU | 2014/30/EU | 2014/30/EU |  | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC |  |  | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | No 89/336/EEC + 92/31/EEC + 93/68/EEC | Not specified
ROHS directive |  |  |  | Common C_Rly Spec | directives | Published |  |  | 2011/65/EU | 2011/65/EU | 2011/65/EU | 2011/65/EU |  | 2002/95/EC | 2002/95/EC |  |  | 2002/95/EC | 2002/95/EC | 2002/95/EC | Not specified
Environment Characteristics
Environmental Condition |  | Climatic category | IEC60721-3-3 | Common C_Rly Spec |  |  |  |  | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) | 3K3 (No Condensation & No Formation of Ice) |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | Environmental category | Germanisher Lloyd | Common C_Rly Spec |  |  |  |  | Class C | Class C | Class C | Class C
Ambient air temperature around the device |  | Storage |  | Common C_Rly Spec | ambient air temperature for storage | Published | Published | oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC | -40oC..+70oC |  | -40…+70 | -40…+70 | Not specified | Not specified | -40…+70 | -40…+70 | -40…+70 | Not specified
|  | Operation |  |  | ambient air temperature for operation | Published | Published | oC | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) | -20oC..+60oC @50Hz or DC -20oC..+50oC @60Hz (F0) -20oC..+70oC (F1) |  | -20…+50 | -20…+50 | Not specified | Not specified | -20…+50 | -20…+50 | -20…+50 | Not specified
Relative humidity |  | Damp heat | IEC60068-2-30 | Common C_Rly Spec | relative humidity | Published | Published |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% |  | 2 cycles 24h ;+25°C +55°C 95%HR | 2 cycles 24h ;+25°C +55°C 95%HR | Not specified | Not specified | 2 cycles 24h ;+25°C +55°C 95%HR | 2 cycles 24h ;+25°C +55°C 95%HR | 2 cycles 24h ;+25°C +55°C 95%HR | Not specified
|  | Cyclic Damp Heat Test | IEC60947-5-1 | Common C_Rly Spec |  |  |  |  | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97% | 6 cycles 24h ; +25°C +55°C ; RH: 93%..97%
Vibration resistance |  |  | IEC60068-2-6 | Common C_Rly Spec | vibration resistance | Published | Published |  | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) | 0.075 mm (f = 10...58.1 Hz), 1 gn (f = 58.1...150Hz) (Non-Operating) 0.035 mm (f = 10...60.1 Hz), 0.5 gn (f = 60.1...150Hz) (Operating) |  | 0.035mm from 10Hz…150Hz | 0.035mm from 10Hz…150Hz | Not specified | Not specified | 0.035mm from 10Hz…150Hz | 0.035mm from 10Hz…150Hz | 0.035mm from 10Hz…150Hz | Not specified
Shock resistance |  |  | IEC60068-2-27 | Common C_Rly Spec | shock resistance | Published | Published |  | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) | 15gn - 11ms ; 3 X 6 axis (Non-Operating) 5gn - 11ms ; 3 X 6 axis (Operating) |  | 5 gn | 5 gn | Not specified | Not specified | 5 gn | 5 gn | 5 gn | Not specified
Bump resistance |  |  | IEC60068-2-29 | Common C_Rly Spec | bump resistance |  |  |  | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating) | 10gn - 16ms ; 1000 X 6 axis (Non-Operating)
Seismic resistance |  |  | IEC60068-3-3 | Common C_Rly Spec | seismic resistance |  |  |  | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz | Horizontal (x,z): ±3.5mm from 1Hz…9Hz 1g from 9Hz..35Hz Vertical (y): ±1.5mm from 1Hz…9Hz 0.5g from 9Hz..35Hz
IP degree of protection |  | Terminal Block | IEC60529 |  | IP degree of protection | Published | Published |  | IP20 | IP20 | IP20 | IP20 |  | IP20 | IP20 | Not specified | Not specified | IP20 | IP20 | IP20 | Not specified
|  | Housing | IEC60529 |  | IP degree of protection | Published | Published |  | IP40 | IP40 | IP30 | IP30 |  | IP30 | IP30 | Not specified | Not specified | IP30 | IP30 | IP30 | Not specified
|  | Front Panel | IEC60529 |  | IP degree of protection |  |  |  | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover) | IP50 (With Transparent Cover)
Installation Data
Dimension (nominal) |  | Width |  |  | width | Published |  | mm | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 | 22.5 x 90 x 73 |  | 35 x 90 x 72 | 35 x 90 x 72 | RM4JA31xx: 22.5 x 78 x 80 RM4JA32xx: 45 x 78 x 80 | 22.5 x 78 x 80 | 17.5 x 90 x 72 | 22.5 x ? x ? | 22.5 x ? x ? | 22.5 x 78.5 x 100
|  | Height |  |  | height | Published |  | mm
|  | Depth |  |  | depth | Published |  | mm
Weight (without packaging) |  |  |  |  | net weight | Published |  | g | 110 | 110 | 120 | 120 |  | 130 | 130 | Not specified | Not specified | 110 | ? | ? | Not specified
Mounting |  | Without socket | IEC/EN 60715 |  | mounting support | Published | Published |  | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail | On 35 mm DIN rail |  | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | On Top Hat 35mm DIN rail | Not specified
|  | With socket | IEC/EN 60715 |  | mounting support |  |  |  | - | - | - | - |  | - | - | - | - | - | - | - | -
Mounting position |  | In relation to normal vertical mounting plane |  | Common C_Rly Spec | mounting position | Published | Published |  | Any position | Any position | Any position | Any position |  | Any position | Any position | Not specified | Not specified | Any position | Any position | Any position | Not specified
Minimum distance to adjacent devices |  | Horizontal |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | Not specified | Not specified | Not specified | Not specified |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
|  | Vertical |  | Common C_Rly Spec | Minimum distance to adjacent devices |  |  | mm | Not specified | Not specified | Not specified | Not specified |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Wiring connection (Clamping Capacity) |  | Solid cable without cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) | 1 conductor: 0.5…3.3 (AWG 20…AWG 12) 2 conductors: 0.5…2.5 (AWG 20…AWG 14) |  | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | Not specified | Not specified | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | 1 conductor:0.5…4 (AWG20…AWG11) 2 conductor:0.5…2.5 (AWG20…AWG14) | Not specified
|  | Flexible cable with cable end (screw terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals | Published | Published | mm2 | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) | 1 conductor: 0.2…2.5 (AWG 24…AWG 14) 2 conductors: 0.2…1.5 (AWG 24…AWG 16) |  | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | Not specified | Not specified | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | 1 conductor:0.2…2.5 (AWG24…AWG12) 2 conductor:0.2…1.5 (AWG24…AWG16) | Not specified
|  | Solid cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | - | - | - |  | - | - | - | - | - | - | - | -
|  | Flexible cable (spring terminal) | IEC60947-1 | Common C_Rly Spec | connections - terminals |  |  | mm2 | - | - | - | - |  | - | - | - | - | - | - | - | -
|  | Tightening torque | IEC60947-1 | Common C_Rly Spec | tightening torque | Published | Published | Nm | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 | 0.6…1.0 |  | 0.6…1 | 0.6…1 | Not specified | Not specified | 0.6…1 | 0.6…1 | 0.6…1 | Not specified
|  | Cable stripping length |  | Common C_Rly Spec | cable stripping length |  |  | mm | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) | 6 (Screw Terminal) 8 (Spring Terminal) |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Duty time |  |  |  | Common C_Rly Spec | duty time |  |  | % | 100% | 100% | 100% | 100% |  | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified | Not specified
Electromagnetic Compatibility
Immunity |  | Generic immunity standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 | IEC61000-6-1, IEC 61000-6-2 |  | IEC61000-6-2 | IEC61000-6-2 | IEC50082-2 | IEC50082-2 | IEC61000-6-2 | IEC61000-6-2 | IEC61000-6-2 | Not specified
|  | Electrostatic discharge | IEC61000-4-2 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) | Level III (Contact : 6kV / Air : 8kV) |  | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Level 3 (6kV / 8kV) | Not specified
|  | Radiated RF & electromagnetic field | IEC61000-4-3 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) | Level I (10V/m: 2.0GHz to 2.7GHz) Level II (10V/m: 1.4 GHz to 2.0GHz) Level III (10V/m : 80MHz to 1GHz) |  | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Level 3 (10V/m) | Not specified
|  | Fast transient / burst | IEC61000-4-4 |  | electromagnetic compatibility | Published |  |  | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) | Level III (F0) (Supply: 2kV, 5kHz/100kHz) (I/O: 1kV, 5kHz/100kHz) Level IV (F1) (Supply: 4kV, 5kHz/100kHz) (I/O: 2kV, 5kHz/100kHz) |  | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Level 3 (2kV coupling / 4kV direct) | Not specified
|  | Surge | IEC61000-4-5 |  | electromagnetic compatibility | Published |  |  | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) | Level III (F0) (Supply:CM: 2kV, DM: 1KV) (I/O:CM: 0.5kV, DM: 0.5KV) Level IV (F1) (Supply:CM: 4kV, DM: 2KV) (I/O:CM: 1kV, DM: 1KV) |  | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Level 3 (1kV phase-phase) | Not specified
|  | Conducted RF disturbance | IEC61000-4-6 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) | Level III (10Vrms : 0.15MHz to 80MHz) (10Vrms : 80MHz to 230MHz) |  | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Level 3 (10V) | Not specified
|  | Power frequency magnetic field | IEC61000-4-8 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s) | Level IV (30A/m : continous) (300A/m : 3s)
|  | Voltage dips, short interruption & variations on power line | IEC61000-4-11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | - | - | - |  | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Class 3 (0%, 40%, 70%, 80% of Us) | Not specified
|  | 1 MHz oscillation wave | IEC61000-4-18 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV) | Level III (Supply:CM: 2.5kV, DM: 1KV) (I/O:CM: 2.5kV, DM: 1KV)
|  | DC voltage interruption | IEC61000-4-29 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms | 0 % residual voltage, 5ms 0 % residual voltage, 10ms 0 % residual voltage, 20ms 0 % residual voltage, 50ms 0 % residual voltage, 100ms 0 % residual voltage, 200ms
|  | Low frequency harmonics | IEC61000-4-13 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | - | - | - | - |  | Not tested | Not tested | Not tested | Not tested | Not tested | Not tested | Not tested | Not specified
|  | Conducted low frequency interference (harmonics) | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W | DC Supply : 50 Hz to 10 kHz, 3Vrms (Max 2W) AC Supply : 1st…200th harmonics, Max 2W |  | · | · | ? | ? | · | · | · | Not specified
Emission |  | Generic emission standard |  | Common C_Rly Spec | electromagnetic compatibility | Published | Published |  | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 | IEC61000-6-3, IEC 61000-6-4 |  | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | IEC61000-6-3, IEC61000-6-4 | Not specified
|  | Radiated RF & electromagnetic field (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B | Class B | Class B |  | Class B | Class B | Class B Group1 | Class B Group1 | Class B | Class B | Class B | Not specified
|  | Radiated RF & electromagnetic field (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 |  | Class B | Class B | Class B Group1 | Class B Group1 | Class B | Class B | Class B | Not specified
|  | Radiated emission from enclosure port | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | Not specified
|  | Conducted RF emission on power line (IT equiment) | EN55022 / CISPR22 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B | Class B | Class B | Class B |  | Class B | Class B | Class B Group1 | Class B Group1 | Class B | Class B | Class B | Not specified
|  | Conducted RF emission on power line (Medical equiment) | EN55011 / CISPR11 | Common C_Rly Spec | electromagnetic compatibility | Published |  |  | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 | Class B, Group 1 |  | Class B | Class B | Class B Group1 | Class B Group1 | Class B | Class B | Class B | Not specified
|  | Conducted emission | Germanisher Lloyd | Common C_Rly Spec | electromagnetic compatibility |  |  |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 |  | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | EMC 2 | Not specified
Electrical Isolation
Degree of pollution |  |  | IEC60664-1 | Common C_Rly Spec | pollution degree | Published | Published |  | 3 | 3 | 3 | 3 |  | 3 | 3 | Not specified | Not specified | 3 | 3 | 3 | Not specified
Overvoltage category |  |  | IEC60664-1 | Common C_Rly Spec | overvoltage category | Published | Published |  | 3 | 3 | 3 | 3 |  | III | III | Not specified | Not specified | III | III | III | Not specified
Circuit Group | Terminal | Supply |  |  | circuit group | Published |  |  | A1, A2 | A1, A2 | A1, A2 | A1, A2
|  | Input 1 |  |  | circuit group | Published |  |  | E1, M | E1, M | E1, M | E1, M
|  | Input 2 |  |  | circuit group | Published |  |  | E2, M | E2, M | E2, M | E2, M
|  | Input 3 |  |  | circuit group | Published |  |  | E3, M | E3, M | E3, M | E3, M
|  | Output 1 |  |  | circuit group | Published |  |  | 11,12,14 | 11,12,14 | 11,12,14 | 11,12,14
|  | Output 2 |  |  | circuit group | Published |  |  | 21,22,24 | 21,22,24 | 21,22,24 | 21,22,24 |  | 600 | 600 | Not specified | Not specified | 600 | 600 | 600 | Not specified
| Rated | Supply | [6 empty] | 24…240 AC/DC | 24…240 AC/DC | 24…240 AC/DC | 380…415 AC |  | 600 | 600 | Not specified | Not specified | 600 | 600 | 600 | Not specified
| Voltage | Input 1 | [6 empty] | 4..40mA AC/DC [full: 4..40mA AC/DC ] | 4..40mA AC/DC [full: 4..40mA AC/DC ] | 0.15..1.5A AC/DC [full: 0.18..1.2A AC/DC] | 0.15..1.5A AC/DC [full: 0.18..1.2A AC/DC] |  | 600 | 600 | Not specified | Not specified | 600 | 600 | 600 | Not specified
| Spec | Input 2 | [6 empty] | 20..200mA AC/DC [full: 20..200mA AC/DC] | 20..200mA AC/DC [full: 20..200mA AC/DC] | 0.5..5A AC/DC [full: 6..4A AC/DC] | 0.5..5A AC/DC [full: 6..4A AC/DC]
|  | Input 3 | [6 empty] | 100..1000mA AC/DC [full: 100..1000mA AC/DC] | 100..1000mA AC/DC [full: 100..1000mA AC/DC] | 1.8..12A AC/DC [full: 1.5..15A AC/DC] | 1.8..12A AC/DC [full: 1.5..15A AC/DC]
|  | Output 1 | [6 empty] | 250V | 250V | 250V | 250V
|  | Output 2 | [6 empty] | 250V | 250V | 250V | 250V
Rated Insulation Voltage |  | Supply | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 400V
|  | Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 10V | 10V | 10V | 10V
|  | Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 10V | 10V | 10V | 10V
|  | Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 10V | 10V | 10V | 10V
|  | Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V |  | 4 | 4 | Not specified | Not specified | 4 | 4 | 4 | Not specified
|  | Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 400V
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 400V
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V
|  | Supply / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V | 250V | 400V
|  | Supply / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V | 250V | 400V
|  | Output 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage | Published |  | V | 250V | 250V | 250V | 250V
|  | Input 1 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V
|  | Input 1 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V
|  | Input 2 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V
|  | Input 2 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V |  | 2 @ 50Hz for 1 minutes | 2 @ 50Hz for 1 minutes | Not specified | Not specified | 2 @ 50Hz for 1 minutes | 2 @ 50Hz for 1 minutes | 2 @ 50Hz for 1 minutes | Not specified
|  | Input 3 / Output 1 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V
|  | Input 3 / Output 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | 250V | 250V | 250V | 250V
|  | Input 1 / Input 2 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Ui] rated insulation voltage |  |  | V | - | - | - | -
Rated Impulse Voltage |  | Supply | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
| Galvanic | Supply / Input 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
| Isolated | Supply / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
| Circuit | Supply / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Supply / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Supply / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Output 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage | Published |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 2 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 2 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 |  | > 500MOhm @ -- 500V | > 500MOhm @ -- 500V | Not specified | Not specified | > 500MOhm @ -- 500V | > 500MOhm @ -- 500V | > 500MOhm @ -- 500V | Not specified
|  | Input 3 / Output 1 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 3 / Output 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3 | 4kV, OVC3
|  | Input 1 / Input 2 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 2 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
|  | Input 1 / Input 3 | IEC60664-1 |  | [Uimp] rated impulse withstand voltage |  |  | kV | - | - | - | -
Dielectric test voltage |  | Supply / Input 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Not specified
|  | Supply / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Not specified
|  | Supply / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Not specified
|  | Supply / Output 1 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Supply / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Output 1 / Output 2 | IEC60255-27 |  | dielectric strength | Published |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 2 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 2 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 3 / Output 1 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 3 / Output 2 | IEC60255-27 |  | dielectric strength |  |  | kV | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min | 2.0kV, 50/60Hz for 1 min
|  | Input 1 / Input 2 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
|  | Input 2 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
|  | Input 1 / Input 3 | IEC60255-27 |  | dielectric strength |  |  | kV | - | - | - | -
Insulation resistance |  | Supply / Input 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Output 1 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Supply / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Output 1 / Output 2 | IEC60255-27 |  | insulation resistance | Published |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 2 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 2 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 3 / Output 1 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 3 / Output 2 | IEC60255-27 |  | insulation resistance |  |  |  | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC | >100 MOhm at 500 V DC
|  | Input 1 / Input 2 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Input 2 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
|  | Input 1 / Input 3 | IEC60255-27 |  | insulation resistance |  |  |  | - | - | - | -
Power Supply Characteristics
Rated supply voltage, Us |  |  |  |  | [Us] rated supply voltage | Published | Published | V | ~/-- 24…240 | ~/-- 24…240 | ~/-- 24…240 | ~380…415 |  | ~/-- 24…240 | ~/-- 24…240 | RM4JA3xMW: ~/-- 24…240 RM4JA3xF: ~110…130 RM4JA3xM: ~220…240 RM4JA3xQ: ~380…415 | RM4JA01B: ~ 24 RM4JA01F: ~110…130 RM4JA01M: ~220…240 | ~/-- 24…240 | ~/-- 24…240 | ~/-- 24…240 | ~ 24…240
Supply voltage operating range |  |  |  |  | supply voltage limits | Published | Published | V | ~/-- 20.4…264 | ~/-- 20.4…264 | ~/-- 20.4…264 | ~323…456.5 |  | ~/-- 20.4…264 | ~/-- 20.4…264 | 0.85…1.1 Un | 0.85…1.1 Un | ~/-- 20.4…264 | ~/-- 20.4…264 | ~/-- 20.4…264 | Not specified
Polarity on d.c. supply |  |  |  |  | polarity |  | Published
Rated frequency |  |  |  |  | supply frequency | Published | Published | Hz | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 |  | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | Not specified
Frequency operating range |  |  |  |  | supply frequency | Published | Published | Hz | 45…66 | 45…66 | 45…66 | 45…66 |  | 45…66 | 45…66 | Not specified | Not specified | 45…66 | 45…66 | 45…66 | Not specified
Maximum power consumption |  |  |  |  | power consumption | Published | Published |  | ~ 3.5VA, -- 0.6W 1.5W | ~ 3.5VA, -- 0.6W 1.5W | ~ 3.5VA, -- 0.6W 1.5W | ~ 10VA ~ 8VA |  | ~ 3.5VA, -- 0.6W | ~ 3.5VA, -- 0.6W | RM4JA3xMW: ~ 3.3VA, -- 1.2W RM4JA3xF: ~ 3.3VA RM4JA3xM: ~ 3.4VA RM4JA3xQ: ~ 3VA | RM4JA01B: ~ 2VA RM4JA01F: ~ 3.3VA RM4JA01M: ~ 3.5VA | ~ 3VA, -- 1W | ~ 3.5VA, -- 0.6W | ~ 3.5VA, -- 0.6W | Not specified
Immunity to micro-breakage |  |  |  |  | immunity to microbreaks | Published | Published | ms | 50 | 50 | 50 | 50 |  | 50 | 10 | Not specified | Not specified | 10 | 10 | 10 | Not specified
Supply terminal |  |  |  |  | supply terminal |  |  |  | A1-A2 | A1-A2 | A1-A2 | A1-A2 |  | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2 | A1-A2
On Load Factor |  |  |  | Common C_Rly Spec | on-load factor |  |  | % | 100% | 100% | 100% | 100%
Release of input voltage |  |  |  |  | release of input voltage |  |  | V | - | - | - | -
Input Circuit Characteristics
Monitoring functions |  | Over / undercurrent (windows mode) | [6 empty] | - | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory |  | - | - | - | - | - | - | - | -
|  | Over current | [6 empty] | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory |  | Selectable with memory / without memory | Selectable with memory / without memory | Without memory | Without memory | · | Selectable with memory / without memory | - | -
|  | Under current | [6 empty] | - | Selectable with memory / without memory | Selectable with memory / without memory | Selectable with memory / without memory |  | Selectable with memory / without memory | Selectable with memory / without memory | Without memory | Without memory | - | Selectable with memory / without memory | · | ·
Full Measurement range | [7 empty] | mA | ~/-- 4…1000 | ~/-- 4…1000 | ~/-- 150…15000 | ~/-- 150…15000 |  | ~/-- 2…500 | ~/-- 150…15000 | RM4JA31xx: ~/-- 3…1000 RM4JA32xx: ~/-- 300…15000 | ~/-- 3…1000 | ~ 2000…20000 | ~/-- 2…500 | Fix 0.7A | Fix 0.7A
Input Resistance |  | E1-M / B1-C | [5 empty] | W | 2.5 | 2.5 | 0.05 | 0.05 |  | 5 | 0.05 | RM4JA31xx: 33 RM4JA32xx: ~/-- 0.06 | 33 | - | 5 | - | Not specified
|  | E2-M / B2-C | [5 empty] | W | 0.5 | 0.5 | 0.015 | 0.015 |  | 1 | 0.015 | RM4JA31xx: 10 RM4JA32xx: ~/-- 0.02 | 10 | - | 1 | 0.015 | Not specified
|  | E3-M / B3-C | [5 empty] | W | 0.1 | 0.1 | 0.005 | 0.005 |  | 0.2 | 0.005 | RM4JA31xx: 1 RM4JA32xx: ~/-- 0.006 | 1 | - | 0.2 | - | Not specified
|  | A1+ / A2- | [5 empty] | W | - | - | - | -
|  | Built in current transformer | [5 empty] | W | - | - |  | - |  | - | - | - | - | · | - | - | Not specified
Sub measurement range |  | E1-M / B1-C | [5 empty] | mA | ~/-- 4…40 | ~/-- 4…40 | ~/-- 150…1500 | ~/-- 150…1500 |  | ~/-- 2…20 | ~/-- 150…1500 | RM4JA31xx: ~/-- 3…30 RM4JA32xx: ~/-- 300…1500 | ~/-- 3…30 | - | ~/-- 2…20 | - | Not specified
|  | E2-M / B2-C | [5 empty] | mA | ~/-- 20…200 | ~/-- 20…200 | ~/-- 500…5000 | ~/-- 500…5000 |  | ~/-- 10…100 | ~/-- 500…5000 | RM4JA31xx: ~/-- 10…1000 RM4JA32xx: ~/-- 1000…5000 | ~/-- 10…1000 | - | ~/-- 10…100 | Max 12A | Max 12A
|  | E3-M / B3-C | [5 empty] | mA | ~/-- 100…1000 | ~/-- 100…1000 | ~/-- 1500…15000 | ~/-- 1500…15000 |  | ~/-- 50…500 | ~/-- 1500…15000 | RM4JA31xx: ~/-- 100…1000 RM4JA32xx: ~/-- 3000…15000 | ~/-- 100…1000 | - | ~/-- 50…500 | - | Not specified
|  | A1+ / A2- | [5 empty] | mA | - | - | - | -
|  | Built in current transformer | [5 empty] | mA | - | - | - | - |  | - | - | - | - | ~ 2000…20000 | - | - | Not specified
Threshold |  | E1-M / B1-C | [5 empty] | mA | Adjustable 10%...100% of 40 | Adjustable 10%...100% of 40 | Adjustable 10%...100% of 1500 | Adjustable 10%...100% of 1500 |  | Adjustable 10%...100% of 20 | Adjustable 10%...100% of 1500 | - | - | - | Adjustable 10%...100% of 20 | - | Not specified
|  | E2-M / B2-C | [5 empty] | mA | Adjustable 10%...100% of 200 | Adjustable 10%...100% of 200 | Adjustable 10%...100% of 5000 | Adjustable 10%...100% of 5000 |  | Adjustable 10%...100% of 100 | Adjustable 10%...100% of 5000 | Adjustable 10%...100% | Adjustable 10%...100% | - | Adjustable 10%...100% of 100 | - | Not specified
|  | E3-M / B3-C | [5 empty] | mA | Adjustable 10%...100% of 1000 | Adjustable 10%...100% of 1000 | Adjustable 10%...100% of 15000 | Adjustable 10%...100% of 15000 |  | Adjustable 10%...100% of 500 | Adjustable 10%...100% of 15000 | Adjustable 10%...100% | Adjustable 10%...100% | - | Adjustable 10%...100% of 500 | - | Not specified
|  | A1+ / A2- | [5 empty] | mA | - | - | - | -
|  | Built in current transformer | [5 empty] | mA | - | - | - | - |  | - | - | - | - | Adjustable 10%...100% of 20000 | - | - | Not specified
Hysteresis |  | E1-M / B1-C | [5 empty] | mA | Adjustable 5%...50% of threshold setting | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value |  | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...30% of threshold setting | Adjustable 5%...30% of threshold setting | - | Adjustable 5%...50% of threshold setting | - | Not specified
|  | E2-M / B2-C | [5 empty] | mA | Adjustable 5%...50% of threshold setting | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value |  | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...30% of threshold setting | Adjustable 5%...30% of threshold setting | - | Adjustable 5%...50% of threshold setting | - | Not specified
|  | E3-M / B3-C | [5 empty] | mA | Adjustable 5%...50% of threshold setting | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value | Overcurrent or Undercurrent: Adjustable 5...50 % of threshold setting Window mode: Fix 3% of full scale value |  | Adjustable 5%...50% of threshold setting | Adjustable 5%...50% of threshold setting | Adjustable 5%...30% of threshold setting | Adjustable 5%...30% of threshold setting | - | Adjustable 5%...50% of threshold setting | - | Not specified
|  | A1+ / A2- | [5 empty] | mA | - | - | - | -
|  | Built in current transformer | [5 empty] | mA | - | - | - | - |  | - | - | - | - | Fixed 15% of threshold setting | - | - | Not specified
Measurement mode | [8 empty] | Shunt resistor | Shunt resistor | Shunt resistor | Shunt resistor |  | Shunt resistor | Shunt resistor | Shunt resistor | Shunt resistor | Current transformer | Shunt resistor | Shunt resistor | Not specified
Connection terminals | [8 empty] | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M |  | E1-M, E2-M, E3-M | E1-M, E2-M, E3-M | B1-C, B2-C, B3-C | B1-C, B2-C, B3-C | Turning conductor around current transformer | E1-M, E2-M, E3-M | E2-M | Not specified
Rated frequency | [7 empty] | Hz | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 |  | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | 50 / 60 | Not specified
Frequency operating range | [7 empty] | Hz | 36…77 | 36…77 | 36…77 | 36…77 |  | 36…77 | 36…77 | Not specified | Not specified | 40…70 | 36…77 | 36…77 | Not specified
Setting accuracy | [8 empty] | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value (For 1.5A and 5A) +/- 20% of full scale value (For 15A) |  | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | +/- 10% of full scale value | Not specified
Repeat accuracy (constant parameters) | [8 empty] | +/- 0.5% | +/- 0.5% | +/- 0.5% | +/- 0.5% |  | +/- 0.5% | +/- 0.5% | Not specified | Not specified | +/- 0.5% | +/- 0.5% | +/- 0.5% | Not specified
Measurement error with supply voltage variation | [7 empty] | %/V | < 1% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range |  | < 1% over whole range | < 1% over whole range | < 0.5% over whole range | < 0.5% over whole range | < 1% over whole range | < 1% over whole range | < 1% over whole range | Not specified
Measurement error with temperature variation | [7 empty] | %/oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | 0.05% / oC |  | 0.05% / oC | 0.05% / oC | 0.06% / oC | 0.06% / oC | 0.05% / oC | 0.05% / oC | 0.05% / oC | Not specified
Maximum measuring cycles | [7 empty] | ms | 30 100 | 30 100 | 30 100 | 30 100 |  | 30 | 30 | 80 | 80 | 30 | 30 | 30 | Not specified
Measurement method | [8 empty] | True RMS | True RMS | True RMS | True RMS |  | True RMS | True RMS | True RMS | True RMS | True RMS | True RMS | True RMS | Not specified
Output Circuit Characteristics
Type of output |  |  |  |  | output type | Published | Published |  | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts |  | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 2 x C/O relay contacts | 1 x C/O relay contacts | 2 x C/O relay contacts | 21x C/O relay contacts | 1 x C/O relay contacts
Output terminal |  |  |  |  | output terminal |  |  |  | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 |  | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14, 21-22-24 | 11-12-14 | 11-12-14, 21-22-24 | 2014-11-12 | 11-12-14
Operation principle |  | R1 (11-12-14) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free |  | Energized on fault-free | Energized on fault-free | De-Energized on fault-free | De-Energized on fault-free | Selectable energized/de-energized on fault-free | Energized on fault-free | Energized on fault-free | De-Energized on fault-free
|  | R2 (21-22-24) |  |  | output logic |  |  |  | Energized on fault-free | Energized on fault-free | Energized on fault-free | Energized on fault-free
Contact material |  |  |  | Common C_Rly Spec | contacts material | Published | Published |  | Cadmium free | Cadmium free | Cadmium free | Cadmium free |  | Cadmium-free | Cadmium-free | Cadmium-free | Cadmium-free | Cadmium-free | Cadmium-free | Cadmium-free | Not specified
Mechanical durability |  |  | IEC61810-1 | Common C_Rly Spec | mechanical durability | Published | Published | Cyc | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles | 10 x 106 cycles |  | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | 30 x 106 switching cycles | Not specified
Electrical durability |  | AC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles | NO: 250VAC/8A, 75k cycles NO: 250VAC/5A, 100k cycles |  | 1 x 105 switching cycles | 1 x 105 switching cycles | 1 x 105 switching cycles | 1 x 105 switching cycles | 1 x 105 switching cycles | 1 x 105 switching cycles | 1 x 105 switching cycles | Not specified
|  | DC-1 | IEC60947-4-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles | NO: 24VDC/5A, 100k cycles
|  | AC-15 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles | NO: 250VAC/0.15A, 100k cycles
|  | DC-13 | IEC60947-5-1 | Common C_Rly Spec | electrical durability | Published |  | Cyc | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles | NO: 24VDC/1A, 100k cycles
Rated capacity |  | Rated switching voltage | IEC61810-1 | Common C_Rly Spec | [Ue] rated operational voltage | Published |  | V | 250V | 250V | 250V | 250V
|  | Rated switching current | IEC61810-1 | Common C_Rly Spec | [Ie] rated operational current | Published | Published | A | 8A | 8A | 8A | 8A
Maximum switching capacity |  | Maximum switching voltage |  | Common C_Rly Spec | maximum switching capacity | Published | Published | V | 250V | 250V | 250V | 250V |  | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250 | ~ 250
|  | Maximum switching current |  | Common C_Rly Spec | maximum switching capacity | Published | Published | A | 8A | 8A | 8A | 8A |  | 5 | ~ 5 | ~ 5 | 8 | 8 | ~ 8 | ~ 5 | ~ 5
|  | Maximum switching capacity |  | Common C_Rly Spec | maximum switching capacity | Published | Published | VA | - | - | - | - |  | 1250 | 1250 | 1250 | 2000 | 2000 | 2000 | 1250 | 1250
Minimum switching capacity |  | Minimum switching voltage | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | V | - | - | - | - |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | Not specified
|  | Minimum switching current | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published |  | mA | - | - | - | - |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | Not specified
|  | Minimum switching capacity | IEC60947-5-4 | Common C_Rly Spec | minimum switching capacity | Published | Published | mW | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 | NO: 12V/10mA, MCTF > 80,000,000 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | Not specified
Maximum voltage drop at terminals |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum voltage drop |  |  | V | - | - | - | - |  | - | - | - | - | - | - | - | -
Leakage current |  | Only for solid state output | IEC62314 | Common C_Rly Spec | maximum leakage current |  |  | mA | - | - | - | - |  | - | - | - | - | - | - | - | -
Thermal Current |  |  | IEC60947-5-1 | Common C_Rly Spec | thermal current |  |  | A | 8A | 8A | 8A | 8A
Short circuit protection |  | Relay Output by external fuse | IEC60947-5-1 | Common C_Rly Spec | short circuit protection |  |  | gG | 8A | 8A | 8A | 8A
|  | Solid State Output by external fuse | IEC62314 | Common C_Rly Spec | short circuit protection |  |  | gG | - | - | - | -
Time Delay Characteristics
Time delay functions |  | "OFF" delay |  |  | time delay type | Published |  |  | Yes | Yes | Yes | Yes |  | · | · | · | · | - | · | - | -
|  | "ON" delay |  |  | time delay type | Published |  |  | - | - | - | - |  | - | - | - | - | - | - | - | -
|  | Inhibition |  |  | time delay type | Published |  |  | - | - | - | - |  | · | · | · | · | - | · | - | -
Timing range |  | "OFF" delay |  |  | time delay range | Published | Published | s | - | Adjustable 0.1…30 | Adjustable 0.1…30 | Adjustable 0.1…30 |  | Adjustable 0.3…30 | Adjustable 0.3…30 | Adjustable 0…30 | Adjustable 0…30 | - | Adjustable 0.3…30 | - | -
|  | "ON" delay |  |  | time delay range | Published |  | s | - | - | - | - |  | - | - | - | - | - | - | - | -
|  | Inhibition |  |  | time delay range | Published | Published | s | - | - | - | - |  | Adjustable 1…20 | Adjustable 1…20 | Adjustable 1…20 | Adjustable 1…20 | - | Adjustable 1…20 | - | -
Response time |  | on crossing the threshold |  |  | response time | Published | Published | ms | Not specified =< 500ms | Not specified =< 500ms | Not specified =< 500ms | Not specified =< 500ms |  | Not specified | Not specified | Not specified | Not specified | =< 200 | Not specified | Not specified | Not specified
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
|  |  |  | Reserved for other products | response time | Published
Time delay of pick-up |  |  |  |  | power on delay | Published | Published | ms | =< 300 | =< 300 | =< 300 | =< 300 |  | =< 300 | =< 300 | =< 600 | =< 600 | =< 500 | =< 300 | =< 300 | Not specified
Reset time |  | through Un power reset |  |  | reset time | Published | Published | ms | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage |  | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage | - | =< 1500 at maximum supply voltage | =< 1500 at maximum supply voltage | Not specified
|  | through front panel reset |  | Reserved for other products | reset time | Published
|  | through input control reset |  | Reserved for other products | reset time | Published
Setting accuracy |  |  |  | Common C_Rly Spec | setting accuracy of time delay | Published | Published | % | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales |  | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | +/- 10% of full scales | - | +/- 10% of full scales | +/- 10% of full scales | Not specified
Repeat accuracy (constant parameters) |  |  |  | Common C_Rly Spec | repeat accuracy of time delay | Published |  | % | +/- 2% | +/- 2% | +/- 2% | +/- 2% |  | +/- 2% | +/- 2% | +/- 0.5% | +/- 0.5% | - | +/- 2% | +/- 2% | Not specified
Timing error with supply voltage variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/V | < 1 | < 1 | < 1 | < 1 |  | Not specified | Not specified | < 0.5% over whole range | < 0.5% over whole range | - | Not specified | Not specified | Not specified
Timing error with temperature variation |  |  |  | Common C_Rly Spec | time delay drift |  |  | %/oC | < 0.05 | < 0.05 | < 0.05 | < 0.05 |  | Not specified | Not specified | 0.07% / oC | 0.07% / oC | - | Not specified | Not specified | Not specified
LED Indication
status LED |  |  |  |  | status LED |  |  |  | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber) | Dial pointer (Green) R (Amber)
local signalling |  | Power supply availability |  |  | local signalling |  |  |  | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON | Dial pointer - ON
|  | Power supply not availability |  |  | local signalling |  |  |  | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF | Dial pointer - OFF
|  | Timing in-progress |  |  | local signalling |  |  |  | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz | R - Slow Blink (50% ON; 50% OFF) @ 1Hz
|  | Output is energized |  |  | local signalling |  |  |  | R - ON | R - ON | R - ON | R - ON
|  | Output is de-energized |  |  | local signalling |  |  |  | R - OFF | R - OFF | R - OFF | R - OFF
|  | Range Setting Changes |  |  | local signalling |  |  |  | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz | All LEDs - Fast Blink (5% ON; 95% OFF) @ 1Hz
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
local signalling
Special Features
True RMS | [8 empty] | Yes | Yes | Yes | Yes
Backlight Indicator | [8 empty] | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product | 1) Will always illuminated when power is supplied to the product
Diagnostic Button |  |  |  |  | diagnostic button | Published |  |  | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated | Output will be de-energized when activated
Pre-Alarm Output | [8 empty] | - | - | - | -
Output | [8 empty] | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized | 1) When input monitored @ normal condition, output is always energized 2) When input monitored @ fault condition, output is always de-energized
Reliability Data
Reliability Data |  | MTTF |  |  | safety reliability data | Published |  |  | 2,600,000 hours | 2,600,000 hours | 2,600,000 hours | 2,600,000 hours
|  | B10 |  |  | safety reliability data | Published |  |  | 270,000 hours | 270,000 hours | 270,000 hours | 270,000 hours
|  | MTTFd | [6 empty] | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product) | Cannot declare MTTF = MTTFd (Note: customer confuses as safety product)
|  | B10d | [6 empty] | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product) | Cannot declare B10 = B10d (Note: customer confuses as safety product)
Drawing / Diagram
Note on D18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.1
Note on A42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Typical Product Operation Rate: 100% - product mostly will be powered and in operation in the actual application 50% - product is powered and in operation in the actual application @ ~50% of the time
Note on A44: Protection : Normal performance within the specification limits Command and control : Normal performance within the specification limits Measurement : Temporary degradation during test, with self-recovery at the end of the test. No loss of stored data Integral human-machine interface and visual alarms: Temporary degradation or loss of function during test, with self-recovery at the end of the test. No loss of stored data Data communication : Possible bit error rate increase but no loss of transmitted data
Note on A156: Measured with Yokogawa power meter and 3P4W connection
Note on A160: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The minimum level of supply voltage that causes the product out-of power to operate. This must be a value other than 0V or total cut-off
Note on D226: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-4-1 GB14048.4
Note on D227: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-4-1 GB14048.4
Note on D228: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-5-1 GB14048.5
Note on D229: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC61810-1 IEC60947-5-1 GB14048.5
Note on D240: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.5
Note on D241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: IEC60947-5-1 GB14048.5
Note on A287: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Product Developed Before 2019: follow UTE C80-810 Product Developed After 2019 and require recalculation of MTBF: follow SN29500

## RM22TG20
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram
Correction
two
two

## RM22TR33
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## RM22TR31
Back To Main
Dimension Drawing |  | Wiring Connection |  | Function Diagram
| Same as RM22TR33 |  | Same as RM22TR33 |  | Combined into RM22TR33

## RM22TU23
Back To Main
Dimension Drawing |  | Wiring Connection |  | Function Diagram
| Same as RM22TR33 |  | Same as RM22TR33

## RM22TU21
Back To Main
Dimension Drawing |  | Wiring Connection |  | Function Diagram
| Same as RM22TR33 |  | Same as RM22TR33 |  | Combined into RM22TU23

## RM22TA33
Back To Main
Dimension Drawing |  | Wiring Connection |  | Function Diagram
| Same as RM22TR33 |  | Same as RM22TR33

## RM22TA31
Back To Main
Dimension Drawing |  | Wiring Connection |  | Function Diagram
| Same as RM22TR33 |  | Same as RM22TR33 |  | Combined into RM22TA33

## RM17TE00
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## RM10TE00
Back To Main
Dimension Drawing |  | Wiring Connection |  | Function Diagram
| Same as RM17TE00 |  | Same as RM17TE00 |  | Same as RM17TE00

## 84873025
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## RM35UB3N30
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873221
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873895
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## RM17UB310
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873222
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873896
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## RM17TU00
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873023
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873804
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873805
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## RM35TF30
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873026
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873893
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## RM17TG20
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram
Same as RM22TG20

## RM17TG00
Back To Main
Dimension Drawing |  | Wiring Connection | Function Diagram
| Same as RM17TG20 |  |  | Same as RM22TG20

## RM10TG00
Back To Main
Dimension Drawing |  | Wiring Connection |  | Function Diagram
| Same as RM17TG00 |  | Same as RM17TG00 |  | Same as RM17TG00

## 84873021
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873034
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873890
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873891
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873195
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873029 (CRZ)
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## RM17TA00
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873024
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873892
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## RM17TT00
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873022
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## RM35TF30SP01
Back To Main
Dimension Drawing |  | Wiring Connection |  | Function Diagram
| Same as RM35TF30 |  | Same as RM35TF30 |  | Same as RM35TF30

## RM35UB330
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873220
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## 84873894
Back To Main
Dimension Drawing | Wiring Connection | Function Diagram

## Form Factor (hidden)
Product Form Factor
|  |  |  | Used for customer installation: - mm + inches - 1 decimal point - include mounting info | Used for 3D image creation - used together with STEP + Laser Marking File | Special needs: - User assembly information used for IS
Type | RM22 | Terminal Assignment + User Interface |  | Product Dimension
|  | Draft (During Initial Proj Phase) | Laser Marking File (pdf format) | 2D (pdf @ 3rd Angle Projection) | 3D (Step File @ Surface) | 3D (pdf, use for IS)
Current | RM22JA21MR |  | Released in Symphony | Released in Symphony | Released in Symphony | Released in Symphony
RM22JA31MR
RM35JA32MR
RM35JA32MT
Voltage | RM22UA21MR
RM22UA22MR
RM22UA23MR
RM22UA31MR
RM22UA32MR
RM22UA33MR
RM22UA33MT
RM22UB34
3 Phase | RM22TA31
RM22TA33
RM22TG20
RM22TR31
RM22TR33
RM22TU21
RM22TU23
Level | RM22LA32MR
RM22LA32MT
RM22LG11MR
RM22LG11MT

## Function Diagram (hidden)
Function Diagram
Type | RM22 |  | Type of Function
|  | Base Reference | Function 1 | Function 2 | Function 3 | Function 4 | Function 5 | Function 6
Current | RM22JA21MR | RM35JA31MW
| RM22JA31MR | RM35JA31MW
| RM35JA32MR | RM35JA32MW
| RM35JA32MT | RM35JA32MW
Voltage | RM22UA21MR | RM35UA11MW
| RM22UA22MR | RM35UA12MW
| RM22UA23MR | RM35UA13MW
| RM22UA31MR | RM35UA11MW
| RM22UA32MR | RM35UA12MW
| RM22UA33MR | RM35UA13MW
| RM22UA33MT | RM35UA13MW
| RM22UB34 | RM17UEB15
3 Phase | RM22TG20 | RM17TG20
| RM22TA31 | RM17TA00
| RM22TA33 | RM17TA00
| RM22TR31 | RM17UB310
| RM22TR33 | RM17UB310
| RM22TU21 | RM17TU00
| RM22TU23 | RM17TU00
Level | RM22LA32MR | RM35LM33MW
| RM22LA32MT | RM35LM33MW
| RM22LG11MR | RM35LM33MW
| RM22LG11MT | RM35LM33MW
REMOVE PORTIONS SHADED IN RED
with Off Delay
with On Delay
NEW
with Off Delay
with On Delay
NEW
with Off Delay
NEW
Change from Tt1 & Tt2 to Tt
with On Delay
NEW
with Off Delay
with On Delay
2 Level
1 Level
with On Delay
with Off Delay
NEW
NEW
1 Level
2 Level
2 Level
1 Level
NEW
1 Level
Refer to online Datasheet or Instruction Sheet for latest function diagram
http://www.schneider-electric.com/en/product-range-selector/528-zelio-control

## Wiring Diagram (hidden)
Wiring Diagram
Type | RM22 |  | Type of Wiring Diagram
|  | Base Reference | Internal | External
Current | RM22JA21MR | RM17TG20 | Refer to laser marking file | -
| RM22JA31MR | RM17TA00 | Refer to laser marking file | -
| RM35JA32MR | RM17TA00 | Refer to laser marking file | -
| RM35JA32MT | RM17TU00 | Refer to laser marking file | -
Voltage | RM22UA21MR | RM17TU00 | Refer to laser marking file | -
| RM22UA22MR | RM17UB310 | Refer to laser marking file | -
| RM22UA23MR | RM17UB310 | Refer to laser marking file | -
| RM22UA31MR | RM35UA11MW | Refer to laser marking file | -
| RM22UA32MR | RM35UA12MW | Refer to laser marking file | -
| RM22UA33MR | RM35UA13MW | Refer to laser marking file | -
| RM22UA33MT | RM35UA11MW | Refer to laser marking file | -
| RM22UB34 | RM35UA12MW | Refer to laser marking file | -
3 Phase | RM22TA31 | RM35UA13MW | Refer to laser marking file | -
| RM22TA33 | RM35UA13MW | Refer to laser marking file | -
| RM22TG20 | RM17UEB15 | Refer to laser marking file | -
| RM22TR31 | RM35JA31MW | Refer to laser marking file | -
| RM22TR33 | RM35JA31MW | Refer to laser marking file | -
| RM22TU21 | RM35JA32MW | Refer to laser marking file | -
| RM22TU23 | RM35JA32MW | Refer to laser marking file | -
Level | RM22LA32MR | RM35LM33MW | Refer to laser marking file | -
| RM22LA32MT | RM35LM33MW | Refer to laser marking file | -
| RM22LG11MR | RM35LM33MW | Refer to laser marking file | -
| RM22LG11MT | RM35LM33MW | Refer to laser marking file | -

## Notation (hidden)
Notation:
Derived from Catalogue
Derived from DOC
Derived from Standard (Assume strictly follow the standard)
Derived from Actual Measurement
General List of Specification Items - All Control Relays share the same specification
Printed Circuit Board Design Parameters
Specification Item is not applicable due to not required in the product standard
Red Text | Unique Value Proposition / Alignment of Specification
Purple Text
Green Italic Text | Not Specified
Brown Text